## Scenario Descriptions
Scenario | Offline | Redispatch
Scenario 1 | · Cooper 1 & 2 | · Import from the North to pick up lost Cooper generation.
· LG&E/KU’s Brown base case generation “as dispatched” in the models

## Thermal Overloads
[13 empty] | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Scenario 4
[12 empty] | Violation Count | 0 | 56 | 0 | 34 | 0 | 54 | 0 | 56
Monitored Facility | Fr Bus | Fr Name | To Bus | To Name | CktId | kVs | Area | Mon Type | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Cont Type | S1_O0_SUM | S1_O0_WIN | S2_O0_SUM | S2_O0_WIN | S3_O0_SUM | S3_O0_WIN | S4_O0_SUM | S4_O0_WIN
342703 5CASEY CO 161 342760 5LIBERTY J 161 1 | 342703 | 5CASEY CO | 342760 | 5LIBERTY J | 1 | 161 | 320 | PJM | 148 | 153 | P6:1983 | N11 | 55.98 | 103.07 | 56.17 | 101.89 | 53.53 | 99.36 | 53.94 | 100.29
342703 5CASEY CO 161 342760 5LIBERTY J 161 1 | 342703 | 5CASEY CO | 342760 | 5LIBERTY J | 1 | 161 | 320 | PJM | 148 | 153 | P6:5525 | N11 | 55.98 | 103.07 | 56.17 | 101.89 | 53.53 | 99.36 | 53.94 | 100.29
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:11091 | N11 | 53.49 | 99 | 60.03 | 112.35 | 50.18 | 98.78 | 50.83 | 96.06
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:11357 | N11 | 68.72 | 125.65 | 68.15 | 125.21 | 66.06 | 124.16 | 66.33 | 123.23
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:11406 | N11 | 52.85 | 98.43 | 58.31 | 106.19 | 48.08 | 95.76 | 49.16 | 93.53
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:11413 | N11 | 53.49 | 99 | 60.03 | 112.35 | 50.18 | 98.78 | 50.83 | 96.06
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:11416 | N11 | 52.99 | 98.2 | 57.55 | 106.55 | 48.32 | 96.15 | 49.29 | 93.85
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:11577 | N11 | 52.99 | 98.2 | 57.55 | 106.55 | 48.32 | 96.15 | 49.29 | 93.85
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:12977 | N11 | 71.3 | 129.14 | 71.42 | 127.33 | 69.69 | 125.34 | 69.88 | 126.38
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:1983 | N11 | 72.91 | 133.43 | 72.91 | 132.09 | 71.21 | 130.03 | 71.38 | 131.05
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:2008 | N11 | 66.28 | 121.66 | 65.21 | 120.91 | 63.97 | 120.07 | 64.22 | 119.01
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:2019 | N11 | 68.72 | 125.65 | 68.15 | 125.21 | 66.06 | 124.16 | 66.33 | 123.23
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:2029 | N11 | 71.3 | 129.14 | 71.42 | 127.33 | 69.69 | 125.34 | 69.88 | 126.38
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:5525 | N11 | 72.91 | 133.43 | 72.91 | 132.09 | 71.21 | 130.03 | 71.38 | 131.05
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:9575 | N11 | 66.28 | 121.66 | 65.21 | 120.91 | 63.97 | 120.07 | 64.22 | 119.01
342703 5CASEY CO 161 342769 5MARION CO 161 1 | 342703 | 5CASEY CO | 342769 | 5MARION CO | 1 | 161 | 320 | PJM | 148 | 153 | P6:9957 | N11 | 52.85 | 98.43 | 58.31 | 106.19 | 48.08 | 95.76 | 49.16 | 93.53
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:10605 | N11 | 75.26 | 103.38 | 63.7 | 98.45 | 79.47 | 111.08 | 79.15 | 109.57
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11080 | N11 | 77.62 | 105.73 | 65.62 | 100.9 | 81.87 | 113.56 | 81.71 | 113.44
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11091 | N11 | 77.68 | 106.54 | 65.72 | 101.04 | 82.18 | 114.05 | 81.41 | 112.94
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11362 | N11 | 74.87 | 105.72 | 62.27 | 97.28 | 78.8 | 109.01 | 78.83 | 110.07
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11364 | N11 | 75.86 | 103.74 | 59.09 | 91.34 | 79.72 | 108.66 | 79.28 | 109.48
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11395 | N11 | 77.14 | 105.32 | 65.09 | 100.15 | 81.8 | 112.9 | 81.39 | 112.73
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11396 | N11 | 76.78 | 104.88 | 64.64 | 99.2 | 81.01 | 112 | 80.86 | 112.02
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11406 | N11 | 75.02 | 102.97 | 61.83 | 93.22 | 79.48 | 107.61 | 78.68 | 107.59
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11410 | N11 | 75.26 | 103.38 | 63.7 | 98.45 | 79.47 | 111.08 | 79.15 | 109.57
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11413 | N11 | 77.68 | 106.54 | 65.72 | 101.04 | 82.18 | 114.05 | 81.41 | 112.94
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11416 | N11 | 75.16 | 102.44 | 61.84 | 93.33 | 79.41 | 108.07 | 78.83 | 107.95
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11424 | N11 | 76.71 | 104.83 | 64.57 | 99.24 | 80.99 | 112.03 | 80.85 | 112.01
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11429 | N11 | 77.51 | 103.65 | 63.32 | 93.33 | 81.58 | 107.98 | 82.05 | 109.76
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:11577 | N11 | 75.16 | 102.44 | 61.84 | 93.33 | 79.41 | 108.07 | 78.83 | 107.95
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:12862 | N11 | 76.64 | 103.73 | 63.98 | 98.01 | 81.5 | 110.78 | 80.78 | 111.22
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:12873 | N11 | 76.71 | 104.83 | 64.57 | 99.24 | 80.99 | 112.03 | 80.85 | 112.01
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:12982 | N11 | 76.26 | 107.77 | 65.34 | 102.89 | 79.6 | 112.57 | 79.83 | 113.11
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:12984 | N11 | 76.4 | 104.46 | 61.29 | 94.68 | 80.63 | 111.14 | 80 | 111.22
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:13683 | N11 | 77.51 | 103.65 | 63.32 | 93.33 | 81.58 | 107.98 | 82.05 | 109.76
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:2793 | N11 | 77.23 | 108.06 | 65.95 | 103.31 | 80.56 | 112.35 | 80.67 | 113.1
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:2818 | N11 | 74.34 | 103.4 | 61.24 | 94.86 | 77.64 | 106.64 | 77.75 | 108
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:2829 | N11 | 74.87 | 105.72 | 62.27 | 97.28 | 78.8 | 109.01 | 78.83 | 110.07
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:2839 | N11 | 76.26 | 107.77 | 65.34 | 102.89 | 79.6 | 112.57 | 79.83 | 113.11
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:3117 | N11 | 77.44 | 105 | 61.71 | 94.73 | 81.4 | 110.67 | 80.62 | 111.2
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:3142 | N11 | 75.18 | 101.97 | 58.29 | 89.59 | 79.34 | 106.7 | 78.47 | 107.89
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:3153 | N11 | 75.86 | 103.74 | 59.09 | 91.34 | 79.72 | 108.66 | 79.28 | 109.48
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:3163 | N11 | 76.4 | 104.46 | 61.29 | 94.68 | 80.63 | 111.14 | 80 | 111.22
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:5530 | N11 | 77.23 | 108.06 | 65.95 | 103.31 | 80.56 | 112.35 | 80.67 | 113.1
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:5532 | N11 | 77.44 | 105 | 61.71 | 94.73 | 81.4 | 110.67 | 80.62 | 111.2
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:8164 | N11 | 77.17 | 104.58 | 65.32 | 99.52 | 81.8 | 111.86 | 81.44 | 112.09
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:8175 | N11 | 77.14 | 105.32 | 65.09 | 100.15 | 81.8 | 112.9 | 81.39 | 112.73
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:8326 | N11 | 76.71 | 103.93 | 64.14 | 97.84 | 81.59 | 110.91 | 80.87 | 111.3
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:8337 | N11 | 76.78 | 104.88 | 64.64 | 99.2 | 81.01 | 112 | 80.86 | 112.02
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:9580 | N11 | 74.34 | 103.4 | 61.24 | 94.86 | 77.64 | 106.64 | 77.75 | 108
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:9582 | N11 | 75.18 | 101.97 | 58.29 | 89.59 | 79.34 | 106.7 | 78.47 | 107.89
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:9631 | N11 | 77.62 | 105.73 | 65.62 | 100.9 | 81.87 | 113.56 | 81.71 | 113.44
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:9642 | N11 | 76.64 | 103.73 | 63.98 | 98.01 | 81.5 | 110.78 | 80.78 | 111.22
342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 1 | 161 | 320\347 | PJM | 334.6 | 334.6 | P6:9957 | N11 | 75.02 | 102.97 | 61.83 | 93.22 | 79.48 | 107.61 | 78.68 | 107.59
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:11357 | N11 | 73.05 | 109.95 | 64.86 | 103.09 | 75.88 | 115.18 | 75.7 | 114.18
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:12977 | N11 | 75.51 | 114.4 | 67.25 | 106.65 | 78.29 | 118.01 | 78.41 | 118.23
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:1983 | N11 | 75.59 | 115.16 | 67.27 | 107.72 | 78.23 | 119.1 | 78.35 | 119.24
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:2008 | N11 | 72.7 | 109.46 | 64.1 | 102.24 | 75.49 | 114.1 | 75.44 | 113.09
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:2019 | N11 | 73.05 | 109.95 | 64.86 | 103.09 | 75.88 | 115.18 | 75.7 | 114.18
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:2029 | N11 | 75.51 | 114.4 | 67.25 | 106.65 | 78.29 | 118.01 | 78.41 | 118.23
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:5525 | N11 | 75.59 | 115.16 | 67.27 | 107.72 | 78.23 | 119.1 | 78.35 | 119.24
342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1 | 342823 | 5WAYNE CO | 360486 | 5WAYNE CO KY | 1 | 161 | 320\347 | PJM | 127 | 131 | P6:9575 | N11 | 72.7 | 109.46 | 64.1 | 102.24 | 75.49 | 114.1 | 75.44 | 113.09

## Low Voltages
[8 empty] | Scenario 1 |  | Scenario 2 |  | Scenario 3 |  | Scenario 4
[7 empty] | Violation Count | 0 | 168 | 0 | 193 | 0 | 204 | 0 | 206
Bus # | Bus Name | Area | Base kV | Cont Name | Cont Type | Min Volt Limit | Max Volt Limit | S1_O0_SUM | S1_O0_WIN | S2_O0_SUM | S2_O0_WIN | S3_O0_SUM | S3_O0_WIN | S4_O0_SUM | S4_O0_WIN
342703 | 5CASEY CO | 320 | 161 | P6:11357 | N11 | 0.93 | 1.06 | 1.0007 | 0.8895 | 0.9947 | 0.8618 | 0.9847 | 0.8485 | 0.9988 | 0.8702
342703 | 5CASEY CO | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9949 | 0.8685 | 0.9861 | 0.8469 | 0.9847 | 0.8388 | 0.99 | 0.8521
342703 | 5CASEY CO | 320 | 161 | P6:1983 | N11 | 0.93 | 1.06 | 0.9949 | 0.8672 | 0.9863 | 0.8435 | 0.9847 | 0.8353 | 0.9957 | 0.8489
342703 | 5CASEY CO | 320 | 161 | P6:2008 | N11 | 0.93 | 1.06 | 1.0031 | 0.8915 | 0.9947 | 0.868 | 0.9903 | 0.8569 | 0.9999 | 0.8779
342703 | 5CASEY CO | 320 | 161 | P6:2019 | N11 | 0.93 | 1.06 | 1.0007 | 0.8895 | 0.9947 | 0.8618 | 0.9847 | 0.8485 | 0.9988 | 0.8702
342703 | 5CASEY CO | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9949 | 0.8685 | 0.9861 | 0.8469 | 0.9847 | 0.8388 | 0.99 | 0.8521
342703 | 5CASEY CO | 320 | 161 | P6:5525 | N11 | 0.93 | 1.06 | 0.9949 | 0.8672 | 0.9863 | 0.8435 | 0.9847 | 0.8353 | 0.9957 | 0.8489
342703 | 5CASEY CO | 320 | 161 | P6:9575 | N11 | 0.93 | 1.06 | 1.0031 | 0.8915 | 0.9947 | 0.868 | 0.9903 | 0.8569 | 0.9999 | 0.8779
342715 | 5COOPER1 | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9896 | 0.842 | 0.9783 | 0.8213 | 0.9876 | 0.8159 | 0.9917 | 0.8289
342715 | 5COOPER1 | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9896 | 0.842 | 0.9783 | 0.8213 | 0.9876 | 0.8159 | 0.9917 | 0.8289
342718 | 5COOPER2 | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9896 | 0.842 | 0.9783 | 0.8214 | 0.9876 | 0.8159 | 0.9917 | 0.829
342733 | 5GREEN CO | 320 | 161 | P6:10075 | N11 | 0.93 | 1.06 | 0.9451 | 0.9072 | 0.9503 | 0.8841 | 0.9444 | 0.8968 | 0.9442 | 0.8883
342733 | 5GREEN CO | 320 | 161 | P6:11371 | N11 | 0.93 | 1.06 | 0.9688 | 0.9163 | 0.9708 | 0.8855 | 0.9571 | 0.8891 | 0.9622 | 0.896
342733 | 5GREEN CO | 320 | 161 | P6:12991 | N11 | 0.93 | 1.06 | 0.9732 | 0.9164 | 0.9717 | 0.8804 | 0.9568 | 0.8857 | 0.961 | 0.8946
342733 | 5GREEN CO | 320 | 161 | P6:1975 | N11 | 0.93 | 1.06 | 0.9798 | 0.9274 | 0.9721 | 0.9172 | 0.9596 | 0.9001 | 0.9683 | 0.8953
342733 | 5GREEN CO | 320 | 161 | P6:2623 | N11 | 0.93 | 1.06 | 0.975 | 0.9404 | 0.9774 | 0.9283 | 0.956 | 0.915 | 0.9628 | 0.9066
342733 | 5GREEN CO | 320 | 161 | P6:4229 | N11 | 0.93 | 1.06 | 0.9798 | 0.9274 | 0.9721 | 0.9172 | 0.9596 | 0.9001 | 0.9683 | 0.8953
342733 | 5GREEN CO | 320 | 161 | P6:4233 | N11 | 0.93 | 1.06 | 0.975 | 0.9404 | 0.9774 | 0.9283 | 0.956 | 0.915 | 0.9628 | 0.9066
342733 | 5GREEN CO | 320 | 161 | P6:4251 | N11 | 0.93 | 1.06 | 0.97 | 0.9213 | 0.9688 | 0.8827 | 0.9544 | 0.8918 | 0.9611 | 0.8965
342733 | 5GREEN CO | 320 | 161 | P6:4257 | N11 | 0.93 | 1.06 | 0.9451 | 0.9079 | 0.9502 | 0.8872 | 0.9445 | 0.8996 | 0.9397 | 0.8918
342733 | 5GREEN CO | 320 | 161 | P6:4273 | N11 | 0.93 | 1.06 | 0.9574 | 0.9262 | 0.9599 | 0.9058 | 0.9506 | 0.9093 | 0.9534 | 0.9002
342733 | 5GREEN CO | 320 | 161 | P6:4276 | N11 | 0.93 | 1.06 | 0.9701 | 0.9244 | 0.9715 | 0.8896 | 0.9548 | 0.897 | 0.9615 | 0.9004
342733 | 5GREEN CO | 320 | 161 | P6:4279 | N11 | 0.93 | 1.06 | 0.9451 | 0.9072 | 0.9503 | 0.8841 | 0.9444 | 0.8968 | 0.9442 | 0.8883
342733 | 5GREEN CO | 320 | 161 | P6:4297 | N11 | 0.93 | 1.06 | 0.9732 | 0.9164 | 0.9717 | 0.8804 | 0.9568 | 0.8857 | 0.961 | 0.8946
342754 | 5LAUREL CO | 320 | 161 | P6:10548 | N11 | 0.93 | 1.06 | 0.9717 | 0.9135 | 0.9696 | 0.9018 | 0.9657 | 0.9034 | 0.9735 | 0.8907
342754 | 5LAUREL CO | 320 | 161 | P6:10556 | N11 | 0.93 | 1.06 | 0.9699 | 0.9116 | 0.9678 | 0.9001 | 0.9639 | 0.9016 | 0.9717 | 0.8889
342754 | 5LAUREL CO | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9912 | 0.8834 | 0.9801 | 0.8689 | 0.9911 | 0.8614 | 0.9983 | 0.8722
342754 | 5LAUREL CO | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9912 | 0.8834 | 0.9801 | 0.8689 | 0.9911 | 0.8614 | 0.9983 | 0.8722
342754 | 5LAUREL CO | 320 | 161 | P6:2134 | N11 | 0.93 | 1.06 | 0.98 | 0.9127 | 0.9813 | 0.8944 | 0.9721 | 0.9009 | 0.9763 | 0.886
342754 | 5LAUREL CO | 320 | 161 | P6:2176 | N11 | 0.93 | 1.06 | 0.9717 | 0.9135 | 0.9696 | 0.9018 | 0.9657 | 0.9034 | 0.9735 | 0.8907
342754 | 5LAUREL CO | 320 | 161 | P6:3430 | N11 | 0.93 | 1.06 | 0.9778 | 0.9106 | 0.9792 | 0.8925 | 0.97 | 0.8988 | 0.9741 | 0.8841
342754 | 5LAUREL CO | 320 | 161 | P6:3472 | N11 | 0.93 | 1.06 | 0.9699 | 0.9116 | 0.9678 | 0.9001 | 0.9639 | 0.9016 | 0.9717 | 0.8889
342754 | 5LAUREL CO | 320 | 161 | P6:3744 | N11 | 0.93 | 1.06 | 0.98 | 0.9127 | 0.9813 | 0.8944 | 0.9721 | 0.9009 | 0.9763 | 0.886
342754 | 5LAUREL CO | 320 | 161 | P6:3752 | N11 | 0.93 | 1.06 | 0.9778 | 0.9106 | 0.9792 | 0.8925 | 0.97 | 0.8988 | 0.9741 | 0.8841
342757 | 5LAUREL DAM | 320 | 161 | P6:10548 | N11 | 0.93 | 1.06 | 0.972 | 0.9137 | 0.9699 | 0.902 | 0.966 | 0.9036 | 0.9738 | 0.8909
342757 | 5LAUREL DAM | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9964 | 0.8676 | 0.9798 | 0.8506 | 0.9959 | 0.844 | 0.9931 | 0.8557
342757 | 5LAUREL DAM | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9964 | 0.8676 | 0.9798 | 0.8506 | 0.9959 | 0.844 | 0.9931 | 0.8557
342757 | 5LAUREL DAM | 320 | 161 | P6:2134 | N11 | 0.93 | 1.06 | 0.9802 | 0.913 | 0.9815 | 0.8946 | 0.9723 | 0.9011 | 0.9765 | 0.8863
342757 | 5LAUREL DAM | 320 | 161 | P6:2176 | N11 | 0.93 | 1.06 | 0.972 | 0.9137 | 0.9699 | 0.902 | 0.966 | 0.9036 | 0.9738 | 0.8909
342757 | 5LAUREL DAM | 320 | 161 | P6:3744 | N11 | 0.93 | 1.06 | 0.9802 | 0.913 | 0.9815 | 0.8946 | 0.9723 | 0.9011 | 0.9765 | 0.8863
342760 | 5LIBERTY J | 320 | 161 | P6:11357 | N11 | 0.93 | 1.06 | 1.0025 | 0.8789 | 0.9916 | 0.8506 | 0.9892 | 0.8372 | 1.0018 | 0.86
342760 | 5LIBERTY J | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9963 | 0.8534 | 0.9858 | 0.8322 | 0.9892 | 0.8251 | 0.9921 | 0.8383
342760 | 5LIBERTY J | 320 | 161 | P6:1983 | N11 | 0.93 | 1.06 | 0.9963 | 0.8523 | 0.9859 | 0.8288 | 0.9892 | 0.8215 | 0.9982 | 0.835
342760 | 5LIBERTY J | 320 | 161 | P6:2008 | N11 | 0.93 | 1.06 | 1.0053 | 0.8804 | 0.9968 | 0.8568 | 0.9892 | 0.8461 | 1.0026 | 0.8682
342760 | 5LIBERTY J | 320 | 161 | P6:2019 | N11 | 0.93 | 1.06 | 1.0025 | 0.8789 | 0.9916 | 0.8506 | 0.9892 | 0.8372 | 1.0018 | 0.86
342760 | 5LIBERTY J | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9963 | 0.8534 | 0.9858 | 0.8322 | 0.9892 | 0.8251 | 0.9921 | 0.8383
342760 | 5LIBERTY J | 320 | 161 | P6:5525 | N11 | 0.93 | 1.06 | 0.9963 | 0.8523 | 0.9859 | 0.8288 | 0.9892 | 0.8215 | 0.9982 | 0.835
342769 | 5MARION CO | 320 | 161 | P6:10075 | N11 | 0.93 | 1.06 | 0.9466 | 0.909 | 0.9511 | 0.8861 | 0.9459 | 0.899 | 0.9458 | 0.8906
342769 | 5MARION CO | 320 | 161 | P6:11357 | N11 | 0.93 | 1.06 | 0.9905 | 0.9121 | 0.9891 | 0.8858 | 0.9799 | 0.8728 | 0.9909 | 0.8923
342769 | 5MARION CO | 320 | 161 | P6:11371 | N11 | 0.93 | 1.06 | 0.9704 | 0.9183 | 0.9729 | 0.888 | 0.9592 | 0.892 | 0.965 | 0.898
342769 | 5MARION CO | 320 | 161 | P6:11493 | N11 | 0.93 | 1.06 | 0.9763 | 0.9216 | 0.9769 | 0.8838 | 0.9622 | 0.9023 | 0.9695 | 0.899
342769 | 5MARION CO | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9905 | 0.8986 | 0.9839 | 0.8766 | 0.9799 | 0.8671 | 0.9844 | 0.8804
342769 | 5MARION CO | 320 | 161 | P6:12991 | N11 | 0.93 | 1.06 | 0.9754 | 0.9185 | 0.9735 | 0.8824 | 0.9589 | 0.8886 | 0.9646 | 0.8967
342769 | 5MARION CO | 320 | 161 | P6:13113 | N11 | 0.93 | 1.06 | 0.9905 | 0.9232 | 0.9732 | 0.8721 | 0.9799 | 0.8966 | 0.9844 | 0.8945
342769 | 5MARION CO | 320 | 161 | P6:13153 | N11 | 0.93 | 1.06 | 0.9357 | 0.9022 | 0.942 | 0.872 | 0.9368 | 0.8846 | 0.936 | 0.8768
342769 | 5MARION CO | 320 | 161 | P6:1975 | N11 | 0.93 | 1.06 | 0.9828 | 0.9309 | 0.973 | 0.9209 | 0.9626 | 0.9041 | 0.9723 | 0.8994
342769 | 5MARION CO | 320 | 161 | P6:1983 | N11 | 0.93 | 1.06 | 0.9905 | 0.8971 | 0.984 | 0.8737 | 0.9799 | 0.8641 | 0.9844 | 0.8776
342769 | 5MARION CO | 320 | 161 | P6:2008 | N11 | 0.93 | 1.06 | 0.9964 | 0.914 | 0.9891 | 0.891 | 0.9799 | 0.8797 | 0.9922 | 0.8984
342769 | 5MARION CO | 320 | 161 | P6:2019 | N11 | 0.93 | 1.06 | 0.9905 | 0.9121 | 0.9891 | 0.8858 | 0.9799 | 0.8728 | 0.9909 | 0.8923
342769 | 5MARION CO | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9905 | 0.8986 | 0.9839 | 0.8766 | 0.9799 | 0.8671 | 0.9844 | 0.8804
342769 | 5MARION CO | 320 | 161 | P6:24051 | N11 | 0.93 | 1.06 | 0.9763 | 0.9216 | 0.9769 | 0.8838 | 0.9622 | 0.9023 | 0.9695 | 0.899
342769 | 5MARION CO | 320 | 161 | P6:24061 | N11 | 0.93 | 1.06 | 0.9905 | 0.9232 | 0.9732 | 0.8721 | 0.9799 | 0.8966 | 0.9844 | 0.8945
342769 | 5MARION CO | 320 | 161 | P6:2623 | N11 | 0.93 | 1.06 | 0.9776 | 0.9423 | 0.9795 | 0.9303 | 0.9581 | 0.9172 | 0.9662 | 0.9087
342769 | 5MARION CO | 320 | 161 | P6:2785 | N11 | 0.93 | 1.06 | 0.9552 | 0.9286 | 0.9552 | 0.922 | 0.9271 | 0.9048 | 0.9397 | 0.8954
342769 | 5MARION CO | 320 | 161 | P6:4229 | N11 | 0.93 | 1.06 | 0.9828 | 0.9309 | 0.973 | 0.9209 | 0.9626 | 0.9041 | 0.9723 | 0.8994
342769 | 5MARION CO | 320 | 161 | P6:4233 | N11 | 0.93 | 1.06 | 0.9776 | 0.9423 | 0.9795 | 0.9303 | 0.9581 | 0.9172 | 0.9662 | 0.9087
342769 | 5MARION CO | 320 | 161 | P6:4234 | N11 | 0.93 | 1.06 | 0.9552 | 0.9286 | 0.9552 | 0.922 | 0.9271 | 0.9048 | 0.9397 | 0.8954
342769 | 5MARION CO | 320 | 161 | P6:4257 | N11 | 0.93 | 1.06 | 0.9466 | 0.9097 | 0.951 | 0.8891 | 0.9459 | 0.9018 | 0.9416 | 0.8941
342769 | 5MARION CO | 320 | 161 | P6:4273 | N11 | 0.93 | 1.06 | 0.9595 | 0.9291 | 0.9621 | 0.9089 | 0.9527 | 0.9126 | 0.9563 | 0.9035
342769 | 5MARION CO | 320 | 161 | P6:4276 | N11 | 0.93 | 1.06 | 0.9718 | 0.9265 | 0.9736 | 0.8923 | 0.9564 | 0.9 | 0.964 | 0.9025
342769 | 5MARION CO | 320 | 161 | P6:4279 | N11 | 0.93 | 1.06 | 0.9466 | 0.909 | 0.9511 | 0.8861 | 0.9459 | 0.899 | 0.9458 | 0.8906
342769 | 5MARION CO | 320 | 161 | P6:4287 | N11 | 0.93 | 1.06 | 0.9704 | 0.9183 | 0.9729 | 0.888 | 0.9592 | 0.892 | 0.965 | 0.898
342769 | 5MARION CO | 320 | 161 | P6:4297 | N11 | 0.93 | 1.06 | 0.9754 | 0.9185 | 0.9735 | 0.8824 | 0.9589 | 0.8886 | 0.9646 | 0.8967
342769 | 5MARION CO | 320 | 161 | P6:4298 | N11 | 0.93 | 1.06 | 0.9357 | 0.9022 | 0.942 | 0.872 | 0.9368 | 0.8846 | 0.936 | 0.8768
342769 | 5MARION CO | 320 | 161 | P6:5525 | N11 | 0.93 | 1.06 | 0.9905 | 0.8971 | 0.984 | 0.8737 | 0.9799 | 0.8641 | 0.9844 | 0.8776
342769 | 5MARION CO | 320 | 161 | P6:9575 | N11 | 0.93 | 1.06 | 0.9964 | 0.914 | 0.9891 | 0.891 | 0.9799 | 0.8797 | 0.9922 | 0.8984
342770 | 4MARION CO | 320 | 138 | P6:10075 | N11 | 0.93 | 1.06 | 0.9415 | 0.899 | 0.9454 | 0.8763 | 0.9398 | 0.889 | 0.9408 | 0.8809
342770 | 4MARION CO | 320 | 138 | P6:10080 | N11 | 0.93 | 1.06 | 0.9592 | 0.9344 | 0.956 | 0.9216 | 0.9559 | 0.9302 | 0.9558 | 0.9185
342770 | 4MARION CO | 320 | 138 | P6:11357 | N11 | 0.93 | 1.06 | 0.9886 | 0.9142 | 0.9797 | 0.8902 | 0.9763 | 0.8765 | 0.9826 | 0.8943
342770 | 4MARION CO | 320 | 138 | P6:11371 | N11 | 0.93 | 1.06 | 0.9686 | 0.9156 | 0.9694 | 0.8884 | 0.9548 | 0.8892 | 0.9623 | 0.8941
342770 | 4MARION CO | 320 | 138 | P6:11493 | N11 | 0.93 | 1.06 | 0.9751 | 0.9215 | 0.9747 | 0.8889 | 0.9594 | 0.9016 | 0.9682 | 0.8983
342770 | 4MARION CO | 320 | 138 | P6:12977 | N11 | 0.93 | 1.06 | 0.9886 | 0.9037 | 0.9797 | 0.8838 | 0.9763 | 0.873 | 0.9826 | 0.8852
342770 | 4MARION CO | 320 | 138 | P6:12991 | N11 | 0.93 | 1.06 | 0.9725 | 0.9168 | 0.97 | 0.8849 | 0.9548 | 0.8874 | 0.9624 | 0.8939
342770 | 4MARION CO | 320 | 138 | P6:13113 | N11 | 0.93 | 1.06 | 0.9886 | 0.9241 | 0.9719 | 0.8801 | 0.9713 | 0.8979 | 0.9826 | 0.8956
342770 | 4MARION CO | 320 | 138 | P6:13153 | N11 | 0.93 | 1.06 | 0.9357 | 0.9022 | 0.942 | 0.872 | 0.9368 | 0.8846 | 0.936 | 0.8768
342770 | 4MARION CO | 320 | 138 | P6:1975 | N11 | 0.93 | 1.06 | 0.9792 | 0.9278 | 0.9719 | 0.9179 | 0.9583 | 0.9008 | 0.9688 | 0.8965
342770 | 4MARION CO | 320 | 138 | P6:1983 | N11 | 0.93 | 1.06 | 0.9886 | 0.9022 | 0.9797 | 0.881 | 0.9763 | 0.8702 | 0.9826 | 0.8826
342770 | 4MARION CO | 320 | 138 | P6:2008 | N11 | 0.93 | 1.06 | 0.9886 | 0.9164 | 0.9859 | 0.8955 | 0.9763 | 0.8833 | 0.9826 | 0.9003
342770 | 4MARION CO | 320 | 138 | P6:2019 | N11 | 0.93 | 1.06 | 0.9886 | 0.9142 | 0.9797 | 0.8902 | 0.9763 | 0.8765 | 0.9826 | 0.8943
342770 | 4MARION CO | 320 | 138 | P6:2029 | N11 | 0.93 | 1.06 | 0.9886 | 0.9037 | 0.9797 | 0.8838 | 0.9763 | 0.873 | 0.9826 | 0.8852
342770 | 4MARION CO | 320 | 138 | P6:24015 | N11 | 0.93 | 1.06 | 0.9765 | 0.9249 | 0.9726 | 0.8813 | 0.9596 | 0.903 | 0.9699 | 0.8967
342770 | 4MARION CO | 320 | 138 | P6:24040 | N11 | 0.93 | 1.06 | 0.9768 | 0.9286 | 0.9759 | 0.8888 | 0.9605 | 0.9084 | 0.9706 | 0.9022
342770 | 4MARION CO | 320 | 138 | P6:24051 | N11 | 0.93 | 1.06 | 0.9751 | 0.9215 | 0.9747 | 0.8889 | 0.9594 | 0.9016 | 0.9682 | 0.8983
342770 | 4MARION CO | 320 | 138 | P6:24061 | N11 | 0.93 | 1.06 | 0.9886 | 0.9241 | 0.9719 | 0.8801 | 0.9713 | 0.8979 | 0.9826 | 0.8956
342770 | 4MARION CO | 320 | 138 | P6:2623 | N11 | 0.93 | 1.06 | 0.9749 | 0.9382 | 0.976 | 0.9267 | 0.9543 | 0.9132 | 0.9637 | 0.9051
342770 | 4MARION CO | 320 | 138 | P6:2785 | N11 | 0.93 | 1.06 | 0.9598 | 0.9323 | 0.9595 | 0.9257 | 0.9319 | 0.9089 | 0.9449 | 0.8996
342770 | 4MARION CO | 320 | 138 | P6:4229 | N11 | 0.93 | 1.06 | 0.9792 | 0.9278 | 0.9719 | 0.9179 | 0.9583 | 0.9008 | 0.9688 | 0.8965
342770 | 4MARION CO | 320 | 138 | P6:4233 | N11 | 0.93 | 1.06 | 0.9749 | 0.9382 | 0.976 | 0.9267 | 0.9543 | 0.9132 | 0.9637 | 0.9051
342770 | 4MARION CO | 320 | 138 | P6:4234 | N11 | 0.93 | 1.06 | 0.9598 | 0.9323 | 0.9595 | 0.9257 | 0.9319 | 0.9089 | 0.9449 | 0.8996
342770 | 4MARION CO | 320 | 138 | P6:4251 | N11 | 0.93 | 1.06 | 0.9698 | 0.921 | 0.9678 | 0.8866 | 0.9527 | 0.8926 | 0.9618 | 0.8955
342770 | 4MARION CO | 320 | 138 | P6:4257 | N11 | 0.93 | 1.06 | 0.9415 | 0.8998 | 0.9453 | 0.8793 | 0.9399 | 0.8918 | 0.9363 | 0.8844
342770 | 4MARION CO | 320 | 138 | P6:4262 | N11 | 0.93 | 1.06 | 0.9698 | 0.9427 | 0.9695 | 0.9282 | 0.9564 | 0.9196 | 0.9572 | 0.9137
342770 | 4MARION CO | 320 | 138 | P6:4273 | N11 | 0.93 | 1.06 | 0.9559 | 0.9221 | 0.9578 | 0.9023 | 0.9479 | 0.9052 | 0.9533 | 0.8961
342770 | 4MARION CO | 320 | 138 | P6:4276 | N11 | 0.93 | 1.06 | 0.9699 | 0.9236 | 0.9702 | 0.8923 | 0.9531 | 0.8971 | 0.9623 | 0.8989
342770 | 4MARION CO | 320 | 138 | P6:4279 | N11 | 0.93 | 1.06 | 0.9415 | 0.899 | 0.9454 | 0.8763 | 0.9398 | 0.889 | 0.9408 | 0.8809
342770 | 4MARION CO | 320 | 138 | P6:4287 | N11 | 0.93 | 1.06 | 0.9686 | 0.9156 | 0.9694 | 0.8884 | 0.9548 | 0.8892 | 0.9623 | 0.8941
342770 | 4MARION CO | 320 | 138 | P6:4297 | N11 | 0.93 | 1.06 | 0.9725 | 0.9168 | 0.97 | 0.8849 | 0.9548 | 0.8874 | 0.9624 | 0.8939
342770 | 4MARION CO | 320 | 138 | P6:4298 | N11 | 0.93 | 1.06 | 0.9357 | 0.9022 | 0.942 | 0.872 | 0.9368 | 0.8846 | 0.936 | 0.8768
342770 | 4MARION CO | 320 | 138 | P6:4301 | N11 | 0.93 | 1.06 | 0.971 | 0.9433 | 0.9701 | 0.9253 | 0.9597 | 0.9197 | 0.9594 | 0.91
342770 | 4MARION CO | 320 | 138 | P6:5089 | N11 | 0.93 | 1.06 | 0.9592 | 0.9344 | 0.956 | 0.9216 | 0.9559 | 0.9302 | 0.9558 | 0.9185
342770 | 4MARION CO | 320 | 138 | P6:5525 | N11 | 0.93 | 1.06 | 0.9886 | 0.9022 | 0.9797 | 0.881 | 0.9763 | 0.8702 | 0.9826 | 0.8826
342770 | 4MARION CO | 320 | 138 | P6:5661 | N11 | 0.93 | 1.06 | 0.9765 | 0.9249 | 0.9726 | 0.8813 | 0.9596 | 0.903 | 0.9699 | 0.8967
342770 | 4MARION CO | 320 | 138 | P6:9575 | N11 | 0.93 | 1.06 | 0.9886 | 0.9164 | 0.9859 | 0.8955 | 0.9763 | 0.8833 | 0.9826 | 0.9003
342770 | 4MARION CO | 320 | 138 | P6:9711 | N11 | 0.93 | 1.06 | 0.9768 | 0.9286 | 0.9759 | 0.8888 | 0.9605 | 0.9084 | 0.9706 | 0.9022
342772 | 5MARION IP | 320 | 161 | P6:10075 | N11 | 0.93 | 1.06 | 0.9405 | 0.9027 | 0.9451 | 0.8796 | 0.9397 | 0.8926 | 0.9397 | 0.8842
342772 | 5MARION IP | 320 | 161 | P6:11357 | N11 | 0.93 | 1.06 | 0.987 | 0.9121 | 0.9805 | 0.8849 | 0.9774 | 0.8727 | 0.9876 | 0.8925
342772 | 5MARION IP | 320 | 161 | P6:11371 | N11 | 0.93 | 1.06 | 0.9645 | 0.9121 | 0.9669 | 0.8815 | 0.9531 | 0.8855 | 0.9589 | 0.8917
342772 | 5MARION IP | 320 | 161 | P6:11493 | N11 | 0.93 | 1.06 | 0.9717 | 0.9172 | 0.9716 | 0.8788 | 0.9577 | 0.8983 | 0.9648 | 0.895
342772 | 5MARION IP | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.987 | 0.8989 | 0.9856 | 0.8758 | 0.9774 | 0.867 | 0.9809 | 0.8808
342772 | 5MARION IP | 320 | 161 | P6:12991 | N11 | 0.93 | 1.06 | 0.9694 | 0.9124 | 0.9675 | 0.876 | 0.9528 | 0.8821 | 0.9583 | 0.8903
342772 | 5MARION IP | 320 | 161 | P6:13113 | N11 | 0.93 | 1.06 | 0.987 | 0.919 | 0.9679 | 0.8671 | 0.9714 | 0.8926 | 0.9809 | 0.8904
342772 | 5MARION IP | 320 | 161 | P6:1975 | N11 | 0.93 | 1.06 | 0.9768 | 0.9246 | 0.9672 | 0.9145 | 0.9564 | 0.8975 | 0.966 | 0.8928
342772 | 5MARION IP | 320 | 161 | P6:1983 | N11 | 0.93 | 1.06 | 0.987 | 0.8975 | 0.9856 | 0.873 | 0.9774 | 0.864 | 0.9809 | 0.878
342772 | 5MARION IP | 320 | 161 | P6:2008 | N11 | 0.93 | 1.06 | 0.9933 | 0.9139 | 0.9856 | 0.89 | 0.9774 | 0.8794 | 0.9889 | 0.8983
342772 | 5MARION IP | 320 | 161 | P6:2019 | N11 | 0.93 | 1.06 | 0.987 | 0.9121 | 0.9805 | 0.8849 | 0.9774 | 0.8727 | 0.9876 | 0.8925
342772 | 5MARION IP | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.987 | 0.8989 | 0.9856 | 0.8758 | 0.9774 | 0.867 | 0.9809 | 0.8808
342772 | 5MARION IP | 320 | 161 | P6:24015 | N11 | 0.93 | 1.06 | 0.9733 | 0.9199 | 0.9689 | 0.8695 | 0.9577 | 0.8986 | 0.9662 | 0.8926
342772 | 5MARION IP | 320 | 161 | P6:24040 | N11 | 0.93 | 1.06 | 0.9736 | 0.9243 | 0.9728 | 0.8791 | 0.9585 | 0.905 | 0.9669 | 0.8991
342772 | 5MARION IP | 320 | 161 | P6:24051 | N11 | 0.93 | 1.06 | 0.9717 | 0.9172 | 0.9716 | 0.8788 | 0.9577 | 0.8983 | 0.9648 | 0.895
342772 | 5MARION IP | 320 | 161 | P6:24061 | N11 | 0.93 | 1.06 | 0.987 | 0.919 | 0.9679 | 0.8671 | 0.9714 | 0.8926 | 0.9809 | 0.8904
342772 | 5MARION IP | 320 | 161 | P6:2623 | N11 | 0.93 | 1.06 | 0.9716 | 0.9364 | 0.9736 | 0.9242 | 0.952 | 0.911 | 0.96 | 0.9025
342772 | 5MARION IP | 320 | 161 | P6:4229 | N11 | 0.93 | 1.06 | 0.9768 | 0.9246 | 0.9672 | 0.9145 | 0.9564 | 0.8975 | 0.966 | 0.8928
342772 | 5MARION IP | 320 | 161 | P6:4233 | N11 | 0.93 | 1.06 | 0.9716 | 0.9364 | 0.9736 | 0.9242 | 0.952 | 0.911 | 0.96 | 0.9025
342772 | 5MARION IP | 320 | 161 | P6:4251 | N11 | 0.93 | 1.06 | 0.9659 | 0.9175 | 0.9649 | 0.8788 | 0.9501 | 0.8884 | 0.9576 | 0.8923
342772 | 5MARION IP | 320 | 161 | P6:4257 | N11 | 0.93 | 1.06 | 0.9405 | 0.9035 | 0.945 | 0.8827 | 0.9398 | 0.8954 | 0.9354 | 0.8877
342772 | 5MARION IP | 320 | 161 | P6:4273 | N11 | 0.93 | 1.06 | 0.9534 | 0.9228 | 0.956 | 0.9025 | 0.9465 | 0.9062 | 0.9501 | 0.897
342772 | 5MARION IP | 320 | 161 | P6:4276 | N11 | 0.93 | 1.06 | 0.9659 | 0.9204 | 0.9676 | 0.8858 | 0.9504 | 0.8935 | 0.9579 | 0.8962
342772 | 5MARION IP | 320 | 161 | P6:4279 | N11 | 0.93 | 1.06 | 0.9405 | 0.9027 | 0.9451 | 0.8796 | 0.9397 | 0.8926 | 0.9397 | 0.8842
342772 | 5MARION IP | 320 | 161 | P6:4297 | N11 | 0.93 | 1.06 | 0.9694 | 0.9124 | 0.9675 | 0.876 | 0.9528 | 0.8821 | 0.9583 | 0.8903
342772 | 5MARION IP | 320 | 161 | P6:5525 | N11 | 0.93 | 1.06 | 0.987 | 0.8975 | 0.9856 | 0.873 | 0.9774 | 0.864 | 0.9809 | 0.878
342772 | 5MARION IP | 320 | 161 | P6:5661 | N11 | 0.93 | 1.06 | 0.9733 | 0.9199 | 0.9689 | 0.8695 | 0.9577 | 0.8986 | 0.9662 | 0.8926
342772 | 5MARION IP | 320 | 161 | P6:9575 | N11 | 0.93 | 1.06 | 0.9933 | 0.9139 | 0.9856 | 0.89 | 0.9774 | 0.8794 | 0.9889 | 0.8983
342772 | 5MARION IP | 320 | 161 | P6:9711 | N11 | 0.93 | 1.06 | 0.9736 | 0.9243 | 0.9728 | 0.8791 | 0.9585 | 0.905 | 0.9669 | 0.8991
342787 | 5PULASK CO | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9901 | 0.8363 | 0.9791 | 0.8155 | 0.9867 | 0.8095 | 0.9934 | 0.8225
342787 | 5PULASK CO | 320 | 161 | P6:1983 | N11 | 0.93 | 1.06 | 0.9877 | 0.8357 | 0.979 | 0.8124 | 0.9941 | 0.8061 | 0.9934 | 0.8195
342787 | 5PULASK CO | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9901 | 0.8363 | 0.9791 | 0.8155 | 0.9867 | 0.8095 | 0.9934 | 0.8225
342787 | 5PULASK CO | 320 | 161 | P6:5525 | N11 | 0.93 | 1.06 | 0.9877 | 0.8357 | 0.979 | 0.8124 | 0.9941 | 0.8061 | 0.9934 | 0.8195
342798 | 5S MARION IP | 320 | 161 | P6:10075 | N11 | 0.93 | 1.06 | 0.9403 | 0.9025 | 0.9449 | 0.8794 | 0.9395 | 0.8924 | 0.9395 | 0.884
342798 | 5S MARION IP | 320 | 161 | P6:11357 | N11 | 0.93 | 1.06 | 0.9868 | 0.9119 | 0.9803 | 0.8847 | 0.9772 | 0.8725 | 0.9875 | 0.8923
342798 | 5S MARION IP | 320 | 161 | P6:11371 | N11 | 0.93 | 1.06 | 0.9643 | 0.9119 | 0.9667 | 0.8813 | 0.9529 | 0.8853 | 0.9587 | 0.8915
342798 | 5S MARION IP | 320 | 161 | P6:11493 | N11 | 0.93 | 1.06 | 0.9715 | 0.917 | 0.9714 | 0.8786 | 0.9575 | 0.8981 | 0.9646 | 0.8948
342798 | 5S MARION IP | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9868 | 0.8987 | 0.9854 | 0.8756 | 0.9772 | 0.8668 | 0.9808 | 0.8805
342798 | 5S MARION IP | 320 | 161 | P6:12991 | N11 | 0.93 | 1.06 | 0.9692 | 0.9122 | 0.9674 | 0.8758 | 0.9526 | 0.8819 | 0.9581 | 0.8901
342798 | 5S MARION IP | 320 | 161 | P6:13113 | N11 | 0.93 | 1.06 | 0.9868 | 0.9188 | 0.9677 | 0.8669 | 0.9712 | 0.8924 | 0.9808 | 0.8902
342798 | 5S MARION IP | 320 | 161 | P6:1975 | N11 | 0.93 | 1.06 | 0.9766 | 0.9244 | 0.9671 | 0.9143 | 0.9562 | 0.8973 | 0.9658 | 0.8926
342798 | 5S MARION IP | 320 | 161 | P6:1983 | N11 | 0.93 | 1.06 | 0.9868 | 0.8973 | 0.9854 | 0.8728 | 0.9772 | 0.8638 | 0.9808 | 0.8778
342798 | 5S MARION IP | 320 | 161 | P6:2008 | N11 | 0.93 | 1.06 | 0.9931 | 0.9137 | 0.9854 | 0.8898 | 0.9772 | 0.8791 | 0.9887 | 0.8981
342798 | 5S MARION IP | 320 | 161 | P6:2019 | N11 | 0.93 | 1.06 | 0.9868 | 0.9119 | 0.9803 | 0.8847 | 0.9772 | 0.8725 | 0.9875 | 0.8923
342798 | 5S MARION IP | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9868 | 0.8987 | 0.9854 | 0.8756 | 0.9772 | 0.8668 | 0.9808 | 0.8805
342798 | 5S MARION IP | 320 | 161 | P6:24015 | N11 | 0.93 | 1.06 | 0.9731 | 0.9197 | 0.9687 | 0.8693 | 0.9575 | 0.8984 | 0.966 | 0.8924
342798 | 5S MARION IP | 320 | 161 | P6:24040 | N11 | 0.93 | 1.06 | 0.9734 | 0.9241 | 0.9726 | 0.8789 | 0.9584 | 0.9048 | 0.9667 | 0.8989
342798 | 5S MARION IP | 320 | 161 | P6:24051 | N11 | 0.93 | 1.06 | 0.9715 | 0.917 | 0.9714 | 0.8786 | 0.9575 | 0.8981 | 0.9646 | 0.8948
342798 | 5S MARION IP | 320 | 161 | P6:24061 | N11 | 0.93 | 1.06 | 0.9868 | 0.9188 | 0.9677 | 0.8669 | 0.9712 | 0.8924 | 0.9808 | 0.8902
342798 | 5S MARION IP | 320 | 161 | P6:2623 | N11 | 0.93 | 1.06 | 0.9714 | 0.9362 | 0.9734 | 0.924 | 0.9518 | 0.9108 | 0.9598 | 0.9023
342798 | 5S MARION IP | 320 | 161 | P6:4229 | N11 | 0.93 | 1.06 | 0.9766 | 0.9244 | 0.9671 | 0.9143 | 0.9562 | 0.8973 | 0.9658 | 0.8926
342798 | 5S MARION IP | 320 | 161 | P6:4233 | N11 | 0.93 | 1.06 | 0.9714 | 0.9362 | 0.9734 | 0.924 | 0.9518 | 0.9108 | 0.9598 | 0.9023
342798 | 5S MARION IP | 320 | 161 | P6:4251 | N11 | 0.93 | 1.06 | 0.9657 | 0.9173 | 0.9647 | 0.8786 | 0.9499 | 0.8882 | 0.9574 | 0.8921
342798 | 5S MARION IP | 320 | 161 | P6:4257 | N11 | 0.93 | 1.06 | 0.9403 | 0.9033 | 0.9448 | 0.8825 | 0.9396 | 0.8952 | 0.9352 | 0.8875
342798 | 5S MARION IP | 320 | 161 | P6:4273 | N11 | 0.93 | 1.06 | 0.9532 | 0.9226 | 0.9558 | 0.9023 | 0.9463 | 0.906 | 0.9499 | 0.8968
342798 | 5S MARION IP | 320 | 161 | P6:4276 | N11 | 0.93 | 1.06 | 0.9657 | 0.9202 | 0.9674 | 0.8856 | 0.9502 | 0.8933 | 0.9577 | 0.896
342798 | 5S MARION IP | 320 | 161 | P6:4279 | N11 | 0.93 | 1.06 | 0.9403 | 0.9025 | 0.9449 | 0.8794 | 0.9395 | 0.8924 | 0.9395 | 0.884
342798 | 5S MARION IP | 320 | 161 | P6:4297 | N11 | 0.93 | 1.06 | 0.9692 | 0.9122 | 0.9674 | 0.8758 | 0.9526 | 0.8819 | 0.9581 | 0.8901
342798 | 5S MARION IP | 320 | 161 | P6:5525 | N11 | 0.93 | 1.06 | 0.9868 | 0.8973 | 0.9854 | 0.8728 | 0.9772 | 0.8638 | 0.9808 | 0.8778
342798 | 5S MARION IP | 320 | 161 | P6:5661 | N11 | 0.93 | 1.06 | 0.9731 | 0.9197 | 0.9687 | 0.8693 | 0.9575 | 0.8984 | 0.966 | 0.8924
342798 | 5S MARION IP | 320 | 161 | P6:9575 | N11 | 0.93 | 1.06 | 0.9931 | 0.9137 | 0.9854 | 0.8898 | 0.9772 | 0.8791 | 0.9887 | 0.8981
342798 | 5S MARION IP | 320 | 161 | P6:9711 | N11 | 0.93 | 1.06 | 0.9734 | 0.9241 | 0.9726 | 0.8789 | 0.9584 | 0.9048 | 0.9667 | 0.8989
342802 | 5SALOMA | 320 | 161 | P6:10075 | N11 | 0.93 | 1.06 | 0.9411 | 0.9034 | 0.946 | 0.8802 | 0.9403 | 0.8931 | 0.9403 | 0.8846
342802 | 5SALOMA | 320 | 161 | P6:11371 | N11 | 0.93 | 1.06 | 0.9652 | 0.9129 | 0.9673 | 0.8821 | 0.9534 | 0.8858 | 0.9589 | 0.8924
342802 | 5SALOMA | 320 | 161 | P6:11493 | N11 | 0.93 | 1.06 | 0.9758 | 0.9232 | 0.9738 | 0.8837 | 0.9629 | 0.9058 | 0.969 | 0.9025
342802 | 5SALOMA | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9941 | 0.9198 | 0.9929 | 0.8937 | 0.9877 | 0.8873 | 0.9883 | 0.9023
342802 | 5SALOMA | 320 | 161 | P6:12991 | N11 | 0.93 | 1.06 | 0.9698 | 0.9131 | 0.9681 | 0.8769 | 0.9531 | 0.8824 | 0.958 | 0.891
342802 | 5SALOMA | 320 | 161 | P6:13113 | N11 | 0.93 | 1.06 | 0.9885 | 0.9253 | 0.9702 | 0.8725 | 0.9763 | 0.9001 | 0.9883 | 0.898
342802 | 5SALOMA | 320 | 161 | P6:1975 | N11 | 0.93 | 1.06 | 0.9768 | 0.9247 | 0.9682 | 0.9145 | 0.9563 | 0.8973 | 0.9656 | 0.8926
342802 | 5SALOMA | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9941 | 0.9198 | 0.9929 | 0.8937 | 0.9877 | 0.8873 | 0.9883 | 0.9023
342802 | 5SALOMA | 320 | 161 | P6:24051 | N11 | 0.93 | 1.06 | 0.9758 | 0.9232 | 0.9738 | 0.8837 | 0.9629 | 0.9058 | 0.969 | 0.9025
342802 | 5SALOMA | 320 | 161 | P6:24061 | N11 | 0.93 | 1.06 | 0.9885 | 0.9253 | 0.9702 | 0.8725 | 0.9763 | 0.9001 | 0.9883 | 0.898
342802 | 5SALOMA | 320 | 161 | P6:2623 | N11 | 0.93 | 1.06 | 0.9718 | 0.9372 | 0.974 | 0.925 | 0.9523 | 0.9116 | 0.9598 | 0.9032
342802 | 5SALOMA | 320 | 161 | P6:4229 | N11 | 0.93 | 1.06 | 0.9768 | 0.9247 | 0.9682 | 0.9145 | 0.9563 | 0.8973 | 0.9656 | 0.8926
342802 | 5SALOMA | 320 | 161 | P6:4233 | N11 | 0.93 | 1.06 | 0.9718 | 0.9372 | 0.974 | 0.925 | 0.9523 | 0.9116 | 0.9598 | 0.9032
342802 | 5SALOMA | 320 | 161 | P6:4251 | N11 | 0.93 | 1.06 | 0.9665 | 0.9181 | 0.9653 | 0.8794 | 0.9506 | 0.8886 | 0.9578 | 0.893
342802 | 5SALOMA | 320 | 161 | P6:4257 | N11 | 0.93 | 1.06 | 0.9411 | 0.9042 | 0.9459 | 0.8833 | 0.9404 | 0.896 | 0.9358 | 0.8882
342802 | 5SALOMA | 320 | 161 | P6:4262 | N11 | 0.93 | 1.06 | 0.9647 | 0.9425 | 0.9652 | 0.9269 | 0.9551 | 0.9196 | 0.9517 | 0.9133
342802 | 5SALOMA | 320 | 161 | P6:4273 | N11 | 0.93 | 1.06 | 0.9538 | 0.9231 | 0.9563 | 0.9026 | 0.9468 | 0.9062 | 0.95 | 0.897
342802 | 5SALOMA | 320 | 161 | P6:4276 | N11 | 0.93 | 1.06 | 0.9665 | 0.9211 | 0.968 | 0.8863 | 0.951 | 0.8938 | 0.9581 | 0.8969
342802 | 5SALOMA | 320 | 161 | P6:4279 | N11 | 0.93 | 1.06 | 0.9411 | 0.9034 | 0.946 | 0.8802 | 0.9403 | 0.8931 | 0.9403 | 0.8846
342802 | 5SALOMA | 320 | 161 | P6:4297 | N11 | 0.93 | 1.06 | 0.9698 | 0.9131 | 0.9681 | 0.8769 | 0.9531 | 0.8824 | 0.958 | 0.891
342820 | 5TYNER | 320 | 161 | P6:10548 | N11 | 0.93 | 1.06 | 0.9777 | 0.9267 | 0.9759 | 0.9172 | 0.9725 | 0.9185 | 0.9798 | 0.9071
342820 | 5TYNER | 320 | 161 | P6:10556 | N11 | 0.93 | 1.06 | 0.9768 | 0.9258 | 0.975 | 0.9165 | 0.9717 | 0.9176 | 0.979 | 0.9062
342820 | 5TYNER | 320 | 161 | P6:12977 | N11 | 0.93 | 1.06 | 0.9936 | 0.9084 | 0.9879 | 0.8993 | 0.9949 | 0.891 | 0.9971 | 0.9006
342820 | 5TYNER | 320 | 161 | P6:2029 | N11 | 0.93 | 1.06 | 0.9936 | 0.9084 | 0.9879 | 0.8993 | 0.9949 | 0.891 | 0.9971 | 0.9006
342820 | 5TYNER | 320 | 161 | P6:2134 | N11 | 0.93 | 1.06 | 0.9759 | 0.9088 | 0.9769 | 0.8906 | 0.9679 | 0.897 | 0.9725 | 0.8823
342820 | 5TYNER | 320 | 161 | P6:2176 | N11 | 0.93 | 1.06 | 0.9777 | 0.9267 | 0.9759 | 0.9172 | 0.9725 | 0.9185 | 0.9798 | 0.9071
342820 | 5TYNER | 320 | 161 | P6:3430 | N11 | 0.93 | 1.06 | 0.9742 | 0.9071 | 0.9753 | 0.8891 | 0.9663 | 0.8954 | 0.9708 | 0.8808
342820 | 5TYNER | 320 | 161 | P6:3472 | N11 | 0.93 | 1.06 | 0.9768 | 0.9258 | 0.975 | 0.9165 | 0.9717 | 0.9176 | 0.979 | 0.9062
342820 | 5TYNER | 320 | 161 | P6:3744 | N11 | 0.93 | 1.06 | 0.9759 | 0.9088 | 0.9769 | 0.8906 | 0.9679 | 0.897 | 0.9725 | 0.8823
342820 | 5TYNER | 320 | 161 | P6:3752 | N11 | 0.93 | 1.06 | 0.9742 | 0.9071 | 0.9753 | 0.8891 | 0.9663 | 0.8954 | 0.9708 | 0.8808

## Voltage Drop Limits
[7 empty] | Violation Count | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0
Bus # | Bus Name | Area | Base kV | Cont Name | Cont Type | %Vdrop Limit | %Vrise Limit | S1_O0_WIN | S2_O0_WIN | S3_O0_WIN | S4_O0_WIN | S1_O0_SUM | S2_O0_SUM | S3_O0_SUM | S4_O0_SUM
342760 | 5LIBERTY J | 320 | 161 | P6:12977 | N11_Vdrop | 10 | 10 | 14.454 | 15.392 | 16.566 | 14.472
342760 | 5LIBERTY J | 320 | 161 | P6:2029 | N11_Vdrop | 10 | 10 | 14.454 | 15.392 | 16.566 | 14.472
342787 | 5PULASK CO | 320 | 161 | P6:12977 | N11_Vdrop | 10 | 10 | 15.969 | 16.768 | 18.025 | 16.04
342787 | 5PULASK CO | 320 | 161 | P6:2029 | N11_Vdrop | 10 | 10 | 15.969 | 16.768 | 18.025 | 16.04

## Contingency Definitions
contingency "P6:79" / 1 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:89" / 2 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:251" / 3 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:403" / 4 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:409" / 5 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:413" / 6 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:529" / 7 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:575" / 8 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:727" / 9 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:737" / 10 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1039" / 11 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1213" / 12 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1223" / 13 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1385" / 14 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1455" / 15 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1547" / 16 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1663" / 17 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:1699" / 18 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1707" / 19 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:1861" / 20 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1871" / 21 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1994" / 22 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:2011" / 23 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2033" / 24 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2090" / 25 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:2092" / 26 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:2103" / 27 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2311" / 28 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:2357" / 29 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2473" / 30 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:2509" / 31 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2519" / 32 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2614" / 33 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:2681" / 34 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2751" / 35 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2775" / 36 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:2843" / 37 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3157" / 38 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3237" / 39 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3319" / 40 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3329" / 41 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3643" / 42 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3653" / 43 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3805" / 44 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3815" / 45 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3967" / 46 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3977" / 47 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4291" / 48 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4301" / 49 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4453" / 50 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4463" / 51 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4579" / 52 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:4615" / 53 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4625" / 54 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4777" / 55 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4787" / 56 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4939" / 57 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4949" / 58 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5111" / 59 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5227" / 60 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:5597" / 61 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5749" / 62 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5759" / 63 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5911" / 64 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5919" / 65 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:5921" / 66 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6157" / 67 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:6161" / 68 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:6171" / 69 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:6175" / 70 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:6189" / 71 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:6204" / 72 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:6240" / 73 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:6271" / 74 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:6272" / 75 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:6277" / 76 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:6300" / 77 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:6301" / 78 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:6304" / 79 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:6315" / 80 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6318" / 81 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:6397" / 82 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6407" / 83 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6559" / 84 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6569" / 85 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6721" / 86 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6731" / 87 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6893" / 88 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7033" / 89 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:7055" / 90 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7207" / 91 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7307" / 92 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7379" / 93 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7400" / 94 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:7432" / 95 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:7541" / 96 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7703" / 97 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7855" / 98 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7865" / 99 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8017" / 100 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8027" / 101 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8179" / 102 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8189" / 103 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8341" / 104 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8351" / 105 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8513" / 106 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8665" / 107 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8675" / 108 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8837" / 109 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8989" / 110 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8999" / 111 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9151" / 112 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9161" / 113 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9313" / 114 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9323" / 115 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9485" / 116 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9637" / 117 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9647" / 118 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9799" / 119 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9809" / 120 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9971" / 121 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10045" / 122 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:10053" / 123 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:10055" / 124 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:10061" / 125 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10092" / 126 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:10120" / 127 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:10123" / 128 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10131" / 129 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:10133" / 130 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10159" / 131 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:10187" / 132 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:10285" / 133 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10457" / 134 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10619" / 135 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10771" / 136 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10779" / 137 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:10781" / 138 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10943" / 139 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11095" / 140 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11105" / 141 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11267" / 142 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11419" / 143 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11429" / 144 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11569" / 145 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11591" / 146 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11743" / 147 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11753" / 148 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11905" / 149 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11915" / 150 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11992" / 151 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11994" / 152 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:11996" / 153 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:12000" / 154 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:12003" / 155 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:12012" / 156 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12015" / 157 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:12016" / 158 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12017" / 159 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:12020" / 160 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:12021" / 161 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:12055" / 162 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12056" / 163 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:12059" / 164 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:12061" / 165 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:12063" / 166 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12067" / 167 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12069" / 168 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12070" / 169 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:12076" / 170 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:12077" / 171 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12078" / 172 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:12079" / 173 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:12080" / 174 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:12082" / 175 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:12083" / 176 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:12084" / 177 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:12085" / 178 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:12086" / 179 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:12087" / 180 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:12089" / 181 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:12091" / 182 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:12093" / 183 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:12094" / 184 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:12096" / 185 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:12099" / 186 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:12100" / 187 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:12101" / 188 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:12102" / 189 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:12103" / 190 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:12104" / 191 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:12105" / 192 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:12106" / 193 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:12108" / 194 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:12110" / 195 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:12111" / 196 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:12112" / 197 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:12113" / 198 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:12114" / 199 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:12115" / 200 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:12117" / 201 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:12118" / 202 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:12119" / 203 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:12120" / 204 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:12121" / 205 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:12122" / 206 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:12123" / 207 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:12124" / 208 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:12126" / 209 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:12128" / 210 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:12129" / 211 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:12131" / 212 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:12133" / 213 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:12135" / 214 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:12137" / 215 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:12138" / 216 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:12140" / 217 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:12141" / 218 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12142" / 219 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:12143" / 220 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:12144" / 221 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:12145" / 222 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:12147" / 223 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12148" / 224 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:12149" / 225 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:12239" / 226 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12401" / 227 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12563" / 228 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12841" / 229 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:12887" / 230 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12964" / 231 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13049" / 232 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13211" / 233 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13299" / 234 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13325" / 235 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:13351" / 236 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13355" / 237 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:13432" / 238 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:13437" / 239 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13443" / 240 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13525" / 241 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13535" / 242 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13609" / 243 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:13611" / 244 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:13612" / 245 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13613" / 246 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:13614" / 247 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:13616" / 248 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:13617" / 249 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:13618" / 250 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:13620" / 251 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:13621" / 252 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:13625" / 253 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13627" / 254 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:13629" / 255 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:13630" / 256 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:13635" / 257 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:13636" / 258 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:13637" / 259 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:13640" / 260 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:13641" / 261 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:13675" / 262 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13677" / 263 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:13678" / 264 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13679" / 265 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:13680" / 266 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13681" / 267 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:13682" / 268 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13683" / 269 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13684" / 270 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13692" / 271 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:13693" / 272 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13694" / 273 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13696" / 274 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13697" / 275 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13699" / 276 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13701" / 277 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:13702" / 278 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:13703" / 279 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:13704" / 280 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13705" / 281 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:13706" / 282 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:13707" / 283 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13709" / 284 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13711" / 285 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13714" / 286 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:13715" / 287 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:13716" / 288 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:13717" / 289 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13718" / 290 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13719" / 291 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:13720" / 292 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13721" / 293 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:13722" / 294 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:13723" / 295 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:13725" / 296 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:13726" / 297 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:13728" / 298 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:13729" / 299 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:13730" / 300 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:13731" / 301 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:13732" / 302 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:13733" / 303 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:13734" / 304 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13735" / 305 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:13736" / 306 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:13737" / 307 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13738" / 308 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13739" / 309 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:13740" / 310 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13742" / 311 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:13743" / 312 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13744" / 313 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:13745" / 314 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13746" / 315 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:13748" / 316 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:13750" / 317 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:13751" / 318 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:13752" / 319 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:13755" / 320 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:13756" / 321 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:13758" / 322 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13760" / 323 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:13761" / 324 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13762" / 325 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13763" / 326 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:13764" / 327 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:13766" / 328 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:13767" / 329 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13768" / 330 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13769" / 331 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:13880" / 332 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:14204" / 333 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16513" / 334 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3
end
contingency "P6:16676" / 335 N11
open branch from bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1
end
contingency "P6:16958" / 336 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:17006" / 337 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:17010" / 338 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:17887" / 339 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18437" / 340 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:22340" / 341 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22353" / 342 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:22423" / 343 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:22502" / 344 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22859" / 345 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22991" / 346 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:23002" / 347 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:23183" / 348 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23253" / 349 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:23569" / 350 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:23579" / 351 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:24055" / 352 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24063" / 353 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24065" / 354 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24217" / 355 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:24379" / 356 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24389" / 357 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24541" / 358 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24551" / 359 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24621" / 360 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24961" / 361 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:24965" / 362 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24969" / 363 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:24972" / 364 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:25035" / 365 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:25104" / 366 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:50" / 367 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:899" / 368 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1061" / 369 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1709" / 370 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1954" / 371 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:1966" / 372 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:2024" / 373 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:2034" / 374 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:2059" / 375 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:2101" / 376 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:2102" / 377 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:2167" / 378 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:2195" / 379 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2264" / 380 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:2750" / 381 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:2771" / 382 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3005" / 383 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3167" / 384 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3236" / 385 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:3463" / 386 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:3491" / 387 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3560" / 388 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:4139" / 389 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4694" / 390 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:5273" / 391 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5394" / 392 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:5421" / 393 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5435" / 394 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5504" / 395 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:5990" / 396 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:6083" / 397 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6245" / 398 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7027" / 399 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:7124" / 400 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:7217" / 401 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7351" / 402 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:7357" / 403 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:7448" / 404 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:9230" / 405 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:9462" / 406 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:9472" / 407 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:9474" / 408 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:9965" / 409 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10094" / 410 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:10189" / 411 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:10202" / 412 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:10295" / 413 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11378" / 414 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:11423" / 415 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11498" / 416 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:11565" / 417 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:11585" / 418 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11909" / 419 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12167" / 420 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12702" / 421 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:12711" / 422 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12712" / 423 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:12714" / 424 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:12725" / 425 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13373" / 426 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13604" / 427 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:13615" / 428 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:13619" / 429 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:13623" / 430 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13632" / 431 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13638" / 432 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:13676" / 433 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:13691" / 434 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13695" / 435 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13698" / 436 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13700" / 437 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:13708" / 438 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:13710" / 439 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13712" / 440 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13713" / 441 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:13724" / 442 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13741" / 443 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13747" / 444 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13749" / 445 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:13753" / 446 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:13754" / 447 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:13757" / 448 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:13759" / 449 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:13765" / 450 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:13787" / 451 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13929" / 452 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:16632" / 453 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:16674" / 454 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:16838" / 455 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:17837" / 456 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22747" / 457 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23597" / 458 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:23642" / 459 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:23964" / 460 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:24134" / 461 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24227" / 462 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:24641" / 463 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24803" / 464 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24807" / 465 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:24810" / 466 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:24819" / 467 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:24853" / 468 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:24861" / 469 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:24874" / 470 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:24939" / 471 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:39" / 472 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:75" / 473 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:226" / 474 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:229" / 475 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:237" / 476 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:241" / 477 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:247" / 478 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:363" / 479 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:388" / 480 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:399" / 481 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:525" / 482 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:553" / 483 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:561" / 484 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:571" / 485 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:712" / 486 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:723" / 487 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:874" / 488 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:885" / 489 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:956" / 490 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:989" / 491 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1036" / 492 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1047" / 493 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1057" / 494 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1173" / 495 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1198" / 496 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1209" / 497 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1335" / 498 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1371" / 499 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1381" / 500 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1475" / 501 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1497" / 502 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1522" / 503 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1537" / 504 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1543" / 505 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1659" / 506 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1695" / 507 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1705" / 508 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1766" / 509 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:1857" / 510 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1953" / 511 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:1955" / 512 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:1958" / 513 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:1965" / 514 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:1968" / 515 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1982" / 516 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:1983" / 517 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1992" / 518 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:2005" / 519 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:2008" / 520 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2019" / 521 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2029" / 522 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2054" / 523 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2094" / 524 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:2181" / 525 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2252" / 526 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:2343" / 527 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2609" / 528 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2667" / 529 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2671" / 530 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2829" / 531 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2833" / 532 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2980" / 533 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2991" / 534 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2995" / 535 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3095" / 536 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3142" / 537 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3153" / 538 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3240" / 539 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3279" / 540 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3315" / 541 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3325" / 542 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3477" / 543 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3548" / 544 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:3603" / 545 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3628" / 546 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3649" / 547 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3765" / 548 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3790" / 549 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3811" / 550 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3927" / 551 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3963" / 552 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4089" / 553 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:4114" / 554 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4125" / 555 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4135" / 556 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4196" / 557 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:4273" / 558 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4279" / 559 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4287" / 560 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4299" / 561 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:4358" / 562 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:4449" / 563 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4575" / 564 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:4603" / 565 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4611" / 566 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4773" / 567 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4935" / 568 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5061" / 569 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5086" / 570 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5101" / 571 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5107" / 572 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5223" / 573 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5259" / 574 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5330" / 575 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:5363" / 576 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5413" / 577 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5512" / 578 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5513" / 579 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:5520" / 580 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:5521" / 581 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:5523" / 582 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:5525" / 583 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5535" / 584 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:5536" / 585 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:5537" / 586 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:5538" / 587 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:5541" / 588 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:5547" / 589 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5549" / 590 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:5553" / 591 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5556" / 592 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:5559" / 593 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:5560" / 594 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:5563" / 595 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:5564" / 596 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:5565" / 597 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:5566" / 598 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:5567" / 599 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:5568" / 600 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:5569" / 601 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5571" / 602 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:5572" / 603 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5573" / 604 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:5574" / 605 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:5575" / 606 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5577" / 607 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:5578" / 608 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5580" / 609 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:5583" / 610 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5584" / 611 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:5586" / 612 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:5587" / 613 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5588" / 614 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:5590" / 615 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:5591" / 616 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5592" / 617 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:5594" / 618 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:5596" / 619 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:5598" / 620 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:5599" / 621 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:5600" / 622 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:5604" / 623 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:5615" / 624 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:5616" / 625 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:5617" / 626 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5618" / 627 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5623" / 628 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:5624" / 629 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:5625" / 630 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:5626" / 631 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:5629" / 632 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:5630" / 633 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:5638" / 634 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5640" / 635 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5641" / 636 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:5645" / 637 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:5647" / 638 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:5648" / 639 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:5653" / 640 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:5657" / 641 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:5658" / 642 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:5660" / 643 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:5663" / 644 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:5666" / 645 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:5670" / 646 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:5882" / 647 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:5907" / 648 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5917" / 649 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6061" / 650 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6069" / 651 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6073" / 652 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6140" / 653 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:6206" / 654 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:6220" / 655 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6231" / 656 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6302" / 657 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:6393" / 658 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6528" / 659 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:6544" / 660 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6555" / 661 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6565" / 662 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6717" / 663 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6879" / 664 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6983" / 665 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7015" / 666 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:7041" / 667 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7049" / 668 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7052" / 669 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:7192" / 670 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7203" / 671 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7354" / 672 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7365" / 673 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7369" / 674 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7373" / 675 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7377" / 676 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:7391" / 677 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:7414" / 678 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:7527" / 679 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7531" / 680 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7537" / 681 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7678" / 682 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7689" / 683 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7851" / 684 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8005" / 685 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8164" / 686 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8175" / 687 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8326" / 688 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8337" / 689 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8347" / 690 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8499" / 691 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8503" / 692 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8661" / 693 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8671" / 694 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8812" / 695 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8827" / 696 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8833" / 697 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8985" / 698 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8995" / 699 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9089" / 700 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9136" / 701 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9147" / 702 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9157" / 703 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9309" / 704 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9559" / 705 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:9561" / 706 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:9562" / 707 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9564" / 708 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:9565" / 709 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:9568" / 710 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:9569" / 711 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:9570" / 712 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:9575" / 713 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9582" / 714 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9585" / 715 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:9586" / 716 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9588" / 717 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:9624" / 718 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:9625" / 719 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:9628" / 720 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9631" / 721 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:9633" / 722 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:9634" / 723 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:9638" / 724 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:9640" / 725 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:9641" / 726 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9642" / 727 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:9644" / 728 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:9648" / 729 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:9650" / 730 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:9659" / 731 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:9660" / 732 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:9665" / 733 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:9666" / 734 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:9668" / 735 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9673" / 736 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:9682" / 737 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:9691" / 738 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:9696" / 739 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:9697" / 740 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:9698" / 741 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:9699" / 742 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:9708" / 743 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:9710" / 744 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:9716" / 745 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:9957" / 746 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9967" / 747 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10041" / 748 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10047" / 749 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:10049" / 750 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:10054" / 751 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:10075" / 752 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:10077" / 753 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:10082" / 754 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:10083" / 755 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10086" / 756 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:10098" / 757 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:10108" / 758 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10119" / 759 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10127" / 760 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10129" / 761 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10132" / 762 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:10136" / 763 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:10139" / 764 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:10144" / 765 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:10145" / 766 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:10168" / 767 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:10170" / 768 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:10172" / 769 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:10181" / 770 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:10183" / 771 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:10281" / 772 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10407" / 773 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10443" / 774 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10569" / 775 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10594" / 776 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10605" / 777 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10615" / 778 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10689" / 779 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10767" / 780 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10893" / 781 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10929" / 782 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10933" / 783 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11080" / 784 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11091" / 785 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11101" / 786 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11253" / 787 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11341" / 788 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:11342" / 789 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:11343" / 790 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:11344" / 791 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11345" / 792 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:11346" / 793 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:11347" / 794 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:11348" / 795 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:11349" / 796 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:11350" / 797 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:11351" / 798 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:11352" / 799 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:11353" / 800 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:11355" / 801 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:11356" / 802 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:11357" / 803 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11358" / 804 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:11359" / 805 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:11361" / 806 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:11362" / 807 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:11363" / 808 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:11364" / 809 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11365" / 810 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:11366" / 811 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:11369" / 812 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:11370" / 813 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:11371" / 814 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:11372" / 815 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:11373" / 816 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:11374" / 817 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:11375" / 818 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:11377" / 819 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:11379" / 820 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:11381" / 821 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:11382" / 822 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:11383" / 823 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:11384" / 824 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:11385" / 825 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11386" / 826 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:11387" / 827 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:11388" / 828 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11389" / 829 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11390" / 830 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:11391" / 831 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:11392" / 832 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:11393" / 833 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:11395" / 834 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:11396" / 835 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:11397" / 836 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:11398" / 837 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:11400" / 838 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:11401" / 839 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:11402" / 840 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11404" / 841 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11406" / 842 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:11407" / 843 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11408" / 844 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:11409" / 845 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:11410" / 846 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11411" / 847 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:11412" / 848 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:11413" / 849 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:11414" / 850 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11415" / 851 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11416" / 852 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11418" / 853 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:11420" / 854 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:11421" / 855 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:11422" / 856 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:11424" / 857 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:11425" / 858 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11426" / 859 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:11430" / 860 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:11431" / 861 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:11433" / 862 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:11435" / 863 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:11436" / 864 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:11437" / 865 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:11439" / 866 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:11441" / 867 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:11442" / 868 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:11443" / 869 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:11444" / 870 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:11449" / 871 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11451" / 872 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:11452" / 873 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:11453" / 874 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:11454" / 875 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:11455" / 876 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:11456" / 877 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:11457" / 878 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:11458" / 879 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:11459" / 880 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:11461" / 881 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:11464" / 882 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:11465" / 883 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:11466" / 884 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:11468" / 885 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:11469" / 886 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:11470" / 887 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:11471" / 888 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:11474" / 889 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:11475" / 890 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:11476" / 891 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:11477" / 892 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:11482" / 893 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:11483" / 894 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:11484" / 895 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:11485" / 896 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:11487" / 897 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:11488" / 898 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:11489" / 899 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:11493" / 900 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11495" / 901 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:11496" / 902 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:11497" / 903 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:11499" / 904 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11500" / 905 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:11541" / 906 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:11566" / 907 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11577" / 908 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11587" / 909 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11661" / 910 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11901" / 911 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11911" / 912 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11991" / 913 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:11997" / 914 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:11998" / 915 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:12009" / 916 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:12010" / 917 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:12060" / 918 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:12072" / 919 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12073" / 920 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12081" / 921 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:12088" / 922 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:12090" / 923 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:12092" / 924 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:12095" / 925 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:12109" / 926 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:12116" / 927 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:12125" / 928 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:12130" / 929 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:12139" / 930 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:12225" / 931 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12387" / 932 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12549" / 933 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12675" / 934 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:12684" / 935 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:12686" / 936 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:12700" / 937 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12703" / 938 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12721" / 939 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12726" / 940 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:12764" / 941 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:12782" / 942 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:12795" / 943 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12837" / 944 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:12862" / 945 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12873" / 946 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12877" / 947 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12883" / 948 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12963" / 949 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:12965" / 950 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:12971" / 951 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:12973" / 952 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:12974" / 953 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:12975" / 954 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:12977" / 955 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12985" / 956 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:12987" / 957 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:12988" / 958 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12990" / 959 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:12996" / 960 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:13001" / 961 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:13005" / 962 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13011" / 963 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:13016" / 964 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:13018" / 965 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:13019" / 966 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:13020" / 967 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:13021" / 968 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:13026" / 969 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:13027" / 970 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13030" / 971 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13033" / 972 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:13035" / 973 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13036" / 974 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13038" / 975 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:13039" / 976 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13043" / 977 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13044" / 978 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:13046" / 979 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13050" / 980 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13051" / 981 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13052" / 982 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:13062" / 983 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13067" / 984 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:13068" / 985 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:13070" / 986 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13075" / 987 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:13081" / 988 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:13082" / 989 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:13093" / 990 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13100" / 991 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:13101" / 992 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:13110" / 993 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13112" / 994 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:13118" / 995 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:13161" / 996 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13170" / 997 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:13186" / 998 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13197" / 999 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13207" / 1000 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13315" / 1001 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:13334" / 1002 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:13389" / 1003 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:13423" / 1004 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13430" / 1005 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:13485" / 1006 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13513" / 1007 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13770" / 1008 N11
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13845" / 1009 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13853" / 1010 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13855" / 1011 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14007" / 1012 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:14017" / 1013 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14161" / 1014 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14179" / 1015 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14331" / 1016 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:14647" / 1017 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14655" / 1018 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:14817" / 1019 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:14979" / 1020 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15063" / 1021 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:15303" / 1022 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15457" / 1023 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15536" / 1024 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:15619" / 1025 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15627" / 1026 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15789" / 1027 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15799" / 1028 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:15860" / 1029 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:15951" / 1030 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:16113" / 1031 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:16287" / 1032 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:16346" / 1033 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:16609" / 1034 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16771" / 1035 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16923" / 1036 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17027" / 1037 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17095" / 1038 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17134" / 1039 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:17148" / 1040 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:17247" / 1041 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17409" / 1042 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17571" / 1043 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17733" / 1044 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17895" / 1045 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17905" / 1046 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18057" / 1047 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:18128" / 1048 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:18219" / 1049 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:18381" / 1050 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:18543" / 1051 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:18766" / 1052 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:18867" / 1053 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:18877" / 1054 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19039" / 1055 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19345" / 1056 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:19353" / 1057 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:19424" / 1058 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:19515" / 1059 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:19669" / 1060 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:19677" / 1061 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:19748" / 1062 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:19993" / 1063 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:20001" / 1064 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:20009" / 1065 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:20072" / 1066 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:20163" / 1067 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:20325" / 1068 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:20487" / 1069 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:20733" / 1070 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:20821" / 1071 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20973" / 1072 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:21135" / 1073 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:21297" / 1074 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:21451" / 1075 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:21459" / 1076 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:21692" / 1077 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:21775" / 1078 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:21795" / 1079 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:21854" / 1080 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:21955" / 1081 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22117" / 1082 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22178" / 1083 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22269" / 1084 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22337" / 1085 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:22342" / 1086 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:22431" / 1087 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22593" / 1088 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22664" / 1089 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22755" / 1090 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22837" / 1091 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:22849" / 1092 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:22857" / 1093 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:22872" / 1094 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:22925" / 1095 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:22929" / 1096 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:22990" / 1097 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:22996" / 1098 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:23079" / 1099 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:23241" / 1100 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:23403" / 1101 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:23507" / 1102 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23529" / 1103 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:23554" / 1104 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:23575" / 1105 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23899" / 1106 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:24051" / 1107 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24135" / 1108 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24284" / 1109 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:24339" / 1110 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24375" / 1111 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24537" / 1112 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24699" / 1113 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:24871" / 1114 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:25018" / 1115 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:25023" / 1116 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:25024" / 1117 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:25031" / 1118 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:25101" / 1119 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:25108" / 1120 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:25185" / 1121 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:25458" / 1122 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:158" / 1123 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:341" / 1124 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1130" / 1125 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:1948" / 1126 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3634" / 1127 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3796" / 1128 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3801" / 1129 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4208" / 1130 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:4537" / 1131 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:10557" / 1132 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:10558" / 1133 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10606" / 1134 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11368" / 1135 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11450" / 1136 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11478" / 1137 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:11572" / 1138 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15872" / 1139 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:17085" / 1140 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:17978" / 1141 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:21621" / 1142 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:24782" / 1143 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:24787" / 1144 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:24797" / 1145 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:24816" / 1146 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:24945" / 1147 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:109" / 1148 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:271" / 1149 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:433" / 1150 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:519" / 1151 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:565" / 1152 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:595" / 1153 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:687" / 1154 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:733" / 1155 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:757" / 1156 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:889" / 1157 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:897" / 1158 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:919" / 1159 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:1051" / 1160 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1081" / 1161 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:1118" / 1162 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:1219" / 1163 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1243" / 1164 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:1405" / 1165 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:1533" / 1166 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1567" / 1167 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:1615" / 1168 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:1684" / 1169 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1729" / 1170 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:1821" / 1171 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1869" / 1172 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:1874" / 1173 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:1891" / 1174 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2031" / 1175 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:2145" / 1176 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2185" / 1177 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2215" / 1178 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2307" / 1179 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2347" / 1180 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2377" / 1181 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2494" / 1182 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2505" / 1183 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2539" / 1184 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2653" / 1185 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:2701" / 1186 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2818" / 1187 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2839" / 1188 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2841" / 1189 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:2863" / 1190 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2959" / 1191 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:3001" / 1192 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3003" / 1193 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:3025" / 1194 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3117" / 1195 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3165" / 1196 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:3187" / 1197 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3231" / 1198 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3349" / 1199 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3441" / 1200 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3481" / 1201 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3487" / 1202 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3511" / 1203 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3639" / 1204 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3673" / 1205 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3813" / 1206 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:3835" / 1207 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3997" / 1208 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4091" / 1209 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:4117" / 1210 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4159" / 1211 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4251" / 1212 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:4262" / 1213 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:4295" / 1214 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4297" / 1215 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4475" / 1216 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:4483" / 1217 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4541" / 1218 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:4570" / 1219 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:4597" / 1220 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4600" / 1221 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4619" / 1222 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4621" / 1223 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4645" / 1224 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4660" / 1225 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:4684" / 1226 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:4731" / 1227 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:4807" / 1228 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4969" / 1229 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5097" / 1230 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5131" / 1231 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5263" / 1232 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5293" / 1233 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5385" / 1234 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5410" / 1235 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5429" / 1236 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5431" / 1237 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5433" / 1238 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:5455" / 1239 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5492" / 1240 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:5514" / 1241 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:5517" / 1242 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:5527" / 1243 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:5532" / 1244 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5550" / 1245 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:5554" / 1246 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:5558" / 1247 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:5570" / 1248 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5581" / 1249 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:5585" / 1250 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:5595" / 1251 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:5602" / 1252 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:5603" / 1253 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:5608" / 1254 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:5631" / 1255 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:5632" / 1256 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:5634" / 1257 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:5642" / 1258 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:5643" / 1259 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:5646" / 1260 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:5649" / 1261 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:5650" / 1262 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:5652" / 1263 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:5654" / 1264 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:5656" / 1265 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:5659" / 1266 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:5665" / 1267 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:5667" / 1268 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5668" / 1269 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:5745" / 1270 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5757" / 1271 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:5779" / 1272 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5862" / 1273 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:5875" / 1274 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:5889" / 1275 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:5896" / 1276 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5941" / 1277 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5956" / 1278 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:5970" / 1279 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:5989" / 1280 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:6058" / 1281 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6079" / 1282 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6235" / 1283 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6236" / 1284 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:6238" / 1285 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:6250" / 1286 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:6260" / 1287 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:6265" / 1288 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:6305" / 1289 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:6309" / 1290 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6382" / 1291 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6405" / 1292 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:6427" / 1293 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:6563" / 1294 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:6572" / 1295 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:6589" / 1296 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:6727" / 1297 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6751" / 1298 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:6891" / 1299 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:6913" / 1300 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:7045" / 1301 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7051" / 1302 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7053" / 1303 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:7058" / 1304 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:7075" / 1305 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:7112" / 1306 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:7123" / 1307 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:7237" / 1308 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:7375" / 1309 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7428" / 1310 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:7561" / 1311 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:7693" / 1312 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7701" / 1313 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:7723" / 1314 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:7885" / 1315 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8025" / 1316 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:8047" / 1317 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8185" / 1318 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8209" / 1319 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8371" / 1320 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8485" / 1321 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8488" / 1322 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8491" / 1323 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8509" / 1324 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8511" / 1325 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:8533" / 1326 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8695" / 1327 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8823" / 1328 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8857" / 1329 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9019" / 1330 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9093" / 1331 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:9105" / 1332 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:9155" / 1333 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9159" / 1334 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:9160" / 1335 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:9164" / 1336 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:9181" / 1337 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9196" / 1338 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:9217" / 1339 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:9221" / 1340 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:9301" / 1341 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:9319" / 1342 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9343" / 1343 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9460" / 1344 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9471" / 1345 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9505" / 1346 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9567" / 1347 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:9573" / 1348 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:9580" / 1349 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:9591" / 1350 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:9626" / 1351 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:9630" / 1352 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:9632" / 1353 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9645" / 1354 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:9646" / 1355 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:9652" / 1356 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:9658" / 1357 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:9661" / 1358 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:9667" / 1359 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9670" / 1360 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:9685" / 1361 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:9694" / 1362 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:9695" / 1363 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:9700" / 1364 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:9702" / 1365 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:9704" / 1366 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:9706" / 1367 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:9707" / 1368 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:9712" / 1369 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:9715" / 1370 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:9717" / 1371 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9718" / 1372 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:9720" / 1373 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:9805" / 1374 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9829" / 1375 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9949" / 1376 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:9969" / 1377 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:9991" / 1378 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10074" / 1379 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:10101" / 1380 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:10106" / 1381 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10110" / 1382 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:10116" / 1383 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:10126" / 1384 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:10153" / 1385 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10201" / 1386 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:10270" / 1387 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10291" / 1388 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10447" / 1389 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10477" / 1390 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10639" / 1391 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10801" / 1392 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10918" / 1393 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10921" / 1394 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10939" / 1395 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10941" / 1396 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:10963" / 1397 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11055" / 1398 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:11125" / 1399 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11242" / 1400 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11265" / 1401 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:11287" / 1402 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11354" / 1403 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:11360" / 1404 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:11367" / 1405 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:11376" / 1406 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:11380" / 1407 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:11399" / 1408 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:11403" / 1409 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:11417" / 1410 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:11427" / 1411 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:11428" / 1412 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:11432" / 1413 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:11434" / 1414 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:11438" / 1415 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:11440" / 1416 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:11445" / 1417 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:11446" / 1418 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:11448" / 1419 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:11460" / 1420 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:11462" / 1421 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:11463" / 1422 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:11467" / 1423 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:11472" / 1424 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:11473" / 1425 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:11479" / 1426 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:11480" / 1427 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:11481" / 1428 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:11486" / 1429 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:11490" / 1430 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:11491" / 1431 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:11492" / 1432 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:11494" / 1433 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:11501" / 1434 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:11502" / 1435 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:11589" / 1436 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:11611" / 1437 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11739" / 1438 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11749" / 1439 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11773" / 1440 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11935" / 1441 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11993" / 1442 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:11995" / 1443 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:11999" / 1444 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:12007" / 1445 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:12057" / 1446 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:12068" / 1447 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:12075" / 1448 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:12097" / 1449 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12127" / 1450 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:12132" / 1451 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:12134" / 1452 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:12136" / 1453 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:12235" / 1454 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12237" / 1455 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:12259" / 1456 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12421" / 1457 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12541" / 1458 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12559" / 1459 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12561" / 1460 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:12583" / 1461 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12667" / 1462 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:12669" / 1463 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:12674" / 1464 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:12681" / 1465 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12697" / 1466 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:12728" / 1467 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:12745" / 1468 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12760" / 1469 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:12784" / 1470 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:12789" / 1471 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12793" / 1472 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:12907" / 1473 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12961" / 1474 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:12966" / 1475 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:12969" / 1476 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:12972" / 1477 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:12982" / 1478 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:12983" / 1479 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:12986" / 1480 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:12991" / 1481 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:12993" / 1482 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:12998" / 1483 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:13002" / 1484 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:13006" / 1485 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:13008" / 1486 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:13010" / 1487 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:13015" / 1488 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:13017" / 1489 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13022" / 1490 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13025" / 1491 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:13028" / 1492 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:13032" / 1493 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13037" / 1494 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:13040" / 1495 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13042" / 1496 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13047" / 1497 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13048" / 1498 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13054" / 1499 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:13055" / 1500 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:13060" / 1501 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:13061" / 1502 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13076" / 1503 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13083" / 1504 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:13084" / 1505 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:13086" / 1506 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13088" / 1507 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:13097" / 1508 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13098" / 1509 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:13104" / 1510 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:13105" / 1511 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:13106" / 1512 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:13117" / 1513 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:13120" / 1514 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13122" / 1515 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13214" / 1516 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:13231" / 1517 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13285" / 1518 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:13291" / 1519 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:13300" / 1520 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:13301" / 1521 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13306" / 1522 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:13307" / 1523 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:13308" / 1524 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13312" / 1525 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:13322" / 1526 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:13323" / 1527 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13324" / 1528 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:13328" / 1529 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:13331" / 1530 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:13332" / 1531 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:13336" / 1532 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:13338" / 1533 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:13341" / 1534 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13345" / 1535 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:13348" / 1536 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13350" / 1537 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:13356" / 1538 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13358" / 1539 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13359" / 1540 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13360" / 1541 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13363" / 1542 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13364" / 1543 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13366" / 1544 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13369" / 1545 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13374" / 1546 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13377" / 1547 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:13379" / 1548 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:13383" / 1549 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13384" / 1550 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:13386" / 1551 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13387" / 1552 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13392" / 1553 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:13393" / 1554 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13394" / 1555 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13395" / 1556 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:13396" / 1557 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13399" / 1558 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:13400" / 1559 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13404" / 1560 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:13409" / 1561 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:13413" / 1562 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13420" / 1563 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:13421" / 1564 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13426" / 1565 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:13427" / 1566 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:13428" / 1567 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:13429" / 1568 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:13431" / 1569 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:13434" / 1570 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13440" / 1571 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:13442" / 1572 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:13444" / 1573 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13445" / 1574 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:13507" / 1575 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:13510" / 1576 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13521" / 1577 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13531" / 1578 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13555" / 1579 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13603" / 1580 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:13857" / 1581 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13916" / 1582 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:14041" / 1583 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:14169" / 1584 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:14177" / 1585 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:14180" / 1586 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:14240" / 1587 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:14343" / 1588 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:14365" / 1589 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:14493" / 1590 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:14503" / 1591 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14527" / 1592 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:14665" / 1593 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14667" / 1594 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:14689" / 1595 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:14851" / 1596 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:15013" / 1597 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:15141" / 1598 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15175" / 1599 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:15315" / 1600 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:15337" / 1601 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:15465" / 1602 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15475" / 1603 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:15477" / 1604 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:15584" / 1605 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:15637" / 1606 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:15661" / 1607 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:15801" / 1608 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:15823" / 1609 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:15963" / 1610 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:15985" / 1611 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16147" / 1612 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16275" / 1613 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:16309" / 1614 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16437" / 1615 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:16471" / 1616 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16633" / 1617 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16761" / 1618 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:16773" / 1619 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:16795" / 1620 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16849" / 1621 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:16851" / 1622 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:16852" / 1623 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:16853" / 1624 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:16854" / 1625 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:16855" / 1626 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:16856" / 1627 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:16857" / 1628 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:16858" / 1629 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:16859" / 1630 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:16860" / 1631 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:16861" / 1632 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:16863" / 1633 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:16867" / 1634 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:16869" / 1635 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:16870" / 1636 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:16872" / 1637 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16875" / 1638 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:16876" / 1639 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:16877" / 1640 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:16878" / 1641 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:16880" / 1642 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:16881" / 1643 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:16915" / 1644 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:16917" / 1645 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:16918" / 1646 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16919" / 1647 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:16920" / 1648 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:16921" / 1649 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:16922" / 1650 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:16924" / 1651 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:16931" / 1652 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:16932" / 1653 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:16934" / 1654 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:16935" / 1655 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:16936" / 1656 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:16957" / 1657 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16959" / 1658 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:16960" / 1659 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:16961" / 1660 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:16962" / 1661 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:16963" / 1662 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:16964" / 1663 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:16965" / 1664 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:16966" / 1665 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:16968" / 1666 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:16969" / 1667 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:16970" / 1668 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:16971" / 1669 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:16973" / 1670 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:16974" / 1671 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:16975" / 1672 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:16977" / 1673 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:16978" / 1674 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:16979" / 1675 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:16980" / 1676 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:16981" / 1677 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:16982" / 1678 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:16983" / 1679 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:16984" / 1680 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:16985" / 1681 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:16987" / 1682 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:16988" / 1683 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:16989" / 1684 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:16991" / 1685 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:16995" / 1686 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:16998" / 1687 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:16999" / 1688 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:17000" / 1689 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:17001" / 1690 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:17003" / 1691 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:17004" / 1692 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:17009" / 1693 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:17097" / 1694 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:17167" / 1695 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:17169" / 1696 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:17172" / 1697 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:17259" / 1698 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:17421" / 1699 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:17907" / 1700 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:18067" / 1701 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18069" / 1702 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:18705" / 1703 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:18717" / 1704 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:19029" / 1705 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:19092" / 1706 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:19191" / 1707 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:19201" / 1708 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19311" / 1709 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:19361" / 1710 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:19363" / 1711 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19403" / 1712 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:19527" / 1713 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:19687" / 1714 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19839" / 1715 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:20011" / 1716 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20175" / 1717 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:20649" / 1718 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:20811" / 1719 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:21309" / 1720 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:21469" / 1721 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21471" / 1722 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:21631" / 1723 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21783" / 1724 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:21945" / 1725 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22107" / 1726 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22281" / 1727 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:22443" / 1728 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:22603" / 1729 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22605" / 1730 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:22765" / 1731 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22767" / 1732 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:22852" / 1733 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:22853" / 1734 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:22917" / 1735 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:22927" / 1736 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23091" / 1737 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:23199" / 1738 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:23249" / 1739 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:23565" / 1740 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:23577" / 1741 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:23599" / 1742 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:23727" / 1743 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:23889" / 1744 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:24000" / 1745 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24019" / 1746 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24059" / 1747 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24085" / 1748 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24177" / 1749 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:24202" / 1750 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:24213" / 1751 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:24409" / 1752 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24549" / 1753 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24571" / 1754 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24691" / 1755 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:24707" / 1756 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:24709" / 1757 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:24712" / 1758 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:24873" / 1759 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:25195" / 1760 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:25197" / 1761 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:25347" / 1762 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:25359" / 1763 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:25509" / 1764 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:25519" / 1765 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:348" / 1766 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:482" / 1767 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:973" / 1768 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:1002" / 1769 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:1022" / 1770 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:1616" / 1771 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:2027" / 1772 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:2631" / 1773 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2677" / 1774 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2793" / 1775 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3082" / 1776 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3163" / 1777 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3802" / 1778 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:3809" / 1779 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4061" / 1780 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:5180" / 1781 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:5529" / 1782 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:5530" / 1783 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:5661" / 1784 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5833" / 1785 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:7286" / 1786 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:7301" / 1787 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:7399" / 1788 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8582" / 1789 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:9952" / 1790 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10040" / 1791 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:10451" / 1792 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10596" / 1793 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:10613" / 1794 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11012" / 1795 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:11530" / 1796 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11660" / 1797 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:12308" / 1798 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:12653" / 1799 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12664" / 1800 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12705" / 1801 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:12706" / 1802 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12736" / 1803 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:12981" / 1804 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:12984" / 1805 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13113" / 1806 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13280" / 1807 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:14351" / 1808 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:15473" / 1809 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:24015" / 1810 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24061" / 1811 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24790" / 1812 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:24858" / 1813 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:24862" / 1814 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:24872" / 1815 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:308" / 1816 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:527" / 1817 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:1005" / 1818 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:1346" / 1819 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:1375" / 1820 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1832" / 1821 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:1974" / 1822 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:1977" / 1823 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:2023" / 1824 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2046" / 1825 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:2083" / 1826 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:2480" / 1827 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:2642" / 1828 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:2675" / 1829 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:2804" / 1830 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:3128" / 1831 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:3776" / 1832 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:4067" / 1833 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4100" / 1834 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:4189" / 1835 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:4305" / 1836 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:4317" / 1837 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:4360" / 1838 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:4371" / 1839 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4424" / 1840 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:4547" / 1841 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:4553" / 1842 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4586" / 1843 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:4598" / 1844 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4608" / 1845 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:4695" / 1846 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5234" / 1847 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:5271" / 1848 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:5396" / 1849 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:5555" / 1850 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:5582" / 1851 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5837" / 1852 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:5842" / 1853 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:5912" / 1854 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:5934" / 1855 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:5980" / 1856 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:5991" / 1857 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6239" / 1858 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:6262" / 1859 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:6307" / 1860 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:6530" / 1861 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:6854" / 1862 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:6889" / 1863 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7016" / 1864 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:7178" / 1865 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:7299" / 1866 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:7300" / 1867 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:7303" / 1868 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:7311" / 1869 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:7312" / 1870 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:7314" / 1871 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:7318" / 1872 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:7320" / 1873 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:7322" / 1874 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:7323" / 1875 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:7345" / 1876 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:7346" / 1877 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:7350" / 1878 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:7352" / 1879 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7353" / 1880 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:7355" / 1881 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:7360" / 1882 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:7363" / 1883 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:7364" / 1884 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7374" / 1885 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:7376" / 1886 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:7387" / 1887 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:7443" / 1888 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:7446" / 1889 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:9267" / 1890 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:9481" / 1891 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9483" / 1892 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:9807" / 1893 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:9873" / 1894 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10531" / 1895 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:10580" / 1896 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:10609" / 1897 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10887" / 1898 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:11011" / 1899 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:11066" / 1900 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:11217" / 1901 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:11228" / 1902 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:11263" / 1903 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12001" / 1904 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:12005" / 1905 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12058" / 1906 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12657" / 1907 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:12679" / 1908 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:12744" / 1909 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:12786" / 1910 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:12848" / 1911 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:13007" / 1912 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:13023" / 1913 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:13034" / 1914 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13172" / 1915 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:13293" / 1916 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:13294" / 1917 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:13321" / 1918 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:13347" / 1919 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:13349" / 1920 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:13381" / 1921 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:13398" / 1922 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:13411" / 1923 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:13425" / 1924 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:14991" / 1925 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:15731" / 1926 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16769" / 1927 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:16845" / 1928 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:17168" / 1929 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:17745" / 1930 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:17966" / 1931 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:19851" / 1932 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:21725" / 1933 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21738" / 1934 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:22119" / 1935 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:22843" / 1936 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:22845" / 1937 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:23573" / 1938 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:23649" / 1939 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:24026" / 1940 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24041" / 1941 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24512" / 1942 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24696" / 1943 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:24981" / 1944 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:25098" / 1945 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:12632" / 1946 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:23000" / 1947 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:346" / 1948 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:1652" / 1949 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:2045" / 1950 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:2758" / 1951 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3179" / 1952 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:4389" / 1953 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:15569" / 1954 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15576" / 1955 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1637" / 1956 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1959" / 1957 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:1975" / 1958 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:4229" / 1959 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4313" / 1960 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:17" / 1961 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24" / 1962 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:28" / 1963 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:70" / 1964 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:179" / 1965 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:186" / 1966 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:190" / 1967 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:232" / 1968 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:352" / 1969 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:355" / 1970 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:394" / 1971 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:477" / 1972 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:503" / 1973 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:510" / 1974 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:514" / 1975 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:556" / 1976 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:665" / 1977 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:672" / 1978 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:676" / 1979 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:718" / 1980 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:827" / 1981 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:834" / 1982 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:838" / 1983 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:880" / 1984 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:996" / 1985 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1000" / 1986 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1042" / 1987 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:1151" / 1988 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1158" / 1989 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1162" / 1990 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1204" / 1991 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:1313" / 1992 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1320" / 1993 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1324" / 1994 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1360" / 1995 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1362" / 1996 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:1366" / 1997 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:1372" / 1998 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:1482" / 1999 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1486" / 2000 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1489" / 2001 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:1528" / 2002 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:1644" / 2003 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1648" / 2004 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1690" / 2005 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:1799" / 2006 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1806" / 2007 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1810" / 2008 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1852" / 2009 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:1945" / 2010 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:1946" / 2011 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:1947" / 2012 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:1949" / 2013 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:1950" / 2014 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:1951" / 2015 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:1952" / 2016 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:1956" / 2017 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:1957" / 2018 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:1960" / 2019 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:1961" / 2020 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1962" / 2021 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:1963" / 2022 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:1964" / 2023 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:1967" / 2024 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:1969" / 2025 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:1970" / 2026 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:1971" / 2027 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:1972" / 2028 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:1973" / 2029 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:1976" / 2030 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:1978" / 2031 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:1979" / 2032 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:1980" / 2033 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:1981" / 2034 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:1984" / 2035 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:1985" / 2036 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:1986" / 2037 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:1987" / 2038 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:1988" / 2039 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:1989" / 2040 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1990" / 2041 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:1991" / 2042 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:1993" / 2043 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:1995" / 2044 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:1996" / 2045 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:1997" / 2046 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:1998" / 2047 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:1999" / 2048 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:2000" / 2049 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:2001" / 2050 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:2002" / 2051 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:2003" / 2052 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:2004" / 2053 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:2006" / 2054 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:2007" / 2055 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:2009" / 2056 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:2010" / 2057 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:2012" / 2058 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:2013" / 2059 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:2014" / 2060 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:2015" / 2061 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:2016" / 2062 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:2017" / 2063 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:2018" / 2064 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:2020" / 2065 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:2021" / 2066 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:2022" / 2067 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:2025" / 2068 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:2026" / 2069 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:2028" / 2070 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:2030" / 2071 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:2032" / 2072 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:2035" / 2073 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:2036" / 2074 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:2037" / 2075 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:2038" / 2076 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:2039" / 2077 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:2040" / 2078 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:2041" / 2079 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:2042" / 2080 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:2043" / 2081 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:2044" / 2082 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:2047" / 2083 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:2048" / 2084 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:2049" / 2085 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:2050" / 2086 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:2051" / 2087 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:2052" / 2088 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:2053" / 2089 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:2055" / 2090 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:2056" / 2091 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:2057" / 2092 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:2058" / 2093 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:2060" / 2094 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:2061" / 2095 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:2062" / 2096 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:2063" / 2097 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2064" / 2098 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:2065" / 2099 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:2066" / 2100 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:2067" / 2101 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:2068" / 2102 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:2069" / 2103 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:2070" / 2104 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:2071" / 2105 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:2072" / 2106 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:2073" / 2107 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2074" / 2108 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2075" / 2109 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:2076" / 2110 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2077" / 2111 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:2078" / 2112 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:2079" / 2113 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:2080" / 2114 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:2081" / 2115 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:2082" / 2116 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:2084" / 2117 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:2085" / 2118 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:2086" / 2119 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:2087" / 2120 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:2088" / 2121 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:2089" / 2122 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:2091" / 2123 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:2093" / 2124 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:2095" / 2125 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:2096" / 2126 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:2097" / 2127 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2098" / 2128 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:2099" / 2129 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:2100" / 2130 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:2104" / 2131 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:2105" / 2132 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:2106" / 2133 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:2123" / 2134 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2130" / 2135 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2134" / 2136 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:2176" / 2137 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:2285" / 2138 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2296" / 2139 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:2338" / 2140 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:2447" / 2141 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2454" / 2142 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2458" / 2143 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:2500" / 2144 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:2616" / 2145 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2620" / 2146 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:2623" / 2147 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:2656" / 2148 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2662" / 2149 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:2778" / 2150 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2782" / 2151 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:2785" / 2152 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:2824" / 2153 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:2933" / 2154 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2940" / 2155 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2944" / 2156 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:2986" / 2157 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3079" / 2158 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:3080" / 2159 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:3081" / 2160 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:3083" / 2161 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:3084" / 2162 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:3085" / 2163 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:3086" / 2164 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:3087" / 2165 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:3088" / 2166 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:3089" / 2167 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:3090" / 2168 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:3091" / 2169 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:3092" / 2170 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:3093" / 2171 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:3094" / 2172 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:3096" / 2173 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:3098" / 2174 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:3099" / 2175 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:3100" / 2176 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:3101" / 2177 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:3102" / 2178 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3103" / 2179 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:3104" / 2180 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:3105" / 2181 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:3106" / 2182 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3107" / 2183 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:3108" / 2184 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:3109" / 2185 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3110" / 2186 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:3111" / 2187 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:3112" / 2188 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:3113" / 2189 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:3114" / 2190 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:3115" / 2191 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:3116" / 2192 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:3118" / 2193 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:3119" / 2194 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:3120" / 2195 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:3121" / 2196 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:3122" / 2197 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:3123" / 2198 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3124" / 2199 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:3125" / 2200 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:3126" / 2201 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:3127" / 2202 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:3129" / 2203 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:3130" / 2204 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:3131" / 2205 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:3132" / 2206 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:3133" / 2207 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:3134" / 2208 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:3135" / 2209 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:3136" / 2210 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:3137" / 2211 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:3138" / 2212 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:3139" / 2213 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:3140" / 2214 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3141" / 2215 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:3143" / 2216 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:3144" / 2217 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:3145" / 2218 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3146" / 2219 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:3147" / 2220 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:3148" / 2221 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3149" / 2222 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:3150" / 2223 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:3151" / 2224 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:3152" / 2225 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3154" / 2226 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:3155" / 2227 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:3156" / 2228 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:3158" / 2229 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:3159" / 2230 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:3160" / 2231 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:3161" / 2232 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3162" / 2233 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:3164" / 2234 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:3166" / 2235 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:3168" / 2236 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3169" / 2237 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:3170" / 2238 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:3171" / 2239 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:3172" / 2240 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:3173" / 2241 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:3174" / 2242 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:3175" / 2243 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3176" / 2244 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:3177" / 2245 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:3178" / 2246 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:3180" / 2247 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:3181" / 2248 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:3182" / 2249 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:3183" / 2250 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:3184" / 2251 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:3185" / 2252 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:3186" / 2253 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:3188" / 2254 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3189" / 2255 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:3190" / 2256 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:3191" / 2257 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:3192" / 2258 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:3193" / 2259 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:3194" / 2260 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:3195" / 2261 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:3196" / 2262 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:3197" / 2263 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3198" / 2264 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:3199" / 2265 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:3200" / 2266 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:3201" / 2267 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:3202" / 2268 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:3203" / 2269 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:3204" / 2270 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:3205" / 2271 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:3206" / 2272 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:3207" / 2273 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3208" / 2274 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3209" / 2275 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:3210" / 2276 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3211" / 2277 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:3212" / 2278 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:3213" / 2279 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:3214" / 2280 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:3215" / 2281 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:3216" / 2282 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:3217" / 2283 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:3218" / 2284 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:3219" / 2285 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:3220" / 2286 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:3221" / 2287 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:3222" / 2288 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:3223" / 2289 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:3224" / 2290 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:3225" / 2291 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:3226" / 2292 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:3227" / 2293 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:3228" / 2294 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:3229" / 2295 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:3230" / 2296 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:3232" / 2297 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:3233" / 2298 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:3234" / 2299 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:3235" / 2300 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:3238" / 2301 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3239" / 2302 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:3257" / 2303 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3264" / 2304 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3268" / 2305 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3310" / 2306 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3419" / 2307 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3426" / 2308 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3430" / 2309 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3472" / 2310 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3581" / 2311 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3588" / 2312 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3592" / 2313 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3616" / 2314 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:3619" / 2315 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:3620" / 2316 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:3630" / 2317 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:3637" / 2318 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:3640" / 2319 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:3648" / 2320 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:3727" / 2321 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:3728" / 2322 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:3729" / 2323 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:3730" / 2324 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3731" / 2325 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:3732" / 2326 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:3733" / 2327 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:3734" / 2328 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:3735" / 2329 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:3736" / 2330 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:3737" / 2331 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:3738" / 2332 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:3739" / 2333 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:3740" / 2334 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:3741" / 2335 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:3742" / 2336 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:3743" / 2337 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3744" / 2338 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:3745" / 2339 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:3746" / 2340 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:3747" / 2341 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:3748" / 2342 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:3749" / 2343 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:3750" / 2344 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3751" / 2345 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:3752" / 2346 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:3753" / 2347 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:3754" / 2348 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3755" / 2349 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:3756" / 2350 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:3757" / 2351 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3758" / 2352 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:3759" / 2353 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:3760" / 2354 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:3761" / 2355 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:3762" / 2356 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:3763" / 2357 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:3764" / 2358 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:3766" / 2359 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:3767" / 2360 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:3768" / 2361 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:3769" / 2362 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:3770" / 2363 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:3771" / 2364 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3772" / 2365 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:3773" / 2366 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:3774" / 2367 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:3775" / 2368 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:3777" / 2369 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:3778" / 2370 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:3779" / 2371 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:3780" / 2372 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:3781" / 2373 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:3782" / 2374 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:3783" / 2375 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:3784" / 2376 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:3785" / 2377 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:3786" / 2378 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:3787" / 2379 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:3788" / 2380 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3789" / 2381 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:3791" / 2382 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:3792" / 2383 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:3793" / 2384 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3794" / 2385 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:3795" / 2386 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:3797" / 2387 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:3798" / 2388 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:3799" / 2389 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:3800" / 2390 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3803" / 2391 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:3804" / 2392 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:3806" / 2393 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:3807" / 2394 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:3808" / 2395 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:3810" / 2396 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:3812" / 2397 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:3814" / 2398 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:3816" / 2399 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3817" / 2400 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:3818" / 2401 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:3819" / 2402 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:3820" / 2403 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:3821" / 2404 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:3822" / 2405 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:3823" / 2406 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:3824" / 2407 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:3825" / 2408 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:3826" / 2409 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:3827" / 2410 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:3828" / 2411 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:3829" / 2412 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:3830" / 2413 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:3831" / 2414 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:3832" / 2415 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:3833" / 2416 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:3834" / 2417 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:3836" / 2418 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3837" / 2419 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:3838" / 2420 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:3839" / 2421 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:3840" / 2422 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:3841" / 2423 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:3842" / 2424 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:3843" / 2425 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:3844" / 2426 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:3845" / 2427 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3846" / 2428 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:3847" / 2429 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:3848" / 2430 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:3849" / 2431 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:3850" / 2432 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:3851" / 2433 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:3852" / 2434 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:3853" / 2435 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:3854" / 2436 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:3855" / 2437 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3856" / 2438 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3857" / 2439 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:3858" / 2440 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:3859" / 2441 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:3860" / 2442 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:3861" / 2443 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:3862" / 2444 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:3863" / 2445 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:3864" / 2446 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:3865" / 2447 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:3866" / 2448 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:3867" / 2449 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:3868" / 2450 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:3869" / 2451 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:3870" / 2452 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:3871" / 2453 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:3872" / 2454 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:3873" / 2455 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:3874" / 2456 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:3875" / 2457 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:3876" / 2458 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:3877" / 2459 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:3878" / 2460 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:3879" / 2461 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3880" / 2462 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:3881" / 2463 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:3882" / 2464 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:3883" / 2465 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:3884" / 2466 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:3885" / 2467 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3886" / 2468 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3887" / 2469 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:3888" / 2470 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3905" / 2471 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3912" / 2472 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3916" / 2473 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3958" / 2474 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:4074" / 2475 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4078" / 2476 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:4081" / 2477 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:4120" / 2478 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:4136" / 2479 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:4216" / 2480 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4233" / 2481 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:4234" / 2482 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:4236" / 2483 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4240" / 2484 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:4242" / 2485 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:4248" / 2486 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:4257" / 2487 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4276" / 2488 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4282" / 2489 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:4298" / 2490 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:4365" / 2491 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4391" / 2492 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4398" / 2493 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4402" / 2494 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:4444" / 2495 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:4560" / 2496 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4564" / 2497 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:4606" / 2498 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:4715" / 2499 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4722" / 2500 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4726" / 2501 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:4768" / 2502 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:4877" / 2503 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4884" / 2504 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4888" / 2505 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:4930" / 2506 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5039" / 2507 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5046" / 2508 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5050" / 2509 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:5067" / 2510 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5089" / 2511 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5092" / 2512 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5201" / 2513 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5208" / 2514 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5212" / 2515 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:5254" / 2516 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5370" / 2517 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5374" / 2518 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:5416" / 2519 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5687" / 2520 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5694" / 2521 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5698" / 2522 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:5740" / 2523 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5849" / 2524 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5856" / 2525 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5860" / 2526 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:5902" / 2527 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6011" / 2528 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6018" / 2529 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6022" / 2530 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:6064" / 2531 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6173" / 2532 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6180" / 2533 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6184" / 2534 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:6226" / 2535 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6335" / 2536 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6342" / 2537 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6346" / 2538 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:6388" / 2539 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6497" / 2540 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6504" / 2541 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6508" / 2542 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:6550" / 2543 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6633" / 2544 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6659" / 2545 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6666" / 2546 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6670" / 2547 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:6712" / 2548 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6821" / 2549 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6828" / 2550 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6832" / 2551 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:6874" / 2552 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6990" / 2553 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:6994" / 2554 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:7036" / 2555 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:7145" / 2556 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7152" / 2557 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:7156" / 2558 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:7198" / 2559 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:7469" / 2560 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7476" / 2561 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:7480" / 2562 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:7522" / 2563 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:7631" / 2564 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7638" / 2565 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:7641" / 2566 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:7642" / 2567 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:7669" / 2568 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:7670" / 2569 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:7680" / 2570 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:7684" / 2571 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:7687" / 2572 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:7690" / 2573 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:7698" / 2574 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:7793" / 2575 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7800" / 2576 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:7804" / 2577 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:7846" / 2578 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:7955" / 2579 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:7962" / 2580 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:7966" / 2581 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8008" / 2582 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:8013" / 2583 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8117" / 2584 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:8124" / 2585 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:8127" / 2586 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:8128" / 2587 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8170" / 2588 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:8279" / 2589 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:8286" / 2590 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:8289" / 2591 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:8290" / 2592 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8332" / 2593 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:8441" / 2594 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:8448" / 2595 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:8452" / 2596 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8494" / 2597 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:8603" / 2598 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:8610" / 2599 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:8614" / 2600 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8650" / 2601 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8652" / 2602 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:8656" / 2603 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:8662" / 2604 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:8765" / 2605 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:8772" / 2606 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:8776" / 2607 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8818" / 2608 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:8927" / 2609 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:8934" / 2610 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:8938" / 2611 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8980" / 2612 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9096" / 2613 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9100" / 2614 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9142" / 2615 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9225" / 2616 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9251" / 2617 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9258" / 2618 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9262" / 2619 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9304" / 2620 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9413" / 2621 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9420" / 2622 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9424" / 2623 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9466" / 2624 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9571" / 2625 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:9579" / 2626 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:9627" / 2627 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:9711" / 2628 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9737" / 2629 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9744" / 2630 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9748" / 2631 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9790" / 2632 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9895" / 2633 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:9899" / 2634 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9906" / 2635 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9909" / 2636 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:9910" / 2637 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9951" / 2638 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:9982" / 2639 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:10010" / 2640 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:10068" / 2641 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10072" / 2642 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10080" / 2643 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:10114" / 2644 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10197" / 2645 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10223" / 2646 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10230" / 2647 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10234" / 2648 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10276" / 2649 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10385" / 2650 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10392" / 2651 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10396" / 2652 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10432" / 2653 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10434" / 2654 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:10438" / 2655 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10444" / 2656 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:10532" / 2657 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:10533" / 2658 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:10534" / 2659 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:10535" / 2660 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:10536" / 2661 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:10537" / 2662 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:10538" / 2663 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:10539" / 2664 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:10540" / 2665 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:10541" / 2666 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:10542" / 2667 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:10543" / 2668 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:10544" / 2669 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:10545" / 2670 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:10546" / 2671 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:10547" / 2672 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10548" / 2673 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:10549" / 2674 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:10550" / 2675 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:10551" / 2676 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:10552" / 2677 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:10553" / 2678 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:10554" / 2679 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10555" / 2680 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:10556" / 2681 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:10559" / 2682 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:10560" / 2683 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:10561" / 2684 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:10562" / 2685 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:10563" / 2686 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:10564" / 2687 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:10565" / 2688 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:10566" / 2689 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:10567" / 2690 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:10568" / 2691 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:10570" / 2692 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:10571" / 2693 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:10572" / 2694 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:10573" / 2695 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:10574" / 2696 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:10575" / 2697 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10576" / 2698 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:10577" / 2699 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:10578" / 2700 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:10579" / 2701 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:10581" / 2702 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:10582" / 2703 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10583" / 2704 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:10584" / 2705 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:10585" / 2706 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10586" / 2707 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:10587" / 2708 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:10588" / 2709 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:10589" / 2710 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:10590" / 2711 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:10591" / 2712 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:10592" / 2713 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10593" / 2714 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:10595" / 2715 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:10597" / 2716 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10598" / 2717 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:10599" / 2718 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:10600" / 2719 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10601" / 2720 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:10602" / 2721 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:10603" / 2722 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:10604" / 2723 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10607" / 2724 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:10608" / 2725 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:10610" / 2726 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:10611" / 2727 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10612" / 2728 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:10614" / 2729 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10616" / 2730 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:10617" / 2731 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:10618" / 2732 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:10620" / 2733 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:10621" / 2734 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:10622" / 2735 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:10623" / 2736 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:10624" / 2737 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:10625" / 2738 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:10626" / 2739 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:10627" / 2740 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:10628" / 2741 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:10629" / 2742 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:10630" / 2743 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:10631" / 2744 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:10632" / 2745 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:10633" / 2746 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:10634" / 2747 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:10635" / 2748 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:10636" / 2749 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:10637" / 2750 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:10638" / 2751 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:10640" / 2752 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10641" / 2753 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:10642" / 2754 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:10643" / 2755 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:10644" / 2756 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:10645" / 2757 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:10646" / 2758 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:10647" / 2759 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:10648" / 2760 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:10649" / 2761 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10650" / 2762 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:10651" / 2763 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:10652" / 2764 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:10653" / 2765 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:10654" / 2766 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:10655" / 2767 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:10656" / 2768 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:10657" / 2769 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:10658" / 2770 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:10659" / 2771 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10660" / 2772 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10661" / 2773 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:10662" / 2774 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10663" / 2775 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:10664" / 2776 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:10665" / 2777 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:10666" / 2778 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:10667" / 2779 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:10668" / 2780 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:10669" / 2781 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:10670" / 2782 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:10671" / 2783 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:10672" / 2784 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:10673" / 2785 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:10674" / 2786 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:10675" / 2787 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:10676" / 2788 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:10677" / 2789 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:10678" / 2790 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:10679" / 2791 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:10680" / 2792 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:10681" / 2793 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:10682" / 2794 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:10683" / 2795 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10684" / 2796 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:10685" / 2797 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:10686" / 2798 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:10687" / 2799 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:10688" / 2800 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:10690" / 2801 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:10691" / 2802 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:10692" / 2803 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:10709" / 2804 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10716" / 2805 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10720" / 2806 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10762" / 2807 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10871" / 2808 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10878" / 2809 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10882" / 2810 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10924" / 2811 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11033" / 2812 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11040" / 2813 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11043" / 2814 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:11044" / 2815 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11068" / 2816 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:11086" / 2817 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11195" / 2818 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11202" / 2819 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11206" / 2820 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11248" / 2821 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11394" / 2822 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:11447" / 2823 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:11515" / 2824 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:11519" / 2825 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11526" / 2826 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11529" / 2827 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:11554" / 2828 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:11560" / 2829 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:11571" / 2830 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:11586" / 2831 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:11602" / 2832 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:11630" / 2833 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:11681" / 2834 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11688" / 2835 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11692" / 2836 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11734" / 2837 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11843" / 2838 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11850" / 2839 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11854" / 2840 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11896" / 2841 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12174" / 2842 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12178" / 2843 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12220" / 2844 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12329" / 2845 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12336" / 2846 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12340" / 2847 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12382" / 2848 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12491" / 2849 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12498" / 2850 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12502" / 2851 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12544" / 2852 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12660" / 2853 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12815" / 2854 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12822" / 2855 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12825" / 2856 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:12826" / 2857 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:12850" / 2858 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:12868" / 2859 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:12874" / 2860 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13139" / 2861 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13146" / 2862 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13150" / 2863 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:13152" / 2864 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:13153" / 2865 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:13192" / 2866 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13275" / 2867 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13354" / 2868 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13463" / 2869 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13470" / 2870 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13474" / 2871 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:13516" / 2872 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13794" / 2873 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13798" / 2874 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:13840" / 2875 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13949" / 2876 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13956" / 2877 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13960" / 2878 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14002" / 2879 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:14111" / 2880 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14118" / 2881 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14122" / 2882 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14164" / 2883 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:14273" / 2884 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14280" / 2885 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14284" / 2886 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14326" / 2887 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:14435" / 2888 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14442" / 2889 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14446" / 2890 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14488" / 2891 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:14597" / 2892 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14604" / 2893 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14608" / 2894 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14650" / 2895 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:14759" / 2896 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14766" / 2897 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14770" / 2898 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14812" / 2899 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:14921" / 2900 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14928" / 2901 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14932" / 2902 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:14974" / 2903 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15083" / 2904 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15090" / 2905 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:15094" / 2906 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15136" / 2907 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15245" / 2908 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15252" / 2909 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:15256" / 2910 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15298" / 2911 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15407" / 2912 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15414" / 2913 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:15418" / 2914 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15460" / 2915 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15466" / 2916 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:15580" / 2917 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15622" / 2918 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15738" / 2919 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:15742" / 2920 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15784" / 2921 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:15893" / 2922 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15900" / 2923 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:15904" / 2924 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15946" / 2925 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16055" / 2926 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16062" / 2927 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16066" / 2928 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:16108" / 2929 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16217" / 2930 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16224" / 2931 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16228" / 2932 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:16270" / 2933 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16379" / 2934 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16386" / 2935 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16390" / 2936 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:16432" / 2937 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16541" / 2938 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16548" / 2939 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16552" / 2940 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:16594" / 2941 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16599" / 2942 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:16703" / 2943 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16710" / 2944 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16714" / 2945 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:16756" / 2946 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:16865" / 2947 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17034" / 2948 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17038" / 2949 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:17080" / 2950 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:17189" / 2951 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17196" / 2952 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17200" / 2953 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:17242" / 2954 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:17351" / 2955 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17358" / 2956 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17362" / 2957 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:17404" / 2958 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:17513" / 2959 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17520" / 2960 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17524" / 2961 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:17566" / 2962 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:17675" / 2963 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17682" / 2964 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17686" / 2965 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:17728" / 2966 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:17844" / 2967 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17848" / 2968 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:17890" / 2969 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:17999" / 2970 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18006" / 2971 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18010" / 2972 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:18052" / 2973 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:18161" / 2974 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18168" / 2975 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18172" / 2976 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:18214" / 2977 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:18323" / 2978 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18330" / 2979 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18334" / 2980 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:18376" / 2981 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:18485" / 2982 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18492" / 2983 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18496" / 2984 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:18538" / 2985 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:18647" / 2986 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18654" / 2987 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18658" / 2988 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:18700" / 2989 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:18809" / 2990 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18816" / 2991 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18820" / 2992 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:18862" / 2993 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:18971" / 2994 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18978" / 2995 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18982" / 2996 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19024" / 2997 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:19133" / 2998 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19140" / 2999 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:19144" / 3000 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19186" / 3001 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:19295" / 3002 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19302" / 3003 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:19306" / 3004 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19348" / 3005 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:19457" / 3006 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19464" / 3007 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:19468" / 3008 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19510" / 3009 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:19619" / 3010 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19626" / 3011 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:19630" / 3012 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19672" / 3013 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:19781" / 3014 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19788" / 3015 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:19792" / 3016 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19834" / 3017 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:19943" / 3018 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19950" / 3019 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:19954" / 3020 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:19996" / 3021 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:20002" / 3022 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:20105" / 3023 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20112" / 3024 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:20116" / 3025 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:20158" / 3026 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:20267" / 3027 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20274" / 3028 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:20278" / 3029 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:20320" / 3030 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:20429" / 3031 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20436" / 3032 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:20440" / 3033 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:20482" / 3034 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:20591" / 3035 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20598" / 3036 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:20602" / 3037 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:20644" / 3038 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:20753" / 3039 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20760" / 3040 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:20764" / 3041 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:20806" / 3042 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:20915" / 3043 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20922" / 3044 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:20926" / 3045 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:20968" / 3046 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:21077" / 3047 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21084" / 3048 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:21088" / 3049 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:21130" / 3050 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:21239" / 3051 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21246" / 3052 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:21250" / 3053 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:21292" / 3054 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:21401" / 3055 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21408" / 3056 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:21412" / 3057 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:21454" / 3058 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:21563" / 3059 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21570" / 3060 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:21574" / 3061 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:21616" / 3062 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:21732" / 3063 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:21736" / 3064 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:21778" / 3065 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:21887" / 3066 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21894" / 3067 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:21898" / 3068 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:21940" / 3069 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:22049" / 3070 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22056" / 3071 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:22060" / 3072 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:22102" / 3073 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:22211" / 3074 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22218" / 3075 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:22222" / 3076 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:22264" / 3077 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:22373" / 3078 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22380" / 3079 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:22384" / 3080 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:22426" / 3081 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:22535" / 3082 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22542" / 3083 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:22546" / 3084 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:22588" / 3085 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:22697" / 3086 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22704" / 3087 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:22708" / 3088 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:22750" / 3089 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:22866" / 3090 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:22870" / 3091 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:22912" / 3092 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23021" / 3093 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23028" / 3094 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:23032" / 3095 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:23074" / 3096 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23190" / 3097 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:23194" / 3098 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:23236" / 3099 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23345" / 3100 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23352" / 3101 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:23356" / 3102 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:23398" / 3103 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23514" / 3104 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:23518" / 3105 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:23560" / 3106 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23669" / 3107 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23676" / 3108 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:23680" / 3109 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:23722" / 3110 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23831" / 3111 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23838" / 3112 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:23842" / 3113 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:23884" / 3114 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:23980" / 3115 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23993" / 3116 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24004" / 3117 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24007" / 3118 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24021" / 3119 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24037" / 3120 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24040" / 3121 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24043" / 3122 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24046" / 3123 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24062" / 3124 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24155" / 3125 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24162" / 3126 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:24166" / 3127 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:24208" / 3128 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:24317" / 3129 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24324" / 3130 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24328" / 3131 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24370" / 3132 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24479" / 3133 N11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24486" / 3134 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24490" / 3135 N11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24532" / 3136 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24648" / 3137 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:24652" / 3138 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:24694" / 3139 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:24814" / 3140 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:24856" / 3141 N11
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:24976" / 3142 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:25127" / 3143 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:25134" / 3144 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:25138" / 3145 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:25180" / 3146 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:25289" / 3147 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:25296" / 3148 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:25300" / 3149 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:25342" / 3150 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:25451" / 3151 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:25462" / 3152 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:25504" / 3153 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:31" / 3154 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:64" / 3155 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:85" / 3156 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:153" / 3157 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:193" / 3158 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:201" / 3159 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:337" / 3160 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:357" / 3161 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:369" / 3162 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:374" / 3163 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:385" / 3164 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:389" / 3165 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:391" / 3166 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:407" / 3167 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:410" / 3168 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:416" / 3169 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:462" / 3170 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:517" / 3171 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:679" / 3172 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:841" / 3173 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:849" / 3174 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:895" / 3175 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1011" / 3176 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1165" / 3177 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:1287" / 3178 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1300" / 3179 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:1323" / 3180 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:1327" / 3181 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:1352" / 3182 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:1369" / 3183 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:1379" / 3184 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:1380" / 3185 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:1449" / 3186 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1611" / 3187 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1651" / 3188 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:1773" / 3189 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1813" / 3190 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:1846" / 3191 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1867" / 3192 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1935" / 3193 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2191" / 3194 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2259" / 3195 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2299" / 3196 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:2332" / 3197 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2353" / 3198 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2421" / 3199 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2515" / 3200 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2583" / 3201 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2659" / 3202 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2745" / 3203 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2837" / 3204 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:2907" / 3205 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:2947" / 3206 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:2955" / 3207 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2999" / 3208 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3069" / 3209 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3271" / 3210 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3304" / 3211 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3393" / 3212 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3433" / 3213 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3466" / 3214 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3555" / 3215 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3577" / 3216 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:3595" / 3217 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3602" / 3218 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:3611" / 3219 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:3612" / 3220 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:3627" / 3221 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:3638" / 3222 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3647" / 3223 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3717" / 3224 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3919" / 3225 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3952" / 3226 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3971" / 3227 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3973" / 3228 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4041" / 3229 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4203" / 3230 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4213" / 3231 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:4215" / 3232 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:4217" / 3233 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:4218" / 3234 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:4219" / 3235 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:4220" / 3236 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:4221" / 3237 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:4222" / 3238 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:4224" / 3239 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:4225" / 3240 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:4227" / 3241 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:4239" / 3242 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:4241" / 3243 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:4244" / 3244 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:4245" / 3245 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:4246" / 3246 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:4247" / 3247 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:4249" / 3248 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:4250" / 3249 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:4252" / 3250 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:4253" / 3251 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:4254" / 3252 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:4255" / 3253 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:4256" / 3254 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:4258" / 3255 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:4259" / 3256 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:4260" / 3257 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:4261" / 3258 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:4263" / 3259 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:4264" / 3260 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:4265" / 3261 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:4266" / 3262 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:4267" / 3263 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:4268" / 3264 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:4269" / 3265 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:4270" / 3266 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:4271" / 3267 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:4272" / 3268 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:4274" / 3269 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4275" / 3270 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:4277" / 3271 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:4278" / 3272 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:4280" / 3273 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:4281" / 3274 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:4283" / 3275 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:4284" / 3276 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:4285" / 3277 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:4286" / 3278 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4288" / 3279 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:4289" / 3280 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:4290" / 3281 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:4292" / 3282 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:4293" / 3283 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:4294" / 3284 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:4296" / 3285 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:4300" / 3286 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:4302" / 3287 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:4303" / 3288 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:4304" / 3289 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:4306" / 3290 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:4307" / 3291 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:4308" / 3292 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:4309" / 3293 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:4310" / 3294 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:4311" / 3295 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:4312" / 3296 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:4314" / 3297 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:4315" / 3298 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:4316" / 3299 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:4318" / 3300 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:4319" / 3301 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:4320" / 3302 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:4321" / 3303 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4322" / 3304 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:4323" / 3305 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:4324" / 3306 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:4325" / 3307 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:4326" / 3308 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:4327" / 3309 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:4328" / 3310 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:4329" / 3311 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:4330" / 3312 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:4332" / 3313 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:4333" / 3314 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:4334" / 3315 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:4335" / 3316 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:4336" / 3317 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:4337" / 3318 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:4338" / 3319 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:4339" / 3320 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:4340" / 3321 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:4341" / 3322 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:4342" / 3323 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:4343" / 3324 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:4344" / 3325 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:4345" / 3326 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:4346" / 3327 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:4347" / 3328 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:4348" / 3329 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:4349" / 3330 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:4350" / 3331 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:4351" / 3332 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:4352" / 3333 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:4353" / 3334 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:4354" / 3335 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:4355" / 3336 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:4356" / 3337 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:4357" / 3338 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:4359" / 3339 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:4361" / 3340 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:4362" / 3341 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:4363" / 3342 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:4364" / 3343 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:4366" / 3344 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:4367" / 3345 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:4368" / 3346 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:4369" / 3347 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:4370" / 3348 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:4372" / 3349 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:4373" / 3350 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:4374" / 3351 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:4405" / 3352 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:4413" / 3353 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:4438" / 3354 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4459" / 3355 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4527" / 3356 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4540" / 3357 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4567" / 3358 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:4689" / 3359 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4737" / 3360 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:4762" / 3361 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4783" / 3362 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4794" / 3363 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:4851" / 3364 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4899" / 3365 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:4924" / 3366 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:4945" / 3367 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5013" / 3368 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5083" / 3369 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5087" / 3370 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:5175" / 3371 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5248" / 3372 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5269" / 3373 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5337" / 3374 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5373" / 3375 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:5499" / 3376 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5509" / 3377 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:5511" / 3378 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:5515" / 3379 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:5516" / 3380 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:5518" / 3381 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:5519" / 3382 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:5540" / 3383 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:5548" / 3384 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:5551" / 3385 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:5552" / 3386 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:5557" / 3387 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:5561" / 3388 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:5562" / 3389 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:5576" / 3390 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:5579" / 3391 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:5589" / 3392 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:5593" / 3393 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5601" / 3394 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:5605" / 3395 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:5606" / 3396 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:5607" / 3397 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:5609" / 3398 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:5610" / 3399 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:5611" / 3400 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:5612" / 3401 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:5613" / 3402 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:5614" / 3403 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:5619" / 3404 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:5620" / 3405 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:5621" / 3406 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:5622" / 3407 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:5628" / 3408 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:5633" / 3409 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:5635" / 3410 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:5636" / 3411 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:5637" / 3412 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5639" / 3413 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:5644" / 3414 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:5651" / 3415 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:5655" / 3416 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:5662" / 3417 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:5664" / 3418 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:5669" / 3419 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:5734" / 3420 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5755" / 3421 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5823" / 3422 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5915" / 3423 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5985" / 3424 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6241" / 3425 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6403" / 3426 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6471" / 3427 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6484" / 3428 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6618" / 3429 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:6706" / 3430 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6831" / 3431 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:6868" / 3432 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:6957" / 3433 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6993" / 3434 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:7030" / 3435 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7042" / 3436 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:7119" / 3437 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:7204" / 3438 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:7211" / 3439 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7213" / 3440 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7281" / 3441 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:7294" / 3442 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:7516" / 3443 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7605" / 3444 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:7697" / 3445 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7699" / 3446 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7767" / 3447 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:7840" / 3448 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:7861" / 3449 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7929" / 3450 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8002" / 3451 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8023" / 3452 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8091" / 3453 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8183" / 3454 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:8253" / 3455 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8275" / 3456 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:8345" / 3457 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:8415" / 3458 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8507" / 3459 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:8577" / 3460 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8669" / 3461 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:8739" / 3462 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8901" / 3463 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:8974" / 3464 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9063" / 3465 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9076" / 3466 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9137" / 3467 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:9298" / 3468 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9387" / 3469 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9423" / 3470 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:9549" / 3471 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9566" / 3472 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:9587" / 3473 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:9590" / 3474 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:9623" / 3475 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:9629" / 3476 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:9635" / 3477 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:9636" / 3478 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:9639" / 3479 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:9643" / 3480 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9649" / 3481 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:9651" / 3482 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:9653" / 3483 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:9654" / 3484 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:9655" / 3485 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:9656" / 3486 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:9657" / 3487 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:9662" / 3488 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:9663" / 3489 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:9664" / 3490 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:9669" / 3491 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:9671" / 3492 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:9672" / 3493 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:9674" / 3494 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:9675" / 3495 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:9676" / 3496 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:9678" / 3497 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:9679" / 3498 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:9680" / 3499 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:9681" / 3500 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:9683" / 3501 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:9684" / 3502 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:9686" / 3503 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:9687" / 3504 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:9688" / 3505 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:9689" / 3506 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:9690" / 3507 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:9692" / 3508 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:9693" / 3509 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:9701" / 3510 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:9703" / 3511 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:9705" / 3512 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:9709" / 3513 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:9713" / 3514 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:9714" / 3515 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:9719" / 3516 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:9724" / 3517 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9795" / 3518 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9796" / 3519 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:9803" / 3520 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9960" / 3521 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:9966" / 3522 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10035" / 3523 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10048" / 3524 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:10065" / 3525 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:10182" / 3526 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:10237" / 3527 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:10245" / 3528 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10399" / 3529 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:10453" / 3530 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10521" / 3531 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10723" / 3532 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:10731" / 3533 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10756" / 3534 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10777" / 3535 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10845" / 3536 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10885" / 3537 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:10937" / 3538 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11007" / 3539 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11029" / 3540 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:11047" / 3541 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:11092" / 3542 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11099" / 3543 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11169" / 3544 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11205" / 3545 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:11209" / 3546 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:11331" / 3547 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11405" / 3548 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:11533" / 3549 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:11550" / 3550 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:11551" / 3551 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:11567" / 3552 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:11575" / 3553 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:11580" / 3554 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:11583" / 3555 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:11655" / 3556 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11817" / 3557 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11902" / 3558 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11979" / 3559 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12303" / 3560 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12388" / 3561 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:12395" / 3562 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12397" / 3563 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12465" / 3564 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12627" / 3565 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12640" / 3566 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12649" / 3567 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:12658" / 3568 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:12659" / 3569 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:12663" / 3570 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:12665" / 3571 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:12677" / 3572 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:12685" / 3573 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:12688" / 3574 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:12691" / 3575 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:12692" / 3576 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:12693" / 3577 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:12694" / 3578 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:12701" / 3579 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:12708" / 3580 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:12709" / 3581 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:12717" / 3582 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12720" / 3583 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12722" / 3584 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:12723" / 3585 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:12727" / 3586 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:12731" / 3587 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:12733" / 3588 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:12737" / 3589 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:12740" / 3590 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:12746" / 3591 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:12758" / 3592 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:12762" / 3593 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:12774" / 3594 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:12811" / 3595 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:12829" / 3596 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:12864" / 3597 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:12881" / 3598 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12951" / 3599 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12962" / 3600 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:12967" / 3601 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:12968" / 3602 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:12970" / 3603 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:12976" / 3604 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12978" / 3605 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:12979" / 3606 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:12980" / 3607 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:12989" / 3608 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:12992" / 3609 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:12994" / 3610 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:12995" / 3611 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:12997" / 3612 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:12999" / 3613 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13000" / 3614 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:13003" / 3615 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:13004" / 3616 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:13009" / 3617 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:13012" / 3618 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:13013" / 3619 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:13014" / 3620 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:13024" / 3621 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13029" / 3622 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:13031" / 3623 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:13041" / 3624 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:13045" / 3625 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13053" / 3626 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:13056" / 3627 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13057" / 3628 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:13058" / 3629 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:13059" / 3630 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13063" / 3631 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13064" / 3632 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13065" / 3633 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:13066" / 3634 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:13069" / 3635 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13071" / 3636 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:13072" / 3637 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13073" / 3638 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:13074" / 3639 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:13077" / 3640 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:13078" / 3641 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:13079" / 3642 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13080" / 3643 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:13085" / 3644 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:13087" / 3645 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:13089" / 3646 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13090" / 3647 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13091" / 3648 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:13092" / 3649 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13094" / 3650 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:13095" / 3651 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13096" / 3652 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:13099" / 3653 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13102" / 3654 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:13103" / 3655 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:13107" / 3656 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:13108" / 3657 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:13109" / 3658 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:13111" / 3659 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:13114" / 3660 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13115" / 3661 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:13116" / 3662 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:13119" / 3663 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13121" / 3664 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:13126" / 3665 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13205" / 3666 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13367" / 3667 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13477" / 3668 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:13599" / 3669 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13923" / 3670 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14015" / 3671 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:14085" / 3672 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14098" / 3673 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:14232" / 3674 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:14247" / 3675 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14341" / 3676 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14409" / 3677 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14571" / 3678 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14663" / 3679 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:14733" / 3680 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14827" / 3681 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14895" / 3682 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14987" / 3683 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:14989" / 3684 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:15030" / 3685 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:15057" / 3686 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:15151" / 3687 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:15219" / 3688 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:15313" / 3689 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:15381" / 3690 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:15543" / 3691 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:15635" / 3692 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:15705" / 3693 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:15961" / 3694 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16029" / 3695 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:16121" / 3696 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:16123" / 3697 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16191" / 3698 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:16285" / 3699 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16353" / 3700 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:16447" / 3701 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16515" / 3702 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:16677" / 3703 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:16839" / 3704 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:16933" / 3705 N11
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17093" / 3706 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:17163" / 3707 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:17257" / 3708 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17325" / 3709 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:17419" / 3710 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17487" / 3711 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:17581" / 3712 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17649" / 3713 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:17743" / 3714 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17811" / 3715 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:17973" / 3716 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:18135" / 3717 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:18229" / 3718 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18297" / 3719 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:18391" / 3720 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18459" / 3721 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:18553" / 3722 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18621" / 3723 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:18715" / 3724 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18783" / 3725 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:18945" / 3726 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:19037" / 3727 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:19107" / 3728 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:19269" / 3729 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:19431" / 3730 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:19525" / 3731 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19593" / 3732 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:19685" / 3733 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:19755" / 3734 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:19849" / 3735 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19917" / 3736 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20079" / 3737 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20173" / 3738 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20241" / 3739 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20335" / 3740 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20403" / 3741 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20497" / 3742 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20565" / 3743 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20659" / 3744 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20727" / 3745 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20889" / 3746 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:20983" / 3747 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21051" / 3748 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:21145" / 3749 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21213" / 3750 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:21307" / 3751 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21375" / 3752 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:21537" / 3753 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:21550" / 3754 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:21613" / 3755 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:21629" / 3756 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:21699" / 3757 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:21793" / 3758 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22023" / 3759 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:22279" / 3760 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22347" / 3761 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:22441" / 3762 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22509" / 3763 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:22671" / 3764 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:22833" / 3765 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:22995" / 3766 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23089" / 3767 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23157" / 3768 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23251" / 3769 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23319" / 3770 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23413" / 3771 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23481" / 3772 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23521" / 3773 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:23643" / 3774 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23737" / 3775 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23805" / 3776 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23967" / 3777 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23978" / 3778 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23984" / 3779 N11
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23985" / 3780 N11
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23986" / 3781 N11
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23988" / 3782 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23989" / 3783 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23990" / 3784 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23991" / 3785 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23992" / 3786 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23994" / 3787 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23995" / 3788 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23996" / 3789 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23997" / 3790 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23998" / 3791 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23999" / 3792 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24001" / 3793 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24002" / 3794 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24003" / 3795 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24005" / 3796 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24006" / 3797 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24008" / 3798 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24009" / 3799 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24010" / 3800 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24011" / 3801 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24012" / 3802 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24013" / 3803 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24014" / 3804 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24016" / 3805 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24017" / 3806 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24020" / 3807 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24023" / 3808 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24024" / 3809 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24025" / 3810 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24027" / 3811 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24028" / 3812 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24029" / 3813 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24030" / 3814 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24031" / 3815 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24032" / 3816 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24033" / 3817 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24034" / 3818 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24035" / 3819 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24036" / 3820 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24038" / 3821 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24039" / 3822 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24042" / 3823 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24045" / 3824 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24047" / 3825 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24048" / 3826 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24049" / 3827 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24050" / 3828 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24052" / 3829 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24053" / 3830 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24054" / 3831 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24056" / 3832 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24057" / 3833 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24058" / 3834 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24060" / 3835 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24064" / 3836 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24066" / 3837 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24067" / 3838 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24068" / 3839 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24069" / 3840 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24070" / 3841 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24071" / 3842 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24072" / 3843 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24073" / 3844 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24074" / 3845 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24075" / 3846 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24076" / 3847 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24077" / 3848 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24079" / 3849 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24080" / 3850 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24081" / 3851 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24082" / 3852 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24083" / 3853 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24084" / 3854 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24086" / 3855 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24087" / 3856 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24088" / 3857 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24089" / 3858 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24090" / 3859 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24091" / 3860 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24092" / 3861 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24093" / 3862 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24094" / 3863 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24095" / 3864 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24096" / 3865 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24097" / 3866 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24098" / 3867 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24099" / 3868 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24100" / 3869 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24101" / 3870 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24102" / 3871 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24103" / 3872 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24104" / 3873 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24105" / 3874 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24106" / 3875 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24107" / 3876 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24108" / 3877 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24109" / 3878 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24110" / 3879 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24111" / 3880 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24112" / 3881 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24113" / 3882 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24114" / 3883 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24116" / 3884 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24118" / 3885 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24119" / 3886 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24120" / 3887 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24121" / 3888 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24122" / 3889 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24123" / 3890 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24124" / 3891 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24125" / 3892 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24126" / 3893 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24127" / 3894 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24128" / 3895 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24129" / 3896 N11
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24130" / 3897 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24131" / 3898 N11
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24132" / 3899 N11
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24133" / 3900 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24136" / 3901 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24137" / 3902 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24138" / 3903 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24169" / 3904 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:24223" / 3905 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:24291" / 3906 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24331" / 3907 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24364" / 3908 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24385" / 3909 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24453" / 3910 N11
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24493" / 3911 N11
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24501" / 3912 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24526" / 3913 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24547" / 3914 N11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24615" / 3915 N11
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24777" / 3916 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:25033" / 3917 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:25263" / 3918 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:25357" / 3919 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:25425" / 3920 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:25587" / 3921 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:4" / 3922 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:45" / 3923 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:61" / 3924 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:67" / 3925 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:86" / 3926 N11
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:166" / 3927 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:207" / 3928 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:315" / 3929 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:325" / 3930 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:326" / 3931 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:327" / 3932 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:328" / 3933 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:329" / 3934 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:330" / 3935 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:331" / 3936 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:332" / 3937 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:333" / 3938 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:334" / 3939 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:335" / 3940 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:336" / 3941 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:338" / 3942 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:339" / 3943 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:343" / 3944 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:345" / 3945 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:347" / 3946 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:349" / 3947 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:350" / 3948 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:351" / 3949 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:353" / 3950 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:354" / 3951 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:356" / 3952 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:358" / 3953 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:359" / 3954 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:360" / 3955 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:361" / 3956 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:362" / 3957 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:364" / 3958 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:365" / 3959 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:366" / 3960 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:367" / 3961 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:368" / 3962 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:370" / 3963 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:371" / 3964 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:372" / 3965 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:373" / 3966 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:375" / 3967 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:376" / 3968 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:377" / 3969 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:378" / 3970 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:379" / 3971 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:380" / 3972 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:381" / 3973 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:382" / 3974 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:383" / 3975 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:384" / 3976 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:386" / 3977 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:387" / 3978 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:390" / 3979 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:392" / 3980 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:393" / 3981 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:395" / 3982 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:396" / 3983 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:397" / 3984 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:398" / 3985 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:400" / 3986 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:401" / 3987 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:402" / 3988 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:404" / 3989 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:405" / 3990 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:406" / 3991 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:408" / 3992 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:411" / 3993 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:412" / 3994 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:414" / 3995 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:415" / 3996 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:417" / 3997 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:418" / 3998 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:419" / 3999 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:420" / 4000 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:421" / 4001 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:422" / 4002 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:423" / 4003 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:424" / 4004 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:425" / 4005 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:426" / 4006 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:427" / 4007 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:428" / 4008 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:429" / 4009 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:430" / 4010 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:431" / 4011 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:432" / 4012 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:434" / 4013 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:435" / 4014 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:436" / 4015 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:437" / 4016 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:438" / 4017 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:439" / 4018 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:440" / 4019 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:441" / 4020 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:442" / 4021 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:444" / 4022 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:445" / 4023 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:446" / 4024 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:447" / 4025 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:448" / 4026 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:449" / 4027 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:450" / 4028 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:451" / 4029 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:452" / 4030 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:453" / 4031 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:454" / 4032 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:455" / 4033 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:456" / 4034 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:457" / 4035 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:458" / 4036 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:459" / 4037 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:460" / 4038 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:461" / 4039 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:463" / 4040 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:464" / 4041 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:465" / 4042 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:466" / 4043 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:467" / 4044 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:468" / 4045 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:469" / 4046 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:470" / 4047 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:471" / 4048 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:472" / 4049 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:473" / 4050 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:474" / 4051 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:475" / 4052 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:476" / 4053 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:478" / 4054 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:479" / 4055 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:480" / 4056 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:481" / 4057 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:483" / 4058 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:484" / 4059 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:485" / 4060 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:486" / 4061 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:490" / 4062 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:531" / 4063 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:550" / 4064 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:639" / 4065 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:652" / 4066 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:693" / 4067 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:715" / 4068 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:801" / 4069 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:814" / 4070 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:855" / 4071 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:877" / 4072 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:963" / 4073 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:976" / 4074 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:1125" / 4075 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1138" / 4076 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:1179" / 4077 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1195" / 4078 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:1201" / 4079 N11
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1334" / 4080 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:1341" / 4081 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1344" / 4082 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:1351" / 4083 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:1354" / 4084 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:1357" / 4085 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:1363" / 4086 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1365" / 4087 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:1382" / 4088 N11
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:1462" / 4089 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:1534" / 4090 N11
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:1624" / 4091 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:1665" / 4092 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1681" / 4093 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:1687" / 4094 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1696" / 4095 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:1706" / 4096 N11
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:1827" / 4097 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:1843" / 4098 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:1849" / 4099 N11
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2173" / 4100 N11
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2272" / 4101 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:2313" / 4102 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2329" / 4103 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:2335" / 4104 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2497" / 4105 N11
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2596" / 4106 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:2637" / 4107 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2658" / 4108 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:2668" / 4109 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:2678" / 4110 N11
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:2781" / 4111 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:2799" / 4112 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2815" / 4113 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:2820" / 4114 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:2821" / 4115 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2830" / 4116 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:2840" / 4117 N11
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:2920" / 4118 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:2961" / 4119 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2977" / 4120 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:2982" / 4121 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:2983" / 4122 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:2992" / 4123 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:3002" / 4124 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:3244" / 4125 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3267" / 4126 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:3285" / 4127 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3301" / 4128 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:3306" / 4129 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:3307" / 4130 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3316" / 4131 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:3326" / 4132 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:3406" / 4133 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3447" / 4134 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3469" / 4135 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3478" / 4136 N11
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:3568" / 4137 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3586" / 4138 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:3589" / 4139 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:3593" / 4140 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:3597" / 4141 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:3605" / 4142 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:3609" / 4143 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3613" / 4144 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:3622" / 4145 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:3623" / 4146 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:3625" / 4147 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:3626" / 4148 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3631" / 4149 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3633" / 4150 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:3642" / 4151 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:3650" / 4152 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:3656" / 4153 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:3659" / 4154 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:3664" / 4155 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:3674" / 4156 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:3686" / 4157 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:3692" / 4158 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:3702" / 4159 N11
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:3892" / 4160 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3915" / 4161 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:3933" / 4162 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3949" / 4163 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:3954" / 4164 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:3955" / 4165 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:3964" / 4166 N11
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:4054" / 4167 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4095" / 4168 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4111" / 4169 N11
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4378" / 4170 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4419" / 4171 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4435" / 4172 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4441" / 4173 N11
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4563" / 4174 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:4581" / 4175 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4602" / 4176 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:4612" / 4177 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:4622" / 4178 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:4702" / 4179 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4743" / 4180 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4759" / 4181 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4765" / 4182 N11
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4864" / 4183 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4905" / 4184 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:4921" / 4185 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4927" / 4186 N11
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5026" / 4187 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5098" / 4188 N11
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:5188" / 4189 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5229" / 4190 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5245" / 4191 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5251" / 4192 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5350" / 4193 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5359" / 4194 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:5391" / 4195 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5407" / 4196 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5412" / 4197 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:5419" / 4198 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:5422" / 4199 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:5425" / 4200 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5432" / 4201 N11
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:5674" / 4202 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5715" / 4203 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5731" / 4204 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5737" / 4205 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5746" / 4206 N11
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:5836" / 4207 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5859" / 4208 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:5877" / 4209 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5893" / 4210 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5898" / 4211 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:5899" / 4212 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5908" / 4213 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:5918" / 4214 N11
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:5998" / 4215 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6039" / 4216 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6147" / 4217 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6160" / 4218 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6201" / 4219 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6223" / 4220 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6242" / 4221 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:6322" / 4222 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6363" / 4223 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6379" / 4224 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:6385" / 4225 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6481" / 4226 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:6483" / 4227 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:6485" / 4228 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:6486" / 4229 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:6487" / 4230 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:6488" / 4231 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:6489" / 4232 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:6490" / 4233 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:6492" / 4234 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:6493" / 4235 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:6495" / 4236 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:6501" / 4237 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:6502" / 4238 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:6507" / 4239 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:6509" / 4240 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:6510" / 4241 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:6512" / 4242 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:6513" / 4243 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:6526" / 4244 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:6527" / 4245 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:6529" / 4246 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:6531" / 4247 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:6532" / 4248 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:6533" / 4249 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:6534" / 4250 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:6535" / 4251 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:6536" / 4252 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:6537" / 4253 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:6538" / 4254 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:6539" / 4255 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:6540" / 4256 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:6541" / 4257 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:6542" / 4258 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:6543" / 4259 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:6545" / 4260 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:6546" / 4261 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:6547" / 4262 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
end
contingency "P6:6548" / 4263 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:6549" / 4264 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:6551" / 4265 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:6552" / 4266 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:6553" / 4267 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:6554" / 4268 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:6556" / 4269 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:6557" / 4270 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:6558" / 4271 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:6560" / 4272 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:6561" / 4273 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:6562" / 4274 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:6564" / 4275 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:6567" / 4276 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:6568" / 4277 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:6570" / 4278 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:6571" / 4279 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:6573" / 4280 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:6574" / 4281 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:6575" / 4282 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:6576" / 4283 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:6577" / 4284 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:6578" / 4285 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:6579" / 4286 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:6580" / 4287 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:6581" / 4288 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:6582" / 4289 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:6583" / 4290 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:6584" / 4291 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:6585" / 4292 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:6586" / 4293 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:6587" / 4294 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:6588" / 4295 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:6590" / 4296 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:6591" / 4297 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:6592" / 4298 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:6593" / 4299 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:6594" / 4300 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:6595" / 4301 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:6596" / 4302 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:6597" / 4303 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:6598" / 4304 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:6600" / 4305 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:6601" / 4306 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:6602" / 4307 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:6603" / 4308 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:6604" / 4309 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:6605" / 4310 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:6606" / 4311 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:6607" / 4312 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:6608" / 4313 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:6609" / 4314 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:6610" / 4315 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:6611" / 4316 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:6612" / 4317 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:6613" / 4318 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:6614" / 4319 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:6615" / 4320 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:6616" / 4321 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:6617" / 4322 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:6619" / 4323 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:6620" / 4324 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:6621" / 4325 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:6622" / 4326 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:6623" / 4327 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:6624" / 4328 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:6625" / 4329 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:6626" / 4330 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:6627" / 4331 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:6628" / 4332 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:6629" / 4333 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:6630" / 4334 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:6631" / 4335 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:6632" / 4336 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:6634" / 4337 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:6635" / 4338 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:6636" / 4339 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:6637" / 4340 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:6638" / 4341 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:6639" / 4342 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6640" / 4343 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:6641" / 4344 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:6642" / 4345 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:6646" / 4346 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6709" / 4347 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6795" / 4348 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6808" / 4349 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6852" / 4350 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:6865" / 4351 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:6870" / 4352 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:6871" / 4353 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6880" / 4354 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:6890" / 4355 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:6970" / 4356 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:6979" / 4357 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:7021" / 4358 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:7022" / 4359 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:7024" / 4360 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:7028" / 4361 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7032" / 4362 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:7035" / 4363 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:7039" / 4364 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:7040" / 4365 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:7050" / 4366 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:7104" / 4367 N11
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:7132" / 4368 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:7155" / 4369 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:7189" / 4370 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:7194" / 4371 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:7195" / 4372 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:7214" / 4373 N11
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:7456" / 4374 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:7513" / 4375 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:7519" / 4376 N11
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:7618" / 4377 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:7675" / 4378 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:7681" / 4379 N11
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:7780" / 4380 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:7837" / 4381 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:7843" / 4382 N11
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:7942" / 4383 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:7999" / 4384 N11
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8104" / 4385 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8113" / 4386 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:8161" / 4387 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8167" / 4388 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8176" / 4389 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:8186" / 4390 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:8266" / 4391 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8320" / 4392 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:8323" / 4393 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8328" / 4394 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:8329" / 4395 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8331" / 4396 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:8338" / 4397 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:8348" / 4398 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:8428" / 4399 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8500" / 4400 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:8510" / 4401 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:8590" / 4402 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8599" / 4403 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:8613" / 4404 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:8647" / 4405 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8653" / 4406 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8659" / 4407 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:8670" / 4408 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:8672" / 4409 N11
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:8752" / 4410 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8775" / 4411 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:8809" / 4412 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8815" / 4413 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8824" / 4414 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:8834" / 4415 N11
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:8914" / 4416 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8971" / 4417 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:8977" / 4418 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:8996" / 4419 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:9080" / 4420 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:9081" / 4421 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:9082" / 4422 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:9084" / 4423 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:9085" / 4424 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:9087" / 4425 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:9094" / 4426 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:9099" / 4427 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:9101" / 4428 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:9102" / 4429 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:9104" / 4430 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:9134" / 4431 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9135" / 4432 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:9138" / 4433 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:9139" / 4434 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:9141" / 4435 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:9143" / 4436 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:9144" / 4437 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:9145" / 4438 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:9146" / 4439 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9148" / 4440 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:9149" / 4441 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:9150" / 4442 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:9152" / 4443 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:9153" / 4444 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:9154" / 4445 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:9156" / 4446 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:9158" / 4447 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:9162" / 4448 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:9163" / 4449 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:9165" / 4450 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:9166" / 4451 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:9167" / 4452 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:9168" / 4453 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:9169" / 4454 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:9170" / 4455 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:9171" / 4456 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:9172" / 4457 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:9173" / 4458 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:9175" / 4459 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:9176" / 4460 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:9178" / 4461 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:9179" / 4462 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:9180" / 4463 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:9182" / 4464 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:9183" / 4465 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:9184" / 4466 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:9185" / 4467 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:9186" / 4468 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:9187" / 4469 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:9188" / 4470 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:9189" / 4471 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:9190" / 4472 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:9192" / 4473 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:9193" / 4474 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:9194" / 4475 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:9195" / 4476 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:9197" / 4477 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:9198" / 4478 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:9199" / 4479 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:9200" / 4480 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:9201" / 4481 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:9202" / 4482 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:9203" / 4483 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:9204" / 4484 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:9206" / 4485 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:9207" / 4486 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:9208" / 4487 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:9209" / 4488 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:9210" / 4489 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:9214" / 4490 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:9215" / 4491 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:9216" / 4492 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:9218" / 4493 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:9219" / 4494 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:9220" / 4495 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:9222" / 4496 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:9223" / 4497 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:9224" / 4498 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:9226" / 4499 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:9227" / 4500 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:9228" / 4501 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:9229" / 4502 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:9231" / 4503 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9232" / 4504 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:9233" / 4505 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:9234" / 4506 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:9238" / 4507 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9261" / 4508 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:9320" / 4509 N11
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:9400" / 4510 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9463" / 4511 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:9482" / 4512 N11
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:9563" / 4513 N11
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:9787" / 4514 N11
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:9886" / 4515 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9903" / 4516 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:9904" / 4517 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:9911" / 4518 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:9915" / 4519 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:9955" / 4520 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:9956" / 4521 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9961" / 4522 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9963" / 4523 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:9968" / 4524 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:9974" / 4525 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:9975" / 4526 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:9985" / 4527 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:9986" / 4528 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:9992" / 4529 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10008" / 4530 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:10020" / 4531 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:10046" / 4532 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:10050" / 4533 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:10051" / 4534 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:10052" / 4535 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:10056" / 4536 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:10057" / 4537 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:10059" / 4538 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:10060" / 4539 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:10062" / 4540 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:10063" / 4541 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:10064" / 4542 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:10066" / 4543 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:10067" / 4544 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:10069" / 4545 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:10070" / 4546 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:10071" / 4547 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:10073" / 4548 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:10076" / 4549 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:10078" / 4550 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:10079" / 4551 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:10081" / 4552 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:10084" / 4553 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:10085" / 4554 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:10087" / 4555 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:10088" / 4556 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:10089" / 4557 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10090" / 4558 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:10091" / 4559 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:10093" / 4560 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:10095" / 4561 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:10096" / 4562 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:10097" / 4563 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:10099" / 4564 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:10100" / 4565 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:10102" / 4566 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:10103" / 4567 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:10104" / 4568 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:10105" / 4569 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10107" / 4570 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:10109" / 4571 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:10111" / 4572 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10112" / 4573 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:10113" / 4574 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:10115" / 4575 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:10117" / 4576 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:10118" / 4577 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10121" / 4578 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:10122" / 4579 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:10124" / 4580 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:10125" / 4581 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10128" / 4582 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10130" / 4583 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:10134" / 4584 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:10135" / 4585 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:10137" / 4586 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:10138" / 4587 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:10140" / 4588 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:10141" / 4589 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:10142" / 4590 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:10143" / 4591 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:10146" / 4592 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:10147" / 4593 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:10148" / 4594 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:10149" / 4595 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:10150" / 4596 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:10151" / 4597 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:10152" / 4598 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:10154" / 4599 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:10155" / 4600 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:10156" / 4601 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:10157" / 4602 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:10158" / 4603 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:10160" / 4604 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:10161" / 4605 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:10162" / 4606 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:10163" / 4607 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10164" / 4608 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:10165" / 4609 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:10166" / 4610 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:10167" / 4611 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:10169" / 4612 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:10171" / 4613 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:10173" / 4614 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10174" / 4615 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10175" / 4616 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:10176" / 4617 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:10177" / 4618 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:10178" / 4619 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:10179" / 4620 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:10180" / 4621 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:10184" / 4622 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:10185" / 4623 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:10186" / 4624 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:10188" / 4625 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:10190" / 4626 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:10191" / 4627 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:10192" / 4628 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:10193" / 4629 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:10194" / 4630 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:10195" / 4631 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:10196" / 4632 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:10198" / 4633 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:10199" / 4634 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:10200" / 4635 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:10203" / 4636 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10204" / 4637 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:10205" / 4638 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:10206" / 4639 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:10210" / 4640 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:10251" / 4641 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10273" / 4642 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10359" / 4643 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10372" / 4644 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:10381" / 4645 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:10395" / 4646 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:10413" / 4647 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10416" / 4648 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:10424" / 4649 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:10429" / 4650 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:10435" / 4651 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10441" / 4652 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:10452" / 4653 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10454" / 4654 N11
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:10696" / 4655 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:10737" / 4656 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10753" / 4657 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:10759" / 4658 N11
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10858" / 4659 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:10899" / 4660 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10915" / 4661 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:10930" / 4662 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:10940" / 4663 N11
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:11020" / 4664 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11054" / 4665 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:11061" / 4666 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11064" / 4667 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:11074" / 4668 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:11077" / 4669 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:11082" / 4670 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:11083" / 4671 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11085" / 4672 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:11102" / 4673 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:11182" / 4674 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11223" / 4675 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11226" / 4676 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:11239" / 4677 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:11244" / 4678 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:11245" / 4679 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11254" / 4680 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11264" / 4681 N11
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:11506" / 4682 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11516" / 4683 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:11517" / 4684 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:11523" / 4685 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:11524" / 4686 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:11525" / 4687 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:11527" / 4688 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:11528" / 4689 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:11531" / 4690 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:11535" / 4691 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:11538" / 4692 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:11540" / 4693 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:11542" / 4694 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:11543" / 4695 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:11547" / 4696 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11549" / 4697 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:11557" / 4698 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:11558" / 4699 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:11559" / 4700 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:11561" / 4701 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:11563" / 4702 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:11574" / 4703 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:11576" / 4704 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11579" / 4705 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:11581" / 4706 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11582" / 4707 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:11584" / 4708 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:11588" / 4709 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:11590" / 4710 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:11593" / 4711 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:11594" / 4712 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:11595" / 4713 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:11597" / 4714 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:11599" / 4715 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:11600" / 4716 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:11601" / 4717 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:11603" / 4718 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:11605" / 4719 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:11606" / 4720 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:11608" / 4721 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:11612" / 4722 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:11624" / 4723 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:11626" / 4724 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:11628" / 4725 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:11629" / 4726 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:11640" / 4727 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:11644" / 4728 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:11645" / 4729 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:11647" / 4730 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:11648" / 4731 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:11650" / 4732 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:11651" / 4733 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:11653" / 4734 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:11658" / 4735 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:11668" / 4736 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11731" / 4737 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11740" / 4738 N11
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11830" / 4739 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:11853" / 4740 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:11893" / 4741 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11912" / 4742 N11
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:12064" / 4743 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:12074" / 4744 N11
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:12154" / 4745 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12217" / 4746 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12226" / 4747 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:12236" / 4748 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:12316" / 4749 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12379" / 4750 N11
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12478" / 4751 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12550" / 4752 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:12560" / 4753 N11
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:12802" / 4754 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12843" / 4755 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12846" / 4756 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:12856" / 4757 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:12859" / 4758 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:12865" / 4759 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:12867" / 4760 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:12884" / 4761 N11
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13124" / 4762 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:13135" / 4763 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:13137" / 4764 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13143" / 4765 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:13144" / 4766 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:13145" / 4767 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:13147" / 4768 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:13149" / 4769 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:13155" / 4770 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:13160" / 4771 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:13163" / 4772 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:13165" / 4773 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:13169" / 4774 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:13171" / 4775 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:13177" / 4776 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:13178" / 4777 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:13179" / 4778 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13180" / 4779 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:13181" / 4780 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:13182" / 4781 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:13183" / 4782 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:13184" / 4783 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13185" / 4784 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:13188" / 4785 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:13189" / 4786 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
end
contingency "P6:13191" / 4787 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:13194" / 4788 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13195" / 4789 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:13196" / 4790 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13198" / 4791 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13200" / 4792 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:13201" / 4793 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13202" / 4794 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13204" / 4795 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13206" / 4796 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:13209" / 4797 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13210" / 4798 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13213" / 4799 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13215" / 4800 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:13217" / 4801 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:13220" / 4802 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:13221" / 4803 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13222" / 4804 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:13223" / 4805 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13225" / 4806 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13226" / 4807 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13232" / 4808 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13244" / 4809 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:13246" / 4810 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:13248" / 4811 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13249" / 4812 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:13250" / 4813 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:13260" / 4814 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:13264" / 4815 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:13268" / 4816 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:13270" / 4817 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:13271" / 4818 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:13288" / 4819 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13329" / 4820 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13370" / 4821 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13385" / 4822 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13450" / 4823 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13491" / 4824 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13522" / 4825 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13532" / 4826 N11
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13774" / 4827 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13837" / 4828 N11
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13936" / 4829 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13999" / 4830 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14008" / 4831 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:14018" / 4832 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:14058" / 4833 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:14121" / 4834 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:14170" / 4835 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:14195" / 4836 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:14260" / 4837 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:14323" / 4838 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14332" / 4839 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:14342" / 4840 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:14422" / 4841 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:14485" / 4842 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14519" / 4843 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:14584" / 4844 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:14607" / 4845 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:14656" / 4846 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:14666" / 4847 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:14746" / 4848 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:14809" / 4849 N11
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14908" / 4850 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:14971" / 4851 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:14980" / 4852 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:15070" / 4853 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:15133" / 4854 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15142" / 4855 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:15152" / 4856 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:15232" / 4857 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:15295" / 4858 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15304" / 4859 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:15314" / 4860 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:15394" / 4861 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:15417" / 4862 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:15476" / 4863 N11
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:15556" / 4864 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:15628" / 4865 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:15638" / 4866 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:15639" / 4867 N11
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:15718" / 4868 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:15781" / 4869 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15867" / 4870 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:15880" / 4871 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:15943" / 4872 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15952" / 4873 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:15962" / 4874 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:16042" / 4875 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:16105" / 4876 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:16114" / 4877 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:16124" / 4878 N11
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:16204" / 4879 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:16267" / 4880 N11
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:16366" / 4881 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:16429" / 4882 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:16438" / 4883 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:16528" / 4884 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:16591" / 4885 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:16690" / 4886 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:16753" / 4887 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:17014" / 4888 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:17037" / 4889 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:17077" / 4890 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:17086" / 4891 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:17096" / 4892 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:17176" / 4893 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:17239" / 4894 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:17338" / 4895 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:17401" / 4896 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:17500" / 4897 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:17563" / 4898 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:17662" / 4899 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:17725" / 4900 N11
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:17824" / 4901 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:17986" / 4902 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:18049" / 4903 N11
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18148" / 4904 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:18211" / 4905 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18310" / 4906 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:18373" / 4907 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18535" / 4908 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18634" / 4909 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:18697" / 4910 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18796" / 4911 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:18859" / 4912 N11
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:18958" / 4913 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:18981" / 4914 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:19021" / 4915 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:19030" / 4916 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:19040" / 4917 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:19080" / 4918 N11
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:19120" / 4919 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:19183" / 4920 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:19282" / 4921 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:19354" / 4922 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:19364" / 4923 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:19444" / 4924 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:19507" / 4925 N11
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:19606" / 4926 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:19678" / 4927 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:19688" / 4928 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:19768" / 4929 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:19831" / 4930 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:19840" / 4931 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:19850" / 4932 N11
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:19930" / 4933 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:19953" / 4934 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:20012" / 4935 N11
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:20092" / 4936 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:20155" / 4937 N11
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:20254" / 4938 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:20317" / 4939 N11
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:20416" / 4940 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:20479" / 4941 N11
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:20578" / 4942 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:20641" / 4943 N11
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:20740" / 4944 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:20803" / 4945 N11
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:20902" / 4946 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:20965" / 4947 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:21064" / 4948 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:21127" / 4949 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:21226" / 4950 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:21289" / 4951 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:21388" / 4952 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:21573" / 4953 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:21622" / 4954 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:21632" / 4955 N11
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:21712" / 4956 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:21861" / 4957 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:21874" / 4958 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:21937" / 4959 N11
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:22036" / 4960 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:22099" / 4961 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:22185" / 4962 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:22198" / 4963 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:22261" / 4964 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:22270" / 4965 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:22280" / 4966 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:22360" / 4967 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:22432" / 4968 N11
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:22522" / 4969 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:22585" / 4970 N11
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:22684" / 4971 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:22756" / 4972 N11
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:22846" / 4973 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:22909" / 4974 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:22918" / 4975 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:22928" / 4976 N11
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:23008" / 4977 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:23071" / 4978 N11
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23170" / 4979 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:23233" / 4980 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23242" / 4981 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:23252" / 4982 N11
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:23332" / 4983 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:23395" / 4984 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23404" / 4985 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:23414" / 4986 N11
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:23494" / 4987 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:23535" / 4988 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23551" / 4989 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:23557" / 4990 N11
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23656" / 4991 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:23719" / 4992 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23728" / 4993 N11
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:23818" / 4994 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:23881" / 4995 N11
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:23977" / 4996 N11
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23979" / 4997 N11
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23981" / 4998 N11
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23982" / 4999 N11
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23983" / 5000 N11
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23987" / 5001 N11
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24018" / 5002 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24022" / 5003 N11
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24044" / 5004 N11
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24078" / 5005 N11
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24115" / 5006 N11
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24117" / 5007 N11
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24142" / 5008 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:24183" / 5009 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:24199" / 5010 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:24205" / 5011 N11
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:24304" / 5012 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24345" / 5013 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24361" / 5014 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24367" / 5015 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24466" / 5016 N11
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24507" / 5017 N11
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24523" / 5018 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24529" / 5019 N11
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24538" / 5020 N11
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24628" / 5021 N11
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:24952" / 5022 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:25015" / 5023 N11
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:25114" / 5024 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:25177" / 5025 N11
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:25276" / 5026 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:25339" / 5027 N11
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:25438" / 5028 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:25501" / 5029 N11
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "OPT_1_1_OPT_1_2" / 5030 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_1_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5031 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5032 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5033 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5034 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5035 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5036 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342718 5COOPER2 161 342727 5DENNY 161 1" / 5037 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5038 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1" / 5039 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5040 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5041 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5042 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5043 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5044 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_1_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5045 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5DENNY 161.0' to bus '5WAYNE CO 161.0' ckt 1 / 342727 5DENNY /! Branch not found
end
contingency "OPT_1_2_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5046 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5047 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5048 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5049 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5050 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5051 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342718 5COOPER2 161 342727 5DENNY 161 1" / 5052 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5053 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1" / 5054 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5055 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5056 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5057 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5058 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5059 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_1_2_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5060 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "OPT_2_1_OPT_2_2" / 5061 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_OPT_2_3" / 5062 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_OPT_2_4" / 5063 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_1_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5064 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5065 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5066 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5067 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5068 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5069 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342718 5COOPER2 161 342727 5DENNY 161 1" / 5070 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5071 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5072 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5073 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5074 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5075 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5076 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_1_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5077 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MCCREARY CO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_OPT_2_3" / 5078 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_OPT_2_4" / 5079 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_2_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5080 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5081 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5082 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5083 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5084 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5085 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342718 5COOPER2 161 342727 5DENNY 161 1" / 5086 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5087 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5088 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5089 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5090 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5091 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5092 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_2_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5093 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_OPT_2_4" / 5094 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_3_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5095 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5096 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5097 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5098 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5099 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5100 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342718 5COOPER2 161 342727 5DENNY 161 1" / 5101 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5102 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5103 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5104 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5105 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5106 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5107 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_3_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5108 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5NEW TIE 161.0' to bus '5MONTICELLO 161.0' ckt 1 / 342614 5NEW TIE /! FromBus not found
end
contingency "OPT_2_4_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5109 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5110 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5111 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5112 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5113 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5114 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342718 5COOPER2 161 342727 5DENNY 161 1" / 5115 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5116 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5117 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5118 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5119 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5120 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5121 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_2_4_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5122 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_OPT_3_2" / 5123 N11
// !!! Failed to map 2 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5124 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5125 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5126 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5127 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5128 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5129 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342718 5COOPER2 161 342727 5DENNY 161 1" / 5130 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5131 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1" / 5132 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5133 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5134 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5135 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5136 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5137 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_1_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5138 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '2MONTICELLO 69.00' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1" / 5139 N11
open branch from bus '2GAP OF RG T 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341503 2GAP OF RG T 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1" / 5140 N11
open branch from bus '2HOMESTEAD S 69.00' to bus '2MONTICELLO 69.00' ckt 1 / 341641 2HOMESTEAD S 69.0 341887 2MONTICELLO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1" / 5141 N11
open branch from bus '2MONTICELLO 69.00' to bus '2SLAT 69.00' ckt 1 / 341887 2MONTICELLO 69.0 342268 2SLAT 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1" / 5142 N11
open branch from bus '2SLAT 69.00' to bus '2WAYNE CO 69.00' ckt 1 / 342268 2SLAT 69.0 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1" / 5143 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA J NO 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342532 2ZULA J NO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1" / 5144 N11
open branch from bus '2WAYNE CO 69.00' to bus '2ZULA T 69.00' ckt 1 / 342478 2WAYNE CO 69.0 342535 2ZULA T 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342718 5COOPER2 161 342727 5DENNY 161 1" / 5145 N11
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1" / 5146 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1" / 5147 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1" / 5148 N11
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1" / 5149 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1" / 5150 N11
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342727 5DENNY 161 341392 2DENNY 69.0 1" / 5151 N11
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1" / 5152 N11
open branch from bus '5MCCREARY CO 161.0' to bus '2MCCREARY CO 69.00' ckt 1 / 342778 5MCCREARY CO 161 341845 2MCCREARY CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "OPT_3_2_342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1" / 5153 N11
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
// !!! Failed to map 1 events reported below
// open branch from bus '5MONTICELLO 161.0' to bus '5DENNY 161.0' ckt 1 / 342657 5MONTICE /! FromBus not found
end
contingency "342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1_342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 2" / 5154 N11
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
// !!! Failed to map 1 events reported below
// open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 2 / 342823 5WAYNE C /! Branch not found
end
contingency "Option_4_N11_1" / 5155 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '2A' FROM BUS 342900 /! Bus not found
// OPEN BRANCH FROM BUS 342715 TO BUS 342799 CKT 1 /! FromBus not found
end
contingency "Option_4_N11_2" / 5156 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '2A' FROM BUS 342900 /! Bus not found
// OPEN BRANCH FROM BUS 342715 TO BUS 342718 CKT 1 /! FromBus not found
end
contingency "Option_4_N11_3" / 5157 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '2A' FROM BUS 342900 /! Bus not found
// OPEN BRANCH FROM BUS 342715 TO BUS 341344 CKT 1 /! FromBus not found
end
contingency "Option_4_N11_4" / 5158 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '2A' FROM BUS 342900 /! Bus not found
// OPEN BRANCH FROM BUS 342715 TO BUS 342790 CKT 1 /! FromBus not found
end
contingency "Option_5_N11_1" / 5159 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '1' FROM BUS 342703 /! Bus not found
// OPEN BRANCH FROM BUS 342703 TO BUS 342760 CKT 1 /! FromBus not found
end
contingency "Option_5_N11_2" / 5160 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '1' FROM BUS 342703 /! Bus not found
// OPEN BRANCH FROM BUS 342703 TO BUS 342769 CKT 1 /! FromBus not found
end
contingency "Option_5_N11_3" / 5161 N11
// !!! Failed to map 2 events reported below
// REMOVE MACHINE '1' FROM BUS 342703 /! Bus not found
// OPEN BRANCH FROM BUS 342703 TO BUS 341269 CKT 1 /! FromBus not found
end
contingency "P6:1" / 1 N11_Vdrop
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:216" / 2 N11_Vdrop
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:341" / 3 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:363" / 4 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:406" / 5 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:409" / 6 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:588" / 7 N11_Vdrop
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:792" / 8 N11_Vdrop
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:970" / 9 N11_Vdrop
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:1061" / 10 N11_Vdrop
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1149" / 11 N11_Vdrop
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:1348" / 12 N11_Vdrop
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:1537" / 13 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1736" / 14 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:1948" / 15 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:1967" / 16 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:1983" / 17 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2008" / 18 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2019" / 19 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2029" / 20 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2113" / 21 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:2505" / 22 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2759" / 23 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:2953" / 24 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:3141" / 25 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:3335" / 26 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:3562" / 27 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:3634" / 28 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3730" / 29 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3796" / 30 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:3886" / 31 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:4087" / 32 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:4265" / 33 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:4455" / 34 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:4627" / 35 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:4827" / 36 N11_Vdrop
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5064" / 37 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:5278" / 38 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:5421" / 39 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5497" / 40 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:5512" / 41 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5525" / 42 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:5673" / 43 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:5909" / 44 N11_Vdrop
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:6108" / 45 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:6348" / 46 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:6601" / 47 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:6857" / 48 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:7080" / 49 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:7311" / 50 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:7537" / 51 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7780" / 52 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:8065" / 53 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:8341" / 54 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8553" / 55 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:8820" / 56 N11_Vdrop
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:9076" / 57 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9336" / 58 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:9575" / 59 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9623" / 60 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:9831" / 61 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:10064" / 62 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:10238" / 63 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:10430" / 64 N11_Vdrop
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10557" / 65 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:10558" / 66 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:10602" / 67 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:10789" / 68 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:10989" / 69 N11_Vdrop
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:11171" / 70 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:11357" / 71 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11370" / 72 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:11378" / 73 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:11429" / 74 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11531" / 75 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:11756" / 76 N11_Vdrop
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:12001" / 77 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:12290" / 78 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:12597" / 79 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:12765" / 80 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:12944" / 81 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:12964" / 82 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12977" / 83 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13093" / 84 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13265" / 85 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:13451" / 86 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:13619" / 87 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:13682" / 88 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13683" / 89 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13766" / 90 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:13927" / 91 N11_Vdrop
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:14230" / 92 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:14546" / 93 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:14870" / 94 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:15193" / 95 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:16513" / 96 N11_Vdrop
open branch from bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3
end
contingency "P6:16676" / 97 N11_Vdrop
open branch from bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1
end
contingency "P6:18437" / 98 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:403" / 99 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3117" / 100 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3157" / 101 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3163" / 102 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3643" / 103 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5532" / 104 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5587" / 105 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6721" / 106 N11_Vdrop
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9151" / 107 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9799" / 108 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11095" / 109 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11905" / 110 N11_Vdrop
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11909" / 111 N11_Vdrop
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:11992" / 112 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:12012" / 113 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12015" / 114 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:12061" / 115 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:12072" / 116 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12073" / 117 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12088" / 118 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:12089" / 119 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:12092" / 120 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:12114" / 121 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:12116" / 122 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:12138" / 123 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:12141" / 124 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:12714" / 125 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:12877" / 126 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12984" / 127 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13039" / 128 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:23569" / 129 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:24055" / 130 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:348" / 131 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1497" / 132 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:1543" / 133 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2631" / 134 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2677" / 135 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2793" / 136 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2839" / 137 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3082" / 138 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:3142" / 139 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3153" / 140 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3790" / 141 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3801" / 142 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5061" / 143 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5107" / 144 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5529" / 145 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:5530" / 146 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:5553" / 147 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5575" / 148 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5578" / 149 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:5594" / 150 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:5600" / 151 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:5661" / 152 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:6565" / 153 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7379" / 154 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8164" / 155 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8175" / 156 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8326" / 157 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:8337" / 158 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9582" / 159 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9586" / 160 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9628" / 161 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:9631" / 162 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:9642" / 163 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:10083" / 164 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10129" / 165 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10569" / 166 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:10594" / 167 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10605" / 168 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:10615" / 169 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11080" / 170 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11091" / 171 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11364" / 172 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11368" / 173 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:11395" / 174 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:11396" / 175 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:11410" / 176 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11413" / 177 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:11424" / 178 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12862" / 179 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12873" / 180 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:12974" / 181 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:12981" / 182 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:12982" / 183 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:12996" / 184 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:13005" / 185 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13027" / 186 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13030" / 187 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13046" / 188 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13052" / 189 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:13113" / 190 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13161" / 191 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13207" / 192 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:14179" / 193 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:24015" / 194 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24061" / 195 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1022" / 196 N11_Vdrop
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:4100" / 197 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:7300" / 198 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:7301" / 199 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:7320" / 200 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:89" / 201 N11_Vdrop
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:251" / 202 N11_Vdrop
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:413" / 203 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:575" / 204 N11_Vdrop
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:737" / 205 N11_Vdrop
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:899" / 206 N11_Vdrop
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1223" / 207 N11_Vdrop
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1385" / 208 N11_Vdrop
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1547" / 209 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1709" / 210 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:1871" / 211 N11_Vdrop
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2033" / 212 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2195" / 213 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2357" / 214 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2519" / 215 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2681" / 216 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2843" / 217 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3005" / 218 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3167" / 219 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3329" / 220 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3491" / 221 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3653" / 222 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3815" / 223 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:3977" / 224 N11_Vdrop
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4139" / 225 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4301" / 226 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4463" / 227 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4787" / 228 N11_Vdrop
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:4949" / 229 N11_Vdrop
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5111" / 230 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5435" / 231 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5597" / 232 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5759" / 233 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:5921" / 234 N11_Vdrop
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6083" / 235 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6245" / 236 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6407" / 237 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6569" / 238 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6731" / 239 N11_Vdrop
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:6893" / 240 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7055" / 241 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7217" / 242 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7541" / 243 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7703" / 244 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7865" / 245 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8027" / 246 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8189" / 247 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8351" / 248 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8513" / 249 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8675" / 250 N11_Vdrop
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8837" / 251 N11_Vdrop
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:8999" / 252 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9161" / 253 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9485" / 254 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9647" / 255 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9809" / 256 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:9971" / 257 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10133" / 258 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10295" / 259 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10457" / 260 N11_Vdrop
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10619" / 261 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10781" / 262 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:10943" / 263 N11_Vdrop
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11105" / 264 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11591" / 265 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11753" / 266 N11_Vdrop
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11915" / 267 N11_Vdrop
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12239" / 268 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12401" / 269 N11_Vdrop
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12563" / 270 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12725" / 271 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12887" / 272 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13049" / 273 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13211" / 274 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13373" / 275 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13535" / 276 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13609" / 277 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:13611" / 278 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:13612" / 279 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:13613" / 280 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:13614" / 281 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:13615" / 282 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:13616" / 283 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:13617" / 284 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:13618" / 285 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:13620" / 286 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:13621" / 287 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:13623" / 288 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13625" / 289 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13627" / 290 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:13629" / 291 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:13630" / 292 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:13632" / 293 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13635" / 294 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:13636" / 295 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:13637" / 296 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:13638" / 297 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:13640" / 298 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:13675" / 299 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:13676" / 300 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:13677" / 301 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:13678" / 302 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:13679" / 303 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:13680" / 304 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13681" / 305 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:13684" / 306 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13691" / 307 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13692" / 308 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:13693" / 309 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13694" / 310 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13695" / 311 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13696" / 312 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13697" / 313 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:13698" / 314 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13699" / 315 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13701" / 316 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:13702" / 317 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:13703" / 318 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:13704" / 319 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13705" / 320 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:13706" / 321 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:13707" / 322 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13709" / 323 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:13710" / 324 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13711" / 325 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13712" / 326 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13713" / 327 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:13714" / 328 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:13715" / 329 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:13716" / 330 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:13717" / 331 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13718" / 332 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13719" / 333 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:13720" / 334 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13721" / 335 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:13722" / 336 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:13723" / 337 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:13724" / 338 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13725" / 339 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:13726" / 340 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:13728" / 341 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:13729" / 342 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:13730" / 343 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:13731" / 344 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:13732" / 345 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:13733" / 346 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:13734" / 347 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13735" / 348 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:13737" / 349 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13738" / 350 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13739" / 351 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:13740" / 352 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13741" / 353 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13742" / 354 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:13743" / 355 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13744" / 356 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:13745" / 357 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13747" / 358 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:13748" / 359 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:13749" / 360 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:13751" / 361 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:13752" / 362 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:13753" / 363 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:13754" / 364 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:13755" / 365 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:13756" / 366 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:13757" / 367 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:13758" / 368 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13760" / 369 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:13761" / 370 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13763" / 371 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:13764" / 372 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:13765" / 373 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:13768" / 374 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13769" / 375 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:23579" / 376 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:24065" / 377 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24389" / 378 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24551" / 379 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:1965" / 380 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:2609" / 381 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1652" / 382 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:4389" / 383 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:4136" / 384 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13152" / 385 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:4475" / 386 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:15584" / 387 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:503" / 388 N11_Vdrop
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1949" / 389 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:1945" / 390 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2ALCAN 69.00' to bus '2W BEREA 69.00' ckt 1 / 341008 2ALCAN 69.0 342430 2W BEREA 69.0 1
open branch from bus '2ALCAN 69.00' to bus '2PPG J 69.00' ckt 1 / 341008 2ALCAN 69.0 342106 2PPG J 69.0 1
open branch from bus '2BEREAKU T 69.00' to bus '2PPG J 69.00' ckt 1 / 341098 2BEREAKU T 69.0 342106 2PPG J 69.0 1
open branch from bus '2PPG 69.00' to bus '2PPG J 69.00' ckt 1 / 342103 2PPG 69.0 342106 2PPG J 69.0 1
open branch from bus '2HICKORY PL 69.00' to bus '2PPG 69.00' ckt 1 / 341611 2HICKORY PL 69.0 342103 2PPG 69.0 1
open branch from bus '2CROOKSVIL T 69.00' to bus '2HICKORY PL 69.00' ckt 1 / 341362 2CROOKSVIL T 69.0 341611 2HICKORY PL 69.0 1
open branch from bus '2CROOKSVIL 69.00' to bus '2CROOKSVIL T 69.00' ckt 1 / 341359 2CROOKSVIL 69.0 341362 2CROOKSVIL T 69.0 1
open branch from bus '2FAWKES 69.00' to bus '2DUNCAN LN T 69.00' ckt 1 / 324530 2FAWKES 69.0 341406 2DUNCAN LN T 69.0 1
end
contingency "P6:1974" / 391 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:4067" / 392 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4298" / 393 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13153" / 394 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:989" / 395 N11_Vdrop
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1955" / 396 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2GREEN CO 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 341563 2GREEN CO 69.0 1
open branch from bus '2GRENSBRG KU 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324554 2GRENSBRG KU 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELV EK 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324830 2CAMPBELV EK 69.0 1
open branch from bus '2GR RVR PLAZ 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324557 2GR RVR PLAZ 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2CAMPBELVIL1 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324829 2CAMPBELVIL1 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2MILE LAN EK 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 326970 2MILE LAN EK 69.0 1
open branch from bus '2MILE LAN TP 69.00' to bus '2TAYLOR CO 69.00' ckt 1 / 324641 2MILE LAN TP 69.0 324751 2TAYLOR CO 69.0 1
end
contingency "P6:665" / 397 N11_Vdrop
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1950" / 398 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:1995" / 399 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:2023" / 400 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:7469" / 401 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12005" / 402 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2039" / 403 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:14597" / 404 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2046" / 405 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
end
contingency "P6:15731" / 406 N11_Vdrop
open branch from bus '5TOMPKNSV TP 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361246 5W TOMPKINST 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2083" / 407 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
end
contingency "P6:21725" / 408 N11_Vdrop
open branch from bus '5TOMPKNSV PS 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 361117 5TOMPKNSV PS 161 361246 5W TOMPKINST 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1970" / 409 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:3419" / 410 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1990" / 411 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:2012" / 412 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:6659" / 413 N11_Vdrop
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10223" / 414 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1962" / 415 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:2123" / 416 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:827" / 417 N11_Vdrop
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1951" / 418 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2MCCREARY CO 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 341845 2MCCREARY CO 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2REVELO KU 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342136 2REVELO KU 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2PINE KNOT 69.00' to bus '2REVELO KU T 69.00' ckt 1 / 342076 2PINE KNOT 69.0 342139 2REVELO KU T 69.0 1
open branch from bus '2E PINE KNOT 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341416 2E PINE KNOT 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2PINE KNOT 69.00' ckt 1 / 341686 2JELLICO C T 69.0 342076 2PINE KNOT 69.0 1
open branch from bus '2JELLICO C T 69.00' to bus '2JELLICO CRK 69.00' ckt 1 / 341686 2JELLICO C T 69.0 341689 2JELLICO CRK 69.0 1
open branch from bus '2GOLDBUG 69.00' to bus '2JELLICO C T 69.00' ckt 1 / 341539 2GOLDBUG 69.0 341686 2JELLICO C T 69.0 1
open branch from bus '2WOFFORD 69.00' to bus '2GOLDBUG 69.00' ckt 1 / 324784 2WOFFORD 69.0 341539 2GOLDBUG 69.0 1
end
contingency "P6:1996" / 419 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:2106" / 420 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:7631" / 421 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:25451" / 422 N11_Vdrop
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:179" / 423 N11_Vdrop
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1947" / 424 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2RUSSEL CO 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 342178 2RUSSEL CO 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2SEWELLTON 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 342232 2SEWELLTON 69.0 1
open branch from bus '2UNION UNDWR 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324787 2UNION UNDWR 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SMRST 615KU 69.00' to bus '2WAITSBORO 69.00' ckt 1 / 324969 2SMRST 615KU 69.0 324990 2WAITSBORO 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SMRST 615KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 324969 2SMRST 615KU 69.0 1
open branch from bus '2SOMERSET SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324737 2SOMERSET SO 69.0 342287 2SOMERSET KU 69.0 1
end
contingency "P6:2059" / 425 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:17837" / 426 N11_Vdrop
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1475" / 427 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1958" / 428 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:1980" / 429 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:2049" / 430 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:5039" / 431 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16217" / 432 N11_Vdrop
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1986" / 433 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:2025" / 434 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:2077" / 435 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:2085" / 436 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
end
contingency "P6:2101" / 437 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:2103" / 438 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:2176" / 439 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:6011" / 440 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10548" / 441 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:12329" / 442 N11_Vdrop
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20753" / 443 N11_Vdrop
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22049" / 444 N11_Vdrop
open branch from bus '5BURKSVLTP 161.0' to bus '5BURKESVL KY 161.0' ckt 1 / 361666 5BURKSVLTP 161 361667 5BURKESVL KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24641" / 445 N11_Vdrop
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24965" / 446 N11_Vdrop
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1953" / 447 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:1963" / 448 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
end
contingency "P6:2285" / 449 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5DENNY 161.0' ckt 1 / 342718 5COOPER2 161 342727 5DENNY 161 1
open branch from bus '5DENNY 161.0' to bus '2DENNY 69.00' ckt 1 / 342727 5DENNY 161 341392 2DENNY 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2021" / 450 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:11681" / 451 N11_Vdrop
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1151" / 452 N11_Vdrop
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1956" / 453 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:2052" / 454 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:2094" / 455 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:16703" / 456 N11_Vdrop
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23507" / 457 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1952" / 458 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:1954" / 459 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:1997" / 460 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:2062" / 461 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:2064" / 462 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:2084" / 463 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:2102" / 464 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:7793" / 465 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18323" / 466 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18647" / 467 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21887" / 468 N11_Vdrop
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24803" / 469 N11_Vdrop
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1961" / 470 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2004" / 471 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:2006" / 472 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:2057" / 473 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:2058" / 474 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:2061" / 475 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:2063" / 476 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2065" / 477 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:2069" / 478 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:2075" / 479 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:2078" / 480 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:2079" / 481 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:8927" / 482 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9251" / 483 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17513" / 484 N11_Vdrop
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17675" / 485 N11_Vdrop
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18161" / 486 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18485" / 487 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18809" / 488 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19457" / 489 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20429" / 490 N11_Vdrop
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20915" / 491 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21077" / 492 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2040" / 493 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:2055" / 494 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:2056" / 495 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:2060" / 496 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:2067" / 497 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:2074" / 498 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2080" / 499 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:2081" / 500 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:2091" / 501 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:14759" / 502 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17189" / 503 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17351" / 504 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17999" / 505 N11_Vdrop
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19133" / 506 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20267" / 507 N11_Vdrop
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21239" / 508 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21401" / 509 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23021" / 510 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1969" / 511 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:1978" / 512 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:1987" / 513 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:2042" / 514 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
end
contingency "P6:2051" / 515 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:2071" / 516 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:2073" / 517 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2076" / 518 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:2096" / 519 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:2104" / 520 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:2105" / 521 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:3257" / 522 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:4715" / 523 N11_Vdrop
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6173" / 524 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15083" / 525 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361618 5KELSEY RD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16541" / 526 N11_Vdrop
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19781" / 527 N11_Vdrop
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20105" / 528 N11_Vdrop
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:20591" / 529 N11_Vdrop
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23831" / 530 N11_Vdrop
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:25127" / 531 N11_Vdrop
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:25289" / 532 N11_Vdrop
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1988" / 533 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:2026" / 534 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:2034" / 535 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:2088" / 536 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:6335" / 537 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12491" / 538 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13787" / 539 N11_Vdrop
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22535" / 540 N11_Vdrop
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2047" / 541 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:2087" / 542 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:2098" / 543 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:15893" / 544 N11_Vdrop
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22373" / 545 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24155" / 546 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1998" / 547 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:2066" / 548 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:2099" / 549 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:7955" / 550 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:18971" / 551 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24317" / 552 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:2031" / 553 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:2035" / 554 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13301" / 555 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13949" / 556 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1984" / 557 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:2024" / 558 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:2038" / 559 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:2050" / 560 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:2095" / 561 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:2134" / 562 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3744" / 563 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:5687" / 564 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:12167" / 565 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14435" / 566 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16379" / 567 N11_Vdrop
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23669" / 568 N11_Vdrop
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2001" / 569 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:2016" / 570 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:2032" / 571 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:2089" / 572 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:2093" / 573 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:2100" / 574 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:8441" / 575 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10871" / 576 N11_Vdrop
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:13463" / 577 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22697" / 578 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23345" / 579 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:24479" / 580 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:2037" / 581 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:3472" / 582 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10556" / 583 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:14273" / 584 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2015" / 585 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:2086" / 586 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:10709" / 587 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:22211" / 588 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2003" / 589 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:8765" / 590 N11_Vdrop
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1971" / 591 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:2043" / 592 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:3581" / 593 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:15245" / 594 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1979" / 595 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:1991" / 596 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:2018" / 597 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:4877" / 598 N11_Vdrop
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:6821" / 599 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:11195" / 600 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1973" / 601 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:2092" / 602 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:3905" / 603 N11_Vdrop
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:23183" / 604 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2048" / 605 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:2933" / 606 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:16055" / 607 N11_Vdrop
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2090" / 608 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22859" / 609 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2068" / 610 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:19295" / 611 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1976" / 612 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:2036" / 613 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:4391" / 614 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:14111" / 615 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2070" / 616 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:19619" / 617 N11_Vdrop
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2044" / 618 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:2072" / 619 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:15407" / 620 N11_Vdrop
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:19943" / 621 N11_Vdrop
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1999" / 622 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:8117" / 623 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1799" / 624 N11_Vdrop
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1960" / 625 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
end
contingency "P6:1981" / 626 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:5201" / 627 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2009" / 628 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:9737" / 629 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2053" / 630 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:16865" / 631 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3430" / 632 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3752" / 633 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:2002" / 634 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:2013" / 635 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:2082" / 636 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:8603" / 637 N11_Vdrop
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:10385" / 638 N11_Vdrop
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:21563" / 639 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1966" / 640 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:2771" / 641 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1994" / 642 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:7307" / 643 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2028" / 644 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12815" / 645 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2017" / 646 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:11033" / 647 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2000" / 648 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:8279" / 649 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1985" / 650 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:5849" / 651 N11_Vdrop
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2054" / 652 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:17027" / 653 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:17" / 654 N11_Vdrop
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1637" / 655 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1946" / 656 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:1959" / 657 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:2022" / 658 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:11843" / 659 N11_Vdrop
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2030" / 660 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13139" / 661 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1977" / 662 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:4553" / 663 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1989" / 664 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:6497" / 665 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2041" / 666 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:14921" / 667 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1993" / 668 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:7145" / 669 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2614" / 670 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:2775" / 671 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:2045" / 672 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:15569" / 673 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2007" / 674 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:2010" / 675 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:9413" / 676 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:9899" / 677 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1982" / 678 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:5363" / 679 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2011" / 680 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10061" / 681 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2020" / 682 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11519" / 683 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2005" / 684 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:9089" / 685 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1992" / 686 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:6983" / 687 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2014" / 688 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10547" / 689 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1972" / 690 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3743" / 691 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1964" / 692 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:2447" / 693 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1313" / 694 N11_Vdrop
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:1957" / 695 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:1975" / 696 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:4229" / 697 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2027" / 698 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12653" / 699 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:2097" / 700 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23993" / 701 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1968" / 702 N11_Vdrop
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3095" / 703 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5RUSSEL CO 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342793 5RUSSEL CO 161 342796 5RUSSEL CO J 161 1
open branch from bus '5RUSSEL CO J 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1
open branch from bus '5JAMESTOWN T 161.0' to bus '5RUSSEL CO J 161.0' ckt 1 / 342751 5JAMESTOWN T 161 342796 5RUSSEL CO J 161 1
open branch from bus '5JAMESTOWN 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342748 5JAMESTOWN 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5JAMESTOWN T 161.0' ckt 1 / 342745 5JABEZ T 161 342751 5JAMESTOWN T 161 1
open branch from bus '5JABEZ 161.0' to bus '5JABEZ T 161.0' ckt 1 / 342742 5JABEZ 161 342745 5JABEZ T 161 1
open branch from bus '5JABEZ T 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342745 5JABEZ T 161 342799 5S OAKHILL 161 1
open branch from bus '5COOPER1 161.0' to bus '5S OAKHILL 161.0' ckt 1 / 342715 5COOPER1 161 342799 5S OAKHILL 161 1
end
contingency "P6:3144" / 704 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:9906" / 705 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3154" / 706 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11526" / 707 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3161" / 708 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3200" / 709 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:12660" / 710 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:18978" / 711 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3169" / 712 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13956" / 713 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3106" / 714 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3750" / 715 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3148" / 716 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:10554" / 717 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2940" / 718 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3101" / 719 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:3182" / 720 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:4257" / 721 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:16062" / 722 N11_Vdrop
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4279" / 723 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10075" / 724 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:3204" / 725 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:19626" / 726 N11_Vdrop
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3231" / 727 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24000" / 728 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:10606" / 729 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11572" / 730 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5FARLEY 161.0' to bus '2FARLEY KU 69.00' ckt 1 / 324143 5FARLEY 161 324527 2FARLEY KU 69.0 1
end
contingency "P6:11416" / 731 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11577" / 732 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1324" / 733 N11_Vdrop
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3739" / 734 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:3792" / 735 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:9910" / 736 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3809" / 737 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12664" / 738 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3802" / 739 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:11530" / 740 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3782" / 741 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:8290" / 742 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3799" / 743 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:11044" / 744 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:3810" / 745 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12826" / 746 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:15705" / 747 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24077" / 748 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:13275" / 749 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24062" / 750 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9157" / 751 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13021" / 752 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5569" / 753 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5599" / 754 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:5630" / 755 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:21699" / 756 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24114" / 757 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:14247" / 758 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24068" / 759 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:9711" / 760 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24040" / 761 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11441" / 762 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:15627" / 763 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:477" / 764 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:23980" / 765 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:11493" / 766 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:24051" / 767 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:3765" / 768 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5536" / 769 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:9957" / 770 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11406" / 771 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:1705" / 772 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12975" / 773 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:1659" / 774 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5523" / 775 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:3160" / 776 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:12498" / 777 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5641" / 778 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
end
contingency "P6:5613" / 779 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:3224" / 780 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22866" / 781 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3178" / 782 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:15414" / 783 N11_Vdrop
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3206" / 784 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:19950" / 785 N11_Vdrop
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13117" / 786 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:24709" / 787 N11_Vdrop
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3143" / 788 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:9744" / 789 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3158" / 790 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:12174" / 791 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:24" / 792 N11_Vdrop
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3080" / 793 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:3140" / 794 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:9258" / 795 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:9641" / 796 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12700" / 797 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13118" / 798 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:24871" / 799 N11_Vdrop
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1219" / 800 N11_Vdrop
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3166" / 801 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:5665" / 802 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BARKLEY HP 161.0' to bus '5PRINCETN TP 161.0' ckt 1 / 360326 5BARKLEY HP 161 361059 5PRINCETN TP 161 1
end
contingency "P6:11432" / 803 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
end
contingency "P6:12972" / 804 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:13470" / 805 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:14169" / 806 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5LAFAYETT TN 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360354 5LAFAYETT TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2818" / 807 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9580" / 808 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:11423" / 809 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:12711" / 810 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3177" / 811 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:6555" / 812 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11385" / 813 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:15252" / 814 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:1773" / 815 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:5666" / 816 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8SHAWNEE FP 500.0' to bus '7SHAWNEE FP 345.0' ckt 11 / 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
end
contingency "P6:23991" / 817 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
remove swshunt from bus '5SUMMER SHAD 161.0' /* 360334 5SUMMER SHAD 161
end
contingency "P6:1173" / 818 N11_Vdrop
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5520" / 819 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2N LONDON KU 69.00' to bus '2N LONDON 69.00' ckt 1 / 324662 2N LONDON KU 69.0 341929 2N LONDON 69.0 1
open branch from bus '2E BERNSTADT 69.00' to bus '2N LONDON 69.00' ckt 1 / 341410 2E BERNSTADT 69.0 341929 2N LONDON 69.0 1
end
contingency "P6:12969" / 820 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:3136" / 821 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:3165" / 822 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:5609" / 823 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:8610" / 824 N11_Vdrop
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13308" / 825 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:2955" / 826 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3135" / 827 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:3150" / 828 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:8448" / 829 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:10878" / 830 N11_Vdrop
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13075" / 831 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:17905" / 832 N11_Vdrop
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13011" / 833 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:13119" / 834 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:25033" / 835 N11_Vdrop
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3147" / 836 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:10392" / 837 N11_Vdrop
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13122" / 838 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:25519" / 839 N11_Vdrop
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5517" / 840 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2NEW HAVEN 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2NEW HAVEN 69.00' to bus '2BARTON 69.00' ckt 1 / 324660 2NEW HAVEN 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2BARTON 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 324801 2BARTON 69.0 1
open branch from bus '2BARDTWN CTY 69.00' to bus '2WOODLAWN KU 69.00' ckt 1 / 324424 2BARDTWN CTY 69.0 326537 2WOODLAWN KU 69.0 1
open branch from bus '2BARDSTOWN 69.00' to bus '2WOODLAWN KU 69.00' ckt Z1 / 324426 2BARDSTOWN 69.0 326537 2WOODLAWN KU 69.0 Z1
end
contingency "P6:6241" / 841 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11101" / 842 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13003" / 843 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:13033" / 844 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:5623" / 845 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5PHIPPBND IP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 360463 5PHIPPBND IP 161 1
end
contingency "P6:8347" / 846 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12883" / 847 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13016" / 848 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:13044" / 849 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:3205" / 850 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:5667" / 851 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05NAGEL 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:11749" / 852 N11_Vdrop
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13037" / 853 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:19788" / 854 N11_Vdrop
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5559" / 855 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7W LEXINGTON 345.0' ckt 1 / 324102 7BROWN NORTH 345 324116 7W LEXINGTON 345 1
end
contingency "P6:5551" / 856 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
end
contingency "P6:5581" / 857 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:5917" / 858 N11_Vdrop
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11055" / 859 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:12968" / 860 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:13001" / 861 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:13068" / 862 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:13078" / 863 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:13110" / 864 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:16771" / 865 N11_Vdrop
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18391" / 866 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23575" / 867 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1867" / 868 N11_Vdrop
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2191" / 869 N11_Vdrop
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2515" / 870 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3187" / 871 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5564" / 872 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:5593" / 873 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5670" / 874 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05BROADF 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242518 05BROADF 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:7861" / 875 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9967" / 876 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12976" / 877 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12978" / 878 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER2 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342718 5COOPER2 161 342757 5LAUREL DAM 161 1
end
contingency "P6:12980" / 879 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5COOPER1 161.0' to bus '5COOPER2 161.0' ckt 1 / 342715 5COOPER1 161 342718 5COOPER2 161 1
end
contingency "P6:12999" / 880 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13013" / 881 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:13026" / 882 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:13045" / 883 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13073" / 884 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:13074" / 885 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:13079" / 886 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13080" / 887 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:13094" / 888 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:13095" / 889 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:16872" / 890 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:17581" / 891 N11_Vdrop
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17743" / 892 N11_Vdrop
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18553" / 893 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18715" / 894 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20983" / 895 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21145" / 896 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5592" / 897 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12837" / 898 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13056" / 899 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:13071" / 900 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:13072" / 901 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13077" / 902 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:13081" / 903 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:13090" / 904 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13091" / 905 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:13096" / 906 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:13097" / 907 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:14827" / 908 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17257" / 909 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:17419" / 910 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18229" / 911 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18877" / 912 N11_Vdrop
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20335" / 913 N11_Vdrop
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20497" / 914 N11_Vdrop
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21307" / 915 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:21469" / 916 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4783" / 917 N11_Vdrop
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8995" / 918 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12994" / 919 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13020" / 920 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:13050" / 921 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13064" / 922 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:13076" / 923 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:13089" / 924 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13107" / 925 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:13120" / 926 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:13855" / 927 N11_Vdrop
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:16123" / 928 N11_Vdrop
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:18067" / 929 N11_Vdrop
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20173" / 930 N11_Vdrop
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23089" / 931 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:25195" / 932 N11_Vdrop
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3125" / 933 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:3152" / 934 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5549" / 935 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:5585" / 936 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05WOOTON 161.0' to bus '5HYDEN 161.0' ckt 1 / 243668 05WOOTON 161 324148 5HYDEN 161 1
end
contingency "P6:6403" / 937 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:6828" / 938 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11202" / 939 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12397" / 940 N11_Vdrop
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13004" / 941 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:13041" / 942 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:13067" / 943 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:13092" / 944 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:13112" / 945 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:13121" / 946 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:16609" / 947 N11_Vdrop
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:20659" / 948 N11_Vdrop
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23899" / 949 N11_Vdrop
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:25357" / 950 N11_Vdrop
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3487" / 951 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5574" / 952 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:5626" / 953 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLUFF CITY 161.0' ckt 1 / 360107 5SULLIVAN #1 161 360484 5BLUFF CITY 161 1
end
contingency "P6:12986" / 954 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
end
contingency "P6:3156" / 955 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:5516" / 956 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2EASTVIEW 69.00' to bus '2STEPHENSBRG 69.00' ckt 1 / 324509 2EASTVIEW 69.0 342307 2STEPHENSBRG 69.0 1
end
contingency "P6:5616" / 957 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
end
contingency "P6:5628" / 958 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5BLOUNT TN T 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361351 5BLOUNT TN T 161 1
end
contingency "P6:5658" / 959 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:11850" / 960 N11_Vdrop
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13114" / 961 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:23529" / 962 N11_Vdrop
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '5SULVAN BNK3 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #2 13.00' ckt 3 /
open threewinding at bus '1SULLIVAN #2 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULVAN BNK3 161.0' ckt 3 /
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:24223" / 963 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1821" / 964 N11_Vdrop
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5561" / 965 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARNOLD 161.0' to bus '5DORCHESTER 161.0' ckt 1 / 324131 5ARNOLD 161 324139 5DORCHESTER 161 1
end
contingency "P6:5604" / 966 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:5612" / 967 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WINFIELD TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 361579 5WINFIELD TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:5621" / 968 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 2 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 2
end
contingency "P6:5622" / 969 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #2 161.0' to bus '5PHIPPS B NP 161.0' ckt 4 / 360101 5J SEVIER #2 161 360103 5PHIPPS B NP 161 4
end
contingency "P6:5625" / 970 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5NEJC TN 161.0' ckt 2 / 360107 5SULLIVAN #1 161 360481 5NEJC TN 161 2
end
contingency "P6:5629" / 971 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #1 161.0' to bus '5MILLIGAN 161.0' ckt 1 / 360107 5SULLIVAN #1 161 361523 5MILLIGAN 161 1
end
contingency "P6:5639" / 972 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BLUFF CITY 161.0' to bus '5SULLIVAN #2 161.0' ckt 2 / 360484 5BLUFF CITY 161 360565 5SULLIVAN #2 161 2
end
contingency "P6:5642" / 973 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z1 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z1
end
contingency "P6:5643" / 974 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5SULVAN BNK3 161.0' ckt Z2 / 360565 5SULLIVAN #2 161 360765 5SULVAN BNK3 161 Z2
end
contingency "P6:13115" / 975 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24385" / 976 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:4737" / 977 N11_Vdrop
open branch from bus '5SUMM SHADE 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 342814 5SUMM SHADE 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5568" / 978 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
end
contingency "P6:5619" / 979 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
end
contingency "P6:5620" / 980 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:5624" / 981 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PHIPPS B NP 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360103 5PHIPPS B NP 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:5638" / 982 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5NEJC TN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360481 5NEJC TN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5644" / 983 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5BLOUNTVL TN 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361058 5BLOUNTVL TN 161 1
end
contingency "P6:5645" / 984 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SULLIVAN #2 161.0' to bus '5FORDTOWN TP 161.0' ckt 1 / 360565 5SULLIVAN #2 161 361096 5FORDTOWN TP 161 1
end
contingency "P6:5552" / 985 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4FAWKES KU 138.0' ckt 1 / 324217 4BROWN PLANT 138 324248 4FAWKES KU 138 1
end
contingency "P6:5598" / 986 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PHIPPS B NP 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:5615" / 987 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
end
contingency "P6:5637" / 988 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BOONE HP 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360475 5BOONE HP 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5640" / 989 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIZABETHTN 161.0' to bus '5SULLIVAN #2 161.0' ckt 1 / 360485 5ELIZABETHTN 161 360565 5SULLIVAN #2 161 1
end
contingency "P6:5655" / 990 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8HIWASSEE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1
end
contingency "P6:5660" / 991 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '5SULLIVAN #1 161.0' to bus '8SULLIVAN TN 500.0' to bus '1SULLIVAN #1 13.00' ckt 1 /
open threewinding at bus '1SULLIVAN #1 13.00' to bus '8SULLIVAN TN 500.0' to bus '5SULLIVAN #1 161.0' ckt 1 /
end
contingency "P6:5668" / 992 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05NAGEL 500.0' to bus '8SULLIVAN TN 500.0' ckt 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1
end
contingency "P6:5669" / 993 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05HOLST1 138.0' to bus '4BOONE HP 138.0' ckt 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1
end
contingency "P6:8023" / 994 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13014" / 995 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:5589" / 996 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:9643" / 997 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13024" / 998 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13069" / 999 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:13104" / 1000 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:13116" / 1001 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:16933" / 1002 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22603" / 1003 N11_Vdrop
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:24547" / 1004 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:3171" / 1005 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
end
contingency "P6:3441" / 1006 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5LAUREL DAM 161.0' ckt 1 / 342754 5LAUREL CO 161 342757 5LAUREL DAM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13066" / 1007 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:13111" / 1008 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:14280" / 1009 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5WOLF CRK HP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360448 5WOLF CRK HP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:16447" / 1010 N11_Vdrop
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23737" / 1011 N11_Vdrop
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5617" / 1012 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360085 8WBNP #1 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5662" / 1013 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
end
contingency "P6:13083" / 1014 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:19201" / 1015 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:24177" / 1016 N11_Vdrop
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 1 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 1
open branch from bus '5J SEVIER #1 161.0' to bus '5PHIPPS B NP 161.0' ckt 3 / 360100 5J SEVIER #1 161 360103 5PHIPPS B NP 161 3
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5663" / 1017 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:24339" / 1018 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5PHIPPS B NP 161.0' /* 360103 5PHIPPS B NP 161
end
contingency "P6:5562" / 1019 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HARLAN WYE 161.0' ckt 1 / 324131 5ARNOLD 161 324146 5HARLAN WYE 161 1
end
contingency "P6:5572" / 1020 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5755" / 1021 N11_Vdrop
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13000" / 1022 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:5614" / 1023 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
end
contingency "P6:5652" / 1024 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8SEQUOYAH NP 500.0' to bus '8WBNP #1 500.0' ckt 1 / 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1
end
contingency "P6:5659" / 1025 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open threewinding at bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '5PHIPPS B NP 161.0' to bus '8PHIPPS B NP 500.0' to bus '1PHIPPBND NP 13.20' ckt 3 /
open threewinding at bus '1PHIPPBND NP 13.20' to bus '8PHIPPS B NP 500.0' to bus '5PHIPPS B NP 161.0' ckt 3 /
end
contingency "P6:5664" / 1026 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:24501" / 1027 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
remove swshunt from bus '5SULLIVAN #1 161.0' /* 360107 5SULLIVAN #1 161
end
contingency "P6:5631" / 1028 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5S SCOTTSVLE 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361139 5S SCOTTSVLE 161 1
end
contingency "P6:7699" / 1029 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13012" / 1030 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:3181" / 1031 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:7678" / 1032 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:15900" / 1033 N11_Vdrop
open branch from bus '5TOMPKNSV TP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 361064 5TOMPKNSV TP 161 361666 5BURKSVLTP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5269" / 1034 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12997" / 1035 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
end
contingency "P6:5548" / 1036 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARNOLD 161.0' to bus '5HYDEN 161.0' ckt 1 / 324131 5ARNOLD 161 324148 5HYDEN 161 1
end
contingency "P6:3649" / 1037 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5560" / 1038 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:9805" / 1039 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12987" / 1040 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:13025" / 1041 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:4276" / 1042 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5554" / 1043 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:5579" / 1044 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:5656" / 1045 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:9319" / 1046 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10731" / 1047 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:12970" / 1048 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:13022" / 1049 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:3188" / 1050 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:5223" / 1051 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324102 7BROWN NORTH 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:17034" / 1052 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3603" / 1053 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:3973" / 1054 N11_Vdrop
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4273" / 1055 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5535" / 1056 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:5573" / 1057 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '4BROWN NORTH 138.0' ckt 1 / 324102 7BROWN NORTH 345 324216 4BROWN NORTH 138 1
end
contingency "P6:12989" / 1058 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:1644" / 1059 N11_Vdrop
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3093" / 1060 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5FOX HOLLOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 342732 5FOX HOLLOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:8671" / 1061 N11_Vdrop
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10119" / 1062 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11407" / 1063 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:11462" / 1064 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:13018" / 1065 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:19029" / 1066 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:13102" / 1067 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:22279" / 1068 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4945" / 1069 N11_Vdrop
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5518" / 1070 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2HODGENV KU 69.00' to bus '2HODGENVILLE 69.00' ckt 1 / 324575 2HODGENV KU 69.0 341632 2HODGENVILLE 69.0 1
open branch from bus '2ETOWN 4 69.00' to bus '2HODGENV KU 69.00' ckt 1 / 324521 2ETOWN 4 69.0 324575 2HODGENV KU 69.0 1
open branch from bus '2ETOWN KU 69.00' to bus '2ETOWN 4 69.00' ckt 1 / 324519 2ETOWN KU 69.0 324521 2ETOWN 4 69.0 1
end
contingency "P6:12995" / 1071 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
end
contingency "P6:13103" / 1072 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:22441" / 1073 N11_Vdrop
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3109" / 1074 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:4236" / 1075 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5570" / 1076 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:10453" / 1077 N11_Vdrop
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11587" / 1078 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13029" / 1079 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:13036" / 1080 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:13084" / 1081 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:19363" / 1082 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3927" / 1083 N11_Vdrop
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5537" / 1084 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5FALL ROCK 161.0' to bus '5TYNER 161.0' ckt 1 / 342730 5FALL ROCK 161 342820 5TYNER 161 1
open branch from bus '5FALL ROCK 161.0' to bus '2FALL ROCK 69.00' ckt 1 / 342730 5FALL ROCK 161 341464 2FALL ROCK 69.0 1
end
contingency "P6:5566" / 1085 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
end
contingency "P6:3133" / 1086 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:4459" / 1087 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:8124" / 1088 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12992" / 1089 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:5650" / 1090 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#1 161.0' ckt 1 / 360097 8VOLUNTEER 500 360098 5VOLUNTEER#1 161 1
end
contingency "P6:11431" / 1091 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:14007" / 1092 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3127" / 1093 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:4899" / 1094 N11_Vdrop
open branch from bus '5TAYLOR CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 325921 5TAYLOR CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5632" / 1095 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:5651" / 1096 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8VOLUNTEER 500.0' to bus '5VOLUNTEER#2 161.0' ckt 2 / 360097 8VOLUNTEER 500 360104 5VOLUNTEER#2 161 2
end
contingency "P6:7152" / 1097 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13070" / 1098 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:17095" / 1099 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5577" / 1100 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
end
contingency "P6:5584" / 1101 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
end
contingency "P6:9481" / 1102 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:9644" / 1103 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:10407" / 1104 N11_Vdrop
open branch from bus '5DELVINTA 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324138 5DELVINTA 161 324165 5W IRVINE T 161 1
open branch from bus '5LAKE REBA T 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324152 5LAKE REBA T 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '5W IRVINE T 161.0' ckt 1 / 324163 5WEST IRVINE 161 324165 5W IRVINE T 161 1
open branch from bus '5WEST IRVINE 161.0' to bus '2WEST IRVINE 69.00' ckt 1 / 324163 5WEST IRVINE 161 324767 2WEST IRVINE 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:11541" / 1105 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
open branch from bus '5PINEVILLE 2 161.0' to bus '2PINEVILLE 69.00' ckt 2 / 324167 5PINEVILLE 2 161 324686 2PINEVILLE 69.0 2
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13023" / 1106 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:13186" / 1107 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:2616" / 1108 N11_Vdrop
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3099" / 1109 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5COOPER1 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342715 5COOPER1 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342787 5PULASK CO 161 342790 5PULASK CO J 161 1
open branch from bus '5PULASK CO 161.0' to bus '2PULASK CO 69.00' ckt 1 / 342787 5PULASK CO 161 342115 2PULASK CO 69.0 1
open branch from bus '5LIBERTY J 161.0' to bus '5PULASK CO J 161.0' ckt 1 / 342760 5LIBERTY J 161 342790 5PULASK CO J 161 1
end
contingency "P6:7051" / 1110 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13008" / 1111 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:13109" / 1112 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:23413" / 1113 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3128" / 1114 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:7213" / 1115 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7314" / 1116 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:11435" / 1117 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:13009" / 1118 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:14655" / 1119 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1482" / 1120 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3092" / 1121 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:3114" / 1122 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:4413" / 1123 N11_Vdrop
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5046" / 1124 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5540" / 1125 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BARREN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342694 5BARREN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5BARREN CO 161.0' to bus '2BARREN CO 69.00' ckt 1 / 342694 5BARREN CO 161 341059 2BARREN CO 69.0 1
end
contingency "P6:5618" / 1126 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '8VOLUNTEER 500.0' ckt 1 / 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1
end
contingency "P6:8185" / 1127 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13015" / 1128 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:13106" / 1129 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:22927" / 1130 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:2829" / 1131 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11362" / 1132 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:13085" / 1133 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:13105" / 1134 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:19525" / 1135 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:22765" / 1136 N11_Vdrop
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5556" / 1137 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
end
contingency "P6:5571" / 1138 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:10291" / 1139 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13028" / 1140 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:11911" / 1141 N11_Vdrop
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13038" / 1142 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:5563" / 1143 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
end
contingency "P6:5657" / 1144 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8BULL RUN FP 500.0' to bus '5BULL RUN FP 161.0' ckt 5 / 360093 8BULL RUN FP 500 360094 5BULL RUN FP 161 5
end
contingency "P6:13055" / 1145 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:14665" / 1146 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5557" / 1147 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
end
contingency "P6:5654" / 1148 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8BULL RUN FP 500.0' ckt 1 / 360085 8WBNP #1 500 360093 8BULL RUN FP 500 1
end
contingency "P6:3116" / 1149 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:5370" / 1150 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5633" / 1151 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5E SUMNER TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361558 5E SUMNER TP 161 1
end
contingency "P6:6727" / 1152 N11_Vdrop
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10777" / 1153 N11_Vdrop
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12559" / 1154 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13006" / 1155 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:13031" / 1156 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BARDSTOWN 138.0' to bus '4BROWN CT 138.0' ckt 1 / 324207 4BARDSTOWN 138 324218 4BROWN CT 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '4NELSON CO 138.0' ckt 1 / 324207 4BARDSTOWN 138 324288 4NELSON CO 138 1
open branch from bus '4BARDSTOWN 138.0' to bus '2BARDSTOWN 69.00' ckt 1 / 324207 4BARDSTOWN 138 324426 2BARDSTOWN 69.0 1
end
contingency "P6:13042" / 1157 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:5653" / 1158 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8WBNP #1 500.0' to bus '8ROANE TN 500.0' ckt 1 / 360085 8WBNP #1 500 360090 8ROANE TN 500 1
end
contingency "P6:6889" / 1159 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11263" / 1160 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13007" / 1161 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:13034" / 1162 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13060" / 1163 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:13108" / 1164 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
end
contingency "P6:15475" / 1165 N11_Vdrop
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:23251" / 1166 N11_Vdrop
open branch from bus '8BULL RUN FP 500.0' to bus '8ANDERSON TN 500.0' ckt 1 / 360093 8BULL RUN FP 500 360120 8ANDERSON TN 500 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3202" / 1167 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
end
contingency "P6:5576" / 1168 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
end
contingency "P6:5586" / 1169 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '05CLNCHR 138.0' to bus '4VIRGINIA CI 138.0' ckt 1 / 242605 05CLNCHR 138 324316 4VIRGINIA CI 138 1
end
contingency "P6:10245" / 1170 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:19302" / 1171 N11_Vdrop
open branch from bus '5LAFAYETT TN 161.0' to bus '5HARTSVLE TP 161.0' ckt 1 / 360354 5LAFAYETT TN 161 361265 5HARTSVLE TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13088" / 1172 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:20011" / 1173 N11_Vdrop
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5431" / 1174 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12998" / 1175 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
end
contingency "P6:5590" / 1176 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
end
contingency "P6:5603" / 1177 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:8833" / 1178 N11_Vdrop
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13019" / 1179 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:13054" / 1180 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:14503" / 1181 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5555" / 1182 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
end
contingency "P6:5582" / 1183 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5608" / 1184 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PINEVILL KY 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360452 5PINEVILL KY 161 360633 5SWEET GUM 161 1
end
contingency "P6:7375" / 1185 N11_Vdrop
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11217" / 1186 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13010" / 1187 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:5636" / 1188 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LAFOLLET TN 161.0' to bus '5SWEET GUM 161.0' ckt 1 / 360453 5LAFOLLET TN 161 360633 5SWEET GUM 161 1
end
contingency "P6:6079" / 1189 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13002" / 1190 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:5385" / 1191 N11_Vdrop
open branch from bus '7PINEVILLE 345.0' to bus '7W GARRARDKU 345.0' ckt 1 / 324112 7PINEVILLE 345 325074 7W GARRARDKU 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13057" / 1192 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:14989" / 1193 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5567" / 1194 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
end
contingency "P6:5602" / 1195 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5S GLASGOW 161.0' ckt 1 / 360334 5SUMMER SHAD 161 360607 5S GLASGOW 161 1
end
contingency "P6:5550" / 1196 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
end
contingency "P6:5558" / 1197 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7BROWN NORTH 345.0' to bus '7HARDIN CO 345.0' ckt 1 / 324102 7BROWN NORTH 345 324106 7HARDIN CO 345 1
end
contingency "P6:11419" / 1198 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
end
contingency "P6:12063" / 1199 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:3105" / 1200 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
end
contingency "P6:3588" / 1201 N11_Vdrop
open branch from bus '5LAUREL CO 161.0' to bus '5PITTSBURG 161.0' ckt 1 / 342754 5LAUREL CO 161 342781 5PITTSBURG 161 1
open branch from bus '5PITTSBURG 161.0' to bus '2PITTSBRG KU 69.00' ckt 1 / 342781 5PITTSBURG 161 324688 2PITTSBRG KU 69.0 1
open branch from bus '5PITTSBURG 161.0' to bus '5TYNER 161.0' ckt 1 / 342781 5PITTSBURG 161 342820 5TYNER 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5605" / 1202 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
end
contingency "P6:3134" / 1203 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
end
contingency "P6:8286" / 1204 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13086" / 1205 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:19687" / 1206 N11_Vdrop
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3151" / 1207 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
end
contingency "P6:11040" / 1208 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5ARTEMUS 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324133 5ARTEMUS 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5FARLEY 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324143 5FARLEY 161 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5ARTEMUS 161.0' to bus '2ARTEMUS 69.00' ckt 1 / 324133 5ARTEMUS 161 324417 2ARTEMUS 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3162" / 1209 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
end
contingency "P6:12721" / 1210 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12822" / 1211 N11_Vdrop
open branch from bus '5ARTEMUS TAP 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324132 5ARTEMUS TAP 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '5PINEVILE SW 161.0' to bus '5PINEVILL KY 161.0' ckt 1 / 324156 5PINEVILE SW 161 360452 5PINEVILL KY 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13043" / 1212 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:13087" / 1213 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:19849" / 1214 N11_Vdrop
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13098" / 1215 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:21631" / 1216 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5634" / 1217 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5ONEIDA TN 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361580 5ONEIDA TN 161 1
end
contingency "P6:3119" / 1218 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
end
contingency "P6:5856" / 1219 N11_Vdrop
open branch from bus '5BLUE LICK 161.0' to bus '5CEDAR GRV 161.0' ckt 1 / 324134 5BLUE LICK 161 326975 5CEDAR GRV 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:5591" / 1220 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
end
contingency "P6:5635" / 1221 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5HUNTSVL TN 161.0' to bus '5KELSEY RD 161.0' ckt 1 / 360450 5HUNTSVL TN 161 361618 5KELSEY RD 161 1
end
contingency "P6:9420" / 1222 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:12235" / 1223 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12675" / 1224 N11_Vdrop
open branch from bus '8PINEVILLE 500.0' to bus '8POCKET N 500.0' ckt 1 / 324072 8PINEVILLE 500 324073 8POCKET N 500 1
open branch from bus '8POCKET N 500.0' to bus '8PHIPPS B NP 500.0' ckt 1 / 324073 8POCKET N 500 360102 8PHIPPS B NP 500 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '8PINEVILLE 500.0' to bus '7PINEVILLE 345.0' ckt 1 / 324072 8PINEVILLE 500 324112 7PINEVILLE 345 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:13040" / 1225 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13048" / 1226 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13531" / 1227 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:4621" / 1228 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12993" / 1229 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:369" / 1230 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:5588" / 1231 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:6484" / 1232 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:5596" / 1233 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
end
contingency "P6:13485" / 1234 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5SUMMER SHAD 161.0' ckt 1 / 324150 5LEBANON JCT 161 360334 5SUMMER SHAD 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:2778" / 1235 N11_Vdrop
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3100" / 1236 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5LIBERTY J 161.0' ckt 1 / 342703 5CASEY CO 161 342760 5LIBERTY J 161 1
open branch from bus '5CASEY CO 161.0' to bus '2CASEY CO 69.00' ckt 1 / 342703 5CASEY CO 161 341269 2CASEY CO 69.0 1
open branch from bus '5CASEY CO 161.0' to bus '5MARION CO 161.0' ckt 1 / 342703 5CASEY CO 161 342769 5MARION CO 161 1
end
contingency "P6:3001" / 1237 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3111" / 1238 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:4560" / 1239 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4575" / 1240 N11_Vdrop
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5541" / 1241 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 326998 5BULLITT TAP 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMM SHADE 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 342814 5SUMM SHADE 161 361788 5SUM SHAD TP 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5SUM SHAD TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361788 5SUM SHAD TP 161 1
open branch from bus '5CEDAR GRV 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT TAP 161.0' to bus '5BULLITT CO 161.0' ckt 1 / 326998 5BULLITT TAP 161 342700 5BULLITT CO 161 1
open branch from bus '5BULLITT CO 161.0' to bus '5LITTLE MT T 161.0' ckt 1 / 342700 5BULLITT CO 161 342766 5LITTLE MT T 161 1
open branch from bus '5BULLITT CO 161.0' to bus '2BULLITT CO 69.00' ckt 1 / 342700 5BULLITT CO 161 341215 2BULLITT CO 69.0 1
end
contingency "P6:12983" / 1242 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5WINFIELD TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 361579 5WINFIELD TN 161 1
end
contingency "P6:13100" / 1243 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:21955" / 1244 N11_Vdrop
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:85" / 1245 N11_Vdrop
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12962" / 1246 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
end
contingency "P6:13047" / 1247 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13369" / 1248 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5648" / 1249 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5KELSEY RD 161.0' to bus '5BYRDSTOWN 161.0' ckt 1 / 361618 5KELSEY RD 161 361619 5BYRDSTOWN 161 1
end
contingency "P6:5646" / 1250 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5S GLASGOW 161.0' to bus '5GLASGOW TP 161.0' ckt 1 / 360607 5S GLASGOW 161 361113 5GLASGOW TP 161 1
end
contingency "P6:39" / 1251 N11_Vdrop
open branch from bus '2LANCASTR KU 69.00' to bus '2GARRARD CO 69.00' ckt 1 / 324600 2LANCASTR KU 69.0 341515 2GARRARD CO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5595" / 1252 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
end
contingency "P6:13059" / 1253 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:13323" / 1254 N11_Vdrop
open branch from bus '4BONNIEVILLE 138.0' to bus '4LEBANON WES 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324270 4LEBANON WES 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '4MERE TVA 138.0' ckt 1 / 324213 4BONNIEVILLE 138 324800 4MERE TVA 138 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIE KU 69.00' ckt 1 / 324213 4BONNIEVILLE 138 324447 2BONNIE KU 69.0 1
open branch from bus '4BONNIEVILLE 138.0' to bus '2BONNIV EK 69.00' ckt 1 / 324213 4BONNIEVILLE 138 341161 2BONNIV EK 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:15313" / 1255 N11_Vdrop
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:3179" / 1256 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
end
contingency "P6:15576" / 1257 N11_Vdrop
open branch from bus '5S GLASGOW 161.0' to bus '5E GLASGOW T 161.0' ckt 1 / 360607 5S GLASGOW 161 361603 5E GLASGOW T 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:13051" / 1258 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
end
contingency "P6:13082" / 1259 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
end
contingency "P6:14017" / 1260 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 360145 5ROYAL BLUE 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:19039" / 1261 N11_Vdrop
open branch from bus '5ROYAL BLUE 161.0' to bus '5ROYL BLU SS 161.0' ckt 1 / 360145 5ROYAL BLUE 161 361771 5ROYL BLU SS 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:571" / 1262 N11_Vdrop
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12965" / 1263 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:3811" / 1264 N11_Vdrop
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:5607" / 1265 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5BURKSVLTP 161.0' ckt 1 / 360448 5WOLF CRK HP 161 361666 5BURKSVLTP 161 1
end
contingency "P6:12988" / 1266 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5GREEN HAL T 161.0' to bus '5TYNER 161.0' ckt 1 / 342736 5GREEN HAL T 161 342820 5TYNER 161 1
open branch from bus '5GREEN HAL T 161.0' to bus '5GREEN HALL 161.0' ckt 1 / 342736 5GREEN HAL T 161 342739 5GREEN HALL 161 1
open branch from bus '5DELVINTA 161.0' to bus '5GREEN HAL T 161.0' ckt 1 / 324138 5DELVINTA 161 342736 5GREEN HAL T 161 1
end
contingency "P6:8509" / 1267 N11_Vdrop
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:10939" / 1268 N11_Vdrop
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13017" / 1269 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:13032" / 1270 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:525" / 1271 N11_Vdrop
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5513" / 1272 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 2 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341722 2KEAVY 2 T 69.0 1
open branch from bus '2KEAVY 69.00' to bus '2KEAVY 1 T 69.00' ckt 1 / 341716 2KEAVY 69.0 341719 2KEAVY 1 T 69.0 1
open branch from bus '2KEAVY 2 T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341722 2KEAVY 2 T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2S CORBIN 69.00' ckt 1 / 341038 2BACON CRK T 69.0 342187 2S CORBIN 69.0 1
open branch from bus '2BACON CRK 69.00' to bus '2BACON CRK T 69.00' ckt 1 / 341035 2BACON CRK 69.0 341038 2BACON CRK T 69.0 1
open branch from bus '2BACON CRK T 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 341038 2BACON CRK T 69.0 341755 2LIBER CH T 69.0 1
open branch from bus '2LIBER CH T 69.00' to bus '2LIBERT CHUR 69.00' ckt 1 / 341755 2LIBER CH T 69.0 341758 2LIBERT CHUR 69.0 1
open branch from bus '2FARLEY KU 69.00' to bus '2LIBER CH T 69.00' ckt 1 / 324527 2FARLEY KU 69.0 341755 2LIBER CH T 69.0 1
end
contingency "P6:733" / 1273 N11_Vdrop
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:1320" / 1274 N11_Vdrop
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:3091" / 1275 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4FAWKES EK 138.0' to bus '4W BEREA 138.0' ckt 1 / 342577 4FAWKES EK 138 342691 4W BEREA 138 1
open branch from bus '4W BEREA 138.0' to bus '2W BEREA 69.00' ckt 1 / 342691 4W BEREA 138 342430 2W BEREA 69.0 1
end
contingency "P6:4297" / 1276 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:11425" / 1277 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12966" / 1278 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:12991" / 1279 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:13035" / 1280 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5565" / 1281 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:5580" / 1282 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
end
contingency "P6:10893" / 1283 N11_Vdrop
open branch from bus '5PADDYS RUN 161.0' to bus '4PADDYS RUN 138.0' ckt 1 / 324154 5PADDYS RUN 161 324295 4PADDYS RUN 138 1
open branch from bus '5LEBANON JCT 161.0' to bus '5PADDYS RUN 161.0' ckt 1 / 324150 5LEBANON JCT 161 324154 5PADDYS RUN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:687" / 1284 N11_Vdrop
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5514" / 1285 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '2HOPEWELL 69.00' to bus '2LAUREL CO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 341740 2LAUREL CO 69.0 1
open branch from bus '2HOPEWELL 69.00' to bus '2SWEET HOLLO 69.00' ckt 1 / 324576 2HOPEWELL 69.0 324748 2SWEET HOLLO 69.0 1
end
contingency "P6:4251" / 1286 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5583" / 1287 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11379" / 1288 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:20821" / 1289 N11_Vdrop
open branch from bus '5W TOMPKINSV 161.0' to bus '5W TOMPKINST 161.0' ckt 1 / 360509 5W TOMPKINSV 161 361246 5W TOMPKINST 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:13065" / 1290 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
end
contingency "P6:16285" / 1291 N11_Vdrop
open branch from bus '5E GLASGOW T 161.0' to bus '5E GLASGOW 161.0' ckt 1 / 361603 5E GLASGOW T 161 361604 5E GLASGOW 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:7689" / 1292 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11392" / 1293 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5ALCALDE 161.0' to bus '5FARLEY 161.0' ckt 1 / 324130 5ALCALDE 161 324143 5FARLEY 161 1
end
contingency "P6:3173" / 1294 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:14604" / 1295 N11_Vdrop
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:4287" / 1296 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11371" / 1297 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5GREEN CO 161.0' to bus '5SUMM SHADE 161.0' ckt 1 / 342733 5GREEN CO 161 342814 5SUMM SHADE 161 1
end
contingency "P6:11426" / 1298 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
end
contingency "P6:13197" / 1299 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON WES 138.0' to bus '4LEBANON 138.0' ckt 1 / 324270 4LEBANON WES 138 324271 4LEBANON 138 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 1 / 324271 4LEBANON 138 324606 2LEBANON 69.0 1
open branch from bus '4LEBANON 138.0' to bus '2LEBANON 69.00' ckt 2 / 324271 4LEBANON 138 324606 2LEBANON 69.0 2
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:1533" / 1300 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:5097" / 1301 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11354" / 1302 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:11376" / 1303 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:391" / 1304 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
end
contingency "P6:10048" / 1305 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILLE N 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324238 4DANVILLE N 138 324239 4DANVILE N T 138 1
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9624" / 1306 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '7PINEVILLE 345.0' to bus '5PINEVILLE 2 161.0' ckt 1 / 324112 7PINEVILLE 345 324167 5PINEVILLE 2 161 1
end
contingency "P6:3325" / 1307 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12985" / 1308 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
end
contingency "P6:3279" / 1309 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5JELLICO TN 161.0' ckt 1 / 342778 5MCCREARY CO 161 360473 5JELLICO TN 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:6544" / 1310 N11_Vdrop
open branch from bus '4DANVILE N T 138.0' to bus '4LEBANON 138.0' ckt 1 / 324239 4DANVILE N T 138 324271 4LEBANON 138 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:385" / 1311 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:4135" / 1312 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
end
contingency "P6:12990" / 1313 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5ELIHU 161.0' to bus '5COOPER2 161.0' ckt 1 / 324141 5ELIHU 161 342718 5COOPER2 161 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 1 / 324141 5ELIHU 161 324514 2ELIHU 69.0 1
open branch from bus '5ELIHU 161.0' to bus '2ELIHU 69.00' ckt 2 / 324141 5ELIHU 161 324514 2ELIHU 69.0 2
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:9471" / 1314 N11_Vdrop
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:9653" / 1315 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '5SUMMER SHAD 161.0' to bus '5TOMPKNSV TP 161.0' ckt 1 / 360334 5SUMMER SHAD 161 361064 5TOMPKNSV TP 161 1
end
contingency "P6:11403" / 1316 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
open branch from bus '8POCKET N 500.0' to bus '5POCKET N 161.0' ckt 1 / 324073 8POCKET N 500 324157 5POCKET N 161 1
end
contingency "P6:360" / 1317 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
end
contingency "P6:3139" / 1318 N11_Vdrop
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
end
contingency "P6:5026" / 1319 N11_Vdrop
open branch from bus '5MARION CO 161.0' to bus '4MARION CO 138.0' ckt 1 / 342769 5MARION CO 161 342770 4MARION CO 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:9096" / 1320 N11_Vdrop
open branch from bus '4BROWN PLANT 138.0' to bus '4DANVILE N T 138.0' ckt 1 / 324217 4BROWN PLANT 138 324239 4DANVILE N T 138 1
open branch from bus '5MCCREARY CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342778 5MCCREARY CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WOLF CRK HP 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 360448 5WOLF CRK HP 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '5WAYNE CO KY 161.0' ckt 1 / 342823 5WAYNE CO 161 360486 5WAYNE CO KY 161 1
open branch from bus '5WAYNE CO 161.0' to bus '2WAYNE CO 69.00' ckt 1 / 342823 5WAYNE CO 161 342478 2WAYNE CO 69.0 1
end
contingency "P6:338" / 1321 N11_Vdrop
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
end
contingency "P6:1462" / 1322 N11_Vdrop
open branch from bus '4LEBANON 138.0' to bus '4MARION CO 138.0' ckt 1 / 324271 4LEBANON 138 342770 4MARION CO 138 1
open branch from bus '2FERGUSON SO 69.00' to bus '2SOMERSET KU 69.00' ckt 1 / 324531 2FERGUSON SO 69.0 342287 2SOMERSET KU 69.0 1
open branch from bus '2ELIHU 69.00' to bus '2FERGUSON SO 69.00' ckt 1 / 324514 2ELIHU 69.0 324531 2FERGUSON SO 69.0 1
end
contingency "P6:4089" / 1323 N11_Vdrop
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
end
contingency "P6:5538" / 1324 N11_Vdrop
open branch from bus '5ALCALDE 161.0' to bus '5ELIHU 161.0' ckt 1 / 324130 5ALCALDE 161 324141 5ELIHU 161 1
open branch from bus '5GREEN CO 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342733 5GREEN CO 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA T 161.0' to bus '5TAYLOR CO J 161.0' ckt 1 / 342805 5SALOMA T 161 342817 5TAYLOR CO J 161 1
open branch from bus '5SALOMA 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342802 5SALOMA 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP T 161.0' to bus '5SALOMA T 161.0' ckt 1 / 342775 5MARION IP T 161 342805 5SALOMA T 161 1
open branch from bus '5MARION IP 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342772 5MARION IP 161 342797 5S MARION IT 161 1
open branch from bus '5MARION IP T 161.0' to bus '5S MARION IT 161.0' ckt 1 / 342775 5MARION IP T 161 342797 5S MARION IT 161 1
open branch from bus '5S MARION IT 161.0' to bus '5S MARION IP 161.0' ckt 1 / 342797 5S MARION IT 161 342798 5S MARION IP 161 1
open branch from bus '5MARION CO 161.0' to bus '5MARION IP T 161.0' ckt 1 / 342769 5MARION CO 161 342775 5MARION IP T 161 1
end
contingency "P6:8823" / 1325 N11_Vdrop
open branch from bus '5PINEVILLE 1 161.0' to bus '5PINEVILE SW 161.0' ckt 1 / 324155 5PINEVILLE 1 161 324156 5PINEVILE SW 161 1
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1
open branch from bus '7ALCALDE 345.0' to bus '5ALCALDE 161.0' ckt 1 / 324100 7ALCALDE 345 324130 5ALCALDE 161 1
end
contingency "P6:11399" / 1326 N11_Vdrop
open branch from bus '7ALCALDE 345.0' to bus '7BROWN NORTH 345.0' ckt 1 / 324100 7ALCALDE 345 324102 7BROWN NORTH 345 1
open branch from bus '7ALCALDE 345.0' to bus '7PINEVILLE 345.0' ckt 1 / 324100 7ALCALDE 345 324112 7PINEVILLE 345 1