## Alternatives
Project:
Alternative | Description | NPV (if applicable) | EKPC Total Construction Costs (Installed Year $) | MSO Total Construction Costs (Installed Year $) | Total Cost | Implementation Time [Months]
Base | Do Nothing |  |  |  | 0
1 | Alt. 1 - Install a 53 MVAR Capacitor Bank on the Cooper 69kV Bus. | 1153965.1313 | 1059922.6236 |  | 1153965.1313
2 | Alt. 2 - Construct a 26 mile 161kV line from McCreary County to Cooper. | 51721286.4285 | 38367662.856 |  | 51721286.4285
3 | Alt. 3 - Construct a 48 mile 345kV line from West Garrard to Cooper. | 183965900.6816 | 140152493.2401 |  | 183965900.6816
3b | Alt. 3b - Construct a 48 mile 161kV line from West Garrard to Cooper. | 108448403.9449 | 81549524.991 |  | 108448403.9449
4 | Alt. 4 - Construct a 29 mile line from West Garrard to Liberty Jct. | 122493958.566 | 93847699.6648 |  | 122493958.566
5 | Alt. 5 - Construct a 5 mile 345kV line from KU Alcalde to Cooper. | 56651890.5989 | 69002498.9187 |  | 56651890.5989
6 | Alt. 6 - Construct a 29 mile 161 kV line from Wayne County to Cooper. | 57597132.5128 | 42433771.8195 |  | 57597132.5128
Help

## Measures
Obj # | Objective | Weight | Applicable | Base | 1 | 2 | 3 | 3b | 4 | 5 | 6 | 0 | 0
1 | Minimize maintenance costs | 8 | TRUE | Note example
2 | Environmental impact | 3 | TRUE
3 | Improve operational flexibility | 7 | TRUE
4 | Improves maintenance activities and opportunities | 9 | TRUE
5 | Reliance on foreign utilities | 6 | TRUE
6 | Future expansion opportunities | 2 | TRUE
7 | Personnel / public safety | 10 | TRUE
8 | Reduce reliance on transmission capacitor banks | 4 | TRUE
9 | Reduce outage frequency | 8 | TRUE
10 | Member system acceptance | 7 | TRUE
11 | Existing or future Telecommunications infrastructure | 4 | TRUE
12 | SCADA/Metering | 4 | TRUE
13 | Maximize relief for planning criteria violations | 3 | TRUE
14 | Minimize restoration time | 5 | TRUE
15 | System Protection | 4 | TRUE
16 | Substation Constructability | 4 | TRUE
17 | Transmission Line Constructability | 4 | TRUE
18 | Obj 18 | 1 | FALSE
19 | Obj 19 | 1 | FALSE
20 | Obj 20 | 1 | FALSE
21 | Obj 21 | 1 | FALSE
22 | Obj 22 | 1 | FALSE
23 | Obj 23 | 1 | FALSE
24 | Obj 24 | 1 | FALSE
25 | Obj 25 | 1 | FALSE
26 | Obj 26 | 1 | FALSE
27 | Obj 27 | 1 | FALSE
28 | Obj 28 | 1 | FALSE
29 | Obj 29 | 1 | FALSE
30 | Obj 30 | 1 | FALSE
Project: | 0
Base | Do Nothing
1 | Alt. 1 - Install a 53 MVAR Capacitor Bank on the Cooper 69kV Bus.
2 | Alt. 2 - Construct a 26 mile 161kV line from McCreary County to Cooper.
3 | Alt. 3 - Construct a 48 mile 345kV line from West Garrard to Cooper.
3b | Alt. 3b - Construct a 48 mile 161kV line from West Garrard to Cooper.
4 | Alt. 4 - Construct a 29 mile line from West Garrard to Liberty Jct.
5 | Alt. 5 - Construct a 5 mile 345kV line from KU Alcalde to Cooper.
6 | Alt. 6 - Construct a 29 mile 161 kV line from Wayne County to Cooper.
0 | 0
0 | 0
Help

## Risks
Risk |  | Base | 1 | 2 | 3 | 3b | 4 | 5 | 6 | 0 | 0
Outage approval for dates and durations required |  | None | Low | Medium | High | N/A | High | High | N/A | N/A | N/A
Radially fed load during construction |  | None | Low | Low | Low | N/A | Low | Low | N/A | N/A | N/A
Condemnation requirements |  | None | None | High | High | High | High | High | High | N/A | N/A
Regulatory approval (PSC, CPCN) |  | None | None | High | High | High | High | High | High | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Aggregate Risk |  | None | Low (-) | Medium | High (-) | High | High (-) | High (-) | High | N/A | N/A
Project: | 0
Base | Do Nothing
1 | Alt. 1 - Install a 53 MVAR Capacitor Bank on the Cooper 69kV Bus.
2 | Alt. 2 - Construct a 26 mile 161kV line from McCreary County to Cooper.
3 | Alt. 3 - Construct a 48 mile 345kV line from West Garrard to Cooper.
3b | Alt. 3b - Construct a 48 mile 161kV line from West Garrard to Cooper.
4 | Alt. 4 - Construct a 29 mile line from West Garrard to Liberty Jct.
5 | Alt. 5 - Construct a 5 mile 345kV line from KU Alcalde to Cooper.
6 | Alt. 6 - Construct a 29 mile 161 kV line from Wayne County to Cooper.
0 | 0
0 | 0
Help

## Scoring
Obj # | Objectives | Weight | Applicable | Base | 1 | 2 | 3 | 3b | 4 | 5 | 6 | 0 | 0 | SMEs Assigning Scores
1 | Minimize maintenance costs | 8 | TRUE | 10 | 9 | 7 | 5 | 8 | 7 | 9 | 8
2 | Environmental impact | 3 | TRUE | 10 | 10 | 4 | 1 | 1 | 3 | 6 | 3
3 | Improve operational flexibility | 7 | TRUE | 1 | 3 | 6 | 10 | 8 | 5 | 9 | 9
4 | Improves maintenance activities and opportunities | 9 | TRUE | 1 | 3 | 7 | 10 | 10 | 5 | 8 | 7
5 | Reliance on foreign utilities | 6 | TRUE | 5 | 6 | 7 | 10 | 7 | 8 | 9 | 5
6 | Future expansion opportunities | 2 | TRUE | 5 | 7 | 8 | 10 | 9 | 6 | 10 | 8
7 | Personnel / public safety | 10 | TRUE | 10 | 10 | 8 | 6 | 6 | 7 | 9 | 7
8 | Reduce reliance on transmission capacitor banks | 4 | TRUE | 8 | 1 | 9 | 10 | 9 | 8 | 10 | 9
9 | Reduce outage frequency | 8 | TRUE | 1 | 3 | 7 | 10 | 8 | 5 | 8 | 9
10 | Member system acceptance | 7 | TRUE | 6 | 7 | 8 | 10 | 9 | 8 | 9 | 8
11 | Existing or future Telecommunications infrastructure | 4 | TRUE | 1 | 1 | 7 | 10 | 10 | 7 | 3 | 7
12 | SCADA/Metering | 4 | TRUE | 10 | 9 | 7 | 9 | 9 | 9 | 5 | 9
13 | Maximize relief for planning criteria violations | 3 | TRUE | 8 | 10 | 9 | 10 | 9 | 8 | 9 | 9
14 | Minimize restoration time | 5 | TRUE | 1 | 3 | 7 | 10 | 8 | 5 | 8 | 9
15 | System Protection | 4 | TRUE | 10 | 2 | 7 | 7 | 7 | 7 | 5 | 7
16 | Substation Constructability | 4 | TRUE | 10 | 10 | 9 | 5 | 9 | 7 | 5 | 9
17 | Transmission Line Constructability | 4 | TRUE | 10 | 10 | 7 | 5 | 6 | 6 | 8 | 7
18 | Obj 18 | 1 | FALSE
19 | Obj 19 | 1 | FALSE
20 | Obj 20 | 1 | FALSE
21 | Obj 21 | 1 | FALSE
22 | Obj 22 | 1 | FALSE
23 | Obj 23 | 1 | FALSE
24 | Obj 24 | 1 | FALSE
25 | Obj 25 | 1 | FALSE
26 | Obj 26 | 1 | FALSE
27 | Obj 27 | 1 | FALSE
28 | Obj 28 | 1 | FALSE
29 | Obj 29 | 1 | FALSE
30 | Obj 30 | 1 | FALSE
Combined Score |  |  |  | 541 | 550 | 669 | 757 | 727 | 596 | 727 | 707 | 0 | 0
$/Point |  |  |  | 0 | 2098.1184 | 77311.34 | 243019.6839 | 149172.4951 | 205526.7761 | 77925.5717 | 81466.9484
Project: |  |  | Legend
Base | Do Nothing |  | High Risk
1 | Alt. 1 - Install a 53 MVAR Capacitor Bank on the Cooper 69kV Bus. |  | Medium Risk
2 | Alt. 2 - Construct a 26 mile 161kV line from McCreary County to Cooper. |  | Best Score
3 | Alt. 3 - Construct a 48 mile 345kV line from West Garrard to Cooper. |  | Best $/Point
3b | Alt. 3b - Construct a 48 mile 161kV line from West Garrard to Cooper.
4 | Alt. 4 - Construct a 29 mile line from West Garrard to Liberty Jct.
5 | Alt. 5 - Construct a 5 mile 345kV line from KU Alcalde to Cooper.
6 | Alt. 6 - Construct a 29 mile 161 kV line from Wayne County to Cooper.
0 | 0
0 | 0
Help

## Reduced Set Scoring
Alt | Total EKPC Added | ISY Cost w con. | NPV | $/MW Increase | Overall $/MW
Alt. 2 - Construct a 26 mile 161kV line from McCreary County to Cooper. | 342.6 | 38367663 | 51721286 | 304045 | 112001.22
Alt. 5 - Construct a 5 mile 345kV line from KU Alcalde to Cooper. | 405.7 | 69002499 | 56651891 | 364474 | 170084.83
Alt. 6 - Construct a 29 mile 161 kV line from Wayne County to Cooper. | 333.5 | 42464494 | 57576349 | 362413 | 127312.37
Objectives | Weight | 2 | 5 | 6
Minimize maintenance costs | 8 | 7 | 9 | 8
Environmental impact | 3 | 4 | 6 | 3
Improve operational flexibility | 7 | 6 | 9 | 9
Improves maintenance activities and opportunities | 9 | 7 | 8 | 7
Reliance on foreign utilities | 6 | 7 | 9 | 5
Future expansion opportunities | 2 | 8 | 10 | 8
Personnel / public safety | 10 | 8 | 9 | 7
Reduce reliance on transmission capacitor banks | 4 | 9 | 10 | 9
Reduce outage frequency | 8 | 7 | 8 | 9
Member system acceptance | 7 | 8 | 9 | 8
Existing or future Telecommunications infrastructure | 4 | 7 | 3 | 7
SCADA/Metering | 4 | 7 | 5 | 9
Maximize relief for planning criteria violations | 3 | 9 | 9 | 9
Minimize restoration time | 5 | 7 | 8 | 9
System Protection | 4 | 7 | 5 | 7
Substation Constructability | 4 | 9 | 5 | 9
Transmission Line Constructability | 4 | 7 | 8 | 7
Combined Score |  | 669 | 727 | 707
$/point |  | 77311.34 | 77925.5717 | 81466.9484

## Help
Alternatives Help
Measures Help
Objectives and weighting have been pre-defined by the CMC and should not normally require modification.
If the solution development team identifies a need to add or modify objectives or weighting, please contact the CMC chair.
Risks Help
Scoring Help
Specify up to 10 alternatives
Alternatives may be titled any short name, number, mnemonic desired
  Alternative labels will be used for column headers and should be kept short
If fewer than 10 alternatives are needed, leave those cells blank
Include descriptions for each alternative
Descriptions can be lengthy and will be shown for reference on each worksheet
If fewer than 10 alternatives are defined, unused descriptions may be left blank
Estimated cost should be specified in $
Total Cost is used as a metric on the score sheet so accuracy is important
Where applicable, provide Net Present Value
If NPV is not applicable, provide EKPC Total construction costs, and Member System Total construction costs as relevant
Estimated Implementation Time should be specified in months
If less than 1 month, specify 1
Objectives and weights are CMC-defined
All workbook fields with a light grey background are locked and should not normally need to be modified by workbook users
Clicking on a specific objective will provide factors to consider when evaluating this specific objective
If an objective is not applicable to the defined project, choose FALSE from the dropdown
This will exclude consideration of this objective for the entire scoring process
Alternative ID Defined on Alternatives page
Each alternative should have details included explaining how it meets the relevant objective
If a risk is not relevant to one or more alternatives, choose N/A in the dropdown
Alternative ID Defined on Alternatives page
Dropdown options:
N/A, None, Low, Medium, High
Combined risks for each alternative are aggregated and used on the Scoring page
Objectives and weights are CMC-defined
All workbook fields with a light grey background are locked and should not normally need to be modified by workbook users
Obj#, Objective, Weight, and Applicable fields are defined on the measures page and should never be altered on the Scoring page
These scores will be excluded for all alternatives regardless of the numeric value specified
This alternative was identified as having an overall Medium (-) to Medium (+) risk
This alternative was identified as having an overall High risk
Aggregate score identified as best $/point
Project cost is defined on the Alternatives page
Aggregate score identified as best overall solution
This alternative was identified as having an overall High risk

## Formulas (hidden)
Risks Pulldown/Lookup |  | Risks Array
N/A | -1 | 0 | 1 | 2 | 3 | -1 | 3 | 3 | -1 | -1 | -1
None | 0 | 0 | 1 | 1 | 1 | -1 | 1 | 1 | -1 | -1 | -1
Low | 1 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | -1 | -1
Medium | 2 | 0 | 0 | 3 | 3 | 3 | 3 | 3 | 3 | -1 | -1
High | 3 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
|  | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
Risks Text Lookup |  | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
-1 | N/A | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
0 | None | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
0.5 | Low (-) | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
1 | Low | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
1.4 | Low (+) | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
1.5 | Medium (-) | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
2 | Medium | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1
2.4 | Medium (+) | 0 | 0.5 | 2.25 | 2.5 | 3 | 2.5 | 2.5 | 3 | -1 | -1
2.5 | High (-)
3 | High
Scoring Pulldown
1
2
3
4
5
6
7
8
9
10
Measures Pulldown
TRUE
FALSE