## Summary
Scaled | RICE Loc | Alt | Base EKPC Load | Scaled EKPC Load | Total EKPC Added | Local Area Voltage Support | Local Area Thermal Support
7% | Campbellsville | Base | 906.6878 | 969.8161 | 63.1283 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank
19% | Campbellsville | Cooper Cap | 906.6878 | 1077.9695 | 171.2817 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank | Address Green Co - KU Greensburg TIE limiting element
20% | Campbellsville | W Garrard LibJ | 906.6878 | 1086.9894 | 180.3016 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank | Address Green Co - KU Greensburg TIE limiting element
29% | Campbellsville | McCreary | 906.6878 | 1168.1548 | 261.467 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV
38% | Campbellsville | W Garrard | 906.6878 | 1249.2525 | 342.5647 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank Rebuild N Albany - Upchurch 556 - 3.8 Miles | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Bullitt Co - Cedar Grove 161kV Foreign Limit Somerset - Cabin Hollow 69kV 556 ACSR @212F 100.04%
38% | Campbellsville | Alcalde | 906.6878 | 1249.2525 | 342.5647 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank Rebuild N Albany - Upchurch 556 - 3.8 Miles | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Bullitt Co - Cedar Grove 161kV Foreign Limit Russel County - Wolf Creek 161kV Foregin Limit Taylor Co - Mile Lane 69kV Pineville Artemus 161kV West Lexington 345/138kV XFM Greensburg - Campbellsville 69kV Eliihu 161/69kV XFM
24% | Liberty | Base | 906.6878 | 1123.0618 | 216.374 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank | Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Russel County - Wolf Creek 161kV Foregin Limit
32% | Liberty | Cooper Cap | 906.6878 | 1195.1402 | 288.4524 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Wayne Co XFM Summershade XFM Russel County - Wolf Creek 161kV Foregin Limit
25% | Liberty | W Garrard LibJ | 906.6878 | 1132.0809 | 225.3931 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank | Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Bullitt Co - Cedar Grove 161kV Foreign Limit
38% | Liberty | McCreary | 906.6878 | 1249.2525 | 342.5647 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Wayne Co XFM Summershade XFM
45% | Liberty | W Garrard | 906.6878 | 1312.3824 | 405.6946 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank Rebuild N Albany - Upchurch 556 - 3.8 Miles | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Bullitt Co - Cedar Grove 161kV Foreign Limit Wayne Co XFM Summershade XFM Liberty Jct XFM Somerset - Cabin Hollow 69kV North London - KU North London 69kV Wayne Co - Slat 69kV Cooper - Somerset 69kV North London - County Farm Road 69kV Russel County - olf Creek 161kV Foregin Limit
45% | Liberty | Alcalde | 906.6878 | 1312.3824 | 405.6946 | Switching Procedure - Serve Tommy Gooch on a radial out of KU Standford Rebuild ThreeLinks-McKee 556 - 12.7 miles Wayne Co 19MVAR cap bank North London 25MVAR cap bank Rebuild N Albany - Upchurch 556 - 3.8 Miles | Address Green Co - KU Greensburg 69kV TIE limiting element Adress CT and Disconnect Switch on Denny - Gregory Road 69kV Bullitt Co - Cedar Grove 161kV Foreign Limit Wayne Co XFM Summershade XFM Somerset - Cabin Hollow 69kV North London - KU North London 69kV Wayne Co - Slat 69kV Cooper - Somerset 69kV North London - County Farm Road 69kV Russel County - Wolf Creek 161kV Foregin Limit Liberty Jct - Mt Olive Taylor Co - Mile Lane 69kV Pineville Artemus 161kV West Lexington 345/138kV XFM Greensburg - Campbellsville 69kV North London - Pittsburg KU 69kV Eliihu 161/69kV XFM

## TIE
| AEP | Dayton | DEO&K | SoCO | TVA | LGEE | AEP | Dayton | DEO&K | SoCO | TVA | LGEE
| 205 | 209 | 212 | 346 | 347 | 363
2033W 2023Series_R4_Cooper1&2Retire_25.sav | 1069.84 | 299.8 | -150.27 | 0 | -726.35 | -284.3
2033W 2023Series_R4_Cooper1&2Retire_25%Alcalde.sav | 1067.35 | 297.72 | -151.69 | 0 | -691.4 | -314.65 | -2.49 | -2.08 | -1.42 | 0 | 34.95 | -30.35 | -1.39
2033W 2023Series_R4_Cooper1&2Retire_25%McCreary.sav | 1068.46 | 302.9 | -148.07 | 0 | -754 | -261.43 | -1.38 | 3.1 | 2.2 | 0 | -27.65 | 22.87 | -0.86
2033W 2023Series_R4_Cooper1&2Retire_25%W Garrard LibJ.sav | 1070.62 | 289.47 | -156.78 | 0 | -689.2 | -306.54 | 0.78 | -10.33 | -6.51 | 0 | 37.15 | -22.24 | -1.15
2033W 2023Series_R4_Cooper1&2Retire_25%W Garrard.sav | 1066.82 | 283.89 | -159.93 | 0 | -671.4 | -312.49 | -3.02 | -15.91 | -9.66 | 0 | 54.95 | -28.19 | -1.83
2033W 2023Series_R4_Cooper1&2Retire_25CCAP.sav | 1068.94 | 299.82 | -150.07 | 0 | -725.87 | -284.63 | -0.9 | 0.02 | 0.2 | 0 | 0.48 | -0.33 | -0.53
2033W 2023Series_R4_Cooper1&2Retire_25%W Garrard161.sav | 1070.59 | 293.08 | -154.4 | 0 | -704.58 | -297.06 | 0.75 | -6.72 | -4.13 | 0 | 21.77 | -12.76 | -1.09
2033W 2023Series_R4_Cooper1&2Retire_25%Wayne.sav | 1068.64 | 301.78 | -148.72 | 0 | -743.51 | -269.52 | -1.2 | 1.98 | 1.55 | 0 | -17.16 | 14.78 | -0.05

## Base-Voltage
Scenario | Scaled | Alt | BUS |  |  | RECORD | MIN | MAX | CONTINGENCY | BASE VOLTS | VOLTAGE | CONT VOLTS | VOLTAGE | Project Voltage | Project
S2 | 5% | Campbellsville | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96566 | 66.6305 | 0.88927 | 61.3597 | 0.9075 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9741 | 67.2128 | 0.85456 | 58.9647 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98334 | 67.8505 | 0.85493 | 58.9899
S2 | 20% | Campbellsville | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98337 | 67.8526 | 0.85497 | 58.9929
S2 | 20% | Campbellsville | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98296 | 67.8241 | 0.86472 | 59.666
S2 | 20% | Campbellsville | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96406 | 66.5199 | 0.86128 | 59.428 | 0.8836 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96221 | 66.3922 | 0.88267 | 60.9041 | 0.8963 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96247 | 66.4102 | 0.88295 | 60.9237 | 0.8966 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97275 | 67.1197 | 0.87169 | 60.1466 | 0.8997 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97295 | 67.1333 | 0.87191 | 60.1618 | 0.8999 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96891 | 66.8551 | 0.877 | 60.5133 | 0.9048 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96741 | 66.751 | 0.87942 | 60.6799 | 0.9062 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97168 | 67.0461 | 0.88197 | 60.8558 | 0.9093 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96221 | 66.3922 | 0.88812 | 61.28 | 0.9088 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96247 | 66.4102 | 0.8884 | 61.2995 | 0.9091 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0079 | 69.543 | 0.88008 | 60.7254 | 0.9385 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0095 | 69.6521 | 0.88189 | 60.8504 | 0.9402 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0079 | 69.543 | 0.88346 | 60.9586 | 0.9421 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0079 | 69.543 | 0.88353 | 60.9634 | 0.9422 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0109 | 69.7539 | 0.88358 | 60.9671 | 0.9418 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0097 | 69.6664 | 0.88384 | 60.9849 | 0.9413 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9795 | 67.5857 | 0.88397 | 60.9943 | 0.9244 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0095 | 69.6521 | 0.88526 | 61.0831 | 0.9438 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0095 | 69.6521 | 0.88533 | 61.0879 | 0.9439 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99075 | 68.3615 | 0.88616 | 61.145 | 0.936 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0169 | 163.7188 | 0.88694 | 142.7973 | 0.9453 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0109 | 69.7539 | 0.88695 | 61.1993 | 0.9454 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0109 | 69.7539 | 0.88702 | 61.2041 | 0.9454 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0097 | 69.6664 | 0.88717 | 61.2148 | 0.9448 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0097 | 69.6664 | 0.88724 | 61.2196 | 0.449 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9795 | 67.5857 | 0.88755 | 61.241 | 0.9281 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9795 | 67.5857 | 0.8876 | 61.2447 | 0.9282 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99297 | 68.5152 | 0.88865 | 61.3169 | 0.9383 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99075 | 68.3615 | 0.88908 | 61.3463 | 0.939 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99075 | 68.3615 | 0.88914 | 61.3505 | 0.9391 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99832 | 68.8841 | 0.88954 | 61.378 | 0.9377 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9851 | 67.9717 | 0.89018 | 61.4223 | 0.9303 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99297 | 68.5152 | 0.89156 | 61.5176 | 0.9414 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99297 | 68.5152 | 0.89162 | 61.5218 | 0.9415 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99832 | 68.8841 | 0.89304 | 61.6197 | 0.9414 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99832 | 68.8841 | 0.8931 | 61.6239 | 0.9415 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97935 | 67.5753 | 0.89332 | 61.639 | 0.9364 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9851 | 67.9717 | 0.89373 | 61.6672 | 0.934 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9851 | 67.9717 | 0.89378 | 61.6709 | 0.9341 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95353 | 65.7938 | 0.89558 | 61.7953 | 0.9258 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95353 | 65.7938 | 0.89591 | 61.8177 | 0.9261 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97935 | 67.5753 | 0.89689 | 61.8853 | 0.94 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97935 | 67.5753 | 0.89694 | 61.8886 | 0.9401 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9883 | 68.1928 | 0.89699 | 61.8921 | 0.942 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95577 | 65.9483 | 0.89797 | 61.9598 | 0.9281 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95577 | 65.9483 | 0.89829 | 61.9821 | 0.9284 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97139 | 67.0262 | 0.89835 | 61.9861 | 0.9285 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9883 | 68.1928 | 0.89962 | 62.0741 | 0.9447 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9883 | 68.1928 | 0.89968 | 62.0779 | 0.9448 | Wayne Co 19MVAR cap bank
S2 | 5% | Liberty | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96688 | 66.7144 | 0.89068 | 61.4572 | 0.9089 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95957 | 66.2105 | 0.85431 | 58.9477 | 0.8769 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96751 | 66.7582 | 0.86714 | 59.8325 | 0.8953 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96771 | 66.7718 | 0.86736 | 59.8477 | 0.8956 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96216 | 66.3891 | 0.87024 | 60.0463 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Liberty | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9731 | 67.1436 | 0.87075 | 60.0818 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Liberty | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97313 | 67.1457 | 0.87079 | 60.0847 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Liberty | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96386 | 66.5067 | 0.87248 | 60.2012 | 0.9005 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96239 | 66.4049 | 0.87491 | 60.3688 | 0.9019 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95736 | 66.058 | 0.87589 | 60.4363 | 0.8897 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95762 | 66.076 | 0.87617 | 60.456 | 0.89 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96657 | 66.6935 | 0.87737 | 60.5383 | 0.9049 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97114 | 67.0084 | 0.88021 | 60.7343 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Liberty | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0071 | 69.4872 | 0.8818 | 60.8442 | 0.9394 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0071 | 69.4872 | 0.88285 | 60.9167 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0071 | 69.4872 | 0.88292 | 60.9215 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0086 | 69.5964 | 0.88361 | 60.9689 | 0.9411 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95736 | 66.058 | 0.88372 | 60.9766 | 0.9045 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95762 | 66.076 | 0.884 | 60.9961 | 0.9048 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97742 | 67.442 | 0.88444 | 61.0265 | 0.9239 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0086 | 69.5964 | 0.88466 | 61.0413 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0086 | 69.5964 | 0.88473 | 61.0461 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0101 | 69.6982 | 0.88529 | 61.0853 | 0.9427 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97742 | 67.442 | 0.88549 | 61.0991 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97742 | 67.442 | 0.88555 | 61.1028 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0088 | 69.6087 | 0.88559 | 61.1056 | 0.9422 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0166 | 163.6654 | 0.88634 | 142.6999 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0101 | 69.6982 | 0.88634 | 61.1576 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0101 | 69.6982 | 0.88641 | 61.1623 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0088 | 69.6087 | 0.88663 | 61.1773 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0088 | 69.6087 | 0.8867 | 61.182 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9893 | 68.2618 | 0.88774 | 61.2543 | 0.9369 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9893 | 68.2618 | 0.88865 | 61.3166 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9893 | 68.2618 | 0.88871 | 61.3208 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95407 | 65.8305 | 0.88873 | 61.322
S2 | 20% | Liberty | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99153 | 68.4157 | 0.89023 | 61.4259 | 0.9392 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99688 | 68.7845 | 0.89052 | 61.446 | 0.9378 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98303 | 67.8288 | 0.89064 | 61.4542 | 0.9299 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94945 | 65.5121 | 0.8911 | 61.486 | 0.9225 | North London 25MVAR cap bank
S2 | 20% | Liberty | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99153 | 68.4157 | 0.89113 | 61.488 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99153 | 68.4157 | 0.89119 | 61.4922 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94945 | 65.5121 | 0.89142 | 61.5081 | 0.9228 | North London 25MVAR cap bank
S2 | 20% | Liberty | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99688 | 68.7845 | 0.89157 | 61.5187 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99688 | 68.7845 | 0.89164 | 61.5228 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98303 | 67.8288 | 0.89169 | 61.5263 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98303 | 67.8288 | 0.89174 | 61.53 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.9517 | 65.6672 | 0.8935 | 61.6514 | 0.9248 | North London 25MVAR cap bank
S2 | 20% | Liberty | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97686 | 67.4033 | 0.8935 | 61.6516 | 0.9277 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.9517 | 65.6672 | 0.89382 | 61.6734 | 0.9252 | North London 25MVAR cap bank
S2 | 20% | Liberty | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96741 | 66.751 | 0.89387 | 61.6773 | 0.9252 | North London 25MVAR cap bank
S2 | 20% | Liberty | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97686 | 67.4033 | 0.89454 | 61.7234 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97686 | 67.4033 | 0.89459 | 61.7267 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96239 | 66.4049 | 0.89564 | 61.7991 | 0.9013 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94776 | 65.3953 | 0.897 | 61.8932 | 0.9282 | North London 25MVAR cap bank
S2 | 20% | Liberty | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94776 | 65.3953 | 0.89727 | 61.9115 | 0.9285 | North London 25MVAR cap bank
S2 | 20% | Liberty | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98659 | 68.0746 | 0.89838 | 61.9885 | 0.9428 | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96657 | 66.6935 | 0.89852 | 61.9979 | 0.9043 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Liberty | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97228 | 67.0874 | 0.89888 | 62.0227 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Liberty | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98659 | 68.0746 | 0.89919 | 62.0444 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Liberty | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98659 | 68.0746 | 0.89925 | 62.0481 |  | Wayne Co 19MVAR cap bank
S2-fixes | 24% | Liberty | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9601 | 66.2472 | 0.85701 | 59.1335 | -0.1031
S2-fixes | 24% | Liberty | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97152 | 67.0346 | 0.85726 | 59.1512 | -0.11425
S2-fixes | 24% | Liberty | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97155 | 67.0369 | 0.85731 | 59.1544 | -0.11424
S2-fixes | 24% | Liberty | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9611 | 66.3157 | 0.85918 | 59.2832 | -0.10192
S2-fixes | 24% | Liberty | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96128 | 66.3282 | 0.85938 | 59.2972 | -0.1019
S2-fixes | 24% | Liberty | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95506 | 65.8992 | 0.86633 | 59.7768 | -0.088731
S2-fixes | 24% | Liberty | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95513 | 65.9037 | 0.8664 | 59.7817 | -0.088725
S2-fixes | 24% | Liberty | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96941 | 66.8895 | 0.86749 | 59.857 | -0.10192
S2-fixes | 24% | Liberty | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96483 | 66.5731 | 0.86797 | 59.8896 | -0.096861
S2-fixes | 24% | Liberty | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96151 | 66.3444 | 0.88138 | 60.8155 | -0.080129
S2-fixes | 24% | Liberty | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96178 | 66.363 | 0.88168 | 60.8358 | -0.080105
S2-fixes | 24% | Liberty | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95234 | 65.7112 | 0.88362 | 60.97 | -0.068714
S2-fixes | 24% | Liberty | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9705 | 66.9645 | 0.88757 | 61.2422 | -0.082932
S2-fixes | 24% | Liberty | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98659 | 68.0746 | 0.89333 | 61.6401 | -0.093255
S2-fixes | 24% | Liberty | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96335 | 66.4709 | 0.89356 | 61.6554 | -0.06979
S2-fixes | 24% | Liberty | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96731 | 66.7443 | 0.89614 | 61.8334 | -0.071173
S2-fixes | 24% | Liberty | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96324 | 66.4638 | 0.89726 | 61.9113 | -0.065979
S2-fixes | 24% | Liberty | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96626 | 66.6722 | 0.89923 | 62.0472 | -0.067029
S2-fixes | 24% | Liberty | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96647 | 66.6863 | 0.89946 | 62.0624 | -0.067013
S2-fixes | 24% | Liberty | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.99233 | 68.4708 | 0.89968 | 62.0779 | -0.092651

## Base-Thermal
Scenario | Scaled | Alt | BRANCH | [6 empty] | CONTINGENCY | MVAFLOW | AMPFLOW | RATE RATE1/RATE2 | % FLOW | OWNER | Project % | Project
S2 | 20% | Campbellsville | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 90.168 | 90.168 | 88 | 102.4636 | TIE | <100 % | Address KU limit
S2 | 20% | Campbellsville | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 88.7092 | 88.7092 | 88 | 100.806 | TIE | <100 % | Address KU limit
S1 | 20% | Liberty | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 90.5555 | 90.5555 | 89 | 101.7478 | EKPC | <100% | Address CT and Disconnect Switch
S2-fixes | 24% | Liberty | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 90.4777 | 90.4777 | 89 | 101.6603 | EKPC
S2-fixes | 24% | Liberty | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 90.4562 | 90.4562 | 89 | 101.6362 | EKPC
S2-fixes | 24% | Liberty | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 90.1756 | 90.1756 | 89 | 101.3209 | EKPC

## Base N-1-1 Voltage
Scenario | Scaled | Alt | First Level Scenario | Bus # | Bus Name | Base kV | Area | Bus Type | Cont Name | Orig Case Cont Volt | Base Volt | Cont Volt | %Vdrop | Scaled Volt | Scaled % | Base Load | Scaled Load | Total
S1 | 20% | Campbellsville | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9751 | 0.956 | 0.8781 | 7.792 | 0.9271 | 7 | 906.6878 | 969.8161 | 63.1283
S1 | 20% | Campbellsville | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9751 | 0.956 | 0.8781 | 7.792 | 0.9271 | 7
S1 | 20% | Campbellsville | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9751 | 0.956 | 0.8781 | 7.792 | 0.9232 | 8
S1 | 20% | Campbellsville | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9751 | 0.956 | 0.8781 | 7.792 | 0.9232 | 8
S1 | 20% | Liberty | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9806 | 0.9647 | 0.9216 | 4.31 | 0.9462 | 20
S1 | 20% | Liberty | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9806 | 0.9647 | 0.9216 | 4.309 | 0.9462 | 20
S1 | 20% | Liberty | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9806 | 0.9647 | 0.9216 | 4.31 | 0.9237 | 25
S1 | 20% | Liberty | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9806 | 0.9647 | 0.9216 | 4.309 | 0.9237 | 25
S1 | 20% | Liberty | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9806 | 0.9647 | 0.9216 | 4.31 | 0.9275 | 24 | 906.6878 | 1123.0618 | 216.374
S1 | 20% | Liberty | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9806 | 0.9647 | 0.9216 | 4.309 | 0.9275 | 24
S1 | 24% | Liberty | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9578 | 0.9824 | 0.9229 | 5.958
S1 | 24% | Liberty | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9578 | 0.9824 | 0.9229 | 5.957

## Base N-1-1 Thermal
Scenario | Scaled | Alt | Scenar_1 | First Level Scenario | Monitored Facility | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Base Flow (MVA) | Cont Flow (MVA) | Orig Case Cont AC %Loading | Final AC %Loading | 8% Load | Project % | Project
S1 | 20% | Campbellsville | 2033W VM&THERM | EKPC_P1-2_LIB-CAS-MAR161_SRT-A | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 252.8 | 373 | 94.15 | 111.68 | 345 | <100 % | Address KU limit
S1 | 20% | Campbellsville | 2033W VM&THERM | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | EKPC_P1-2_LIB-CAS-MAR161_SRT-A | 314.8 | 372 | 75.69 | 111.37 | 345 | <100 % | Address KU limit
S1 | 20% | Liberty | 2033W VM&THERM | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | EKPC_P1-2_LIB-S CAS | 285.7 | 336.6 | 69.58 | 100.79
|  |  |  | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | EKPC_P1-2_LIB-S CAS | 291.7 | 342.7 | 70.76 | 102.62
|  |  |  | EKPC_P1-2_LIB-S CAS | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 342796 | 5RUSSEL CO J | 360448 | 5WOLF CRK HP | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 235.8 | 342.4 | 87.29 | 102.5

## N-1 Voltage
Scenario | Scaled | RICE | Alt | BUS |  |  | RECORD | MIN | MAX | CONTINGENCY | BASE VOLTS | VOLTAGE | CONT VOLTS | Project Voltage | Project
S2 | 5% | Campbellsville | CCAP | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97284 | 67.1261 | 0.89875 | 0.9167 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98168 | 67.7358 | 0.86949 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | CCAP | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99036 | 68.3347 | 0.87 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | CCAP | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99039 | 68.3367 | 0.87004 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | CCAP | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99047 | 68.3422 | 0.87947 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | CCAP | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99451 | 68.6214 | 0.89817 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | CCAP | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97178 | 67.0527 | 0.87197 | 0.8939 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9809 | 67.682 | 0.88132 | 0.9089 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.98109 | 67.6954 | 0.88154 | 0.9091 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97707 | 67.4176 | 0.88657 | 0.9139 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97555 | 67.3131 | 0.88896 | 0.9153 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97998 | 67.6188 | 0.8917 | 0.9186 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97023 | 66.9459 | 0.89309 | 0.9065 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97049 | 66.9637 | 0.89337 | 0.9068 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0124 | 69.8552 | 0.89703 | 0.95779 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97023 | 66.9459 | 0.89743 | 0.9177 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97049 | 66.9637 | 0.8977 | 0.918 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | CCAP | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.014 | 69.9638 | 0.8988 | 0.95612 | Wayne Co 19MVAR cap bank
S2 | 5% | Campbellsville | W Garrard LibJ | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97052 | 66.9658 | 0.89438 | 0.9149 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97013 | 66.9388 | 0.86822 | 0.9007 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98269 | 67.8055 | 0.88039 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard LibJ | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97831 | 67.5033 | 0.8804 | 0.9135 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9785 | 67.5168 | 0.88061 | 0.9137 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99143 | 68.4088 | 0.881 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard LibJ | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99146 | 68.4108 | 0.88104 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard LibJ | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97476 | 67.2587 | 0.88565 | 0.9185 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0096 | 69.6607 | 0.88619 | 0.9493 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0112 | 69.7697 | 0.88799 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97331 | 67.1581 | 0.88804 | 0.9199 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96819 | 66.8053 | 0.88943 | 0.9132 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0126 | 69.8712 | 0.88967 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96845 | 66.8231 | 0.88971 | 0.9135 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0096 | 69.6607 | 0.88974 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0096 | 69.6607 | 0.88981 | 0.9482 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0114 | 69.7849 | 0.88989 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9824 | 67.7857 | 0.89004 | 0.9353 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99147 | 68.4112 | 0.89024 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard LibJ | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97769 | 67.4609 | 0.89077 | 0.9233 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0112 | 69.7697 | 0.89153 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0112 | 69.7697 | 0.8916 | 0.9499 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99261 | 68.4904 | 0.89162 | 0.9451 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0178 | 163.8722 | 0.8932 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0126 | 69.8712 | 0.8932 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0126 | 69.8712 | 0.89327 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0114 | 69.7849 | 0.89339 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0114 | 69.7849 | 0.89346 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9824 | 67.7857 | 0.89376 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9824 | 67.7857 | 0.89381 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99484 | 68.6438 | 0.89409 | 0.9474 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99261 | 68.4904 | 0.89467 | 0.9481 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99261 | 68.4904 | 0.89473 | 0.9445 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0008 | 69.0555 | 0.89564 | 0.9486 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98798 | 68.1705 | 0.8962 | 0.9411 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96819 | 66.8053 | 0.89653 | 0.9222 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96845 | 66.8231 | 0.89681 | 0.9225 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99484 | 68.6438 | 0.89714 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99484 | 68.6438 | 0.8972 | 0.9468 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98244 | 67.7884 | 0.89929 | 0.9392 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0008 | 69.0555 | 0.89929 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0008 | 69.0555 | 0.89936 | 0.9474 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98798 | 68.1705 | 0.89989 | 0.9446 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard LibJ | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98798 | 68.1705 | 0.89994 | 0.9399 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard LibJ | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96758 | 66.7631 | 0.8417 | 58.0772 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98659 | 68.0744 | 0.84878 | 58.5656 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9768 | 67.3989 | 0.8488 | 58.5674 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98662 | 68.0768 | 0.84883 | 58.5692 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9864 | 68.0615 | 0.85993 | 59.335 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0061 | 69.4229 | 0.85994 | 59.3359 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0078 | 69.5414 | 0.86195 | 59.4747 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97273 | 67.1186 | 0.86363 | 59.5902 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0061 | 69.4229 | 0.86373 | 59.5971 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0061 | 69.4229 | 0.8638 | 59.6023 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0094 | 69.652 | 0.86383 | 59.6043 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97295 | 67.1333 | 0.86387 | 59.6068 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0079 | 69.5465 | 0.86395 | 59.6128 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98579 | 68.0193 | 0.86436 | 59.6406 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96348 | 66.4804 | 0.8655 | 59.7197 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0078 | 69.5414 | 0.86573 | 59.7353 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0078 | 69.5414 | 0.8658 | 59.7404 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96377 | 66.4999 | 0.86582 | 59.7414 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97731 | 67.4347 | 0.86651 | 59.7894 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98822 | 68.1869 | 0.86713 | 59.8319 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.017 | 163.74 | 0.86759 | 139.6824 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0094 | 69.652 | 0.8676 | 59.8643 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98579 | 68.0193 | 0.86767 | 59.8694 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0094 | 69.652 | 0.86767 | 59.8694 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0079 | 69.5465 | 0.86769 | 59.8705 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98579 | 68.0193 | 0.86774 | 59.8739 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0079 | 69.5465 | 0.86776 | 59.8756 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96935 | 66.8852 | 0.86947 | 59.9931 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98822 | 68.1869 | 0.87043 | 60.0599 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97731 | 67.4347 | 0.87044 | 60.0603 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97731 | 67.4347 | 0.8705 | 60.0643 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98822 | 68.1869 | 0.8705 | 60.0644 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99648 | 68.7569 | 0.87104 | 60.1014 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96792 | 66.7866 | 0.87212 | 60.1761 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9834 | 67.8544 | 0.87338 | 60.2632 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97162 | 67.0416 | 0.87385 | 60.2958 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99648 | 68.7569 | 0.87491 | 60.3688 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99648 | 68.7569 | 0.87498 | 60.3734 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98228 | 67.7775 | 0.87513 | 60.3842 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9834 | 67.8544 | 0.87727 | 60.5319 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9834 | 67.8544 | 0.87733 | 60.5359 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97791 | 67.4761 | 0.87797 | 60.58 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98228 | 67.7775 | 0.87815 | 60.5926 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98228 | 67.7775 | 0.87821 | 60.5967 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98586 | 68.0242 | 0.87915 | 60.6613 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99043 | 68.3396 | 0.8817 | 60.837 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97791 | 67.4761 | 0.88186 | 60.8486 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97791 | 67.4761 | 0.88192 | 60.8522 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98586 | 68.0242 | 0.88216 | 60.8688 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98586 | 68.0242 | 0.88222 | 60.8729 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96348 | 66.4804 | 0.88229 | 60.8779 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96377 | 66.4999 | 0.8826 | 60.8992 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98605 | 68.0377 | 0.88705 | 61.2067 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96792 | 66.7866 | 0.88732 | 61.2254 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96717 | 66.7345 | 0.88805 | 61.2754 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98579 | 68.0193 | 0.88831 | 61.2936 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97162 | 67.0416 | 0.88938 | 61.3675 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99081 | 68.3659 | 0.88945 | 61.372 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98579 | 68.0193 | 0.88955 | 61.3792 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99068 | 68.3568 | 0.89002 | 61.4116 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98605 | 68.0377 | 0.89091 | 61.4726 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98605 | 68.0377 | 0.89096 | 61.4762 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98822 | 68.1869 | 0.89101 | 61.4796 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98822 | 68.1869 | 0.89225 | 61.565 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99081 | 68.3659 | 0.89226 | 61.5662 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99081 | 68.3659 | 0.89232 | 61.57 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0079 | 69.5465 | 0.89234 | 61.5713 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99068 | 68.3568 | 0.89282 | 61.6044 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99068 | 68.3568 | 0.89287 | 61.6082 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95646 | 65.9961 | 0.89375 | 61.669 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95646 | 65.9961 | 0.89408 | 61.6915 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96935 | 66.8852 | 0.89468 | 61.7328 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97532 | 67.2971 | 0.89577 | 61.8081 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95889 | 66.1631 | 0.89635 | 61.8478 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95889 | 66.1631 | 0.89667 | 61.8702 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97535 | 67.2988 | 0.89673 | 61.8742 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98228 | 67.7775 | 0.89686 | 61.8833 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96171 | 66.3583 | 0.89772 | 61.9427 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96247 | 66.4101 | 0.89776 | 61.9454 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96114 | 66.3188 | 0.89791 | 61.9557 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98228 | 67.7775 | 0.89798 | 61.9609 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96905 | 66.8641 | 0.89847 | 61.9942 | N-1-1 Limit
S2 | 30% | Campbellsville | W Garrard LibJ | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96167 | 66.3554 | 0.89848 | 61.9949 | N-1-1 Limit
S2 | 5% | Campbellsville | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97338 | 67.1633 | 0.89612 | 0.9142 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98271 | 67.8067 | 0.8665 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99168 | 68.4261 | 0.86698 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99171 | 68.4281 | 0.86702 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97328 | 67.1565 | 0.87031 | 0.8898 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99148 | 68.4124 | 0.87652 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.98058 | 67.6597 | 0.88525 | 0.9086 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.98077 | 67.6732 | 0.88547 | 0.9089 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97725 | 67.4305 | 0.89048 | 0.9137 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.971 | 66.9989 | 0.89147 | 0.9024 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97126 | 67.0167 | 0.89175 | 0.9027 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97588 | 67.3358 | 0.89285 | 0.9151 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99508 | 68.6603 | 0.89533 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0115 | 69.7914 | 0.89558 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.98032 | 67.642 | 0.89568 | 0.9184 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.013 | 69.9002 | 0.89736 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0115 | 69.7914 | 0.89876 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0115 | 69.7914 | 0.89883 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0145 | 70.0015 | 0.89902 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98589 | 68.0265 | 0.89904 | 0.9371 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0132 | 69.912 | 0.89918 | >0.95 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99375 | 68.5684 | 0.89979 | 0.9479 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98572 | 68.0145 | 0.83005 | >0.95 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98575 | 68.017 | 0.8301 | >0.95 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97557 | 67.3141 | 0.83026 | >0.95 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98518 | 67.9775 | 0.84165 | >0.95 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97067 | 66.9763 | 0.84358 | 0.8689 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98866 | 68.2179 | 0.86422 | >0.95 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96619 | 66.6669 | 0.86733 | 0.883 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96647 | 66.6863 | 0.86764 | 0.8833 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97484 | 67.2638 | 0.86882 | 0.9001 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97505 | 67.2785 | 0.86906 | 0.9004 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.008 | 69.551 | 0.87063 | 0.9294 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0097 | 69.6693 | 0.87262 | 0.9312 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9868 | 68.0892 | 0.87389 | 0.9243 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.008 | 69.551 | 0.87392 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.008 | 69.551 | 0.874 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0113 | 69.7797 | 0.87448 | 0.933 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0097 | 69.6705 | 0.87455 | 0.9323 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97171 | 67.0478 | 0.87462 | 0.9057 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0097 | 69.6693 | 0.8759 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0097 | 69.6693 | 0.87598 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98923 | 68.2566 | 0.87663 | 0.9269 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98067 | 67.6659 | 0.87666 | 0.9173 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9868 | 68.0892 | 0.87675 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9868 | 68.0892 | 0.87681 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97037 | 66.9557 | 0.87726 | 0.9072 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.018 | 163.8917 | 0.87775 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0113 | 69.7797 | 0.87775 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0097 | 69.6705 | 0.87779 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0113 | 69.7797 | 0.87782 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0097 | 69.6705 | 0.87786 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97412 | 67.214 | 0.8791 | 0.9097 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98923 | 68.2566 | 0.87948 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98923 | 68.2566 | 0.87955 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98067 | 67.6659 | 0.88006 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98067 | 67.6659 | 0.88012 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99933 | 68.9538 | 0.88143 | 0.9298 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98673 | 68.0842 | 0.88344 | 0.9238 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98289 | 67.8195 | 0.88386 | 0.9295 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99933 | 68.9538 | 0.88479 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99933 | 68.9538 | 0.88485 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98289 | 67.8195 | 0.88645 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98289 | 67.8195 | 0.88651 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98673 | 68.0842 | 0.88682 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98673 | 68.0842 | 0.88688 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96619 | 66.6669 | 0.88729 | 0.9105 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96647 | 66.6863 | 0.8876 | 0.9108 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98148 | 67.7224 | 0.88783 | 0.923 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98646 | 68.066 | 0.88784 | 0.9333 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9868 | 68.0892 | 0.88826 | 0.8951 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97037 | 66.9557 | 0.8891 | 0.8958 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9868 | 68.0892 | 0.8895 | 0.8963 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98646 | 68.066 | 0.89042 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98646 | 68.066 | 0.89048 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98923 | 68.2566 | 0.89095 | 0.8977 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97412 | 67.214 | 0.8912 | 0.898 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98148 | 67.7224 | 0.89121 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98148 | 67.7224 | 0.89126 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98923 | 68.2566 | 0.89219 | 0.899 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0097 | 69.6705 | 0.89228 | 0.8991 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96963 | 66.9045 | 0.89246 | 0.8934 | All of other specified Projects
S2 | 30% | Campbellsville | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97171 | 67.0478 | 0.89643 | 0.9371 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | W Garrard | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97876 | 67.5342 | 0.89644 | 0.9023 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98289 | 67.8195 | 0.8968 | 0.8979 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98959 | 68.2819 | 0.89681 | 0.9317 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95978 | 66.2245 | 0.89692 | 0.9269 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95978 | 66.2245 | 0.89725 | 0.9272 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9915 | 68.4135 | 0.89791 | 0.9386 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98289 | 67.8195 | 0.89793 | 0.8991 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96513 | 66.5942 | 0.89812 | 0.9041 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96592 | 66.6483 | 0.89816 | 0.9042 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96455 | 66.554 | 0.89829 | 0.9043 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99136 | 68.4041 | 0.89842 | 0.9388 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96508 | 66.5905 | 0.89885 | 0.9049 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97248 | 67.1014 | 0.89914 | 0.905 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.96219 | 66.391 | 0.8995 | 0.9294 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96219 | 66.391 | 0.89983 | 0.9297 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | W Garrard | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97852 | 67.5181 | 0.89989 | 0.9298 | North London 25MVAR cap bank
S2 | 5% | Campbellsville | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96886 | 66.8515 | 0.8926 |  | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9776 | 67.4543 | 0.8596 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98666 | 68.0799 | 0.86002 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98669 | 68.0819 | 0.86006 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96737 | 66.7487 | 0.86499 | 0.8847 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98642 | 68.0633 | 0.8697 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | McCreary | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97578 | 67.3287 | 0.87663 | 0.9004 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97597 | 67.3422 | 0.87684 | 0.9006 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97209 | 67.0741 | 0.88191 | 0.9056 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0069 | 69.4746 | 0.88274 | 0.9391 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97061 | 66.9721 | 0.88431 | 0.9069 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0085 | 69.5838 | 0.88455 | 0.9408 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0099 | 69.6857 | 0.88623 | 0.9423 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96547 | 66.6171 | 0.88629 | 0.8974 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0087 | 69.6002 | 0.88647 | 0.9418 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96573 | 66.635 | 0.88657 | 0.8977 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98033 | 67.643 | 0.88671 | 0.9249 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97495 | 67.2714 | 0.88696 | 0.9101 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99024 | 68.3268 | 0.8885 | 0.9365 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98998 | 68.3088 | 0.88879 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0069 | 69.4746 | 0.88888 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0069 | 69.4746 | 0.88895 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0085 | 69.5838 | 0.89068 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0085 | 69.5838 | 0.89075 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99247 | 68.4805 | 0.89099 | 0.9388 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99851 | 68.8969 | 0.89225 | 0.9382 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0153 | 163.459 | 0.89234 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0099 | 69.6857 | 0.89235 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0099 | 69.6857 | 0.89242 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0087 | 69.6002 | 0.89253 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0087 | 69.6002 | 0.8926 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96547 | 66.6171 | 0.89289 | 0.9095 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98592 | 68.0286 | 0.89289 | 0.9308 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98033 | 67.643 | 0.89299 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98033 | 67.643 | 0.89305 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96573 | 66.635 | 0.89317 | 0.9098 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99024 | 68.3268 | 0.89382 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99024 | 68.3268 | 0.89388 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98052 | 67.6558 | 0.89603 | 0.9368 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99247 | 68.4805 | 0.89629 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99247 | 68.4805 | 0.89635 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99851 | 68.8969 | 0.89849 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99851 | 68.8969 | 0.89855 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98804 | 68.1745 | 0.89913 | 0.9424 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98592 | 68.0286 | 0.89913 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98592 | 68.0286 | 0.89919 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95729 | 66.0533 | 0.89943 | 0.9243 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95729 | 66.0533 | 0.89975 | 0.9246 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9807 | 67.6681 | 0.82106 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98073 | 67.6706 | 0.82111 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97054 | 66.9671 | 0.82137 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98021 | 67.6342 | 0.83287 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96419 | 66.5293 | 0.83758 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0032 | 69.2174 | 0.8539 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98379 | 67.8813 | 0.85584 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0049 | 69.3364 | 0.85593 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0065 | 69.4473 | 0.85782 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.005 | 69.3448 | 0.85794 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98349 | 67.8608 | 0.85849 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96957 | 66.9 | 0.85899 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96978 | 66.9148 | 0.85923 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97483 | 67.2634 | 0.86083 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97837 | 67.5079 | 0.86112 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0032 | 69.2174 | 0.86118 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0032 | 69.2174 | 0.86126 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98592 | 68.0287 | 0.86128 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97856 | 67.5208 | 0.86133 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96011 | 66.2474 | 0.86151 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96039 | 66.267 | 0.86182 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0049 | 69.3364 | 0.86319 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0049 | 69.3364 | 0.86327 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96603 | 66.6558 | 0.86486 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98349 | 67.8608 | 0.86499 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98349 | 67.8608 | 0.86506 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0141 | 163.2623 | 0.86506 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0065 | 69.4473 | 0.86506 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.005 | 69.3448 | 0.86514 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0065 | 69.4473 | 0.86514 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99382 | 68.5736 | 0.86519 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.005 | 69.3448 | 0.86522 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96458 | 66.5557 | 0.86753 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98093 | 67.6842 | 0.86775 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98592 | 68.0287 | 0.86776 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98592 | 68.0287 | 0.86783 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97483 | 67.2634 | 0.86818 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97483 | 67.2634 | 0.86824 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96974 | 66.9123 | 0.86862 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96981 | 66.9169 | 0.86869 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96821 | 66.8062 | 0.86917 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98033 | 67.6426 | 0.86945 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97555 | 67.3131 | 0.87249 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99382 | 68.5736 | 0.87252 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99382 | 68.5736 | 0.87259 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98391 | 67.8898 | 0.87349 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98093 | 67.6842 | 0.87503 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98093 | 67.6842 | 0.87509 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98033 | 67.6426 | 0.87543 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98033 | 67.6426 | 0.87549 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96011 | 66.2474 | 0.87782 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96039 | 66.267 | 0.87813 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98391 | 67.8898 | 0.87944 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98391 | 67.8898 | 0.87951 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97555 | 67.3131 | 0.87972 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97555 | 67.3131 | 0.87978 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98371 | 67.8761 | 0.88163 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96458 | 66.5557 | 0.88344 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98885 | 68.2309 | 0.88386 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98873 | 68.2227 | 0.88448 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96821 | 66.8062 | 0.88542 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96404 | 66.5185 | 0.88677 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98349 | 67.8608 | 0.88745 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98349 | 67.8608 | 0.88869 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98371 | 67.8761 | 0.88879 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98371 | 67.8761 | 0.88884 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97445 | 67.2368 | 0.88919 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98885 | 68.2309 | 0.88952 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98885 | 68.2309 | 0.88958 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95957 | 66.2101 | 0.88998 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96036 | 66.2649 | 0.89004 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95892 | 66.1656 | 0.89009 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98873 | 68.2227 | 0.89009 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98592 | 68.0287 | 0.89015 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98873 | 68.2227 | 0.89015 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95945 | 66.2023 | 0.89066 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96603 | 66.6558 | 0.89085 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95415 | 65.836 | 0.89092 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95415 | 65.836 | 0.89124 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98592 | 68.0287 | 0.89139 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.005 | 69.3448 | 0.89148 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96778 | 66.7766 | 0.8919 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95657 | 66.0035 | 0.89352 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95657 | 66.0035 | 0.89384 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97331 | 67.1584 | 0.8939 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96515 | 66.5954 | 0.89399 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96566 | 66.6307 | 0.89454 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.95892 | 66.1656 | 0.89599 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98033 | 67.6426 | 0.896 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.95957 | 66.2101 | 0.89628 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.95945 | 66.2023 | 0.89656 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.96036 | 66.2649 | 0.8967 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98033 | 67.6426 | 0.89713 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95244 | 65.7181 | 0.89733 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95244 | 65.7181 | 0.8976 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97483 | 67.2634 | 0.89882 |  | N-1-1 Limit
S2 | 30% | Campbellsville | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98391 | 67.8898 | 0.89993 |  | N-1-1 Limit
S2 | 5% | Campbellsville | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9682 | 66.8061 | 0.89142 | 0.9096 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 5% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94248 | 65.031 | 0.89817
S2 | 5% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94378 | 65.121 | 0.89954
S2 | 20% | Campbellsville | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97765 | 67.4575 | 0.859 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98676 | 68.0863 | 0.85941 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98679 | 68.0883 | 0.85945 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96764 | 66.7674 | 0.86475 | 0.8869 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98647 | 68.0665 | 0.86911 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97577 | 67.3282 | 0.87708 | 0.9008 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97597 | 67.3418 | 0.8773 | 0.901 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97216 | 67.0789 | 0.88236 | 0.9059 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9707 | 66.9784 | 0.88476 | 0.9073 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96562 | 66.628 | 0.88605 | 0.8971 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96588 | 66.6459 | 0.88634 | 0.8974 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97504 | 67.2779 | 0.88742 | 0.9104 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.93794 | 64.7177 | 0.8879
S2 | 20% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0096 | 69.659 | 0.88805 | 0.9445 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98996 | 68.3071 | 0.88821 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 20% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.93944 | 64.8214 | 0.88949
S2 | 20% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0111 | 69.7679 | 0.88984 | 0.9462 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98229 | 67.7781 | 0.89146 | 0.9296 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0096 | 69.659 | 0.89146 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0126 | 69.8694 | 0.89152 | 0.9477 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0096 | 69.659 | 0.89153 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0113 | 69.7809 | 0.89174 | 0.9472 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99209 | 68.454 | 0.89323 | 0.9413 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0111 | 69.7679 | 0.89325 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0111 | 69.7679 | 0.89332 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96562 | 66.628 | 0.89333 | 0.9098 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96588 | 66.6459 | 0.89361 | 0.9101 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 20% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.93794 | 64.7177 | 0.89388
S2 | 20% | Campbellsville | Alcalde | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0179 | 163.8772 | 0.89491 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0126 | 69.8694 | 0.89492 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0126 | 69.8694 | 0.89499 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98229 | 67.7781 | 0.89504 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98229 | 67.7781 | 0.89509 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0113 | 69.7809 | 0.89511 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0113 | 69.7809 | 0.89518 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.93944 | 64.8214 | 0.89546
S2 | 20% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99431 | 68.6074 | 0.8957 | 0.9436 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99209 | 68.454 | 0.89616 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99209 | 68.454 | 0.89622 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0008 | 69.0535 | 0.89724 | 0.9433 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98787 | 68.163 | 0.89761 | 0.9355 | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.9474 | 65.3708 | 0.89791
S2 | 20% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99431 | 68.6074 | 0.89863 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99431 | 68.6074 | 0.89869 |  | Wayne Co 19MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95708 | 66.0389 | 0.89913 | 0.9236 | North London 25MVAR cap bank
S2 | 20% | Campbellsville | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95708 | 66.0389 | 0.89945 | 0.924 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98106 | 67.693 | 0.82156 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 30% | Campbellsville | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98109 | 67.6954 | 0.82162 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 30% | Campbellsville | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97085 | 66.989 | 0.82187 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 30% | Campbellsville | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98052 | 67.6558 | 0.83337 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 30% | Campbellsville | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9648 | 66.5712 | 0.83771 | 0.8633 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98402 | 67.8976 | 0.85632 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 30% | Campbellsville | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96987 | 66.921 | 0.85995 | 0.8918 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.97008 | 66.9358 | 0.8602 | 0.892 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9606 | 66.2813 | 0.86163 | 0.8775 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96088 | 66.3008 | 0.86195 | 0.8778 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0062 | 69.4279 | 0.86259 | 0.9215 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.93157 | 64.2784 | 0.86397
S2 | 30% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0079 | 69.5465 | 0.86459 | 0.9233 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.93321 | 64.3917 | 0.86574
S2 | 30% | Campbellsville | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96642 | 66.6829 | 0.86582 | 0.8974 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0062 | 69.4279 | 0.86619 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0062 | 69.4279 | 0.86627 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0095 | 69.657 | 0.86646 | 0.9251 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.008 | 69.5499 | 0.86659 | 0.9245 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98545 | 67.996 | 0.86674 | 0.9173 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0079 | 69.5465 | 0.86819 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0079 | 69.5465 | 0.86826 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96499 | 66.5845 | 0.86848 | 0.899 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97728 | 67.4323 | 0.86866 | 0.9096 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98788 | 68.1636 | 0.8695 | 0.9199 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98545 | 67.996 | 0.86989 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98545 | 67.996 | 0.86996 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0171 | 163.7504 | 0.87005 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0095 | 69.657 | 0.87006 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0095 | 69.657 | 0.87013 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96863 | 66.8356 | 0.87014 | 0.9013 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.008 | 69.5499 | 0.87015 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.008 | 69.5499 | 0.87022 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97728 | 67.4323 | 0.87241 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97728 | 67.4323 | 0.87247 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98788 | 68.1636 | 0.87265 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98788 | 68.1636 | 0.87271 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99654 | 68.7614 | 0.87339 | 0.9221 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.94192 | 64.9925 | 0.87514
S2 | 30% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98336 | 67.8521 | 0.87551 | 0.9161 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99654 | 68.7614 | 0.87709 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99654 | 68.7614 | 0.87715 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98176 | 67.7412 | 0.8773 | 0.9232 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.93157 | 64.2784 | 0.87763
S2 | 30% | Campbellsville | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9606 | 66.2813 | 0.87875 | 0.9024 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96088 | 66.3008 | 0.87906 | 0.9027 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98336 | 67.8521 | 0.87923 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98336 | 67.8521 | 0.87929 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.93321 | 64.3917 | 0.87937
S2 | 30% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9778 | 67.4682 | 0.87998 | 0.9155 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98176 | 67.7412 | 0.88017 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98176 | 67.7412 | 0.88023 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98533 | 67.988 | 0.88131 | 0.927 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96499 | 66.5845 | 0.88357 | 0.8904 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9778 | 67.4682 | 0.8837 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9778 | 67.4682 | 0.88375 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98533 | 67.988 | 0.88417 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98533 | 67.988 | 0.88422 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96863 | 66.8356 | 0.88555 | 0.8925 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96366 | 66.4925 | 0.88599 | 0.8869 | All of other specified Projects
S2 | 30% | Campbellsville | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.95363 | 65.8005 | 0.88783
S2 | 30% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98545 | 67.996 | 0.88795 | 0.8974 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94192 | 64.9925 | 0.88863
S2 | 30% | Campbellsville | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98594 | 68.0298 | 0.88904 | 0.9242 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98545 | 67.996 | 0.8892 | 0.896 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97322 | 67.1525 | 0.8892 | 0.8953 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95905 | 66.1743 | 0.89053 | 0.8968 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95983 | 66.2281 | 0.89058 | 0.8968 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98788 | 68.1636 | 0.89065 | 0.8974 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95845 | 66.1328 | 0.89069 | 0.8969 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95425 | 65.8429 | 0.89093 | 0.9149 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96642 | 66.6829 | 0.89097 | 0.9322 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 30% | Campbellsville | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95425 | 65.8429 | 0.89125 | 0.9211 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95898 | 66.1695 | 0.89126 | 0.8975 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99038 | 68.336 | 0.89167 | 0.9326 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98788 | 68.1636 | 0.89189 | 0.8987 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96676 | 66.7064 | 0.89192 | 0.898 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.008 | 69.5499 | 0.89198 | 0.8987 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99025 | 68.3271 | 0.89222 | 0.9329 | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98594 | 68.0298 | 0.89272 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98594 | 68.0298 | 0.89277 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.94526 | 65.2227 | 0.89308
S2 | 30% | Campbellsville | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95667 | 66.0104 | 0.89353 | 0.9236 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95667 | 66.0104 | 0.89385 | 0.9239 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97325 | 67.1544 | 0.89391 | 0.924 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96416 | 66.5272 | 0.89396 | 0.9 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95845 | 66.1328 | 0.89406
S2 | 30% | Campbellsville | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99038 | 68.336 | 0.89434 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99038 | 68.336 | 0.89439 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96467 | 66.5625 | 0.89451 | 0.9005 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95898 | 66.1695 | 0.89463
S2 | 30% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95905 | 66.1743 | 0.89465
S2 | 30% | Campbellsville | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99025 | 68.3271 | 0.89488 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99025 | 68.3271 | 0.89493 |  | Wayne Co 19MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95983 | 66.2281 | 0.89533
S2 | 30% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98176 | 67.7412 | 0.8965 | 0.8976 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95264 | 65.7318 | 0.89734 | 0.9273 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95264 | 65.7318 | 0.89761 | 0.9276 | North London 25MVAR cap bank
S2 | 30% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98176 | 67.7412 | 0.89763 | 0.8988 | Rebuild N Albany-Upchurch 556 -3.8 miles
S2 | 30% | Campbellsville | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.9508 | 65.605 | 0.89895
S2 | 30% | Campbellsville | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.96213 | 66.3867 | 0.89967
S2 | 30% | Campbellsville | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95264 | 65.7318 | 0.8998
S2-Fixes | 19% | Campbellsville | CCAP | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97598 | 67.3423 | 0.89805
S2-Fixes | 29% | Campbellsville | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98762 | 68.1458 | 0.83385
S2-Fixes | 29% | Campbellsville | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98765 | 68.1482 | 0.8339
S2-Fixes | 29% | Campbellsville | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97742 | 67.4418 | 0.83399
S2-Fixes | 29% | Campbellsville | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98694 | 68.0986 | 0.84523
S2-Fixes | 29% | Campbellsville | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99017 | 68.3219 | 0.86741
S2-Fixes | 29% | Campbellsville | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98449 | 67.9295 | 0.87039
S2-Fixes | 29% | Campbellsville | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98467 | 67.9423 | 0.8706
S2-Fixes | 29% | Campbellsville | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97839 | 67.5091 | 0.87072
S2-Fixes | 29% | Campbellsville | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97607 | 67.3491 | 0.87774
S2-Fixes | 29% | Campbellsville | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97614 | 67.3537 | 0.87781
S2-Fixes | 29% | Campbellsville | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97372 | 67.1867 | 0.88466
S2-Fixes | 29% | Campbellsville | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.974 | 67.2058 | 0.88496
S2-Fixes | 29% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0005 | 69.0366 | 0.89071
S2-Fixes | 29% | Campbellsville | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0005 | 69.0366 | 0.89195
S2-Fixes | 29% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0029 | 69.2004 | 0.89337
S2-Fixes | 29% | Campbellsville | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0029 | 69.2004 | 0.89461
S2-Fixes | 29% | Campbellsville | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0242 | 70.6711 | 0.8947
S2-Fixes | 29% | Campbellsville | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97055 | 66.9683 | 0.89553
S2-Fixes | 29% | Campbellsville | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97488 | 67.2666 | 0.89732
S2-Fixes | 29% | Campbellsville | McCreary | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98036 | 67.6446 | 0.89868
S2-Fixes | 29% | Campbellsville | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99584 | 68.713 | 0.89916
S2-Fixes | 29% | Campbellsville | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97877 | 67.535 | 0.89965
S2-Fixes | 29% | Campbellsville | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96616 | 66.6647 | 0.89969
S2-Fixes | 29% | Campbellsville | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96693 | 66.7184 | 0.89975
S2-Fixes | 29% | Campbellsville | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96553 | 66.6214 | 0.8998
S2-Fixes | 38% | Campbellsville | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96862 | 66.8345 | 0.84518
S2-Fixes | 38% | Campbellsville | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97598 | 67.3423 | 0.84794
S2-Fixes | 38% | Campbellsville | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97618 | 67.3561 | 0.84817
S2-Fixes | 38% | Campbellsville | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96702 | 66.7242 | 0.85605
S2-Fixes | 38% | Campbellsville | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96709 | 66.7291 | 0.85613
S2-Fixes | 38% | Campbellsville | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96353 | 66.4837 | 0.86062
S2-Fixes | 38% | Campbellsville | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96383 | 66.5043 | 0.86095
S2-Fixes | 38% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99356 | 68.5555 | 0.86679
S2-Fixes | 38% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99356 | 68.5555 | 0.86825
S2-Fixes | 38% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99612 | 68.7321 | 0.86973
S2-Fixes | 38% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99153 | 68.4158 | 0.86997
S2-Fixes | 38% | Campbellsville | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99612 | 68.7321 | 0.87119
S2-Fixes | 38% | Campbellsville | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0216 | 70.4924 | 0.87127
S2-Fixes | 38% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99153 | 68.4158 | 0.87134
S2-Fixes | 38% | Campbellsville | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9953 | 68.6754 | 0.87426
S2-Fixes | 38% | Campbellsville | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96477 | 66.5692 | 0.87469
S2-Fixes | 38% | Campbellsville | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9953 | 68.6754 | 0.87563
S2-Fixes | 38% | Campbellsville | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96121 | 66.3235 | 0.87574
S2-Fixes | 38% | Campbellsville | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96793 | 66.7871 | 0.87595
S2-Fixes | 38% | Campbellsville | W Garrard | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97295 | 67.1333 | 0.87664
S2-Fixes | 38% | Campbellsville | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95656 | 66.0026 | 0.87795
S2-Fixes | 38% | Campbellsville | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95742 | 66.0617 | 0.87798
S2-Fixes | 38% | Campbellsville | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95591 | 65.9576 | 0.87817
S2-Fixes | 38% | Campbellsville | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95647 | 65.9967 | 0.87879
S2-Fixes | 38% | Campbellsville | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9646 | 66.5573 | 0.87929
S2-Fixes | 38% | Campbellsville | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.9655 | 66.6195 | 0.87958
S2-Fixes | 38% | Campbellsville | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96274 | 66.4289 | 0.88191
S2-Fixes | 38% | Campbellsville | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96325 | 66.4643 | 0.88247
S2-Fixes | 38% | Campbellsville | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9988 | 68.9175 | 0.88585
S2-Fixes | 38% | Campbellsville | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99882 | 68.9185 | 0.88667
S2-Fixes | 38% | Campbellsville | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9988 | 68.9175 | 0.88709
S2-Fixes | 38% | Campbellsville | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99882 | 68.9185 | 0.8879
S2-Fixes | 38% | Campbellsville | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9676 | 66.7643 | 0.88898
S2-Fixes | 38% | Campbellsville | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96783 | 66.78 | 0.88923
S2-Fixes | 38% | Campbellsville | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96025 | 66.2575 | 0.88947
S2-Fixes | 38% | Campbellsville | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96609 | 66.6602 | 0.88968
S2-Fixes | 38% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98455 | 67.9338 | 0.89125
S2-Fixes | 38% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98455 | 67.9338 | 0.89143
S2-Fixes | 38% | Campbellsville | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.9627 | 66.4263 | 0.89212
S2-Fixes | 38% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98455 | 67.9338 | 0.89478
S2-Fixes | 38% | Campbellsville | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9646 | 66.5573 | 0.89501
S2-Fixes | 38% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98455 | 67.9338 | 0.89513
S2-Fixes | 38% | Campbellsville | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95966 | 66.2164 | 0.89517
S2-Fixes | 38% | Campbellsville | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98455 | 67.9338 | 0.8952
S2-Fixes | 38% | Campbellsville | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96477 | 66.5692 | 0.89665
S2-Fixes | 38% | Campbellsville | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.97712 | 67.4211 | 0.89696
S2-Fixes | 38% | Campbellsville | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.97716 | 67.4239 | 0.89701
S2-Fixes | 38% | Campbellsville | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99153 | 68.4158 | 0.89774
S2-Fixes | 38% | Campbellsville | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99096 | 68.3765 | 0.89834
S2-Fixes | 38% | Campbellsville | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99356 | 68.5555 | 0.89837
S2-Fixes | 38% | Campbellsville | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96793 | 66.7871 | 0.89839
S2-Fixes | 38% | Campbellsville | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.99096 | 68.3765 | 0.89852
S2-Fixes | 38% | Campbellsville | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98384 | 67.8852 | 0.89864
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.98327 | 67.8453 | 0.8814
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98683 | 68.0913 | 0.88166
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.987 | 68.1031 | 0.88185
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99199 | 68.4472 | 0.88202
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99202 | 68.4492 | 0.88206
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9794 | 67.5783 | 0.88839
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97946 | 67.5825 | 0.88845
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.97236 | 67.0926 | 0.89108
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.99204 | 68.4507 | 0.89124
S2-Fixes | 38% | Campbellsville | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97179 | 67.0534 | 0.77652
S2-Fixes | 38% | Campbellsville | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97183 | 67.0563 | 0.77658
S2-Fixes | 38% | Campbellsville | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96067 | 66.2864 | 0.77759
S2-Fixes | 38% | Campbellsville | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97107 | 67.0038 | 0.79055
S2-Fixes | 38% | Campbellsville | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97465 | 67.2508 | 0.8176
S2-Fixes | 38% | Campbellsville | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9622 | 66.3916 | 0.83855
S2-Fixes | 38% | Campbellsville | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96972 | 66.9108 | 0.84019
S2-Fixes | 38% | Campbellsville | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96992 | 66.9247 | 0.84042
S2-Fixes | 38% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.92259 | 63.6585 | 0.84561
S2-Fixes | 38% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.92435 | 63.7801 | 0.84753
S2-Fixes | 38% | Campbellsville | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96056 | 66.2789 | 0.84838
S2-Fixes | 38% | Campbellsville | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96064 | 66.2838 | 0.84846
S2-Fixes | 38% | Campbellsville | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95724 | 66.0497 | 0.85412
S2-Fixes | 38% | Campbellsville | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95754 | 66.0705 | 0.85446
S2-Fixes | 38% | Campbellsville | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.9337 | 64.4252 | 0.85775
S2-Fixes | 38% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.92259 | 63.6585 | 0.86031
S2-Fixes | 38% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.92435 | 63.7801 | 0.8622
S2-Fixes | 38% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99213 | 68.4572 | 0.86452
S2-Fixes | 38% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99213 | 68.4572 | 0.86598
S2-Fixes | 38% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9947 | 68.6341 | 0.86746
S2-Fixes | 38% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99013 | 68.3188 | 0.8677
S2-Fixes | 38% | Campbellsville | Alcalde | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96674 | 66.7054 | 0.86822
S2-Fixes | 38% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95458 | 65.866 | 0.86828
S2-Fixes | 38% | Campbellsville | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95859 | 66.1426 | 0.86832
S2-Fixes | 38% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9947 | 68.6341 | 0.86892
S2-Fixes | 38% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0197 | 70.3615 | 0.86901
S2-Fixes | 38% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99013 | 68.3188 | 0.86907
S2-Fixes | 38% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94978 | 65.5347 | 0.86914
S2-Fixes | 38% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95063 | 65.5936 | 0.86916
S2-Fixes | 38% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94911 | 65.4883 | 0.86934
S2-Fixes | 38% | Campbellsville | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96162 | 66.3519 | 0.86944
S2-Fixes | 38% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94968 | 65.5277 | 0.86996
S2-Fixes | 38% | Campbellsville | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95911 | 66.1788 | 0.87119
S2-Fixes | 38% | Campbellsville | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.94629 | 65.2942 | 0.87157
S2-Fixes | 38% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9939 | 68.5788 | 0.87201
S2-Fixes | 38% | Campbellsville | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.9337 | 64.4252 | 0.87224
S2-Fixes | 38% | Campbellsville | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95847 | 66.1348 | 0.873
S2-Fixes | 38% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9939 | 68.5788 | 0.87337
S2-Fixes | 38% | Campbellsville | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95635 | 65.9882 | 0.87357
S2-Fixes | 38% | Campbellsville | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95687 | 66.0239 | 0.87413
S2-Fixes | 38% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.94911 | 65.4883 | 0.87538
S2-Fixes | 38% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.94968 | 65.5277 | 0.876
S2-Fixes | 38% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.94978 | 65.5347 | 0.87607
S2-Fixes | 38% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95063 | 65.5936 | 0.87684
S2-Fixes | 38% | Campbellsville | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9619 | 66.3711 | 0.8793
S2-Fixes | 38% | Campbellsville | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96213 | 66.387 | 0.87955
S2-Fixes | 38% | Campbellsville | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95388 | 65.8179 | 0.88125
S2-Fixes | 38% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98089 | 67.6815 | 0.88153
S2-Fixes | 38% | Campbellsville | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96067 | 66.2864 | 0.88176
S2-Fixes | 38% | Campbellsville | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95388 | 65.8179 | 0.88257
S2-Fixes | 38% | Campbellsville | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95311 | 65.7647 | 0.8826
S2-Fixes | 38% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95458 | 65.866 | 0.88315
S2-Fixes | 38% | Campbellsville | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99744 | 68.8237 | 0.88363
S2-Fixes | 38% | Campbellsville | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95635 | 65.9879 | 0.88392
S2-Fixes | 38% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98089 | 67.6815 | 0.88393
S2-Fixes | 38% | Campbellsville | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99747 | 68.8253 | 0.88447
S2-Fixes | 38% | Campbellsville | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95635 | 65.9882 | 0.88471
S2-Fixes | 38% | Campbellsville | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99744 | 68.8237 | 0.88488
S2-Fixes | 38% | Campbellsville | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95635 | 65.9879 | 0.88523
S2-Fixes | 38% | Campbellsville | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95687 | 66.0239 | 0.88527
S2-Fixes | 38% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98089 | 67.6815 | 0.88532
S2-Fixes | 38% | Campbellsville | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95847 | 66.1348 | 0.8854
S2-Fixes | 38% | Campbellsville | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99747 | 68.8253 | 0.88571
S2-Fixes | 38% | Campbellsville | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94629 | 65.2942 | 0.8858
S2-Fixes | 38% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98089 | 67.6815 | 0.88593
S2-Fixes | 38% | Campbellsville | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98089 | 67.6815 | 0.886
S2-Fixes | 38% | Campbellsville | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95311 | 65.7647 | 0.8866
S2-Fixes | 38% | Campbellsville | Alcalde | 324965 | 2SOMERSET NO | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.96019 | 66.2534 | 0.88681
S2-Fixes | 38% | Campbellsville | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95859 | 66.1426 | 0.88705
S2-Fixes | 38% | Campbellsville | Alcalde | 324903 | 2MCKEE ROAD | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.96053 | 66.2763 | 0.88717
S2-Fixes | 38% | Campbellsville | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95911 | 66.1788 | 0.88742
S2-Fixes | 38% | Campbellsville | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95877 | 66.1549 | 0.88821
S2-Fixes | 38% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99013 | 68.3188 | 0.88836
S2-Fixes | 38% | Campbellsville | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96162 | 66.3519 | 0.88858
S2-Fixes | 38% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98733 | 68.1259 | 0.8887
S2-Fixes | 38% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99213 | 68.4572 | 0.88892
S2-Fixes | 38% | Campbellsville | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.97179 | 67.0534 | 0.88902
S2-Fixes | 38% | Campbellsville | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.97183 | 67.0563 | 0.88907
S2-Fixes | 38% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97987 | 67.6109 | 0.88921
S2-Fixes | 38% | Campbellsville | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.96056 | 66.2789 | 0.89012
S2-Fixes | 38% | Campbellsville | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.96064 | 66.2838 | 0.8902
S2-Fixes | 38% | Campbellsville | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95253 | 65.7246 | 0.89105
S2-Fixes | 38% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98733 | 68.1259 | 0.89108
S2-Fixes | 38% | Campbellsville | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95724 | 66.0497 | 0.89124
S2-Fixes | 38% | Campbellsville | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95754 | 66.0705 | 0.89157
S2-Fixes | 38% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9947 | 68.6341 | 0.89178
S2-Fixes | 38% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0183 | 70.2596 | 0.89194
S2-Fixes | 38% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99013 | 68.3188 | 0.89209
S2-Fixes | 38% | Campbellsville | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99013 | 68.3188 | 0.89217
S2-Fixes | 38% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98733 | 68.1259 | 0.89246
S2-Fixes | 38% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9939 | 68.5788 | 0.89256
S2-Fixes | 38% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99213 | 68.4572 | 0.89277
S2-Fixes | 38% | Campbellsville | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99213 | 68.4572 | 0.89286
S2-Fixes | 38% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95458 | 65.866 | 0.89287
S2-Fixes | 38% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98733 | 68.1259 | 0.89307
S2-Fixes | 38% | Campbellsville | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.97107 | 67.0038 | 0.89313
S2-Fixes | 38% | Campbellsville | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98733 | 68.1259 | 0.89314
S2-Fixes | 38% | Campbellsville | Alcalde | 324964 | 2SOMERSET 3 | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.96609 | 66.66 | 0.89327
S2-Fixes | 38% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0038 | 69.2654 | 0.8934
S2-Fixes | 38% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97987 | 67.6109 | 0.89355
S2-Fixes | 38% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97987 | 67.6109 | 0.89362
S2-Fixes | 38% | Campbellsville | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95877 | 66.1549 | 0.89369
S2-Fixes | 38% | Campbellsville | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96056 | 66.2789 | 0.89373
S2-Fixes | 38% | Campbellsville | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96064 | 66.2838 | 0.89381
S2-Fixes | 38% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97987 | 67.6109 | 0.89384
S2-Fixes | 38% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0201 | 70.384 | 0.894
S2-Fixes | 38% | Campbellsville | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97987 | 67.6109 | 0.89404
S2-Fixes | 38% | Campbellsville | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95698 | 66.0315 | 0.89432
S2-Fixes | 38% | Campbellsville | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95698 | 66.0317 | 0.89439
S2-Fixes | 38% | Campbellsville | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95311 | 65.7647 | 0.8945
S2-Fixes | 38% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.95063 | 65.5936 | 0.89503
S2-Fixes | 38% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94978 | 65.5347 | 0.89516
S2-Fixes | 38% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0197 | 70.3615 | 0.89538
S2-Fixes | 38% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 1.0038 | 69.2654 | 0.89544
S2-Fixes | 38% | Campbellsville | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96056 | 66.2789 | 0.8955
S2-Fixes | 38% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94911 | 65.4883 | 0.89553
S2-Fixes | 38% | Campbellsville | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96064 | 66.2838 | 0.89558
S2-Fixes | 38% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.92259 | 63.6585 | 0.8956
S2-Fixes | 38% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9947 | 68.6341 | 0.89563
S2-Fixes | 38% | Campbellsville | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9947 | 68.6341 | 0.89571
S2-Fixes | 38% | Campbellsville | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96056 | 66.2789 | 0.89578
S2-Fixes | 38% | Campbellsville | Alcalde | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.96674 | 66.7054 | 0.8958
S2-Fixes | 38% | Campbellsville | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96064 | 66.2838 | 0.89586
S2-Fixes | 38% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0217 | 70.5001 | 0.89592
S2-Fixes | 38% | Campbellsville | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95877 | 66.1549 | 0.89592
S2-Fixes | 38% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94968 | 65.5277 | 0.89613
S2-Fixes | 38% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9939 | 68.5788 | 0.89628
S2-Fixes | 38% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0183 | 70.2596 | 0.89629
S2-Fixes | 38% | Campbellsville | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9939 | 68.5788 | 0.89635
S2-Fixes | 38% | Campbellsville | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0183 | 70.2596 | 0.89638
S2-Fixes | 38% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95458 | 65.866 | 0.89644
S2-Fixes | 38% | Campbellsville | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95829 | 66.1222 | 0.89644
S2-Fixes | 38% | Campbellsville | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95851 | 66.137 | 0.8965
S2-Fixes | 38% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94911 | 65.4883 | 0.89663
S2-Fixes | 38% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94978 | 65.5347 | 0.89671
S2-Fixes | 38% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95063 | 65.5936 | 0.89698
S2-Fixes | 38% | Campbellsville | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96972 | 66.9108 | 0.89715
S2-Fixes | 38% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94968 | 65.5277 | 0.89724
S2-Fixes | 38% | Campbellsville | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95837 | 66.1278 | 0.89731
S2-Fixes | 38% | Campbellsville | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96992 | 66.9247 | 0.89736
S2-Fixes | 38% | Campbellsville | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.92435 | 63.7801 | 0.89741
S2-Fixes | 38% | Campbellsville | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97007 | 66.9348 | 0.89746
S2-Fixes | 38% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0038 | 69.2654 | 0.89779
S2-Fixes | 38% | Campbellsville | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95877 | 66.1549 | 0.8978
S2-Fixes | 38% | Campbellsville | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0038 | 69.2654 | 0.89787
S2-Fixes | 38% | Campbellsville | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95388 | 65.8179 | 0.89792
S2-Fixes | 38% | Campbellsville | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95877 | 66.1549 | 0.89807
S2-Fixes | 38% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95458 | 65.866 | 0.89813
S2-Fixes | 38% | Campbellsville | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95724 | 66.0496 | 0.89814
S2-Fixes | 38% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0201 | 70.384 | 0.89834
S2-Fixes | 38% | Campbellsville | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95458 | 65.866 | 0.89839
S2-Fixes | 38% | Campbellsville | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94911 | 65.4883 | 0.8984
S2-Fixes | 38% | Campbellsville | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0201 | 70.384 | 0.89843
S2-Fixes | 38% | Campbellsville | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94978 | 65.5347 | 0.89848
S2-Fixes | 38% | Campbellsville | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9885 | 68.2067 | 0.89875
S2-Fixes | 38% | Campbellsville | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95063 | 65.5936 | 0.89875
S2-Fixes | 38% | Campbellsville | Alcalde | 324372 | 2BURNSIDE | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.97102 | 67.0006 | 0.89883
S2-Fixes | 38% | Campbellsville | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96972 | 66.9108 | 0.89897
S2-Fixes | 38% | Campbellsville | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94968 | 65.5277 | 0.899
S2-Fixes | 38% | Campbellsville | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.95878 | 66.1556 | 0.89906
S2-Fixes | 38% | Campbellsville | Alcalde | 326533 | 2BUSH EKPC | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.95955 | 66.2086 | 0.89913
S2-Fixes | 38% | Campbellsville | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96992 | 66.9247 | 0.89919
S2-Fixes | 38% | Campbellsville | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.96086 | 66.2994 | 0.89919
S2-Fixes | 38% | Campbellsville | Alcalde | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97732 | 157.3482 | 0.89923
S2-Fixes | 38% | Campbellsville | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96972 | 66.9108 | 0.89927
S2-Fixes | 38% | Campbellsville | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97007 | 66.9348 | 0.89929
S2-Fixes | 38% | Campbellsville | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96992 | 66.9247 | 0.89949
S2-Fixes | 38% | Campbellsville | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-RUS-WLF161 | 0.92259 | 63.6585 | 0.89953
S2-Fixes | 38% | Campbellsville | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97007 | 66.9348 | 0.89958
S2-Fixes | 38% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0197 | 70.3615 | 0.89967
S2-Fixes | 38% | Campbellsville | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0197 | 70.3615 | 0.89976
S2-Fixes | 38% | Campbellsville | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95388 | 65.8179 | 0.8998
S2-Fixes | 38% | Campbellsville | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99744 | 68.8237 | 0.89992
S2 | 25% | Liberty | CCAP | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95731 | 66.0545 | 0.84572 | 0.8715 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95837 | 66.1275 | 0.85895 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 25% | Liberty | CCAP | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96945 | 66.892 | 0.85919 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 25% | Liberty | CCAP | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96948 | 66.8943 | 0.85923 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 25% | Liberty | CCAP | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96666 | 66.6993 | 0.86535 | 0.8869 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96686 | 66.7135 | 0.86558 | 0.8871 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96906 | 66.865 | 0.86731
S2 | 25% | Liberty | CCAP | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96924 | 66.8775 | 0.86751
S2 | 25% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95513 | 65.9041 | 0.86846 | 0.885 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95541 | 65.923 | 0.86876 | 0.8853 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96777 | 66.7764 | 0.86949 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 25% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96212 | 66.3866 | 0.87094 | 0.8924 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96046 | 66.2721 | 0.87349 | 0.8938 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96307 | 66.4518 | 0.87445
S2 | 25% | Liberty | CCAP | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96313 | 66.4562 | 0.87452
S2 | 25% | Liberty | CCAP | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0073 | 69.5047 | 0.87536 | 0.9365 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96431 | 66.5376 | 0.87558 | 0.8964 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.009 | 69.6185 | 0.87725 | 0.9383 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0073 | 69.5047 | 0.87887 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0073 | 69.5047 | 0.87895 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0105 | 69.7246 | 0.87903 | 0.9399 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.009 | 69.6244 | 0.87918 | 0.9393 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98769 | 68.1503 | 0.87967 | 0.9323 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97982 | 67.6073 | 0.8802 | 0.9233 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.009 | 69.6185 | 0.88076 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.009 | 69.6185 | 0.88084 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99001 | 68.311 | 0.88229 | 0.9347 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0164 | 163.638 | 0.88252 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0105 | 69.7246 | 0.88253 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0105 | 69.7246 | 0.8826 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.009 | 69.6244 | 0.88265 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.009 | 69.6244 | 0.88272 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98769 | 68.1503 | 0.88275 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98769 | 68.1503 | 0.88282 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95513 | 65.9041 | 0.88298 | 0.897 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95541 | 65.923 | 0.88328 | 0.8972 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97982 | 67.6073 | 0.88391 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97982 | 67.6073 | 0.88397 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99001 | 68.311 | 0.88536 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99841 | 68.8904 | 0.88541 | 0.9363 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99001 | 68.311 | 0.88543 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94876 | 65.4645 | 0.88634 | 0.9181 | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94876 | 65.4645 | 0.88666 |  | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98565 | 68.0096 | 0.88669 | 0.9295 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95111 | 65.6264 | 0.88885 | 0.9205 | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99841 | 68.8904 | 0.88905 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99841 | 68.8904 | 0.88912 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95111 | 65.6264 | 0.88917 |  | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96792 | 66.7865 | 0.88923 |  | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96046 | 66.2721 | 0.8893 | 0.8972 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96952 | 66.8972 | 0.88972 |  | Inclusive of Liberty Jct cap bank. Serving Tommy Gooch on a radial out of KU Standford mitigates all voltages concerns.
S2 | 25% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9843 | 67.9165 | 0.88985 | 0.9376 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98565 | 68.0096 | 0.89038 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98565 | 68.0096 | 0.89044 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98024 | 67.6365 | 0.89044 | 0.9281 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9604 | 66.2673 | 0.89171
S2 | 25% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96431 | 66.5376 | 0.89172 | 0.8998 | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94681 | 65.3296 | 0.89253 | 0.924 | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9843 | 67.9165 | 0.89267 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9843 | 67.9165 | 0.89273 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94681 | 65.3296 | 0.8928 |  | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98772 | 68.153 | 0.89365 | 0.9412 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98024 | 67.6365 | 0.89414 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98024 | 67.6365 | 0.8942 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96212 | 66.3866 | 0.89623 |  | Rebuild ThreeLinks-McKee 556 - 12.7 miles
S2 | 25% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98772 | 68.153 | 0.89645 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98772 | 68.153 | 0.89651 |  | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | CCAP | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93937 | 64.8168 | 0.89712 | 0.9285 | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93937 | 64.8168 | 0.89733 |  | North London 25MVAR cap bank
S2 | 25% | Liberty | CCAP | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98804 | 68.1746 | 0.89904 | 0.9364 | Wayne Co 19MVAR cap bank
S2 | 25% | Liberty | W Garrard Lib J | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95445 | 65.8572 | 0.84038 |  | -0.11407
S2 | 25% | Liberty | W Garrard Lib J | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95778 | 66.087 | 0.85252 |  | -0.10526
S2 | 25% | Liberty | W Garrard Lib J | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95797 | 66.0997 | 0.85273 |  | -0.10524
S2 | 25% | Liberty | W Garrard Lib J | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95756 | 66.0719 | 0.85787 |  | -0.09969
S2 | 25% | Liberty | W Garrard Lib J | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96881 | 66.8477 | 0.85811 |  | -0.1107
S2 | 25% | Liberty | W Garrard Lib J | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96884 | 66.85 | 0.85815 |  | -0.11069
S2 | 25% | Liberty | W Garrard Lib J | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95189 | 65.6803 | 0.85979 |  | -0.092097
S2 | 25% | Liberty | W Garrard Lib J | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95195 | 65.6848 | 0.85986 |  | -0.09209
S2 | 25% | Liberty | W Garrard Lib J | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96302 | 66.4485 | 0.86227 |  | -0.10076
S2 | 25% | Liberty | W Garrard Lib J | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96323 | 66.4628 | 0.8625 |  | -0.10073
S2 | 25% | Liberty | W Garrard Lib J | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95192 | 65.6825 | 0.86328 |  | -0.088644
S2 | 25% | Liberty | W Garrard Lib J | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95219 | 65.7014 | 0.86358 |  | -0.088616
S2 | 25% | Liberty | W Garrard Lib J | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95869 | 66.1497 | 0.86788 |  | -0.090811
S2 | 25% | Liberty | W Garrard Lib J | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96698 | 66.7213 | 0.86844 |  | -0.098539
S2 | 25% | Liberty | W Garrard Lib J | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.004 | 69.2792 | 0.86853 |  | -0.13552
S2 | 25% | Liberty | W Garrard Lib J | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.004 | 69.2792 | 0.8686 |  | -0.13544
S2 | 25% | Liberty | W Garrard Lib J | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95707 | 66.0381 | 0.87043 |  | -0.086644
S2 | 25% | Liberty | W Garrard Lib J | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0057 | 69.3934 | 0.87044 |  | -0.13526
S2 | 25% | Liberty | W Garrard Lib J | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0057 | 69.3934 | 0.87052 |  | -0.13518
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9723 | 67.0888 | 0.87205 |  | -0.10025
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9723 | 67.0888 | 0.87211 |  | -0.10019
S2 | 25% | Liberty | W Garrard Lib J | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0155 | 163.4957 | 0.87222 |  | -0.14328
S2 | 25% | Liberty | W Garrard Lib J | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0072 | 69.4999 | 0.87223 |  | -0.13502
S2 | 25% | Liberty | W Garrard Lib J | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0072 | 69.4999 | 0.8723 |  | -0.13494
S2 | 25% | Liberty | W Garrard Lib J | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96086 | 66.2991 | 0.87246 |  | -0.088396
S2 | 25% | Liberty | W Garrard Lib J | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0058 | 69.4028 | 0.8725 |  | -0.13334
S2 | 25% | Liberty | W Garrard Lib J | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0058 | 69.4028 | 0.87257 |  | -0.13327
S2 | 25% | Liberty | W Garrard Lib J | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.004 | 69.2792 | 0.87357 |  | -0.13048
S2 | 25% | Liberty | W Garrard Lib J | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98492 | 67.9595 | 0.87403 |  | -0.11089
S2 | 25% | Liberty | W Garrard Lib J | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98492 | 67.9595 | 0.87409 |  | -0.11083
S2 | 25% | Liberty | W Garrard Lib J | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0057 | 69.3934 | 0.87547 |  | -0.13023
S2 | 25% | Liberty | W Garrard Lib J | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98726 | 68.1206 | 0.87666 |  | -0.11059
S2 | 25% | Liberty | W Garrard Lib J | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98726 | 68.1206 | 0.87673 |  | -0.11053
S2 | 25% | Liberty | W Garrard Lib J | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0072 | 69.4999 | 0.87725 |  | -0.13
S2 | 25% | Liberty | W Garrard Lib J | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94934 | 65.5043 | 0.87739 |  | -0.07195
S2 | 25% | Liberty | W Garrard Lib J | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0058 | 69.4028 | 0.87746 |  | -0.12838
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9723 | 67.0888 | 0.87761 |  | -0.094696
S2 | 25% | Liberty | W Garrard Lib J | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99272 | 68.4977 | 0.87779 |  | -0.11493
S2 | 25% | Liberty | W Garrard Lib J | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99272 | 68.4977 | 0.87785 |  | -0.11487
S2 | 25% | Liberty | W Garrard Lib J | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98492 | 67.9595 | 0.87848 |  | -0.10644
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97818 | 67.4941 | 0.87861 |  | -0.09957
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97818 | 67.4941 | 0.87866 |  | -0.099512
S2 | 25% | Liberty | W Garrard Lib J | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95192 | 65.6825 | 0.88 |  | -0.071921
S2 | 25% | Liberty | W Garrard Lib J | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95219 | 65.7014 | 0.8803 |  | -0.071898
S2 | 25% | Liberty | W Garrard Lib J | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98726 | 68.1206 | 0.8811 |  | -0.10615
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97168 | 67.0459 | 0.88212 |  | -0.089559
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97168 | 67.0459 | 0.88217 |  | -0.089507
S2 | 25% | Liberty | W Garrard Lib J | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94407 | 65.141 | 0.88221 |  | -0.061859
S2 | 25% | Liberty | W Garrard Lib J | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94407 | 65.141 | 0.88253 |  | -0.061538
S2 | 25% | Liberty | W Garrard Lib J | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99272 | 68.4977 | 0.88314 |  | -0.10958
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97818 | 67.4941 | 0.88412 |  | -0.094057
S2 | 25% | Liberty | W Garrard Lib J | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95707 | 66.0381 | 0.88425 |  | -0.07282
S2 | 25% | Liberty | W Garrard Lib J | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94643 | 65.3036 | 0.88474 |  | -0.061693
S2 | 25% | Liberty | W Garrard Lib J | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98182 | 67.7458 | 0.88485 |  | -0.096972
S2 | 25% | Liberty | W Garrard Lib J | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98182 | 67.7458 | 0.88491 |  | -0.09691
S2 | 25% | Liberty | W Garrard Lib J | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94643 | 65.3036 | 0.88506 |  | -0.061373
S2 | 25% | Liberty | W Garrard Lib J | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96283 | 66.4353 | 0.88511 |  | -0.077718
S2 | 25% | Liberty | W Garrard Lib J | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96086 | 66.2991 | 0.88658 |  | -0.07428
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97168 | 67.0459 | 0.8877 |  | -0.083982
S2 | 25% | Liberty | W Garrard Lib J | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94236 | 65.0229 | 0.88843 |  | -0.053928
S2 | 25% | Liberty | W Garrard Lib J | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98526 | 67.9829 | 0.88867 |  | -0.096592
S2 | 25% | Liberty | W Garrard Lib J | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94236 | 65.0229 | 0.8887 |  | -0.053663
S2 | 25% | Liberty | W Garrard Lib J | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96859 | 66.833 | 0.8887 |  | -0.079891
S2 | 25% | Liberty | W Garrard Lib J | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98526 | 67.9829 | 0.88873 |  | -0.09653
S2 | 25% | Liberty | W Garrard Lib J | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98182 | 67.7458 | 0.88897 |  | -0.092856
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9723 | 67.0888 | 0.88971 |  | -0.082588
S2 | 25% | Liberty | W Garrard Lib J | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97955 | 67.5889 | 0.8908 |  | -0.088744
S2 | 25% | Liberty | W Garrard Lib J | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97955 | 67.5889 | 0.89086 |  | -0.088692
S2 | 25% | Liberty | W Garrard Lib J | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95869 | 66.1497 | 0.89126 |  | -0.067432
S2 | 25% | Liberty | W Garrard Lib J | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98526 | 67.9829 | 0.89277 |  | -0.092493
S2 | 25% | Liberty | W Garrard Lib J | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93504 | 64.5179 | 0.89304 |  | -0.041998
S2 | 25% | Liberty | W Garrard Lib J | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93504 | 64.5179 | 0.89326 |  | -0.041781
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97818 | 67.4941 | 0.89614 |  | -0.082039
S2 | 25% | Liberty | W Garrard Lib J | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97955 | 67.5889 | 0.89633 |  | -0.083222
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9723 | 67.0888 | 0.89691 |  | -0.075388
S2 | 25% | Liberty | W Garrard Lib J | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96173 | 66.3595 | 0.89792 |  | -0.063813
S2 | 25% | Liberty | W Garrard Lib J | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94042 | 64.8892 | 0.89868 |  | -0.041741
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97168 | 67.0459 | 0.89876 |  | -0.072916
S2 | 25% | Liberty | W Garrard Lib J | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94042 | 64.8892 | 0.8989 |  | -0.041525
S2 | 25% | Liberty | W Garrard Lib J | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99064 | 68.3544 | 0.89913 |  | -0.091512
S2 | 25% | Liberty | W Garrard Lib J | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99064 | 68.3544 | 0.89919 |  | -0.091454
S2 | 25% | Liberty | W Garrard Lib J | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99039 | 68.3367 | 0.8995 |  | -0.09089
S2 | 25% | Liberty | W Garrard Lib J | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99039 | 68.3367 | 0.89956 |  | -0.090832
S2 | 25% | Liberty | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95359 | 65.7976 | 0.83941 | 57.9192 | -0.11418
S2 | 25% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95936 | 66.1961 | 0.85413 | 58.9349 | -0.10524
S2 | 25% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95955 | 66.2088 | 0.85434 | 58.9491 | -0.10521
S2 | 25% | Liberty | McCreary | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96226 | 66.3961 | 0.86102 | 59.4106 | -0.10124
S2 | 25% | Liberty | McCreary | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96247 | 66.4104 | 0.86125 | 59.4266 | -0.10121
S2 | 25% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95306 | 65.7612 | 0.86139 | 59.4357 | -0.091673
S2 | 25% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95313 | 65.7656 | 0.86146 | 59.4407 | -0.091666
S2 | 25% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95107 | 65.6241 | 0.86233 | 59.5007 | -0.088745
S2 | 25% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95135 | 65.643 | 0.86263 | 59.5216 | -0.088717
S2 | 25% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95619 | 65.9768 | 0.86407 | 59.6207 | -0.092117
S2 | 25% | Liberty | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96742 | 66.7523 | 0.86436 | 59.6408 | -0.10306
S2 | 25% | Liberty | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96746 | 66.7546 | 0.86441 | 59.644 | -0.10305
S2 | 25% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95787 | 66.0928 | 0.86665 | 59.7985 | -0.091221
S2 | 25% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0003 | 69.0228 | 0.86857 | 59.931 | -0.13177
S2 | 25% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0003 | 69.0228 | 0.86864 | 59.9365 | -0.13169
S2 | 25% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95624 | 65.9807 | 0.8692 | 59.9747 | -0.087043
S2 | 25% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0003 | 69.0228 | 0.86982 | 60.0176 | -0.13051
S2 | 25% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.002 | 69.1374 | 0.87048 | 60.063 | -0.13151
S2 | 25% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.002 | 69.1374 | 0.87056 | 60.0685 | -0.13143
S2 | 25% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96001 | 66.2406 | 0.8712 | 60.113 | -0.088805
S2 | 25% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.002 | 69.1374 | 0.87173 | 60.1494 | -0.13026
S2 | 25% | Liberty | McCreary | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.011 | 162.7691 | 0.87226 | 140.4336 | -0.13873
S2 | 25% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0035 | 69.2443 | 0.87226 | 60.1863 | -0.13128
S2 | 25% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0035 | 69.2443 | 0.87234 | 60.1917 | -0.1312
S2 | 25% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0022 | 69.1511 | 0.87249 | 60.2016 | -0.1297
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97018 | 66.9424 | 0.87253 | 60.2045 | -0.097652
S2 | 25% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0022 | 69.1511 | 0.87257 | 60.2071 | -0.12962
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97018 | 66.9424 | 0.87259 | 60.2087 | -0.09759
S2 | 25% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0035 | 69.2443 | 0.87351 | 60.2724 | -0.13003
S2 | 25% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.982 | 67.7578 | 0.87355 | 60.2746 | -0.10845
S2 | 25% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.982 | 67.7578 | 0.87362 | 60.2796 | -0.10838
S2 | 25% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0022 | 69.1511 | 0.87372 | 60.287 | -0.12847
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97018 | 66.9424 | 0.8741 | 60.3131 | -0.096077
S2 | 25% | Liberty | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96561 | 66.6272 | 0.87455 | 60.344 | -0.091061
S2 | 25% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.982 | 67.7578 | 0.87481 | 60.3621 | -0.10718
S2 | 25% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98434 | 67.9194 | 0.87618 | 60.4565 | -0.10816
S2 | 25% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98434 | 67.9194 | 0.87625 | 60.4614 | -0.10809
S2 | 25% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98434 | 67.9194 | 0.87744 | 60.5437 | -0.1069
S2 | 25% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98996 | 68.3072 | 0.87808 | 60.5873 | -0.11188
S2 | 25% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98996 | 68.3072 | 0.87815 | 60.5921 | -0.11181
S2 | 25% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95107 | 65.6241 | 0.8788 | 60.6372 | -0.072273
S2 | 25% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95005 | 65.5533 | 0.87895 | 60.6473 | -0.071102
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97607 | 67.3487 | 0.87908 | 60.6565 | -0.096988
S2 | 25% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95135 | 65.643 | 0.8791 | 60.6577 | -0.072251
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97607 | 67.3487 | 0.87914 | 60.6608 | -0.096926
S2 | 25% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98996 | 68.3072 | 0.87953 | 60.6874 | -0.11043
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97607 | 67.3487 | 0.88064 | 60.7644 | -0.095425
S2 | 25% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94425 | 65.1534 | 0.88201 | 60.8585 | -0.062244
S2 | 25% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94425 | 65.1534 | 0.88233 | 60.8806 | -0.061925
S2 | 25% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.96996 | 66.9273 | 0.88271 | 60.9069 | -0.087252
S2 | 25% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.96996 | 66.9273 | 0.88276 | 60.9107 | -0.087196
S2 | 25% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95624 | 65.9807 | 0.88333 | 60.9499 | -0.07291
S2 | 25% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97931 | 67.5727 | 0.8841 | 61.003 | -0.095214
S2 | 25% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97931 | 67.5727 | 0.88417 | 61.0075 | -0.095148
S2 | 25% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.96996 | 66.9273 | 0.88432 | 61.0179 | -0.085643
S2 | 25% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94661 | 65.316 | 0.88453 | 61.0326 | -0.062077
S2 | 25% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94661 | 65.316 | 0.88485 | 61.0546 | -0.061758
S2 | 25% | Liberty | McCreary | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96322 | 66.4619 | 0.88491 | 61.0585 | -0.078309
S2 | 25% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97931 | 67.5727 | 0.88539 | 61.0919 | -0.093924
S2 | 25% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96001 | 66.2406 | 0.88564 | 61.1088 | -0.074373
S2 | 25% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98276 | 67.8104 | 0.88792 | 61.2665 | -0.094839
S2 | 25% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98276 | 67.8104 | 0.88799 | 61.2711 | -0.094774
S2 | 25% | Liberty | McCreary | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94243 | 65.0279 | 0.88823 | 61.2878 | -0.054204
S2 | 25% | Liberty | McCreary | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94243 | 65.0279 | 0.88849 | 61.306 | -0.053939
S2 | 25% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98276 | 67.8104 | 0.8892 | 61.3551 | -0.093555
S2 | 25% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95787 | 66.0928 | 0.89035 | 61.4342 | -0.067516
S2 | 25% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97784 | 67.4712 | 0.89139 | 61.5056 | -0.086457
S2 | 25% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97784 | 67.4712 | 0.89144 | 61.5094 | -0.086402
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97018 | 66.9424 | 0.89262 | 61.5907 | -0.077561
S2 | 25% | Liberty | McCreary | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93507 | 64.5195 | 0.89284 | 61.606 | -0.042225
S2 | 25% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97784 | 67.4712 | 0.89298 | 61.6156 | -0.084864
S2 | 25% | Liberty | McCreary | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93507 | 64.5195 | 0.89306 | 61.621 | -0.042008
S2 | 25% | Liberty | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96718 | 66.7352 | 0.89457 | 61.7251 | -0.072609
S2 | 25% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98826 | 68.1899 | 0.89819 | 61.9752 | -0.090069
S2 | 25% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98826 | 68.1899 | 0.89825 | 61.9795 | -0.090007
S2 | 25% | Liberty | McCreary | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94045 | 64.8908 | 0.89848 | 61.9951 | -0.041966
S2 | 25% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98802 | 68.1733 | 0.89856 | 62.0009 | -0.089456
S2 | 25% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98802 | 68.1733 | 0.89863 | 62.0051 | -0.089394
S2 | 25% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95619 | 65.9768 | 0.89865 | 62.0071 | -0.057531
S2 | 25% | Liberty | McCreary | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94045 | 64.8908 | 0.8987 | 62.01 | -0.041751
S2 | 25% | Liberty | McCreary | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96361 | 66.4893 | 0.89886 | 62.021 | -0.064758
S2 | 25% | Liberty | McCreary | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96747 | 66.7554 | 0.8989 | 62.0243 | -0.068566
S2 | 25% | Liberty | McCreary | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96747 | 66.7554 | 0.89894 | 62.0268 | -0.06853
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97607 | 67.3487 | 0.89902 | 62.0325 | -0.077046
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97018 | 66.9424 | 0.89908 | 62.0364 | -0.071102
S2 | 25% | Liberty | McCreary | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96765 | 66.7678 | 0.8991 | 62.0377 | -0.068552
S2 | 25% | Liberty | McCreary | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96765 | 66.7678 | 0.89913 | 62.0401 | -0.068517
S2 | 25% | Liberty | McCreary | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96789 | 66.7842 | 0.89913 | 62.0402 | -0.068754
S2 | 25% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98826 | 68.1899 | 0.89933 | 62.0537 | -0.088931
S2 | 25% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98802 | 68.1733 | 0.89969 | 62.0788 | -0.088326
S2-Fixes | 37% | Liberty | CCAP | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97092 | 66.9934 | 0.81608 | 56.3096 | -0.15484
S2-Fixes | 37% | Liberty | CCAP | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97096 | 66.9962 | 0.81614 | 56.3138 | -0.15482
S2-Fixes | 37% | Liberty | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96057 | 66.2794 | 0.81668 | 56.351 | -0.14389
S2-Fixes | 37% | Liberty | CCAP | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97089 | 66.9915 | 0.82891 | 57.1948 | -0.14198
S2-Fixes | 37% | Liberty | CCAP | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96389 | 66.5087 | 0.8471 | 58.4499 | -0.11679
S2-Fixes | 37% | Liberty | CCAP | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97543 | 67.3048 | 0.85376 | 58.9093 | -0.12168
S2-Fixes | 37% | Liberty | CCAP | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98243 | 67.7878 | 0.85452 | 58.9617 | -0.12791
S2-Fixes | 37% | Liberty | CCAP | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98263 | 67.8013 | 0.85474 | 58.9773 | -0.12788
S2-Fixes | 37% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95967 | 66.2175 | 0.86239 | 59.5047 | -0.097287
S2-Fixes | 37% | Liberty | CCAP | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97311 | 67.1448 | 0.8625 | 59.5125 | -0.11061
S2-Fixes | 37% | Liberty | CCAP | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97318 | 67.1496 | 0.86258 | 59.518 | -0.1106
S2-Fixes | 37% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95997 | 66.2381 | 0.86272 | 59.5276 | -0.097254
S2-Fixes | 37% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9967 | 68.7721 | 0.8656 | 59.7263 | -0.1311
S2-Fixes | 37% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9967 | 68.7721 | 0.86688 | 59.8145 | -0.12982
S2-Fixes | 37% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99923 | 68.9469 | 0.86852 | 59.9278 | -0.13071
S2-Fixes | 37% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99923 | 68.9469 | 0.86979 | 60.0157 | -0.12944
S2-Fixes | 37% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0237 | 70.632 | 0.86988 | 60.0218 | -0.15377
S2-Fixes | 37% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99086 | 68.3692 | 0.87487 | 60.3658 | -0.11599
S2-Fixes | 37% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99086 | 68.3692 | 0.87603 | 60.446 | -0.11483
S2-Fixes | 37% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9614 | 66.3369 | 0.87631 | 60.4655 | -0.085092
S2-Fixes | 37% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96455 | 66.5542 | 0.87767 | 60.5595 | -0.086881
S2-Fixes | 37% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9946 | 68.6271 | 0.87911 | 60.6583 | -0.11549
S2-Fixes | 37% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9946 | 68.6271 | 0.88026 | 60.7381 | -0.11433
S2-Fixes | 37% | Liberty | CCAP | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96545 | 66.6158 | 0.88078 | 60.7742 | -0.084662
S2-Fixes | 37% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9614 | 66.3367 | 0.88085 | 60.7786 | -0.080552
S2-Fixes | 37% | Liberty | CCAP | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96567 | 66.6315 | 0.88103 | 60.7913 | -0.08464
S2-Fixes | 37% | Liberty | CCAP | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96679 | 66.7088 | 0.88187 | 60.8493 | -0.084921
S2-Fixes | 37% | Liberty | CCAP | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98307 | 67.8316 | 0.88301 | 60.9277 | -0.10006
S2-Fixes | 37% | Liberty | CCAP | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96308 | 66.4525 | 0.88321 | 60.9418 | -0.079865
S2-Fixes | 37% | Liberty | CCAP | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96403 | 66.5178 | 0.8833 | 60.9477 | -0.080725
S2-Fixes | 37% | Liberty | CCAP | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96223 | 66.3942 | 0.88332 | 60.9492 | -0.078912
S2-Fixes | 37% | Liberty | CCAP | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96279 | 66.4327 | 0.88393 | 60.9912 | -0.078862
S2-Fixes | 37% | Liberty | CCAP | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97402 | 67.2075 | 0.8859 | 61.1273 | -0.088119
S2-Fixes | 37% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9614 | 66.3367 | 0.88683 | 61.191 | -0.074575
S2-Fixes | 37% | Liberty | CCAP | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97115 | 67.0091 | 0.88836 | 61.2969 | -0.082785
S2-Fixes | 37% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9614 | 66.3369 | 0.88847 | 61.3043 | -0.072937
S2-Fixes | 37% | Liberty | CCAP | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97166 | 67.0442 | 0.88892 | 61.3353 | -0.082738
S2-Fixes | 37% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96455 | 66.5542 | 0.89009 | 61.4165 | -0.074459
S2-Fixes | 37% | Liberty | CCAP | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9985 | 68.8964 | 0.89057 | 61.4496 | -0.10792
S2-Fixes | 37% | Liberty | CCAP | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99849 | 68.8958 | 0.89134 | 61.5022 | -0.10715
S2-Fixes | 37% | Liberty | CCAP | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9985 | 68.8964 | 0.89161 | 61.5212 | -0.10689
S2-Fixes | 37% | Liberty | CCAP | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99849 | 68.8958 | 0.89237 | 61.5732 | -0.10612
S2-Fixes | 37% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95967 | 66.2175 | 0.89256 | 61.5867 | -0.067114
S2-Fixes | 37% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95997 | 66.2381 | 0.89288 | 61.6088 | -0.067091
S2-Fixes | 37% | Liberty | CCAP | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98605 | 68.0374 | 0.89514 | 61.7649 | -0.090906
S2-Fixes | 37% | Liberty | CCAP | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98605 | 68.0374 | 0.89518 | 61.7674 | -0.090868
S2-Fixes | 37% | Liberty | CCAP | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98623 | 68.0496 | 0.89534 | 61.7783 | -0.090888
S2-Fixes | 37% | Liberty | CCAP | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98623 | 68.0496 | 0.89538 | 61.7809 | -0.09085
S2-Fixes | 37% | Liberty | CCAP | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98663 | 68.0772 | 0.89538 | 61.7809 | -0.09125
S2-Fixes | 37% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98824 | 68.1888 | 0.89605 | 61.8276 | -0.092192
S2-Fixes | 37% | Liberty | CCAP | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96844 | 66.8225 | 0.89615 | 61.8343 | -0.072292
S2-Fixes | 37% | Liberty | CCAP | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98547 | 67.9977 | 0.89686 | 61.8836 | -0.08861
S2-Fixes | 37% | Liberty | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96057 | 66.2794 | 0.89686 | 61.8836 | -0.063707
S2-Fixes | 37% | Liberty | CCAP | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98547 | 67.9977 | 0.8969 | 61.886 | -0.088574
S2-Fixes | 37% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98824 | 68.1888 | 0.89806 | 61.9662 | -0.090183
S2-Fixes | 37% | Liberty | CCAP | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97085 | 66.9887 | 0.89875 | 62.0141 | -0.072096
S2-Fixes | 37% | Liberty | CCAP | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98131 | 67.7107 | 0.89899 | 62.0303 | -0.082324
S2-Fixes | 37% | Liberty | CCAP | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98131 | 67.7107 | 0.89902 | 62.0323 | -0.082295
S2-Fixes | 37% | Liberty | CCAP | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96497 | 66.5831 | 0.89947 | 62.0635 | -0.065502
S2-Fixes | 38% | Liberty | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96764 | 66.7673 | 0.80632 | 55.6359 | -0.16132
S2-Fixes | 38% | Liberty | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96768 | 66.7702 | 0.80638 | 55.6403 | -0.1613
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95708 | 66.0383 | 0.80706 | 55.6871 | -0.15002
S2-Fixes | 38% | Liberty | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96752 | 66.7585 | 0.81954 | 56.548 | -0.14798
S2-Fixes | 38% | Liberty | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95872 | 66.1514 | 0.83756 | 57.7918 | -0.12115
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97195 | 67.0648 | 0.83876 | 57.8745 | -0.13319
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97215 | 67.0786 | 0.83899 | 57.8905 | -0.13316
S2-Fixes | 38% | Liberty | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97197 | 67.0657 | 0.84509 | 58.3115 | -0.12687
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96219 | 66.3914 | 0.84696 | 58.4405 | -0.11523
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96227 | 66.3963 | 0.84704 | 58.4461 | -0.11522
S2-Fixes | 38% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9542 | 65.8401 | 0.85315 | 58.8677 | -0.10105
S2-Fixes | 38% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95451 | 65.861 | 0.85349 | 58.891 | -0.10101
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99076 | 68.3625 | 0.86163 | 59.4527 | -0.12913
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99076 | 68.3625 | 0.86292 | 59.5413 | -0.12784
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99333 | 68.5397 | 0.86459 | 59.6567 | -0.12874
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99333 | 68.5397 | 0.86587 | 59.7449 | -0.12746
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0172 | 70.1866 | 0.86596 | 59.751 | -0.15124
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95544 | 65.9253 | 0.8669 | 59.8164 | -0.088534
S2-Fixes | 38% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95582 | 65.9518 | 0.86737 | 59.8485 | -0.088454
S2-Fixes | 38% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9588 | 66.1572 | 0.86847 | 59.9241 | -0.090335
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98533 | 67.9876 | 0.87102 | 60.1001 | -0.11431
S2-Fixes | 38% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95581 | 65.9511 | 0.87206 | 60.1719 | -0.083755
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98533 | 67.9876 | 0.87218 | 60.1807 | -0.11314
S2-Fixes | 38% | Liberty | McCreary | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95987 | 66.2307 | 0.87339 | 60.2639 | -0.086476
S2-Fixes | 38% | Liberty | McCreary | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9601 | 66.2466 | 0.87364 | 60.2813 | -0.086453
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97833 | 67.5046 | 0.87467 | 60.3524 | -0.10365
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98911 | 68.2489 | 0.87531 | 60.3961 | -0.11381
S2-Fixes | 38% | Liberty | McCreary | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96627 | 66.6729 | 0.87638 | 60.47 | -0.089897
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98911 | 68.2489 | 0.87647 | 60.4763 | -0.11265
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94972 | 65.5308 | 0.87679 | 60.4986 | -0.07293
S2-Fixes | 38% | Liberty | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95056 | 65.5889 | 0.87686 | 60.5033 | -0.073704
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94904 | 65.4839 | 0.87693 | 60.5083 | -0.07211
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94961 | 65.5232 | 0.87755 | 60.5509 | -0.072063
S2-Fixes | 38% | Liberty | McCreary | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95915 | 66.1813 | 0.87931 | 60.6727 | -0.079835
S2-Fixes | 38% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95581 | 65.9511 | 0.87953 | 60.6877 | -0.07628
S2-Fixes | 38% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95582 | 65.9518 | 0.8812 | 60.8029 | -0.074622
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97833 | 67.5046 | 0.88122 | 60.8042 | -0.097106
S2-Fixes | 38% | Liberty | McCreary | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95676 | 66.0164 | 0.8818 | 60.8439 | -0.074965
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98479 | 67.9502 | 0.8819 | 60.8512 | -0.10288
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97833 | 67.5046 | 0.88191 | 60.8515 | -0.096422
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97833 | 67.5046 | 0.88197 | 60.8561 | -0.096354
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99076 | 68.3625 | 0.88221 | 60.8727 | -0.10855
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97833 | 67.5046 | 0.88229 | 60.8783 | -0.096033
S2-Fixes | 38% | Liberty | McCreary | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95728 | 66.0521 | 0.88236 | 60.8826 | -0.074921
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9773 | 67.434 | 0.88252 | 60.8937 | -0.094786
S2-Fixes | 38% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9588 | 66.1572 | 0.8826 | 60.8997 | -0.076196
S2-Fixes | 38% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0156 | 70.0765 | 0.88508 | 61.0709 | -0.13052
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99333 | 68.5397 | 0.8851 | 61.0718 | -0.10823
S2-Fixes | 38% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9542 | 65.8401 | 0.8855 | 61.0995 | -0.068705
S2-Fixes | 38% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95451 | 65.861 | 0.88583 | 61.122 | -0.068681
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0013 | 69.0898 | 0.88652 | 61.1699 | -0.11478
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96219 | 66.3914 | 0.88695 | 61.1996 | -0.075244
S2-Fixes | 38% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99326 | 68.5348 | 0.88696 | 61.2001 | -0.1063
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96227 | 66.3963 | 0.88703 | 61.2049 | -0.075238
S2-Fixes | 38% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0174 | 70.2013 | 0.88716 | 61.2141 | -0.13025
S2-Fixes | 38% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99331 | 68.5384 | 0.88777 | 61.2565 | -0.10553
S2-Fixes | 38% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99326 | 68.5348 | 0.888 | 61.2721 | -0.10526
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98479 | 67.9502 | 0.8884 | 61.2993 | -0.096389
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0172 | 70.1866 | 0.88857 | 61.3116 | -0.12862
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99076 | 68.3625 | 0.88861 | 61.3142 | -0.10215
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99076 | 68.3625 | 0.88869 | 61.3194 | -0.10207
S2-Fixes | 38% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99331 | 68.5384 | 0.88881 | 61.3279 | -0.1045
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98479 | 67.9502 | 0.88907 | 61.3461 | -0.095711
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0191 | 70.3177 | 0.8891 | 61.3479 | -0.13
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98479 | 67.9502 | 0.88914 | 61.3508 | -0.095643
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98479 | 67.9502 | 0.88946 | 61.3728 | -0.095324
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98533 | 67.9876 | 0.88955 | 61.3791 | -0.095776
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95544 | 65.9253 | 0.88955 | 61.3792 | -0.065886
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9773 | 67.434 | 0.88962 | 61.3839 | -0.087682
S2-Fixes | 38% | Liberty | McCreary | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96034 | 66.2631 | 0.88963 | 61.3843 | -0.070708
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95499 | 65.8944 | 0.88964 | 61.3851 | -0.065352
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9773 | 67.434 | 0.88968 | 61.3881 | -0.087621
S2-Fixes | 38% | Liberty | McCreary | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96923 | 66.8766 | 0.89001 | 61.4105 | -0.079219
S2-Fixes | 38% | Liberty | McCreary | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96923 | 66.8766 | 0.89005 | 61.4131 | -0.079181
S2-Fixes | 38% | Liberty | McCreary | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96941 | 66.889 | 0.8902 | 61.4241 | -0.079202
S2-Fixes | 38% | Liberty | McCreary | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96941 | 66.889 | 0.89024 | 61.4267 | -0.079165
S2-Fixes | 38% | Liberty | McCreary | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96968 | 66.9082 | 0.89024 | 61.4267 | -0.079443
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97195 | 67.0648 | 0.89055 | 61.448 | -0.081403
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97215 | 67.0786 | 0.89077 | 61.4631 | -0.081385
S2-Fixes | 38% | Liberty | McCreary | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97231 | 67.0891 | 0.89087 | 61.4698 | -0.08144
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9773 | 67.434 | 0.89089 | 61.4713 | -0.086415
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9773 | 67.434 | 0.89137 | 61.5044 | -0.085936
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99333 | 68.5397 | 0.89148 | 61.5119 | -0.10185
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99333 | 68.5397 | 0.89155 | 61.5171 | -0.10178
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95499 | 65.8944 | 0.89167 | 61.525 | -0.063325
S2-Fixes | 38% | Liberty | McCreary | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96935 | 66.8854 | 0.89174 | 61.53 | -0.077615
S2-Fixes | 38% | Liberty | McCreary | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96935 | 66.8854 | 0.89177 | 61.5324 | -0.077579
S2-Fixes | 38% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98596 | 68.0313 | 0.89212 | 61.5565 | -0.093837
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95708 | 66.0383 | 0.89225 | 61.5653 | -0.064826
S2-Fixes | 38% | Liberty | McCreary | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95745 | 66.0642 | 0.89228 | 61.5675 | -0.06517
S2-Fixes | 38% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0156 | 70.0765 | 0.89233 | 61.5708 | -0.12327
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 1.0013 | 69.0898 | 0.89239 | 61.5746 | -0.10892
S2-Fixes | 38% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0156 | 70.0765 | 0.89242 | 61.5768 | -0.12318
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96219 | 66.3914 | 0.8926 | 61.5892 | -0.069597
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96227 | 66.3963 | 0.89267 | 61.5945 | -0.069592
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96219 | 66.3914 | 0.89282 | 61.6048 | -0.069371
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96227 | 66.3963 | 0.8929 | 61.6101 | -0.069365
S2-Fixes | 38% | Liberty | McCreary | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.96841 | 66.8203 | 0.89296 | 61.6144 | -0.075448
S2-Fixes | 38% | Liberty | McCreary | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95329 | 65.7769 | 0.89317 | 61.6289 | -0.060116
S2-Fixes | 38% | Liberty | McCreary | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95329 | 65.7769 | 0.89351 | 61.652 | -0.059782
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98911 | 68.2489 | 0.89375 | 61.6688 | -0.095364
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0013 | 69.0898 | 0.89377 | 61.6703 | -0.10753
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0013 | 69.0898 | 0.89385 | 61.6755 | -0.10745
S2-Fixes | 38% | Liberty | McCreary | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96718 | 66.7357 | 0.89397 | 61.6839 | -0.073214
S2-Fixes | 38% | Liberty | McCreary | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96718 | 66.7357 | 0.894 | 61.686 | -0.073184
S2-Fixes | 38% | Liberty | McCreary | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95745 | 66.0642 | 0.8943 | 61.707 | -0.063149
S2-Fixes | 38% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0174 | 70.2013 | 0.89439 | 61.7129 | -0.12302
S2-Fixes | 38% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0174 | 70.2013 | 0.89448 | 61.7189 | -0.12293
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95544 | 65.9253 | 0.89506 | 61.7594 | -0.060375
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95544 | 65.9253 | 0.89527 | 61.7733 | -0.060173
S2-Fixes | 38% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95434 | 65.8492 | 0.89529 | 61.7753 | -0.059042
S2-Fixes | 38% | Liberty | McCreary | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96034 | 66.2631 | 0.8953 | 61.7759 | -0.065032
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98533 | 67.9876 | 0.8954 | 61.7828 | -0.089924
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98533 | 67.9876 | 0.89547 | 61.7876 | -0.089854
S2-Fixes | 38% | Liberty | McCreary | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96034 | 66.2631 | 0.89552 | 61.7907 | -0.064817
S2-Fixes | 38% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95434 | 65.8492 | 0.89562 | 61.7981 | -0.058712
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0172 | 70.1866 | 0.89573 | 61.8053 | -0.12147
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0172 | 70.1866 | 0.89581 | 61.8112 | -0.12138
S2-Fixes | 38% | Liberty | McCreary | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96899 | 66.8603 | 0.89593 | 61.8189 | -0.073064
S2-Fixes | 38% | Liberty | McCreary | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96899 | 66.8603 | 0.89596 | 61.8209 | -0.073035
S2-Fixes | 38% | Liberty | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.95056 | 65.5889 | 0.89611 | 61.8318 | -0.054451
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94972 | 65.5308 | 0.89624 | 61.8407 | -0.053479
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97195 | 67.0648 | 0.89625 | 61.8416 | -0.075699
S2-Fixes | 38% | Liberty | McCreary | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0163 | 163.6246 | 0.89631 | 144.3053 | -0.12
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0191 | 70.3177 | 0.89631 | 61.8456 | -0.12278
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0191 | 70.3177 | 0.8964 | 61.8515 | -0.1227
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95708 | 66.0383 | 0.89645 | 61.8554 | -0.060622
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97215 | 67.0786 | 0.89647 | 61.8566 | -0.075682
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97195 | 67.0648 | 0.8965 | 61.8584 | -0.075455
S2-Fixes | 38% | Liberty | McCreary | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.98093 | 157.9305 | 0.89651 | 144.3383 | -0.084424
S2-Fixes | 38% | Liberty | McCreary | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97231 | 67.0891 | 0.89657 | 61.8633 | -0.075737
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94904 | 65.4839 | 0.89661 | 61.8659 | -0.052434
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97215 | 67.0786 | 0.89672 | 61.8734 | -0.075438
S2-Fixes | 38% | Liberty | McCreary | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97231 | 67.0891 | 0.89681 | 61.8801 | -0.075493
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94961 | 65.5232 | 0.89721 | 61.9076 | -0.0524
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95499 | 65.8944 | 0.89734 | 61.9164 | -0.057653
S2-Fixes | 38% | Liberty | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.97197 | 67.0657 | 0.89736 | 61.9179 | -0.074606
S2-Fixes | 38% | Liberty | McCreary | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95602 | 65.965 | 0.89754 | 61.93 | -0.058479
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95499 | 65.8944 | 0.89754 | 61.9304 | -0.057449
S2-Fixes | 38% | Liberty | McCreary | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94827 | 65.4303 | 0.8976 | 61.9347 | -0.050661
S2-Fixes | 38% | Liberty | McCreary | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95602 | 65.9654 | 0.8976 | 61.9347 | -0.058415
S2-Fixes | 38% | Liberty | McCreary | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96958 | 66.9007 | 0.89804 | 61.9647 | -0.071536
S2-Fixes | 38% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95692 | 66.0272 | 0.89804 | 61.9651 | -0.058871
S2-Fixes | 38% | Liberty | McCreary | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96958 | 66.9007 | 0.89807 | 61.9666 | -0.071509
S2-Fixes | 38% | Liberty | McCreary | 341893 | 2MT OLIVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.002 | 69.137 | 0.89824 | 61.9784 | -0.10375
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94904 | 65.4839 | 0.89829 | 61.9822 | -0.050748
S2-Fixes | 38% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95692 | 66.0272 | 0.89837 | 61.9878 | -0.058542
S2-Fixes | 38% | Liberty | McCreary | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97088 | 66.9908 | 0.89843 | 61.9917 | -0.072451
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.94904 | 65.4839 | 0.89858 | 62.0023 | -0.050457
S2-Fixes | 38% | Liberty | McCreary | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95329 | 65.7769 | 0.89859 | 62.0029 | -0.054696
S2-Fixes | 38% | Liberty | McCreary | 341896 | 2MT OLIVE J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.0009 | 69.0609 | 0.89866 | 62.0077 | -0.10222
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95708 | 66.0383 | 0.8988 | 62.0172 | -0.058278
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94961 | 65.5232 | 0.8989 | 62.0238 | -0.050716
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.94972 | 65.5308 | 0.89895 | 62.0276 | -0.050771
S2-Fixes | 38% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98596 | 68.0313 | 0.89915 | 62.0413 | -0.086812
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.94961 | 65.5232 | 0.89919 | 62.0439 | -0.050425
S2-Fixes | 38% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98596 | 68.0313 | 0.89921 | 62.0455 | -0.086751
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94972 | 65.5308 | 0.89938 | 62.0575 | -0.050337
S2-Fixes | 38% | Liberty | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.95056 | 65.5889 | 0.89945 | 62.0619 | -0.051115
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98911 | 68.2489 | 0.89957 | 62.0706 | -0.08954
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98911 | 68.2489 | 0.89964 | 62.0754 | -0.089471
S2-Fixes | 45% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9607 | 66.2885 | 0.7869 | 54.2961 | -0.1738
S2-Fixes | 45% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96075 | 66.2916 | 0.78697 | 54.3009 | -0.17378
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.94957 | 65.5202 | 0.78811 | 54.3795 | -0.16146
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96065 | 66.2846 | 0.80158 | 55.3087 | -0.15907
S2-Fixes | 45% | Liberty | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95235 | 65.7124 | 0.8169 | 56.366 | -0.13546
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96723 | 66.7391 | 0.8217 | 56.6974 | -0.14553
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96744 | 66.7537 | 0.82195 | 56.7146 | -0.14549
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96551 | 66.6202 | 0.82983 | 57.2585 | -0.13568
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95696 | 66.03 | 0.83053 | 57.3065 | -0.12643
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95703 | 66.0352 | 0.83062 | 57.3125 | -0.12642
S2-Fixes | 45% | Liberty | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94748 | 65.3764 | 0.83377 | 57.5298 | -0.11372
S2-Fixes | 45% | Liberty | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9478 | 65.3985 | 0.83413 | 57.5549 | -0.11368
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98579 | 68.0192 | 0.83795 | 57.8188 | -0.14783
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98579 | 68.0192 | 0.83954 | 57.9286 | -0.14624
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9885 | 68.2065 | 0.84115 | 58.0393 | -0.14735
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98382 | 67.8836 | 0.84143 | 58.0583 | -0.1424
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9885 | 68.2065 | 0.84274 | 58.1487 | -0.14576
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0164 | 70.1284 | 0.84282 | 58.1547 | -0.17353
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98382 | 67.8836 | 0.84293 | 58.1621 | -0.14089
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98781 | 68.1589 | 0.8461 | 58.3807 | -0.14171
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98781 | 68.1589 | 0.84759 | 58.4838 | -0.14022
S2-Fixes | 45% | Liberty | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94915 | 65.4911 | 0.84919 | 58.5941 | -0.099957
S2-Fixes | 45% | Liberty | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95156 | 65.6577 | 0.84939 | 58.6079 | -0.10217
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94988 | 65.5417 | 0.85206 | 58.7923 | -0.097817
S2-Fixes | 45% | Liberty | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9541 | 65.8328 | 0.85389 | 58.9185 | -0.10021
S2-Fixes | 45% | Liberty | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95434 | 65.8496 | 0.85416 | 58.9373 | -0.10018
S2-Fixes | 45% | Liberty | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94924 | 65.4975 | 0.85446 | 58.958 | -0.094774
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99189 | 68.4406 | 0.85905 | 59.2743 | -0.13285
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9752 | 67.2887 | 0.85995 | 59.3363 | -0.11525
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99213 | 68.4569 | 0.86029 | 59.3597 | -0.13184
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99189 | 68.4406 | 0.86042 | 59.3688 | -0.13148
S2-Fixes | 45% | Liberty | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94924 | 65.4975 | 0.86052 | 59.3759 | -0.088718
S2-Fixes | 45% | Liberty | W Garrard | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96177 | 66.3622 | 0.86119 | 59.4223 | -0.10058
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99213 | 68.4569 | 0.86164 | 59.4534 | -0.13049
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94385 | 65.1254 | 0.86195 | 59.4746 | -0.081896
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94475 | 65.1877 | 0.86199 | 59.4773 | -0.082759
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94316 | 65.0781 | 0.86218 | 59.4904 | -0.08098
S2-Fixes | 45% | Liberty | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94915 | 65.4911 | 0.86232 | 59.5004 | -0.086822
S2-Fixes | 45% | Liberty | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95156 | 65.6577 | 0.86283 | 59.5354 | -0.088728
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94376 | 65.1197 | 0.86284 | 59.536 | -0.080923
S2-Fixes | 45% | Liberty | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95402 | 65.8271 | 0.86434 | 59.6396 | -0.089673
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9752 | 67.2887 | 0.86472 | 59.6655 | -0.11048
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9752 | 67.2887 | 0.86479 | 59.6708 | -0.11041
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98579 | 68.0192 | 0.86702 | 59.8247 | -0.11876
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95156 | 65.6576 | 0.8671 | 59.8299 | -0.08446
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98382 | 67.8836 | 0.86733 | 59.846 | -0.11649
S2-Fixes | 45% | Liberty | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94748 | 65.3764 | 0.86751 | 59.8583 | -0.079973
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95208 | 65.6935 | 0.86767 | 59.8693 | -0.084409
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98201 | 67.7589 | 0.86768 | 59.87 | -0.11433
S2-Fixes | 45% | Liberty | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9478 | 65.3985 | 0.86786 | 59.8824 | -0.079943
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97416 | 67.2169 | 0.86905 | 59.9647 | -0.1051
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9752 | 67.2887 | 0.86994 | 60.0262 | -0.10525
S2-Fixes | 45% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0149 | 70.0281 | 0.8701 | 60.0372 | -0.1448
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9885 | 68.2065 | 0.87011 | 60.0378 | -0.11839
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98579 | 68.0192 | 0.87126 | 60.1166 | -0.11453
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98579 | 68.0192 | 0.87134 | 60.1226 | -0.11444
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98382 | 67.8836 | 0.87143 | 60.1288 | -0.11239
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98382 | 67.8836 | 0.87152 | 60.1347 | -0.1123
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99934 | 68.9543 | 0.87171 | 60.1478 | -0.12763
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98781 | 68.1589 | 0.87186 | 60.1586 | -0.11595
S2-Fixes | 45% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0168 | 70.1594 | 0.87233 | 60.1905 | -0.14448
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98201 | 67.7589 | 0.87241 | 60.1962 | -0.1096
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98201 | 67.7589 | 0.87248 | 60.2014 | -0.10953
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.94957 | 65.5202 | 0.87267 | 60.214 | -0.0769
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9752 | 67.2887 | 0.87326 | 60.2552 | -0.10194
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94957 | 65.5202 | 0.87354 | 60.274 | -0.076032
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97416 | 67.2169 | 0.87374 | 60.288 | -0.10042
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97416 | 67.2169 | 0.87381 | 60.2927 | -0.10035
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0164 | 70.1284 | 0.87391 | 60.2995 | -0.14245
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9885 | 68.2065 | 0.87433 | 60.3287 | -0.11417
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0186 | 70.2819 | 0.8744 | 60.3336 | -0.14418
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9885 | 68.2065 | 0.87442 | 60.3347 | -0.11408
S2-Fixes | 45% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0149 | 70.0281 | 0.87483 | 60.3635 | -0.14007
S2-Fixes | 45% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0149 | 70.0281 | 0.87493 | 60.3702 | -0.13997
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95696 | 66.03 | 0.8754 | 60.4029 | -0.081552
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94955 | 65.5192 | 0.87543 | 60.4047 | -0.074123
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95703 | 66.0352 | 0.87549 | 60.4086 | -0.081545
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98781 | 68.1589 | 0.87594 | 60.44 | -0.11187
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98781 | 68.1589 | 0.87603 | 60.4458 | -0.11178
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99934 | 68.9543 | 0.87647 | 60.4765 | -0.12287
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99934 | 68.9543 | 0.87656 | 60.4823 | -0.12278
S2-Fixes | 45% | Liberty | W Garrard | 341893 | 2MT OLIVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99754 | 68.8303 | 0.87702 | 60.5143 | -0.12052
S2-Fixes | 45% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0168 | 70.1594 | 0.87704 | 60.516 | -0.13976
S2-Fixes | 45% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0168 | 70.1594 | 0.87714 | 60.5226 | -0.13966
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98201 | 67.7589 | 0.87759 | 60.5536 | -0.10442
S2-Fixes | 45% | Liberty | W Garrard | 341896 | 2MT OLIVE J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99683 | 68.7815 | 0.87816 | 60.5928 | -0.11868
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95513 | 65.9041 | 0.87816 | 60.5929 | -0.076973
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95216 | 65.6988 | 0.87826 | 60.5997 | -0.073901
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96551 | 66.6202 | 0.87845 | 60.613 | -0.087062
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0164 | 70.1284 | 0.87858 | 60.6217 | -0.13778
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96723 | 66.7391 | 0.87866 | 60.6277 | -0.088571
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0164 | 70.1284 | 0.87867 | 60.6283 | -0.13768
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94988 | 65.5417 | 0.87876 | 60.6344 | -0.07112
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96744 | 66.7537 | 0.87889 | 60.6437 | -0.08855
S2-Fixes | 45% | Liberty | W Garrard | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96761 | 66.7649 | 0.87899 | 60.6506 | -0.088612
S2-Fixes | 45% | Liberty | W Garrard | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0181 | 163.9182 | 0.8791 | 141.535 | -0.13903
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0186 | 70.2819 | 0.87911 | 60.6583 | -0.13947
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0186 | 70.2819 | 0.8792 | 60.6649 | -0.13938
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95696 | 66.03 | 0.87932 | 60.6728 | -0.077641
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9833 | 67.8474 | 0.87932 | 60.673 | -0.10398
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95703 | 66.0352 | 0.8794 | 60.6784 | -0.077634
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95696 | 66.03 | 0.87954 | 60.688 | -0.07742
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97416 | 67.2169 | 0.8796 | 60.6927 | -0.094554
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95703 | 66.0352 | 0.87962 | 60.6937 | -0.077413
S2-Fixes | 45% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.9607 | 66.2885 | 0.87967 | 60.6976 | -0.081027
S2-Fixes | 45% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96075 | 66.2916 | 0.87973 | 60.7015 | -0.081017
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.99934 | 68.9543 | 0.87998 | 60.7189 | -0.11935
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.9473 | 65.3638 | 0.88014 | 60.7296 | -0.067162
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9473 | 65.3638 | 0.88043 | 60.7496 | -0.066872
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94955 | 65.5192 | 0.88066 | 60.7658 | -0.068889
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98201 | 67.7589 | 0.88088 | 60.7806 | -0.10113
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99189 | 68.4406 | 0.88097 | 60.7872 | -0.11092
S2-Fixes | 45% | Liberty | W Garrard | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.96311 | 66.4548 | 0.88148 | 60.822 | -0.081635
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99213 | 68.4569 | 0.88203 | 60.8604 | -0.1101
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95513 | 65.9041 | 0.88212 | 60.8662 | -0.073013
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95513 | 65.9041 | 0.88233 | 60.8806 | -0.072804
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94988 | 65.5417 | 0.88257 | 60.8971 | -0.067313
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96723 | 66.7391 | 0.88262 | 60.9011 | -0.084609
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94988 | 65.5417 | 0.88276 | 60.9107 | -0.067115
S2-Fixes | 45% | Liberty | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94783 | 65.4002 | 0.88284 | 60.9161 | -0.064987
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96744 | 66.7537 | 0.88286 | 60.9171 | -0.084588
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96723 | 66.7391 | 0.88286 | 60.9175 | -0.084371
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94475 | 65.1877 | 0.88289 | 60.9193 | -0.061861
S2-Fixes | 45% | Liberty | W Garrard | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97785 | 157.4337 | 0.8829 | 142.1467 | -0.09495
S2-Fixes | 45% | Liberty | W Garrard | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96761 | 66.7649 | 0.88296 | 60.924 | -0.084651
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94385 | 65.1254 | 0.88307 | 60.9316 | -0.060779
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96744 | 66.7537 | 0.88309 | 60.9335 | -0.08435
S2-Fixes | 45% | Liberty | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94783 | 65.4002 | 0.88317 | 60.9388 | -0.064657
S2-Fixes | 45% | Liberty | W Garrard | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96761 | 66.7649 | 0.88319 | 60.9404 | -0.084412
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95216 | 65.6988 | 0.88347 | 60.9597 | -0.068683
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94316 | 65.0781 | 0.88352 | 60.9628 | -0.059641
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9833 | 67.8474 | 0.88395 | 60.9924 | -0.099347
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9833 | 67.8474 | 0.88402 | 60.997 | -0.09928
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97416 | 67.2169 | 0.88406 | 61.0001 | -0.090099
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94376 | 65.1197 | 0.88416 | 61.0073 | -0.0596
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94849 | 65.4457 | 0.88422 | 61.0113 | -0.064266
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94849 | 65.4461 | 0.88429 | 61.0164 | -0.0642
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94955 | 65.5192 | 0.88462 | 61.0387 | -0.064935
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96065 | 66.2846 | 0.88477 | 61.0492 | -0.075876
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99189 | 68.4406 | 0.88481 | 61.0521 | -0.10708
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94955 | 65.5192 | 0.88482 | 61.0523 | -0.064737
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94957 | 65.5202 | 0.88487 | 61.0564 | -0.064693
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99189 | 68.4406 | 0.88489 | 61.0576 | -0.107
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96065 | 66.2846 | 0.88563 | 61.1082 | -0.075021
S2-Fixes | 45% | Liberty | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95056 | 65.5886 | 0.88578 | 61.1185 | -0.064784
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99213 | 68.4569 | 0.88584 | 61.1232 | -0.10629
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99213 | 68.4569 | 0.88592 | 61.1287 | -0.10621
S2-Fixes | 45% | Liberty | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95056 | 65.5886 | 0.8861 | 61.1411 | -0.064456
S2-Fixes | 45% | Liberty | W Garrard | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96547 | 66.6172 | 0.88616 | 61.145 | -0.079307
S2-Fixes | 45% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94124 | 64.9457 | 0.88697 | 61.2009 | -0.054273
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95216 | 65.6988 | 0.88741 | 61.2316 | -0.064742
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94988 | 65.5417 | 0.88745 | 61.2343 | -0.062426
S2-Fixes | 45% | Liberty | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95235 | 65.7124 | 0.88761 | 61.2449 | -0.064746
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95216 | 65.6988 | 0.88761 | 61.2452 | -0.064544
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94316 | 65.0781 | 0.88842 | 61.3009 | -0.054741
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.9473 | 65.3638 | 0.88847 | 61.3047 | -0.058828
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95513 | 65.9041 | 0.88878 | 61.3258 | -0.066351
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94376 | 65.1197 | 0.88906 | 61.3452 | -0.054704
S2-Fixes | 45% | Liberty | W Garrard | 341343 | 2CONTOWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99407 | 68.5907 | 0.88951 | 61.3765 | -0.10455
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94385 | 65.1254 | 0.88953 | 61.3775 | -0.054318
S2-Fixes | 45% | Liberty | W Garrard | 341342 | 2CONTOWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99419 | 68.5991 | 0.88965 | 61.3858 | -0.10454
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9833 | 67.8474 | 0.88974 | 61.3923 | -0.093552
S2-Fixes | 45% | Liberty | W Garrard | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94788 | 65.4038 | 0.89009 | 61.4161 | -0.057792
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96551 | 66.6202 | 0.8903 | 61.4309 | -0.075208
S2-Fixes | 45% | Liberty | W Garrard | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94788 | 65.4038 | 0.89036 | 61.435 | -0.057518
S2-Fixes | 45% | Liberty | W Garrard | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96473 | 66.5662 | 0.89044 | 61.4402 | -0.074289
S2-Fixes | 45% | Liberty | W Garrard | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96473 | 66.5662 | 0.89048 | 61.4429 | -0.074251
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94316 | 65.0781 | 0.89063 | 61.4532 | -0.052534
S2-Fixes | 45% | Liberty | W Garrard | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96491 | 66.5787 | 0.89063 | 61.4538 | -0.074274
S2-Fixes | 45% | Liberty | W Garrard | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96491 | 66.5787 | 0.89067 | 61.4564 | -0.074236
S2-Fixes | 45% | Liberty | W Garrard | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96525 | 66.602 | 0.89067 | 61.4564 | -0.074573
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94385 | 65.1254 | 0.8907 | 61.458 | -0.053151
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94475 | 65.1877 | 0.89082 | 61.4666 | -0.053929
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94475 | 65.1877 | 0.891 | 61.4788 | -0.053753
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94376 | 65.1197 | 0.89127 | 61.4973 | -0.052498
S2-Fixes | 45% | Liberty | W Garrard | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94913 | 65.49 | 0.89156 | 61.5178 | -0.057569
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94316 | 65.0781 | 0.89192 | 61.5422 | -0.051244
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94385 | 65.1254 | 0.89199 | 61.547 | -0.051861
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95696 | 66.03 | 0.892 | 61.5478 | -0.06496
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95703 | 66.0352 | 0.89208 | 61.5533 | -0.064954
S2-Fixes | 45% | Liberty | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9541 | 65.8328 | 0.89212 | 61.5562 | -0.061979
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.9473 | 65.3638 | 0.89216 | 61.5589 | -0.055144
S2-Fixes | 45% | Liberty | W Garrard | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96456 | 66.5548 | 0.89217 | 61.5596 | -0.072393
S2-Fixes | 45% | Liberty | W Garrard | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95037 | 65.5755 | 0.89218 | 61.5602 | -0.058192
S2-Fixes | 45% | Liberty | W Garrard | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96456 | 66.5548 | 0.8922 | 61.5621 | -0.072357
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94316 | 65.0781 | 0.89225 | 61.5651 | -0.050913
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94475 | 65.1877 | 0.89229 | 61.5678 | -0.052462
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.9473 | 65.3638 | 0.89234 | 61.5712 | -0.054965
S2-Fixes | 45% | Liberty | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95434 | 65.8496 | 0.89238 | 61.5742 | -0.061962
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94316 | 65.0781 | 0.89243 | 61.5773 | -0.050735
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94376 | 65.1197 | 0.89256 | 61.5863 | -0.051209
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94376 | 65.1197 | 0.89289 | 61.6091 | -0.050878
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94376 | 65.1197 | 0.89306 | 61.6214 | -0.050701
S2-Fixes | 45% | Liberty | W Garrard | 342067 | 2PHIL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.9738 | 67.1925 | 0.8932 | 61.6306 | -0.080607
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94385 | 65.1254 | 0.89337 | 61.6423 | -0.05048
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94385 | 65.1254 | 0.89354 | 61.6545 | -0.050303
S2-Fixes | 45% | Liberty | W Garrard | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94746 | 65.375 | 0.89357 | 61.6567 | -0.053889
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9833 | 67.8474 | 0.89415 | 61.6961 | -0.089149
S2-Fixes | 45% | Liberty | W Garrard | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96201 | 66.3788 | 0.89459 | 61.7267 | -0.067423
S2-Fixes | 45% | Liberty | W Garrard | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96201 | 66.3788 | 0.89462 | 61.7287 | -0.067393
S2-Fixes | 45% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.9607 | 66.2885 | 0.89464 | 61.7304 | -0.066058
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94475 | 65.1877 | 0.89466 | 61.7318 | -0.050085
S2-Fixes | 45% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96075 | 66.2916 | 0.8947 | 61.7342 | -0.06605
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94475 | 65.1877 | 0.89484 | 61.744 | -0.049909
S2-Fixes | 45% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94124 | 64.9457 | 0.89549 | 61.7888 | -0.045752
S2-Fixes | 45% | Liberty | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95402 | 65.8271 | 0.8955 | 61.7897 | -0.058513
S2-Fixes | 45% | Liberty | W Garrard | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 0.96311 | 66.4548 | 0.89567 | 61.8011 | -0.067444
S2-Fixes | 45% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94124 | 64.9457 | 0.89572 | 61.8044 | -0.045527
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95156 | 65.6576 | 0.89595 | 61.8206 | -0.055609
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95208 | 65.6935 | 0.8965 | 61.8587 | -0.055577
S2-Fixes | 45% | Liberty | W Garrard | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96392 | 66.5106 | 0.89665 | 61.8685 | -0.067277
S2-Fixes | 45% | Liberty | W Garrard | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96392 | 66.5106 | 0.89667 | 61.8706 | -0.067247
S2-Fixes | 45% | Liberty | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95402 | 65.8271 | 0.89676 | 61.8762 | -0.057259
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95156 | 65.6576 | 0.89679 | 61.8784 | -0.054772
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96065 | 66.2846 | 0.8968 | 61.8794 | -0.063844
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94849 | 65.4457 | 0.89697 | 61.8912 | -0.051514
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4457 | 0.89698 | 61.8917 | -0.051508
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94849 | 65.4461 | 0.89702 | 61.8946 | -0.051472
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4461 | 0.89703 | 61.895 | -0.051466
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4457 | 0.89733 | 61.9158 | -0.051157
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94316 | 65.0781 | 0.89733 | 61.916 | -0.045827
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95208 | 65.6935 | 0.89734 | 61.9164 | -0.05474
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4461 | 0.89738 | 61.9192 | -0.051115
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94376 | 65.1197 | 0.89797 | 61.9598 | -0.045796
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95156 | 65.6576 | 0.89804 | 61.9647 | -0.053521
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95208 | 65.6935 | 0.89859 | 62.0027 | -0.05349
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96551 | 66.6202 | 0.8987 | 62.0106 | -0.066806
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94385 | 65.1254 | 0.89872 | 62.0119 | -0.045123
S2-Fixes | 45% | Liberty | W Garrard | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96448 | 66.5494 | 0.89889 | 62.0236 | -0.065592
S2-Fixes | 45% | Liberty | W Garrard | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96448 | 66.5494 | 0.89892 | 62.0255 | -0.065565
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94316 | 65.0781 | 0.89911 | 62.0384 | -0.044053
S2-Fixes | 45% | Liberty | W Garrard | 339208 | AE2-254 MAIN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98943 | 68.2706 | 0.89938 | 62.0569 | -0.090054
S2-Fixes | 45% | Liberty | W Garrard | 342205 | 2S LANCASTER | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98943 | 68.2706 | 0.89938 | 62.0569 | -0.090054
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94376 | 65.1197 | 0.89974 | 62.0821 | -0.044024
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95156 | 65.6576 | 0.89984 | 62.0891 | -0.051718
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342193 | 2S FLOYD | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96148 |  | 0.85824 |  | -0.08176
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341473 | 2FLOYD-SFL | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96167 |  | 0.85845 |  | -0.081555
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341210 | 2BROUGHT TW | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96155 |  | 0.85885 |  | -0.081153
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342364 | 2TOMM GOOC | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97302 |  | 0.85909 |  | -0.08091
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342367 | 2TOMM GOOC | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97306 |  | 0.85914 |  | -0.080863
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341470 | 2FLOYD EK | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95576 |  | 0.86546 |  | -0.074538
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341471 | 2FLOYD TAP | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95582 |  | 0.86553 |  | -0.074466
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341848 | 2MCKEE | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96647 |  | 0.86823 |  | -0.071769
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341209 | 2BROUGTWN T | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97092 |  | 0.86942 |  | -0.070583
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342220 | 2SAND GAP | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96303 |  | 0.88176 |  | -0.058242
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342223 | 2SAND GAP T | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9633 |  | 0.88205 |  | -0.057946
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342511 | 2WOODSTOCK | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95339 |  | 0.88293 |  | -0.057073
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341617 | 2HIGHLAND E | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97213 |  | 0.88967 |  | -0.050326
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341641 | 2HOMESTEAD | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98628 |  | 0.89281 |  | -0.047194
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341115 | 2BIG HILL T | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96482 |  | 0.89403 |  | -0.045968
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341114 | 2BIG HILL | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96875 |  | 0.89656 |  | -0.043443
S2-Fixes | 25% | Liberty | W Garrard LibJ | 342346 | 2THREE LINK | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9647 |  | 0.89779 |  | -0.042215
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341887 | 2MONTICELLO | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.99207 |  | 0.89921 |  | -0.040792
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95679 | 66.0186 | 0.7829 | 54.0203 | -0.17389
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95684 | 66.0219 | 0.78297 | 54.0252 | -0.17386
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.94577 | 65.2581 | 0.78416 | 54.1069 | -0.16161
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9569 | 66.0258 | 0.7977 | 55.041 | -0.1592
S2-Fixes | 45% | Liberty | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94616 | 65.2848 | 0.81039 | 55.9167 | -0.13577
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96191 | 66.3717 | 0.81432 | 56.1882 | -0.14759
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96212 | 66.3864 | 0.81457 | 56.2056 | -0.14755
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95136 | 65.6439 | 0.82323 | 56.8031 | -0.12813
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95144 | 65.6491 | 0.82332 | 56.8092 | -0.12811
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.962 | 66.378 | 0.82617 | 57.0055 | -0.13583
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94143 | 64.9585 | 0.8274 | 57.0905 | -0.11403
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94175 | 64.9808 | 0.82777 | 57.1158 | -0.11398
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98442 | 67.9253 | 0.83436 | 57.5708 | -0.15006
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98442 | 67.9253 | 0.83595 | 57.6807 | -0.14847
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98714 | 68.1128 | 0.83757 | 57.7922 | -0.14957
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98247 | 67.7905 | 0.83785 | 57.8114 | -0.14462
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98714 | 68.1128 | 0.83916 | 57.9017 | -0.14799
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0145 | 70.0028 | 0.83924 | 57.9076 | -0.17529
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98247 | 67.7905 | 0.83935 | 57.9153 | -0.14312
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98647 | 68.0661 | 0.84254 | 58.1349 | -0.14393
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94321 | 65.0812 | 0.84296 | 58.1644 | -0.10024
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9455 | 65.2392 | 0.84302 | 58.1682 | -0.10248
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94867 | 65.4582 | 0.84389 | 58.2286 | -0.10478
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98647 | 68.0661 | 0.84403 | 58.2382 | -0.14243
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94891 | 65.4751 | 0.84417 | 58.2476 | -0.10475
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.944 | 65.1363 | 0.84499 | 58.3042 | -0.099016
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.90906 | 62.7254 | 0.84625 | 58.3915 | -0.062809
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.91094 | 62.8552 | 0.84828 | 58.531 | -0.062668
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94336 | 65.0919 | 0.84832 | 58.5337 | -0.095046
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97173 | 67.0492 | 0.84948 | 58.6142 | -0.12225
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94336 | 65.0919 | 0.85061 | 58.6918 | -0.092755
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94321 | 65.0812 | 0.85243 | 58.8178 | -0.090773
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9455 | 65.2392 | 0.85271 | 58.837 | -0.092785
S2-Fixes | 45% | Liberty | Alcalde | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95607 | 65.9691 | 0.85427 | 58.9445 | -0.10181
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93772 | 64.7029 | 0.85457 | 58.9653 | -0.083153
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93862 | 64.7649 | 0.85462 | 58.9686 | -0.084005
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97173 | 67.0492 | 0.85474 | 58.9768 | -0.11699
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93702 | 64.6542 | 0.85478 | 58.9796 | -0.082241
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97173 | 67.0492 | 0.85481 | 58.9821 | -0.11691
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93763 | 64.6962 | 0.85544 | 59.0256 | -0.082183
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99058 | 68.35 | 0.85556 | 59.0336 | -0.13502
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98442 | 67.9253 | 0.85631 | 59.0851 | -0.12812
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98247 | 67.7905 | 0.85661 | 59.1064 | -0.12586
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99083 | 68.3669 | 0.85682 | 59.1208 | -0.134
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99058 | 68.35 | 0.85693 | 59.1282 | -0.13365
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97857 | 67.521 | 0.85731 | 59.1545 | -0.12125
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94825 | 65.4293 | 0.85744 | 59.1637 | -0.090806
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94143 | 64.9585 | 0.85782 | 59.1893 | -0.083612
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94175 | 64.9808 | 0.85817 | 59.2137 | -0.083581
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99083 | 68.3669 | 0.85818 | 59.2146 | -0.13264
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.90906 | 62.7254 | 0.85867 | 59.2485 | -0.050389
S2-Fixes | 45% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.013 | 69.8996 | 0.85885 | 59.261 | -0.15418
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97039 | 66.9572 | 0.85899 | 59.2705 | -0.1114
S2-Fixes | 45% | Liberty | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.92093 | 63.5442 | 0.85902 | 59.2724 | -0.06191
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98714 | 68.1128 | 0.85943 | 59.3009 | -0.12771
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94583 | 65.2625 | 0.86027 | 59.3584 | -0.085567
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97173 | 67.0492 | 0.86066 | 59.3856 | -0.11107
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.91094 | 62.8552 | 0.86067 | 59.386 | -0.050278
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94636 | 65.2986 | 0.86084 | 59.3981 | -0.085515
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99646 | 68.7558 | 0.86089 | 59.4016 | -0.13557
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98442 | 67.9253 | 0.861 | 59.4089 | -0.12343
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98442 | 67.9253 | 0.86109 | 59.4151 | -0.12334
S2-Fixes | 45% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0149 | 70.0312 | 0.86111 | 59.4163 | -0.15384
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98247 | 67.7905 | 0.86116 | 59.4201 | -0.12131
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98647 | 68.0661 | 0.8612 | 59.4229 | -0.12526
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98247 | 67.7905 | 0.86125 | 59.426 | -0.12122
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97857 | 67.521 | 0.86252 | 59.5137 | -0.11605
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97857 | 67.521 | 0.86259 | 59.519 | -0.11597
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0145 | 70.0028 | 0.86273 | 59.5287 | -0.1518
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0167 | 70.1539 | 0.86321 | 59.5612 | -0.15352
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95136 | 65.6439 | 0.86387 | 59.607 | -0.087491
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95144 | 65.6491 | 0.86395 | 59.6127 | -0.087484
S2-Fixes | 45% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.013 | 69.8996 | 0.86407 | 59.6208 | -0.14897
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98714 | 68.1128 | 0.86411 | 59.6235 | -0.12303
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97039 | 66.9572 | 0.86415 | 59.6262 | -0.10625
S2-Fixes | 45% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.013 | 69.8996 | 0.86417 | 59.6275 | -0.14887
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98714 | 68.1128 | 0.8642 | 59.6297 | -0.12294
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97039 | 66.9572 | 0.86422 | 59.631 | -0.10618
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97173 | 67.0492 | 0.86547 | 59.7172 | -0.10626
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98647 | 68.0661 | 0.86572 | 59.7349 | -0.12074
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98647 | 68.0661 | 0.86581 | 59.7409 | -0.12066
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99646 | 68.7558 | 0.86614 | 59.7638 | -0.13032
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99646 | 68.7558 | 0.86623 | 59.7698 | -0.13023
S2-Fixes | 45% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0149 | 70.0312 | 0.86631 | 59.7751 | -0.14864
S2-Fixes | 45% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0149 | 70.0312 | 0.8664 | 59.7818 | -0.14854
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94959 | 65.522 | 0.86712 | 59.8312 | -0.082476
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.944 | 65.1363 | 0.86725 | 59.84 | -0.076759
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96191 | 66.3717 | 0.86726 | 59.8409 | -0.09465
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94577 | 65.2581 | 0.86744 | 59.853 | -0.078334
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96212 | 66.3864 | 0.86749 | 59.8571 | -0.094627
S2-Fixes | 45% | Liberty | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96229 | 66.3977 | 0.8676 | 59.8641 | -0.094689
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0145 | 70.0028 | 0.86788 | 59.884 | -0.14665
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0145 | 70.0028 | 0.86798 | 59.8907 | -0.14655
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97857 | 67.521 | 0.86839 | 59.9188 | -0.11018
S2-Fixes | 45% | Liberty | Alcalde | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0172 | 163.7671 | 0.86839 | 139.8105 | -0.1488
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0167 | 70.1539 | 0.86839 | 59.9192 | -0.14833
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0167 | 70.1539 | 0.86849 | 59.9259 | -0.14823
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94391 | 65.1301 | 0.86873 | 59.9422 | -0.075186
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97957 | 67.5901 | 0.86938 | 59.9872 | -0.11019
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.94577 | 65.2581 | 0.86947 | 59.9934 | -0.076299
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94391 | 65.1301 | 0.86969 | 60.0085 | -0.074226
S2-Fixes | 45% | Liberty | Alcalde | 341893 | 2MT OLIVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99462 | 68.6287 | 0.87051 | 60.0655 | -0.1241
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99058 | 68.35 | 0.87055 | 60.0679 | -0.12003
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97039 | 66.9572 | 0.87056 | 60.0683 | -0.099838
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.99646 | 68.7558 | 0.87062 | 60.0727 | -0.12584
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95136 | 65.6439 | 0.87076 | 60.0824 | -0.080601
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95144 | 65.6491 | 0.87084 | 60.0881 | -0.080594
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95136 | 65.6439 | 0.87101 | 60.0995 | -0.080353
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95144 | 65.6491 | 0.87109 | 60.1052 | -0.080346
S2-Fixes | 45% | Liberty | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.92093 | 63.5442 | 0.87125 | 60.1164 | -0.049679
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94653 | 65.3108 | 0.87158 | 60.1387 | -0.074958
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99083 | 68.3669 | 0.87169 | 60.1468 | -0.11913
S2-Fixes | 45% | Liberty | Alcalde | 341896 | 2MT OLIVE J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99395 | 68.5828 | 0.87176 | 60.1514 | -0.12219
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.962 | 66.378 | 0.8723 | 60.1886 | -0.089701
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94653 | 65.3108 | 0.87253 | 60.2048 | -0.074
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94142 | 64.9583 | 0.8729 | 60.2303 | -0.068521
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97857 | 67.521 | 0.87315 | 60.2474 | -0.10541
S2-Fixes | 45% | Liberty | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.9344 | 64.4738 | 0.87355 | 60.2753 | -0.060848
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94142 | 64.9583 | 0.87365 | 60.2817 | -0.067777
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.944 | 65.1363 | 0.87394 | 60.3018 | -0.070065
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94959 | 65.522 | 0.87408 | 60.3115 | -0.075515
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.944 | 65.1363 | 0.87416 | 60.3172 | -0.069842
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96191 | 66.3717 | 0.87425 | 60.3232 | -0.08766
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94959 | 65.522 | 0.87432 | 60.3278 | -0.075279
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97957 | 67.5901 | 0.87447 | 60.3386 | -0.10509
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96212 | 66.3864 | 0.87448 | 60.3393 | -0.087639
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96191 | 66.3717 | 0.87451 | 60.3414 | -0.087395
S2-Fixes | 45% | Liberty | Alcalde | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97355 | 156.7417 | 0.87453 | 140.799 | -0.099023
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97957 | 67.5901 | 0.87454 | 60.3433 | -0.10503
S2-Fixes | 45% | Liberty | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96229 | 66.3977 | 0.87458 | 60.3463 | -0.087701
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96212 | 66.3864 | 0.87475 | 60.3576 | -0.087374
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99058 | 68.35 | 0.87481 | 60.3616 | -0.11577
S2-Fixes | 45% | Liberty | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96229 | 66.3977 | 0.87485 | 60.3646 | -0.087436
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99058 | 68.35 | 0.87489 | 60.3672 | -0.11569
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99083 | 68.3669 | 0.87592 | 60.4382 | -0.11491
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99083 | 68.3669 | 0.876 | 60.4438 | -0.11483
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93862 | 64.7649 | 0.87617 | 60.456 | -0.062448
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94192 | 64.9925 | 0.87621 | 60.4586 | -0.065709
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93772 | 64.7029 | 0.87636 | 60.469 | -0.061361
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97039 | 66.9572 | 0.87637 | 60.4693 | -0.094027
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95679 | 66.0186 | 0.87647 | 60.4763 | -0.080324
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95684 | 66.0219 | 0.87652 | 60.4802 | -0.080314
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94192 | 64.9925 | 0.87654 | 60.4813 | -0.06538
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94391 | 65.1301 | 0.87663 | 60.4876 | -0.067282
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93702 | 64.6542 | 0.87683 | 60.5012 | -0.060189
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94391 | 65.1301 | 0.87686 | 60.5031 | -0.067057
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94351 | 65.102 | 0.87691 | 60.5069 | -0.066596
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94351 | 65.1023 | 0.87699 | 60.512 | -0.066526
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93702 | 64.6542 | 0.87705 | 60.5161 | -0.059973
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94142 | 64.9583 | 0.87727 | 60.5317 | -0.064153
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93763 | 64.6962 | 0.87748 | 60.546 | -0.060147
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93763 | 64.6962 | 0.87769 | 60.5609 | -0.059931
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93772 | 64.7029 | 0.8782 | 60.5955 | -0.059527
S2-Fixes | 45% | Liberty | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94616 | 65.2848 | 0.87843 | 60.612 | -0.067722
S2-Fixes | 45% | Liberty | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94467 | 65.1821 | 0.87917 | 60.6625 | -0.065501
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94653 | 65.3108 | 0.87945 | 60.6823 | -0.06708
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94577 | 65.2581 | 0.87946 | 60.6829 | -0.066307
S2-Fixes | 45% | Liberty | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94467 | 65.1821 | 0.87949 | 60.6851 | -0.065174
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93862 | 64.7649 | 0.8795 | 60.6855 | -0.059122
S2-Fixes | 45% | Liberty | Alcalde | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95987 | 66.2311 | 0.87955 | 60.689 | -0.08032
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.9569 | 66.0258 | 0.87961 | 60.6934 | -0.077282
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94653 | 65.3108 | 0.87968 | 60.6978 | -0.066855
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.944 | 65.1363 | 0.88041 | 60.7486 | -0.06359
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.93521 | 64.5298 | 0.88049 | 60.7539 | -0.054724
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97957 | 67.5901 | 0.8808 | 60.7754 | -0.098764
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.9569 | 66.0258 | 0.88162 | 60.8317 | -0.075277
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94959 | 65.522 | 0.88223 | 60.8736 | -0.067369
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94185 | 64.9876 | 0.88352 | 60.9626 | -0.058334
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94142 | 64.9583 | 0.88373 | 60.9776 | -0.057692
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93702 | 64.6542 | 0.88376 | 60.9796 | -0.053256
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94185 | 64.9876 | 0.88379 | 60.9814 | -0.058061
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93702 | 64.6542 | 0.88384 | 60.9847 | -0.053181
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93772 | 64.7029 | 0.88393 | 60.9911 | -0.053795
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94142 | 64.9583 | 0.88394 | 60.9915 | -0.057489
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93702 | 64.6542 | 0.88396 | 60.9936 | -0.053053
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93862 | 64.7649 | 0.88424 | 61.0123 | -0.054386
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94391 | 65.13 | 0.88431 | 61.0176 | -0.059599
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93763 | 64.6962 | 0.88441 | 61.024 | -0.05322
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93763 | 64.6962 | 0.88448 | 61.0292 | -0.053145
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93763 | 64.6962 | 0.88461 | 61.038 | -0.053017
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9451 | 65.2116 | 0.88485 | 61.0545 | -0.060248
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.962 | 66.378 | 0.88493 | 61.06 | -0.077072
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93772 | 64.7029 | 0.88493 | 61.06 | -0.052795
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93772 | 64.7029 | 0.88513 | 61.074 | -0.052592
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94583 | 65.2625 | 0.8852 | 61.0785 | -0.060638
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93702 | 64.6542 | 0.88527 | 61.0838 | -0.051746
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93772 | 64.7029 | 0.88536 | 61.0901 | -0.05236
S2-Fixes | 45% | Liberty | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.9344 | 64.4738 | 0.88556 | 61.1039 | -0.048839
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95136 | 65.6439 | 0.88561 | 61.107 | -0.065753
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93862 | 64.7649 | 0.88567 | 61.1114 | -0.05295
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95144 | 65.6491 | 0.88569 | 61.1126 | -0.065747
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-LIBJ-PU161 | 0.90906 | 62.7254 | 0.88573 | 61.1154 | -0.023333
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94636 | 65.2986 | 0.88575 | 61.1171 | -0.060602
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93763 | 64.6962 | 0.88592 | 61.1282 | -0.05171
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93862 | 64.7649 | 0.88624 | 61.1507 | -0.05238
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93862 | 64.7649 | 0.88644 | 61.1647 | -0.052178
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94867 | 65.4582 | 0.88652 | 61.1699 | -0.062149
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97957 | 67.5901 | 0.88654 | 61.1716 | -0.093022
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94891 | 65.4751 | 0.88678 | 61.1879 | -0.062132
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94148 | 64.9619 | 0.88714 | 61.213 | -0.054332
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-LIBJ-PU161 | 0.91094 | 62.8552 | 0.88766 | 61.2486 | -0.023283
S2-Fixes | 45% | Liberty | Alcalde | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95926 | 66.1886 | 0.88767 | 61.2492 | -0.071586
S2-Fixes | 45% | Liberty | Alcalde | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95926 | 66.1886 | 0.88771 | 61.2519 | -0.071548
S2-Fixes | 45% | Liberty | Alcalde | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95944 | 66.2012 | 0.88787 | 61.2628 | -0.071571
S2-Fixes | 45% | Liberty | Alcalde | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95944 | 66.2012 | 0.8879 | 61.2654 | -0.071533
S2-Fixes | 45% | Liberty | Alcalde | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95975 | 66.2227 | 0.88791 | 61.2654 | -0.071844
S2-Fixes | 45% | Liberty | Alcalde | 324758 | 2US STEEL | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.96396 | 66.5134 | 0.88791 | 61.2661 | -0.076047
S2-Fixes | 45% | Liberty | Alcalde | 324833 | 2CORBIN 2 | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.9633 | 66.4678 | 0.88812 | 61.2805 | -0.075179
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94351 | 65.102 | 0.88843 | 61.3018 | -0.055077
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.102 | 0.88844 | 61.3022 | -0.05507
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94351 | 65.1023 | 0.88848 | 61.3052 | -0.055031
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.1023 | 0.88849 | 61.3057 | -0.055024
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95679 | 66.0186 | 0.88876 | 61.3246 | -0.06803
S2-Fixes | 45% | Liberty | Alcalde | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 0.95947 | 66.2036 | 0.88877 | 61.3248 | -0.070706
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.102 | 0.88879 | 61.3267 | -0.054715
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95684 | 66.0219 | 0.88882 | 61.3284 | -0.068021
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.1023 | 0.88884 | 61.3301 | -0.05467
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93521 | 64.5298 | 0.88896 | 61.3384 | -0.046252
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94825 | 65.4293 | 0.88918 | 61.3533 | -0.059073
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93521 | 64.5298 | 0.88919 | 61.3539 | -0.046027
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.90906 | 62.7254 | 0.88938 | 61.3669 | -0.019687
S2-Fixes | 45% | Liberty | Alcalde | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95923 | 66.187 | 0.88941 | 61.369 | -0.069826
S2-Fixes | 45% | Liberty | Alcalde | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95923 | 66.187 | 0.88944 | 61.3715 | -0.069791
S2-Fixes | 45% | Liberty | Alcalde | 324965 | 2SOMERSET NO | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94927 | 65.4997 | 0.88959 | 61.3816 | -0.059683
S2-Fixes | 45% | Liberty | Alcalde | 324832 | 2CORBIN 1 | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.96051 | 66.2754 | 0.88995 | 61.4068 | -0.07056
S2-Fixes | 45% | Liberty | Alcalde | 324903 | 2MCKEE ROAD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94963 | 65.5243 | 0.88997 | 61.4082 | -0.059653
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93702 | 64.6542 | 0.89041 | 61.438 | -0.046612
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94583 | 65.2625 | 0.8905 | 61.4444 | -0.055335
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94825 | 65.4293 | 0.89057 | 61.4494 | -0.057679
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93702 | 64.6542 | 0.89061 | 61.4521 | -0.046408
S2-Fixes | 45% | Liberty | Alcalde | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.95947 | 66.2036 | 0.89068 | 61.457 | -0.06879
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-RUS-WLF161 | 0.90906 | 62.7254 | 0.8907 | 61.4581 | -0.018367
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.93521 | 64.5298 | 0.89088 | 61.4709 | -0.044332
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93763 | 64.6962 | 0.89105 | 61.4822 | -0.04658
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94636 | 65.2986 | 0.89105 | 61.4827 | -0.055302
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.93521 | 64.5298 | 0.89108 | 61.4844 | -0.044136
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93772 | 64.7029 | 0.89117 | 61.491 | -0.046549
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93763 | 64.6962 | 0.89125 | 61.4962 | -0.046376
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.91094 | 62.8552 | 0.8913 | 61.4996 | -0.019645
S2-Fixes | 45% | Liberty | Alcalde | 324482 | 2CORBIN EAST | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.95868 | 66.1489 | 0.89146 | 61.5107 | -0.06722
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.9569 | 66.0258 | 0.89147 | 61.5113 | -0.065428
S2-Fixes | 45% | Liberty | Alcalde | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95703 | 66.0351 | 0.89187 | 61.539 | -0.065161
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94583 | 65.2625 | 0.89189 | 61.5403 | -0.053945
S2-Fixes | 45% | Liberty | Alcalde | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95703 | 66.0351 | 0.8919 | 61.541 | -0.065132
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93862 | 64.7649 | 0.89201 | 61.5489 | -0.046609
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94583 | 65.2625 | 0.89202 | 61.5492 | -0.053816
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94583 | 65.2625 | 0.89222 | 61.5634 | -0.05361
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94636 | 65.2986 | 0.89244 | 61.5786 | -0.053913
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94636 | 65.2986 | 0.89257 | 61.5874 | -0.053785
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93772 | 64.7029 | 0.89259 | 61.5886 | -0.045135
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-RUS-WLF161 | 0.91094 | 62.8552 | 0.89262 | 61.5906 | -0.018328
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.90906 | 62.7254 | 0.89271 | 61.5973 | -0.016348
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94636 | 65.2986 | 0.89278 | 61.6016 | -0.053579
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89287 | 61.6079 | -0.016195
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93702 | 64.6542 | 0.89298 | 61.6153 | -0.044043
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93772 | 64.7029 | 0.89339 | 61.6437 | -0.044336
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94391 | 65.13 | 0.89352 | 61.6529 | -0.050392
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94391 | 65.13 | 0.89353 | 61.6534 | -0.050385
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95136 | 65.6439 | 0.89357 | 61.6562 | -0.057793
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93763 | 64.6962 | 0.89361 | 61.6593 | -0.044013
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.944 | 65.1363 | 0.89364 | 61.661 | -0.050367
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95144 | 65.6491 | 0.89365 | 61.6617 | -0.057788
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94391 | 65.13 | 0.89385 | 61.6754 | -0.050067
S2-Fixes | 45% | Liberty | Alcalde | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95895 | 66.1676 | 0.89393 | 61.6813 | -0.065019
S2-Fixes | 45% | Liberty | Alcalde | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95895 | 66.1676 | 0.89396 | 61.6833 | -0.06499
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.90906 | 62.7254 | 0.89409 | 61.692 | -0.014976
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.9451 | 65.2116 | 0.89416 | 61.6969 | -0.050938
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89416 | 61.6974 | -0.050931
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_TYN-DELV161 | 0.90906 | 62.7254 | 0.8942 | 61.7001 | -0.014859
S2-Fixes | 45% | Liberty | Alcalde | 324787 | 2UNION UNDWR | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 0.98939 | 68.2679 | 0.89439 | 61.7127 | -0.095002
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89449 | 61.7196 | -0.05061
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.91094 | 62.8552 | 0.89463 | 61.7295 | -0.016314
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89478 | 61.7401 | -0.01616
S2-Fixes | 45% | Liberty | Alcalde | 324787 | 2UNION UNDWR | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 0.98939 | 68.2679 | 0.89483 | 61.7435 | -0.094556
S2-Fixes | 45% | Liberty | Alcalde | 341439 | 2ELK MT IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94649 | 65.3078 | 0.89496 | 61.7526 | -0.051525
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_MCCR-WAYNE161 | 0.90906 | 62.7254 | 0.89505 | 61.7582 | -0.014017
S2-Fixes | 45% | Liberty | Alcalde | 341439 | 2ELK MT IP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94649 | 65.3078 | 0.89516 | 61.7659 | -0.051332
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94825 | 65.4293 | 0.89516 | 61.7661 | -0.053089
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89537 | 61.7805 | -0.013694
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94148 | 64.9619 | 0.89556 | 61.7934 | -0.045921
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.962 | 66.378 | 0.89566 | 61.8008 | -0.066336
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94148 | 64.9619 | 0.89578 | 61.8088 | -0.045697
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94391 | 65.1301 | 0.89591 | 61.8178 | -0.048004
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.91094 | 62.8552 | 0.896 | 61.824 | -0.014944
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93862 | 64.7649 | 0.89603 | 61.8264 | -0.042587
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89605 | 61.8271 | -0.013018
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_TYN-DELV161 | 0.91094 | 62.8552 | 0.89612 | 61.8321 | -0.014827
S2-Fixes | 45% | Liberty | Alcalde | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95962 | 66.2135 | 0.8962 | 61.8376 | -0.06342
S2-Fixes | 45% | Liberty | Alcalde | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95962 | 66.2135 | 0.89622 | 61.8395 | -0.063392
S2-Fixes | 45% | Liberty | Alcalde | 339208 | AE2-254 MAIN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98547 | 67.9978 | 0.89623 | 61.8399 | -0.089245
S2-Fixes | 45% | Liberty | Alcalde | 342205 | 2S LANCASTER | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98547 | 67.9978 | 0.89623 | 61.8399 | -0.089245
S2-Fixes | 45% | Liberty | Alcalde | 324964 | 2SOMERSET 3 | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.95558 | 65.9348 | 0.89639 | 61.8512 | -0.059183
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.90906 | 62.7254 | 0.89643 | 61.8534 | -0.012638
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89643 | 61.8539 | -0.01263
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | 0.90906 | 62.7254 | 0.89649 | 61.8581 | -0.012568
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94336 | 65.0919 | 0.89662 | 61.8665 | -0.046746
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94336 | 65.0919 | 0.89662 | 61.867 | -0.046737
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 0.90906 | 62.7254 | 0.89671 | 61.8733 | -0.012349
S2-Fixes | 45% | Liberty | Alcalde | 342232 | 2SEWELLTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 1.0032 | 69.2195 | 0.89679 | 61.8788 | -0.10639
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325140 [7GLENDALE S 345.00] CKT 1 | 0.90906 | 62.7254 | 0.89694 | 61.8891 | -0.01212
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_MCCR-WAYNE161 | 0.91094 | 62.8552 | 0.89696 | 61.8901 | -0.013987
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94336 | 65.0919 | 0.89697 | 61.8912 | -0.046386
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 0.90906 | 62.7254 | 0.89703 | 61.8951 | -0.012033
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-26 | 0.90906 | 62.7254 | 0.89705 | 61.8967 | -0.01201
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94321 | 65.0812 | 0.89711 | 61.9003 | -0.0461
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94867 | 65.4582 | 0.89711 | 61.9006 | -0.051559
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94321 | 65.0812 | 0.89711 | 61.9009 | -0.046092
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94867 | 65.4582 | 0.89712 | 61.9011 | -0.051552
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.94142 | 64.9583 | 0.89726 | 61.911 | -0.044163
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89728 | 61.9123 | -0.013665
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94391 | 65.1301 | 0.89729 | 61.9131 | -0.046624
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | B-69-26 | 0.93521 | 64.5298 | 0.89733 | 61.916 | -0.037881
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94891 | 65.4751 | 0.89737 | 61.9184 | -0.051545
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94891 | 65.4751 | 0.89738 | 61.919 | -0.051538
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94321 | 65.0812 | 0.89745 | 61.9241 | -0.045755
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93521 | 64.5298 | 0.89745 | 61.9243 | -0.037761
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94148 | 64.9619 | 0.89746 | 61.9248 | -0.044015
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94867 | 65.4582 | 0.89755 | 61.9307 | -0.051122
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94391 | 65.13 | 0.89755 | 61.9313 | -0.046358
S2-Fixes | 45% | Liberty | Alcalde | 341581 | 2GREGORY RD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9866 | 68.0752 | 0.89758 | 61.9333 | -0.089012
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94148 | 64.9619 | 0.89766 | 61.9383 | -0.043821
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94142 | 64.9583 | 0.89766 | 61.9383 | -0.043768
S2-Fixes | 45% | Liberty | Alcalde | 341578 | 2GREGORY R T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98667 | 68.0804 | 0.89767 | 61.9391 | -0.089004
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94142 | 64.9583 | 0.89778 | 61.9465 | -0.043649
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94185 | 64.9876 | 0.89778 | 61.947 | -0.044067
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94143 | 64.9585 | 0.89779 | 61.9473 | -0.043641
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94143 | 64.9585 | 0.8978 | 61.9479 | -0.043633
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94891 | 65.4751 | 0.89781 | 61.9486 | -0.051108
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 0.90906 | 62.7254 | 0.89782 | 61.9498 | -0.01124
S2-Fixes | 45% | Liberty | Alcalde | 324737 | 2SOMERSET SO | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.96034 | 66.2637 | 0.89787 | 61.953 | -0.062475
S2-Fixes | 45% | Liberty | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-LIBJ-PU161 | 0.92093 | 63.5442 | 0.89792 | 61.9562 | -0.023014
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.90906 | 62.7254 | 0.89793 | 61.9572 | -0.011132
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89795 | 61.9588 | -0.01299
S2-Fixes | 45% | Liberty | Alcalde | 326533 | 2BUSH EKPC | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.9435 | 65.1012 | 0.89802 | 61.9633 | -0.045477
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94391 | 65.13 | 0.89805 | 61.9651 | -0.045867
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94143 | 64.9585 | 0.89809 | 61.968 | -0.043341
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94175 | 64.9808 | 0.89812 | 61.9706 | -0.043625
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94175 | 64.9808 | 0.89813 | 61.9712 | -0.043617
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | 0.90906 | 62.7254 | 0.89813 | 61.9713 | -0.010929
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95186 | 65.6783 | 0.89816 | 61.9732 | -0.053697
S2-Fixes | 45% | Liberty | Alcalde | 326533 | 2BUSH EKPC | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_TYN-DELV161 | 0.9435 | 65.1012 | 0.89822 | 61.977 | -0.045278
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89824 | 61.9784 | -0.046859
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 0.90906 | 62.7254 | 0.8983 | 61.9829 | -0.01076
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 0.93521 | 64.5298 | 0.89831 | 61.9837 | -0.0369
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.91094 | 62.8552 | 0.89833 | 61.985 | -0.012611
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89834 | 61.9856 | -0.012603
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.9455 | 65.2392 | 0.8984 | 61.9896 | -0.047095
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | 0.91094 | 62.8552 | 0.8984 | 61.9898 | -0.012542
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9455 | 65.2392 | 0.89841 | 61.9902 | -0.047086
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94175 | 64.9808 | 0.89842 | 61.9913 | -0.043326
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 0.90906 | 62.7254 | 0.89856 | 62.0009 | -0.010499
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 0.91094 | 62.8552 | 0.89862 | 62.0049 | -0.012323
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.94336 | 65.0919 | 0.89862 | 62.005 | -0.044737
S2-Fixes | 45% | Liberty | Alcalde | 326542 | 2N CORBIN | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.95243 | 65.7178 | 0.89862 | 62.0051 | -0.053807
S2-Fixes | 45% | Liberty | Alcalde | 341343 | 2CONTOWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99103 | 68.3808 | 0.89863 | 62.0056 | -0.092394
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94653 | 65.3108 | 0.89867 | 62.0083 | -0.047862
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89868 | 62.0091 | -0.010381
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89873 | 62.0126 | -0.046363
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9455 | 65.2392 | 0.89875 | 62.014 | -0.046742
S2-Fixes | 45% | Liberty | Alcalde | 341342 | 2CONTOWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99115 | 68.3891 | 0.89877 | 62.0148 | -0.092381
S2-Fixes | 45% | Liberty | Alcalde | 324969 | 2SMRST 615KU | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.95993 | 66.2355 | 0.8988 | 62.0169 | -0.061139
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325140 [7GLENDALE S 345.00] CKT 1 | 0.91094 | 62.8552 | 0.89885 | 62.0207 | -0.012094
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.95186 | 65.6783 | 0.89891 | 62.0248 | -0.052949
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95186 | 65.6783 | 0.89892 | 62.0253 | -0.052941
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 0.91094 | 62.8552 | 0.89894 | 62.0267 | -0.012007
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-26 | 0.91094 | 62.8552 | 0.89896 | 62.0282 | -0.011984
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 0.93521 | 64.5298 | 0.89896 | 62.0284 | -0.036251
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94185 | 64.9876 | 0.89901 | 62.0314 | -0.042844
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94142 | 64.9583 | 0.89905 | 62.0346 | -0.042373
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94391 | 65.13 | 0.89916 | 62.0423 | -0.044748
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94185 | 64.9876 | 0.8992 | 62.0446 | -0.042653
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.94321 | 65.0812 | 0.89927 | 62.0494 | -0.04394
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95186 | 65.6783 | 0.89936 | 62.0562 | -0.052495
S2-Fixes | 45% | Liberty | Alcalde | 324990 | 2WAITSBORO | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.95967 | 66.2172 | 0.89939 | 62.058 | -0.060278
S2-Fixes | 45% | Liberty | Alcalde | 342433 | 2W BEREA J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95491 | 65.8887 | 0.89942 | 62.0597 | -0.055493
S2-Fixes | 45% | Liberty | Alcalde | 341098 | 2BEREAKU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95491 | 65.8888 | 0.89942 | 62.0597 | -0.055493
S2-Fixes | 45% | Liberty | Alcalde | 341110 | 2BIG CREEK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.95077 | 65.603 | 0.8995 | 62.0657 | -0.051264
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94351 | 65.102 | 0.89965 | 62.0757 | -0.043861
S2-Fixes | 45% | Liberty | Alcalde | 341110 | 2BIG CREEK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.95077 | 65.603 | 0.8997 | 62.079 | -0.051072
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94192 | 64.9925 | 0.8997 | 62.0792 | -0.042223
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94351 | 65.1023 | 0.8997 | 62.0793 | -0.043812
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 0.91094 | 62.8552 | 0.89973 | 62.0812 | -0.011216
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95679 | 66.0186 | 0.89979 | 62.0858 | -0.056997
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.944 | 65.1363 | 0.8998 | 62.0861 | -0.044206
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.91094 | 62.8552 | 0.89984 | 62.0887 | -0.011109
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95684 | 66.0219 | 0.89985 | 62.0896 | -0.05699
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.9451 | 65.2116 | 0.89986 | 62.0906 | -0.045232
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 0.93521 | 64.5298 | 0.89988 | 62.092 | -0.03533
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94192 | 64.9925 | 0.89989 | 62.0922 | -0.042033
S2-Fixes | 37% | Liberty | CCAP | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97092 | 66.9934 | 0.81608 | 56.3096 | -0.15484
S2-Fixes | 37% | Liberty | CCAP | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97096 | 66.9962 | 0.81614 | 56.3138 | -0.15482
S2-Fixes | 37% | Liberty | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96057 | 66.2794 | 0.81668 | 56.351 | -0.14389
S2-Fixes | 37% | Liberty | CCAP | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97089 | 66.9915 | 0.82891 | 57.1948 | -0.14198
S2-Fixes | 37% | Liberty | CCAP | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96389 | 66.5087 | 0.8471 | 58.4499 | -0.11679
S2-Fixes | 37% | Liberty | CCAP | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97543 | 67.3048 | 0.85376 | 58.9093 | -0.12168
S2-Fixes | 37% | Liberty | CCAP | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98243 | 67.7878 | 0.85452 | 58.9617 | -0.12791
S2-Fixes | 37% | Liberty | CCAP | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.98263 | 67.8013 | 0.85474 | 58.9773 | -0.12788
S2-Fixes | 37% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95967 | 66.2175 | 0.86239 | 59.5047 | -0.097287
S2-Fixes | 37% | Liberty | CCAP | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97311 | 67.1448 | 0.8625 | 59.5125 | -0.11061
S2-Fixes | 37% | Liberty | CCAP | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97318 | 67.1496 | 0.86258 | 59.518 | -0.1106
S2-Fixes | 37% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95997 | 66.2381 | 0.86272 | 59.5276 | -0.097254
S2-Fixes | 37% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9967 | 68.7721 | 0.8656 | 59.7263 | -0.1311
S2-Fixes | 37% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9967 | 68.7721 | 0.86688 | 59.8145 | -0.12982
S2-Fixes | 37% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99923 | 68.9469 | 0.86852 | 59.9278 | -0.13071
S2-Fixes | 37% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99923 | 68.9469 | 0.86979 | 60.0157 | -0.12944
S2-Fixes | 37% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0237 | 70.632 | 0.86988 | 60.0218 | -0.15377
S2-Fixes | 37% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99086 | 68.3692 | 0.87487 | 60.3658 | -0.11599
S2-Fixes | 37% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99086 | 68.3692 | 0.87603 | 60.446 | -0.11483
S2-Fixes | 37% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9614 | 66.3369 | 0.87631 | 60.4655 | -0.085092
S2-Fixes | 37% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96455 | 66.5542 | 0.87767 | 60.5595 | -0.086881
S2-Fixes | 37% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9946 | 68.6271 | 0.87911 | 60.6583 | -0.11549
S2-Fixes | 37% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9946 | 68.6271 | 0.88026 | 60.7381 | -0.11433
S2-Fixes | 37% | Liberty | CCAP | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96545 | 66.6158 | 0.88078 | 60.7742 | -0.084662
S2-Fixes | 37% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9614 | 66.3367 | 0.88085 | 60.7786 | -0.080552
S2-Fixes | 37% | Liberty | CCAP | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96567 | 66.6315 | 0.88103 | 60.7913 | -0.08464
S2-Fixes | 37% | Liberty | CCAP | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96679 | 66.7088 | 0.88187 | 60.8493 | -0.084921
S2-Fixes | 37% | Liberty | CCAP | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98307 | 67.8316 | 0.88301 | 60.9277 | -0.10006
S2-Fixes | 37% | Liberty | CCAP | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96308 | 66.4525 | 0.88321 | 60.9418 | -0.079865
S2-Fixes | 37% | Liberty | CCAP | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96403 | 66.5178 | 0.8833 | 60.9477 | -0.080725
S2-Fixes | 37% | Liberty | CCAP | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96223 | 66.3942 | 0.88332 | 60.9492 | -0.078912
S2-Fixes | 37% | Liberty | CCAP | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96279 | 66.4327 | 0.88393 | 60.9912 | -0.078862
S2-Fixes | 37% | Liberty | CCAP | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97402 | 67.2075 | 0.8859 | 61.1273 | -0.088119
S2-Fixes | 37% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9614 | 66.3367 | 0.88683 | 61.191 | -0.074575
S2-Fixes | 37% | Liberty | CCAP | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97115 | 67.0091 | 0.88836 | 61.2969 | -0.082785
S2-Fixes | 37% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9614 | 66.3369 | 0.88847 | 61.3043 | -0.072937
S2-Fixes | 37% | Liberty | CCAP | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97166 | 67.0442 | 0.88892 | 61.3353 | -0.082738
S2-Fixes | 37% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96455 | 66.5542 | 0.89009 | 61.4165 | -0.074459
S2-Fixes | 37% | Liberty | CCAP | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9985 | 68.8964 | 0.89057 | 61.4496 | -0.10792
S2-Fixes | 37% | Liberty | CCAP | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99849 | 68.8958 | 0.89134 | 61.5022 | -0.10715
S2-Fixes | 37% | Liberty | CCAP | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9985 | 68.8964 | 0.89161 | 61.5212 | -0.10689
S2-Fixes | 37% | Liberty | CCAP | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99849 | 68.8958 | 0.89237 | 61.5732 | -0.10612
S2-Fixes | 37% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95967 | 66.2175 | 0.89256 | 61.5867 | -0.067114
S2-Fixes | 37% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95997 | 66.2381 | 0.89288 | 61.6088 | -0.067091
S2-Fixes | 37% | Liberty | CCAP | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98605 | 68.0374 | 0.89514 | 61.7649 | -0.090906
S2-Fixes | 37% | Liberty | CCAP | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98605 | 68.0374 | 0.89518 | 61.7674 | -0.090868
S2-Fixes | 37% | Liberty | CCAP | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98623 | 68.0496 | 0.89534 | 61.7783 | -0.090888
S2-Fixes | 37% | Liberty | CCAP | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98623 | 68.0496 | 0.89538 | 61.7809 | -0.09085
S2-Fixes | 37% | Liberty | CCAP | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98663 | 68.0772 | 0.89538 | 61.7809 | -0.09125
S2-Fixes | 37% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98824 | 68.1888 | 0.89605 | 61.8276 | -0.092192
S2-Fixes | 37% | Liberty | CCAP | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96844 | 66.8225 | 0.89615 | 61.8343 | -0.072292
S2-Fixes | 37% | Liberty | CCAP | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98547 | 67.9977 | 0.89686 | 61.8836 | -0.08861
S2-Fixes | 37% | Liberty | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96057 | 66.2794 | 0.89686 | 61.8836 | -0.063707
S2-Fixes | 37% | Liberty | CCAP | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98547 | 67.9977 | 0.8969 | 61.886 | -0.088574
S2-Fixes | 37% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98824 | 68.1888 | 0.89806 | 61.9662 | -0.090183
S2-Fixes | 37% | Liberty | CCAP | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.97085 | 66.9887 | 0.89875 | 62.0141 | -0.072096
S2-Fixes | 37% | Liberty | CCAP | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.98131 | 67.7107 | 0.89899 | 62.0303 | -0.082324
S2-Fixes | 37% | Liberty | CCAP | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.98131 | 67.7107 | 0.89902 | 62.0323 | -0.082295
S2-Fixes | 37% | Liberty | CCAP | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96497 | 66.5831 | 0.89947 | 62.0635 | -0.065502
S2-Fixes | 38% | Liberty | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96764 | 66.7673 | 0.80632 | 55.6359 | -0.16132
S2-Fixes | 38% | Liberty | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96768 | 66.7702 | 0.80638 | 55.6403 | -0.1613
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95708 | 66.0383 | 0.80706 | 55.6871 | -0.15002
S2-Fixes | 38% | Liberty | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96752 | 66.7585 | 0.81954 | 56.548 | -0.14798
S2-Fixes | 38% | Liberty | McCreary | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95872 | 66.1514 | 0.83756 | 57.7918 | -0.12115
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97195 | 67.0648 | 0.83876 | 57.8745 | -0.13319
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.97215 | 67.0786 | 0.83899 | 57.8905 | -0.13316
S2-Fixes | 38% | Liberty | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97197 | 67.0657 | 0.84509 | 58.3115 | -0.12687
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96219 | 66.3914 | 0.84696 | 58.4405 | -0.11523
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96227 | 66.3963 | 0.84704 | 58.4461 | -0.11522
S2-Fixes | 38% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9542 | 65.8401 | 0.85315 | 58.8677 | -0.10105
S2-Fixes | 38% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95451 | 65.861 | 0.85349 | 58.891 | -0.10101
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99076 | 68.3625 | 0.86163 | 59.4527 | -0.12913
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99076 | 68.3625 | 0.86292 | 59.5413 | -0.12784
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99333 | 68.5397 | 0.86459 | 59.6567 | -0.12874
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99333 | 68.5397 | 0.86587 | 59.7449 | -0.12746
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0172 | 70.1866 | 0.86596 | 59.751 | -0.15124
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95544 | 65.9253 | 0.8669 | 59.8164 | -0.088534
S2-Fixes | 38% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95582 | 65.9518 | 0.86737 | 59.8485 | -0.088454
S2-Fixes | 38% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9588 | 66.1572 | 0.86847 | 59.9241 | -0.090335
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98533 | 67.9876 | 0.87102 | 60.1001 | -0.11431
S2-Fixes | 38% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95581 | 65.9511 | 0.87206 | 60.1719 | -0.083755
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98533 | 67.9876 | 0.87218 | 60.1807 | -0.11314
S2-Fixes | 38% | Liberty | McCreary | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95987 | 66.2307 | 0.87339 | 60.2639 | -0.086476
S2-Fixes | 38% | Liberty | McCreary | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9601 | 66.2466 | 0.87364 | 60.2813 | -0.086453
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97833 | 67.5046 | 0.87467 | 60.3524 | -0.10365
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98911 | 68.2489 | 0.87531 | 60.3961 | -0.11381
S2-Fixes | 38% | Liberty | McCreary | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96627 | 66.6729 | 0.87638 | 60.47 | -0.089897
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98911 | 68.2489 | 0.87647 | 60.4763 | -0.11265
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94972 | 65.5308 | 0.87679 | 60.4986 | -0.07293
S2-Fixes | 38% | Liberty | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95056 | 65.5889 | 0.87686 | 60.5033 | -0.073704
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94904 | 65.4839 | 0.87693 | 60.5083 | -0.07211
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94961 | 65.5232 | 0.87755 | 60.5509 | -0.072063
S2-Fixes | 38% | Liberty | McCreary | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95915 | 66.1813 | 0.87931 | 60.6727 | -0.079835
S2-Fixes | 38% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95581 | 65.9511 | 0.87953 | 60.6877 | -0.07628
S2-Fixes | 38% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95582 | 65.9518 | 0.8812 | 60.8029 | -0.074622
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97833 | 67.5046 | 0.88122 | 60.8042 | -0.097106
S2-Fixes | 38% | Liberty | McCreary | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95676 | 66.0164 | 0.8818 | 60.8439 | -0.074965
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98479 | 67.9502 | 0.8819 | 60.8512 | -0.10288
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97833 | 67.5046 | 0.88191 | 60.8515 | -0.096422
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97833 | 67.5046 | 0.88197 | 60.8561 | -0.096354
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99076 | 68.3625 | 0.88221 | 60.8727 | -0.10855
S2-Fixes | 38% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97833 | 67.5046 | 0.88229 | 60.8783 | -0.096033
S2-Fixes | 38% | Liberty | McCreary | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95728 | 66.0521 | 0.88236 | 60.8826 | -0.074921
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9773 | 67.434 | 0.88252 | 60.8937 | -0.094786
S2-Fixes | 38% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9588 | 66.1572 | 0.8826 | 60.8997 | -0.076196
S2-Fixes | 38% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0156 | 70.0765 | 0.88508 | 61.0709 | -0.13052
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99333 | 68.5397 | 0.8851 | 61.0718 | -0.10823
S2-Fixes | 38% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9542 | 65.8401 | 0.8855 | 61.0995 | -0.068705
S2-Fixes | 38% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95451 | 65.861 | 0.88583 | 61.122 | -0.068681
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0013 | 69.0898 | 0.88652 | 61.1699 | -0.11478
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96219 | 66.3914 | 0.88695 | 61.1996 | -0.075244
S2-Fixes | 38% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99326 | 68.5348 | 0.88696 | 61.2001 | -0.1063
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96227 | 66.3963 | 0.88703 | 61.2049 | -0.075238
S2-Fixes | 38% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0174 | 70.2013 | 0.88716 | 61.2141 | -0.13025
S2-Fixes | 38% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99331 | 68.5384 | 0.88777 | 61.2565 | -0.10553
S2-Fixes | 38% | Liberty | McCreary | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99326 | 68.5348 | 0.888 | 61.2721 | -0.10526
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98479 | 67.9502 | 0.8884 | 61.2993 | -0.096389
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0172 | 70.1866 | 0.88857 | 61.3116 | -0.12862
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99076 | 68.3625 | 0.88861 | 61.3142 | -0.10215
S2-Fixes | 38% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99076 | 68.3625 | 0.88869 | 61.3194 | -0.10207
S2-Fixes | 38% | Liberty | McCreary | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99331 | 68.5384 | 0.88881 | 61.3279 | -0.1045
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98479 | 67.9502 | 0.88907 | 61.3461 | -0.095711
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0191 | 70.3177 | 0.8891 | 61.3479 | -0.13
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98479 | 67.9502 | 0.88914 | 61.3508 | -0.095643
S2-Fixes | 38% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98479 | 67.9502 | 0.88946 | 61.3728 | -0.095324
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98533 | 67.9876 | 0.88955 | 61.3791 | -0.095776
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95544 | 65.9253 | 0.88955 | 61.3792 | -0.065886
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9773 | 67.434 | 0.88962 | 61.3839 | -0.087682
S2-Fixes | 38% | Liberty | McCreary | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96034 | 66.2631 | 0.88963 | 61.3843 | -0.070708
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95499 | 65.8944 | 0.88964 | 61.3851 | -0.065352
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9773 | 67.434 | 0.88968 | 61.3881 | -0.087621
S2-Fixes | 38% | Liberty | McCreary | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96923 | 66.8766 | 0.89001 | 61.4105 | -0.079219
S2-Fixes | 38% | Liberty | McCreary | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96923 | 66.8766 | 0.89005 | 61.4131 | -0.079181
S2-Fixes | 38% | Liberty | McCreary | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96941 | 66.889 | 0.8902 | 61.4241 | -0.079202
S2-Fixes | 38% | Liberty | McCreary | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96941 | 66.889 | 0.89024 | 61.4267 | -0.079165
S2-Fixes | 38% | Liberty | McCreary | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96968 | 66.9082 | 0.89024 | 61.4267 | -0.079443
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97195 | 67.0648 | 0.89055 | 61.448 | -0.081403
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97215 | 67.0786 | 0.89077 | 61.4631 | -0.081385
S2-Fixes | 38% | Liberty | McCreary | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.97231 | 67.0891 | 0.89087 | 61.4698 | -0.08144
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9773 | 67.434 | 0.89089 | 61.4713 | -0.086415
S2-Fixes | 38% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9773 | 67.434 | 0.89137 | 61.5044 | -0.085936
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99333 | 68.5397 | 0.89148 | 61.5119 | -0.10185
S2-Fixes | 38% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99333 | 68.5397 | 0.89155 | 61.5171 | -0.10178
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95499 | 65.8944 | 0.89167 | 61.525 | -0.063325
S2-Fixes | 38% | Liberty | McCreary | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96935 | 66.8854 | 0.89174 | 61.53 | -0.077615
S2-Fixes | 38% | Liberty | McCreary | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96935 | 66.8854 | 0.89177 | 61.5324 | -0.077579
S2-Fixes | 38% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98596 | 68.0313 | 0.89212 | 61.5565 | -0.093837
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95708 | 66.0383 | 0.89225 | 61.5653 | -0.064826
S2-Fixes | 38% | Liberty | McCreary | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95745 | 66.0642 | 0.89228 | 61.5675 | -0.06517
S2-Fixes | 38% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0156 | 70.0765 | 0.89233 | 61.5708 | -0.12327
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 1.0013 | 69.0898 | 0.89239 | 61.5746 | -0.10892
S2-Fixes | 38% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0156 | 70.0765 | 0.89242 | 61.5768 | -0.12318
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96219 | 66.3914 | 0.8926 | 61.5892 | -0.069597
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96227 | 66.3963 | 0.89267 | 61.5945 | -0.069592
S2-Fixes | 38% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96219 | 66.3914 | 0.89282 | 61.6048 | -0.069371
S2-Fixes | 38% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96227 | 66.3963 | 0.8929 | 61.6101 | -0.069365
S2-Fixes | 38% | Liberty | McCreary | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.96841 | 66.8203 | 0.89296 | 61.6144 | -0.075448
S2-Fixes | 38% | Liberty | McCreary | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95329 | 65.7769 | 0.89317 | 61.6289 | -0.060116
S2-Fixes | 38% | Liberty | McCreary | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95329 | 65.7769 | 0.89351 | 61.652 | -0.059782
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98911 | 68.2489 | 0.89375 | 61.6688 | -0.095364
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0013 | 69.0898 | 0.89377 | 61.6703 | -0.10753
S2-Fixes | 38% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0013 | 69.0898 | 0.89385 | 61.6755 | -0.10745
S2-Fixes | 38% | Liberty | McCreary | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96718 | 66.7357 | 0.89397 | 61.6839 | -0.073214
S2-Fixes | 38% | Liberty | McCreary | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96718 | 66.7357 | 0.894 | 61.686 | -0.073184
S2-Fixes | 38% | Liberty | McCreary | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95745 | 66.0642 | 0.8943 | 61.707 | -0.063149
S2-Fixes | 38% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0174 | 70.2013 | 0.89439 | 61.7129 | -0.12302
S2-Fixes | 38% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0174 | 70.2013 | 0.89448 | 61.7189 | -0.12293
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95544 | 65.9253 | 0.89506 | 61.7594 | -0.060375
S2-Fixes | 38% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95544 | 65.9253 | 0.89527 | 61.7733 | -0.060173
S2-Fixes | 38% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95434 | 65.8492 | 0.89529 | 61.7753 | -0.059042
S2-Fixes | 38% | Liberty | McCreary | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96034 | 66.2631 | 0.8953 | 61.7759 | -0.065032
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98533 | 67.9876 | 0.8954 | 61.7828 | -0.089924
S2-Fixes | 38% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98533 | 67.9876 | 0.89547 | 61.7876 | -0.089854
S2-Fixes | 38% | Liberty | McCreary | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96034 | 66.2631 | 0.89552 | 61.7907 | -0.064817
S2-Fixes | 38% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95434 | 65.8492 | 0.89562 | 61.7981 | -0.058712
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0172 | 70.1866 | 0.89573 | 61.8053 | -0.12147
S2-Fixes | 38% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0172 | 70.1866 | 0.89581 | 61.8112 | -0.12138
S2-Fixes | 38% | Liberty | McCreary | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96899 | 66.8603 | 0.89593 | 61.8189 | -0.073064
S2-Fixes | 38% | Liberty | McCreary | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96899 | 66.8603 | 0.89596 | 61.8209 | -0.073035
S2-Fixes | 38% | Liberty | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.95056 | 65.5889 | 0.89611 | 61.8318 | -0.054451
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94972 | 65.5308 | 0.89624 | 61.8407 | -0.053479
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97195 | 67.0648 | 0.89625 | 61.8416 | -0.075699
S2-Fixes | 38% | Liberty | McCreary | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0163 | 163.6246 | 0.89631 | 144.3053 | -0.12
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0191 | 70.3177 | 0.89631 | 61.8456 | -0.12278
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0191 | 70.3177 | 0.8964 | 61.8515 | -0.1227
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95708 | 66.0383 | 0.89645 | 61.8554 | -0.060622
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97215 | 67.0786 | 0.89647 | 61.8566 | -0.075682
S2-Fixes | 38% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97195 | 67.0648 | 0.8965 | 61.8584 | -0.075455
S2-Fixes | 38% | Liberty | McCreary | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.98093 | 157.9305 | 0.89651 | 144.3383 | -0.084424
S2-Fixes | 38% | Liberty | McCreary | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97231 | 67.0891 | 0.89657 | 61.8633 | -0.075737
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94904 | 65.4839 | 0.89661 | 61.8659 | -0.052434
S2-Fixes | 38% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97215 | 67.0786 | 0.89672 | 61.8734 | -0.075438
S2-Fixes | 38% | Liberty | McCreary | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.97231 | 67.0891 | 0.89681 | 61.8801 | -0.075493
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94961 | 65.5232 | 0.89721 | 61.9076 | -0.0524
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95499 | 65.8944 | 0.89734 | 61.9164 | -0.057653
S2-Fixes | 38% | Liberty | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.97197 | 67.0657 | 0.89736 | 61.9179 | -0.074606
S2-Fixes | 38% | Liberty | McCreary | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95602 | 65.965 | 0.89754 | 61.93 | -0.058479
S2-Fixes | 38% | Liberty | McCreary | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95499 | 65.8944 | 0.89754 | 61.9304 | -0.057449
S2-Fixes | 38% | Liberty | McCreary | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94827 | 65.4303 | 0.8976 | 61.9347 | -0.050661
S2-Fixes | 38% | Liberty | McCreary | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95602 | 65.9654 | 0.8976 | 61.9347 | -0.058415
S2-Fixes | 38% | Liberty | McCreary | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96958 | 66.9007 | 0.89804 | 61.9647 | -0.071536
S2-Fixes | 38% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95692 | 66.0272 | 0.89804 | 61.9651 | -0.058871
S2-Fixes | 38% | Liberty | McCreary | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96958 | 66.9007 | 0.89807 | 61.9666 | -0.071509
S2-Fixes | 38% | Liberty | McCreary | 341893 | 2MT OLIVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.002 | 69.137 | 0.89824 | 61.9784 | -0.10375
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94904 | 65.4839 | 0.89829 | 61.9822 | -0.050748
S2-Fixes | 38% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95692 | 66.0272 | 0.89837 | 61.9878 | -0.058542
S2-Fixes | 38% | Liberty | McCreary | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.97088 | 66.9908 | 0.89843 | 61.9917 | -0.072451
S2-Fixes | 38% | Liberty | McCreary | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.94904 | 65.4839 | 0.89858 | 62.0023 | -0.050457
S2-Fixes | 38% | Liberty | McCreary | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95329 | 65.7769 | 0.89859 | 62.0029 | -0.054696
S2-Fixes | 38% | Liberty | McCreary | 341896 | 2MT OLIVE J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 1.0009 | 69.0609 | 0.89866 | 62.0077 | -0.10222
S2-Fixes | 38% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95708 | 66.0383 | 0.8988 | 62.0172 | -0.058278
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94961 | 65.5232 | 0.8989 | 62.0238 | -0.050716
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.94972 | 65.5308 | 0.89895 | 62.0276 | -0.050771
S2-Fixes | 38% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98596 | 68.0313 | 0.89915 | 62.0413 | -0.086812
S2-Fixes | 38% | Liberty | McCreary | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.94961 | 65.5232 | 0.89919 | 62.0439 | -0.050425
S2-Fixes | 38% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98596 | 68.0313 | 0.89921 | 62.0455 | -0.086751
S2-Fixes | 38% | Liberty | McCreary | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94972 | 65.5308 | 0.89938 | 62.0575 | -0.050337
S2-Fixes | 38% | Liberty | McCreary | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-69-25 | 0.95056 | 65.5889 | 0.89945 | 62.0619 | -0.051115
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98911 | 68.2489 | 0.89957 | 62.0706 | -0.08954
S2-Fixes | 38% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98911 | 68.2489 | 0.89964 | 62.0754 | -0.089471
S2-Fixes | 45% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9607 | 66.2885 | 0.7869 | 54.2961 | -0.1738
S2-Fixes | 45% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96075 | 66.2916 | 0.78697 | 54.3009 | -0.17378
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.94957 | 65.5202 | 0.78811 | 54.3795 | -0.16146
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96065 | 66.2846 | 0.80158 | 55.3087 | -0.15907
S2-Fixes | 45% | Liberty | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95235 | 65.7124 | 0.8169 | 56.366 | -0.13546
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96723 | 66.7391 | 0.8217 | 56.6974 | -0.14553
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96744 | 66.7537 | 0.82195 | 56.7146 | -0.14549
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96551 | 66.6202 | 0.82983 | 57.2585 | -0.13568
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95696 | 66.03 | 0.83053 | 57.3065 | -0.12643
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95703 | 66.0352 | 0.83062 | 57.3125 | -0.12642
S2-Fixes | 45% | Liberty | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94748 | 65.3764 | 0.83377 | 57.5298 | -0.11372
S2-Fixes | 45% | Liberty | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9478 | 65.3985 | 0.83413 | 57.5549 | -0.11368
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98579 | 68.0192 | 0.83795 | 57.8188 | -0.14783
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98579 | 68.0192 | 0.83954 | 57.9286 | -0.14624
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9885 | 68.2065 | 0.84115 | 58.0393 | -0.14735
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98382 | 67.8836 | 0.84143 | 58.0583 | -0.1424
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.9885 | 68.2065 | 0.84274 | 58.1487 | -0.14576
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0164 | 70.1284 | 0.84282 | 58.1547 | -0.17353
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98382 | 67.8836 | 0.84293 | 58.1621 | -0.14089
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98781 | 68.1589 | 0.8461 | 58.3807 | -0.14171
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98781 | 68.1589 | 0.84759 | 58.4838 | -0.14022
S2-Fixes | 45% | Liberty | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94915 | 65.4911 | 0.84919 | 58.5941 | -0.099957
S2-Fixes | 45% | Liberty | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95156 | 65.6577 | 0.84939 | 58.6079 | -0.10217
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94988 | 65.5417 | 0.85206 | 58.7923 | -0.097817
S2-Fixes | 45% | Liberty | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9541 | 65.8328 | 0.85389 | 58.9185 | -0.10021
S2-Fixes | 45% | Liberty | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95434 | 65.8496 | 0.85416 | 58.9373 | -0.10018
S2-Fixes | 45% | Liberty | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94924 | 65.4975 | 0.85446 | 58.958 | -0.094774
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99189 | 68.4406 | 0.85905 | 59.2743 | -0.13285
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9752 | 67.2887 | 0.85995 | 59.3363 | -0.11525
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99213 | 68.4569 | 0.86029 | 59.3597 | -0.13184
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99189 | 68.4406 | 0.86042 | 59.3688 | -0.13148
S2-Fixes | 45% | Liberty | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94924 | 65.4975 | 0.86052 | 59.3759 | -0.088718
S2-Fixes | 45% | Liberty | W Garrard | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96177 | 66.3622 | 0.86119 | 59.4223 | -0.10058
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99213 | 68.4569 | 0.86164 | 59.4534 | -0.13049
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94385 | 65.1254 | 0.86195 | 59.4746 | -0.081896
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94475 | 65.1877 | 0.86199 | 59.4773 | -0.082759
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94316 | 65.0781 | 0.86218 | 59.4904 | -0.08098
S2-Fixes | 45% | Liberty | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94915 | 65.4911 | 0.86232 | 59.5004 | -0.086822
S2-Fixes | 45% | Liberty | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95156 | 65.6577 | 0.86283 | 59.5354 | -0.088728
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94376 | 65.1197 | 0.86284 | 59.536 | -0.080923
S2-Fixes | 45% | Liberty | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95402 | 65.8271 | 0.86434 | 59.6396 | -0.089673
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9752 | 67.2887 | 0.86472 | 59.6655 | -0.11048
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9752 | 67.2887 | 0.86479 | 59.6708 | -0.11041
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98579 | 68.0192 | 0.86702 | 59.8247 | -0.11876
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95156 | 65.6576 | 0.8671 | 59.8299 | -0.08446
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98382 | 67.8836 | 0.86733 | 59.846 | -0.11649
S2-Fixes | 45% | Liberty | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94748 | 65.3764 | 0.86751 | 59.8583 | -0.079973
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95208 | 65.6935 | 0.86767 | 59.8693 | -0.084409
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98201 | 67.7589 | 0.86768 | 59.87 | -0.11433
S2-Fixes | 45% | Liberty | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9478 | 65.3985 | 0.86786 | 59.8824 | -0.079943
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97416 | 67.2169 | 0.86905 | 59.9647 | -0.1051
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9752 | 67.2887 | 0.86994 | 60.0262 | -0.10525
S2-Fixes | 45% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0149 | 70.0281 | 0.8701 | 60.0372 | -0.1448
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9885 | 68.2065 | 0.87011 | 60.0378 | -0.11839
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98579 | 68.0192 | 0.87126 | 60.1166 | -0.11453
S2-Fixes | 45% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98579 | 68.0192 | 0.87134 | 60.1226 | -0.11444
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98382 | 67.8836 | 0.87143 | 60.1288 | -0.11239
S2-Fixes | 45% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98382 | 67.8836 | 0.87152 | 60.1347 | -0.1123
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99934 | 68.9543 | 0.87171 | 60.1478 | -0.12763
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98781 | 68.1589 | 0.87186 | 60.1586 | -0.11595
S2-Fixes | 45% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0168 | 70.1594 | 0.87233 | 60.1905 | -0.14448
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98201 | 67.7589 | 0.87241 | 60.1962 | -0.1096
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98201 | 67.7589 | 0.87248 | 60.2014 | -0.10953
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.94957 | 65.5202 | 0.87267 | 60.214 | -0.0769
S2-Fixes | 45% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9752 | 67.2887 | 0.87326 | 60.2552 | -0.10194
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94957 | 65.5202 | 0.87354 | 60.274 | -0.076032
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97416 | 67.2169 | 0.87374 | 60.288 | -0.10042
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97416 | 67.2169 | 0.87381 | 60.2927 | -0.10035
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0164 | 70.1284 | 0.87391 | 60.2995 | -0.14245
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9885 | 68.2065 | 0.87433 | 60.3287 | -0.11417
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0186 | 70.2819 | 0.8744 | 60.3336 | -0.14418
S2-Fixes | 45% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9885 | 68.2065 | 0.87442 | 60.3347 | -0.11408
S2-Fixes | 45% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0149 | 70.0281 | 0.87483 | 60.3635 | -0.14007
S2-Fixes | 45% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0149 | 70.0281 | 0.87493 | 60.3702 | -0.13997
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95696 | 66.03 | 0.8754 | 60.4029 | -0.081552
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94955 | 65.5192 | 0.87543 | 60.4047 | -0.074123
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95703 | 66.0352 | 0.87549 | 60.4086 | -0.081545
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98781 | 68.1589 | 0.87594 | 60.44 | -0.11187
S2-Fixes | 45% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98781 | 68.1589 | 0.87603 | 60.4458 | -0.11178
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99934 | 68.9543 | 0.87647 | 60.4765 | -0.12287
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99934 | 68.9543 | 0.87656 | 60.4823 | -0.12278
S2-Fixes | 45% | Liberty | W Garrard | 341893 | 2MT OLIVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99754 | 68.8303 | 0.87702 | 60.5143 | -0.12052
S2-Fixes | 45% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0168 | 70.1594 | 0.87704 | 60.516 | -0.13976
S2-Fixes | 45% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0168 | 70.1594 | 0.87714 | 60.5226 | -0.13966
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.98201 | 67.7589 | 0.87759 | 60.5536 | -0.10442
S2-Fixes | 45% | Liberty | W Garrard | 341896 | 2MT OLIVE J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99683 | 68.7815 | 0.87816 | 60.5928 | -0.11868
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95513 | 65.9041 | 0.87816 | 60.5929 | -0.076973
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95216 | 65.6988 | 0.87826 | 60.5997 | -0.073901
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96551 | 66.6202 | 0.87845 | 60.613 | -0.087062
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0164 | 70.1284 | 0.87858 | 60.6217 | -0.13778
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96723 | 66.7391 | 0.87866 | 60.6277 | -0.088571
S2-Fixes | 45% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0164 | 70.1284 | 0.87867 | 60.6283 | -0.13768
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94988 | 65.5417 | 0.87876 | 60.6344 | -0.07112
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96744 | 66.7537 | 0.87889 | 60.6437 | -0.08855
S2-Fixes | 45% | Liberty | W Garrard | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96761 | 66.7649 | 0.87899 | 60.6506 | -0.088612
S2-Fixes | 45% | Liberty | W Garrard | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0181 | 163.9182 | 0.8791 | 141.535 | -0.13903
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0186 | 70.2819 | 0.87911 | 60.6583 | -0.13947
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0186 | 70.2819 | 0.8792 | 60.6649 | -0.13938
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95696 | 66.03 | 0.87932 | 60.6728 | -0.077641
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9833 | 67.8474 | 0.87932 | 60.673 | -0.10398
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95703 | 66.0352 | 0.8794 | 60.6784 | -0.077634
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95696 | 66.03 | 0.87954 | 60.688 | -0.07742
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97416 | 67.2169 | 0.8796 | 60.6927 | -0.094554
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95703 | 66.0352 | 0.87962 | 60.6937 | -0.077413
S2-Fixes | 45% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.9607 | 66.2885 | 0.87967 | 60.6976 | -0.081027
S2-Fixes | 45% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96075 | 66.2916 | 0.87973 | 60.7015 | -0.081017
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.99934 | 68.9543 | 0.87998 | 60.7189 | -0.11935
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.9473 | 65.3638 | 0.88014 | 60.7296 | -0.067162
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9473 | 65.3638 | 0.88043 | 60.7496 | -0.066872
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94955 | 65.5192 | 0.88066 | 60.7658 | -0.068889
S2-Fixes | 45% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98201 | 67.7589 | 0.88088 | 60.7806 | -0.10113
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99189 | 68.4406 | 0.88097 | 60.7872 | -0.11092
S2-Fixes | 45% | Liberty | W Garrard | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.96311 | 66.4548 | 0.88148 | 60.822 | -0.081635
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99213 | 68.4569 | 0.88203 | 60.8604 | -0.1101
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95513 | 65.9041 | 0.88212 | 60.8662 | -0.073013
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95513 | 65.9041 | 0.88233 | 60.8806 | -0.072804
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94988 | 65.5417 | 0.88257 | 60.8971 | -0.067313
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96723 | 66.7391 | 0.88262 | 60.9011 | -0.084609
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94988 | 65.5417 | 0.88276 | 60.9107 | -0.067115
S2-Fixes | 45% | Liberty | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94783 | 65.4002 | 0.88284 | 60.9161 | -0.064987
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96744 | 66.7537 | 0.88286 | 60.9171 | -0.084588
S2-Fixes | 45% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96723 | 66.7391 | 0.88286 | 60.9175 | -0.084371
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94475 | 65.1877 | 0.88289 | 60.9193 | -0.061861
S2-Fixes | 45% | Liberty | W Garrard | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97785 | 157.4337 | 0.8829 | 142.1467 | -0.09495
S2-Fixes | 45% | Liberty | W Garrard | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96761 | 66.7649 | 0.88296 | 60.924 | -0.084651
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94385 | 65.1254 | 0.88307 | 60.9316 | -0.060779
S2-Fixes | 45% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96744 | 66.7537 | 0.88309 | 60.9335 | -0.08435
S2-Fixes | 45% | Liberty | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94783 | 65.4002 | 0.88317 | 60.9388 | -0.064657
S2-Fixes | 45% | Liberty | W Garrard | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96761 | 66.7649 | 0.88319 | 60.9404 | -0.084412
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95216 | 65.6988 | 0.88347 | 60.9597 | -0.068683
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94316 | 65.0781 | 0.88352 | 60.9628 | -0.059641
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9833 | 67.8474 | 0.88395 | 60.9924 | -0.099347
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9833 | 67.8474 | 0.88402 | 60.997 | -0.09928
S2-Fixes | 45% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97416 | 67.2169 | 0.88406 | 61.0001 | -0.090099
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94376 | 65.1197 | 0.88416 | 61.0073 | -0.0596
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94849 | 65.4457 | 0.88422 | 61.0113 | -0.064266
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94849 | 65.4461 | 0.88429 | 61.0164 | -0.0642
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94955 | 65.5192 | 0.88462 | 61.0387 | -0.064935
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96065 | 66.2846 | 0.88477 | 61.0492 | -0.075876
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99189 | 68.4406 | 0.88481 | 61.0521 | -0.10708
S2-Fixes | 45% | Liberty | W Garrard | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94955 | 65.5192 | 0.88482 | 61.0523 | -0.064737
S2-Fixes | 45% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94957 | 65.5202 | 0.88487 | 61.0564 | -0.064693
S2-Fixes | 45% | Liberty | W Garrard | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99189 | 68.4406 | 0.88489 | 61.0576 | -0.107
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96065 | 66.2846 | 0.88563 | 61.1082 | -0.075021
S2-Fixes | 45% | Liberty | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95056 | 65.5886 | 0.88578 | 61.1185 | -0.064784
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99213 | 68.4569 | 0.88584 | 61.1232 | -0.10629
S2-Fixes | 45% | Liberty | W Garrard | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99213 | 68.4569 | 0.88592 | 61.1287 | -0.10621
S2-Fixes | 45% | Liberty | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95056 | 65.5886 | 0.8861 | 61.1411 | -0.064456
S2-Fixes | 45% | Liberty | W Garrard | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96547 | 66.6172 | 0.88616 | 61.145 | -0.079307
S2-Fixes | 45% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94124 | 64.9457 | 0.88697 | 61.2009 | -0.054273
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95216 | 65.6988 | 0.88741 | 61.2316 | -0.064742
S2-Fixes | 45% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94988 | 65.5417 | 0.88745 | 61.2343 | -0.062426
S2-Fixes | 45% | Liberty | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95235 | 65.7124 | 0.88761 | 61.2449 | -0.064746
S2-Fixes | 45% | Liberty | W Garrard | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95216 | 65.6988 | 0.88761 | 61.2452 | -0.064544
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94316 | 65.0781 | 0.88842 | 61.3009 | -0.054741
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.9473 | 65.3638 | 0.88847 | 61.3047 | -0.058828
S2-Fixes | 45% | Liberty | W Garrard | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95513 | 65.9041 | 0.88878 | 61.3258 | -0.066351
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94376 | 65.1197 | 0.88906 | 61.3452 | -0.054704
S2-Fixes | 45% | Liberty | W Garrard | 341343 | 2CONTOWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99407 | 68.5907 | 0.88951 | 61.3765 | -0.10455
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94385 | 65.1254 | 0.88953 | 61.3775 | -0.054318
S2-Fixes | 45% | Liberty | W Garrard | 341342 | 2CONTOWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99419 | 68.5991 | 0.88965 | 61.3858 | -0.10454
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9833 | 67.8474 | 0.88974 | 61.3923 | -0.093552
S2-Fixes | 45% | Liberty | W Garrard | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94788 | 65.4038 | 0.89009 | 61.4161 | -0.057792
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96551 | 66.6202 | 0.8903 | 61.4309 | -0.075208
S2-Fixes | 45% | Liberty | W Garrard | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94788 | 65.4038 | 0.89036 | 61.435 | -0.057518
S2-Fixes | 45% | Liberty | W Garrard | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96473 | 66.5662 | 0.89044 | 61.4402 | -0.074289
S2-Fixes | 45% | Liberty | W Garrard | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96473 | 66.5662 | 0.89048 | 61.4429 | -0.074251
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94316 | 65.0781 | 0.89063 | 61.4532 | -0.052534
S2-Fixes | 45% | Liberty | W Garrard | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96491 | 66.5787 | 0.89063 | 61.4538 | -0.074274
S2-Fixes | 45% | Liberty | W Garrard | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96491 | 66.5787 | 0.89067 | 61.4564 | -0.074236
S2-Fixes | 45% | Liberty | W Garrard | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96525 | 66.602 | 0.89067 | 61.4564 | -0.074573
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94385 | 65.1254 | 0.8907 | 61.458 | -0.053151
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94475 | 65.1877 | 0.89082 | 61.4666 | -0.053929
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94475 | 65.1877 | 0.891 | 61.4788 | -0.053753
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94376 | 65.1197 | 0.89127 | 61.4973 | -0.052498
S2-Fixes | 45% | Liberty | W Garrard | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94913 | 65.49 | 0.89156 | 61.5178 | -0.057569
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94316 | 65.0781 | 0.89192 | 61.5422 | -0.051244
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94385 | 65.1254 | 0.89199 | 61.547 | -0.051861
S2-Fixes | 45% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95696 | 66.03 | 0.892 | 61.5478 | -0.06496
S2-Fixes | 45% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95703 | 66.0352 | 0.89208 | 61.5533 | -0.064954
S2-Fixes | 45% | Liberty | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9541 | 65.8328 | 0.89212 | 61.5562 | -0.061979
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.9473 | 65.3638 | 0.89216 | 61.5589 | -0.055144
S2-Fixes | 45% | Liberty | W Garrard | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96456 | 66.5548 | 0.89217 | 61.5596 | -0.072393
S2-Fixes | 45% | Liberty | W Garrard | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95037 | 65.5755 | 0.89218 | 61.5602 | -0.058192
S2-Fixes | 45% | Liberty | W Garrard | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96456 | 66.5548 | 0.8922 | 61.5621 | -0.072357
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94316 | 65.0781 | 0.89225 | 61.5651 | -0.050913
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94475 | 65.1877 | 0.89229 | 61.5678 | -0.052462
S2-Fixes | 45% | Liberty | W Garrard | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.9473 | 65.3638 | 0.89234 | 61.5712 | -0.054965
S2-Fixes | 45% | Liberty | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95434 | 65.8496 | 0.89238 | 61.5742 | -0.061962
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94316 | 65.0781 | 0.89243 | 61.5773 | -0.050735
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94376 | 65.1197 | 0.89256 | 61.5863 | -0.051209
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94376 | 65.1197 | 0.89289 | 61.6091 | -0.050878
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94376 | 65.1197 | 0.89306 | 61.6214 | -0.050701
S2-Fixes | 45% | Liberty | W Garrard | 342067 | 2PHIL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.9738 | 67.1925 | 0.8932 | 61.6306 | -0.080607
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94385 | 65.1254 | 0.89337 | 61.6423 | -0.05048
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94385 | 65.1254 | 0.89354 | 61.6545 | -0.050303
S2-Fixes | 45% | Liberty | W Garrard | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94746 | 65.375 | 0.89357 | 61.6567 | -0.053889
S2-Fixes | 45% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9833 | 67.8474 | 0.89415 | 61.6961 | -0.089149
S2-Fixes | 45% | Liberty | W Garrard | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96201 | 66.3788 | 0.89459 | 61.7267 | -0.067423
S2-Fixes | 45% | Liberty | W Garrard | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96201 | 66.3788 | 0.89462 | 61.7287 | -0.067393
S2-Fixes | 45% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.9607 | 66.2885 | 0.89464 | 61.7304 | -0.066058
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94475 | 65.1877 | 0.89466 | 61.7318 | -0.050085
S2-Fixes | 45% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96075 | 66.2916 | 0.8947 | 61.7342 | -0.06605
S2-Fixes | 45% | Liberty | W Garrard | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94475 | 65.1877 | 0.89484 | 61.744 | -0.049909
S2-Fixes | 45% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94124 | 64.9457 | 0.89549 | 61.7888 | -0.045752
S2-Fixes | 45% | Liberty | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95402 | 65.8271 | 0.8955 | 61.7897 | -0.058513
S2-Fixes | 45% | Liberty | W Garrard | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 0.96311 | 66.4548 | 0.89567 | 61.8011 | -0.067444
S2-Fixes | 45% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94124 | 64.9457 | 0.89572 | 61.8044 | -0.045527
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95156 | 65.6576 | 0.89595 | 61.8206 | -0.055609
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95208 | 65.6935 | 0.8965 | 61.8587 | -0.055577
S2-Fixes | 45% | Liberty | W Garrard | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96392 | 66.5106 | 0.89665 | 61.8685 | -0.067277
S2-Fixes | 45% | Liberty | W Garrard | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96392 | 66.5106 | 0.89667 | 61.8706 | -0.067247
S2-Fixes | 45% | Liberty | W Garrard | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95402 | 65.8271 | 0.89676 | 61.8762 | -0.057259
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95156 | 65.6576 | 0.89679 | 61.8784 | -0.054772
S2-Fixes | 45% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.96065 | 66.2846 | 0.8968 | 61.8794 | -0.063844
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94849 | 65.4457 | 0.89697 | 61.8912 | -0.051514
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4457 | 0.89698 | 61.8917 | -0.051508
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94849 | 65.4461 | 0.89702 | 61.8946 | -0.051472
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4461 | 0.89703 | 61.895 | -0.051466
S2-Fixes | 45% | Liberty | W Garrard | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4457 | 0.89733 | 61.9158 | -0.051157
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94316 | 65.0781 | 0.89733 | 61.916 | -0.045827
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.95208 | 65.6935 | 0.89734 | 61.9164 | -0.05474
S2-Fixes | 45% | Liberty | W Garrard | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94849 | 65.4461 | 0.89738 | 61.9192 | -0.051115
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94376 | 65.1197 | 0.89797 | 61.9598 | -0.045796
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95156 | 65.6576 | 0.89804 | 61.9647 | -0.053521
S2-Fixes | 45% | Liberty | W Garrard | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.95208 | 65.6935 | 0.89859 | 62.0027 | -0.05349
S2-Fixes | 45% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.96551 | 66.6202 | 0.8987 | 62.0106 | -0.066806
S2-Fixes | 45% | Liberty | W Garrard | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94385 | 65.1254 | 0.89872 | 62.0119 | -0.045123
S2-Fixes | 45% | Liberty | W Garrard | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.96448 | 66.5494 | 0.89889 | 62.0236 | -0.065592
S2-Fixes | 45% | Liberty | W Garrard | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.96448 | 66.5494 | 0.89892 | 62.0255 | -0.065565
S2-Fixes | 45% | Liberty | W Garrard | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94316 | 65.0781 | 0.89911 | 62.0384 | -0.044053
S2-Fixes | 45% | Liberty | W Garrard | 339208 | AE2-254 MAIN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98943 | 68.2706 | 0.89938 | 62.0569 | -0.090054
S2-Fixes | 45% | Liberty | W Garrard | 342205 | 2S LANCASTER | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98943 | 68.2706 | 0.89938 | 62.0569 | -0.090054
S2-Fixes | 45% | Liberty | W Garrard | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94376 | 65.1197 | 0.89974 | 62.0821 | -0.044024
S2-Fixes | 45% | Liberty | W Garrard | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95156 | 65.6576 | 0.89984 | 62.0891 | -0.051718
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342193 | 2S FLOYD | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96148 |  | 0.85824 |  | -0.08176
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341473 | 2FLOYD-SFL | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96167 |  | 0.85845 |  | -0.081555
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341210 | 2BROUGHT TW | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96155 |  | 0.85885 |  | -0.081153
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342364 | 2TOMM GOOC | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97302 |  | 0.85909 |  | -0.08091
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342367 | 2TOMM GOOC | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97306 |  | 0.85914 |  | -0.080863
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341470 | 2FLOYD EK | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95576 |  | 0.86546 |  | -0.074538
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341471 | 2FLOYD TAP | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95582 |  | 0.86553 |  | -0.074466
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341848 | 2MCKEE | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96647 |  | 0.86823 |  | -0.071769
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341209 | 2BROUGTWN T | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97092 |  | 0.86942 |  | -0.070583
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342220 | 2SAND GAP | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96303 |  | 0.88176 |  | -0.058242
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342223 | 2SAND GAP T | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9633 |  | 0.88205 |  | -0.057946
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342511 | 2WOODSTOCK | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95339 |  | 0.88293 |  | -0.057073
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341617 | 2HIGHLAND E | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97213 |  | 0.88967 |  | -0.050326
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341641 | 2HOMESTEAD | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.98628 |  | 0.89281 |  | -0.047194
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341115 | 2BIG HILL T | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96482 |  | 0.89403 |  | -0.045968
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341114 | 2BIG HILL | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96875 |  | 0.89656 |  | -0.043443
S2-Fixes | 45% | Liberty | W Garrard LibJ | 342346 | 2THREE LINK | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9647 |  | 0.89779 |  | -0.042215
S2-Fixes | 45% | Liberty | W Garrard LibJ | 341887 | 2MONTICELLO | 69.000 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.99207 |  | 0.89921 |  | -0.040792
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95679 | 66.0186 | 0.7829 | 54.0203 | -0.17389
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95684 | 66.0219 | 0.78297 | 54.0252 | -0.17386
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.94577 | 65.2581 | 0.78416 | 54.1069 | -0.16161
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9569 | 66.0258 | 0.7977 | 55.041 | -0.1592
S2-Fixes | 45% | Liberty | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94616 | 65.2848 | 0.81039 | 55.9167 | -0.13577
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96191 | 66.3717 | 0.81432 | 56.1882 | -0.14759
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96212 | 66.3864 | 0.81457 | 56.2056 | -0.14755
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95136 | 65.6439 | 0.82323 | 56.8031 | -0.12813
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95144 | 65.6491 | 0.82332 | 56.8092 | -0.12811
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.962 | 66.378 | 0.82617 | 57.0055 | -0.13583
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94143 | 64.9585 | 0.8274 | 57.0905 | -0.11403
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94175 | 64.9808 | 0.82777 | 57.1158 | -0.11398
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98442 | 67.9253 | 0.83436 | 57.5708 | -0.15006
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98442 | 67.9253 | 0.83595 | 57.6807 | -0.14847
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98714 | 68.1128 | 0.83757 | 57.7922 | -0.14957
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98247 | 67.7905 | 0.83785 | 57.8114 | -0.14462
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98714 | 68.1128 | 0.83916 | 57.9017 | -0.14799
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 1.0145 | 70.0028 | 0.83924 | 57.9076 | -0.17529
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98247 | 67.7905 | 0.83935 | 57.9153 | -0.14312
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98647 | 68.0661 | 0.84254 | 58.1349 | -0.14393
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94321 | 65.0812 | 0.84296 | 58.1644 | -0.10024
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9455 | 65.2392 | 0.84302 | 58.1682 | -0.10248
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94867 | 65.4582 | 0.84389 | 58.2286 | -0.10478
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.98647 | 68.0661 | 0.84403 | 58.2382 | -0.14243
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94891 | 65.4751 | 0.84417 | 58.2476 | -0.10475
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.944 | 65.1363 | 0.84499 | 58.3042 | -0.099016
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.90906 | 62.7254 | 0.84625 | 58.3915 | -0.062809
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.91094 | 62.8552 | 0.84828 | 58.531 | -0.062668
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94336 | 65.0919 | 0.84832 | 58.5337 | -0.095046
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97173 | 67.0492 | 0.84948 | 58.6142 | -0.12225
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94336 | 65.0919 | 0.85061 | 58.6918 | -0.092755
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94321 | 65.0812 | 0.85243 | 58.8178 | -0.090773
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9455 | 65.2392 | 0.85271 | 58.837 | -0.092785
S2-Fixes | 45% | Liberty | Alcalde | 341233 | 2CABIN HOLLW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95607 | 65.9691 | 0.85427 | 58.9445 | -0.10181
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93772 | 64.7029 | 0.85457 | 58.9653 | -0.083153
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93862 | 64.7649 | 0.85462 | 58.9686 | -0.084005
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97173 | 67.0492 | 0.85474 | 58.9768 | -0.11699
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93702 | 64.6542 | 0.85478 | 58.9796 | -0.082241
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97173 | 67.0492 | 0.85481 | 58.9821 | -0.11691
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.93763 | 64.6962 | 0.85544 | 59.0256 | -0.082183
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99058 | 68.35 | 0.85556 | 59.0336 | -0.13502
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98442 | 67.9253 | 0.85631 | 59.0851 | -0.12812
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98247 | 67.7905 | 0.85661 | 59.1064 | -0.12586
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342397 [2UPCHURCH T 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99083 | 68.3669 | 0.85682 | 59.1208 | -0.134
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99058 | 68.35 | 0.85693 | 59.1282 | -0.13365
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97857 | 67.521 | 0.85731 | 59.1545 | -0.12125
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94825 | 65.4293 | 0.85744 | 59.1637 | -0.090806
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94143 | 64.9585 | 0.85782 | 59.1893 | -0.083612
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94175 | 64.9808 | 0.85817 | 59.2137 | -0.083581
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342532 [2ZULA J NO 69.000] CKT 1 | 0.99083 | 68.3669 | 0.85818 | 59.2146 | -0.13264
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.90906 | 62.7254 | 0.85867 | 59.2485 | -0.050389
S2-Fixes | 45% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.013 | 69.8996 | 0.85885 | 59.261 | -0.15418
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97039 | 66.9572 | 0.85899 | 59.2705 | -0.1114
S2-Fixes | 45% | Liberty | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.92093 | 63.5442 | 0.85902 | 59.2724 | -0.06191
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98714 | 68.1128 | 0.85943 | 59.3009 | -0.12771
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94583 | 65.2625 | 0.86027 | 59.3584 | -0.085567
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97173 | 67.0492 | 0.86066 | 59.3856 | -0.11107
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.91094 | 62.8552 | 0.86067 | 59.386 | -0.050278
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94636 | 65.2986 | 0.86084 | 59.3981 | -0.085515
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99646 | 68.7558 | 0.86089 | 59.4016 | -0.13557
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98442 | 67.9253 | 0.861 | 59.4089 | -0.12343
S2-Fixes | 45% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98442 | 67.9253 | 0.86109 | 59.4151 | -0.12334
S2-Fixes | 45% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0149 | 70.0312 | 0.86111 | 59.4163 | -0.15384
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98247 | 67.7905 | 0.86116 | 59.4201 | -0.12131
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98647 | 68.0661 | 0.8612 | 59.4229 | -0.12526
S2-Fixes | 45% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98247 | 67.7905 | 0.86125 | 59.426 | -0.12122
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97857 | 67.521 | 0.86252 | 59.5137 | -0.11605
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97857 | 67.521 | 0.86259 | 59.519 | -0.11597
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0145 | 70.0028 | 0.86273 | 59.5287 | -0.1518
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 1.0167 | 70.1539 | 0.86321 | 59.5612 | -0.15352
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95136 | 65.6439 | 0.86387 | 59.607 | -0.087491
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.95144 | 65.6491 | 0.86395 | 59.6127 | -0.087484
S2-Fixes | 45% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.013 | 69.8996 | 0.86407 | 59.6208 | -0.14897
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98714 | 68.1128 | 0.86411 | 59.6235 | -0.12303
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97039 | 66.9572 | 0.86415 | 59.6262 | -0.10625
S2-Fixes | 45% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.013 | 69.8996 | 0.86417 | 59.6275 | -0.14887
S2-Fixes | 45% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98714 | 68.1128 | 0.8642 | 59.6297 | -0.12294
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97039 | 66.9572 | 0.86422 | 59.631 | -0.10618
S2-Fixes | 45% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97173 | 67.0492 | 0.86547 | 59.7172 | -0.10626
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98647 | 68.0661 | 0.86572 | 59.7349 | -0.12074
S2-Fixes | 45% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98647 | 68.0661 | 0.86581 | 59.7409 | -0.12066
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99646 | 68.7558 | 0.86614 | 59.7638 | -0.13032
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99646 | 68.7558 | 0.86623 | 59.7698 | -0.13023
S2-Fixes | 45% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0149 | 70.0312 | 0.86631 | 59.7751 | -0.14864
S2-Fixes | 45% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0149 | 70.0312 | 0.8664 | 59.7818 | -0.14854
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94959 | 65.522 | 0.86712 | 59.8312 | -0.082476
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.944 | 65.1363 | 0.86725 | 59.84 | -0.076759
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96191 | 66.3717 | 0.86726 | 59.8409 | -0.09465
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94577 | 65.2581 | 0.86744 | 59.853 | -0.078334
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96212 | 66.3864 | 0.86749 | 59.8571 | -0.094627
S2-Fixes | 45% | Liberty | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.96229 | 66.3977 | 0.8676 | 59.8641 | -0.094689
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0145 | 70.0028 | 0.86788 | 59.884 | -0.14665
S2-Fixes | 45% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0145 | 70.0028 | 0.86798 | 59.8907 | -0.14655
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97857 | 67.521 | 0.86839 | 59.9188 | -0.11018
S2-Fixes | 45% | Liberty | Alcalde | 342823 | 5WAYNE CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0172 | 163.7671 | 0.86839 | 139.8105 | -0.1488
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0167 | 70.1539 | 0.86839 | 59.9192 | -0.14833
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0167 | 70.1539 | 0.86849 | 59.9259 | -0.14823
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94391 | 65.1301 | 0.86873 | 59.9422 | -0.075186
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.97957 | 67.5901 | 0.86938 | 59.9872 | -0.11019
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.94577 | 65.2581 | 0.86947 | 59.9934 | -0.076299
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94391 | 65.1301 | 0.86969 | 60.0085 | -0.074226
S2-Fixes | 45% | Liberty | Alcalde | 341893 | 2MT OLIVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99462 | 68.6287 | 0.87051 | 60.0655 | -0.1241
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99058 | 68.35 | 0.87055 | 60.0679 | -0.12003
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97039 | 66.9572 | 0.87056 | 60.0683 | -0.099838
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.99646 | 68.7558 | 0.87062 | 60.0727 | -0.12584
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95136 | 65.6439 | 0.87076 | 60.0824 | -0.080601
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.95144 | 65.6491 | 0.87084 | 60.0881 | -0.080594
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95136 | 65.6439 | 0.87101 | 60.0995 | -0.080353
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.95144 | 65.6491 | 0.87109 | 60.1052 | -0.080346
S2-Fixes | 45% | Liberty | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.92093 | 63.5442 | 0.87125 | 60.1164 | -0.049679
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94653 | 65.3108 | 0.87158 | 60.1387 | -0.074958
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.99083 | 68.3669 | 0.87169 | 60.1468 | -0.11913
S2-Fixes | 45% | Liberty | Alcalde | 341896 | 2MT OLIVE J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.99395 | 68.5828 | 0.87176 | 60.1514 | -0.12219
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.962 | 66.378 | 0.8723 | 60.1886 | -0.089701
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94653 | 65.3108 | 0.87253 | 60.2048 | -0.074
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94142 | 64.9583 | 0.8729 | 60.2303 | -0.068521
S2-Fixes | 45% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97857 | 67.521 | 0.87315 | 60.2474 | -0.10541
S2-Fixes | 45% | Liberty | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.9344 | 64.4738 | 0.87355 | 60.2753 | -0.060848
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94142 | 64.9583 | 0.87365 | 60.2817 | -0.067777
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.944 | 65.1363 | 0.87394 | 60.3018 | -0.070065
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94959 | 65.522 | 0.87408 | 60.3115 | -0.075515
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.944 | 65.1363 | 0.87416 | 60.3172 | -0.069842
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96191 | 66.3717 | 0.87425 | 60.3232 | -0.08766
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94959 | 65.522 | 0.87432 | 60.3278 | -0.075279
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97957 | 67.5901 | 0.87447 | 60.3386 | -0.10509
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96212 | 66.3864 | 0.87448 | 60.3393 | -0.087639
S2-Fixes | 45% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96191 | 66.3717 | 0.87451 | 60.3414 | -0.087395
S2-Fixes | 45% | Liberty | Alcalde | 342787 | 5PULASK CO | 161 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.97355 | 156.7417 | 0.87453 | 140.799 | -0.099023
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97957 | 67.5901 | 0.87454 | 60.3433 | -0.10503
S2-Fixes | 45% | Liberty | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.96229 | 66.3977 | 0.87458 | 60.3463 | -0.087701
S2-Fixes | 45% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96212 | 66.3864 | 0.87475 | 60.3576 | -0.087374
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99058 | 68.35 | 0.87481 | 60.3616 | -0.11577
S2-Fixes | 45% | Liberty | Alcalde | 342115 | 2PULASK CO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.96229 | 66.3977 | 0.87485 | 60.3646 | -0.087436
S2-Fixes | 45% | Liberty | Alcalde | 342277 | 2SNOW | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99058 | 68.35 | 0.87489 | 60.3672 | -0.11569
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99083 | 68.3669 | 0.87592 | 60.4382 | -0.11491
S2-Fixes | 45% | Liberty | Alcalde | 342283 | 2SNOW T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99083 | 68.3669 | 0.876 | 60.4438 | -0.11483
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93862 | 64.7649 | 0.87617 | 60.456 | -0.062448
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94192 | 64.9925 | 0.87621 | 60.4586 | -0.065709
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93772 | 64.7029 | 0.87636 | 60.469 | -0.061361
S2-Fixes | 45% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97039 | 66.9572 | 0.87637 | 60.4693 | -0.094027
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95679 | 66.0186 | 0.87647 | 60.4763 | -0.080324
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95684 | 66.0219 | 0.87652 | 60.4802 | -0.080314
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94192 | 64.9925 | 0.87654 | 60.4813 | -0.06538
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94391 | 65.1301 | 0.87663 | 60.4876 | -0.067282
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93702 | 64.6542 | 0.87683 | 60.5012 | -0.060189
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94391 | 65.1301 | 0.87686 | 60.5031 | -0.067057
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94351 | 65.102 | 0.87691 | 60.5069 | -0.066596
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94351 | 65.1023 | 0.87699 | 60.512 | -0.066526
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93702 | 64.6542 | 0.87705 | 60.5161 | -0.059973
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94142 | 64.9583 | 0.87727 | 60.5317 | -0.064153
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93763 | 64.6962 | 0.87748 | 60.546 | -0.060147
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93763 | 64.6962 | 0.87769 | 60.5609 | -0.059931
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93772 | 64.7029 | 0.8782 | 60.5955 | -0.059527
S2-Fixes | 45% | Liberty | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94616 | 65.2848 | 0.87843 | 60.612 | -0.067722
S2-Fixes | 45% | Liberty | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94467 | 65.1821 | 0.87917 | 60.6625 | -0.065501
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94653 | 65.3108 | 0.87945 | 60.6823 | -0.06708
S2-Fixes | 45% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.94577 | 65.2581 | 0.87946 | 60.6829 | -0.066307
S2-Fixes | 45% | Liberty | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94467 | 65.1821 | 0.87949 | 60.6851 | -0.065174
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.93862 | 64.7649 | 0.8795 | 60.6855 | -0.059122
S2-Fixes | 45% | Liberty | Alcalde | 341719 | 2KEAVY 1 T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95987 | 66.2311 | 0.87955 | 60.689 | -0.08032
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.9569 | 66.0258 | 0.87961 | 60.6934 | -0.077282
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94653 | 65.3108 | 0.87968 | 60.6978 | -0.066855
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.944 | 65.1363 | 0.88041 | 60.7486 | -0.06359
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.93521 | 64.5298 | 0.88049 | 60.7539 | -0.054724
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97957 | 67.5901 | 0.8808 | 60.7754 | -0.098764
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.9569 | 66.0258 | 0.88162 | 60.8317 | -0.075277
S2-Fixes | 45% | Liberty | Alcalde | 341971 | 2NORWOOD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94959 | 65.522 | 0.88223 | 60.8736 | -0.067369
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94185 | 64.9876 | 0.88352 | 60.9626 | -0.058334
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94142 | 64.9583 | 0.88373 | 60.9776 | -0.057692
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93702 | 64.6542 | 0.88376 | 60.9796 | -0.053256
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94185 | 64.9876 | 0.88379 | 60.9814 | -0.058061
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93702 | 64.6542 | 0.88384 | 60.9847 | -0.053181
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93772 | 64.7029 | 0.88393 | 60.9911 | -0.053795
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94142 | 64.9583 | 0.88394 | 60.9915 | -0.057489
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93702 | 64.6542 | 0.88396 | 60.9936 | -0.053053
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93862 | 64.7649 | 0.88424 | 61.0123 | -0.054386
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94391 | 65.13 | 0.88431 | 61.0176 | -0.059599
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93763 | 64.6962 | 0.88441 | 61.024 | -0.05322
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.93763 | 64.6962 | 0.88448 | 61.0292 | -0.053145
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93763 | 64.6962 | 0.88461 | 61.038 | -0.053017
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341197 [2BRODHEAD 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9451 | 65.2116 | 0.88485 | 61.0545 | -0.060248
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.962 | 66.378 | 0.88493 | 61.06 | -0.077072
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93772 | 64.7029 | 0.88493 | 61.06 | -0.052795
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93772 | 64.7029 | 0.88513 | 61.074 | -0.052592
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94583 | 65.2625 | 0.8852 | 61.0785 | -0.060638
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93702 | 64.6542 | 0.88527 | 61.0838 | -0.051746
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93772 | 64.7029 | 0.88536 | 61.0901 | -0.05236
S2-Fixes | 45% | Liberty | Alcalde | 324950 | 2SCIENC HILL | 69 | LGEE' | 0.94 | 1.06 | B-345-100 | 0.9344 | 64.4738 | 0.88556 | 61.1039 | -0.048839
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95136 | 65.6439 | 0.88561 | 61.107 | -0.065753
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93862 | 64.7649 | 0.88567 | 61.1114 | -0.05295
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.95144 | 65.6491 | 0.88569 | 61.1126 | -0.065747
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-LIBJ-PU161 | 0.90906 | 62.7254 | 0.88573 | 61.1154 | -0.023333
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94636 | 65.2986 | 0.88575 | 61.1171 | -0.060602
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.93763 | 64.6962 | 0.88592 | 61.1282 | -0.05171
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.93862 | 64.7649 | 0.88624 | 61.1507 | -0.05238
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.93862 | 64.7649 | 0.88644 | 61.1647 | -0.052178
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94867 | 65.4582 | 0.88652 | 61.1699 | -0.062149
S2-Fixes | 45% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97957 | 67.5901 | 0.88654 | 61.1716 | -0.093022
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94891 | 65.4751 | 0.88678 | 61.1879 | -0.062132
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94148 | 64.9619 | 0.88714 | 61.213 | -0.054332
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-LIBJ-PU161 | 0.91094 | 62.8552 | 0.88766 | 61.2486 | -0.023283
S2-Fixes | 45% | Liberty | Alcalde | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95926 | 66.1886 | 0.88767 | 61.2492 | -0.071586
S2-Fixes | 45% | Liberty | Alcalde | 341977 | 2OAK HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95926 | 66.1886 | 0.88771 | 61.2519 | -0.071548
S2-Fixes | 45% | Liberty | Alcalde | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95944 | 66.2012 | 0.88787 | 61.2628 | -0.071571
S2-Fixes | 45% | Liberty | Alcalde | 341983 | 2OAK HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95944 | 66.2012 | 0.8879 | 61.2654 | -0.071533
S2-Fixes | 45% | Liberty | Alcalde | 341980 | 2OAK HILL NO | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95975 | 66.2227 | 0.88791 | 61.2654 | -0.071844
S2-Fixes | 45% | Liberty | Alcalde | 324758 | 2US STEEL | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.96396 | 66.5134 | 0.88791 | 61.2661 | -0.076047
S2-Fixes | 45% | Liberty | Alcalde | 324833 | 2CORBIN 2 | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.9633 | 66.4678 | 0.88812 | 61.2805 | -0.075179
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94351 | 65.102 | 0.88843 | 61.3018 | -0.055077
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.102 | 0.88844 | 61.3022 | -0.05507
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94351 | 65.1023 | 0.88848 | 61.3052 | -0.055031
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.1023 | 0.88849 | 61.3057 | -0.055024
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95679 | 66.0186 | 0.88876 | 61.3246 | -0.06803
S2-Fixes | 45% | Liberty | Alcalde | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 342067 [2PHIL 69.000] CKT 1 | 0.95947 | 66.2036 | 0.88877 | 61.3248 | -0.070706
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.102 | 0.88879 | 61.3267 | -0.054715
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341761 [2LIBERTY J 69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95684 | 66.0219 | 0.88882 | 61.3284 | -0.068021
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94351 | 65.1023 | 0.88884 | 61.3301 | -0.05467
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93521 | 64.5298 | 0.88896 | 61.3384 | -0.046252
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94825 | 65.4293 | 0.88918 | 61.3533 | -0.059073
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93521 | 64.5298 | 0.88919 | 61.3539 | -0.046027
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.90906 | 62.7254 | 0.88938 | 61.3669 | -0.019687
S2-Fixes | 45% | Liberty | Alcalde | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95923 | 66.187 | 0.88941 | 61.369 | -0.069826
S2-Fixes | 45% | Liberty | Alcalde | 342469 | 2W SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95923 | 66.187 | 0.88944 | 61.3715 | -0.069791
S2-Fixes | 45% | Liberty | Alcalde | 324965 | 2SOMERSET NO | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94927 | 65.4997 | 0.88959 | 61.3816 | -0.059683
S2-Fixes | 45% | Liberty | Alcalde | 324832 | 2CORBIN 1 | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.96051 | 66.2754 | 0.88995 | 61.4068 | -0.07056
S2-Fixes | 45% | Liberty | Alcalde | 324903 | 2MCKEE ROAD | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.94963 | 65.5243 | 0.88997 | 61.4082 | -0.059653
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93702 | 64.6542 | 0.89041 | 61.438 | -0.046612
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94583 | 65.2625 | 0.8905 | 61.4444 | -0.055335
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94825 | 65.4293 | 0.89057 | 61.4494 | -0.057679
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93702 | 64.6542 | 0.89061 | 61.4521 | -0.046408
S2-Fixes | 45% | Liberty | Alcalde | 341350 | 2CRESTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.95947 | 66.2036 | 0.89068 | 61.457 | -0.06879
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-RUS-WLF161 | 0.90906 | 62.7254 | 0.8907 | 61.4581 | -0.018367
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.93521 | 64.5298 | 0.89088 | 61.4709 | -0.044332
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93763 | 64.6962 | 0.89105 | 61.4822 | -0.04658
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94636 | 65.2986 | 0.89105 | 61.4827 | -0.055302
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.93521 | 64.5298 | 0.89108 | 61.4844 | -0.044136
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93772 | 64.7029 | 0.89117 | 61.491 | -0.046549
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93763 | 64.6962 | 0.89125 | 61.4962 | -0.046376
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 0.91094 | 62.8552 | 0.8913 | 61.4996 | -0.019645
S2-Fixes | 45% | Liberty | Alcalde | 324482 | 2CORBIN EAST | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.95868 | 66.1489 | 0.89146 | 61.5107 | -0.06722
S2-Fixes | 45% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.9569 | 66.0258 | 0.89147 | 61.5113 | -0.065428
S2-Fixes | 45% | Liberty | Alcalde | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95703 | 66.0351 | 0.89187 | 61.539 | -0.065161
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94583 | 65.2625 | 0.89189 | 61.5403 | -0.053945
S2-Fixes | 45% | Liberty | Alcalde | 342523 | 2ZOLLICOF | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95703 | 66.0351 | 0.8919 | 61.541 | -0.065132
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93862 | 64.7649 | 0.89201 | 61.5489 | -0.046609
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94583 | 65.2625 | 0.89202 | 61.5492 | -0.053816
S2-Fixes | 45% | Liberty | Alcalde | 341422 | 2E SOMERSET | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94583 | 65.2625 | 0.89222 | 61.5634 | -0.05361
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94636 | 65.2986 | 0.89244 | 61.5786 | -0.053913
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.94636 | 65.2986 | 0.89257 | 61.5874 | -0.053785
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93772 | 64.7029 | 0.89259 | 61.5886 | -0.045135
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-RUS-WLF161 | 0.91094 | 62.8552 | 0.89262 | 61.5906 | -0.018328
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.90906 | 62.7254 | 0.89271 | 61.5973 | -0.016348
S2-Fixes | 45% | Liberty | Alcalde | 341419 | 2E SOMERSE T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.94636 | 65.2986 | 0.89278 | 61.6016 | -0.053579
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89287 | 61.6079 | -0.016195
S2-Fixes | 45% | Liberty | Alcalde | 341029 | 2ASAHI M W | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93702 | 64.6542 | 0.89298 | 61.6153 | -0.044043
S2-Fixes | 45% | Liberty | Alcalde | 341379 | 2DAHL ROAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93772 | 64.7029 | 0.89339 | 61.6437 | -0.044336
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94391 | 65.13 | 0.89352 | 61.6529 | -0.050392
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94391 | 65.13 | 0.89353 | 61.6534 | -0.050385
S2-Fixes | 45% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95136 | 65.6439 | 0.89357 | 61.6562 | -0.057793
S2-Fixes | 45% | Liberty | Alcalde | 341032 | 2ASAHI M W T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341379 [2DAHL ROAD 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.93763 | 64.6962 | 0.89361 | 61.6593 | -0.044013
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341471 [2FLOYD TAP 69.000] TO BUS 341473 [2FLOYD-SFL T69.000] CKT 1 | 0.944 | 65.1363 | 0.89364 | 61.661 | -0.050367
S2-Fixes | 45% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95144 | 65.6491 | 0.89365 | 61.6617 | -0.057788
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94391 | 65.13 | 0.89385 | 61.6754 | -0.050067
S2-Fixes | 45% | Liberty | Alcalde | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95895 | 66.1676 | 0.89393 | 61.6813 | -0.065019
S2-Fixes | 45% | Liberty | Alcalde | 342526 | 2ZOLLICOF T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95895 | 66.1676 | 0.89396 | 61.6833 | -0.06499
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.90906 | 62.7254 | 0.89409 | 61.692 | -0.014976
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.9451 | 65.2116 | 0.89416 | 61.6969 | -0.050938
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89416 | 61.6974 | -0.050931
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_TYN-DELV161 | 0.90906 | 62.7254 | 0.8942 | 61.7001 | -0.014859
S2-Fixes | 45% | Liberty | Alcalde | 324787 | 2UNION UNDWR | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324787 [2UNION UNDWR69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 0.98939 | 68.2679 | 0.89439 | 61.7127 | -0.095002
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89449 | 61.7196 | -0.05061
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | 0.91094 | 62.8552 | 0.89463 | 61.7295 | -0.016314
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89478 | 61.7401 | -0.01616
S2-Fixes | 45% | Liberty | Alcalde | 324787 | 2UNION UNDWR | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 0.98939 | 68.2679 | 0.89483 | 61.7435 | -0.094556
S2-Fixes | 45% | Liberty | Alcalde | 341439 | 2ELK MT IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94649 | 65.3078 | 0.89496 | 61.7526 | -0.051525
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_MCCR-WAYNE161 | 0.90906 | 62.7254 | 0.89505 | 61.7582 | -0.014017
S2-Fixes | 45% | Liberty | Alcalde | 341439 | 2ELK MT IP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94649 | 65.3078 | 0.89516 | 61.7659 | -0.051332
S2-Fixes | 45% | Liberty | Alcalde | 341974 | 2NORWOOD T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94825 | 65.4293 | 0.89516 | 61.7661 | -0.053089
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89537 | 61.7805 | -0.013694
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94148 | 64.9619 | 0.89556 | 61.7934 | -0.045921
S2-Fixes | 45% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.962 | 66.378 | 0.89566 | 61.8008 | -0.066336
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94148 | 64.9619 | 0.89578 | 61.8088 | -0.045697
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94391 | 65.1301 | 0.89591 | 61.8178 | -0.048004
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.91094 | 62.8552 | 0.896 | 61.824 | -0.014944
S2-Fixes | 45% | Liberty | Alcalde | 342256 | 2SHOPVILLE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.93862 | 64.7649 | 0.89603 | 61.8264 | -0.042587
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89605 | 61.8271 | -0.013018
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_TYN-DELV161 | 0.91094 | 62.8552 | 0.89612 | 61.8321 | -0.014827
S2-Fixes | 45% | Liberty | Alcalde | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 341983 [2OAK HILL T 69.000] CKT 1 | 0.95962 | 66.2135 | 0.8962 | 61.8376 | -0.06342
S2-Fixes | 45% | Liberty | Alcalde | 341938 | 2NANCY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341980 [2OAK HILL NO69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.95962 | 66.2135 | 0.89622 | 61.8395 | -0.063392
S2-Fixes | 45% | Liberty | Alcalde | 339208 | AE2-254 MAIN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98547 | 67.9978 | 0.89623 | 61.8399 | -0.089245
S2-Fixes | 45% | Liberty | Alcalde | 342205 | 2S LANCASTER | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.98547 | 67.9978 | 0.89623 | 61.8399 | -0.089245
S2-Fixes | 45% | Liberty | Alcalde | 324964 | 2SOMERSET 3 | 69 | LGEE' | 0.94 | 1.06 | B-69-25 | 0.95558 | 65.9348 | 0.89639 | 61.8512 | -0.059183
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.90906 | 62.7254 | 0.89643 | 61.8534 | -0.012638
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89643 | 61.8539 | -0.01263
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | 0.90906 | 62.7254 | 0.89649 | 61.8581 | -0.012568
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94336 | 65.0919 | 0.89662 | 61.8665 | -0.046746
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94336 | 65.0919 | 0.89662 | 61.867 | -0.046737
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 0.90906 | 62.7254 | 0.89671 | 61.8733 | -0.012349
S2-Fixes | 45% | Liberty | Alcalde | 342232 | 2SEWELLTON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342178 [2RUSSEL CO 69.000] TO BUS 342232 [2SEWELLTON 69.000] CKT 1 | 1.0032 | 69.2195 | 0.89679 | 61.8788 | -0.10639
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325140 [7GLENDALE S 345.00] CKT 1 | 0.90906 | 62.7254 | 0.89694 | 61.8891 | -0.01212
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_MCCR-WAYNE161 | 0.91094 | 62.8552 | 0.89696 | 61.8901 | -0.013987
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94336 | 65.0919 | 0.89697 | 61.8912 | -0.046386
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 0.90906 | 62.7254 | 0.89703 | 61.8951 | -0.012033
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | B-69-26 | 0.90906 | 62.7254 | 0.89705 | 61.8967 | -0.01201
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94321 | 65.0812 | 0.89711 | 61.9003 | -0.0461
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94867 | 65.4582 | 0.89711 | 61.9006 | -0.051559
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94321 | 65.0812 | 0.89711 | 61.9009 | -0.046092
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94867 | 65.4582 | 0.89712 | 61.9011 | -0.051552
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.94142 | 64.9583 | 0.89726 | 61.911 | -0.044163
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324130 [5ALCALDE 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89728 | 61.9123 | -0.013665
S2-Fixes | 45% | Liberty | Alcalde | 341947 | 2NELSON VAL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94391 | 65.1301 | 0.89729 | 61.9131 | -0.046624
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | B-69-26 | 0.93521 | 64.5298 | 0.89733 | 61.916 | -0.037881
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94891 | 65.4751 | 0.89737 | 61.9184 | -0.051545
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94891 | 65.4751 | 0.89738 | 61.919 | -0.051538
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94321 | 65.0812 | 0.89745 | 61.9241 | -0.045755
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.93521 | 64.5298 | 0.89745 | 61.9243 | -0.037761
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94148 | 64.9619 | 0.89746 | 61.9248 | -0.044015
S2-Fixes | 45% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94867 | 65.4582 | 0.89755 | 61.9307 | -0.051122
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.94391 | 65.13 | 0.89755 | 61.9313 | -0.046358
S2-Fixes | 45% | Liberty | Alcalde | 341581 | 2GREGORY RD | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.9866 | 68.0752 | 0.89758 | 61.9333 | -0.089012
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94148 | 64.9619 | 0.89766 | 61.9383 | -0.043821
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94142 | 64.9583 | 0.89766 | 61.9383 | -0.043768
S2-Fixes | 45% | Liberty | Alcalde | 341578 | 2GREGORY R T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_MCCR-WAYNE161 | 0.98667 | 68.0804 | 0.89767 | 61.9391 | -0.089004
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341974 [2NORWOOD T 69.000] TO BUS 342256 [2SHOPVILLE 69.000] CKT 1 | 0.94142 | 64.9583 | 0.89778 | 61.9465 | -0.043649
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.94185 | 64.9876 | 0.89778 | 61.947 | -0.044067
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94143 | 64.9585 | 0.89779 | 61.9473 | -0.043641
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94143 | 64.9585 | 0.8978 | 61.9479 | -0.043633
S2-Fixes | 45% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94891 | 65.4751 | 0.89781 | 61.9486 | -0.051108
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 0.90906 | 62.7254 | 0.89782 | 61.9498 | -0.01124
S2-Fixes | 45% | Liberty | Alcalde | 324737 | 2SOMERSET SO | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.96034 | 66.2637 | 0.89787 | 61.953 | -0.062475
S2-Fixes | 45% | Liberty | Alcalde | 325084 | 2FLOYD EKP T | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_COP-LIBJ-PU161 | 0.92093 | 63.5442 | 0.89792 | 61.9562 | -0.023014
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.90906 | 62.7254 | 0.89793 | 61.9572 | -0.011132
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324130 [5ALCALDE 161.00] TO BUS 324141 [5ELIHU 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89795 | 61.9588 | -0.01299
S2-Fixes | 45% | Liberty | Alcalde | 326533 | 2BUSH EKPC | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.9435 | 65.1012 | 0.89802 | 61.9633 | -0.045477
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94391 | 65.13 | 0.89805 | 61.9651 | -0.045867
S2-Fixes | 45% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94143 | 64.9585 | 0.89809 | 61.968 | -0.043341
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.94175 | 64.9808 | 0.89812 | 61.9706 | -0.043625
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94175 | 64.9808 | 0.89813 | 61.9712 | -0.043617
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | 0.90906 | 62.7254 | 0.89813 | 61.9713 | -0.010929
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95186 | 65.6783 | 0.89816 | 61.9732 | -0.053697
S2-Fixes | 45% | Liberty | Alcalde | 326533 | 2BUSH EKPC | 69 | LGEE' | 0.94 | 1.06 | EKPC_P1-2_TYN-DELV161 | 0.9435 | 65.1012 | 0.89822 | 61.977 | -0.045278
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 342286 [2SOMERSET 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89824 | 61.9784 | -0.046859
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 0.90906 | 62.7254 | 0.8983 | 61.9829 | -0.01076
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 324143 [5FARLEY 161.00] TO BUS 324527 [2FARLEY KU 69.000] CKT 1 | 0.93521 | 64.5298 | 0.89831 | 61.9837 | -0.0369
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.91094 | 62.8552 | 0.89833 | 61.985 | -0.012611
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.91094 | 62.8552 | 0.89834 | 61.9856 | -0.012603
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.9455 | 65.2392 | 0.8984 | 61.9896 | -0.047095
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324112 [7PINEVILLE 345.00] CKT 1 | 0.91094 | 62.8552 | 0.8984 | 61.9898 | -0.012542
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9455 | 65.2392 | 0.89841 | 61.9902 | -0.047086
S2-Fixes | 45% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.94175 | 64.9808 | 0.89842 | 61.9913 | -0.043326
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342751 [5JAMESTOWN T161.00] CKT 1 | 0.90906 | 62.7254 | 0.89856 | 62.0009 | -0.010499
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324100 [7ALCALDE 345.00] TO BUS 324102 [7BROWN NORTH345.00] CKT 1 | 0.91094 | 62.8552 | 0.89862 | 62.0049 | -0.012323
S2-Fixes | 45% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.94336 | 65.0919 | 0.89862 | 62.005 | -0.044737
S2-Fixes | 45% | Liberty | Alcalde | 326542 | 2N CORBIN | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324527 [2FARLEY KU 69.000] TO BUS 324758 [2US STEEL 69.000] CKT 1 | 0.95243 | 65.7178 | 0.89862 | 62.0051 | -0.053807
S2-Fixes | 45% | Liberty | Alcalde | 341343 | 2CONTOWN | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99103 | 68.3808 | 0.89863 | 62.0056 | -0.092394
S2-Fixes | 45% | Liberty | Alcalde | 341941 | 2NELSN VAL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341233 [2CABIN HOLLW69.000] TO BUS 341974 [2NORWOOD T 69.000] CKT 1 | 0.94653 | 65.3108 | 0.89867 | 62.0083 | -0.047862
S2-Fixes | 45% | Liberty | Alcalde | 324816 | 2CEMETARY RD | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342745 [5JABEZ T 161.00] TO BUS 342799 [5S OAKHILL 161.00] CKT 1 | 0.90906 | 62.7254 | 0.89868 | 62.0091 | -0.010381
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9451 | 65.2116 | 0.89873 | 62.0126 | -0.046363
S2-Fixes | 45% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.9455 | 65.2392 | 0.89875 | 62.014 | -0.046742
S2-Fixes | 45% | Liberty | Alcalde | 341342 | 2CONTOWN T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341342 [2CONTOWN T 69.000] TO BUS 341761 [2LIBERTY J 69.000] CKT 1 | 0.99115 | 68.3891 | 0.89877 | 62.0148 | -0.092381
S2-Fixes | 45% | Liberty | Alcalde | 324969 | 2SMRST 615KU | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.95993 | 66.2355 | 0.8988 | 62.0169 | -0.061139
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325140 [7GLENDALE S 345.00] CKT 1 | 0.91094 | 62.8552 | 0.89885 | 62.0207 | -0.012094
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_W BER-THRLJ 69 | 0.95186 | 65.6783 | 0.89891 | 62.0248 | -0.052949
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342349 [2THREE LNK J69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95186 | 65.6783 | 0.89892 | 62.0253 | -0.052941
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342751 [5JAMESTOWN T161.00] TO BUS 342796 [5RUSSEL CO J161.00] CKT 1 | 0.91094 | 62.8552 | 0.89894 | 62.0267 | -0.012007
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | B-69-26 | 0.91094 | 62.8552 | 0.89896 | 62.0282 | -0.011984
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342754 [5LAUREL CO 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 0.93521 | 64.5298 | 0.89896 | 62.0284 | -0.036251
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94185 | 64.9876 | 0.89901 | 62.0314 | -0.042844
S2-Fixes | 45% | Liberty | Alcalde | 342472 | 2WALNUT GROV | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_SOMERSET-NORWOOD69 | 0.94142 | 64.9583 | 0.89905 | 62.0346 | -0.042373
S2-Fixes | 45% | Liberty | Alcalde | 341818 | 2MARETBURG T | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.94391 | 65.13 | 0.89916 | 62.0423 | -0.044748
S2-Fixes | 45% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94185 | 64.9876 | 0.8992 | 62.0446 | -0.042653
S2-Fixes | 45% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.94321 | 65.0812 | 0.89927 | 62.0494 | -0.04394
S2-Fixes | 45% | Liberty | Alcalde | 342349 | 2THREE LNK J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95186 | 65.6783 | 0.89936 | 62.0562 | -0.052495
S2-Fixes | 45% | Liberty | Alcalde | 324990 | 2WAITSBORO | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324737 [2SOMERSET SO69.000] TO BUS 342287 [2SOMERSET KU69.000] CKT 1 | 0.95967 | 66.2172 | 0.89939 | 62.058 | -0.060278
S2-Fixes | 45% | Liberty | Alcalde | 342433 | 2W BEREA J | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95491 | 65.8887 | 0.89942 | 62.0597 | -0.055493
S2-Fixes | 45% | Liberty | Alcalde | 341098 | 2BEREAKU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342430 [2W BEREA 69.000] TO BUS 342433 [2W BEREA J 69.000] CKT 1 | 0.95491 | 65.8888 | 0.89942 | 62.0597 | -0.055493
S2-Fixes | 45% | Liberty | Alcalde | 341110 | 2BIG CREEK | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.95077 | 65.603 | 0.8995 | 62.0657 | -0.051264
S2-Fixes | 45% | Liberty | Alcalde | 341197 | 2BRODHEAD | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94351 | 65.102 | 0.89965 | 62.0757 | -0.043861
S2-Fixes | 45% | Liberty | Alcalde | 341110 | 2BIG CREEK | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.95077 | 65.603 | 0.8997 | 62.079 | -0.051072
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342820 [5TYNER 161.00] TO BUS 342736 [5GREEN HAL T161.00] CKT 1 | 0.94192 | 64.9925 | 0.8997 | 62.0792 | -0.042223
S2-Fixes | 45% | Liberty | Alcalde | 341199 | 2BRODHD KU T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94351 | 65.1023 | 0.8997 | 62.0793 | -0.043812
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 0.91094 | 62.8552 | 0.89973 | 62.0812 | -0.011216
S2-Fixes | 45% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95679 | 66.0186 | 0.89979 | 62.0858 | -0.056997
S2-Fixes | 45% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | 0.94 | 1.05 | B-345-100 | 0.944 | 65.1363 | 0.8998 | 62.0861 | -0.044206
S2-Fixes | 45% | Liberty | Alcalde | 324995 | 2WAYNESBURG | 69 | LGEE' | 0.94 | 1.06 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.91094 | 62.8552 | 0.89984 | 62.0887 | -0.011109
S2-Fixes | 45% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 341617 [2HIGHLAND EK69.000] TO BUS 341896 [2MT OLIVE J 69.000] CKT 1 | 0.95684 | 66.0219 | 0.89985 | 62.0896 | -0.05699
S2-Fixes | 45% | Liberty | Alcalde | 341815 | 2MARETBURG | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_COP-LIBJ-PU161 | 0.9451 | 65.2116 | 0.89986 | 62.0906 | -0.045232
S2-Fixes | 45% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | 0.94 | 1.05 | OPEN LINE FROM BUS 342718 [5COOPER2 161.00] TO BUS 342757 [5LAUREL DAM 161.00] CKT 1 | 0.93521 | 64.5298 | 0.89988 | 62.092 | -0.03533
S2-Fixes | 45% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | 0.94 | 1.05 | EKPC_P1-2_TYN-DELV161 | 0.94192 | 64.9925 | 0.89989 | 62.0922 | -0.042033

## Sheet3
CONTINGENCY | (All)
Min of CONT VOLTS | Column Labels
Row Labels | Base | CCAP | McCreary | W Garrard | W Garrard Lib J | Alcalde | (blank) | Grand Total | CCAP | McCreary | W Garrard | W Garrard Lib J | Alcalde
2BIG HILL | 0.86667 | 0.87558 | 0.8712 | 0.86923 | 0.87246 | 0.8724 |  | 0.86667 | 0.0089039 | 0.0045296 | 0.0025523 | 0.0057865 | 0.0057232
2BIG HILL T | 0.86476 | 0.87349 | 0.8692 | 0.86726 | 0.87043 | 0.87037 |  | 0.86476 | 0.0087219 | 0.0044354 | 0.0024977 | 0.0056662 | 0.0056041
2BROUGHT TWN | 0.86154 | 0.85895 | 0.86407 | 0.85633 | 0.85787 | 0.86424 |  | 0.85633 | -0.0025975 | 0.0025251 | -0.0052097 | -0.003669 | 0.0026939
2BROUGTWN T | 0.87206 | 0.86949 | 0.87455 | 0.86691 | 0.86844 | 0.87472 |  | 0.86691 | -0.0025644 | 0.0024928 | -0.0051432 | -0.0036209 | 0.0026594
2CONWAY | 0.85654 | 0.86535 | 0.86102 | 0.85907 | 0.86227 | 0.8622 |  | 0.85654 | 0.0088081 | 0.0044811 | 0.0025252 | 0.0057245 | 0.005662
2CONWAY T | 0.85677 | 0.86558 | 0.86125 | 0.8593 | 0.8625 | 0.86244 |  | 0.85677 | 0.0088058 | 0.0044799 | 0.0025244 | 0.0057229 | 0.0056604
2FLOYD EK | 0.85704 | 0.87445 | 0.86139 | 0.86716 | 0.85979 | 0.86135 |  | 0.85704 | 0.017408 | 0.0043466 | 0.010118 | 0.0027514 | 0.0043112
2FLOYD TAP | 0.85711 | 0.87452 | 0.86146 | 0.86723 | 0.85986 | 0.86142 |  | 0.85711 | 0.017406 | 0.0043463 | 0.010117 | 0.0027511 | 0.0043108
2FLOYD-SFL T | 0.84995 | 0.86751 | 0.85434 | 0.86016 | 0.85273 | 0.8543 |  | 0.84995 | 0.017559 | 0.0043848 | 0.010206 | 0.0027757 | 0.0043491
2GAP OF RG T | 0.89079 | 0.89904 | 0.89139 | 0.89607 | 0.8908 | 0.89151 |  | 0.89079 | 0.008246 | 0.00059134 | 0.0052752 | 1.0133e-05 | 0.00071937
2GAP OF RIDG | 0.88211 | 0.89044 | 0.88271 | 0.88744 | 0.88212 | 0.88284 |  | 0.88211 | 0.0083291 | 0.00059742 | 0.0053286 | 1.0312e-05 | 0.0007267
2HIGHLAND EK | 0.89218 | 0.88972 | 0.89457 | 0.88724 | 0.8887 | 0.89473 |  | 0.88724 | -0.0024599 | 0.0023915 | -0.0049333 | -0.0034713 | 0.0025513
2HOMESTEAD S | 0.87186 | 0.8802 | 0.87253 | 0.87761 | 0.87205 | 0.87287 |  | 0.87186 | 0.0083367 | 0.00066698 | 0.0057521 | 0.00018895 | 0.0010094
2KEAVY 1 T | 0.88147 | 0.88923 | 0.88491 | 0.89029 | 0.88511 | 0.88503 |  | 0.88147 | 0.0077595 | 0.0034379 | 0.0088203 | 0.0036444 | 0.0035635
2LAUR CO IP | 0.88944 | 0.89712 | 0.89284 | 0.89817 | 0.89304 | 0.89297 |  | 0.88944 | 0.0076795 | 0.0034027 | 0.0087303 | 0.0036061 | 0.0035282
2MCKEE | 0.83619 | 0.84572 | 0.83941 | 0.84443 | 0.84038 | 0.83962 |  | 0.83619 | 0.0095291 | 0.0032216 | 0.0082452 | 0.0041969 | 0.00343
2MONTICELLO | 0.87842 | 0.88669 | 0.87908 | 0.88413 | 0.87861 | 0.87942 |  | 0.87842 | 0.0082738 | 0.00066185 | 0.0057087 | 0.00018752 | 0.0010018
2N ALBANY | 0.88721 | 0.89365 | 0.88792 | 0.89388 | 0.88867 | 0.88966 |  | 0.88721 | 0.0064352 | 0.00070637 | 0.0066694 | 0.0014539 | 0.0024439
2PINE GROVE | 0.87856 | 0.88634 | 0.88201 | 0.8874 | 0.88221 | 0.88213 |  | 0.87856 | 0.0077809 | 0.0034479 | 0.0088455 | 0.003654 | 0.003575
2PINE GRV T | 0.88109 | 0.88885 | 0.88453 | 0.88991 | 0.88474 | 0.88466 |  | 0.88109 | 0.0077586 | 0.0034381 | 0.0088202 | 0.0036435 | 0.0035647
2S ALBANY | 0.88339 | 0.88985 | 0.8841 | 0.89009 | 0.88485 | 0.88585 |  | 0.88339 | 0.0064633 | 0.00070947 | 0.0066986 | 0.0014603 | 0.0024546
2S FLOYD | 0.84974 | 0.86731 | 0.85413 | 0.85995 | 0.85252 | 0.85409 |  | 0.84974 | 0.017563 | 0.0043859 | 0.010209 | 0.0027764 | 0.0043501
2SAND GAP | 0.8592 | 0.86846 | 0.86233 | 0.86721 | 0.86328 | 0.86253 |  | 0.8592 | 0.0092605 | 0.0031303 | 0.0080124 | 0.0040779 | 0.0033327
2SAND GAP T | 0.8595 | 0.86876 | 0.86263 | 0.86751 | 0.86358 | 0.86283 |  | 0.8595 | 0.0092572 | 0.0031291 | 0.0080096 | 0.0040764 | 0.0033316
2SLAT | 0.87729 | 0.88541 | 0.87808 | 0.88366 | 0.87779 | 0.87878 |  | 0.87729 | 0.0081151 | 0.00078434 | 0.0063693 | 0.00049353 | 0.0014902
2THREE LINKS | 0.8622 | 0.87094 | 0.86665 | 0.8647 | 0.86788 | 0.86782 |  | 0.8622 | 0.0087485 | 0.0044496 | 0.0025063 | 0.0056843 | 0.0056221
2TOMM GOOC | 0.86181 | 0.85919 | 0.86436 | 0.85655 | 0.85811 | 0.86453 |  | 0.85655 | -0.0026229 | 0.0025496 | -0.0052606 | -0.0037047 | 0.00272
2TOMM GOOC T | 0.86186 | 0.85923 | 0.86441 | 0.8566 | 0.85815 | 0.86458 |  | 0.8566 | -0.0026225 | 0.0025492 | -0.0052599 | -0.0037042 | 0.0027196
2UPCHURCH | 0.87273 | 0.87967 | 0.87355 | 0.87971 | 0.87403 | 0.87514 |  | 0.87273 | 0.0069427 | 0.00081635 | 0.006984 | 0.0012981 | 0.002409
2UPCHURCH T | 0.87537 | 0.88229 | 0.87618 | 0.88233 | 0.87666 | 0.87777 |  | 0.87537 | 0.0069216 | 0.00081378 | 0.0069628 | 0.0012941 | 0.0024016
2W LONDON | 0.88481 | 0.89253 | 0.88823 | 0.89359 | 0.88843 | 0.88835 |  | 0.88481 | 0.0077242 | 0.0034226 | 0.0087811 | 0.0036272 | 0.0035488
2WAYNE CO | 0.87132 | 0.87903 | 0.87226 | 0.8785 | 0.87223 | 0.87347 |  | 0.87132 | 0.0077102 | 0.00094903 | 0.0071868 | 0.00091326 | 0.0021567
2WOODSTOCK | 0.8747 | 0.89171 | 0.87895 | 0.88458 | 0.87739 | 0.87891 |  | 0.8747 | 0.017008 | 0.0042452 | 0.0098835 | 0.0026869 | 0.0042107
2ZULA | 0.86761 | 0.87536 | 0.86857 | 0.87483 | 0.86853 | 0.86978 |  | 0.86761 | 0.0077434 | 0.00095308 | 0.0072176 | 0.00091714 | 0.002166
2ZULA J NO | 0.87154 | 0.87918 | 0.87249 | 0.87876 | 0.8725 | 0.87374 |  | 0.87154 | 0.0076388 | 0.00095075 | 0.0072185 | 0.00095874 | 0.0022079
2ZULA T | 0.86953 | 0.87725 | 0.87048 | 0.87673 | 0.87044 | 0.87169 |  | 0.86953 | 0.0077263 | 0.00095099 | 0.0072017 | 0.00091511 | 0.0021612
5WAYNE CO | 0.87131 | 0.88252 | 0.87226 | 0.88168 | 0.87222 | 0.87468 |  | 0.87131 | 0.011212 | 0.00094897 | 0.010367 | 0.00091314 | 0.0033691
(blank)
Grand Total | 0.83619 | 0.84572 | 0.83941 | 0.84443 | 0.84038 | 0.83962 |  | 0.83619 | 9

## Sheet2
Scenario | Scaled | RICE | Alt | BUS # | BUS Name | BUS V | RECORD | CONTINGENCY | BASE VOLTS | VOLTAGE | CONT VOLTS
S2 | 25% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96042 | 66.2689 | 0.8724 | 341114OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96042 | 66.2689 | 0.88584 | 341114OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95664 | 66.0085 | 0.87037 | 341115OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95664 | 66.0085 | 0.88353 | 341115OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95644 | 65.9941 | 0.86424 | 341210OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95644 | 65.9941 | 0.89906 | 341210OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341209 | 2BROUGTWN T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96586 | 66.6443 | 0.87472 | 341209OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341338 | 2CONWAY | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96256 | 66.4168 | 0.8622 | 341338OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341341 | 2CONWAY T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96277 | 66.4311 | 0.86244 | 341341OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341470 | 2FLOYD EK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95297 | 65.755 | 0.86135 | 341470OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341471 | 2FLOYD TAP | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95304 | 65.7595 | 0.86142 | 341471OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341473 | 2FLOYD-SFL T | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95929 | 66.191 | 0.8543 | 341473OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98122 | 67.7045 | 0.89151 | 341503EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98122 | 67.7045 | 0.89269 | 341503OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98122 | 67.7045 | 0.89274 | 341503OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97337 | 67.1625 | 0.88284 | 341506EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97337 | 67.1625 | 0.88402 | 341506OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97337 | 67.1625 | 0.88407 | 341506OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341617 | 2HIGHLAND EK | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96742 | 66.7519 | 0.89473 | 341617OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97388 | 67.1977 | 0.87287 | 341641EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97388 | 67.1977 | 0.87407 | 341641OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97388 | 67.1977 | 0.87413 | 341641OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97388 | 67.1977 | 0.8943 | 341641OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341719 | 2KEAVY 1 T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.9633 | 66.4675 | 0.88503 | 341719OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.9353 | 64.5357 | 0.89297 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.9353 | 64.5357 | 0.89318 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341848 | 2MCKEE | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95416 | 65.8369 | 0.83962 | 341848OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97974 | 67.6024 | 0.87942 | 341887EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97974 | 67.6024 | 0.88061 | 341887OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97974 | 67.6024 | 0.88067 | 341887OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98543 | 67.9946 | 0.88966 | 341926EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98543 | 67.9946 | 0.89058 | 341926OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98543 | 67.9946 | 0.89064 | 341926OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94445 | 65.1672 | 0.88213 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94445 | 65.1672 | 0.88245 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94681 | 65.3298 | 0.88466 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94681 | 65.3298 | 0.88498 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98199 | 67.7575 | 0.88585 | 342181EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98199 | 67.7575 | 0.88678 | 342181OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98199 | 67.7575 | 0.88684 | 342181OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342193 | 2S FLOYD | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95911 | 66.1783 | 0.85409 | 342193OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95154 | 65.6563 | 0.86253 | 342220OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95154 | 65.6563 | 0.87994 | 342220OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95182 | 65.6752 | 0.86283 | 342223OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95182 | 65.6752 | 0.88024 | 342223OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.99405 | 68.5895 | 0.87878 | 342268EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99405 | 68.5895 | 0.87999 | 342268OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99405 | 68.5895 | 0.88006 | 342268OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95825 | 66.119 | 0.86782 | 342346OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95825 | 66.119 | 0.89054 | 342346OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342364 | 2TOMM GOOC | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96769 | 66.7703 | 0.86453 | 342364OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342367 | 2TOMM GOOC T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96772 | 66.7726 | 0.86458 | 342367OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98531 | 67.9861 | 0.87514 | 342394EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98531 | 67.9861 | 0.87618 | 342394OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98531 | 67.9861 | 0.87625 | 342394OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98764 | 68.1471 | 0.87777 | 342397EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98764 | 68.1471 | 0.87881 | 342397OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98764 | 68.1471 | 0.87887 | 342397OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94271 | 65.047 | 0.88835 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94271 | 65.047 | 0.88862 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0081 | 69.5578 | 0.87347 | 342478EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0081 | 69.5578 | 0.87468 | 342478OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0081 | 69.5578 | 0.87476 | 342478OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342511 | 2WOODSTOCK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95014 | 65.5597 | 0.87891 | 342511OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0049 | 69.3374 | 0.86978 | 342529EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0049 | 69.3374 | 0.871 | 342529OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0049 | 69.3374 | 0.87107 | 342529OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0066 | 69.4587 | 0.87374 | 342532EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0066 | 69.4587 | 0.87495 | 342532OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0066 | 69.4587 | 0.87502 | 342532OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0065 | 69.4515 | 0.87169 | 342535EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0065 | 69.4515 | 0.8729 | 342535OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0065 | 69.4515 | 0.87298 | 342535OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | Alcalde | 342823 | 5WAYNE CO | 161 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0159 | 163.5608 | 0.87468 | 342823OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96431 | 66.5376 | 0.87558 | 341114OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96431 | 66.5376 | 0.89172 | 341114OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96046 | 66.2721 | 0.87349 | 341115OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96046 | 66.2721 | 0.8893 | 341115OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95837 | 66.1275 | 0.85895 | 341210OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341209 | 2BROUGTWN T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96777 | 66.7764 | 0.86949 | 341209OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341338 | 2CONWAY | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96666 | 66.6993 | 0.86535 | 341338OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341341 | 2CONWAY T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96686 | 66.7135 | 0.86558 | 341341OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341470 | 2FLOYD EK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96307 | 66.4518 | 0.87445 | 341470OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341471 | 2FLOYD TAP | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96313 | 66.4562 | 0.87452 | 341471OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341473 | 2FLOYD-SFL T | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96924 | 66.8775 | 0.86751 | 341473OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341503 | 2GAP OF RG T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98804 | 68.1746 | 0.89904 | 341503EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 341506 | 2GAP OF RIDG | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98024 | 67.6365 | 0.89044 | 341506EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98024 | 67.6365 | 0.89414 | 341506OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98024 | 67.6365 | 0.8942 | 341506OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341617 | 2HIGHLAND EK | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96952 | 66.8972 | 0.88972 | 341617OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97982 | 67.6073 | 0.8802 | 341641EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97982 | 67.6073 | 0.88391 | 341641OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97982 | 67.6073 | 0.88397 | 341641OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341719 | 2KEAVY 1 T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96792 | 66.7865 | 0.88923 | 341719OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93937 | 64.8168 | 0.89712 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93937 | 64.8168 | 0.89733 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341848 | 2MCKEE | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95731 | 66.0545 | 0.84572 | 341848OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 341887 | 2MONTICELLO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98565 | 68.0096 | 0.88669 | 341887EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98565 | 68.0096 | 0.89038 | 341887OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98565 | 68.0096 | 0.89044 | 341887OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98772 | 68.153 | 0.89365 | 341926EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98772 | 68.153 | 0.89645 | 341926OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98772 | 68.153 | 0.89651 | 341926OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94876 | 65.4645 | 0.88634 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94876 | 65.4645 | 0.88666 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95111 | 65.6264 | 0.88885 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95111 | 65.6264 | 0.88917 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.9843 | 67.9165 | 0.88985 | 342181EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9843 | 67.9165 | 0.89267 | 342181OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9843 | 67.9165 | 0.89273 | 342181OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342193 | 2S FLOYD | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96906 | 66.865 | 0.86731 | 342193OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95513 | 65.9041 | 0.86846 | 342220OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95513 | 65.9041 | 0.88298 | 342220OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95541 | 65.923 | 0.86876 | 342223OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95541 | 65.923 | 0.88328 | 342223OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342268 | 2SLAT | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.99841 | 68.8904 | 0.88541 | 342268EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99841 | 68.8904 | 0.88905 | 342268OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99841 | 68.8904 | 0.88912 | 342268OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96212 | 66.3866 | 0.87094 | 342346OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96212 | 66.3866 | 0.89623 | 342346OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342364 | 2TOMM GOOC | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96945 | 66.892 | 0.85919 | 342364OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342367 | 2TOMM GOOC T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96948 | 66.8943 | 0.85923 | 342367OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98769 | 68.1503 | 0.87967 | 342394EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98769 | 68.1503 | 0.88275 | 342394OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98769 | 68.1503 | 0.88282 | 342394OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.99001 | 68.311 | 0.88229 | 342397EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99001 | 68.311 | 0.88536 | 342397OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99001 | 68.311 | 0.88543 | 342397OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94681 | 65.3296 | 0.89253 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94681 | 65.3296 | 0.8928 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0105 | 69.7246 | 0.87903 | 342478EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0105 | 69.7246 | 0.88253 | 342478OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0105 | 69.7246 | 0.8826 | 342478OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342511 | 2WOODSTOCK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.9604 | 66.2673 | 0.89171 | 342511OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | CCAP | 342529 | 2ZULA | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0073 | 69.5047 | 0.87536 | 342529EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0073 | 69.5047 | 0.87887 | 342529OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0073 | 69.5047 | 0.87895 | 342529OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.009 | 69.6244 | 0.87918 | 342532EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.009 | 69.6244 | 0.88265 | 342532OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.009 | 69.6244 | 0.88272 | 342532OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342535 | 2ZULA T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.009 | 69.6185 | 0.87725 | 342535EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | CCAP | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.009 | 69.6185 | 0.88076 | 342535OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.009 | 69.6185 | 0.88084 | 342535OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | CCAP | 342823 | 5WAYNE CO | 161 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0164 | 163.638 | 0.88252 | 342823OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96001 | 66.2406 | 0.8712 | 341114OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96001 | 66.2406 | 0.88564 | 341114OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95624 | 65.9807 | 0.8692 | 341115OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95624 | 65.9807 | 0.88333 | 341115OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95619 | 65.9768 | 0.86407 | 341210OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95619 | 65.9768 | 0.89865 | 341210OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341209 | 2BROUGTWN T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96561 | 66.6272 | 0.87455 | 341209OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341338 | 2CONWAY | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96226 | 66.3961 | 0.86102 | 341338OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341341 | 2CONWAY T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96247 | 66.4104 | 0.86125 | 341341OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341470 | 2FLOYD EK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95306 | 65.7612 | 0.86139 | 341470OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341471 | 2FLOYD TAP | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95313 | 65.7656 | 0.86146 | 341471OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341473 | 2FLOYD-SFL T | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95955 | 66.2088 | 0.85434 | 341473OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97784 | 67.4712 | 0.89139 | 341503OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97784 | 67.4712 | 0.89144 | 341503OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341503 | 2GAP OF RG T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97784 | 67.4712 | 0.89298 | 341503EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.96996 | 66.9273 | 0.88271 | 341506OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.96996 | 66.9273 | 0.88276 | 341506OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341506 | 2GAP OF RIDG | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.96996 | 66.9273 | 0.88432 | 341506EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 341617 | 2HIGHLAND EK | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96718 | 66.7352 | 0.89457 | 341617OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97018 | 66.9424 | 0.87253 | 341641OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97018 | 66.9424 | 0.87259 | 341641OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97018 | 66.9424 | 0.8741 | 341641EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97018 | 66.9424 | 0.89262 | 341641OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.97018 | 66.9424 | 0.89908 | 341641OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341719 | 2KEAVY 1 T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96322 | 66.4619 | 0.88491 | 341719OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93507 | 64.5195 | 0.89284 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93507 | 64.5195 | 0.89306 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341848 | 2MCKEE | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95359 | 65.7976 | 0.83941 | 341848OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97607 | 67.3487 | 0.87908 | 341887OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97607 | 67.3487 | 0.87914 | 341887OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97607 | 67.3487 | 0.88064 | 341887EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97607 | 67.3487 | 0.89902 | 341887OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98276 | 67.8104 | 0.88792 | 341926OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98276 | 67.8104 | 0.88799 | 341926OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 341926 | 2N ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98276 | 67.8104 | 0.8892 | 341926EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94425 | 65.1534 | 0.88201 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94425 | 65.1534 | 0.88233 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94661 | 65.316 | 0.88453 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94661 | 65.316 | 0.88485 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97931 | 67.5727 | 0.8841 | 342181OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97931 | 67.5727 | 0.88417 | 342181OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342181 | 2S ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97931 | 67.5727 | 0.88539 | 342181EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342193 | 2S FLOYD | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95936 | 66.1961 | 0.85413 | 342193OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95107 | 65.6241 | 0.86233 | 342220OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95107 | 65.6241 | 0.8788 | 342220OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95135 | 65.643 | 0.86263 | 342223OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95135 | 65.643 | 0.8791 | 342223OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98996 | 68.3072 | 0.87808 | 342268OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98996 | 68.3072 | 0.87815 | 342268OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342268 | 2SLAT | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98996 | 68.3072 | 0.87953 | 342268EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95787 | 66.0928 | 0.86665 | 342346OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95787 | 66.0928 | 0.89035 | 342346OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342364 | 2TOMM GOOC | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96742 | 66.7523 | 0.86436 | 342364OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342367 | 2TOMM GOOC T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96746 | 66.7546 | 0.86441 | 342367OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.982 | 67.7578 | 0.87355 | 342394OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.982 | 67.7578 | 0.87362 | 342394OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342394 | 2UPCHURCH | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.982 | 67.7578 | 0.87481 | 342394EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98434 | 67.9194 | 0.87618 | 342397OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98434 | 67.9194 | 0.87625 | 342397OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342397 | 2UPCHURCH T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98434 | 67.9194 | 0.87744 | 342397EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94243 | 65.0279 | 0.88823 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94243 | 65.0279 | 0.88849 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0035 | 69.2443 | 0.87226 | 342478OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0035 | 69.2443 | 0.87234 | 342478OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0035 | 69.2443 | 0.87351 | 342478EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342511 | 2WOODSTOCK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95005 | 65.5533 | 0.87895 | 342511OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0003 | 69.0228 | 0.86857 | 342529OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0003 | 69.0228 | 0.86864 | 342529OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342529 | 2ZULA | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0003 | 69.0228 | 0.86982 | 342529EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0022 | 69.1511 | 0.87249 | 342532OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0022 | 69.1511 | 0.87257 | 342532OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342532 | 2ZULA J NO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0022 | 69.1511 | 0.87372 | 342532EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.002 | 69.1374 | 0.87048 | 342535OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.002 | 69.1374 | 0.87056 | 342535OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | McCreary | 342535 | 2ZULA T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.002 | 69.1374 | 0.87173 | 342535EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | McCreary | 342823 | 5WAYNE CO | 161 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.011 | 162.7691 | 0.87226 | 342823OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96516 | 66.5961 | 0.86923 | 341114OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96516 | 66.5961 | 0.89048 | 341114OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9613 | 66.3295 | 0.86726 | 341115OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9613 | 66.3295 | 0.88808 | 341115OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95942 | 66.2 | 0.85633 | 341210OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341209 | 2BROUGTWN T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96881 | 66.8481 | 0.86691 | 341209OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341338 | 2CONWAY | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96681 | 66.71 | 0.85907 | 341338OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341341 | 2CONWAY T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96702 | 66.7242 | 0.8593 | 341341OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341470 | 2FLOYD EK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95793 | 66.0972 | 0.86716 | 341470OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341471 | 2FLOYD TAP | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.958 | 66.1017 | 0.86723 | 341471OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341473 | 2FLOYD-SFL T | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96406 | 66.5204 | 0.86016 | 341473OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98464 | 67.9399 | 0.89607 | 341503EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98464 | 67.9399 | 0.89938 | 341503OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98464 | 67.9399 | 0.89943 | 341503OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97681 | 67.3999 | 0.88744 | 341506EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97681 | 67.3999 | 0.89079 | 341506OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97681 | 67.3999 | 0.89083 | 341506OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341617 | 2HIGHLAND EK | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97021 | 66.9445 | 0.88724 | 341617OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97703 | 67.4149 | 0.87761 | 341641EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97703 | 67.4149 | 0.88097 | 341641OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97703 | 67.4149 | 0.88103 | 341641OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341719 | 2KEAVY 1 T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96808 | 66.7977 | 0.89029 | 341719OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94032 | 64.882 | 0.89817 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94032 | 64.882 | 0.89838 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341848 | 2MCKEE | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95932 | 66.1927 | 0.84443 | 341848OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98287 | 67.8183 | 0.88413 | 341887EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98287 | 67.8183 | 0.88746 | 341887OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98287 | 67.8183 | 0.88751 | 341887OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98638 | 68.06 | 0.89388 | 341926EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98638 | 68.06 | 0.89635 | 341926OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98638 | 68.06 | 0.8964 | 341926OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94944 | 65.511 | 0.8874 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94944 | 65.511 | 0.88772 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.95178 | 65.6727 | 0.88991 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95178 | 65.6727 | 0.89023 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98294 | 67.8232 | 0.89009 | 342181EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98294 | 67.8232 | 0.89257 | 342181OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98294 | 67.8232 | 0.89262 | 342181OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342193 | 2S FLOYD | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.96388 | 66.5078 | 0.85995 | 342193OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9564 | 65.9918 | 0.86721 | 342220OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9564 | 65.9918 | 0.87691 | 342220OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95668 | 66.0106 | 0.86751 | 342223OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95668 | 66.0106 | 0.87721 | 342223OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.99663 | 68.7672 | 0.88366 | 342268EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99663 | 68.7672 | 0.88696 | 342268OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99663 | 68.7672 | 0.88702 | 342268OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96281 | 66.4339 | 0.8647 | 342346OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96281 | 66.4339 | 0.89503 | 342346OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342364 | 2TOMM GOOC | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97075 | 66.982 | 0.85655 | 342364OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342367 | 2TOMM GOOC T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.97079 | 66.9844 | 0.8566 | 342367OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98648 | 68.0671 | 0.87971 | 342394EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98648 | 68.0671 | 0.88246 | 342394OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98648 | 68.0671 | 0.88252 | 342394OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98881 | 68.228 | 0.88233 | 342397EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98881 | 68.228 | 0.88507 | 342397OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98881 | 68.228 | 0.88513 | 342397OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94777 | 65.3962 | 0.89359 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94777 | 65.3962 | 0.89385 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0097 | 69.6694 | 0.8785 | 342478EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0097 | 69.6694 | 0.88168 | 342478OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0097 | 69.6694 | 0.88175 | 342478OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342511 | 2WOODSTOCK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95528 | 65.9142 | 0.88458 | 342511OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0065 | 69.4494 | 0.87483 | 342529EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0065 | 69.4494 | 0.87802 | 342529OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0065 | 69.4494 | 0.87809 | 342529OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0082 | 69.5682 | 0.87876 | 342532EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0082 | 69.5682 | 0.8819 | 342532OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0082 | 69.5682 | 0.88197 | 342532OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0082 | 69.5632 | 0.87673 | 342535EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0082 | 69.5632 | 0.87992 | 342535OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0082 | 69.5632 | 0.87999 | 342535OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard | 342823 | 5WAYNE CO | 161 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0167 | 163.69 | 0.88168 | 342823OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96086 | 66.2991 | 0.87246 | 341114OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.96086 | 66.2991 | 0.88658 | 341114OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95707 | 66.0381 | 0.87043 | 341115OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95707 | 66.0381 | 0.88425 | 341115OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95756 | 66.0719 | 0.85787 | 341210OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341209 | 2BROUGTWN T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96698 | 66.7213 | 0.86844 | 341209OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341338 | 2CONWAY | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96302 | 66.4485 | 0.86227 | 341338OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341341 | 2CONWAY T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.96323 | 66.4628 | 0.8625 | 341341OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341470 | 2FLOYD EK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95189 | 65.6803 | 0.85979 | 341470OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341471 | 2FLOYD TAP | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95195 | 65.6848 | 0.85986 | 341471OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341473 | 2FLOYD-SFL T | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95797 | 66.0997 | 0.85273 | 341473OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97955 | 67.5889 | 0.8908 | 341503OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97955 | 67.5889 | 0.89086 | 341503OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341503 | 2GAP OF RG T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97955 | 67.5889 | 0.89633 | 341503EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97168 | 67.0459 | 0.88212 | 341506OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97168 | 67.0459 | 0.88217 | 341506OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341506 | 2GAP OF RIDG | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97168 | 67.0459 | 0.8877 | 341506EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 341617 | 2HIGHLAND EK | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96859 | 66.833 | 0.8887 | 341617OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9723 | 67.0888 | 0.87205 | 341641OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9723 | 67.0888 | 0.87211 | 341641OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.9723 | 67.0888 | 0.87761 | 341641EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.9723 | 67.0888 | 0.88971 | 341641OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.9723 | 67.0888 | 0.89691 | 341641OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341719 | 2KEAVY 1 T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.96283 | 66.4353 | 0.88511 | 341719OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93504 | 64.5179 | 0.89304 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93504 | 64.5179 | 0.89326 | 341737OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341848 | 2MCKEE | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95445 | 65.8572 | 0.84038 | 341848OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97818 | 67.4941 | 0.87861 | 341887OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97818 | 67.4941 | 0.87866 | 341887OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97818 | 67.4941 | 0.88412 | 341887EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97818 | 67.4941 | 0.89614 | 341887OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98526 | 67.9829 | 0.88867 | 341926OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98526 | 67.9829 | 0.88873 | 341926OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 341926 | 2N ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98526 | 67.9829 | 0.89277 | 341926EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94407 | 65.141 | 0.88221 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94407 | 65.141 | 0.88253 | 342070OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94643 | 65.3036 | 0.88474 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94643 | 65.3036 | 0.88506 | 342073OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98182 | 67.7458 | 0.88485 | 342181OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98182 | 67.7458 | 0.88491 | 342181OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342181 | 2S ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98182 | 67.7458 | 0.88897 | 342181EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342193 | 2S FLOYD | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95778 | 66.087 | 0.85252 | 342193OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95192 | 65.6825 | 0.86328 | 342220OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95192 | 65.6825 | 0.88 | 342220OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95219 | 65.7014 | 0.86358 | 342223OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95219 | 65.7014 | 0.8803 | 342223OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99272 | 68.4977 | 0.87779 | 342268OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99272 | 68.4977 | 0.87785 | 342268OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342268 | 2SLAT | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.99272 | 68.4977 | 0.88314 | 342268EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95869 | 66.1497 | 0.86788 | 342346OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95869 | 66.1497 | 0.89126 | 342346OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342364 | 2TOMM GOOC | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96881 | 66.8477 | 0.85811 | 342364OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342367 | 2TOMM GOOC T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96884 | 66.85 | 0.85815 | 342367OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98492 | 67.9595 | 0.87403 | 342394OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98492 | 67.9595 | 0.87409 | 342394OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342394 | 2UPCHURCH | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98492 | 67.9595 | 0.87848 | 342394EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98726 | 68.1206 | 0.87666 | 342397OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98726 | 68.1206 | 0.87673 | 342397OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342397 | 2UPCHURCH T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98726 | 68.1206 | 0.8811 | 342397EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94236 | 65.0229 | 0.88843 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94236 | 65.0229 | 0.8887 | 342451OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0072 | 69.4999 | 0.87223 | 342478OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0072 | 69.4999 | 0.8723 | 342478OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342478 | 2WAYNE CO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0072 | 69.4999 | 0.87725 | 342478EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342511 | 2WOODSTOCK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94934 | 65.5043 | 0.87739 | 342511OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.004 | 69.2792 | 0.86853 | 342529OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.004 | 69.2792 | 0.8686 | 342529OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342529 | 2ZULA | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.004 | 69.2792 | 0.87357 | 342529EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0058 | 69.4028 | 0.8725 | 342532OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0058 | 69.4028 | 0.87257 | 342532OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342532 | 2ZULA J NO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0058 | 69.4028 | 0.87746 | 342532EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0057 | 69.3934 | 0.87044 | 342535OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0057 | 69.3934 | 0.87052 | 342535OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1
S2 | 25% | Liberty | W Garrard Lib J | 342535 | 2ZULA T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0057 | 69.3934 | 0.87547 | 342535EKPC_P1-2_MCCR-WAYNE161
S2 | 25% | Liberty | W Garrard Lib J | 342823 | 5WAYNE CO | 161 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0155 | 163.4957 | 0.87222 | 342823OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1
S2 | 25% | Liberty | Base | 341848 | 2MCKEE | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95064 | 65.5941 | 0.83619
| 25% | Liberty | Base | 342193 | 2S FLOYD | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95552 | 65.9309 | 0.84974
| 25% | Liberty | Base | 341473 | 2FLOYD-SFL T | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.95571 | 65.9437 | 0.84995
| 25% | Liberty | Base | 341338 | 2CONWAY | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95966 | 66.2163 | 0.85654
| 25% | Liberty | Base | 341341 | 2CONWAY T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95986 | 66.2307 | 0.85677
| 25% | Liberty | Base | 341470 | 2FLOYD EK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94917 | 65.4925 | 0.85704
| 25% | Liberty | Base | 341471 | 2FLOYD TAP | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94923 | 65.4971 | 0.85711
| 25% | Liberty | Base | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94821 | 65.4262 | 0.8592
| 25% | Liberty | Base | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.94848 | 65.4452 | 0.8595
| 25% | Liberty | Base | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.95425 | 65.8433 | 0.86154
| 25% | Liberty | Base | 342364 | 2TOMM GOOC | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9655 | 66.6193 | 0.86181
| 25% | Liberty | Base | 342367 | 2TOMM GOOC T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96553 | 66.6217 | 0.86186
| 25% | Liberty | Base | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.9551 | 65.9019 | 0.8622
| 25% | Liberty | Base | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95344 | 65.7875 | 0.86476
| 25% | Liberty | Base | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.95715 | 66.0437 | 0.86667
| 25% | Liberty | Base | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0016 | 69.1096 | 0.86761
| 25% | Liberty | Base | 342529 | 2ZULA | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0016 | 69.1096 | 0.86769
| 25% | Liberty | Base | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0032 | 69.224 | 0.86953
| 25% | Liberty | Base | 342535 | 2ZULA T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0032 | 69.224 | 0.86961
| 25% | Liberty | Base | 342529 | 2ZULA | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0016 | 69.1096 | 0.87049
| 25% | Liberty | Base | 342823 | 5WAYNE CO | 161 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0129 | 163.0721 | 0.87131
| 25% | Liberty | Base | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0048 | 69.3307 | 0.87132
| 25% | Liberty | Base | 342478 | 2WAYNE CO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0048 | 69.3307 | 0.8714
| 25% | Liberty | Base | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 1.0034 | 69.2353 | 0.87154
| 25% | Liberty | Base | 342532 | 2ZULA J NO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 1.0034 | 69.2353 | 0.87162
| 25% | Liberty | Base | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.96978 | 66.915 | 0.87186
| 25% | Liberty | Base | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.96978 | 66.915 | 0.87192
| 25% | Liberty | Base | 341209 | 2BROUGTWN T | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.9637 | 66.4952 | 0.87206
| 25% | Liberty | Base | 342535 | 2ZULA T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0032 | 69.224 | 0.8724
| 25% | Liberty | Base | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98276 | 67.8103 | 0.87273
| 25% | Liberty | Base | 342394 | 2UPCHURCH | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98276 | 67.8103 | 0.8728
| 25% | Liberty | Base | 342478 | 2WAYNE CO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0048 | 69.3307 | 0.87418
| 25% | Liberty | Base | 342532 | 2ZULA J NO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 1.0034 | 69.2353 | 0.87437
| 25% | Liberty | Base | 342220 | 2SAND GAP | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94821 | 65.4262 | 0.87448
| 25% | Liberty | Base | 342511 | 2WOODSTOCK | 69 | EKPC' | OPEN LINE FROM BUS 341473 [2FLOYD-SFL T69.000] TO BUS 342115 [2PULASK CO 69.000] CKT 1 | 0.94613 | 65.2832 | 0.8747
| 25% | Liberty | Base | 342223 | 2SAND GAP T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | 0.94848 | 65.4452 | 0.87478
| 25% | Liberty | Base | 341641 | 2HOMESTEAD S | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.96978 | 66.915 | 0.87503
| 25% | Liberty | Base | 342394 | 2UPCHURCH | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98276 | 67.8103 | 0.8753
| 25% | Liberty | Base | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.9851 | 67.9718 | 0.87537
| 25% | Liberty | Base | 342397 | 2UPCHURCH T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.9851 | 67.9718 | 0.87544
| 25% | Liberty | Base | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.99016 | 68.3209 | 0.87729
| 25% | Liberty | Base | 342268 | 2SLAT | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.99016 | 68.3209 | 0.87736
| 25% | Liberty | Base | 342397 | 2UPCHURCH T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.9851 | 67.9718 | 0.87793
| 25% | Liberty | Base | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97567 | 67.3214 | 0.87842
| 25% | Liberty | Base | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97567 | 67.3214 | 0.87848
| 25% | Liberty | Base | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.94083 | 64.9175 | 0.87856
| 25% | Liberty | Base | 342070 | 2PINE GROVE | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.94083 | 64.9175 | 0.87888
| 25% | Liberty | Base | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95344 | 65.7875 | 0.88029
| 25% | Liberty | Base | 342268 | 2SLAT | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.99016 | 68.3209 | 0.88035
| 25% | Liberty | Base | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.9432 | 65.0807 | 0.88109
| 25% | Liberty | Base | 342073 | 2PINE GRV T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.9432 | 65.0807 | 0.88141
| 25% | Liberty | Base | 341719 | 2KEAVY 1 T | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.95979 | 66.2255 | 0.88147
| 25% | Liberty | Base | 341887 | 2MONTICELLO | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97567 | 67.3214 | 0.88156
| 25% | Liberty | Base | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.96924 | 66.8777 | 0.88211
| 25% | Liberty | Base | 341506 | 2GAP OF RIDG | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.96924 | 66.8777 | 0.88217
| 25% | Liberty | Base | 341114 | 2BIG HILL | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.95715 | 66.0437 | 0.88253
| 25% | Liberty | Base | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97983 | 67.6085 | 0.88339
| 25% | Liberty | Base | 342181 | 2S ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97983 | 67.6085 | 0.88346
| 25% | Liberty | Base | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93904 | 64.7937 | 0.88481
| 25% | Liberty | Base | 342451 | 2W LONDON | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93904 | 64.7937 | 0.88507
| 25% | Liberty | Base | 341506 | 2GAP OF RIDG | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.96924 | 66.8777 | 0.88529
| 25% | Liberty | Base | 342181 | 2S ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97983 | 67.6085 | 0.88578
| 25% | Liberty | Base | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.98328 | 67.8461 | 0.88721
| 25% | Liberty | Base | 341926 | 2N ALBANY | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.98328 | 67.8461 | 0.88728
| 25% | Liberty | Base | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341848 [2MCKEE 69.000] TO BUS 342391 [2TYNER 69.000] CKT 1 | 0.9551 | 65.9019 | 0.88735
| 25% | Liberty | Base | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 0.93172 | 64.2886 | 0.88944
| 25% | Liberty | Base | 341926 | 2N ALBANY | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.98328 | 67.8461 | 0.8896
| 25% | Liberty | Base | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 0.93172 | 64.2886 | 0.88966
| 25% | Liberty | Base | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 0.97713 | 67.422 | 0.89079
| 25% | Liberty | Base | 341503 | 2GAP OF RG T | 69 | EKPC' | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 0.97713 | 67.422 | 0.89085
| 25% | Liberty | Base | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.96978 | 66.915 | 0.89159
| 25% | Liberty | Base | 341617 | 2HIGHLAND EK | 69 | EKPC' | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 0.96529 | 66.6048 | 0.89218
| 25% | Liberty | Base | 341503 | 2GAP OF RG T | 69 | EKPC' | EKPC_P1-2_MCCR-WAYNE161 | 0.97713 | 67.422 | 0.89394
| 25% | Liberty | Base | 341210 | 2BROUGHT TWN | 69 | EKPC' | OPEN LINE FROM BUS 341515 [2GARRARD CO 69.000] TO BUS 342205 [2S LANCASTER69.000] CKT 1 | 0.95425 | 65.8433 | 0.89633
| 25% | Liberty | Base | 341737 | 2LAUR CO IP | 69 | EKPC' | OPEN LINE FROM BUS 341348 [2COUNTRYFARM69.000] TO BUS 341929 [2N LONDON 69.000] CKT 1 | 0.93172 | 64.2886 | 0.89659
| 25% | Liberty | Base | 342346 | 2THREE LINKS | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.9551 | 65.9019 | 0.89771
| 25% | Liberty | Base | 341887 | 2MONTICELLO | 69 | EKPC' | OPEN LINE FROM BUS 341887 [2MONTICELLO 69.000] TO BUS 342268 [2SLAT 69.000] CKT 1 | 0.97567 | 67.3214 | 0.898
| 25% | Liberty | Base | 341470 | 2FLOYD EK | 69 | EKPC' | EKPC_P1-2_COP-LIBJ-PU161 | 0.94917 | 65.4925 | 0.89805
| 25% | Liberty | Base | 341115 | 2BIG HILL T | 69 | EKPC' | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342346 [2THREE LINKS69.000] CKT 1 | 0.95344 | 65.7875 | 0.89867
| 25% | Liberty | Base | 341641 | 2HOMESTEAD S | 69 | EKPC' | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 0.96978 | 66.915 | 0.8987

## N-1 Thermal
Scenario | Scaled | RICE | Alt | BRANCH | [6 empty] | CONTINGENCY | MVAFLOW | AMPFLOW | RATE RATE1/RATE2 | % FLOW | OWNER | Project % | Project
S2 | 20% | Campbellsville | CCAP | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 89.7281 | 89.7281 | 88 | 101.9637 | TIE | <100 % | Address KU limit
S2 | 20% | Campbellsville | CCAP | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 88.0944 | 88.0944 | 88 | 100.1073 | TIE | <100 % | Address KU limit
S2 | 20% | Campbellsville | W Garrard LibJ | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 89.5266 | 89.5266 | 88 | 101.7347 | TIE | <100 % | Address KU limit
S2 | 20% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 90.5672 | 90.5672 | 89 | 101.7609 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 20% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 90.546 | 90.546 | 89 | 101.7371 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 20% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 90.1445 | 90.1445 | 89 | 101.286 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 30% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 101.1783 | 101.1783 | 89 | 113.6835 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 30% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 101.1568 | 101.1568 | 89 | 113.6594 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 30% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 100.8037 | 100.8037 | 89 | 113.2626 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 30% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 94.1047 | 94.1048 | 88 | 106.9372 | TIE | <100 % | Address KU limit
S2 | 30% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 92.2002 | 92.2002 | 88 | 104.773 | TIE | <100 % | Address KU limit
S2 | 30% | Campbellsville | W Garrard | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -71.1343 | 71.1343 | 69 | 103.0932 | EKPC | <100 % | Invalid ratings in model
S2 | 30% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 90.5173 | 90.5173 | 88 | 102.8605 | TIE | <100 % | Address KU limit
S2 | 30% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 90.509 | 90.509 | 88 | 102.8512 | TIE | <100 % | Address KU limit
S2 | 30% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 89.9488 | 89.9488 | 89 | 101.066 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 20% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 89.9363 | 89.9363 | 88 | 102.2003 | TIE | <100 % | Address KU limit
S2 | 30% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 99.352 | 99.352 | 89 | 111.6315 | EKPC
S2 | 30% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 99.3299 | 99.3299 | 89 | 111.6066 | EKPC
S2 | 30% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 98.6757 | 98.6757 | 89 | 110.8716 | EKPC
S2 | 30% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 96.6108 | 96.6108 | 88 | 109.785 | TIE
S2 | 30% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 93.3334 | 93.3334 | 88 | 106.0607 | TIE
S2 | 30% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 91.6514 | 91.6514 | 88 | 104.1493 | TIE
S2 | 30% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 91.6426 | 91.6426 | 88 | 104.1394 | TIE
S2 | 30% | Campbellsville | McCreary | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -71.3154 | 71.3154 | 69 | 103.3556 | EKPC
S2 | 30% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 90.1713 | 90.1713 | 89 | 101.3161 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1 | -104.5172 | 104.5172 | 88 | 118.7696 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 104.2228 | 104.2228 | 89 | 117.1042 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 104.1996 | 104.1996 | 89 | 117.0782 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 103.8964 | 103.8964 | 89 | 116.7375 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 101.0565 | 101.0565 | 88 | 114.8369 | TIE
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | EKPC_P1-2_GREEN-CAMPBELV EK | -99.6006 | 99.6006 | 88 | 113.1825 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | -99.3953 | 99.3953 | 88 | 112.9492 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 98.564 | 98.564 | 88 | 112.0046 | TIE
S2-Fixes | 38% | Campbellsville | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 96.1892 | 96.1892 | 88 | 109.306 | TIE
S2-Fixes | 38% | Campbellsville | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 96.1814 | 96.1814 | 88 | 109.2971 | TIE
S2-Fixes | 38% | Campbellsville | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 96.895 | 96.895 | 89 | 108.8707 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -74.7731 | 74.7731 | 69 | 108.3668 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324829 | 2CAMPBELVIL1 | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1 | 86.6326 | 86.6326 | 80 | 108.2908 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324132 | 5ARTEMUS TAP | 161 | 324156 | 5PINEVILE SW | 161 | 1 | B-345-100 | -243.0956 | 243.0956 | 225 | 108.0425 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 93.5276 | 93.5276 | 88 | 106.2814 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | OPEN LINE FROM BUS 341563 [2GREEN CO 69.000] TO BUS 342733 [5GREEN CO 161.00] CKT 1 | -92.6852 | 92.6852 | 88 | 105.3241 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324751 | 2TAYLOR CO | 69 | 325921 | 5TAYLOR CO | 161 | 1 | OPEN LINE FROM BUS 342797 [5S MARION IT161.00] TO BUS 342798 [5S MARION IP161.00] CKT 1 | -128.3304 | 128.3304 | 122 | 105.1889 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324751 | 2TAYLOR CO | 69 | 325921 | 5TAYLOR CO | 161 | 1 | OPEN LINE FROM BUS 341999 [5RICE 161.00] TO BUS 342797 [5S MARION IT161.00] CKT 1 | -128.2569 | 128.2569 | 122 | 105.1286 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 92.4405 | 92.4405 | 88 | 105.046 | TIE
S2-Fixes | 38% | Campbellsville | Alcalde | 342796 | 5RUSSEL CO J | 161 | 360448 | 5WOLF CRK HP | 161 | 1 | B-345-100 | -345.8218 | 345.8218 | 334 | 103.5395 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324116 | 7W LEXINGTON | 345 | 324320 | 4W LEXINGTON | 138 | 1 | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | 605.3898 | 605.3899 | 585 | 103.4855 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | B-161-128 | 90.9861 | 90.9861 | 88 | 103.3933 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -135.1916 | 135.1916 | 131 | 103.1997 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324829 | 2CAMPBELVIL1 | 69 | 1 | EKPC_P1-2_GREEN-CAMPBELV EK | 81.8271 | 81.8271 | 80 | 102.2838 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | -133.7644 | 133.7644 | 131 | 102.1102 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324641 | 2MILE LAN TP | 69 | 324829 | 2CAMPBELVIL1 | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | 81.6213 | 81.6213 | 80 | 102.0266 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 342700 | 5BULLITT CO | 161 | 326975 | 5CEDAR GRV | 161 | 1 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | -377.6859 | 377.6859 | 371 | 101.8021 | TIE
S2-Fixes | 38% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -132.8448 | 132.8448 | 131 | 101.4083 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324662 | 2N LONDON KU | 69 | 324688 | 2PITTSBRG KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | -88.8768 | 88.8768 | 88 | 100.9963 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324662 | 2N LONDON KU | 69 | 324688 | 2PITTSBRG KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | -88.8681 | 88.8681 | 88 | 100.9865 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | EKPC_P1-2_COP-RUS-WLF161 | 132.2332 | 132.2332 | 131 | 100.9414 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 88.6644 | 88.6644 | 88 | 100.755 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 88.6568 | 88.6568 | 88 | 100.7464 | LGEE
S2-Fixes | 38% | Campbellsville | Alcalde | 342322 | 2SUMM SHADE | 69 | 342814 | 5SUMM SHADE | 161 | 1 | OPEN LINE FROM BUS 360607 [5S GLASGOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | -143.2334 | 143.2334 | 143 | 100.1632 | EKPC
S2-Fixes | 38% | Campbellsville | Alcalde | 324141 | 5ELIHU | 161 | 324514 | 2ELIHU | 69 | 2 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 126.1522 | 126.1522 | 126 | 100.1208 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 113.7399 | 113.7399 | 89 | 127.7976 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 113.7163 | 113.7163 | 89 | 127.7711 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 113.507 | 113.507 | 89 | 127.5359 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 103.2011 | 103.2011 | 89 | 115.9563 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -79.7832 | 79.7832 | 69 | 115.6278 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 100.8812 | 100.8812 | 88 | 114.6377 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 100.3068 | 100.3068 | 88 | 113.985 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1 | -99.7003 | 99.7003 | 88 | 113.2958 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 97.3526 | 97.3526 | 88 | 110.628 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -142.1523 | 142.1522 | 131 | 108.5132 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | EKPC_P1-2_GREEN-CAMPBELV EK | -94.4224 | 94.4224 | 88 | 107.2982 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324641 | 2MILE LAN TP | 69 | 324751 | 2TAYLOR CO | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 324830 [2CAMPBELV EK69.000] CKT 1 | -94.1906 | 94.1906 | 88 | 107.0348 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324132 | 5ARTEMUS TAP | 161 | 324156 | 5PINEVILE SW | 161 | 1 | B-345-100 | -240.5388 | 240.5388 | 225 | 106.9061 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324662 | 2N LONDON KU | 69 | 324688 | 2PITTSBRG KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | -93.8157 | 93.8157 | 88 | 106.6087 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324662 | 2N LONDON KU | 69 | 324688 | 2PITTSBRG KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | -93.811 | 93.811 | 88 | 106.6034 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -139.3089 | 139.3089 | 131 | 106.3426 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 342322 | 2SUMM SHADE | 69 | 342814 | 5SUMM SHADE | 161 | 1 | OPEN LINE FROM BUS 360607 [5S GLASGOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | -151.033 | 151.033 | 143 | 105.6175 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 92.8638 | 92.8638 | 88 | 105.527 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -137.6144 | 137.6144 | 131 | 105.0492 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 92.3159 | 92.3159 | 88 | 104.9044 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324141 | 5ELIHU | 161 | 324514 | 2ELIHU | 69 | 2 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 1 | 131.6524 | 131.6524 | 126 | 104.486 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324141 | 5ELIHU | 161 | 324514 | 2ELIHU | 69 | 1 | OPEN LINE FROM BUS 324141 [5ELIHU 161.00] TO BUS 324514 [2ELIHU 69.000] CKT 2 | 131.4661 | 131.4661 | 126 | 104.3382 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 91.6802 | 91.6802 | 88 | 104.1821 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 91.6734 | 91.6734 | 88 | 104.1743 | TIE
S2 | 25% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 95.0887 | 95.0887 | 89 | 106.8412 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 25% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 95.0669 | 95.0669 | 89 | 106.8167 | EKPC | <100 % | Address CT and Disconnect Switch
S2 | 25% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 94.8283 | 94.8283 | 89 | 106.5487 | EKPC | <100 % | Address CT and Disconnect Switch
S2-Fixes | 45% | Liberty | Alcalde | 324116 | 7W LEXINGTON | 345 | 324320 | 4W LEXINGTON | 138 | 1 | OPEN LINE FROM BUS 324102 [7BROWN NORTH345.00] TO BUS 324116 [7W LEXINGTON345.00] CKT 1 | 609.2333 | 609.2333 | 585 | 104.1424 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 342700 | 5BULLITT CO | 161 | 326975 | 5CEDAR GRV | 161 | 1 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | -386.2631 | 386.2631 | 371 | 104.114 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 342268 | 2SLAT | 69 | 342478 | 2WAYNE CO | 69 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -100.9388 | 100.9388 | 97 | 104.0606 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | -135.9207 | 135.9206 | 131 | 103.7562 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 89.0699 | 89.0699 | 86 | 103.5697 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -138.4763 | 138.4763 | 134 | 103.3405 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | -138.4556 | 138.4556 | 134 | 103.3251 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341929 | 2N LONDON | 69 | 324662 | 2N LONDON KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 98.0139 | 98.0139 | 95 | 103.1725 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 341929 | 2N LONDON | 69 | 324662 | 2N LONDON KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 98.0114 | 98.0114 | 95 | 103.1699 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | -138.007 | 138.007 | 134 | 102.9903 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | EKPC_P1-2_COP-RUS-WLF161 | -134.404 | 134.404 | 131 | 102.5985 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 324554 | 2GRENSBRG KU | 69 | 324830 | 2CAMPBELV EK | 69 | 1 | B-161-128 | 89.3917 | 89.3917 | 88 | 101.5815 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 324641 | 2MILE LAN TP | 69 | 324829 | 2CAMPBELVIL1 | 69 | 1 | OPEN LINE FROM BUS 324554 [2GRENSBRG KU69.000] TO BUS 341563 [2GREEN CO 69.000] CKT 1 | 80.4474 | 80.4474 | 80 | 100.5593 | LGEE
S2-Fixes | 45% | Liberty | Alcalde | 341344 | 2COOPER | 69 | 342286 | 2SOMERSET | 69 | 1 | B-69-25 | 89.4109 | 89.4109 | 89 | 100.4617 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341344 | 2COOPER | 69 | 342286 | 2SOMERSET | 69 | 2 | B-69-25 | 89.4109 | 89.4109 | 89 | 100.4617 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | 341929 | 2N LONDON | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | -86.1094 | 86.1094 | 86 | 100.1272 | EKPC
S2-Fixes | 45% | Liberty | Alcalde | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 342733 [5GREEN CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 88.1112 | 88.1112 | 88 | 100.1264 | TIE
S2-Fixes | 45% | Liberty | Alcalde | 341348 | 2COUNTRYFARM | 69 | 341929 | 2N LONDON | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | -86.0816 | 86.0815 | 86 | 100.0948 | EKPC
S2-Fixes | 19% | Campbellsville | CCAP | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 88.9653 | 88.9653 | 88 | 101.0969 | TIE
S2-Fixes | 37% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 103.7982 | 103.7982 | 89 | 116.6272 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 103.7755 | 103.7755 | 89 | 116.6017 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 103.537 | 103.537 | 89 | 116.3337 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 95.9723 | 95.9723 | 88 | 109.0594 | TIE
S2-Fixes | 37% | Liberty | CCAP | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 95.058 | 95.058 | 88 | 108.0204 | TIE
S2-Fixes | 37% | Liberty | CCAP | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 95.6913 | 95.6913 | 89 | 107.5183 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -74.1408 | 74.1408 | 69 | 107.4504 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 92.64 | 92.64 | 88 | 105.2727 | TIE
S2-Fixes | 37% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | 137.6744 | 137.6745 | 131 | 105.095 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | 136.0438 | 136.0438 | 131 | 103.8502 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 342322 | 2SUMM SHADE | 69 | 342814 | 5SUMM SHADE | 161 | 1 | OPEN LINE FROM BUS 360607 [5S GLASGOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | -148.1176 | 148.1176 | 143 | 103.5787 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | EKPC_P1-2_COP-RUS-WLF161 | 135.569 | 135.569 | 131 | 103.4878 | EKPC
S2-Fixes | 37% | Liberty | CCAP | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -132.3414 | 132.3414 | 131 | 101.0239 | EKPC
S2-Fixes | 29% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 95.7236 | 95.7236 | 88 | 108.7769 | TIE
S2-Fixes | 29% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 94.475 | 94.475 | 89 | 106.1517 | EKPC
S2-Fixes | 29% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 94.4526 | 94.4526 | 89 | 106.1265 | EKPC
S2-Fixes | 29% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 93.6445 | 93.6445 | 89 | 105.2186 | EKPC
S2-Fixes | 29% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 92.306 | 92.306 | 88 | 104.8932 | TIE
S2-Fixes | 29% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 90.8458 | 90.8458 | 88 | 103.2339 | TIE
S2-Fixes | 29% | Campbellsville | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 90.8377 | 90.8377 | 88 | 103.2246 | TIE
S2-Fixes | 29% | Campbellsville | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 89.2185 | 89.2185 | 89 | 100.2455 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 105.1701 | 105.1701 | 89 | 118.1687 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 105.1479 | 105.1479 | 89 | 118.1437 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 104.4775 | 104.4775 | 89 | 117.3904 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 96.1235 | 96.1235 | 88 | 109.2312 | TIE
S2-Fixes | 38% | Liberty | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 95.9323 | 95.9323 | 88 | 109.014 | TIE
S2-Fixes | 38% | Liberty | McCreary | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 96.9719 | 96.9719 | 89 | 108.9572 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -74.8784 | 74.8784 | 69 | 108.5195 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 92.6345 | 92.6345 | 88 | 105.2665 | TIE
S2-Fixes | 38% | Liberty | McCreary | 342322 | 2SUMM SHADE | 69 | 342814 | 5SUMM SHADE | 161 | 1 | OPEN LINE FROM BUS 360607 [5S GLASGOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | -148.6435 | 148.6435 | 143 | 103.9465 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -133.4494 | 133.4494 | 131 | 101.8698 | EKPC
S2-Fixes | 38% | Liberty | McCreary | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -132.1021 | 132.1021 | 131 | 100.8413 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 105.1899 | 105.1899 | 89 | 118.1909 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 105.1674 | 105.1674 | 89 | 118.1657 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 104.8059 | 104.8059 | 89 | 117.7595 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 99.8632 | 99.8632 | 88 | 113.4809 | TIE
S2-Fixes | 38% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 97.6001 | 97.6002 | 88 | 110.9093 | TIE
S2-Fixes | 38% | Campbellsville | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 96.6555 | 96.6555 | 89 | 108.6017 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 95.4679 | 95.4679 | 88 | 108.4863 | TIE
S2-Fixes | 38% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 95.4591 | 95.4591 | 88 | 108.4762 | TIE
S2-Fixes | 38% | Campbellsville | W Garrard | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -74.5944 | 74.5944 | 69 | 108.1078 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 91.594 | 91.594 | 88 | 104.0841 | TIE
S2-Fixes | 38% | Campbellsville | W Garrard | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -133.2455 | 133.2455 | 131 | 101.7142 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 342700 | 5BULLITT CO | 161 | 326975 | 5CEDAR GRV | 161 | 1 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | -375.9274 | 375.9274 | 371 | 101.3281 | TIE
S2-Fixes | 38% | Campbellsville | W Garrard | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -132.644 | 132.644 | 131 | 101.255 | EKPC
S2-Fixes | 38% | Campbellsville | W Garrard | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | -134.0491 | 134.0491 | 134 | 100.0366 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 114.4603 | 114.4603 | 89 | 128.6071 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 114.4368 | 114.4368 | 89 | 128.5806 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 114.1789 | 114.1789 | 89 | 128.2909 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342268 [2SLAT 69.000] TO BUS 342478 [2WAYNE CO 69.000] CKT 1 | 102.9245 | 102.9245 | 89 | 115.6455 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341848 | 2MCKEE | 69 | 342391 | 2TYNER | 69 | 1 | OPEN LINE FROM BUS 341341 [2CONWAY T 69.000] TO BUS 342349 [2THREE LNK J69.000] CKT 1 | -79.5649 | 79.5649 | 69 | 115.3115 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | EKPC_P1-2_GRE-TAY-AF1-083161 | 100.0726 | 100.0726 | 88 | 113.7189 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 99.2541 | 99.2541 | 88 | 112.7888 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | B-161-128 | 96.5729 | 96.5729 | 88 | 109.7419 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -142.602 | 142.602 | 131 | 108.8565 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | OPEN LINE FROM BUS 342787 [5PULASK CO 161.00] TO BUS 342790 [5PULASK CO J161.00] CKT 1 | -141.388 | 141.388 | 134 | 105.5134 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | OPEN LINE FROM BUS 342115 [2PULASK CO 69.000] TO BUS 342787 [5PULASK CO 161.00] CKT 1 | -141.3667 | 141.3667 | 134 | 105.4975 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 341503 [2GAP OF RG T69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -138.0626 | 138.0626 | 131 | 105.3913 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341233 | 2CABIN HOLLW | 69 | 342286 | 2SOMERSET | 69 | 1 | EKPC_P1-2_COP-LIBJ-PU161 | -141.1341 | 141.1341 | 134 | 105.324 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 342322 | 2SUMM SHADE | 69 | 342814 | 5SUMM SHADE | 161 | 1 | OPEN LINE FROM BUS 360607 [5S GLASGOW 161.00] TO BUS 361603 [5E GLASGOW T161.00] CKT 1 | -149.9436 | 149.9436 | 143 | 104.8557 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341929 | 2N LONDON | 69 | 324662 | 2N LONDON KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | 99.2809 | 99.2809 | 95 | 104.5062 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 341929 | 2N LONDON | 69 | 324662 | 2N LONDON KU | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | 99.2772 | 99.2772 | 95 | 104.5024 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342283 [2SNOW T 69.000] TO BUS 342322 [2SUMM SHADE 69.000] CKT 1 | -136.7998 | 136.7998 | 131 | 104.4273 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 342268 | 2SLAT | 69 | 342478 | 2WAYNE CO | 69 | 1 | OPEN LINE FROM BUS 341392 [2DENNY 69.000] TO BUS 341578 [2GREGORY R T69.000] CKT 1 | -100.8337 | 100.8337 | 97 | 103.9522 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 342700 | 5BULLITT CO | 161 | 326975 | 5CEDAR GRV | 161 | 1 | OPEN LINE FROM BUS 324106 [7HARDIN CO 345.00] TO BUS 325073 [7REDMON RD 345.00] CKT 1 | -384.0141 | 384.0141 | 371 | 103.5079 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 325921 [5TAYLOR CO 161.00] TO BUS 342817 [5TAYLOR CO J161.00] CKT 1 | 91.0203 | 91.0203 | 88 | 103.4321 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324751 [2TAYLOR CO 69.000] TO BUS 325921 [5TAYLOR CO 161.00] CKT 1 | 91.0134 | 91.0134 | 88 | 103.4243 | TIE
S2-Fixes | 45% | Liberty | W Garrard | 341761 | 2LIBERTY J | 69 | 341896 | 2MT OLIVE J | 69 | 1 | OPEN LINE FROM BUS 342205 [2S LANCASTER69.000] TO BUS 342367 [2TOMM GOOC T69.000] CKT 1 | 88.8822 | 88.8822 | 86 | 103.3514 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341761 | 2LIBERTY J | 69 | 342760 | 5LIBERTY J | 161 | 1 | EKPC_P1-2_SOUTH CASEY-CAS-MAR161 | 132.6605 | 132.6605 | 129 | 102.8376 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341344 | 2COOPER | 69 | 342286 | 2SOMERSET | 69 | 1 | B-69-25 | 90.0449 | 90.0449 | 89 | 101.1741 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341344 | 2COOPER | 69 | 342286 | 2SOMERSET | 69 | 2 | B-69-25 | 90.0449 | 90.0449 | 89 | 101.1741 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 342478 | 2WAYNE CO | 69 | 342823 | 5WAYNE CO | 161 | 1 | OPEN LINE FROM BUS 342796 [5RUSSEL CO J161.00] TO BUS 360448 [5WOLF CRK HP161.00] CKT 1 | -132.1575 | 132.1575 | 131 | 100.8836 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341348 | 2COUNTRYFARM | 69 | 341929 | 2N LONDON | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 342073 [2PINE GRV T 69.000] CKT 1 | -86.0474 | 86.0474 | 86 | 100.0551 | EKPC
S2-Fixes | 45% | Liberty | W Garrard | 341348 | 2COUNTRYFARM | 69 | 341929 | 2N LONDON | 69 | 1 | OPEN LINE FROM BUS 341719 [2KEAVY 1 T 69.000] TO BUS 341740 [2LAUREL CO 69.000] CKT 1 | -86.0193 | 86.0193 | 86 | 100.0225 | EKPC
S2-Fixes | 20% | Campbellsville | W Garrard LibJ | 341563 | 2GREEN CO | 69 | 324554 | 2GRENSBRG KU | 69 | 1 | OPEN LINE FROM BUS 324641 [2MILE LAN TP69.000] TO BUS 324751 [2TAYLOR CO 69.000] CKT 1 | 89.4904 | 89.4904 | 88 | 101.6936 | TIE
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342823 [5WAYNE CO 161.00] TO BUS 360486 [5WAYNE CO KY161.00] CKT 1 | 92.0014 | 92.0014 | 89 | 103.3724 | EKPC
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | OPEN LINE FROM BUS 342478 [2WAYNE CO 69.000] TO BUS 342823 [5WAYNE CO 161.00] CKT 1 | 91.98 | 91.98 | 89 | 103.3483 | EKPC
S2-Fixes | 25% | Liberty | W Garrard LibJ | 341392 | 2DENNY | 69 | 341578 | 2GREGORY R T | 69 | 1 | EKPC_P1-2_MCCR-WAYNE161 | 91.6398 | 91.6398 | 89 | 102.9661 | EKPC

## N-1-1 Voltage
Scenario | Scaled | RICE | Alt | First Level Scenario | Bus # | Bus Name | Base kV | Area | Bus Type | Pload | Cont Name | Orig Case Cont Volt | Base Volt | Cont Volt | %Vdrop | Scaled Volt | Scaled % | Base EKPC Load | Scaled EKPC Load | Total EKPC Added
S1 | 20% | Campbellsivlle | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9678 | 0.9931 | 0.9161 | 7.703 | 0.9474 | 15
S1 | 20% | Campbellsivlle | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9678 | 0.9932 | 0.9161 | 7.706 | 0.9474 | 15
S1 | 20% | Campbellsivlle | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9678 | 0.9931 | 0.9161 | 7.703 | 0.9223 | 20
S1 | 20% | Campbellsivlle | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9678 | 0.9932 | 0.9161 | 7.706 | 0.9223 | 20
S1 | 20% | Campbellsivlle | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9678 | 0.9931 | 0.9161 | 7.703 | 0.9284 | 19 | 906.6878 | 1077.9695 | 171.2817
S1 | 20% | Campbellsivlle | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9678 | 0.9932 | 0.9161 | 7.706 | 0.9284 | 19
S1 | 20% | Campbellsivlle | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9646 | 0.9855 | 0.9247 | 6.082 | 0.9274 | 20 | 906.6878 | 1086.9894 | 180.3016
S1 | 20% | Campbellsivlle | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9646 | 0.9855 | 0.9247 | 6.081 | 0.9274 | 20
S1 | 20% | Campbellsivlle | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9646 | 0.9855 | 0.9247 | 6.082 | 0.9223 | 22
S1 | 20% | Campbellsivlle | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9646 | 0.9855 | 0.9247 | 6.081 | 0.9223 | 22
S1 | 20% | Campbellsivlle | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9646 | 0.9855 | 0.9247 | 6.082 | 0.9247 | 21
S1 | 20% | Campbellsivlle | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9646 | 0.9855 | 0.9247 | 6.081 | 0.9247 | 21
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9598 | 0.9597 | 0.9255 | 3.42 | 0.9458 | 30
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9648 | 0.9629 | 0.9271 | 3.577 | 0.94735 | 30
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342831 | 7COOPER | 345 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9845 | 0.9821 | 0.9359 | 4.629 | 0.95252 | 30
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.9359 | 4.524 | 0.95262 | 30
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.936 | 4.523 | 0.95262 | 30
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9598 | 0.9597 | 0.9255 | 3.42 | 0.9353 | 35
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9648 | 0.9629 | 0.9271 | 3.577 | 0.9368 | 35
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342831 | 7COOPER | 345 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9845 | 0.9821 | 0.9359 | 4.629 | 0.9435 | 35
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.9359 | 4.524 | 0.9436 | 35
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.936 | 4.523 | 0.9436 | 35
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9598 | 0.9597 | 0.9255 | 3.42 | 0.9255 | 38 | 906.6878 | 1249.2525 | 342.5647
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9648 | 0.9629 | 0.9271 | 3.577 | 0.9266 | 38
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342831 | 7COOPER | 345 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9845 | 0.9821 | 0.9359 | 4.629 | 0.9334 | 38
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.9359 | 4.524 | 0.9335 | 38
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.936 | 4.523 | 0.9335 | 38
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9598 | 0.9597 | 0.9255 | 3.42 | 0.9221 | 39
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9648 | 0.9629 | 0.9271 | 3.577 | 0.9231 | 39
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342831 | 7COOPER | 345 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9845 | 0.9821 | 0.9359 | 4.629 | 0.9298 | 39
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.9359 | 4.524 | 0.9299 | 39
S1 | 30% | Campbellsivlle | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9846 | 0.9812 | 0.936 | 4.523 | 0.9299 | 39
S1 | 20% | Campbellsivlle | McCreary | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9613 | 0.9837 | 0.9346 | 4.906 | 0.944 | 20
S1 | 20% | Campbellsivlle | McCreary | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9613 | 0.9837 | 0.9346 | 4.906 | 0.944 | 20
S1 | 30% | Campbellsivlle | McCreary | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9489 | 0.9769 | 0.9135 | 6.344 | 0.9232 | 30
S1 | 30% | Campbellsivlle | McCreary | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9489 | 0.9769 | 0.9135 | 6.344 | 0.9232 | 30
S1 | 30% | Campbellsivlle | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9601 | 0.9461 | 0.9136 | 3.249 | 0.9355 | 30
S1 | 30% | Campbellsivlle | McCreary | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9489 | 0.9769 | 0.9135 | 6.344 | 0.9263 | 29 | 906.6878 | 1168.1548 | 261.467
S1 | 30% | Campbellsivlle | McCreary | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9489 | 0.9769 | 0.9135 | 6.344 | 0.9263 | 29
S1 | 30% | Campbellsivlle | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9601 | 0.9461 | 0.9136 | 3.249 | 0.9384 | 29
S1 | 30% | Campbellsivlle | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9628 | 0.9605 | 0.9261 | 3.436 | 0.9458 | 30
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9643 | 0.9676 | 0.9272 | 4.037 | 0.9474 | 30
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342831 | 7COOPER | 345 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9865 | 0.9865 | 0.9359 | 5.065 | 0.95256 | 30
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9841 | 0.9866 | 0.936 | 5.065 | 0.95266 | 30
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9841 | 0.9866 | 0.936 | 5.065 | 0.95266 | 30
S1 | 30% | Campbellsivlle | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9628 | 0.9605 | 0.9261 | 3.436 | 0.9255 | 38 | 906.6878 | 1249.2525 | 342.5647
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9643 | 0.9676 | 0.9272 | 4.037 | 0.9266 | 38
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342831 | 7COOPER | 345 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9865 | 0.9865 | 0.9359 | 5.065 | 0.9334 | 38
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9841 | 0.9866 | 0.936 | 5.065 | 0.9335 | 38
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9841 | 0.9866 | 0.936 | 5.065 | 0.9335 | 38
S1 | 30% | Campbellsivlle | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9628 | 0.9605 | 0.9261 | 3.436 | 0.9221 | 39
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9643 | 0.9676 | 0.9272 | 4.037 | 0.9231 | 39
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342831 | 7COOPER | 345 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9865 | 0.9865 | 0.9359 | 5.065 | 0.9298 | 39
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9841 | 0.9866 | 0.936 | 5.065 | 0.9299 | 39
S1 | 30% | Campbellsivlle | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9841 | 0.9866 | 0.936 | 5.065 | 0.9299 | 39
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9531 | 0.9505 | 0.9193 | 3.117 | 0.9317 | 40
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9509 | 0.9529 | 0.9193 | 3.362 | 0.9317 | 40
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9587 | 0.9551 | 0.9228 | 3.235 | 0.934 | 40
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9555 | 0.9586 | 0.9228 | 3.584 | 0.934 | 40
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9531 | 0.9505 | 0.9193 | 3.117 | 0.9301 | 42
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9509 | 0.9529 | 0.9193 | 3.362 | 0.9301 | 42
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9587 | 0.9551 | 0.9228 | 3.235 | 0.9327 | 42
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9555 | 0.9586 | 0.9228 | 3.584 | 0.9327 | 42
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9531 | 0.9505 | 0.9193 | 3.117 | 0.926 | 45 | 906.6878 | 1312.3824 | 405.6946
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9509 | 0.9529 | 0.9193 | 3.362 | 0.926 | 45
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9587 | 0.9551 | 0.9228 | 3.235 | 0.9284 | 45
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9555 | 0.9586 | 0.9228 | 3.584 | 0.9284 | 45
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9531 | 0.9505 | 0.9193 | 3.117 | 0.9238 | 46
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9509 | 0.9529 | 0.9193 | 3.362 | 0.9238 | 46
S1 | 40% | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9587 | 0.9551 | 0.9228 | 3.235 | 0.9261 | 46
S1 | 40% | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9555 | 0.9586 | 0.9228 | 3.584 | 0.9261 | 46
S1-fixes |  | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9586 | 0.9561 | 0.9233 | 3.275 | 0.926 | 45 | 906.6878 | 1312.3824 | 405.6946
S1-fixes |  | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-3_COOPER 345/161_SRT-A | 0.9591 | 0.9561 | 0.9238 | 3.231 |  | 45
S1-fixes |  | Liberty | Alcalde | EKPC_P1-3_COOPER 345/161_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9562 | 0.9589 | 0.9242 | 3.472 |  | 45
S1-fixes |  | Liberty | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9562 | 0.9585 | 0.9251 | 3.339 | 0.9262 | 45 | 906.6878 | 1312.3824 | 405.6946
S1-fixes |  | Liberty | Alcalde | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 0.9631 | 0.9595 | 0.9255 | 3.395 | 0.9284 | 45
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9847 | 0.893 | 9.174 | 0.9143 | 40
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9848 | 0.893 | 9.176 | 0.9143 | 40
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9847 | 0.893 | 9.174 | 0.9206 | 38
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9848 | 0.893 | 9.176 | 0.9206 | 38
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9847 | 0.893 | 9.174 | 0.93 | 36
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9848 | 0.893 | 9.176 | 0.93 | 36
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9847 | 0.893 | 9.174 | 0.926 | 37 | 906.6878 | 1240.2335 | 333.5457
S1 | 40% | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9561 | 0.9848 | 0.893 | 9.176 | 0.926 | 37
S1-fixes |  | Liberty | CCAP | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9671 | 0.9502 | 0.9176 | 3.26 | 0.9268 | 34 | 906.6878 | 1213.1775 | 306.4897
S1-fixes |  | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9505 | 0.9702 | 0.9181 | 5.206 | 0.9279 | 32 | 906.6878 | 1195.1402 | 288.4524
S1-fixes |  | Liberty | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9505 | 0.967 | 0.9182 | 4.88 | 0.9268 | 34
S1-fixes |  | Liberty | CCAP | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9548 | 0.9755 | 0.9191 | 5.646 | 0.9298 | 32
S1-fixes |  | Liberty | CCAP | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9757 | 0.9546 | 0.9196 | 3.503 | 0.9298 | 32
S1-fixes |  | Liberty | CCAP | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 0.9718 | 0.9546 | 0.9198 | 3.477 | 0.929 | 34
S1-fixes |  | Liberty | CCAP | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9548 | 0.9717 | 0.9203 | 5.146 | 0.929 | 34
S1 | 40% | Liberty | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9516 | 0.9311 | 0.902 | 2.901 | 0.92 | 40
S1 | 40% | Liberty | McCreary | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9313 | 0.9513 | 0.9021 | 4.918 | 0.92 | 40
S1 | 40% | Liberty | McCreary | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9759 | 0.9512 | 0.9077 | 4.344 | 0.9258 | 40
S1 | 40% | Liberty | McCreary | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9759 | 0.9512 | 0.9077 | 4.344 | 0.9258 | 40
S1 | 40% | Liberty | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9516 | 0.9311 | 0.902 | 2.901 | 0.923 | 39
S1 | 40% | Liberty | McCreary | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9313 | 0.9513 | 0.9021 | 4.918 | 0.932 | 39
S1 | 40% | Liberty | McCreary | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9759 | 0.9512 | 0.9077 | 4.344 | 0.9292 | 39
S1 | 40% | Liberty | McCreary | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9759 | 0.9512 | 0.9077 | 4.344 | 0.9292 | 39
S1 | 40% | Liberty | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9462 | 0.9273 | 0.9016 | 2.577 | 0.9253 | 38
S1 | 40% | Liberty | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9516 | 0.9311 | 0.902 | 2.901 | 0.9259 | 38 | 906.6878 | 1249.2525 | 342.5647
S1 | 40% | Liberty | McCreary | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9313 | 0.9513 | 0.9021 | 4.918 | 0.9259 | 38
S1 | 40% | Liberty | McCreary | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9759 | 0.9512 | 0.9077 | 4.344 | 0.9322 | 38
S1 | 40% | Liberty | McCreary | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9759 | 0.9512 | 0.9077 | 4.344 | 0.9322 | 38
S1-fixes |  | Liberty | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.964 | 0.947 | 0.9237 | 2.328 | 0.9253 | 38 | 906.6878 | 1249.2525 | 342.5647
S1-fixes |  | Liberty | McCreary | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9471 | 0.9639 | 0.9238 | 4.005 | 0.9253 | 38
S1-fixes |  | Liberty | McCreary | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9683 | 0.9498 | 0.9245 | 2.529 | 0.9285 | 38
S1-fixes |  | Liberty | McCreary | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9499 | 0.9681 | 0.9246 | 4.356 | 0.9285 | 38
S1 | 40% | Liberty | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.953 | 0.9527 | 0.9193 | 3.334 | 0.9317 | 40
S1 | 40% | Liberty | W Garrard | EKPC_P1-2_COOPER-WGARR345_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9529 | 0.9529 | 0.9193 | 3.362 | 0.9317 | 40
S1 | 40% | Liberty | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9587 | 0.9566 | 0.9228 | 3.381 | 0.934 | 40
S1 | 40% | Liberty | W Garrard | EKPC_P1-2_COOPER-WGARR345_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9568 | 0.9586 | 0.9228 | 3.584 | 0.934 | 40
S1 | 40% | Liberty | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.953 | 0.9527 | 0.9193 | 3.334 | 0.926 | 45 | 906.6878 | 1312.3824 | 405.6946
S1 | 40% | Liberty | W Garrard | EKPC_P1-2_COOPER-WGARR345_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9529 | 0.9529 | 0.9193 | 3.362 | 0.926 | 45
S1 | 40% | Liberty | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9587 | 0.9566 | 0.9228 | 3.381 | 0.9284 | 45
S1 | 40% | Liberty | W Garrard | EKPC_P1-2_COOPER-WGARR345_SRT-A | 342754 | 5LAUREL CO | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9568 | 0.9586 | 0.9228 | 3.584 | 0.9284 | 45
S1-fixes |  | Liberty | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 0.9586 | 0.9582 | 0.9234 | 3.488 | 0.926 | 45
S1-fixes |  | Liberty | W Garrard | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EKPC_P1-3_COOPER 345/161_SRT-A | 0.9608 | 0.9582 | 0.9246 | 3.362 |  | 45
S1-fixes |  | Liberty | W Garrard | EKPC_P1-3_COOPER 345/161_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9585 | 0.9606 | 0.9246 | 3.599 |  | 45
S1-fixes |  | Liberty | W Garrard | EKPC_P1-2_COOPER-WGARR345_SRT-A | 342783 | 5PITTSBURG | 161 | 320 | Load | 0 | EXT_324100 7ALCALDE 345 324130 5ALCALDE 161 1 _SRT-S | 0.9585 | 0.9585 | 0.9251 | 3.338 | 0.926 | 45
S1 | 25% | Liberty | W Garrard LibJ | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9745 | 0.9552 | 0.914 | 4.119 | 0.9258 | 25 | 906.6878 | 1132.0809 | 225.3931
S1 | 25% | Liberty | W Garrard LibJ | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9745 | 0.9552 | 0.914 | 4.118 | 0.9258 | 25
S1-fixes |  | Liberty | W Garrard LibJ | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9615 | 0.9824 | 0.9209 | 6.153 | 0.9258 | 25 | 906.6878 | 1132.0809 | 225.3931
S1-fixes |  | Liberty | W Garrard LibJ | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9615 | 0.9824 | 0.9209 | 6.153 | 0.9258 | 25
S1-fixes |  | Liberty | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9615 | 0.979 | 0.925 | 5.395 | 0.9315 | 25
S1-fixes |  | Liberty | W Garrard LibJ | EKPC_P1-2_COP-RUS-WLF161_SRT-A | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 0.9615 | 0.979 | 0.9251 | 5.395 | 0.9315 | 25
S1-fixes |  | Liberty | W Garrard LibJ | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342715 | 5COOPER1 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9824 | 0.9615 | 0.9259 | 3.556 | 0.9258 | 25
S1-fixes |  | Liberty | W Garrard LibJ | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342718 | 5COOPER2 | 161 | 320 | Load | 0 | EKPC_P1-2_COP-LIBJ-PU161_SRT-A | 0.9824 | 0.9615 | 0.9259 | 3.557 | 0.9258 | 25

## N-1-1 Thermal
Scenario | Scaled | RICE | Alt | First Level Scenario | Monitored Facility | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Base Flow (MVA) | Cont Flow (MVA) | Orig Case Cont AC %Loading | Final AC %Loading | Scaled % | Scaled Flow | Project % | Project
S1 | 20% | Campbellsville | CCAP | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | EKPC_P1-2_LIB-CAS-MAR161_SRT-A | 314.3 | 369.6 | 75.31 | 110.67 | 19 | 367.7 | <100 % | Address KU limit
S1 | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 173.2 | 305.7 | 63.14 | 110.75
S1 | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 174.2 | 305.6 | 62.73 | 110.73
S1 | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 165.5 | 294.3 | 60.31 | 106.62
S1 | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 166.4 | 294.2 | 59.94 | 106.6
S1 | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 310.4 | 430.4 | 73.92 | 100.1
S1 | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 317.9 | 430.4 | 72.18 | 100.1
S1 | 30% | Campbellsville | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 174.5 | 307.6 | 63.53 | 111.45
S1 | 30% | Campbellsville | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 175.3 | 307.6 | 63.23 | 111.44
S1 | 30% | Campbellsville | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 166.8 | 296 | 60.69 | 107.25
S1 | 30% | Campbellsville | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 167.5 | 296 | 60.42 | 107.24
S1 | 30% | Campbellsville | W Garrard | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | Base Case | 359.2 | - | 91.31 | 106.91
S1 | 30% | Campbellsville | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 312 | 432.8 | 74.24 | 100.66
S1 | 30% | Campbellsville | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 319.2 | 432.8 | 72.55 | 100.66
S1-fixes | 12% | Campbellsville | Base | EKPC_P1-2_LIB-CAS-MAR161_SRT-A | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 242 | 353.3 | 89.34 | 105.77
S1-fixes | 19% | Campbellsville | CCAP | EKPC_P1-2_LIB-CAS-MAR161_SRT-A | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 249.5 | 368.2 | 93.74 | 110.25
S1-fixes | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 173.2 | 305.6 | 63.14 | 110.74
S1-fixes | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 165.5 | 294.2 | 60.31 | 106.61
S1-fixes | 20% | Campbellsville | W Garrard LibJ | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | Base Case | 352.4 | - | 89.63 | 104.89
S1-fixes | 20% | Campbellsville | W Garrard LibJ | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 310.4 | 430.4 | 73.92 | 100.08
S1-fixes | 38% | Campbellsville | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 177.5 | 311.8 | 64.63 | 112.96
S1-fixes | 38% | Campbellsville | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 169.6 | 299.9 | 61.75 | 108.65
S1-fixes | 38% | Campbellsville | W Garrard | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | Base Case | 363.7 | - | 92.44 | 108.24
S1-fixes | 38% | Campbellsville | W Garrard | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | EKPC_P1-2_COOPER-WGARR345_SRT-A | 227.4 | 347 | 74.44 | 103.9
S1-fixes | 38% | Campbellsville | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 313.4 | 435.6 | 74.6 | 101.31
S1-fixes | 38% | Campbellsville | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 181.9 | 320.2 | 66.37 | 116
S1-fixes | 38% | Campbellsville | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 173.9 | 307.8 | 63.43 | 111.53
S1-fixes | 38% | Campbellsville | Alcalde | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | Base Case | 365.5 | - | 93.11 | 108.79
S1-fixes | 38% | Campbellsville | Alcalde | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 230.7 | 347.5 | 74.24 | 104.04
S1-fixes | 38% | Campbellsville | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 321 | 447.1 | 76.48 | 103.98
S1-fixes | 38% | Campbellsville | Alcalde | EKPC_P1-2_COOPER-ALCALDE_SRT-A | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 247.9 | 346.9 | 69.11 | 103.87
S1-fixes | 38% | Campbellsville | Alcalde | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 342577 4FAWKES EK 138 342607 4JK SMITH 138 1 | 138 | 320 | 362 | 387 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 270 | 395.2 | 76.4 | 102.11
S1-fixes | 38% | Campbellsville | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342607 4JK SMITH 138 342688 4UNION CTY T 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 341.1 | 435.6 | 75.69 | 101.3
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 183.8 | 322.7 | 67.08 | 116.92
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 185.1 | 322.7 | 66.6 | 116.9
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 175.7 | 310.2 | 64.09 | 112.38
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 176.9 | 310.1 | 63.65 | 112.36
S1-fixes | 45% | Liberty | Alcalde | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | Base Case | 373.3 | - | 95.31 | 111.11
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 322.3 | 448.8 | 76.81 | 104.37
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 330.3 | 448.8 | 74.96 | 104.37
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_SPUR-NCLA345_SRT-A | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 327.4 | 383.6 | 100.4 | 103.38
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342607 4JK SMITH 138 1 | 138 | 320 | 362 | 387 | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 297.7 | 397.2 | 70.17 | 102.65
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 342577 4FAWKES EK 138 342607 4JK SMITH 138 1 | 138 | 320 | 362 | 387 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 271.5 | 397.2 | 76.93 | 102.64
S1-fixes | 45% | Liberty | Alcalde | P2E1_360354-361265-1_SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 327.9 | 380.3 | 100.4 | 102.5
S1-fixes | 45% | Liberty | Alcalde | P1E2_L5110_SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 327.7 | 380.1 | 100.4 | 102.46
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342607 4JK SMITH 138 342688 4UNION CTY T 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 343.4 | 437.8 | 76.11 | 101.82
S1-fixes | 45% | Liberty | Alcalde | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 342607 4JK SMITH 138 342688 4UNION CTY T 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 327.3 | 437.8 | 79.84 | 101.82
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 179.4 | 314.5 | 65.33 | 113.95
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 180.3 | 314.5 | 64.98 | 113.94
S1-fixes | 45% | Liberty | W Garrard | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | Base Case | 371.5 | - | 94.62 | 110.55
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 171.4 | 302.4 | 62.41 | 109.56
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 172.2 | 302.3 | 62.09 | 109.55
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_SPUR-NCLA345_SRT-A | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 325.8 | 382.7 | 99.88 | 103.16
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 314.9 | 437.8 | 74.97 | 101.8
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 322.4 | 437.8 | 73.24 | 101.8
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342607 4JK SMITH 138 1 | 138 | 320 | 362 | 387 | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 290.1 | 387 | 68.53 | 100
S1-fixes | 45% | Liberty | W Garrard | EKPC_P1-2_HUNT-JKSM 138_SRT-A | 342577 4FAWKES EK 138 342607 4JK SMITH 138 1 | 138 | 320 | 362 | 387 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 265.2 | 387 | 74.97 | 100
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 175.6 | 309.6 | 64.05 | 112.19
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342574 4DALE 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 176.7 | 309.6 | 63.62 | 112.17
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 167.8 | 297.9 | 61.18 | 107.93
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342577 4FAWKES EK 138 342676 4THREE FK T 138 1 | 138 | 320 | 264 | 276 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 168.8 | 297.8 | 60.78 | 107.91
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 313.9 | 435.5 | 74.76 | 101.28
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_JKSMTH-REBA138_SRT-A | 342596 4HUNT 138 342607 4JK SMITH 138 1 | 138 | 320 | 396 | 430 | EKPC_P1-2_JK SMIT-FAW138_SRT-A | 321.5 | 435.5 | 73 | 101.28
S1-fixes | 25% | Liberty | W Garrard Lib J | EKPC_P1-2_SPUR-NCLA345_SRT-A | 326975 5CEDAR GRV 161 342700 5BULLITT CO 161 1 | 161 | 363/320 | 336 | 371 | EXT_324106 7HARDIN CO 345 325073 7REDMON RD 345 1 _SRT-S | 315.9 | 371.5 | 96.92 | 100.13
S1-fixes | 37% | Liberty | CCAP | EKPC_P1-2_LIB-S CAS | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 247.1 | 368.8 | 93.42 | 110.42
S1-fixes | 37% | Liberty | CCAP | 324130 5ALCALDE 161 324141 5ELIHU 161 1_SRT-S | 342796 5RUSSEL CO J 161 360448 5WOLF CRK HP 161 1 | 161 | 320/347 | 334 | 334 | EKPC_P1-2_LIB-S CAS | 311.8 | 368.7 | 73.99 | 110.4