## Sheet1
Project Number Table for DR2 Request #1
Project Reference Number: | 49
Project: | Spurlock Unit 3 & 4 Cooling Tower Concentrated Acid Tank - Add second tank
Prepared by: | Varble, Bill
Description: | Add a second 6,500 gallon concentrated sulfuric acid tank north of existing tank for U3 and U4 cooling tower water treatment. Horizontal 6,500 gallon sulfuric acid tank including tank access platform and desiccant vent system. Containment basin including acid resistant coating. Pumping and piping system. Wiring (power and I&C) required to operate
Justification: | Spurlock has had difficulty recently with receiving shipments of sulfuric acid, which can jeopardize the availability of the cooling tower and units. Request made to double storage capacity to offset delivery interruptions.
Alternative Considered: | Chemical totes—this solution would be much more dangerous to operate than a hard piped, permanent system, and generally more expensive than bulk purchase. No sulfuric acid treatment—this would require withdrawal of excessive amounts of water from the river, perhaps exceeding permitted levels, and would require greatly increased blowdown. Probability of plating out of calcium carbonate on tower components and condenser would be expected to increase.
Installed Date: (forecast) | 2024-12-13
Capital Cost: (forecast) | 796929
Operations and Maintenance Cost: | $20,000/year
Supporting Documentation of O&M Cost: | For the Spurlock Unit 3 & 4 Cooling Tower Concentrated Acid Tank – Add Second Tank, O&M cost estimates were based on operations cost for oversight of operation of the tank (including filling of the tank) and preventative maintenance and inspections (approximately 20 hours total per month). The addition of a second acid tank will not increase the usage volume of acid, so cost for purchase of acid were not included in this O&M estimate
Useful Life of Project: | 25 years with proper maintenance
Cost of Alternatives Considered: | Based on safety and permitting risk, no additional alternatives were costed out
Project Reference Number: | 38
Project: | Spurlock Landfill - Haul Road Paving Phase 2
Prepared by: | Varble, Bill
Description: | Pave an additional 5000’ of heavy-duty roadway asphalt pavement on the existing gravel haul road from the previous Phase 1 project to the existing construction entrance at South Ripley Rd.
Justification: | This project will contribute to the mitigation of fugitive dust and stormwater runoff water quality by replacing the current gravel surface with asphalt pavement, helping meet environmental compliance. This also provides safer travel conditions for haul trucks, reduction of water needed for dust control, and reduces roadside maintenance.
Alternative Considered: | Maintaining a gravel surface on the haul road section would be the highest risk option. The options for paving were heavy duty asphalt and concrete, with concrete being the more expensive option.
Installed Date: (forecast) | 2026-09-30
Capital Cost: (forecast) | 3414357
Operations and Maintenance Cost: | $35,000/year
Supporting Documentation of O&M Cost: | EKPC utilized a rehabilitation frequency of 5 years based on a previous recommendation from a consultant based on the nature of the traffic loading and material being hauled. The rehabilitation would include the cost associated with milling and paving the surface course on the 5-year frequency, as well as repair of spot failure that occur and ditch line maintenance.
Useful Life of Project: | Approximately 20 years with proper maintenance.
Cost of Alternatives Considered: | Maintain gravel, with no additional capital cost. Phase 2 will be a continuation of the cost determinations made in the development of Phase 1. The cost analysis completed during Plant pavement projects and Phase 1, which showed that for two pavement types asphalt had an 85% less capital investment compared to concrete.
Project Reference Number: | 55
Project: | Spurlock CCR ELG Operations Control Facility (Environmental Plant Operational Facility)
Prepared by: | Varble, Bill
Description: | Office addition is 652sf in area, metal framed walls with insulated metal panel exterior to match adjacent structures, standing seam metal roof and on a concrete slab/footing. Extend existing building to include new foundations, floors, doors, windows, structure, roof, siding, walls, HVAC, plumbing and electrical. Fit up new building with furniture and appliances.
Justification: | The original CCR/ELG plan was to build a breakroom for the additional manpower needed to operate the Waste Water Treatment (WWT) Facility and didn’t include a dedicated control room. The project planned for the WWT equipment to operate from the WWT engineering station which, posed challenges with commissioning and concerns for long term operation. EKPC evaluated operating the Waste Water Treatment Equipment with the existing Scrubbers and the Four Units in the main plant control room, however, this would have caused extra congestion and complexity in the existing plant control room as well as the operating team. The selected alternative was to divide control operations for the whole station to create two operating teams that would split at the Unit 1&2 Scrubbers. The temporary WWT and Scrubbers Control room was placed in what was originally planned to be the WWT break room, meaning very limited space for both the control room and break rooms. With this capital project, there will be a dedicated control room and a dedicated breakroom that will give the WWT Operators the same amenities that are provided to the rest of the station employees including lockers, one office for the ability to check emails, perform training, or a private meeting with their supervisor, and an additional bathroom.
Alternative Considered: | As noted in justification above: 1) Operation at the WWT engineering station, 2) Operation in the main plant control room, 3) Temporary WWT & Scrubber control in break room.
Installed Date: (forecast) | 2025-08-21
Capital Cost: (forecast) | 700000
Operations and Maintenance Cost: | $11,760/year
Supporting Documentation of O&M Cost: | Utilized approximately a 1.5% of the cost of the original capital investment.
Useful Life of Project: | over 30 years
Cost of Alternatives Considered: | No alternatives were evaluated from a cost perspective.
Project Reference Number: | 42
Project: | Spurlock South Side Cap
Prepared by: | Burton, Jarrad
Description: | Cap the South side of the landfill over portions of Area B and Area C that are at final slope per our landfill permit. The cap will be approximately 10 acres. It will include regrading the slope to meet permitted top of waste, placing FML, recomposite, and two feet of clay as required by the CCR rule. This project scope will also include establishing vegetative cover and performance of field and engineering services per the Spurlock Landfill Permit.
Justification: | As part of compliance with the Coal Combustion Residual Rule for Spurlock Landfill, EKPC is required to install a closure cap on the areas of the landfill that reach final permitted limits. In accordance with the CCR Rule, the cap permeability must be equal to or less than the subgrade. The bond will be reduced when cap is established.
Alternative Considered: | No alternatives were considered. This is an Asset Retirement Obligation (ARO) associated with the landfill.
Installed Date: (forecast) | 2026-12-31
Capital Cost: (forecast) | 3750000
Operations and Maintenance Cost: | $20,000/year
Supporting Documentation of O&M Cost: | Estimated cost for maintenance of the down drains ($5,000), mowing ($10,000), and erosion and sediment control ($5,000) per year. The down drain and erosion and sediment control costs are based on previous experience from the caps and down drains currently maintained by EKPC. The cost to develop the mowing cost took into consideration the current landfill operations contract EKPC has in place for Spurlock Landfill.
Useful Life of Project: | over 30 years
Cost of Alternatives Considered: | No alternatives considered.
Project Reference Number: | 54
Project: | Spurlock Landfill A, B, C Runon and Runoff Upgrade
Prepared by: | Burton, Jarrad
Description: | Upgrade legacy portions of the Spurlock landfill to adequately handle a 25 year, 24 hour rain event in accordance with the CCR Rule. Work to include 223 feet of 2-42" reinforced concrete pipe, 70 feet of 24"x38" elliptical reinforced concrete pipe and 983 feet of stone lined ditches.
Justification: | This work is required by EPA's Code of Federal Regulations 40 CRF 257. In accordance with 40 CRF 257.82 the Periodic Run-on/Run-off Assessments is due every five years. It was initially performed in 2016 and is due again this year. This work needed to be completed this summer in order to complete the assessment by the due date.
Alternative Considered: | No alternatives were considered. This work was necessary in order to complete the required assessment.
Installed Date: (forecast) | 2021-07-07
Capital Cost: (forecast) | 197176
Operations and Maintenance Cost: | $2,500/year
Supporting Documentation of O&M Cost: | General maintenance of the stone-lined ditches associated with this project would be required. The cost was based EKPC’s experience with the unit rates for purchase and placement of stone.
Useful Life of Project: | 30 years
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 48
Project: | Spurlock West Side Pump Station
Prepared by: | Burton, Jarrad
Description: | Wet areas exist on the west side of Spurlock Landfill. The project scope includes installing toe drains within the landfill cap and a pump station capable of moving the water to the adjacent landfill ditch. In addition, the area will be regraded to promote stormwater runoff.
Justification: | The wet areas on the west side of Spurlock landfill are beginning to cause stability issues on the slope including minor sloughing. If not addressed, the stability issues will continue to worsen, and the integrity of the landfill cap system and perimeter haul road could be at risk of failure.
Alternative Considered: | The following alternatives were considered to address this problem: - Do nothing - Regrade the area and re-evaluate in the future - Install drains and a pump station to remove water from the area
Installed Date: (forecast) | 2025-12-17
Capital Cost: (forecast) | 809600
Operations and Maintenance Cost: | $20,000/year
Supporting Documentation of O&M Cost: | O&M costs were developed to cover the monitoring of the pump station on a regular basis utilizing standard unit rates and a contingency for repairs and spare parts required to maintain operation of the pump station.
Useful Life of Project: | 25 years with proper maintenance
Cost of Alternatives Considered: | Alternatives were not costed, selection of alternatives was based on risk.
Project Reference Number: | 43
Project: | Smith Landfill Final Cap
Prepared by: | Burton, Jarrad
Description: | Place a CCR compliant cap on JK Smith Landfill and initiate final closure. It will include regrading the slopes to meet permitted top of waste, placing FML, geocomposite, and two feet of clay as required by the CCR rule. This project scope will also include establishing vegetative cover and performance of field and engineering services per the Smith Landfill Permit.
Justification: | JK Smith has no future plans to take any CCR material, therefore, the landfill is no longer needed and can be closed consistent with the CCR Legacy Rule. In accordance with the CCR Rule, the cap permeability must be equal to or less than the subgrade.
Alternative Considered: | No alternatives were considered. This is an Asset Retirement Obligation (ARO) associated with the landfill.
Installed Date: (forecast) | 2026-12-31
Capital Cost: (forecast) | 4000000
Operations and Maintenance Cost: | $20,000/year
Supporting Documentation of O&M Cost: | Estimated cost for maintenance of the down drains ($5,000), mowing ($10,000), and erosion and sediment control ($5,000) per year. The down drain and erosion and sediment control costs are based on previous experience from the caps and down drains currently maintained by EKPC. The cost to develop the mowing cost took into consideration the current landfill operations contract EKPC has in place for Spurlock Landfill.
Useful Life of Project: | over 30 years
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 56
Project: | Spurlock Unit 3 and Unit 4 - Dust Suppression for BC3, BC4, PC3 and PC4 Conveyors
Prepared by: | Caldwell, Jeff
Description: | This project will provide dust suppression for bunker coal conveyors BC3 and BC4 as well as plant coal conveyors PC3 and PC4. The discharge of the PC3 and PC4 conveyors are located in the tripper floor room at the top of the main plant building. The BC3 and BC4 conveyors are located entirely within the tripper floor room. The project scope to provide a fogging dust suppression system is listed below. Third-party vendor, Dust Solution Inc. (DSI) will design and supply the dust suppression equipment. DSI has provided several dust suppression systems for ash and coal at Spurlock. Construction contract will provide the following: installation of one multi-function module (MFM), installation of one electric control module (ECM), installation of four (4) flow control modules (FCM), installation of 28 fogger nozzles, installation of all piping and hoses to connect the MFM, FCMs and fogger nozzles, provide materials and install air, water and electrical supply to the dust suppression system.
Justification: | Plant coal conveyors PC3 and PC4 supply coal to the tripper floor at the top of the main plant building. The coal is then discharged onto the bunker coal conveyors BC3 and BC4. The coal then leaves BC3 and BC4 to fill the silos, ready for Unit 3 and Unit 4 boilers. As the coal transfers from conveyor to conveyor and conveyor to silo there is a significant amount of dust created. That dust can make its way throughout the entire tripper floor room. The coal dust can create a fire hazard. It can also be a health issue for employees working in the tripper floor room.
Alternative Considered: | None – This is approximately the 7th one of these systems the plant has installed and they have been proven reliable.
Installed Date: (forecast) | 2024-12-13
Capital Cost: (forecast) | 247080
Operations and Maintenance Cost: | $5,000/year
Supporting Documentation of O&M Cost: | Includes cost for the labor cost associated with Preventative Maintenance activities and inspections (approximately four hours per month) as well as allowance for miscellaneous repairs, including minor material procurement and replacement such as a plug nozzle.
Useful Life of Project: | 20 years with proper maintenance
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 47
Project: | Spurlock WWT - Ash Reliability Improvements
Prepared by: | Caldwell, Jeff
Description: | Cable tray covers, service water flush capabilities for wastewater elimination system, new isolation valve for brine forwarding leg, plenum cover at WWT & Ash PCM's to prevent potential water seepage, A/C bypass source at ash PCM, removable handrail at WWT & ash PCM's and lid for distribution, service and clarifier clearwell tanks.
Justification: | After operating the new systems for nearly two years and during that time period successfully operating through Winter Storm Elliot, several opportunities to improve reliability that are needed have been identified. This scope improves reliability of the electrical system that powers all of the ash systems for U1 & U2 as well as the WWT Plant needed to operate U1 & U2. Also, this project is in accordance with EPKC’s Winter (cold weather) Preparedness Plan reviewing lessons learned from past winter events (Winter Storm Elliot). Proper winter readiness is also part of NERC requirement EOP-012 (Emergency Operation Plans).
Alternative Considered: | None –These projects are reliability driven, permanent solutions to the issues identified over the past two years. Tank lid covers – 1) Currently there is netting over the 2 tanks that does not have the same longevity as a solid fiberglass lid. 2)service water mods are to have permanent water lines versus red rubber hoses run where several were tripping hazards. The outdoor lines will be run with heat trace and insulation so they do not have to be rolled back up when not in use during the colder months outside.
Installed Date: (forecast) | 2025-02-20
Capital Cost: (forecast) | 1264820
Operations and Maintenance Cost: | $10,000/year
Supporting Documentation of O&M Cost: | O&M cost of $10,000 per year took into account the cost for the labor cost associated with approximately 7 hours Preventative Maintenance activities and inspections per month, as well as allowance for miscellaneous repairs.
Useful Life of Project: | 30 years
Cost of Alternatives Considered: | No alternatives considered – reliability and safety driven.
Project Reference Number: | 50
Project: | Spurlock Vac Truck Air Compressor
Prepared by: | Caldwell, Jeff
Description: | Purchase a new air compressor for the vacuum truck ash transfer station. The new air compressor will need to be the same capacity as the existing. The new compressor will need to have remote start capability so that it only runs during the unloading process. It will also need to have a cold start kit with interlock to prevent startup before the oil is warm. The new air compressor will need to be installed at a location remote to the vacuum truck ash transfer station to prevent it from being contaminated with ash particulate. This will require a new concrete pad. Piping and cables will need to be ran from the existing compressor location to connect to the new remote location.
Justification: | The existing air compressor for the vacuum truck ash transfer station has been damaged by ash particulate due to it being mounted in close proximity to the ash unloading. It has also incurred damage from cold starting during the winter. The compressor was also being operated 24/7 since there was not a remote start for the truck drivers. The air compressor repair cost is a significant portion of a new compressor price. The option to tie into the waste water treatment plant air system was explored but found to have insufficient capacity for this additional operation. Since the ash pond operation has ceased, it is no longer an option for the vacuum trucks to unload there. If the vacuum trucks were to haul directly to the landfill it would require the landfill to operate 24/7 rather than the current day shift operation. At present time a rental air compressor is being utilized to allow the transfer station to continue to operate.
Alternative Considered: | None – In-kind replacement was not an option as current compressor did not survive the environment it was in. the fogging system has an air requirement and there was not any reasonable local air that could be tied into.
Installed Date: (forecast) | 2025-01-20
Capital Cost: (forecast) | 740000
Operations and Maintenance Cost: | $20,000/year
Supporting Documentation of O&M Cost: | A bi annual service check quote was received for approximately $13,000 per year. The Air compressor will also require Preventative maintenance (approximately 4 hours per month) and miscellaneous repairs including minor material procurement and replacement such air filters.
Useful Life of Project: | 15 - 20 years with proper maintenance
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 52
Project: | Spurlock WWT Distillate System Upgrades
Prepared by: | Caldwell, Jeff
Description: | Install a lid on the distillate tank to prevent contamination from the adjacent coal pile. Heat trace and insulate distillate line from WWT to U2 scrubber
Justification: | The existing distillate tank had an open top and was susceptible to dust, debris and coal from the coal pile nearby. The water from this tank goes to a permitted outfall and needs to comply with the associated water quality limits. The installation of a lid to avoid water contamination was the only solution. In addition, during Winter Storm Elliot, the distillate line had freezing issues brought about by the cold temperatures, so EKPC added heat trace and insulating line to avoid freezing. This project is in accordance with EPKC’s Winter (cold weather) Preparedness Plan reviewing lessons learned from past winter events (Winter Storm Elliot). Proper winter readiness is also part of NERC requirement EOP-012 (Emergency Operation Plans).
Alternative Considered: | None – Tank lid was best option to keep out unwanted particles and it had to be stainless since the tank could not be removed from service. We also wanted the security/permanency of a solid lid since the water ends up at a permitted outfall. Freeze Protection – It is standard at power plants to use heat trace and insulate to prevent freeze protection of lines.
Installed Date: (forecast) | 2024-01-03
Capital Cost: (forecast) | 611855
Operations and Maintenance Cost: | $5,000/year
Supporting Documentation of O&M Cost: | Includes cost for the labor cost associated with Preventative Maintenance activities and inspections (approximately four hours per month) as well as allowance for miscellaneous repairs, including minor material procurement
Useful Life of Project: | 25 years
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 53
Project: | Spurlock Water Mass Balance Pond- Install Heat Trace on Supply/Return Lines to Pond
Prepared by: | Caldwell, Jeff
Description: | Purchase and installation of heat trace and insulation for the Spurlock Water Mass Balance Treatment Recirculation Lines to the WMB Pond.
Justification: | Current piping supply/return are subject to freezing. This project is in accordance with EPKC’s Winter (cold weather) Preparedness Plan reviewing lessons learned from past winter events (Winter Storm Elliot). Proper winter readiness is also part of NERC requirement EOP-012 (Emergency Operation Plans).
Alternative Considered: | None - Freeze Protection – It is standard at power plants to use heat trace and insulate to prevent freeze protection of lines. Also part of Winter Readiness.
Installed Date: (forecast) | 2024-10-10
Capital Cost: (forecast) | 229342
Operations and Maintenance Cost: | $5,000/year
Supporting Documentation of O&M Cost: | Includes cost for the labor cost associated with Preventative Maintenance activities and inspections (approximately four hours per month) as well as allowance for miscellaneous repairs, including minor material procurement
Useful Life of Project: | 25 years with proper maintenance
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 46
Project: | Cooper SCR - Top Catalyst Layer Replacement 2024/25
Prepared by: | Ackerman, Paul
Description: | Purchase one (1) new layer/63 modules of plate catalyst in 2024 and replace the Cooper Unit 2 SCR top layer in 2025. Catalyst layer will come with new ash baffles to seal the 63 modules inside the reactor.
Justification: | Fall 2022 catalyst testing results showed 9,000 hours of remaining life left in the reactor. Unit 2's total activity factor (Z) for the reactor required to meet emissions is 4.5 minimum. The testing showed the current Z factor to be 5.4.
Alternative Considered: | Replacement of modules is required to maintain environmental compliance, no known alternatives
Installed Date: (forecast) | 2025-06-13
Capital Cost: (forecast) | 1159180
Operations and Maintenance Cost: | $0 added expense
Supporting Documentation of O&M Cost: | $0 added operations and maintenance expenditures
Useful Life of Project: | Approximately 10 years, based on annual testing
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 51
Project: | Cooper Landfill Leachate System 480 Volt Electric
Prepared by: | Ackerman, Paul
Description: | 480Volt electric to be run to Cooper landfill leachate system.
Justification: | The leachate pumps are currently powered by a portable propane generator. The generator has failed multiple times and has resulted in significant maintenance attention. This project will supply a new 480V electric feed to the leachate farm to power submersible pumps that will reduce maintenance time and increase reliability for the landfill leachate pump system.
Alternative Considered: | Continue with existing unreliable operations requiring high maintenance efforts.
Installed Date: (forecast) | 2025-03-27
Capital Cost: (forecast) | 656240
Operations and Maintenance Cost: | $0 added expense
Supporting Documentation of O&M Cost: | $0 added operations and maintenance expenditures
Useful Life of Project: | 30 years
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 44
Project: | Cooper U2 Air Heater Basket/Seal Replacement
Prepared by: | Ackerman, Paul
Description: | 2022 Arvos air heater inspection revealed that the cold end baskets were approaching end of life. Project will consist of replacing the air preheater cold and hot baskets and seals. The hot baskets and top seals must be removed prior to being able to access the cold baskets and in order to provide the same heat transfer system performance as existing, and to maximize life expectancy of the combined hot/cold basket system, the hot baskets must be replaced at the same time as the cold baskets.
Justification: | Air heater has to remain in service for the unit to operate.
Alternative Considered: | No known alternatives
Installed Date: (forecast) | 2025-06-13
Capital Cost: (forecast) | 1915981
Operations and Maintenance Cost: | $0 added expense
Supporting Documentation of O&M Cost: | $0 added operations and maintenance expenditures
Useful Life of Project: | 10-15 years
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 45
Project: | Cooper Unit 2 Replace Middle Layer SCR Catalyst
Prepared by: | Ackerman, Paul
Description: | Replace middle layer SCR catalyst.
Justification: | End of life.
Alternative Considered: | Replacement is required to maintain environmental compliance, no known alternatives.
Installed Date: (forecast) | 2026-05-11
Capital Cost: (forecast) | $1,343,853.00, top catalyst layer cost with 10% contingency and 5% inflation factor
Operations and Maintenance Cost: | $0 added expense
Supporting Documentation of O&M Cost: | $0 added operations and maintenance expenditures
Useful Life of Project: | Approximately 10 years, based on annual testing
Cost of Alternatives Considered: | No alternatives considered
Project Reference Number: | 57
Project: | Spurlock Station Ash Cooling Actuators
Prepared by: | Scott, Quinten
Description: | New actuators to automate cooling valves on the United Conveyor Corporation Pneumatic Ash Extractor System. All control wiring and necessary terminations and inputs into the DCS System to be able to control from control room.
Justification: | Flue Gas is currently discharging into the old tool room due to the ash cooling system not being able to control the amount of air pulled. This is a personnel safety concern.
Alternative Considered: | Logic revisions were made to full load, no load, and timers between sequences, but this change did little to prevent conveying flu gas.
Installed Date: (forecast) | 2023-12-01
Capital Cost: (forecast) | 31816.38
Operations and Maintenance Cost: | $500 /year
Supporting Documentation of O&M Cost: | O&M costs included assume that one of the eight valves installed will need replacement approximately once every 10 years. The cost for a replacement is $3,900 in material cost and approximately $1,000 in labor for installation costs. Please see attachment PSC DR1 Request 5 – FloSource Quote.pdf. Amortizing this into an annual O&M rate, EKPC determined the costs would equal approximately $500/year.
Useful Life of Project: | 20 years
Cost of Alternatives Considered: | No alternatives considered