## Export
DEK FAC 2025-00077
PSC DR 1.15
Review Period: 11/1/2023 - 4/30/2024
Unit | Event Type | Scheduled Hours | Forced Hours | Actual Hours | Event Duration Hours | Event Start | Event End | Event Description
East Bend Steam-2 | PO | 1199 | 0 | 1199 | 1199 | 2023-09-18 04:00 | 2023-11-07 03:00 | Fall Planned Outage
East Bend Steam-2 | PO | 19.7 | 0 | 19.7 | 19.7 | 2023-11-07 10:54 | 2023-11-08 06:36 | Boiler Feed Pump and Turbine Overspeed Protection Control Upgrade Testing
East Bend Steam-2 | PO | 9.3 | 0 | 9.3 | 9.3 | 2023-11-12 03:56 | 2023-11-12 13:14 | Boiler Feed Pump and Turbine Overspeed Protection Control Upgrade Testing
East Bend Steam-2 | PO | 16.3 | 0 | 16.3 | 16.3 | 2023-11-12 13:28 | 2023-11-13 05:46 | Boiler Feed Pump and Turbine Overspeed Protection Control Upgrade Testing
Woodsdale CT-1 | PO | 12 | 0 | 12 | 12 | 2023-11-16 11:00 | 2023-11-16 23:00 | Repairs made on main plant UPS system, both primary and backups.
Woodsdale CT-2 | PO | 12 | 0 | 12 | 12 | 2023-11-16 11:00 | 2023-11-16 23:00 | Repairs made on main plant UPS system, both primary and backups.
Woodsdale CT-3 | PO | 12 | 0 | 12 | 12 | 2023-11-16 11:00 | 2023-11-16 23:00 | Repairs made on main plant UPS system, both primary and backups.
Woodsdale CT-4 | PO | 12 | 0 | 12 | 12 | 2023-11-16 11:00 | 2023-11-16 23:00 | Repairs made on main plant UPS system, both primary and backups.
Woodsdale CT-5 | PO | 12 | 0 | 12 | 12 | 2023-11-16 11:00 | 2023-11-16 23:00 | Repairs made on main plant UPS system, both primary and backups.
Woodsdale CT-6 | PO | 12 | 0 | 12 | 12 | 2023-11-16 11:00 | 2023-11-16 23:00 | Repairs made on main plant UPS system, both primary and backups.
East Bend Steam-2 | MO | 65.533 | 0 | 65.533 | 65.533 | 2023-11-26 07:32 | 2023-11-29 01:04 | Waste Stabilization Flyash Feeder Gearbox Repair
Woodsdale CT-5 | U1 | 0 | 47 | 47 | 47 | 2023-11-29 03:00 | 2023-12-01 02:00 | Unit automatically tripped due to CB1508 yard breaker opening. Still under investigat
Woodsdale CT-6 | U1 | 0 | 47 | 47 | 47 | 2023-11-29 03:00 | 2023-12-01 02:00 | Unit manually tripped due to CB1508 yard breaker opening. Still under investigation.
Woodsdale CT-6 | SF | 0 | 76.217 | 76.217 | 76.217 | 2023-12-04 11:10 | 2023-12-07 15:23 | Unit Sync. Not giving Close command to BKR
Woodsdale CT-4 | MO | 3.867 | 0 | 3.867 | 3.867 | 2023-12-08 20:10 | 2023-12-09 00:02 | Repaired electrical short on NOZ valve solenoid.
Woodsdale CT-2 | U1 | 0 | 2.317 | 2.317 | 2.317 | 2023-12-10 12:41 | 2023-12-10 15:00 | Tested SFC after Trouble shooting (crank test successful made unit available) 12/10/23
Woodsdale CT-3 | U1 | 0 | 2.317 | 2.317 | 2.317 | 2023-12-10 12:41 | 2023-12-10 15:00 | Unit back available after sync work, 12/10/23 10:00
Woodsdale CT-6 | SF | 0 | 2.833 | 2.833 | 2.833 | 2023-12-12 10:58 | 2023-12-12 13:48 | Unit back Available After Sync work, 12/12/23 8:48
Woodsdale CT-5 | MO | 1 | 0 | 1 | 1 | 2023-12-18 13:00 | 2023-12-18 14:00 | Unit unavailable to add SF6 gas to gen breaker
Woodsdale CT-4 | MO | 1 | 0 | 1 | 1 | 2023-12-18 14:00 | 2023-12-18 15:00 | Unit unavailable to add SF6 gas to gen breaker
Woodsdale CT-3 | MO | 1 | 0 | 1 | 1 | 2023-12-18 15:00 | 2023-12-18 16:00 | Unit unavailable to add SF6 gas to gen breaker
Woodsdale CT-4 | MO | 6.317 | 0 | 6.317 | 6.317 | 2023-12-20 11:00 | 2023-12-20 17:19 | Had to calibrate gas fuel flow meter for compliance.
Woodsdale CT-4 | SF | 0 | 3.05 | 3.05 | 3.05 | 2024-01-08 11:58 | 2024-01-08 15:01 | Unit back available after FO breaker calibration
Woodsdale CT-1 | SF | 0 | 3 | 3 | 3 | 2024-01-08 12:01 | 2024-01-08 15:01 | Unit back available after FO breaker calibration
Woodsdale CT-3 | SF | 0 | 3 | 3 | 3 | 2024-01-08 12:01 | 2024-01-08 15:01 | Unit back available after FO breaker calibration
Woodsdale CT-4 | SF | 0 | 8.533 | 8.533 | 8.533 | 2024-01-15 11:45 | 2024-01-15 20:17 | Unit back available after ignition system trouble
Woodsdale CT-3 | SF | 0 | 1.233 | 1.233 | 1.233 | 2024-01-15 11:50 | 2024-01-15 13:04 | Unit back available after ignition system trouble
East Bend Steam-2 | MO | 193.75 | 0 | 193.75 | 193.75 | 2024-01-22 19:27 | 2024-01-30 21:12 | FGD Chemistry
Woodsdale CT-4 | SF | 0 | 8.783 | 8.783 | 8.783 | 2024-01-30 11:58 | 2024-01-30 20:45 | Replaced bad card on FO control valve.
East Bend Steam-2 | U1 | 0 | 3.733 | 3.733 | 3.733 | 2024-01-31 05:32 | 2024-01-31 09:16 | 2-1 mill, wet coal causing feeder plugging and drum level to trip
Woodsdale CT-5 | U1 | 0 | 2.85 | 2.85 | 2.85 | 2024-02-20 12:12 | 2024-02-20 15:03 | Replaced blowoff solenoid.
Woodsdale CT-1 | PO | 2006.667 | 0 | 2006.667 | 2006.667 | 2024-03-01 05:01 | 2024-05-23 19:41 | Turbine blade replacement, rows 1-4
Woodsdale CT-5 | U1 | 0 | 2.217 | 2.217 | 2.217 | 2024-03-21 09:52 | 2024-03-21 12:05 | Unit would not sync due to low SF6 gas pressure, raised gas pressure and test ran unit
Woodsdale CT-6 | PO | 9.433 | 0 | 9.433 | 9.433 | 2024-03-27 04:01 | 2024-03-27 13:27 | Unit unavailable to change out gas fuel flow meter.
Woodsdale CT-2 | U1 | 0 | 1 | 1 | 1 | 2024-03-29 09:00 | 2024-03-29 10:00 | Reset SFC, test cranked, remoted started successfully @ 17:12 on 3/29.
Woodsdale CT-2 | U1 | 0 | 5.833 | 5.833 | 5.833 | 2024-04-05 08:47 | 2024-04-05 14:37 | Unit would not sync, cranked a few times, test ran unit.
East Bend Steam-2 | MO | 359.967 | 0 | 359.967 | 359.967 | 2024-04-13 04:01 | 2024-04-28 03:59 | Superheat spray valve repairs
Woodsdale CT-2 | PO | 328.833 | 0 | 328.833 | 328.833 | 2024-04-20 04:01 | 2024-05-03 20:51 | Spring outage/Borescope
Woodsdale CT-4 | U1 | 0 | 33.267 | 33.267 | 33.267 | 2024-04-21 10:00 | 2024-04-22 19:16 | Stroked blow-off valves, check water injection, test ran, returned to service 4/22 @ 1
Woodsdale CT-5 | SF | 0 | 4.3 | 4.3 | 4.3 | 2024-04-23 08:25 | 2024-04-23 12:43 | Unit would not sync due to low SF6 gas pressure, raised gas pressure, test ran, return
Woodsdale CT-4 | U1 | 0 | 16.017 | 16.017 | 16.017 | 2024-04-24 20:45 | 2024-04-25 12:46 | Swapped power oil pump filter, test ran 4/25 @ 0836 unit tested fine.
Woodsdale CT-4 | PO | 305.15 | 0 | 305.15 | 305.15 | 2024-04-27 04:01 | 2024-05-09 21:10 | Spring outage/Borescope
Woodsdale CT-3 | PO | 323.283 | 0 | 323.283 | 323.283 | 2024-04-27 04:01 | 2024-05-10 15:18 | Spring outage/Borescope
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure (Forced Outage)