## > $100k
Items Over $100k
Actuals Spend thought April 2025
Category | Project | Kentucky Power | Wheeling Power | Total Actual
Ash, Wastewater CCR | MLWSPCCHN ML S Collection Cnv Chain Repl | 57079.53 | 395087.37 | 452166.9 | The collection chains must be replaced due to wear. If not replaced the chains will bind on the sprocket and prevent bottom ash removal resulting in a curtailment or unit outage.
Boiler & Auxiliaries | MLWSPBRNN ML S Burner Nozzle Rplcmt | 574067.28 | 3361057.62 | 3935124.9 | The burner nozzles were replaced to improve combustion efficiency.
| MLWSPSOOT ML S Sootblower Replace Remove | 153356.57 | 831255.39 | 984611.96 | Removed obsolete sootblower seal air fans no longer needed for operation.
| MLWSPVALV ML S Blr Brnr Steam Valve Repl | 64671.26 | 427526.09 | 492197.35 | Replacing valves over 6in for pulverized coal, steam, and ash transport due to age and wear.
| MLWNPINSL ML N Insulation & Lagging Rplc | 99488.27 | 486591.94 | 586080.21 | Replaced insulation to improve unit heat rate.
| MLWSPDUCT ML S Duct Lag Insul Replace | 23644.99 | 117779.16 | 141424.15 | Replaced insulation to improve unit heat rate.
| MLWSPNPPB ML S Other Non Outage PPB | 51520.45 | 293866.73 | 345387.18 | Miscellaneous unit repairs not covered by other projects.
| MLW2CGRPL ML U2 Clinker Grinder Replace | 169146.62 | 1057307.9 | 1226454.52 | The original bottom ash grinders were not able to effectively remove bottom ash. The replacements prevent ash buildup and slagging.
| MLW1CGRPL ML U1 Clinker Grinder Replace | 205765.08 | 1367675.06 | 1573440.14 | The original bottom ash grinders were not able to effectively remove bottom ash. The replacements prevent ash buildup and slagging.
Boiler Make-up Water Sup Syst | MLWEPRESN ML E Resin Replacements | 43246.29 | 232620.26 | 275866.55 | Replaced demineralizer resin that has reached end of life to maintain condensate purity.
Boiler/Boiler Components | MLWOPNONP ML O Non-Process Outage PPB | 315461.84 | 1708146.5 | 2023608.34 | Miscellaneous unit repairs not covered by other projects.
| MLWSC1AHB ML S U1 Air Heater Basket Rplc | 577060.31 | 3149896.39 | 3726956.7 | The in service air heater baskets were past end of life. They were causing the air heater rotors to lock up and reduced unit efficiency.
| MLWSC2AHB ML S U2 Air Heater Basket Rplc | 649887.76 | 3194252.44 | 3844140.2 | The in service air heater baskets were past end of life. They were causing the air heater rotors to lock up and reduced unit efficiency.
| MLWSP2LSO ML S U2 Lower Sidewl Weld Ovly | 235084.74 | 1149788.72 | 1384873.46 | Weld overlay was installed to protect sidewall tubes from fire side corrosion and reduce boiler EFOR rate.
Condenser & Auxiliaries | MLWEPVALV ML E Valve Replacements | 48998.38 | 282546.15 | 331544.53 | Replacement of condensate valves over 6 inches.
Cooling Twr, Misc Wtr, ChemGrp | MLWPC2CTC ML PCC U2 Cooling Tower Comp | 666383.03 | 3255657.45 | 3922040.48 | Replaced aging cooling tower hot deck to improve circulating water temperatures and unit performance.
| 000026265 ML U2 Cooling Tower Reinforce | 2455312.87 | 16311029.41 | 18766342.28 | The existing cooling tower shell must be reinforced to ensure structural integrity.
Cooling Water Facilities | MLWEPCWPM ML E Circ Water Pump Reb (Cap) | 161698.93 | 942705.03 | 1104403.96 | Routine pump rebuilds are required to ensure pump performance and reduce circulating water temperatures.
CT/CC Group | MLWEC1CTF ML E U1 Cooling Tower Compnnts | 1336903.56 | 7352605.55 | 8689509.11 | Replaced aging cooling tower hot deck to improve circulating water temperatures and unit performance.
| MLWPCT1BP ML U1 Cooling Tower Canopy RPL | 622366.72 | 3706128.12 | 4328494.84 | The existing canopy had multiple beam failures which were a safety concern for personnel. Failure of the canopy would also result in the inability to cool circulating water which would result in a unit curtailment.
Environmental | MLWSPEJNT ML S Expansion Joint Repl | 425980.95 | 2323783.64 | 2749764.59 | Replaced aging pulverizer expansion joints to prevent coal leaks.
| MLWDFALND ML DFA LAND ACQUISITION | 126333.59 | 690579.2 | 816912.79
| MLWMPDRNG ML M Drainage Projects (Cap) | 15734.78 | 89714.81 | 105449.59
| MLWEPCATT ML E Cation Tank Rplc | 17318.65 | 119390.15 | 136708.8 | The existing tank has through wall leaks that cannot be repaired, this time is required to maintain condensate purity.
FGD (Scrubber) Group | MLWMPECRN ML M ECrane Capital Work | 55151.06 | 284093.68 | 339244.74 | Component replacements required to maintain E-crane used to supply limestone to FGD.
| MLWOPFGDP ML O FGD Process Outage PPB | 266913.47 | 1513108.59 | 1780022.06 | Miscellaneous FGD repairs not covered by other projects.
| MLWPC0LIM ML PCC U0 Lime Conversion | 1636278.6 | 8141749.13 | 9778027.73 | The conversion from trona to lime allowed Unit 1 to reach lower minimum loading by reducing the formation of acid in the flue gas steam.
| MLWVPFGDN ML V FGD Other Non Outage PPB | 292401.97 | 1637819.04 | 1930221.01 | Miscellaneous FGD repairs not covered by other projects.
| MLWVPPUMP ML V FGD CPS Pumps | 178353.49 | 1104119.67 | 1282473.16 | Replace critical pumps for CPS environmental compliance.
| MLWVPVALV ML V FGD CPS Valve Replace | 76210.64 | 403652.36 | 479863 | Replace critical valves for CPS environmental compliance.
| MLWVPGRBX ML V Gearbox Replacements | 28004.56 | 155538.16 | 183542.72 | Replace critical equipment gearboxes that have reached end of life.
| MLWVPOPIP ML V Outage FGD Pipe Replace | 303694.51 | 1834304.27 | 2137998.78 | Aging reagent supply headers were replaced to reduce unit curtailments.
| MLWVPPIPE ML V Non Outage FGD Pipe Repl | 200326.35 | 1116229.88 | 1316556.23 | Aging oxidation air headers were replaced to reduce unit curtailments.
| MLWVPEJNT ML V FGD CPS Expansion Joints | 35546.15 | 246322.13 | 281868.28 | Replacement of liquid and gas expansion joints that have reached end of life.
| MLWVIDFMR ML VP OUT ID FAN MOTOR REPL | 45903.75 | 294914.18 | 340817.93 | The ID fan motors failed in service and required replacements.
| MLWVPBLML ML V Ball Mill Liner Replace | 47692.69 | 330363.37 | 378056.06 | Routine replacement due to liner wear from normal use.
| MLWVP21ID MLP V REBUILD #21 ID FAN | 53738.72 | 381460.86 | 435199.58 | Routine rebuild of ID fan to ensure efficiency and prevent breakdowns in service.
| MLWVP11ID MLP V REBUILD #11 ID FAN | 42757.89 | 315518.95 | 358276.84 | Routine rebuild of ID fan to ensure efficiency and prevent breakdowns in service.
| MLWVPHBSH ML V ID Fan Hub Shell Rplc | 22294.12 | 161802.68 | 184096.8 | Replacement of ID fan hub shell that had worn beyond weld repair. Required to ensure ID fan performance.
Fly Ash Landfill | MLWHAULRD Mitchell Haul Road Relocate | 956108.65 | 6261566.8 | 7217675.45 | Project was completed to move fly ash haul road away from active ACNR mine floating road.
Fossil/Steam-OthDirectUnitCost | MLWEPHVAC MLP E HVAC Unit Replacements | 81612.68 | 443710.67 | 525323.35 | Replacement of failed obsolete HVAC units.
| MLWNPBLDG ML N Capital Building Upgrades | 271380.01 | 1585483.03 | 1856863.04 | Replacement of obsolete elevator equipment no longer supported by the OEM or service vendors.
| MLWNPTOOL ML N Capital Tool Purchases | 262462.79 | 1471812.68 | 1734275.47 | Replacement tooling to mobile equipment for unit maintenance.
| MLWNPWINT ML CAPITAL WINTERIZATION | 53357.44 | 345123.15 | 398480.59 | Complete installations of new equipment for winterization.
| MLWEP2BAT ML E U2 Station Battery Rep | 19381.79 | 133361.51 | 152743.3 | Plant batteries are replaced every 15 years to ensure emergency DC control power.
| MLWMPHSTF ML M HS TUNNEL FIRE CAPITAL | 31547.99 | 219776.35 | 251324.34 | Component replacement caused by tunnel fire in 2024.
Fuel | MLWMPOCOM ML M Out Conv Component Repl | 36532.16 | 233085.77 | 269617.93 | Replace aging conveyer structures.
Fuel Systems Group | MLWMPBELT ML M Conveyor Belt Rplcmts | 227949.77 | 1249790.99 | 1477740.76 | Routine replacement of conveyor belts for lime gypsum and coal.
| MLWMPCHUT ML M Chute Replacements | 145792.35 | 743324.86 | 889117.21 | Routine complete replacement of chutes for lime, gypsum, and coal.
| MLWMPHEAT ML M Heat Trace Instl/Rplc | 33350.35 | 174762.59 | 208112.94 | Install new heat trace for winterization.
| MLWMPPUMP ML M CY Pump Replace Cap >10HP | 43746.86 | 258123.8 | 301870.66 | Replace leachate and sump pumps to maintain environmental compliance.
| MLWSPPULV ML S Pulverizer Rebuilds | 400754.34 | 2199513.96 | 2600268.3 | Routine pulverizer rebuilds to ensure coal fineness and combustion.
| MLWMPVALV ML M CY Valve Replacements | 18170.93 | 100176.33 | 118347.26 | Replace failing regulating and isolation valves in the coal yard and landfill.
| MLWMPOTHR ML M Other Non-Outage PPB | 25346.98 | 169260.91 | 194607.89 | Miscellaneous unit repairs not covered by other projects.
Generator & Support Systems | MLWEP0DCS ML E U0 Ovation DCS Upgrade | 131688.78 | 634608.61 | 766297.39 | The existing DCS system relied on obsolete hardware and software.
| MLWEP1DCS ML E U1 Ovation DCS Upgrade | 115789.88 | 558172.61 | 673962.49 | The existing DCS system relied on obsolete hardware and software.
| MLWEP2DCS ML E U2 Ovation DCS Upgrade | 117579.01 | 566642.19 | 684221.2 | The existing DCS system relied on obsolete hardware and software.
| MLWEPCTRL ML E Control Upgds Rplcmts | 249953.7 | 1510451.66 | 1760405.36 | Replace unit critical control systems to maintain unit performance.
| MLWEPDGHR ML E Doghouse Rectifier | 29952.5 | 148194.63 | 178147.13 | The replacement rectifiers are air cooled instead of water cooled. This reduces the chance of a leak which would force the unit out of service.
| MLWEPFTCL ML E Flash Tank Controls | 35928.48 | 216689.08 | 252617.56 | Replaced obsolete control hardware that could not be maintained.
| MLWEPMOTR ML E Motor Rewind/Rplc >10HP | 72313.31 | 445667.01 | 517980.32 | Rebuild and replace unit critical motors to maintain performance.
| MLWEPPUMP ML E Pump Replacements | 317225.78 | 1838777.67 | 2156003.45 | Rebuild and replace unit critical pumps to maintain performance.
| MLWEPSERV ML E Server Replacements | 100960.84 | 501165.02 | 602125.86 | Replaced obsolete servers to address cybersecurity concerns.
| MLWEPSWGR ML E Switchgear Breaker Rplcmt | 118899.54 | 628220.15 | 747119.69 | Upgraded obsolete Unit 2 CC2S2 main unit disconnect with modern hardware.
| MLWEPTRMT ML E Transmitter Replacements | 46009.79 | 299324.7 | 345334.49 | Replace unit critical transmitters used for control and monitoring.
| MLWEPCABL ML E Cable Replacements | 15283.51 | 87146.59 | 102430.1 | Replaced damaged or failing cables for unit control.
| MLWMPCOMP ML M CY Conv Component Repl | 68541.51 | 443096.7 | 511638.21 | Replace aging conveyer structures.
| MLWEPTFRM ML E Transformers | 82699.93 | 551566.82 | 634266.75 | Replaced failed PPT transformer for Unit 1 exciter.
| MLWEPAIRD ML E Air Dryer Install Replace | 15615.64 | 108715.33 | 124330.97 | Replaced aging equipment to reduce control air moisture for winter weather preparedness.
| MLWMPROTO ML M Roto Booster Fan Replace | 60073.02 | 418431.07 | 478504.09 | Required to ensure flammable gasses are removed from the coal handling areas.
| MLWSPSBSR MLP STACK BREACH CASING REPL | 47095.69 | 345351.56 | 392447.25 | Repaired leaking duct work causing ID fan performance issues and unit curtailments.
Industrial Safety | MLWEPDFPM ML E Diesel Fire Pump Replace | 125295.57 | 745675.22 | 870970.79 | The original engines were obsolete and unable to be repaired. Replacement was required to meet NFPA requirements.
| MLWEPLGHT ML E Lighting Replacements | 68705.53 | 358151.33 | 426856.86 | Upgrading lighting to LED to reduce auxiliary loading and improve visibility in the plant for personnel safety.
Main Generator System | MLWEP1GGB ML E U1 Gen Gas Baffle Purch | 124757.7 | 887180.03 | 1011937.73 | The in service gas baffles had damage from excessive vibration. The new baffles restored the generator rotor clearance to the OEM requirement to ensure proper rotor cooling.
| MLWEP1GNI ML E U1 Generator Field Out In | 110307.74 | 812795.34 | 923103.08 | The in service rotor had shorted winding turns resulting in elevated vibration which curtailed the unit.
Main Turbine System | MLWEP2LAI ML E U2 LPA Turb Insp | 266203.86 | 1303903.74 | 1570107.6 | The running rotor had reached the end of it's run cycle, continued operation would have an increased probability of L-0 blade failure.
| MLWEP2LBI ML E U2 LPB Turb Insp | 218887.75 | 1070461.48 | 1289349.23 | The running rotor had reached the end of it's run cycle, continued operation would have an increased probability of L-0 blade failure.
| MLWEPMTRL ML E Main Trb Redundnt LVDT | 31331.34 | 163467.54 | 194798.88 | Increase the reliability of the turbine control valves by replacing the LVDTs. These instruments provide valve position feedback. Failure would result in a unit curtailment.
| MLWES1BTI ML1 E BFPT INSPECTION | 42015.17 | 304125.83 | 346141 | The running rotor had reached the end of their run cycle, continued operation would have an increased probability of L-0 blade failure.
| MLWEC1VHL ML E U1 VHP/HP&LPA Turbn Insp | 582966.7 | 3273003.66 | 3855970.36 | The running rotor had reached the end of their run cycle, continued operation would cause a decrease in turbine efficiency and increased probability of blade failure.
| MLWEP2LA1 ML2 E LPA L1 Rotor Repr at CMS | 86748.59 | 581104.79 | 667853.38 | The rotors removed from service require replacement L-0 and L-1 blades before they can be placed back in service. Expected to be used during the next Amos rotor inspection.
| MLWEP2LB0 ML2 E LPB L0 Rotor Repr at CMS | 271139.45 | 1816288.55 | 2087428 | The rotors removed from service require replacement L-0 and L-1 blades before they can be placed back in service. Expected to be used during the next Amos rotor inspection.
| MLWEP2LA0 ML2 E LPA L0 Rotor Repr at CMS | 271139.45 | 1816288.55 | 2087428 | The rotors removed from service require replacement L-0 and L-1 blades before they can be placed back in service. Expected to be used during the next Amos rotor inspection.
| MLWEP2LB1 ML2 E LPB L1 Rotor Repr at CMS | 86748.59 | 581104.79 | 667853.38 | The rotors removed from service require replacement L-0 and L-1 blades before they can be placed back in service. Expected to be used during the next Amos rotor inspection.
Precipitator | MLWPC2ESP ML PCC U2 ESP Upgrades | 558790.27 | 3682090.97 | 4240881.24 | Installed new purge air heaters to prevent corrosion in the precipitator structure and TR sets.
SCR | MLWVC2CL4 ML V U2 Catalyst Layer 4 Rplc | 213011.96 | 1040464.52 | 1253476.48 | The in service catalyst had reached end of life, replacement was required for environmental compliance.
| MLWVC1CL1 Mitchell U1 SCR Catalyst L1 | 322198.41 | 2257007.57 | 2579205.98 | The in service catalyst had reached end of life, replacement was required for environmental compliance.
Stm, Condensate, FeedwtrSysGrp | MLWEPBFPB ML E BFP Rebuild Removed (Cap) | 144181 | 418062.79 | 562243.79 | The pump rotating element was replaced to restore pump efficiency.
Telecommunications | ITCB413W0 KENTUCKY POWER - GEN | 31620.02 | 161845.92 | 193465.94
Turbine & Support Systems | MLWEPTURB ML E Trb Brg, Rtr, Shaft Rbld | 22337.81 | 165226.28 | 187564.09
Grand Total |  | 20415084.17 | 118369219.76 | 138784303.93

## Capital Install Dates
Site ID | Status | WO Description | Maximo Work Order Number | GL Project | GL Account | In Service Date | Actual Dollars | Material Cost | Labor Cost | Other Cost
MLP | CLOSE | STORES TOOLS GEN PLT BLKT WPCO 413 MRO VENDING MACHINE EXPANSION MITCHELL PLANT | E10867807 | 000026231 | 1070001 | 2025-02-28
MLP | CLOSE | STORES TOOLS GEN PLT BLKT WPCO 413 MRO VENDING MACHINE EXPANSION MITCHELL PLANT | E10764097 | 000026231 | 1070001 | 2025-02-28
MLP | INSERV | MLP U1: CLINKER GRINDER, MOTOR, & GATE UPGRADE | E10712699 | MLW1CGRPL | 1070001 | 2025-05-13 | 2185453.39 | 310774.97 | 1335849.48 | 538828.94
MLP | INSERV | ML U1 Cooling Tower | E10608669 | MLWEC1CTF | 1070001 | 2023-12-06 | 8780525.34 | 114967.31 | 7919476.48 | 746081.55
MLP | CLOSE | MLU1 HP/VHP TURBINE ROTOR INSP & REPLACEMENT | E10634457 | MLWEC1VHL | 1070001 | 2024-01-29 | 2242528.3 | 684217.58 | 648389.51 | 909921.21
MLP | CLOSE | MLU1 LPA TURBINE ROTOR INSP & REPLACEMENT | E10634268 | MLWEC1VHL | 1070001 | 2024-01-29 | 1655651.7 | 388915.17 | 589809.24 | 676927.29
MLP | CLOSE | MLU0 OVATION DCS UPGRADE | E10539567 | MLWEP0DCS | 1070001 | 2022-12-14 | 1086876.88 | 14874.82 | 1006981.42 | 65020.64
MLP | CLOSE | MLU1 OVATION DCS UPGRADE | E10539568 | MLWEP1DCS | 1070001 | 2022-12-14 | 949736.62 | 26681.49 | 865466.79 | 57588.34
MLP | COMP | MLP U1: Generator Gas Baffles Purchase | E10840929 | MLWEP1GGB | 1070001 | 2025-05-09 | 1456501.27 | 861713.72 | 323580.45 | 271207.1
MLP | INSERV | MLP U1: GENERATOR FIELD OUT INSPECTION | E10863838 | MLWEP1GNI | 1070001 | 2025-06-10 | 2000532.5 | 223907.73 | 641501.25 | 1135123.52
MLP | CLOSE | MLU2 OVATION DCS UPGRADE | E10539569 | MLWEP2DCS | 1070001 | 2022-12-14 | 972173.95 | 14023.94 | 900400.83 | 57749.18
MLP | CLOSE | MLU2 LPA DOGBONE EXPANSION JOINTS (4) REPLACE | E10539548 | MLWEP2LAI | 1070001 | 2022-11-30 | 188415.59 | 94618.77 | 83308.34 | 10488.48
MLP | CLOSE | MLU2 LPA TURBINE ROTOR INSP & REPLACEMENT | E10539524 | MLWEP2LAI | 1070001 | 2022-12-01 | 1677320.15 | 91486.93 | 867554.02 | 718279.2
MLP | CLOSE | MLU2 LPB DOGBONE EXPANSION JOINTS (4) REPLACE | E10539549 | MLWEP2LBI | 1070001 | 2022-11-30 | 106288.32 | 36851.16 | 65481.99 | 3955.17
MLP | CLOSE | MLU2 LPB TURBINE ROTOR INSP & REPLACEMENT | E10539525 | MLWEP2LBI | 1070001 | 2022-12-01 | 1448935.54 | 376814.16 | 365871.9 | 706249.48
MLP | COMP | MLP U1: CONTROL AIR DRYER | E10840169 | MLWEPAIRD | 1070001 | 2025-05-19 | 86387.94 | 58965.97 | 22774.69 | 4647.28
MLP | COMP | MLP - U2: BFP ROTATING ELEMENT REBUILD | E10712686 | MLWEPBFPB | 1070001 | 2024-12-19 | 365306.48 | 233546.86 | 49530.17 | 82229.45
MLP | CLOSE | MLU1 Replace Shaft & 1st Stage Impellor on BFP Element removed in 2021 | E10539510 | MLWEPBFPB | 1070001 | 2022-11-09 | 217647.39 | 188924 | 19730.54 | 8992.85
MLP | CLOSE | MLU2 BFP ROTATING ELEMENT (CSP) REPLACEMENT | E10539547 | MLWEPBFPE | 1070001 | 2022-11-01 | 59144.8 | 8562.48 | 35737.32 | 14845
MLP | CLOSE | MLP U1: BOILER SWING RECEPTACLES | E10870871 | MLWEPCABL | 1070001 | 2025-02-21 | 18069.85 | 3539.76 | 13583.4 | 946.69
MLP | CLOSE | MLP U2: INSTALL CONDENSER CORROSION MONITOR & POWER SUPPLY | E10797885 | MLWEPCABL | 1070001 | 2024-08-07 | 6745.95 | 244.52 | 6175.84 | 325.59
MLP | CLOSE | MLP - U1: PULL NEW CABLE TO KINNEAR DOOR 69 ON TBG-B | E10736536 | MLWEPCABL | 1070001 | 2024-05-01 | 9297.26 | 805.42 | 7570.42 | 921.42
MLP | CLOSE | MLP U1: #12 DRIP TANK POWER FEED REPLACEMENT | E10722602 | MLWEPCABL | 1070001 | 2023-12-15 | 19267.65 | 2425.1 | 16023.15 | 819.4
MLP | CLOSE | MLU0 INSTALL PWR SUPPLY EMERGENCY FUEL TANK SHUT OFF'S | E10680559 | MLWEPCABL | 1070001 | 2023-09-22 | 9415.4 | 354.91 | 8875.23 | 185.26
MLP | CLOSE | MLU1 HYDROGEN SEAL OIL PP WIRE PULL | E10648477 | MLWEPCABL | 1070001 | 2024-03-13
MLP | CLOSE | MLU2 Pull New Cable to Generator Bus Duct Fan 2 From MCC | E10641262 | MLWEPCABL | 1070001 | 2023-05-21 | 6764.58 | 606.69 | 6083.97 | 73.92
MLP | CLOSE | MLU2 HOTWELL SUBPANEL CONDUCTIVITY TRANSMITTERS | E10634843 | MLWEPCABL | 1070001 | 2023-11-01 | 9692.59 | 8612 | 0 | 1080.59
MLP | CLOSE | MLU0 FOSTER WHEELER BLDG 208Y FEED- RM 115 | E10568722 | MLWEPCABL | 1070001 | 2023-01-08 | 6195.23 | 258 | 5782.66 | 154.57
MLP | CLOSE | MLU2 FFC-1 SENSING LINES HEAT TRACE CABLE REPLACE | E10539530 | MLWEPCABL | 1070001 | 2022-12-28 | 9065.34 | 3255.42 | 5607.32 | 202.6
MLP | CLOSE | MLU1 FFC-1 SENSING LINES HEAT TRACE CABLE REPLACE | E10539529 | MLWEPCABL | 1070001 | 2022-12-28 | 8185.02 | 2820.12 | 5135.4 | 229.5
MLP | INPRG | MLP U2: SLAGBLOWER PLC CONTROLLER REPLACEMENT | E10925653 | MLWEPCTRL | 1070001 |  | 6974.13 | 5870.1 | 417.66 | 686.37
MLP | COMP | MLP U2: Replace Dewpoint Transmitter | E10908710 | MLWEPCTRL | 1070001 | 2025-05-27 | 4611.24 | 4329.9 | 0 | 281.34
MLP | INPRG | MLP U2: KRV-521 CONTROLLER REPLACEMENT | E10899429 | MLWEPCTRL | 1070001 |  | 24659.17 | 19033.25 | 3725.37 | 1900.55
MLP | COMP | MLP U2: #21 NASH PUMP MAGNETROL REPLACEMENT | E10894359 | MLWEPCTRL | 1070001 | 2025-06-10 | 3656.57 | 2958.04 | 451.65 | 246.88
MLP | COMP | MLP U2: KRV-541 CONTROLLER REPLACEMENT | E10894358 | MLWEPCTRL | 1070001 | 2025-05-27 | 7576.86 | 4713.59 | 2423.48 | 439.79
MLP | INPRG | MLP U0: PURCHASE SPARE BUS MULTILIN RELAYS | E10890169 | MLWEPCTRL | 1070001 |  | 22880.79 | 21155 | 0 | 1725.79
MLP | CLOSE | MLP U0: BACKUP COMMUNICATION MODULE REPLACE | E10879559 | MLWEPCTRL | 1070001 | 2025-03-04 | 3839.55 | 3263.54 | 378.01 | 198
MLP | COMP | MLP U0: OX AIR BLOWER A PLC REPLACEMENT | E10872917 | MLWEPCTRL | 1070001 | 2025-05-01 | 7329.82 | 6897.82 | 0 | 432
MLP | CLOSE | MLP U2: DBA TRAIN 2 PLUGGED CHUTE ALARM | E10869736 | MLWEPCTRL | 1070001 | 2025-02-10 | 3564.49 | 2076.8 | 1314.28 | 173.41
MLP | CLOSE | MLP U1: ASH PIT SUMP LEVEL CONTROL UPGRADE | E10868092 | MLWEPCTRL | 1070001 | 2025-02-26 | 8626.23 | 5622.05 | 2539.24 | 464.94
MLP | CLOSE | MLP U0: REPLACE FILTER PRESS 3 HMI | E10841270 | MLWEPCTRL | 1070001 | 2024-12-12 | 7064.86 | 2898.01 | 3921.9 | 244.95
MLP | CLOSE | MLP U2: RRV520 CONTROLLER REPLACEMENT | E10835886 | MLWEPCTRL | 1070001 | 2025-03-04 | 6475.67 | 5519.25 | 408.54 | 547.88
MLP | CLOSE | MLP U1: Upgrade DBA Sump Pump Level Controls | E10830310 | MLWEPCTRL | 1070001 | 2025-01-21 | 12951.56 | 6751.66 | 5120.89 | 1079.01
MLP | CLOSE | MLP U1 GRV-9092: REPLACE INDICATION | E10823805 | MLWEPCTRL | 1070001 | 2024-10-29 | 2391.85 | 1633 | 636.89 | 121.96
MLP | CLOSE | MLP U1: Replace Touch Screen on Air Compressor #13 | E10820964 | MLWEPCTRL | 1070001 | 2024-10-15 | 5167.08 | 3240.83 | 1652.6 | 273.65
MLP | CLOSE | MLU1 REPLACE DBA Sump PP 3 Controller | E10796968 | MLWEPCTRL | 1070001 | 2024-08-05 | 4648.22 | 3551.6 | 955.09 | 141.53
MLP | CLOSE | MLP U2: SILICA ANALYZER REPLACEMENT | E10769856 | MLWEPCTRL | 1070001 | 2024-11-26 | 26715.51 | 22102.83 | 4000 | 612.68
MLP | CLOSE | MLP U2: PURCHASE U2 COMPRESSED AIR FLOW METER | E10769213 | MLWEPCTRL | 1070001 | 2024-09-05 | 23326.59 | 15690.32 | 3604.65 | 4031.62
MLP | COMP | MLP U1: PURCHASE U1 COMPRESSED AIR FLOW METER | E10769206 | MLWEPCTRL | 1070001 | 2024-12-17 | 39726.8 | 16326.91 | 19267.63 | 4132.26
MLP | CLOSE | MLP U2: EHC CONDITIONING UNIT INSTALL | E10754872 | MLWEPCTRL | 1070001 | 2024-06-03 | 57549.44 | 3596.24 | 42787.86 | 11165.34
MLP | CLOSE | MLP - MLU1 LABOR TO INSTALL EHC CONDITIONING UNIT | E10736638 | MLWEPCTRL | 1070001 | 2024-06-03 | 38674.16 | 3136.03 | 30221.84 | 5316.29
MLP | CLOSE | MLP - U1 RRV-1 DVC POSITIONER REPLACEMENT | E10735747 | MLWEPCTRL | 1070001 | 2024-06-11 | 7611.01 | 5969.58 | 915.16 | 726.27
MLP | CLOSE | MLP U2: EHC CONDITIONING UNIT PURCHASE | E10720474 | MLWEPCTRL | 1070001 | 2023-12-20 | 51651.63 | 49812.5 | 0 | 1839.13
MLP | CLOSE | MLP U1: EHC CONDITIONING UNIT PURCHASE | E10720468 | MLWEPCTRL | 1070001 | 2024-03-26 | 49666.92 | 47000 | 0 | 2666.92
MLP | CLOSE | MLP - U0: DFA SILO PANEL VIEW REPLACEMENT | E10710530 | MLWEPCTRL | 1070001 | 2024-04-05 | 9713.06 | 8274.82 | 661.88 | 776.36
MLP | CLOSE | MLU0 GRV-9764 DVC 2000 CONTROLLER | E10695079 | MLWEPCTRL | 1070001 | 2024-09-30 | 6943.82 | 5255.64 | 1202.25 | 485.93
MLP | CLOSE | MLU0 FILTER PRESS 1 HMI REPLACEMENT | E10690099 | MLWEPCTRL | 1070001 | 2024-02-05 | 3699.22 | 2780.54 | 646.1 | 272.58
MLP | CLOSE | MLU2 Well Water Head Tank Level Indication Replace | E10687111 | MLWEPCTRL | 1070001 | 2023-09-25 | 3526.36 | 2183 | 1251.29 | 92.07
MLP | CLOSE | MLU1 - Replace BMO-4 Indication Bargraph | E10678168 | MLWEPCTRL | 1070001 | 2024-08-26 | 15148.54 | 12823.82 | 1126.63 | 1198.09
MLP | CLOSE | MLU1 Replace Stepdown Transformer for GSU Cooling Fans | E10649402 | MLWEPCTRL | 1070001 | 2023-06-22 | 8369.15 | 4378.57 | 3799.53 | 191.05
MLP | CLOSE | MLU2 EHC TRIP HEADER PRESSURE TRANSMITTER REPLACE | E10647864 | MLWEPCTRL | 1070001 | 2023-10-26 | 3978.71 | 3477 | 373.74 | 127.97
MLP | CLOSE | MLU2 PRECIP CONTROL AIR HEAT TRACE INSTALL | E10643899 | MLWEPCTRL | 1070001 | 2023-11-03 | 69813.15 | 5597.67 | 61607.88 | 2607.6
MLP | CLOSE | MLU2 PURCHASE 2 SERVO MANIFOLDS ON CONTROL VALVES | E10642753 | MLWEPCTRL | 1070001 | 2023-05-31 | 30346.31 | 30000 | 0 | 346.31
MLP | CLOSE | MLU0 Replace Temperature Monitor on 51A Transformer | E10633409 | MLWEPCTRL | 1070001 | 2023-10-09 | 9813.76 | 8287.44 | 1448.87 | 77.45
MLP | CLOSE | MLU2 PRECIP TR SET CONTROL MODULE | E10593837 | MLWEPCTRL | 1070001 | 2023-05-04 | 12030.27 | 11500 | 0 | 530.27
MLP | CLOSE | MLU0 HEAT TRACE & WINTERIZATION INSTALLATION | E10576409 | MLWEPCTRL | 1070001 | 2023-05-04 | 83356.34 | 52542.68 | 30248.02 | 565.64
MLP | CLOSE | MLU2 INSTALL PRECIP CONTROL AIR HEAT TRACE | E10575680 | MLWEPCTRL | 1070001 | 2023-05-04 | 22332.79 | 2582.12 | 19380.19 | 370.48
MLP | CLOSE | MLU2 BATTERY ROOM CONDENSATE LINE INSTALL | E10572818 | MLWEPCTRL | 1070001 | 2023-05-08 | 17189.39 | 0 | 16054.49 | 1134.9
MLP | CLOSE | MLU1 BATTERY ROOM CONDENSATE LINE INSTALL | E10572814 | MLWEPCTRL | 1070001 | 2023-05-04 | 29754.84 | 431.9 | 27315.82 | 2007.12
MLP | CLOSE | MLU 1 & U2 DFA XFER STN CTRL AIR HEAT TRACE INSTALL | E10571827 | MLWEPCTRL | 1070001 | 2023-05-04 | 68931.32 | 11344.94 | 54558.99 | 3027.39
MLP | CLOSE | MLU0 INSTALL NEW VFD'S ON HS BELTS | E10567471 | MLWEPCTRL | 1070001 | 2023-12-05 | 98557.86 | 60292.62 | 31288.05 | 6977.19
MLP | CLOSE | MLU0 FGD VAC BELT A VFD REPLACEMENT | E10549400 | MLWEPCTRL | 1070001 | 2023-04-26
MLP | CLOSE | MLU0 CPS #3 LP & HP SLUDGE PUMPS VFD UPGRADES | E10549388 | MLWEPCTRL | 1070001 | 2023-10-27 | 29647.54 | 25276.2 | 2653.07 | 1718.27
MLP | CLOSE | MLU0 FGD VAC BELT #3 VFD REPLACEMENT | E10545020 | MLWEPCTRL | 1070001 | 2022-12-21 | 12694.95 | 9266.9 | 2862.36 | 565.69
MLP | CLOSE | MLU2 INSTALL CABLE/CONDUIT TO NETWORK STOCK COAL FEEDERS | E10539551 | MLWEPCTRL | 1070001 | 2022-10-11 | 23346.28 | 837.11 | 20997.58 | 1511.59
MLP | CLOSE | MLU1 INSTALL CABLE/CONDUIT TO NETWORK STOCK COAL FEEDERS | E10539550 | MLWEPCTRL | 1070001 | 2022-10-11 | 24878.98 | 4401 | 18794.22 | 1683.76
MLP | CLOSE | MLU0 DROP 122 POWER SUPPLY | E10539511 | MLWEPCTRL | 1070001 | 2022-10-01 | 2984.23 | 2834 | 0 | 150.23
MLP | CLOSE | MLU0 Install 4-East and 4-West Coal Conveyor Soft Starters | E10539500 | MLWEPCTRL | 1070001 | 2023-11-17 | 189310.93 | 67609.49 | 100696.66 | 21004.78
MLP | CLOSE | MLU0 FUEL OIL STORAGE TANK LEVEL PROBE/PROCESSOR | E10539473 | MLWEPCTRL | 1070001 | 2023-11-21 | 4336.83 | 4023 | 0 | 313.83
MLP | CLOSE | MLU2 #23 AIR COMP INNER STAGE COOLERS REPLACEMENT | E10539472 | MLWEPCTRL | 1070001 | 2022-12-14 | 21276.29 | 18469 | 0 | 2807.29
MLP | CLOSE | MLP U2: 22B CIRC WATER PUMP REBUILD | E10797898 | MLWEPCWPM | 1070001 | 2024-10-14 | 128440.5 | 52022.96 | 43078.34 | 33339.2
MLP | CLOSE | MLP U2: 22A CIRC WATER PUMP REBUILD | E10797890 | MLWEPCWPM | 1070001 | 2024-10-14 | 152167.12 | 108913.44 | 21257 | 21996.68
MLP | CLOSE | MLP - 12A CIRCULATING WATER PUMP | E10747369 | MLWEPCWPM | 1070001 | 2024-05-27 | 183071.51 | 92913.46 | 39140.77 | 51017.28
MLP | CLOSE | MLP - 12B CIRCULATING WATER PUMP | E10732312 | MLWEPCWPM | 1070001 | 2024-02-27 | 129061.49 | 85477.27 | 25633.07 | 17951.15
MLP | CLOSE | MLU2 21B CIRC WATER PUMP SHAFT REPLACEMENT | E10601053 | MLWEPCWPM | 1070001 | 2023-05-05 | 149546.51 | 84218.66 | 41532.54 | 23795.31
MLP | CLOSE | MLU1 11B CIRC WATER PUMP SHAFT REPLACEMENT | E10601045 | MLWEPCWPM | 1070001 | 2023-05-05 | 192704.77 | 115453.19 | 50757.58 | 26494
MLP | COMP | MLU2 DIESEL ENGINE FIRE PUMP & MOTOR REPLACE | E10611410 | MLWEPDFPM | 1070001 | 2025-05-27 | 305054.88 | 142797.77 | 128267.62 | 33989.49
MLP | COMP | MLU2 DIESEL ENGINE FIRE PUMP FUEL TANK REPLACE | E10611402 | MLWEPDFPM | 1070001 | 2025-05-27 | 178090.86 | 21647.15 | 136534.84 | 19908.87
MLP | COMP | MLU1 DIESEL FIRE PUMP & MOTOR REPLACEMENT | E10539513 | MLWEPDFPM | 1070001 | 2024-07-25 | 465514.17 | 155206.59 | 217448.03 | 92859.55
MLP | CLOSE | MLU2 RECTIFIER BRIDGE REPLACEMENT | E10539544 | MLWEPDGHR | 1070001 | 2023-02-02 | 244493.85 | 162585.71 | 68228.03 | 13680.11
MLP | CLOSE | MLU2 SLAG BLOWER PLC AND FIBER PULLS | E10539515 | MLWEPFTCL | 1070001 | 2024-10-10 | 237606.09 | 89893.89 | 103330.7 | 44381.5
MLP | CLOSE | MLU1 SLAG BLOWER PLC & FIBER PULLS | E10539514 | MLWEPFTCL | 1070001 | 2024-05-31 | 218374.59 | 58461.35 | 94193.69 | 65719.55
MLP | INPRG | MLP U0: FGD ELEVATOR RM HVAC REPLACEMENT | E10888121 | MLWEPHVAC | 1070001 |  | 13719.39 | 5004.73 | 7467.99 | 1246.67
MLP | INPRG | MLP U0: REPLACE HEAT PUMP AT CFB | E10878577 | MLWEPHVAC | 1070001 |  | 66036.4 | 46809.05 | 12997.79 | 6229.56
MLP | COMP | MLP U0: WINDOW HVAC UNIT - CONEX RR - OLD TRLR PARK | E10869749 | MLWEPHVAC | 1070001 | 2025-03-10 | 2468.61 | 1967.73 | 353.1 | 147.78
MLP | COMP | MLP U0: OFFICE ZONE 2 UNIT 24 HVAC REPLACEMENT | E10829676 | MLWEPHVAC | 1070001 | 2025-05-09 | 60120.99 | 44951.88 | 11188.97 | 3980.14
MLP | CLOSE | MLP U0: GAURD HOUSE HVAC REPLACEMENT | E10824558 | MLWEPHVAC | 1070001 | 2024-11-05 | 2792.02 | 2307.99 | 420 | 64.03
MLP | CLOSE | MLP U0: SERVICE BLDG 2ND FLOOR HVAC UNIT REPLACE | E10795823 | MLWEPHVAC | 1070001 | 2024-11-07 | 52000.9 | 41370.86 | 7344.17 | 3285.87
MLP | CLOSE | MLP U1: AUX BOILER MCC AC COND UNIT REPLACEMENT | E10779543 | MLWEPHVAC | 1070001 | 2024-10-25 | 16637.2 | 11734.1 | 4416.41 | 486.69
MLP | CLOSE | MLP U0: UREA BLDG MCC RM MARVAIR AC UNIT REPLACE | E10779541 | MLWEPHVAC | 1070001 | 2024-10-15 | 20365.66 | 16031.81 | 3830.32 | 503.53
MLP | CLOSE | MLP U2: LABOR TO I/R CR & DCS RM HVAC | E10750208 | MLWEPHVAC | 1070001 | 2024-05-13 | 120122.57 | 28259.62 | 77241.51 | 14621.44
MLP | COMP | MLP U1: LABOR TO I/R CR & DCS RM HVAC | E10750190 | MLWEPHVAC | 1070001 | 2024-05-23 | 98876.71 | 24375.82 | 62972.07 | 11528.82
MLP | CLOSE | MLP - U0: LABOR TO I/R RSO BREAK ROOM HVAC | E10750182 | MLWEPHVAC | 1070001 | 2024-09-17 | 5757.22 | 2033 | 3360 | 364.22
MLP | CLOSE | MLP - U1 OH LUMEX MERC MONITOR HVAC REPLACEMENT | E10700453 | MLWEPHVAC | 1070001 | 2023-12-06 | 5007.06 | 4857.83 | 0 | 149.23
MLP | CLOSE | MLU2 CR & DCS RM HVAC UNIT REPLACEMENT | E10572732 | MLWEPHVAC | 1070001 | 2023-11-15 | 75538.51 | 66350.7 | 3268.26 | 5919.55
MLP | CLOSE | MLU0 RSO BREAK ROOM HVAC REPLACEMENT | E10572455 | MLWEPHVAC | 1070001 | 2023-11-15 | 42488.38 | 39999.17 | 0 | 2489.21
MLP | CLOSE | MLU1 CR & DCS ROOM HVAC UNIT REPLACEMENT | E10572451 | MLWEPHVAC | 1070001 | 2023-11-15 | 70572.92 | 66438.33 | 0 | 4134.59
MLP | CLOSE | MLU0 PLANT JANITOR ROOM / SHOWER HVAC REPLACEMENT | E10539546 | MLWEPHVAC | 1070001 | 2022-09-26 | 21739.7 | 1531.2 | 19188.3 | 1020.2
MLP | CLOSE | MLU0 PURCH & INST NEW AC/HEATPUMP ON RIVER BARGE CRANE | E10539475 | MLWEPHVAC | 1070001 | 2022-10-05 | 4907 | 2620 | 2040 | 247
MLP | INPRG | MLP U0: EMERGENCY LIGHTING BATTERY BANK REPLACEMENT | E10802604 | MLWEPLGHT | 1070001 |  | 72752.69 | 53971.9 | 11410.91 | 7369.88
MLP | CLOSE | MLU1 PRECIP LIGHTING UPGRADES | E10646178 | MLWEPLGHT | 1070001 | 2023-09-21
MLP | CLOSE | MLU0 Replace Stacker MCC Lighting (New conduit, receptables, lights, and wiring) | E10633395 | MLWEPLGHT | 1070001 | 2023-06-09 | 13226.95 | 1820.24 | 11156.35 | 250.36
MLP | CLOSE | MLU0 HRC3 LIGHTING INSTALLATION | E10630137 | MLWEPLGHT | 1070001 | 2023-05-24 | 13440.71 | 2033.37 | 11530.62 | -123.28
MLP | CLOSE | MLU0 INSTALL LIGHTS ON BC-9 FOR FUEL OIL UNLOADING | E10619507 | MLWEPLGHT | 1070001 | 2023-06-14 | 13458.93 | 1682.32 | 11311.3 | 465.31
MLP | CLOSE | MLU1 PURCHASE/INSTALL TURBINE ROOM LIGHTS | E10552618 | MLWEPLGHT | 1070001 | 2023-04-29 | 335495.47 | 199236.4 | 120400.1 | 15858.97
MLP | COMP | MLP U2: LABOR TO I/R 23 CONDENSATE BOOSTER PUMP MOTOR (CSP) | E10899661 | MLWEPMOTR | 1070001 | 2025-05-13 | 21539.67 | 16966.27 | 3096.15 | 1477.25
MLP | CLOSE | MLP U2: 22 ASH WATER PUMP MOTOR REPLACE | E10879889 | MLWEPMOTR | 1070001 | 2025-03-07 | 2552.81 | 0 | 2910.01 | -357.2
MLP | CLOSE | MLP FGD: Replace Ball Mill A Reducer Skid Motor | E10876094 | MLWEPMOTR | 1070001 | 2025-02-07 | 8122.08 | 6787 | 875.24 | 459.84
MLP | CLOSE | MLP U1: #13 FILTERED WATER PUMP MOTOR REPLACEMENT | E10863802 | MLWEPMOTR | 1070001 | 2025-01-10 | 3630.86 | 2205.53 | 1124.01 | 301.32
MLP | CLOSE | MLP U2: #21 AIR COMPRESSOR MOTOR REPLACEMENT | E10838769 | MLWEPMOTR | 1070001 | 2025-03-18 | 74467.12 | 65700.75 | 5333.96 | 3432.41
MLP | CLOSE | MLP U2: 22 BOOSTER PUMP MOTOR REBUILD | E10834708 | MLWEPMOTR | 1070001 | 2024-12-17 | -823.86 | -823.86 | 0 | 7.1054e-15
MLP | CLOSE | MLP U2: 22 CLINKER GRINGER MOTOR REPLACEMENT | E10834333 | MLWEPMOTR | 1070001 | 2024-11-01 | 2737.36 | 1510 | 1037.09 | 190.27
MLP | CLOSE | MLP U2: 21 CLINKER GRINDER MOTOR REPLACEMENT | E10834309 | MLWEPMOTR | 1070001 | 2024-11-01 | 2656.46 | 1510 | 961.19 | 185.27
MLP | CLOSE | MLP U1: REPLACE #12 CONDENSATE BOOSTER PUMP MOTOR | E10830305 | MLWEPMOTR | 1070001 | 2024-10-09 | 8105.17 | 0 | 7654.08 | 451.09
MLP | CLOSE | MLP U1: UMO-1 MOTOR REPLACMENT | E10823427 | MLWEPMOTR | 1070001 | 2024-10-02 | 2130.09 | 2043.12 | 0 | 86.97
MLP | CLOSE | MLP U1: 13 SOFTENED WATER BOOSTER PUMP MOTOR | E10795548 | MLWEPMOTR | 1070001 | 2024-07-23 | 5452.68 | 2860 | 2013.78 | 578.9
MLP | CLOSE | MLP U1: REPLACE 13 CONDENSATE BOOSTER PUMP MOTOR | E10794526 | MLWEPMOTR | 1070001 | 2024-08-02 | 7473.17 | 0 | 6677.16 | 796.01
MLP | CLOSE | MLP U2: 21 AIR HEATER WASH MOTOR REWIND | E10756001 | MLWEPMOTR | 1070001 | 2024-09-14 | 21810.81 | 16907.8 | 1193 | 3710.01
MLP | CLOSE | MLP U1: 11 ASH WATER PUMP MOTOR/VALVES | E10749873 | MLWEPMOTR | 1070001 | 2024-05-07 | 102810.55 | 68704.33 | 16086.49 | 18019.73
MLP | CLOSE | MLP U1: REPLACE 12 ASH H20 PP MOTOR | E10749160 | MLWEPMOTR | 1070001 | 2024-02-16 | 55983.37 | 55985 | 1339.7 | -1341.33
MLP | CLOSE | MLP - U1 #11 SOFTENED WATER BOOSTER PUMP MOTOR | E10747123 | MLWEPMOTR | 1070001 | 2024-03-07 | 7307.89 | 2802.8 | 3985.08 | 520.01
MLP | CLOSE | MLP - U1: #13 SOFTENED WATER BOOSTER PUMP MOTOR | E10746792 | MLWEPMOTR | 1070001 | 2024-03-05 | 2417.89 | 1519.3 | 730.25 | 168.34
MLP | CLOSE | MLP - U0: ABSORBER AGITATOR 2H MOTOR REPLACEMENT | E10731467 | MLWEPMOTR | 1070001 | 2024-02-20 | 10048.93 | 7955.07 | 1600.13 | 493.73
MLP | CLOSE | MLP U1: LABOR TO I/R 16 PULV MOTOR CSP | E10720449 | MLWEPMOTR | 1070001 | 2023-12-15 | 15635.64 | 128.29 | 11289.59 | 4217.76
MLP | CLOSE | MLP U1: 13 COOLING WATER PUMP MOTOR REPLACE | E10720127 | MLWEPMOTR | 1070001 | 2024-01-19 | 18400.55 | 14541.39 | 2593.13 | 1266.03
MLP | CLOSE | MLP - U0 RO SKID A 2ND STAGE MOTOR REPLACEMENT | E10691062 | MLWEPMOTR | 1070001 | 2023-10-24 | 8705.66 | 5479.11 | 3005.76 | 220.79
MLP | CLOSE | MLU2 - REPLACE HD FIRE PUMP MOTOR | E10689498 | MLWEPMOTR | 1070001 | 2023-09-10 | 21999.23 | 19300 | 2273 | 426.23
MLP | CLOSE | MLU1 - Replace East Clinker Grinder Motor | E10666372 | MLWEPMOTR | 1070001 | 2023-08-11 | 2700.3 | 0 | 2586.52 | 113.78
MLP | CLOSE | MLU1 - Replace West Clinker Grinder Motor | E10666370 | MLWEPMOTR | 1070001 | 2023-08-11 | 6052.23 | 2254 | 3371 | 427.23
MLP | CLOSE | MLU0 R1 CONVEYOR MOTOR REPLACEMENT | E10665586 | MLWEPMOTR | 1070001 | 2023-07-25 | 5826.56 | 2931.57 | 1727.81 | 1167.18
MLP | CLOSE | MLU2 - #21 WWS SUMP PUMP MOTOR REPLACEMENT | E10661299 | MLWEPMOTR | 1070001 | 2023-08-07 | 3460.56 | 2372 | 884.63 | 203.93
MLP | CLOSE | MLU1 - Replace Ash PP 12 Motor | E10649410 | MLWEPMOTR | 1070001 | 2023-06-27 | 38309.02 | 32241.29 | 5386.72 | 681.01
MLP | CLOSE | MLU1 - Replace Service Water Pump 11 | E10644851 | MLWEPMOTR | 1070001 | 2023-07-18 | 2867.58 | 0 | 2669.65 | 197.93
MLP | CLOSE | MLU1 - 13 ASH WATER SUMP PUMP MOTOR REPLACE | E10634250 | MLWEPMOTR | 1070001 | 2024-03-13 | 0 | 0 | 0 | 0
MLP | CLOSE | MLU1 #12 COOLING WATER PUMP MOTOR REPLACE | E10593302 | MLWEPMOTR | 1070001 | 2023-02-02 | 6153.04 | 4600.72 | 1414.24 | 138.08
MLP | CLOSE | MLU1 Replace the Burnt Up Motor _ UMO 1 Super Heater Bypass Block Valve | E10593105 | MLWEPMOTR | 1070001 | 2023-02-02 | 4295.95 | 4167.27 | 0 | 128.68
MLP | CLOSE | MLU1 Replace #11 ash pit sump pump | E10539630 | MLWEPMOTR | 1070001 | 2023-03-14 | 4770.72 | 14.82 | 4444.66 | 311.24
MLP | CLOSE | MLU1 #11 WASTE WATER SUMP PUMP MOTOR | E10539614 | MLWEPMOTR | 1070001 | 2023-03-14 | 975.71 | 0 | 856.85 | 118.86
MLP | CLOSE | MLU0 R10 FAN MOTOR REPLACEMENT | E10539508 | MLWEPMOTR | 1070001 | 2022-09-30 | 4651.76 | 1148.56 | 3223.62 | 279.58
MLP | CLOSE | MLU0 MH #1 CONVEYOR MOTOR REPLACEMENT | E10539453 | MLWEPMOTR | 1070001 | 2024-03-12 | 825.3 | 0 | 734.77 | 90.53
MLP | CLOSE | MLU0 REPLACE 5 FGD EJ FOR NON UNIT PUMPS/TANKS | E10539623 | MLWEPMTRL | 1070001 | 2023-10-09 | 32753.88 | 26999.59 | 3409.82 | 2344.47
MLP | CLOSE | MLU1 REPLACE 1A BLEED PUMP EJ | E10539622 | MLWEPMTRL | 1070001 | 2023-05-03 | 4858.08 | 3824.02 | 391.71 | 642.35
MLP | CLOSE | MLU2 DEMIN FILTER PLC UPGRADE | E10539535 | MLWEPMTRL | 1070001 | 2023-11-22 | 241887.05 | 134557.16 | 80174.6 | 27155.29
MLP | CLOSE | MLU2 PRECIP POWER FEED | E10539540 | MLWEPPTPF | 1070001 | 2022-12-01 | 162872.8 | 79923.69 | 69849.61 | 13099.5
MLP | COMP | MLP U2: 21 CONDENSATE BOOSTER PUMP REPLACE | E10899431 | MLWEPPUMP | 1070001 | 2025-04-28 | 19330.55 | 8704.2 | 9448.77 | 1177.58
MLP | INPRG | MLP U1: 11A CIRCULATING WATER PUMP REBUILD | E10898933 | MLWEPPUMP | 1070001 |  | 59180.58 | 19684.04 | 25831.85 | 13664.69
MLP | COMP | MLP U2: 22B CIRC WATER PUMP REBUILD | E10881140 | MLWEPPUMP | 1070001 | 2025-05-13 | 42085.09 | 5846.83 | 26578.46 | 9659.8
MLP | COMP | MLP U0: LABOR TO I/R CSP RO SKID A 1ST STAGE FEED PUMP | E10869619 | MLWEPPUMP | 1070001 | 2025-01-30 | 1051.89 | 0 | 996.17 | 55.72
MLP | COMP | MLP U1: ASH PIT SUMP PUMP REBUILD | E10840105 | MLWEPPUMP | 1070001 | 2025-05-07 | 44275.05 | 41440 | 131 | 2704.05
MLP | CLOSE | MLP U2: #3 ASH PIT SUMP PUMP REPLACEMENT | E10834360 | MLWEPPUMP | 1070001 | 2024-11-15 | 35995.79 | 33376.97 | 973.19 | 1645.63
MLP | CLOSE | MLP U2 ASH PIT SUMP PUMP 1 REPLACEMENT | E10834344 | MLWEPPUMP | 1070001 | 2025-04-15 | 101328.56 | 85932.54 | 6567.73 | 8828.29
MLP | CLOSE | MLP U2: STATOR WATER PUMP REPLACEMENT | E10829951 | MLWEPPUMP | 1070001 | 2024-12-17 | 0 | 0 | 0 | 0
MLP | CLOSE | MLP U1: LABOR TO MOVE ASH PIT SUMP PUMP U2 TO U1 | E10820742 | MLWEPPUMP | 1070001 | 2024-09-05 | 4221.88 | 22.59 | 4011.49 | 187.8
MLP | CLOSE | MLU1 Ash Pit Sump Pump 2 Replacement | E10796846 | MLWEPPUMP | 1070001 | 2024-12-04 | 107856.92 | 82380 | 17856.92 | 7620
MLP | CLOSE | MLU1 Ash Pit Sump Pump 1 Replacement | E10796845 | MLWEPPUMP | 1070001 | 2024-11-13 | 105764.54 | 84736.25 | 15533.07 | 5495.22
MLP | CLOSE | MLP U2: #23 RDV PUMP REPLACEMENT | E10783909 | MLWEPPUMP | 1070001 | 2024-07-10 | 2550.95 | 0 | 2332.03 | 218.92
MLP | CLOSE | MLU0 Station 1A Sump Pump Replacement | E10764089 | MLWEPPUMP | 1070001 | 2024-04-05 | 40755.43 | 30310.55 | 3393.57 | 7051.31
MLP | CLOSE | MLP U0: RO A 1ST STAGE PUMP REBUILD | E10750313 | MLWEPPUMP | 1070001 | 2024-10-15 | 68854.72 | 54994.2 | 0 | 13860.52
MLP | CLOSE | MLP U1: PURCHASE 4 WWS PUMPS | E10720476 | MLWEPPUMP | 1070001 | 2024-04-10 | 118330.18 | 109611.08 | 0 | 8719.1
MLP | COMP | MLP U2: AT2006E NASH VACUUM PUMP SKID | E10714209 | MLWEPPUMP | 1070001 | 2024-10-17 | 517528.73 | 326241.48 | 158032.92 | 33254.33
MLP | CLOSE | MLU1 #12 HOTWELL PUMP REPLACEMENT | E10683303 | MLWEPPUMP | 1070001 | 2023-10-02 | 15821.22 | 7905.51 | 7503.56 | 412.15
MLP | CLOSE | MLU0 RO SKID B 2ND STAGE PUMP REPLACEMENT | E10680567 | MLWEPPUMP | 1070001 | 2023-09-21 | -0.05 | 0 | 0 | -0.05
MLP | CLOSE | MLU2 WASTE WATER PUMP REPLACEMENT | E10639423 | MLWEPPUMP | 1070001 | 2023-10-31 | 138753.3 | 108614.78 | 17360.78 | 12777.74
MLP | CLOSE | MLU0 Purchase Diesel Trash Pump | E10633430 | MLWEPPUMP | 1070001 | 2023-06-07 | 55698.92 | 56750 | 0 | -1051.08
MLP | CLOSE | MLU1 #12 GLSO Fan replacement | E10630360 | MLWEPPUMP | 1070001 | 2023-08-15
MLP | CLOSE | MLU2 22 EHC PUMP REPLACEMENT | E10618865 | MLWEPPUMP | 1070001 | 2024-10-24 | -629.39 | 0 | -616.47 | -12.92
MLP | CLOSE | MLU1 REPLACE #11 GSLO FAN | E10615599 | MLWEPPUMP | 1070001 | 2023-03-08 | 13217.44 | 11832 | 697.09 | 688.35
MLP | CLOSE | MLP - MLU1 - Replace check valves on Waste Water Sump Pumps #11, #12, and #13 | E10610281 | MLWEPPUMP | 1070001 | 2023-04-26 | 9213.28 | 8326.95 | 286.89 | 599.44
MLP | CLOSE | MLU0 Install 3" sump pump in HS tunnel | E10605002 | MLWEPPUMP | 1070001 | 2023-06-30 | 16168.77 | 14950 | 0 | 1218.77
MLP | CLOSE | MLU0 1ST STAGE REVERSE OSMOSIS SYSTEM PUMP CAP SPARE | E10593846 | MLWEPPUMP | 1070001 | 2023-10-26 | 117340.19 | 62557.72 | 50996.95 | 3785.52
MLP | CLOSE | MLU2 REPLACE #2 ASH PIT SUMP PUMP | E10590875 | MLWEPPUMP | 1070001 | 2023-01-26 | 63284.27 | 60467 | 1221.14 | 1596.13
MLP | CLOSE | MLU0 DIESEL TRASH PUMP PURCHASE | E10553487 | MLWEPPUMP | 1070001 | 2023-02-06 | 50688.41 | 49170 | 0 | 1518.41
MLP | CLOSE | MLP REPLACE 4 RIVER WTR ROOT VLVS BTTM ASH CNVSN PRJCT BOTH UNITS | E10552396 | MLWEPPUMP | 1070001 | 2022-10-13 | 10575.45 | 10182.94 | 0 | 392.51
MLP | CLOSE | MLU0 Replace #1 RWMU Pump | E10539632 | MLWEPPUMP | 1070001 | 2022-11-01 | 33499.07 | 12313.17 | 19460.27 | 1725.63
MLP | CLOSE | MLU1 #11 FILTERED WATER PUMP REPLACEMENT | E10539628 | MLWEPPUMP | 1070001 | 2023-05-05 | 28046.21 | 19550.68 | 7133.52 | 1362.01
MLP | CLOSE | MLU2 #21 COOLING WATER BLOWDOWN PUMP REPLACE | E10539618 | MLWEPPUMP | 1070001 | 2023-07-19 | 14649.13 | 8526.48 | 5373.25 | 749.4
MLP | CLOSE | MLU0 DFA SILO AREA B SUMP PUMP REPLACEMENT | E10539611 | MLWEPPUMP | 1070001 | 2022-09-29 | 46221.02 | 25820.39 | 17563.68 | 2836.95
MLP | CLOSE | MLU2 AUX CONDENSER INSTALL PERMANENT SUMP PUMP | E10539586 | MLWEPPUMP | 1070001 | 2023-04-04 | 25624.3 | 5335.9 | 17891.05 | 2397.35
MLP | CLOSE | MLU1 AUX CONDENSER INSTALL PERMANENT SUMP PUMP | E10539585 | MLWEPPUMP | 1070001 | 2023-04-04 | 28756.62 | 12908.66 | 12538.92 | 3309.04
MLP | CLOSE | MLU2 DEMIN ACID PUMP/PIPING UPGRADE | E10539489 | MLWEPPUMP | 1070001 | 2023-11-14 | 87747.61 | 65556.02 | 16910.62 | 5280.97
MLP | CLOSE | MLU1 DEMIN ACID PUMP/PIPING UPGRADE | E10539488 | MLWEPPUMP | 1070001 | 2022-11-19 | 73862.31 | 68833.65 | 0 | 5028.66
MLP | CLOSE | MLU2 26 ASH WATER PUMP REPLACEMENT | E10539470 | MLWEPPUMP | 1070001 | 2022-11-30 | 2238.48 | 0 | 2165.79 | 72.69
MLP | CLOSE | MLU1 PURCHASE ASH WATER PUMP CAPITAL SPARE | E10539469 | MLWEPPUMP | 1070001 | 2022-11-07 | 73865.96 | 70484 | 0 | 3381.96
MLP | CLOSE | MLU1 #12 ASH WATER PUMP REPLACEMENT | E10539461 | MLWEPPUMP | 1070001 | 2023-04-26
MLP | CLOSE | MLU2 DEMINERALIZER RESIN REPLACEMENT (5 YR) | E10614270 | MLWEPRESN | 1070001 | 2023-10-29 | 279824.24 | 263136.65 | 13217.3 | 3470.29
MLP | CLOSE | MLU0 INSTALL OVATION EDS SERVER | E10573005 | MLWEPSERV | 1070001 | 2023-06-20 | 194955.95 | 176874.4 | 9876.2 | 8205.35
MLP | CLOSE | MLU2 INSTALL OVATION PLAYBACK RECORDER | E10573004 | MLWEPSERV | 1070001 | 2023-08-31 | 103106.57 | 88685 | 7685.02 | 6736.55
MLP | CLOSE | MLU1 INSTALL OVATION PLAYBACK RECORDER | E10573000 | MLWEPSERV | 1070001 | 2023-08-31 | 99535.85 | 88685 | 4463.59 | 6387.26
MLP | CLOSE | MLU0 INSTALL OVATION PLAYBACK RECORDER | E10572995 | MLWEPSERV | 1070001 | 2023-08-31 | 98172.96 | 88685 | 2972.39 | 6515.57
MLP | CLOSE | MLU2 REPLACE SECURITY APPLIANCE SERVER | E10539591 | MLWEPSERV | 1070001 | 2022-10-11 | 9055.67 | 8636.02 | 0 | 419.65
MLP | CLOSE | MLU1 REPLACE SECURITY APPLIANCE SERVER | E10539590 | MLWEPSERV | 1070001 | 2022-10-11 | 9066.21 | 8636.02 | 0 | 430.19
MLP | CLOSE | MLU0 REPLACE SECURITY APPLIANCE SERVER | E10539589 | MLWEPSERV | 1070001 | 2022-10-11 | 7372.28 | 7015.92 | 0 | 356.36
MLP | CLOSE | MLU2 Purchase Multipurpose Data Diode For Vendor Connections | E10539554 | MLWEPSERV | 1070001 | 2023-05-05 | 4970.17 | 4601 | 0 | 369.17
MLP | CLOSE | MLU1 Purchase Multipurpose Data Diode For Vendor Connections | E10539553 | MLWEPSERV | 1070001 | 2023-05-05 | 54672.17 | 50611 | 0 | 4061.17
MLP | CLOSE | MLU2 Replace OPC Server Unit 2 | E10539522 | MLWEPSERV | 1070001 | 2022-10-11 | 15447.65 | 14739.02 | 0 | 708.63
MLP | CLOSE | MLU1 Replace OPC Server Unit 1 | E10539521 | MLWEPSERV | 1070001 | 2022-10-11 | 11549.5 | 11060.02 | 0 | 489.48
MLP | CLOSE | MLU0 Replace OPC Server Unit 0 | E10539520 | MLWEPSERV | 1070001 | 2022-10-11 | 13064.54 | 12502.34 | 0 | 562.2
MLP | COMP | MLP U2: TR SET 4-17B BREAKER REPLACEMENT | E10906936 | MLWEPSWGR | 1070001 | 2025-05-08 | 1665.58 | 1157.85 | 402.17 | 105.56
MLP | CLOSE | MLU0 TRANSFORMER 14A HYDRAN MONITOR REPLACE | E10665203 | MLWEPSWGR | 1070001 | 2024-02-22 | 4834.22 | 200 | 4196.07 | 438.15
MLP | CLOSE | MLU0 TRANSFORMER 12B HYDRAN MONITOR REPLACE | E10665196 | MLWEPSWGR | 1070001 | 2024-02-07 | 36046.42 | 33620 | 780.77 | 1645.65
MLP | CLOSE | MLU0 HVF-4 BREAKER REPLACEMENT | E10643882 | MLWEPSWGR | 1070001 | 2023-06-05 | 2146.04 | 2177.47 | 0 | -31.43
MLP | CLOSE | MLU2 TURBINE ROOM LIGHTING BREAKER UPGRADE | E10615977 | MLWEPSWGR | 1070001 | 2023-04-25 | 19400.06 | 6840.63 | 11974.17 | 585.26
MLP | CLOSE | MLU2 TURBINE ROOM LIGHTING BREAKER UPGRADE | E10615977 | MLWEPSWGR | 1070001 | 2023-04-25 | 1146.88 | 0 | 1146.88 | 0
MLP | CLOSE | MLU1 FGD OXIDATION AIR BLOWER A MULTILIN RELAY 869 | E10611125 | MLWEPSWGR | 1070001 | 2023-10-26 | 12985.11 | 10925 | 1641.08 | 419.03
MLP | CLOSE | MLU2 OXIDATION AIR BLOWER C MULTILIN RELAY 869 | E10611120 | MLWEPSWGR | 1070001 | 2023-10-26 | 15624.47 | 10925 | 3981.6 | 717.87
MLP | CLOSE | MLU0 FGD 469 MULTILIN RELAY SPARE CUBICLE REPLACEMENT | E10611117 | MLWEPSWGR | 1070001 | 2023-10-26 | 34218.85 | 32775 | 383.53 | 1060.32
MLP | CLOSE | MLU0 CPS LIME VALVE LSAR 7104B & LSAR 7204B POSITIONER | E10610709 | MLWEPSWGR | 1070001 | 2023-06-15 | 4772.81 | 4154.32 | 0 | 618.49
MLP | CLOSE | MLU2 Replace CC2S2 Line Breaker Disconnect | E10539617 | MLWEPSWGR | 1070001 | 2023-12-21 | 237474.4 | 86949.91 | 64772.02 | 85752.47
MLP | CLOSE | MLU0 TSFMR 12A/12B TIE BREAKER GE MULTILIN RELAY REPLACE | E10539600 | MLWEPSWGR | 1070001 | 2024-06-26 | 2067.89 | 1683.9 | 100.13 | 283.86
MLP | CLOSE | MLU0 CPS REGULATING TRANSFORMER REPLACE | E10539580 | MLWEPSWGR | 1070001 | 2023-02-02 | 74320.37 | 58234 | 11481.45 | 4604.92
MLP | CLOSE | MLU0 STATION 2 TRANSFORMER REPLACEMENT | E10539499 | MLWEPSWGR | 1070001 | 2024-03-08 | 401408.38 | 239008.57 | 114651.93 | 47747.88
MLP | CLOSE | MLU1 REPLACE ID FAN 12 PROTECTIVE RELAY | E10539486 | MLWEPSWGR | 1070001 | 2022-10-01 | 16498.35 | 15810 | 0 | 688.35
MLP | COMP | MLP U0: PURCHASE STEP DOWN TRANSFORMER 575 TO 480 V | E10754684 | MLWEPTFRM | 1070001 | 2025-06-06 | 16785.87 | 8537.07 | 7155.4 | 1093.4
MLP | COMP | MLP U1: U1 EXCITER POWER POTENTIAL TRANSFORMER | E10749172 | MLWEPTFRM | 1070001 | 2025-05-08 | 653741.06 | 556629.14 | 36472.6 | 60639.32
MLP | COMP | MLP U2: ECON PRESSURE PROBE C ROSEMOUNT TRANSMITTER | E10910456 | MLWEPTRMT | 1070001 | 2025-05-30 | 4237.33 | 3539.96 | 429.03 | 268.34
MLP | COMP | MLP U1: REPLACE DVC ON IRV-20 | E10902811 | MLWEPTRMT | 1070001 | 2025-05-13 | 10004.3 | 4924.8 | 4511.95 | 567.55
MLP | COMP | MLP U2: 22 DEMIN ROSEMOUNT TRANSMITTER REPLACE | E10887734 | MLWEPTRMT | 1070001 | 2025-05-13 | 7653.69 | 3095.76 | 4117.59 | 440.34
MLP | CLOSE | MLP U1: FURNACE PRESSURE TRANSMITTER A REPLACE | E10887155 | MLWEPTRMT | 1070001 | 2025-03-19 | 4171.24 | 3460.37 | 493.86 | 217.01
MLP | CLOSE | MLP U1: 14 LP HEATER LEVEL TRANSMITTER REPLACEMENT | E10881046 | MLWEPTRMT | 1070001 | 2025-03-31 | 6152.36 | 4132.52 | 1657.56 | 362.28
MLP | CLOSE | MLP U2: Replace Furnace Pressure Transmitter | E10876332 | MLWEPTRMT | 1070001 | 2025-02-07 | 3993.74 | 3187.45 | 575.84 | 230.45
MLP | CLOSE | MLP U1: CONDENSATE TANK LEVEL TRANSMITTER REPLACE | E10860947 | MLWEPTRMT | 1070001 | 2024-12-26 | 3130.13 | 2710.57 | 307.89 | 111.67
MLP | COMP | MLP U1: CR PRESSURE GAUGE REPLACEMENT | E10859355 | MLWEPTRMT | 1070001 | 2025-05-07 | 80367.97 | 41531.75 | 34173.72 | 4662.5
MLP | INPRG | MLP U1: HYDROGEN DEWPOINT METER REPLACEMENT | E10858459 | MLWEPTRMT | 1070001 |  | 21470.01 | 12706.07 | 6995.99 | 1767.95
MLP | CLOSE | MLP U1: FUEL OIL CORIOLIS FLOWMETER | E10800644 | MLWEPTRMT | 1070001 | 2024-09-12 | 2289.93 | 0 | 2166.32 | 123.61
MLP | CLOSE | MLP U1: WATER CANNON SKID DCHG FLOW TRANSMITTER | E10797763 | MLWEPTRMT | 1070001 | 2024-10-17 | 3945.08 | 2980.43 | 751.03 | 213.62
MLP | CLOSE | MLP U2: WATER CANNON STRAINER DIFF PRESSURE TRANSMITTER | E10797755 | MLWEPTRMT | 1070001 | 2024-09-25 | 2216.4 | 1977.58 | 0 | 238.82
MLP | CLOSE | MLP U2: WATER CANNON SKID DCHG FLOW TRANSMITTER | E10797750 | MLWEPTRMT | 1070001 | 2024-10-17 | 4141.91 | 2980.43 | 751.03 | 410.45
MLP | CLOSE | MLP U2: 21 HOTWELL PUMP DISCHARGE TRANSMITTER | E10756193 | MLWEPTRMT | 1070001 | 2024-03-08 | 3064.13 | 2001.34 | 856.94 | 205.85
MLP | CLOSE | MLP U0: NORTH CY CAUSTIC SYSTEM ECD TRANSMITTERS | E10710681 | MLWEPTRMT | 1070001 | 2024-02-21 | 1816.62 | 1705 | 0 | 111.62
MLP | CLOSE | MLP U1 - HP Heater 7B Lvl Probe A - Reading Erratic | E10709392 | MLWEPTRMT | 1070001 | 2023-11-15 | 2832.8 | 2067 | 678.81 | 86.99
MLP | CLOSE | MLU0 DSI CONV AIR BLWR 1 PRESSURE TRANSMITTER REPLACEMENT | E10665719 | MLWEPTRMT | 1070001 | 2023-08-11 | 3284.34 | 2353.97 | 613 | 317.37
MLP | CLOSE | MLU0 FGD VAC BELT C TRANSMITTER REPLACE | E10650484 | MLWEPTRMT | 1070001 | 2023-06-22 | 2327.79 | 1460.24 | 830.73 | 36.82
MLP | CLOSE | MLU1 HOTWELL SUBPANEL CONDUCTIVITY TRANSMITTERS | E10634834 | MLWEPTRMT | 1070001 | 2023-11-01 | 10187.96 | 9091.09 | 0 | 1096.87
MLP | CLOSE | MLU0 CPS EFFLUENT SUMP PH TRANSMITTERS REPLACE | E10633642 | MLWEPTRMT | 1070001 | 2023-11-01 | 6202.78 | 5834 | 0 | 368.78
MLP | CLOSE | MLU1 HP HEATER LEVEL PROBE ( CORRECT INV) | E10572740 | MLWEPTRMT | 1070001 | 2023-05-08 | 5818.05 | 5495 | 0 | 323.05
MLP | CLOSE | MLU1 SCR DISCHARGE TRIP PRESSURE TRANSMITTER | E10567555 | MLWEPTRMT | 1070001 | 2023-10-26 | 4506.83 | 3678 | 373.74 | 455.09
MLP | CLOSE | MLU2 HYDROGEN PURITY METER REPLACEMENT | E10557783 | MLWEPTRMT | 1070001 | 2023-03-29 | 24186.07 | 21163.53 | 1426.55 | 1595.99
MLP | CLOSE | MLU1 HIGH DEMAND FIRE PMP DSCHG PRESSURE XMTR | E10549384 | MLWEPTRMT | 1070001 | 2023-02-15 | 3081.57 | 2588.71 | 400.64 | 92.22
MLP | CLOSE | MLU2 #2 & #4 FFC TRANSMITTER REPLACEMENT | E10539625 | MLWEPTRMT | 1070001 | 2022-12-22 | 9623.15 | 8134.41 | 990.84 | 497.9
MLP | CLOSE | MLU2 YOKOGAWA DISSOLVED OXYGEN TRANSMITTER | E10539517 | MLWEPTRMT | 1070001 | 2023-04-06 | 12544.58 | 10593 | 0 | 1951.58
MLP | CLOSE | MLU1 YOKOGAWA DISSOLVED OXYGEN TRANSMITTER | E10539516 | MLWEPTRMT | 1070001 | 2023-04-25 | 12544.58 | 10593 | 0 | 1951.58
MLP | CLOSE | MLU2 DA TANK LEVEL TRANSMITTER REPLACEMENT | E10539512 | MLWEPTRMT | 1070001 | 2023-04-26
MLP | CLOSE | MLU0 CPS FERRIC CHLORIDE MIX TANK 2 ECD PH TRANSMITTER REPLACEMENT | E10539509 | MLWEPTRMT | 1070001 | 2022-11-09 | 2104.52 | 2010 | 0 | 94.52
MLP | COMP | MLU2 CIRC WATER PH TRANSMITTER REPLACEMENT | E10539507 | MLWEPTRMT | 1070001 | 2023-07-31 | 8071.72 | 7414 | 0 | 657.72
MLP | COMP | MLU1 CIRC WATER PH TRANSMITTER REPLACEMENT | E10539506 | MLWEPTRMT | 1070001 | 2023-07-31 | 8263.63 | 7584.26 | 0 | 679.37
MLP | CLOSE | MLU1 CIRC WATER DCHG PRESSURE TRANSMITTER REPLACEMENT | E10539496 | MLWEPTRMT | 1070001 | 2023-12-21 | 2443.24 | 0 | 2268.55 | 174.69
MLP | CLOSE | MLU1 TURB RM COMB COIL PRESSURE TRANSMITTER | E10539495 | MLWEPTRMT | 1070001 | 2023-11-21 | 1818.45 | 0 | 1676.11 | 142.34
MLP | CLOSE | MLU2 COOLING TWR LEVEL STILLWELL & LEVEL TRANSMITTER | E10539459 | MLWEPTRMT | 1070001 | 2024-01-01 | 27517.63 | 16765 | 2364.49 | 8388.14
MLP | COMP | MLP U1: TURBINE CROSSOVER BELLOWS REPLACEMENT | E10878682 | MLWEPTURB | 1070001 | 2025-04-24 | 187885.04 | 153927 | 3132.63 | 30825.41
MLP | CLOSE | MLP U2: #24 CLARITE FILTER INLET HSO REPLACE | E10838901 | MLWEPVALV | 1070001 | 2025-01-31 | 13232.61 | 8348.41 | 3935.6 | 948.6
MLP | CLOSE | MLP U2: #22 CLARITE FILTER INLET HSO REPLACE | E10838885 | MLWEPVALV | 1070001 | 2025-01-31 | 12688.25 | 8049.02 | 3718.28 | 920.95
MLP | CLOSE | MLP U2: #22 HYDROGEN COOLING PUMP SUCTION HSO | E10821720 | MLWEPVALV | 1070001 | 2024-12-17 | 1.6653e-16 | 0 | 1.6653e-16 | 2.1337e-16
MLP | CLOSE | MLP U1: 13 CLARITE FILTER VALVE (KMO-532) REPLACE | E10779325 | MLWEPVALV | 1070001 | 2024-05-24 | 4980.03 | 4080.52 | 0 | 899.51
MLP | CLOSE | MLP - U0: STATION 3 HEADER AND DELUGE REPLACEMENT | E10745800 | MLWEPVALV | 1070001 | 2024-07-01 | 139297.17 | 70190.34 | 55305.45 | 13801.38
MLP | CLOSE | MLP U1: Replace ARV-706 Valve | E10730016 | MLWEPVALV | 1070001 | 2024-01-03 | 2670.06 | 976.4 | 1054.45 | 639.21
MLP | CLOSE | MLP U2: REPLACE Valve, Gate, 6 IN 300 LB Bolted Bonnet | E10730011 | MLWEPVALV | 1070001 | 2024-01-10 | 1907.96 | 921.44 | 889.34 | 97.18
MLP | CLOSE | MLP U1: #12 WWS PUMP CHECK VALVE REPLACE | E10721082 | MLWEPVALV | 1070001 | 2023-12-20 | 3248.8 | 2775.65 | 357.61 | 115.54
MLP | CLOSE | MLP U1: UPPER S. COMBUSTION COIL HSO REPLACE | E10719985 | MLWEPVALV | 1070001 | 2024-01-10 | 5332.4 | 1478.49 | 1226.22 | 2627.69
MLP | CLOSE | MLP U1: WW SUMP PUMP SUCTION / DISCHARGE VALVE | E10719811 | MLWEPVALV | 1070001 | 2024-01-11 | 6254.61 | 6018 | 0 | 236.61
MLP | CLOSE | MLU0 - H2 BULK STORAGE TANK SAFETY VALVE REPLACE | E10695080 | MLWEPVALV | 1070001 | 2023-12-01 | 13933.99 | 13420 | 0 | 513.99
MLP | CLOSE | MLU1 #12 ASH WATER PUMP DISCHARGE VALVE REPLACE | E10656180 | MLWEPVALV | 1070001 | 2023-06-20 | 2423.58 | 2338.94 | 0 | 84.64
MLP | CLOSE | MLU2 REPLACE WW SUMP PIPING SUCTION / DCHG VALVES | E10646779 | MLWEPVALV | 1070001 | 2023-10-24 | 6572.79 | 3009 | 3374.55 | 189.24
MLP | CLOSE | MLU0 MAINT SHOP DOOR FIRE HEADER REPLACEMENT | E10644246 | MLWEPVALV | 1070001 | 2023-08-15 | 17930.69 | 9345.65 | 7623.33 | 961.71
MLP | CLOSE | MLU2 #23 Waste Water Sump Check Valve Replacement | E10642245 | MLWEPVALV | 1070001 | 2023-05-31 | 4985.8 | 3433.19 | 1595.28 | -42.67
MLP | CLOSE | MLU2 6TH FLOOR FIRE HEADER REPLACEMENT | E10640690 | MLWEPVALV | 1070001 | 2023-08-15 | 29853.04 | 3147.95 | 24752.37 | 1952.72
MLP | CLOSE | MLU1 6TH FLOOR FIRE HEADER REPLACEMENT | E10640685 | MLWEPVALV | 1070001 | 2023-08-04 | 25319.05 | 4467.09 | 19264.22 | 1587.74
MLP | CLOSE | MLU1 REPLACE FIRE ISOLATION VALVE 50 | E10611094 | MLWEPVALV | 1070001 | 2023-04-26 | 4478.91 | 3568.51 | 665.81 | 244.59
MLP | CLOSE | MLU1 REPLACE RMO 8 VALVE | E10584145 | MLWEPVALV | 1070001 | 2023-01-16 | 8722.95 | 4660.7 | 3803.58 | 258.67
MLP | CLOSE | MLU1 7A HP Heater safety replacement | E10582090 | MLWEPVALV | 1070001 | 2023-01-02 | 3010.74 | 2935.6 | 0 | 75.14
MLP | CLOSE | MLU1 REPLACE PLANT AIR RISER 8 IN ROOT VALVE | E10558775 | MLWEPVALV | 1070001 | 2022-11-05 | 4669.76 | 4169.1 | 347.28 | 153.38
MLP | CLOSE | MLU2 #22 CONDENSATE BOOSTER PUMP 12" GATE VALVE | E10552741 | MLWEPVALV | 1070001 | 2022-10-21 | 12799.88 | 11402.45 | 836.75 | 560.68
MLP | CLOSE | MLU1 REPLACE THE 12" GATE VALVE ON #13 CLARITE FILTER H.S.O | E10539629 | MLWEPVALV | 1070001 | 2023-01-11 | 9021.8 | 6333.75 | 2204.23 | 483.82
MLP | CLOSE | MLU1 #12 WASTE WATER SUMP PUMP CHECK VALVE | E10539616 | MLWEPVALV | 1070001 | 2022-09-28 | 1065.85 | 0 | 1006.8 | 59.05
MLP | COMP | MLP U1: BFPT INSPECTION | E10863835 | MLWES1BTI | 1070001 | 2025-05-05 | 737048.84 | 139386.45 | 207120 | 390542.39
MLP | CLOSE | MLU1 - 2 LPA DOGBONE EJ REPLACEMENT | E10634778 | MLWES1BTI | 1070001 | 2023-12-31 | 15996.19 | 350 | 15051.36 | 594.83
MLP | INSERV | MLP Haul Rd Relocate | E10712461 | MLWHAULRD | 1070001 | 2024-11-20 | 7255765.92 | 13735 | 6231972.71 | 1010058.21
MLP | INPRG | MLP U0: HBF-1B CONVEYOR BELT REPLACEMENT | E10927880 | MLWMPBELT | 1070001 |  | 5309.34 | 4276.2 | 504.48 | 528.66
MLP | CLOSE | MLP U0: LABOR TO I/R 4 W BELT MOTOR & GEARBOX CSP'S | E10870483 | MLWMPBELT | 1070001 | 2025-02-17 | 33518.68 | 11064.98 | 19513.43 | 2940.27
MLP | COMP | MLP U0: R6 CONVEYOR MOTOR REPLACEMENT | E10861850 | MLWMPBELT | 1070001 | 2025-05-13 | 9874.6 | 4467.22 | 4088.99 | 1318.39
MLP | INPRG | MLP U0: BC9 BELT REPLACEMENT | E10840412 | MLWMPBELT | 1070001 |  | 36143.73 | 30598.75 | 2890.9 | 2654.08
MLP | CLOSE | MLP U0: BF-1 GYPSUM FEEDER BELT REPLACEMENT | E10835360 | MLWMPBELT | 1070001 | 2024-12-04 | 6758.82 | 2205 | 4378.69 | 175.13
MLP | CLOSE | MLP U0: BC-8 CONVEYOR BELT REPLACEMENT | E10768566 | MLWMPBELT | 1070001 | 2024-05-09 | 18911.18 | 9267 | 6927 | 2717.18
MLP | CLOSE | MLP U0: HSC3 CONVEYOR BELT REPLACEMENT | E10756194 | MLWMPBELT | 1070001 | 2024-03-27 | 89162.43 | 67400 | 14229.13 | 7533.3
MLP | CLOSE | MLP U1: CONVEYOR BELT 8 REPLACEMENT | E10754866 | MLWMPBELT | 1070001 | 2024-03-06 | 24159.63 | 10039.38 | 12542.35 | 1577.9
MLP | CLOSE | MLP - U0: HBF-1A FEEDER BELT REPLACEMENT | E10743670 | MLWMPBELT | 1070001 | 2024-02-08 | 10810.6 | 4125 | 5935.37 | 750.23
MLP | CLOSE | MLP - U0: BC-20 CONVEYOR BELT REPLACEMENT | E10736916 | MLWMPBELT | 1070001 | 2024-01-25 | 233526.09 | 181143.25 | 38319.48 | 14063.36
MLP | CLOSE | MLP - U0 HSC-2 SNUB PULLEY & BEARINGS | E10736865 | MLWMPBELT | 1070001 | 2024-02-01 | 21727.15 | 12953.8 | 7640.01 | 1133.34
MLP | CLOSE | MLP U0 - HRC2 CONV BELT REPLACE | E10736545 | MLWMPBELT | 1070001 | 2024-02-27 | 27832.11 | 0 | 26081.03 | 1751.08
MLP | CLOSE | MLP U0: HRC2 CONVEYOR BELT REPLACEMENT | E10729799 | MLWMPBELT | 1070001 | 2024-02-07 | 136269.03 | 129560 | 0 | 6709.03
MLP | CLOSE | MLU0 HIGH SULFUR FEEDER BELT BF-1A REPLACE | E10693655 | MLWMPBELT | 1070001 | 2024-04-11
MLP | CLOSE | MLU0 REPLACE CONVEYOR BC21 | E10688609 | MLWMPBELT | 1070001 | 2023-09-22 | 74541.54 | 57072 | 15845.2 | 1624.34
MLP | CLOSE | MLU0 REPLACE CONVEYOR BC14 | E10688600 | MLWMPBELT | 1070001 | 2023-09-22 | 140038.22 | 116496 | 20451.18 | 3091.04
MLP | CLOSE | MLU0 BF1 CONV BELT REPLACEMENT | E10682682 | MLWMPBELT | 1070001 | 2023-08-29 | 7359.23 | 2744 | 4488 | 127.23
MLP | CLOSE | MLU0 HRC-2 CONVEYOR SNUB PULLEY REPLACEMENT | E10680731 | MLWMPBELT | 1070001 | 2023-10-11 | 14024.57 | 7334.1 | 6232.16 | 458.31
MLP | CLOSE | MLU0 BEND PULLEY ON 4E CONV. REPLACEMENT | E10679246 | MLWMPBELT | 1070001 | 2023-08-18 | 10243.02 | 6414.56 | 2820.72 | 1007.74
MLP | CLOSE | MLU0 R2 CONVEYOR BELT REPLACEMENT | E10630106 | MLWMPBELT | 1070001 | 2023-10-18 | 107525.7 | 97895.67 | 8473.08 | 1156.95
MLP | CLOSE | MLU0 BF1 FEEDER BELT REPLACEMENT | E10610957 | MLWMPBELT | 1070001 | 2023-03-03 | 5727.94 | 2480.38 | 3383.4 | -135.84
MLP | CLOSE | MLU0 REPLACE BELT SCRAPERS FROM 4E/W TO SILOS | E10576378 | MLWMPBELT | 1070001 | 2022-12-31 | 64728.65 | 62628 | 0 | 2100.65
MLP | CLOSE | MLU0 REPLACE HRC-1 CONVEYOR BELT | E10575679 | MLWMPBELT | 1070001 | 2023-01-12 | 91666.73 | 86699.5 | 2325.82 | 2641.41
MLP | CLOSE | MLU0 BC-17 CONVEYOR BELT REPLACEMENT | E10571222 | MLWMPBELT | 1070001 | 2023-01-31 | 91333.04 | 56762 | 31864.26 | 2706.78
MLP | CLOSE | MLU0 REPLACE R6 CONVEYOR BELT | E10557598 | MLWMPBELT | 1070001 | 2022-11-18 | 15448.76 | 7200 | 7803.7 | 445.06
MLP | CLOSE | MLU0 REPLACE R8 CONVEYOR BELT | E10544982 | MLWMPBELT | 1070001 | 2022-12-16 | 53550.68 | 44001 | 7820.4 | 1729.28
MLP | CLOSE | MLU0 4E CONVEYOR BELT REPLACEMENT | E10542785 | MLWMPBELT | 1070001 | 2022-11-23 | 106284.48 | 97201 | 5805.45 | 3278.03
MLP | CLOSE | MLU0 ROTOCLONE BOOSTER FAN REPLACEMENT | E10539620 | MLWMPBELT | 1070001 | 2023-02-01 | 22940.22 | 19328 | 2628.7 | 983.52
MLP | CLOSE | MLU0 BF1 FEEDER BELT REPLACEMENT | E10539603 | MLWMPBELT | 1070001 | 2022-09-29 | 13093.2 | 0 | 12772.57 | 320.63
MLP | CLOSE | MLU0 Change BC-10 conveyor | E10539572 | MLWMPBELT | 1070001 | 2022-10-04 | 118283.42 | 81590 | 27681.8 | 9011.62
MLP | CLOSE | MLU0 #3 HSF VFD REPLACEMENT | E10539557 | MLWMPBELT | 1070001 | 2023-09-21 | 2.87 | 0 | -1.4211e-14 | 2.87
MLP | CLOSE | MLU0 REPLACE R5 HEAD CHUTE | E10630103 | MLWMPCHUT | 1070001 | 2023-11-14 | 308937.79 | 229657.05 | 53367.47 | 25913.27
MLP | CLOSE | MLU0 R6 Head Chute | E10574868 | MLWMPCHUT | 1070001 | 2023-11-14 | 212927.16 | 132678.65 | 68391.78 | 11856.73
MLP | CLOSE | MLU0 R9 CONVEYOR CHUTE REPLACEMENT | E10539552 | MLWMPCHUT | 1070001 | 2022-12-01 | 238351.97 | 122854 | 105751.15 | 9746.82
MLP | CLOSE | MLU0 REPLACE 3B & 3C CHUTES | E10539523 | MLWMPCHUT | 1070001 | 2022-12-31 | 139363.62 | 107768.79 | 27499.14 | 4095.69
MLP | INSERV | MLP U0: PURCHASE HSC2 GEARBOX | E10869633 | MLWMPCOMP | 1070001 | 2025-06-23 | 54414.95 | 50631.95 | 0 | 3783
MLP | COMP | MLP U0: PURCHASE HSC1 GEARBOX | E10869632 | MLWMPCOMP | 1070001 | 2025-06-10 | 69240.64 | 64426.94 | 0 | 4813.7
MLP | COMP | MLP U0: HSC-3 GEARBOX REPLACEMENT | E10850821 | MLWMPCOMP | 1070001 | 2025-04-30 | 171669.55 | 159954.5 | 2793.96 | 8921.09
MLP | CLOSE | MLP U0: BC12 TAIL PULLEY REPLACEMENT | E10840400 | MLWMPCOMP | 1070001 | 2025-01-03 | 4467.76 | 2884 | 1418.68 | 165.08
MLP | CLOSE | MLP U0: BF1 GYPSUM FEEDER MOTOR & GEARBOX REPLACEMENT | E10833899 | MLWMPCOMP | 1070001 | 2024-12-14 | 50331.26 | 29767.68 | 16950.57 | 3613.01
MLP | CLOSE | MLP U0: SILO A FLUIDIZING AIR BLOWER B REPLACEMENT | E10829678 | MLWMPCOMP | 1070001 | 2024-10-29 | 15052.05 | 13660.99 | 748.03 | 643.03
MLP | CLOSE | MLP U0: SILO A FLUIDIZING AIR BLOWER A REPLACE | E10819465 | MLWMPCOMP | 1070001 | 2024-09-12 | 12711.9 | 11468.03 | 720.94 | 522.93
MLP | CLOSE | MLP U0: BC 12 BEND PULLEY REPLACEMENT | E10798759 | MLWMPCOMP | 1070001 | 2024-08-09 | 15969.8 | 6504.12 | 7823.89 | 1641.79
MLP | CLOSE | MLP U0: R4 TAIL PULLEY REPLACEMENT | E10769848 | MLWMPCOMP | 1070001 | 2024-06-26 | 14263.76 | 7539.34 | 4792.63 | 1931.79
MLP | CLOSE | MLP U0: STAMLER CONV CHAIN REPLACEMENT | E10768670 | MLWMPCOMP | 1070001 | 2024-05-28 | 152767.37 | 83479.71 | 42469.9 | 26817.76
MLP | CLOSE | MLP U0: R2 CONVEYOR ROLLER REPLACEMENT | E10768525 | MLWMPCOMP | 1070001 | 2024-06-14 | 4183.12 | 3504.81 | 0 | 678.31
MLP | CLOSE | MLP - U0: HRC-3 Gearbox Replacement/Rebuild | E10747400 | MLWMPCOMP | 1070001 | 2024-03-01 | 69090.44 | 51714.11 | 6243.63 | 11132.7
MLP | CLOSE | MLP U0: HBF-1 VFD REPLACEMENT PF70 & SPARE 753 | E10802758 | MLWMPCTRL | 1070001 | 2024-09-07 | 15419.57 | 14680.59 | 0 | 738.98
MLP | COMP | MLP U0: FUEL OIL TANK LEVEL INDICATION AND CABLE/CONDUIT REPLACEMENT | E10773078 | MLWMPCTRL | 1070001 | 2025-03-03 | 49509.12 | 16211.92 | 26370.91 | 6926.29
MLP | CLOSE | MLU0 Clearwater Pond Upper Outfall Line Replacement | E10645214 | MLWMPDRNG | 1070001 | 2023-11-10 | 105538.3 | 84902.89 | 17409.18 | 3226.23
MLP | CLOSE | MLP - U0: PURCHASE E-CRANE BUCKET | E10719809 | MLWMPECRN | 1070001 | 2024-08-29 | 111779.3 | 105254.24 | 0 | 6525.06
MLP | CLOSE | MLU0 REPLACE ECRANE SWING MOTORS | E10539621 | MLWMPECRN | 1070001 | 2022-09-29 | 135116.82 | 65432.17 | 63439.25 | 6245.4
MLP | CLOSE | MLU0 PURCHASE E-CRANE BUCKET | E10539595 | MLWMPECRN | 1070001 | 2023-04-14 | 136706.23 | 128773.7 | 0 | 7932.53
MLP | CLOSE | MLU0 E-CRANE BARGE HAUL MOTOR REPLACEMENT | E10539577 | MLWMPECRN | 1070001 | 2022-09-29 | 24885.78 | 19076.73 | 4970.39 | 838.66
MLP | COMP | MLP U0: REPLACE HEATERS IN TRACTOR SHED | E10840336 | MLWMPHEAT | 1070001 | 2025-03-04 | 37788.27 | 22474.06 | 12942.35 | 2371.86
MLP | CLOSE | MLU0 PURCHASE ALLMAND MH 500IQ HEATER-2023 | E10631279 | MLWMPHEAT | 1070001 | 2023-09-15 | 44153.89 | 44339.1 | 0 | -185.21
MLP | CLOSE | MLU0 REMOVE AND INSTALL 480V HEATERS IN SILO B | E10574851 | MLWMPHEAT | 1070001 | 2023-11-29
MLP | CLOSE | MLU0 PURCHASE & INSTALL HEATERS IN DTE BUILDING | E10557530 | MLWMPHEAT | 1070001 | 2023-01-05 | 40480.17 | 26612.45 | 12514.76 | 1352.96
MLP | CLOSE | MLU0 PURCHASE ALLMAND MH 500IQ HEATER | E10539594 | MLWMPHEAT | 1070001 | 2022-09-29 | 49460.38 | 47188.23 | 0 | 2272.15
MLP | CLOSE | MLU0 TH10 INSTALL HEAT TRACE | E10539570 | MLWMPHEAT | 1070001 | 2022-11-30 | 39404.95 | 9119.31 | 28840.1 | 1445.54
MLP | CLOSE | MLU0 HTS-2A & HTS-2B STATION HEATERS | E10539555 | MLWMPHEAT | 1070001 | 2022-12-06 | 86150.93 | 42105.47 | 39960.09 | 4085.37
MLP | CLOSE | MLP U0: CAT D10T RJG00726 FINAL DRIVE | E10840395 | MLWMPHEVY | 1070001 | 2024-11-20 | 31211.04 | 24350.73 | 6144.54 | 715.77
MLP | COMP | MLP U0: HS COAL TUNNERL CABLE TRAY EXP JOINT | E10868680 | MLWMPHSTF | 1070001 | 2025-01-28 | 1975.72 | 1191.9 | 677.56 | 106.26
MLP | CLOSE | MLP U0: REPLACE MSA GAS MONITORS IN HS COAL TUNNEL | E10867492 | MLWMPHSTF | 1070001 | 2025-02-01 | 61496.24 | 25289.44 | 32816.37 | 3390.43
MLP | COMP | MLP U0: Replace HRC-1 Conveyor Pulleys (Total 4) | E10861471 | MLWMPHSTF | 1070001 | 2025-02-14 | 72035.57 | 49600.81 | 17276.16 | 5158.6
MLP | CLOSE | MLP U0: HRC-1 CONVEYOR BELT REPLACEMENT | E10861003 | MLWMPHSTF | 1070001 | 2025-03-05 | 118083.22 | 85480 | 23399.79 | 9203.43
MLP | COMP | MLP U0: HSC3 MOTOR REPLACEMENT | E10866024 | MLWMPMOTR | 1070001 | 2025-05-13 | 84874.8 | 77323.95 | 1583.69 | 5967.16
MLP | CLOSE | MLP U2: HVF-2 MOTOR REPLACEMENT | E10814247 | MLWMPMOTR | 1070001 | 2024-10-25 | 4295.75 | 1731 | 2339.99 | 224.76
MLP | CLOSE | MLP U0: PURCHASE HRC1 CONV GEARBOX | E10757489 | MLWMPOCOM | 1070001 | 2024-08-30 | 59835.25 | 56947.14 | 0 | 2888.11
MLP | CLOSE | MLP U0: PURCHASE HRC2, HRC3 CONV GEARBOX | E10757488 | MLWMPOCOM | 1070001 | 2024-08-20 | 68203.69 | 64911.55 | 0 | 3292.14
MLP | CLOSE | MLP U0 - PURCHASE BC4, BC17, BC19, BC20, BC21 CONV GEARBOX | E10757480 | MLWMPOCOM | 1070001 | 2024-08-30 | 142263.78 | 131300.03 | 0 | 10963.75
MLP | COMP | MLP U0: Replace Shaft, Sprockets, Bearings and Wheels on Barge Unloader Bucket Drive | E10844462 | MLWMPOTHR | 1070001 | 2025-05-13 | 182164.18 | 139870.55 | 29549.19 | 12744.44
MLP | CLOSE | MLP U0: DTE BLDG AIR COMP CONTROL SCREEN REPLACEMENT | E10835420 | MLWMPOTHR | 1070001 | 2025-01-16 | -2272.93 | -7433.36 | 5203.35 | -42.92
MLP | CLOSE | MLP U0 DFA SILO B FLUIDIZING CLOTH REPLACEMENT | E10804050 | MLWMPOTHR | 1070001 | 2024-10-15 | 25557.64 | 23638.5 | 785.66 | 1133.48
MLP | CLOSE | MLP U0: REPLACE DFA SCALE MOXA TOUCH SCREEN DISPLAY | E10746661 | MLWMPOTHR | 1070001 | 2024-03-01 | 10487.33 | 0 | 8605.02 | 1882.31
MLP | CLOSE | MLU0 INSTALL PERM VAC LINES IN TUNNELS/STATIONS | E10637298 | MLWMPOTHR | 1070001 | 2023-11-09 | 30055.46 | 21744.53 | 7089.16 | 1221.77
MLP | COMP | MLP U1: SERV WTR PMP A SWING CK VLV REPLACE | E10914135 | MLWMPPUMP | 1070001 | 2025-06-10 | 3832.27 | 3234.34 | 326.41 | 271.52
MLP | COMP | MLP U0: LEACHATE HIGH FLOW SUMP PUMP REPLACE | E10884193 | MLWMPPUMP | 1070001 | 2025-05-08 | 59234.63 | 53658.42 | 2054.87 | 3521.34
MLP | CLOSE | MLP U0: 3B SUMP PUMP REPLACEMENT | E10850670 | MLWMPPUMP | 1070001 | 2025-01-08 | 40391.85 | 33695.23 | 5045.3 | 1651.32
MLP | CLOSE | MLU0 Replace Leachate High Flow Sump Pump | E10775686 | MLWMPPUMP | 1070001 | 2024-07-16 | 66761.46 | 50304.29 | 4267.31 | 12189.86
MLP | CLOSE | MLU0 Remove and replace 3B Sump Pump | E10633400 | MLWMPPUMP | 1070001 | 2024-02-20 | 40848.51 | 36329.75 | 2569.02 | 1949.74
MLP | CLOSE | MLU0 Remove and replace 3C West Sump Pump | E10633391 | MLWMPPUMP | 1070001 | 2024-02-28 | 39926.32 | 33071.68 | 4642.66 | 2211.98
MLP | CLOSE | MLU0 Remove and replace 3C East sump pump | E10631584 | MLWMPPUMP | 1070001 | 2024-02-08 | 52257.39 | 35145.66 | 12834.2 | 4277.53
MLP | CLOSE | MLU0 SILO B FLUIDIZING AIR BLOWER A REPLACEMENT | E10614280 | MLWMPPUMP | 1070001 | 2023-04-27 | 9882.38 | 8482 | 734.83 | 665.55
MLP | CLOSE | MLU0 4E & 4W TUNNEL SUMP PUMP REPLACEMENT | E10539501 | MLWMPPUMP | 1070001 | 2023-01-31 | 37180.15 | 25060.85 | 9192.48 | 2926.82
MLP | CLOSE | MLU0 REPLACE LEACHATE POND PUMP | E10539497 | MLWMPPUMP | 1070001 | 2022-09-29 | 4907.2 | 4747 | 0 | 160.2
MLP | COMP | MLP U1: ROTOCLONES REPLACEMENT | E10840408 | MLWMPROTO | 1070001 | 2025-05-28 | 327867.47 | 228931.07 | 80065.33 | 18871.07
MLP | COMP | MLP U0: LABOR TO INSTALL / REMOVE BC-20 GEARBOX | E10907143 | MLWMPVALV | 1070001 | 2025-05-27 | 20441.26 | 2952.17 | 16195.01 | 1294.08
MLP | COMP | MLP U0: LABOR TO INSTALL / REMOVE BC-19 GEARBOX | E10907142 | MLWMPVALV | 1070001 | 2025-05-16 | 6991.7 | 0 | 6565.14 | 426.56
MLP | CLOSE | MLU0 REPLACE Silo Side Service Water Pump A Check Valve | E10786757 | MLWMPVALV | 1070001 | 2024-06-21 | 3286.11 | 1905.58 | 1137.91 | 242.62
MLP | CLOSE | MLP UO: BF-1 GEARBOX REPLACEMENT | E10720305 | MLWMPVALV | 1070001 | 2024-01-05 | 48579.79 | 40632.26 | 5041.51 | 2906.02
MLP | CLOSE | MLU0 REBUILD TWO 514C GEARBOXES ON WM ROBINSON | E10642663 | MLWMPVALV | 1070001 | 2023-12-13 | 44446.99 | 37389 | 5524.05 | 1533.94
MLP | CLOSE | MLU0 DFA SILOS BACK PRESSURE REGULATING VLV REPLACE | E10539534 | MLWMPVALV | 1070001 | 2022-11-15 | 22511.73 | 17168.74 | 4709.93 | 633.06
MLP | INPRG | MLP U0: SERVICE BLDG 2ND FLOOR BATHROOM INSTALL | E10919794 | MLWNPBLDG | 1070001 |  | 46221.96 | 13707.51 | 27998.37 | 4516.08
MLP | CLOSE | MLP U0: PURCHASE PLANNER OFFICE DESKS | E10879851 | MLWNPBLDG | 1070001 | 2025-03-04 | 10580.41 | 6842.46 | 3214.74 | 523.21
MLP | COMP | MLP U0: CFB 1ST FLOOR WATER HEATER REPLACEMENT | E10867127 | MLWNPBLDG | 1070001 | 2025-03-27 | 24253.16 | 20272.66 | 2886.55 | 1093.95
MLP | CLOSE | MLP U0: PURCHASE OFFICE FURNITURE | E10865988 | MLWNPBLDG | 1070001 | 2025-01-19 | 2043.03 | 1887.97 | 0 | 155.06
MLP | COMP | MLP U0: SERVICE BLDG 2ND FLOOR OFFICES | E10865858 | MLWNPBLDG | 1070001 | 2025-03-07 | 119701.72 | 26835.1 | 85775.36 | 7091.26
MLP | CLOSE | MLP U0: PLANT PARKING LOT PAVING | E10799122 | MLWNPBLDG | 1070001 | 2024-09-05 | 113932.77 | 0 | 109430.46 | 4502.31
MLP | CLOSE | MLP U0: LABOR TO INSTALL BATTERY CHARGER IN WH7 | E10794189 | MLWNPBLDG | 1070001 | 2024-10-01 | 27272.15 | 7450.37 | 18606.94 | 1214.84
MLP | CLOSE | MLP U0: INSTALL POWER PANEL IN I&C SHOP | E10789345 | MLWNPBLDG | 1070001 | 2024-09-20 | 33847.3 | 8337.17 | 23982.45 | 1527.68
MLP | CLOSE | MLP - U0: ADDITIONAL INSTALL/RETIREMENT | E10752190 | MLWNPBLDG | 1070001 | 2024-09-30
MLP | CLOSE | MLP U0: CABLE PULL FOR STATOR HEATERS WH7 | E10750771 | MLWNPBLDG | 1070001 | 2024-04-04 | 8757.53 | 349.78 | 7820.37 | 587.38
MLP | CLOSE | MLP U0: OLD STACK MAN DOOR REPLACEMENT | E10734260 | MLWNPBLDG | 1070001 | 2024-06-21 | 26211.74 | 12426.22 | 9914.54 | 3870.98
MLP | CLOSE | MLP: U2 ACCESS PLATFORM #23 PULVERIZER ROLL WHEEL DOOR | E10732866 | MLWNPBLDG | 1070001 | 2024-02-08 | 33760.7 | 3017.47 | 28679.51 | 2063.72
MLP | CLOSE | MLP: U1 ACCESS PLATFORM #13 PULVERIZER ROLL WHEEL DOOR | E10732861 | MLWNPBLDG | 1070001 | 2024-01-25 | 28258.42 | 4261.01 | 22414.19 | 1583.22
MLP | CLOSE | MLU2 Replace Pulverizer Access Platforms | E10719387 | MLWNPBLDG | 1070001 | 2024-02-15 | 116026.37 | 16512.27 | 93982.18 | 5531.92
MLP | CLOSE | MLU1 Replace Pulverizer Access Platforms | E10719385 | MLWNPBLDG | 1070001 | 2024-01-05 | 121623.73 | 21074.73 | 95243.09 | 5305.91
MLP | CLOSE | MLU0 REPLACE WATER SOFTENER IN HRLY SHOWERHOUSE | E10646625 | MLWNPBLDG | 1070001 | 2023-08-10 | 6070.14 | 0 | 5965.2 | 104.94
MLP | CLOSE | MLU0 INSTALL NEW PLATFORM AT CBU | E10642429 | MLWNPBLDG | 1070001 | 2023-10-23 | 6134.37 | 568.84 | 5374.33 | 191.2
MLP | CLOSE | MLU2 Install DFA Transfer Station Structural Enclosure | E10640962 | MLWNPBLDG | 1070001 | 2024-09-30 | 0 | 0 | 21190 | -21190
MLP | CLOSE | MLU2 WASTE WATER SUMP PUMP MONORAIL | E10635552 | MLWNPBLDG | 1070001 | 2023-12-08 | 196044.48 | 52765.36 | 130882.7 | 12396.42
MLP | CLOSE | MLU1 WASTE WATER SUMP PUMP MONORAIL | E10635551 | MLWNPBLDG | 1070001 | 2024-05-31 | 115568.24 | 12364.18 | 92734.42 | 10469.64
MLP | CLOSE | MLU0 PURCHASE & INSTALL O2 PROBE MONORAIL SYSTEM | E10623961 | MLWNPBLDG | 1070001 | 2023-08-01 | 75019.88 | 21351.65 | 50563.7 | 3104.53
MLP | CLOSE | MLU0 INSTALL DFA SERVICE WATER VALVE PLATFORM | E10619509 | MLWNPBLDG | 1070001 | 2023-05-31 | 6695.66 | 977.82 | 5507.4 | 210.44
MLP | CLOSE | MLU0 N CY RUN OFF POND - PLATFORM FOR LAB SAMPLES | E10611100 | MLWNPBLDG | 1070001 | 2023-07-14 | 3166.37 | 585.23 | 2365.57 | 215.57
MLP | CLOSE | MLU0 R2 TRANSFORMER COVER | E10558777 | MLWNPBLDG | 1070001 | 2023-12-13 | 424531.66 | 212198.5 | 172421.96 | 39911.2
MLP | CLOSE | MLU0 SERVICE BLDG CONF RM TABLE 2ND FLOOR | E10558500 | MLWNPBLDG | 1070001 | 2023-09-21 | 0 | 0 | -2.7756e-17 | 0
MLP | CLOSE | MLU2 ALIMANK RAMP AND PLATFORM REPLACE | E10539584 | MLWNPBLDG | 1070001 | 2023-01-31 | 82913.76 | 21499.22 | 47183.89 | 14230.65
MLP | CLOSE | MLU0 NEW STEPS FROM PARKING LOT TO BLUE BLDG | E10539576 | MLWNPBLDG | 1070001 | 2023-02-03 | 101208.98 | 21781.44 | 73206.7 | 6220.84
MLP | CLOSE | MLU0 CHLORINE BUILDING ROOF AND SIDING | E10539531 | MLWNPBLDG | 1070001 | 2022-09-30 | 90178 | 21631.69 | 61359.61 | 7186.7
MLP | CLOSE | MLU0 PURCH 2 CONNEX TRAILERS FOR OPER BRKRMS | E10539498 | MLWNPBLDG | 1070001 | 2022-11-05 | 138205.29 | 54230.07 | 73901.08 | 10074.14
MLP | CLOSE | MLU2 REPLACE PULVERIZER ACCESS PLATFORMS | E10539491 | MLWNPBLDG | 1070001 | 2023-03-07 | 46974.99 | 11425.64 | 15307.29 | 20242.06
MLP | CLOSE | MLU1 REPLACE PULVERIZER ACCESS PLATFORMS | E10539490 | MLWNPBLDG | 1070001 | 2023-03-07 | 68673.42 | 12732.79 | 27182.17 | 28758.46
MLP | INPRG | MLP U2: FIRE HEADER & VALVE REPLACEMENT | E10910686 | MLWNPFIRE | 1070001 |  | 43807.7 | 30994.44 | 10143.02 | 2670.24
MLP | CLOSE | MLU0 DFA Silo B Bin Vent Filter Bag Replacement | E10641321 | MLWNPINSL | 1070001 | 2023-11-10 | 41439.57 | 29731.6 | 8632.44 | 3075.53
MLP | CLOSE | MLU2 Install Isomebrane in Steam Generator Penthouse to replace Penetration Seals | E10539561 | MLWNPINSL | 1070001 | 2022-12-01 | 546885.06 | 0 | 528364.72 | 18520.34
MLP | INPRG | ML HAUL ROAD RELOCATION PRELIMINARY ENGINEERING | E10539448 | MLWNPROAD | 1070001 |  | 6110.38 | 849.85 | 4315.22 | 945.31
MLP | CLOSE | MLU0 INSTALL CARD READER AT CCC DOORS | E10539558 | MLWNPSECU | 1070001 | 2023-07-13 | 14339.85 | 269.74 | 8704.38 | 5365.73
MLP | CLOSE | MLU0 INSTALL CARD READERS AT U1&U2 CR AND DCS ROOMS | E10539479 | MLWNPSECU | 1070001 | 2023-10-03 | 147043.64 | 5208.52 | 102446.42 | 39388.7
MLP | INPRG | MLP U0: PURCHASE HANDHELF FLUKE METERS FOR NEW TECHNICIAN | E10902820 | MLWNPTOOL | 1070001 |  | 8410.34 | 7776 | 0 | 634.34
MLP | COMP | MLP U0: PURCHASE FLUKE 1630-2-FC EARTH GROUND METER | E10899646 | MLWNPTOOL | 1070001 | 2025-04-15 | 2445.83 | 2332 | 0 | 113.83
MLP | CLOSE | MLP U0: PURCHASE LABEL MAKER FOR EQUIP ID | E10890043 | MLWNPTOOL | 1070001 | 2025-04-14 | 6013.93 | 5734.02 | 0 | 279.91
MLP | CLOSE | MLP U0: Purchase 2 Battery Welders | E10888475 | MLWNPTOOL | 1070001 | 2025-04-09 | 7594.33 | 7240.86 | 0 | 353.47
MLP | COMP | MLP U0: Purchase Two (2) Altair 5x Confined Space portable monitors to replace two (2) broken monito | E10888454 | MLWNPTOOL | 1070001 | 2025-05-21 | 9184.47 | 8624.1 | 0 | 560.37
MLP | CLOSE | MLP U0: PURCHASE MIG WELDING MACHINE FOR GVH | E10886942 | MLWNPTOOL | 1070001 | 2025-03-20 | 4733.07 | 4499 | 0 | 234.07
MLP | CLOSE | MLP U0: PURCH COMMERCIAL FLOOR BUFFER / WET DRY VAC | E10886487 | MLWNPTOOL | 1070001 | 2025-03-10 | 3146.88 | 2991.31 | 0 | 155.57
MLP | CLOSE | MLP U0: PURCH ADJUSTABLE GANTRY CRANES - CPS PUMP HOUSES | E10886466 | MLWNPTOOL | 1070001 | 2025-03-18 | 9487.02 | 9017.87 | 0 | 469.15
MLP | CLOSE | MLP U0: PURCHASE AEROSOL CAN STORAGE CABINETS | E10880288 | MLWNPTOOL | 1070001 | 2025-03-20 | 12688.05 | 8062.42 | 3794.51 | 831.12
MLP | CLOSE | MLP U0: PURCHASE SNOWBLOWER | E10872792 | MLWNPTOOL | 1070001 | 2025-02-04 | 3614.47 | 3414.98 | 0 | 199.49
MLP | CLOSE | MLP U0: PURCHASE EXPLOSION PROOF STRING LIGHTS | E10868020 | MLWNPTOOL | 1070001 | 2025-02-18 | 33799.87 | 31095.94 | 0 | 2703.93
MLP | CLOSE | MLP U0: PURCHASE ELECTRIC WIRE CABLE TRACER | E10867736 | MLWNPTOOL | 1070001 | 2025-01-17 | 3434.59 | 3173.88 | 0 | 260.71
MLP | CLOSE | MLP U0: 3/4 DRIVE 36V HYTORC GUN 200-1200 FT LBS | E10842519 | MLWNPTOOL | 1070001 | 2024-12-10 | 10283.3 | 10033.93 | 0 | 249.37
MLP | CLOSE | MLP U0: SNAP ON CORDLESS TORQUE MULTIPLIER 2KFLBS | E10842518 | MLWNPTOOL | 1070001 | 2024-12-10 | 9006.34 | 8787.94 | 0 | 218.4
MLP | CLOSE | MLP U0: Purchase Flir infrared camera | E10841207 | MLWNPTOOL | 1070001 | 2024-12-18 | 1998.47 | 1950 | 0 | 48.47
MLP | CLOSE | MLP U0: Coping power generator battery replacement | E10840846 | MLWNPTOOL | 1070001 | 2024-12-19 | 4664.44 | 3879 | 409.63 | 375.81
MLP | CLOSE | MLP U0: FGD JLG BATTERY REPLACMENT | E10840845 | MLWNPTOOL | 1070001 | 2025-01-08 | 5081.61 | 4445.28 | 221.18 | 415.15
MLP | CLOSE | MLP U0: Ball mill dumper tool purchase | E10840836 | MLWNPTOOL | 1070001 | 2025-04-02 | 23043.82 | 21794.7 | 0 | 1249.12
MLP | CLOSE | MLP U0: KUBOTA RTVX 1100CC REPLACEMENT | E10840377 | MLWNPTOOL | 1070001 | 2024-12-09 | 30051.36 | 27998.46 | 0 | 2052.9
MLP | CLOSE | MLP U0: PURCHASE RIGHT ANGLE GRINDER | E10840324 | MLWNPTOOL | 1070001 | 2024-12-31 | 1038.9 | 1009 | 0 | 29.9
MLP | CLOSE | MLP U2: PURCHASE 4 15KVA MILL PANELS | E10840185 | MLWNPTOOL | 1070001 | 2024-11-12 | 8551.86 | 8000 | 0 | 551.86
MLP | CLOSE | MLP U0: PURCHASE JOB SITE OFFICE TRAILERS | E10840167 | MLWNPTOOL | 1070001 | 2024-11-19 | 61267.3 | 57452 | 0 | 3815.3
MLP | CLOSE | MLP U0: PURCHASE SEA LAND BOX FOR CNTR STORAGE | E10824632 | MLWNPTOOL | 1070001 | 2024-10-09 | 4681.16 | 0 | 4490 | 191.16
MLP | CLOSE | MLP U0: PURCH FLAMMABLE LIQUIDS FIRE CABINET FOR LABOR GANG | E10819725 | MLWNPTOOL | 1070001 | 2024-10-01 | 1933.78 | 1847.73 | 0 | 86.05
MLP | CLOSE | MLP U0: PURCHASE DYNAMOMETER | E10804074 | MLWNPTOOL | 1070001 | 2024-09-13 | 3198.23 | 3031.25 | 0 | 166.98
MLP | CLOSE | MLP U0: DSI LIME TRANSFER SPLITTER TOOL | E10785776 | MLWNPTOOL | 1070001 | 2024-09-10 | 4011.54 | 3723.5 | 0 | 288.04
MLP | CLOSE | MLP U0: Purchase D10 Blade | E10773819 | MLWNPTOOL | 1070001 | 2024-05-21 | 33301.8 | 20650.3 | 7992 | 4659.5
MLP | CLOSE | MLP U0: PURCHASE PERISTALTIC PUMPS FOR ENV. WORK | E10768956 | MLWNPTOOL | 1070001 | 2024-09-04 | 3939.84 | 3780.09 | 0 | 159.75
MLP | CLOSE | MLP U0: PURCHASE BIOREACTOR ANALYSES EQUIPMENT | E10768530 | MLWNPTOOL | 1070001 | 2024-06-20 | 18624.64 | 15755.16 | 0 | 2869.48
MLP | CLOSE | MLP U0: PURCHASE 2 NEW SEA BOXES | E10768149 | MLWNPTOOL | 1070001 | 2024-07-30
MLP | CLOSE | MLP U0: PURCHASE 2 NEW SEA BOXES | E10766074 | MLWNPTOOL | 1070001 | 2024-05-08 | 11880.88 | 9801.45 | 0 | 2079.43
MLP | CLOSE | MLP U0: PURCHASE FORK TRUCK MAN BASKET | E10758982 | MLWNPTOOL | 1070001 | 2024-03-28 | 1884.59 | 1738.7 | 0 | 145.89
MLP | CLOSE | MLP U0: PURCH ID FAN HUB I/R HEATER KIT | E10750219 | MLWNPTOOL | 1070001 | 2024-11-04 | 10939.33 | 10271.46 | 0 | 667.87
MLP | CLOSE | MLP U0: PURCHASE PROCESS METERS | E10744900 | MLWNPTOOL | 1070001 | 2024-05-01 | 24479.09 | 20194.66 | 0 | 4284.43
MLP | CLOSE | MLP - U0: PURCHASE RIGID DRAIN CLEANING MACHINE | E10744792 | MLWNPTOOL | 1070001 | 2024-03-08 | 5566.12 | 5202.73 | 0 | 363.39
MLP | CLOSE | MLP - U0: PURCHASE PORTABLE GENERATOR | E10739022 | MLWNPTOOL | 1070001 | 2024-01-29 | 1291.09 | 1241.12 | 0 | 49.97
MLP | CLOSE | MLU0 PURCHASE FIVE MEGGER TESTERS FOR ICE | E10730126 | MLWNPTOOL | 1070001 | 2024-01-08 | 14392.82 | 13763.3 | 0 | 629.52
MLP | CLOSE | MLP U0: PURCHASE ACOUSTIC MONITOR | E10729800 | MLWNPTOOL | 1070001 | 2024-01-03 | 24885.44 | 23796.99 | 0 | 1088.45
MLP | CLOSE | MLP - U0: PURCHASE PORTABLE HYDRAULIC PUMP | E10729052 | MLWNPTOOL | 1070001 | 2024-01-07 | 39633.53 | 37900 | 0 | 1733.53
MLP | CLOSE | MLP - U0: PURCHASE PORTABLE AIR COMPRESSOR | E10729049 | MLWNPTOOL | 1070001 | 2023-12-29 | 68148.13 | 65250 | 0 | 2898.13
MLP | CLOSE | MLP - U0: PURCHASE ID FAN HUB REMOVAL TOOK KITS | E10728108 | MLWNPTOOL | 1070001 | 2024-04-17 | 24674.14 | 20440.52 | 0 | 4233.62
MLP | CLOSE | MLP -U0: PURCHASE ICP-MS INST FOR WATER COMPLIANCE | E10727754 | MLWNPTOOL | 1070001 | 2024-05-17 | 161179.47 | 149060.12 | 0 | 12119.35
MLP | CLOSE | MLP U0: PURCHASE PORTABLE HEATERS FOR PLANT | E10725480 | MLWNPTOOL | 1070001 | 2024-01-10 | 15138.66 | 14567.45 | 0 | 571.21
MLP | CLOSE | MLP U0: PURCHASE HOIST WINCH FOR OLD STACK | E10723556 | MLWNPTOOL | 1070001 | 2024-01-31 | 3547.76 | 3332.19 | 0 | 215.57
MLP | CLOSE | MLP U0: PURCH VLV TURNING TOOL CUSTOM SOCKETS | E10720466 | MLWNPTOOL | 1070001 | 2023-12-31 | 2496.16 | 2390 | 0 | 106.16
MLP | CLOSE | MLP U0: PURCHASE 2 PORTABLE FILTER CARTS | E10720320 | MLWNPTOOL | 1070001 | 2024-01-09 | 14891.72 | 14240.38 | 0 | 651.34
MLP | CLOSE | MLP - U0 PURCH 2 ROD OVENS FOR QC COMPLICANCE | E10706082 | MLWNPTOOL | 1070001 | 2023-11-08 | 3447.38 | 3357.96 | 0 | 89.42
MLP | CLOSE | MLU0 Purchase Label Engraver for Operations Control Rooms | E10688107 | MLWNPTOOL | 1070001 | 2023-10-05 | 7538.98 | 7366.28 | 0 | 172.7
MLP | CLOSE | MLU0 PURCHASE IH SAMPLING PUMPS / CHARGING STATION | E10646179 | MLWNPTOOL | 1070001 | 2023-08-01 | 5256.52 | 0 | 0 | 5256.52
MLP | CLOSE | MLU0 PURCHASE ANCHOR KITS FOR RIVER OIL BOOM SYSTEM | E10638622 | MLWNPTOOL | 1070001 | 2023-06-22 | 5530.09 | 5454.31 | 0 | 75.78
MLP | CLOSE | MLU0 Purchase New confined space monitor | E10633406 | MLWNPTOOL | 1070001 | 2023-05-01 | 4837.04 | 0 | 0 | 4837.04
MLP | CLOSE | TEST STATUS PROGRESSION WAM-10603 | E10630570 | MLWNPTOOL | 1070001 | 2022-04-14
MLP | CLOSE | MLU0 PURCHASE VALVE OPERATOR FOR ENPR | E10619235 | MLWNPTOOL | 1070001 | 2023-04-19 | 34451.52 | 35268.55 | 0 | -817.03
MLP | CLOSE | MLU0 PURCHASE MILWAUKEE DRILL | E10605222 | MLWNPTOOL | 1070001 | 2023-03-07 | 2928.6 | 2830 | 0 | 98.6
MLP | CLOSE | MLU0 PURCHASE HACH AT1000 AUTOTITRATOR | E10589279 | MLWNPTOOL | 1070001 | 2023-09-12 | 4756.15 | 4759.92 | 0 | -3.77
MLP | CLOSE | MLU0 PURCHASE CIRC WATER PUMP BLANKS | E10586659 | MLWNPTOOL | 1070001 | 2023-02-08 | 27679.14 | 26850 | 0 | 829.14
MLP | CLOSE | MLU0 Purchase Powered Pallet Jack For Chemical Totes at CPS | E10574856 | MLWNPTOOL | 1070001 | 2023-01-31 | 4965.61 | 4831.36 | 0 | 134.25
MLP | CLOSE | MLU0 PURCHASE USM-GO+ FLAW DETECTOR | E10573761 | MLWNPTOOL | 1070001 | 2023-02-13 | 9311.89 | 8929 | 0 | 382.89
MLP | COMP | MLU0 PURCHASE SNAP-ON TOOL BOXES & LOCKERS | E10573707 | MLWNPTOOL | 1070001 | 2024-07-23 | 172276.65 | 158993.86 | 0 | 13282.79
MLP | CLOSE | MLU0 Purchase Sullair 185CFM Air Compressor number 2 | E10573400 | MLWNPTOOL | 1070001 | 2023-10-17 | 30062.44 | 28200 | 0 | 1862.44
MLP | CLOSE | MLU0 PURCH 2 ALBER CELLCORDER BATTERY TESTERS & LEADS | E10572743 | MLWNPTOOL | 1070001 | 2023-05-04 | 12295.5 | 11616 | 0 | 679.5
MLP | CLOSE | MLU0 PURCH 2 LAPTOPS FOR ICE INST TESTING | E10572738 | MLWNPTOOL | 1070001 | 2022-12-16 | 4286 | 4183.67 | 0 | 102.33
MLP | CLOSE | MLU0 PURCHASE UNDERGROUND PIPE LOCATOR | E10572450 | MLWNPTOOL | 1070001 | 2023-04-26 | 17333.65 | 16576.9 | 0 | 756.75
MLP | CLOSE | MLU0 PURCH PORTABLE BATTERY OPERATED WELDER | E10571225 | MLWNPTOOL | 1070001 | 2023-01-28 | 4043.07 | 3911.82 | 0 | 131.25
MLP | CLOSE | MLU0 PURCH CATERPILLAR BROOM | E10571220 | MLWNPTOOL | 1070001 | 2022-12-29 | 5889.46 | 5711.2 | 0 | 178.26
MLP | CLOSE | MLU0 PURCH PORTABLE VALVE OPERATOR & ADAPTER | E10570982 | MLWNPTOOL | 1070001 | 2022-12-28 | 32172.19 | 31235.99 | 0 | 936.2
MLP | CLOSE | MLU0 PURCH OIL BOOM, TRAILER, & MOTOR FOR SPILL RESPONSE | E10563702 | MLWNPTOOL | 1070001 | 2023-03-13 | 77455.59 | 73977 | 0 | 3478.59
MLP | CLOSE | MLU0 PURCHASE 2023 EASYGO VALOR 48V GOLF CART | E10558353 | MLWNPTOOL | 1070001 | 2022-11-10 | 10942.57 | 10646.5 | 0 | 296.07
MLP | CLOSE | MLU0 PURCH ELIOS 3 AND SKYDIO X2E DRONES FOR PLANT INSP | E10553569 | MLWNPTOOL | 1070001 | 2023-01-30 | 137400.2 | 132912.19 | 0 | 4488.01
MLP | CLOSE | MLU 0 PURCHASE LAB CPS SECONDARY POLYMER SKID DUMPER | E10553489 | MLWNPTOOL | 1070001 | 2023-01-11 | 1952.23 | 1897.2 | 0 | 55.03
MLP | CLOSE | MLU0 PURCHASE SULLAIR 185CFM AIR COMPRESSOR | E10550033 | MLWNPTOOL | 1070001 | 2024-03-12 | -19744.58 | 800 | 0 | -20544.58
MLP | CLOSE | MLU0 THERMOLYNE FURNACE | E10545276 | MLWNPTOOL | 1070001 | 2022-12-15 | 4099.36 | 3980 | 0 | 119.36
MLP | CLOSE | MLU0 PURCHASE BALL MILL REJECT ROTARY DUMPER | E10545275 | MLWNPTOOL | 1070001 | 2023-02-01 | 26414.67 | 25509.49 | 0 | 905.18
MLP | CLOSE | MLU0 PULVERIZER ROLL WHEEL STANDS (3) | E10541674 | MLWNPTOOL | 1070001 | 2022-11-20 | 23556.34 | 22350 | 0 | 1206.34
MLP | CLOSE | MLP CAP SPARE RETIREMENTS/WRITE OFF | E10539635 | MLWNPTOOL | 1070001 | 2024-12-09 | 38285.2 | -91871 | 121.36 | 130034.84
MLP | CLOSE | MLP CP WO MATERIAL CORRECTIONS | E10539634 | MLWNPTOOL | 1070001 | 2024-09-30 | 92943.27 | 85859.48 | 0 | 7083.79
MLP | CLOSE | MLU0 - FUEL MANAGEMENT SYSTEM PURCHASE/INSTALL | E10539626 | MLWNPTOOL | 1070001 | 2023-02-21 | 185030.12 | 113390.02 | 65196.04 | 6444.06
MLP | CLOSE | MLU0 Purchase ISCO sampler for new sample point, CPS effluent discharge | E10539612 | MLWNPTOOL | 1070001 | 2023-02-14 | 6388.36 | 6197 | 0 | 191.36
MLP | CLOSE | MLU0 PURCHASE 2 TREX UNITS FOR ICE SHOP | E10539588 | MLWNPTOOL | 1070001 | 2023-03-15 | 32319.79 | 30153.9 | 0 | 2165.89
MLP | CLOSE | MLU0 ICE - PURCHASE CAPITAL TOOLS (LIST IN LONG DESC) | E10539587 | MLWNPTOOL | 1070001 | 2022-09-20 | 42419.05 | 39361.1 | 0 | 3057.95
MLP | CLOSE | MLU0 PURCHASE FILTER FOR METAL CLEANING WASTE BLDG | E10539583 | MLWNPTOOL | 1070001 | 2023-04-26
MLP | CLOSE | MLU0 PURCHASE MAN OVERBOARD ALERT SYSTEM FOR RIVER WORK | E10539573 | MLWNPTOOL | 1070001 | 2022-09-29 | 11312.3 | 10917 | 0 | 395.3
MLP | CLOSE | MLU0 PURCHASE HELIUM LEAK DETECTOR | E10539543 | MLWNPTOOL | 1070001 | 2022-10-11 | 29097.34 | 26573.99 | 0 | 2523.35
MLP | CLOSE | MLU0 LAB STORE ROOM FLAMMABLE CABINET | E10539541 | MLWNPTOOL | 1070001 | 2022-10-18 | 3253.74 | 2855.06 | 0 | 398.68
MLP | COMP | MLU0 PURCHASE VALVE EXERCISER TOOL FOR FGD VALVES | E10539533 | MLWNPTOOL | 1070001 | 2023-04-26
MLP | CLOSE | MLU0 ELECTRIC STACKER BATTERY REPLACEMENT | E10539528 | MLWNPTOOL | 1070001 | 2022-11-13 | 5956.59 | 5474 | 268.49 | 214.1
MLP | CLOSE | MLU0 PURCHASE GENERAC MLT6SKDS LIGHT TOWER | E10539505 | MLWNPTOOL | 1070001 | 2022-09-29 | 13543.44 | 12900 | 0 | 643.44
MLP | CLOSE | MLU0 HAWKER FORK TRUCK BATTERY REPLACEMENT | E10539493 | MLWNPTOOL | 1070001 | 2022-11-07 | 7794.22 | 7346 | 0 | 448.22
MLP | CLOSE | MLU0 PURCH 2 YSI HAND HELD CONDUCTIVITY/PH METERS | E10539483 | MLWNPTOOL | 1070001 | 2023-08-15
MLP | CLOSE | MLU0 ICE PROCESS METER, CALIBRATION METER, GOLF CARTS | E10539482 | MLWNPTOOL | 1070001 | 2022-03-10 | 26138.58 | 24051 | 0 | 2087.58
MLP | CLOSE | MLU0 PURCHASE 2 FLIR E6XT INFARED CAMERAS | E10539471 | MLWNPTOOL | 1070001 | 2023-04-26
MLP | CLOSE | MLP U0: MAINT STORAGE BLDG HEATER REPLACEMENT | E10870486 | MLWNPWINT | 1070001 | 2025-03-04 | 2573.42 | 1810.5 | 622.56 | 140.36
MLP | CLOSE | MLP U0: REPLACE DOORS AT DELUGE HOUSES & TRANSFER STATION | E10869634 | MLWNPWINT | 1070001 | 2025-03-18 | 15926.21 | 7446 | 7576.14 | 904.07
MLP | CLOSE | MLP U0: CHLORINE DIOXIDE GEN TOTE HEATERS WINTERIZATION | E10843375 | MLWNPWINT | 1070001 | 2024-12-18 | 10661.11 | 4933.17 | 5317.81 | 410.13
MLP | CLOSE | MLP U2: ID FAN WINTERIZATION HEATERS | E10842345 | MLWNPWINT | 1070001 | 2024-12-09 | 10455.91 | 6614.58 | 3587.77 | 253.56
MLP | CLOSE | MLP U1: ID FAN WINTERIZATION HEATERS | E10842342 | MLWNPWINT | 1070001 | 2024-12-09 | 10455.92 | 6614.58 | 3587.78 | 253.56
MLP | COMP | MLP U0 BIOREACTOR HEAT TRACE & INSULATION INSTALL | E10839739 | MLWNPWINT | 1070001 | 2024-12-30 | 207790.62 | 54556.16 | 141985.03 | 11249.43
MLP | CLOSE | MLP U0: CHLORINE HOUSE SERVICE WATER LINE HEAT TRACE | E10785813 | MLWNPWINT | 1070001 | 2024-08-02 | 12843.32 | 9008.52 | 2645.32 | 1189.48
MLP | CLOSE | MLP - U0: PURCHASE 2 HEATERS FOR AZOLE COPPER CHEM TOTES | E10713605 | MLWNPWINT | 1070001 | 2024-01-25 | 6205.76 | 5965.48 | 0 | 240.28
MLP | CLOSE | MLP U0 - Reclaim/Makeup Water Tank Piping Heat Trace | E10709383 | MLWNPWINT | 1070001 | 2023-12-27 | 23715.47 | 1743.01 | 21039.42 | 933.04
MLP | CLOSE | MLP U0 - 2023 DIVERTER VALVE WINTERIZATION | E10709180 | MLWNPWINT | 1070001 | 2023-12-27 | 16437.31 | 4872.63 | 10896.38 | 668.3
MLP | CLOSE | MLP - U2 CONTROL AIR DEWPOINT MONITOR & WIRE RUN | E10702189 | MLWNPWINT | 1070001 | 2023-11-20 | 38816.62 | 8331.91 | 29405.03 | 1079.68
MLP | CLOSE | MLP - U1 CONTROL AIR DEWPOINT MONITOR & WIRE RUN | E10702188 | MLWNPWINT | 1070001 | 2023-12-01 | 37525.84 | 8654.9 | 27669.26 | 1201.68
MLP | CLOSE | MLP U0: DSI DX SKID COMMON HEADER INSTALLATION | E10760287 | MLWOPFGDP | 1070001 | 2024-05-03 | 46565.11 | 5893.8 | 36778.44 | 3892.87
MLP | CLOSE | MLP U1: #12 ID FAN REG END HUB W/ NEW SHELL & INTERNALS | E10757760 | MLWOPFGDP | 1070001 | 2024-06-07 | 235537.01 | 46497.02 | 143177.16 | 45862.83
MLP | CLOSE | MLP U0: RECLAIM TANK B - INTERNAL COATING | E10755142 | MLWOPFGDP | 1070001 | 2024-06-07 | 226115.18 | 61384.73 | 144431.86 | 20298.59
MLP | CLOSE | MLP U2: #21 ID FAN HYDRAULIC CYLINDER | E10755119 | MLWOPFGDP | 1070001 | 2024-05-17 | 91691.28 | 17873.85 | 59212.51 | 14604.92
MLP | CLOSE | MLP - U2: DSI DIVERTER GATE REPLACEMENT | E10755063 | MLWOPFGDP | 1070001 | 2024-06-06 | 70194.95 | 27048.44 | 30527.03 | 12619.48
MLP | CLOSE | MLP -U1: DSI DIVERTER GATE REPLACEMENT | E10755046 | MLWOPFGDP | 1070001 | 2024-05-23 | 73214.32 | 26596.6 | 34827.21 | 11790.51
MLP | CLOSE | MLP 2F ABSORBER AGITATOR GEARBOX REPLACEMENT | E10752121 | MLWOPFGDP | 1070001 | 2024-05-17 | 51879.83 | 43712.58 | 3725.87 | 4441.38
MLP | CLOSE | MLP U1: #12 ID FAN HYDRAULIC CYLINDER (CSP) | E10749162 | MLWOPFGDP | 1070001 | 2024-06-03 | 83176.49 | 15935.07 | 57725.02 | 9516.4
MLP | CLOSE | MLP - U0: PRIMARY CLARIFIER SLUDGE PUMP #3 | E10710362 | MLWOPFGDP | 1070001 | 2023-11-15 | 13454.16 | 11326 | 1388.67 | 739.49
MLP | CLOSE | MLU0 FGD SERVICE WATER PUMP A | E10705652 | MLWOPFGDP | 1070001 | 2023-11-03 | 12288.31 | 10619 | 1395.04 | 274.27
MLP | CLOSE | MLU2 #22 ID FAN HYDRAULIC CYLINDER | E10683308 | MLWOPFGDP | 1070001 | 2023-11-05 | 118887.9 | 24459.18 | 88188.34 | 6240.38
MLP | CLOSE | MLU0 RECLAIM TANK A INTERNAL COATING | E10648184 | MLWOPFGDP | 1070001 | 2023-12-07 | 275909.36 | 54807.78 | 208058.42 | 13043.16
MLP | CLOSE | MLU0 OXIDATION AIR BLOWER DSCHGE VLV ZOAS 8001 | E10615470 | MLWOPFGDP | 1070001 | 2023-05-14 | 27928.44 | 16507.2 | 10388.55 | 1032.69
MLP | CLOSE | MLU2 PLANT AIR DRYER INSTALLATION | E10539538 | MLWOPFGDP | 1070001 | 2023-06-16 | 587380.27 | 289237.91 | 272824.81 | 25317.55
MLP | CLOSE | MLP U2: CC2 TRANMITTER & RECORDER TO MONITOR VOLTAGE | E10802596 | MLWOPNONP | 1070001 | 2024-10-08 | 11645.37 | 10230.6 | 801.31 | 613.46
MLP | CLOSE | MLP U2: 21 PENTHOUSE SEAL AIR FAN EXP JOINT | E10802595 | MLWOPNONP | 1070001 | 2024-10-02 | 2984.65 | 2187.13 | 664.73 | 132.79
MLP | CLOSE | MLP U2: CIRC WATER & RIVER WATER SUPPLY HSO | E10777070 | MLWOPNONP | 1070001 | 2025-02-10 | 10851.39 | 7204.2 | 2884.62 | 762.57
MLP | CLOSE | MLU2 NERC Protective Relay Replacement | E10775734 | MLWOPNONP | 1070001 | 2024-07-03 | 7936.27 | 7150 | 0 | 786.27
MLP | CLOSE | MLU1 7B heater safety valve replacement | E10764279 | MLWOPNONP | 1070001 | 2024-05-18 | 1045.67 | 0 | 989.27 | 56.4
MLP | CLOSE | MLU1 7A heater safety valve replacement | E10764074 | MLWOPNONP | 1070001 | 2024-05-18 | 22759.83 | 13890.51 | 4745 | 4124.32
MLP | CLOSE | MLP U2: #22 RAW COAL CHUTE AND SILO GATE | E10762667 | MLWOPNONP | 1070001 | 2024-06-05 | 52316.87 | 35241.38 | 7570.61 | 9504.88
MLP | CLOSE | MLP U1: WASTE WATER SUMP PUMP REPLACE | E10754721 | MLWOPNONP | 1070001 | 2024-05-24 | 40413.18 | 22967.25 | 10040.64 | 7405.29
MLP | CLOSE | MLP U2: BRV-5 POWER RELIEF VALVE REPLACE | E10746723 | MLWOPNONP | 1070001 | 2024-10-14 | 113914.99 | 78269.19 | 29677.82 | 5967.98
MLP | CLOSE | MLP U1: BRV-5 POWER RELIEF VALVE REPLACE | E10746719 | MLWOPNONP | 1070001 | 2024-09-15 | 97297.34 | 64158.88 | 28421.72 | 4716.74
MLP | CLOSE | MLU1 #8 CONVEYOR GEARBOX REPLACEMENT | E10711973 | MLWOPNONP | 1070001 | 2023-11-27 | 12702.61 | 11081.07 | 1267.96 | 353.58
MLP | CLOSE | MLP - U0 AUX BOILER TIE HEADER BYPASS VALVE | E10708155 | MLWOPNONP | 1070001 | 2023-11-08 | 4501.41 | 3377.41 | 1018.53 | 105.47
MLP | CLOSE | MLP - U2: PRECIP BOX 4 HOPPER 1-5 | E10706078 | MLWOPNONP | 1070001 | 2023-11-09 | 7551.37 | 6372.32 | 960.96 | 218.09
MLP | CLOSE | MLP - U2 PRECIP BOX 4 HOPPER 1-4 VALVE REPLACE | E10705649 | MLWOPNONP | 1070001 | 2023-11-02 | 7039.57 | 6314.3 | 573.12 | 152.15
MLP | CLOSE | MLU1 BOX 2 ROW 2 HOPPER 1 GATE VALVE REPLACEMENT | E10695671 | MLWOPNONP | 1070001 | 2023-11-09 | 11690.64 | 6372.32 | 5004.35 | 313.97
MLP | CLOSE | MLU2 AIR COMPRESSOR HSO - REPLACEMENT | E10695573 | MLWOPNONP | 1070001 | 2023-10-13 | 1998.1 | 1187.47 | 750.48 | 60.15
MLP | CLOSE | MLU1 BOX 1 ROW 1 HOPPER 2 GATE VALVE REPLACEMENT | E10695550 | MLWOPNONP | 1070001 | 2023-10-06 | 7253.48 | 6382 | 691.29 | 180.19
MLP | CLOSE | MLU2 BOX 3 ROW 1 HOPPER 1 RECEIVING GATE | E10677489 | MLWOPNONP | 1070001 | 2023-10-30 | 4344.31 | 4224 | 0 | 120.31
MLP | CLOSE | MLU1 #50 SAFETY VALVE REPLACEMENT (CSP) | E10648483 | MLWOPNONP | 1070001 | 2023-11-07 | 55981.61 | 8892.65 | 45907.63 | 1181.33
MLP | CLOSE | MLU2 INSTALL BREAKER & CABLE FROM TBG TO DISCONNECT | E10639669 | MLWOPNONP | 1070001 | 2023-11-14 | 4022.19 | 1879.49 | 2028.74 | 113.96
MLP | CLOSE | MLU1 INSTALL BREAKER & CABLE FROM TBG TO DISCONNECT | E10639668 | MLWOPNONP | 1070001 | 2024-01-03 | 3291.83 | 1620.74 | 1400.07 | 271.02
MLP | CLOSE | MLU2 BOX 4 TRANSFER STATION A & B BAG REPLACEMENT 1 SET EA | E10635698 | MLWOPNONP | 1070001 | 2023-10-11 | 18881.38 | 15571.2 | 2171.29 | 1138.89
MLP | CLOSE | MLU2 26F BURNER SLIP JOINT REPLACEMENT | E10635597 | MLWOPNONP | 1070001 | 2023-11-03 | 39844.76 | 28314.66 | 10519.37 | 1010.73
MLP | CLOSE | MLU2 RRV-01 ACTUATOR REPLACEMENT | E10635257 | MLWOPNONP | 1070001 | 2023-06-20 | 14005.69 | 14270 | 0 | -264.31
MLP | CLOSE | MLU2 - 24 & 25 COAL SILO RAW COAL CHUTE REPLACEMENT | E10630134 | MLWOPNONP | 1070001 | 2023-11-19 | 16166.97 | 12401.25 | 3327.27 | 438.45
MLP | CLOSE | MLU1 12, 14, & 15 COAL SILO RAW COAL CHUTE REPLACE | E10630129 | MLWOPNONP | 1070001 | 2023-11-30 | 26668.19 | 12768 | 13027.09 | 873.1
MLP | CLOSE | MLU2 Replace Boiler Feed Pump Rotating Element (CSP) | E10619554 | MLWOPNONP | 1070001 | 2023-04-05 | 145669.49 | 23066.85 | 25857.76 | 96744.88
MLP | CLOSE | MLU2 BFP ROTATING ELEMENT REBUILD | E10619232 | MLWOPNONP | 1070001 | 2023-12-01 | 299888.07 | 241102.68 | 20271.08 | 38514.31
MLP | CLOSE | MLU2 UPGRADE ION METERS TO ION 9000 | E10610217 | MLWOPNONP | 1070001 | 2023-11-02 | 160486.41 | 101886.27 | 34394.1 | 24206.04
MLP | CLOSE | MLU1 UPGRADE ION METERS TO ION 9000 | E10610215 | MLWOPNONP | 1070001 | 2023-11-02 | 168612.8 | 109733.43 | 34533.96 | 24345.41
MLP | CLOSE | MLU1 PURCHASE #58 SAFETY VALVE | E10601145 | MLWOPNONP | 1070001 | 2023-11-22 | 80828.23 | 67228.68 | 11376.7 | 2222.85
MLP | CLOSE | MLU1 PURCHASE BRV-5 VALVES | E10601144 | MLWOPNONP | 1070001 | 2023-12-04 | 119256.48 | 92188.88 | 22677.45 | 4390.15
MLP | CLOSE | MLU2 22 AIR HEATER GEARBOX REPLACE | E10567475 | MLWOPNONP | 1070001 | 2023-06-06 | 53190.96 | 29326.6 | 21106.13 | 2758.23
MLP | CLOSE | MLU2 CORESENSE M10 REPLACEMENT | E10539602 | MLWOPNONP | 1070001 | 2022-11-30 | 67987.66 | 55945.55 | 8612.1 | 3430.01
MLP | CLOSE | MLU2 RAW COAL CHUTE REPLACEMENT | E10539596 | MLWOPNONP | 1070001 | 2022-12-22 | 25039.8 | 23725.07 | 0 | 1314.73
MLP | CLOSE | MLU1 RAW COAL CHUTE REPLACEMENT | E10539593 | MLWOPNONP | 1070001 | 2022-12-22 | 12376.23 | 11722.49 | 0 | 653.74
MLP | CLOSE | MLU2 Install Turbine Room Lights | E10539559 | MLWOPNONP | 1070001 | 2022-09-30 | 260922.38 | 143511.33 | 104011.11 | 13399.94
MLP | CLOSE | MLU1 PHASE 3 CORESENSE M10 MONITOR | E10539542 | MLWOPNONP | 1070001 | 2022-11-30 | 80171.94 | 61692.86 | 11865.26 | 6613.82
MLP | CLOSE | MLU1 PRECIP PWER FEED | E10539539 | MLWOPNONP | 1070001 | 2022-12-01 | 200629.89 | 107393.67 | 79239.16 | 13997.06
MLP | CLOSE | MLU122 HIGH ENERGY PIPING INSPECTION | E10539536 | MLWOPNONP | 1070001 | 2022-11-11 | 406769.11 | 80792.55 | 304677.32 | 21299.24
MLP | CLOSE | MLU2 CIRC WATER RELAY UPGRADE | E10539504 | MLWOPNONP | 1070001 | 2023-11-22 | 67502.89 | 13285.62 | 38630.91 | 15586.36
MLP | CLOSE | MLP U2: INFRA-VIEW STARTUP PROBE REPLACEMENT | E10794205 | MLWOPSOOT | 1070001 | 2024-09-12 | 11266.23 | 10056.99 | 0 | 1209.24
MLP | INSERV | ML0 CCR Compliance | E10567546 | MLWPC0ELG | 1070001 | 2024-09-10 | 40497043.733 | 2927505.58 | 27277829.4 | 10291708.753
MLP | INSERV | ML0 ELG Compliance | E10539457 | MLWPC0ELG | 1070001 | 2024-08-05 | 48851799.15 | 1624146.41 | 41547052.09 | 5680600.65
MLP | INSERV | ML0 CCR Compliance | E10539454 | MLWPC0ELG | 1070001 | 2024-09-10 | -4602.09 | 1024.56 | 25205.3 | -30831.95
MLP | INSERV | ML ELG Cmplianc Bottom Ash Pond | E10539452 | MLWPC0ELG | 1070001 | 2023-11-18 | 78842591.77 | 5212516.93 | 64065741.74 | 9564333.1
MLP | CLOSE | ML2 Hydrated Lime Conversion Project | E10539450 | MLWPC0LIM | 1070001 | 2022-12-14 | 5650633.96 | 128569.63 | 4421251.64 | 1100812.69
MLP | CLOSE | ML1 Hydrated Lime Conversion Prj | E10539449 | MLWPC0LIM | 1070001 | 2023-05-30 | 7084196.04 | 271506.58 | 5752935.69 | 1059753.77
MLP | CLOSE | ML1 Catalyst Replacement | E10539460 | MLWPC1CL4 | 1070001 | 2021-12-15 | 2702236.84 | 67411.54 | 2141439.8 | 493385.5
MLP | CLOSE | ML2 E Cooling Tower Components | E10539477 | MLWPC2CTC | 1070001 | 2022-12-16 | 8177797.9 | 85384.77 | 7071469.81 | 1020943.32
MLP | CLOSE | ML2 ESP PURGE AIR HEATER | E10539465 | MLWPC2ESP | 1070001 | 2022-12-17 | 7438538.62 | 2038609.74 | 4408108.01 | 991820.87
MLP | COMP | ML U1 Cooling Twr Canopy Rep | E10745400 | MLWPCT1BP | 1070001 | 2024-05-31 | 4372009.04 | 1342922.94 | 2614891.87 | 414194.23
MLP | CLOSE | MLP -U1 CT CANOPY MATERIAL ONLY (PRE CI WO) | E10713645 | MLWPCT1PC | 1070001 | 2025-01-09 | 1226.61 | 0 | 0 | 1226.61
MLP | CLOSE | ML U1 Air Heater Basket | E10539599 | MLWSC1AHB | 1070001 | 2023-12-30 | 5510861.31 | 219314.36 | 4638490.55 | 653056.4
MLP | CLOSE | ML2 AIR HEATER BASKET REPLACEMENT | E10539464 | MLWSC2AHB | 1070001 | 2022-12-13 | 6446613.07 | 2255141.26 | 3414739.58 | 776732.23
MLP | CLOSE | MLU2 Install Weld Overlay in Lower Furnace | E10539560 | MLWSP2LSO | 1070001 | 2022-12-01 | 1388024.42 | 413215.96 | 934559.53 | 40248.93
MLP | CLOSE | MLP U2: ASH PIT SUMP LEVEL CONTROL UPGRADE | E10878775 | MLWSPASHL | 1070001 | 2025-03-05 | 9004.35 | 5270 | 3166.8 | 567.55
MLP | CLOSE | MLU2 PRECIP NEUNDORFER POS REPLACEMENT | E10539474 | MLWSPASHL | 1070001 | 2022-10-01 | 16689.1 | 13480 | 0 | 3209.1
MLP | CLOSE | MLU2 22A BURNER SLIP JOINT REPLACEMENT | E10539615 | MLWSPBRNE | 1070001 | 2022-11-20 | 2181.13 | 0 | 2117.08 | 64.05
MLP | COMP | MLP U1: #12 COAL SILO GATE REPLACEMENT | E10840522 | MLWSPBRNN | 1070001 | 2025-05-01 | 32728.48 | 20932.83 | 9016.16 | 2779.49
MLP | COMP | MLP U1: PULV CAPACITY DAMPER REPLACEMENT | E10840385 | MLWSPBRNN | 1070001 | 2025-05-07 | 102512.44 | 38527.94 | 56778.73 | 7205.77
MLP | COMP | MLP U1: PULV PA DAMPER REPLACEMENT | E10840380 | MLWSPBRNN | 1070001 | 2025-05-07 | 107414.67 | 42570.16 | 56996.65 | 7847.86
MLP | COMP | MLP U1: 48 OIL LIGHTER ASSEMBLIES | E10840298 | MLWSPBRNN | 1070001 | 2025-05-13 | 453945.5 | 364925.46 | 47997.44 | 41022.6
MLP | COMP | MLP U1: #12 RAW COAL PIPE REPLACEMENT | E10840297 | MLWSPBRNN | 1070001 | 2025-05-01 | 21377.96 | 15974.23 | 3418.58 | 1985.15
MLP | COMP | MLP U1 & U2: SLIP JOINT REPLACEMENTS | E10840191 | MLWSPBRNN | 1070001 | 2025-05-03 | 176203.31 | 87630.08 | 78348.16 | 10225.07
MLP | CLOSE | MLP U2: 12 BURNER OIL LIGHTER ASSEMBLIES - REPLACE | E10795959 | MLWSPBRNN | 1070001 | 2024-09-25 | 100728.17 | 91908.7 | 4751.17 | 4068.3
MLP | CLOSE | MLP U2: 26F BURNER SLIP JOINT REPLACEMENT | E10786930 | MLWSPBRNN | 1070001 | 2024-10-09 | 19766.75 | 18632 | 0 | 1134.75
MLP | CLOSE | MLP U2: 22E BURNER SLIP JOINT REPLACEMENT | E10766902 | MLWSPBRNN | 1070001 | 2024-05-08 | 13937.92 | 9709.16 | 1343.88 | 2884.88
MLP | CLOSE | MLP U1: 16A, 16B, 16C BURNER SLIP JOINT REPLACEMENT | E10754728 | MLWSPBRNN | 1070001 | 2024-06-05 | 102088.19 | 46017.04 | 39062.67 | 17008.48
MLP | CLOSE | MLP U2: 26A, 26B, 26F BURNER SLIP JOINT REPLACEMENT | E10754723 | MLWSPBRNN | 1070001 | 2024-10-13 | 170276.55 | 35779.46 | 118832.27 | 15664.82
MLP | CLOSE | MLP U1: #16 COAL SILO GATE REPLACEMENT | E10754717 | MLWSPBRNN | 1070001 | 2024-06-05 | 37575.08 | 19590.81 | 11069.48 | 6914.79
MLP | CLOSE | MLP U1 REPLACE 12 BURNER OIL LIGHTER ASSEMBLIES | E10752248 | MLWSPBRNN | 1070001 | 2024-06-05 | 137101.07 | 98032.06 | 15430.73 | 23638.28
MLP | CLOSE | MLP U2: REPLACE 13 BURNER NOZZLES | E10752098 | MLWSPBRNN | 1070001 | 2024-10-01 | 654315.09 | 424084.66 | 184331.68 | 45898.75
MLP | CLOSE | MLU1 - #16 COAL FEEDER RAW COAL CHUTE | E10751276 | MLWSPBRNN | 1070001 | 2024-06-05 | 17319.43 | 13284.82 | 916.51 | 3118.1
MLP | CLOSE | MLU2 - #25 COAL FEEDER RAW COAL CHUTE | E10751271 | MLWSPBRNN | 1070001 | 2024-06-05 | 24553.48 | 14054 | 6054.41 | 4445.07
MLP | CLOSE | MLU1 LABOR TO I/R 24 BURNER NOZZLES | E10677431 | MLWSPBRNN | 1070001 | 2023-11-24 | 590710.2 | 63794.41 | 507679.37 | 19236.42
MLP | CLOSE | MLU1 PURCHASE 24 BURNER NOZZLES | E10573704 | MLWSPBRNN | 1070001 | 2023-08-08 | 353669.66 | 332482.1 | 0 | 21187.56
MLP | CLOSE | MLU1 11F BURNER NOZZLE TIP & THERMOCOUPLE REPLACEMENT | E10555517 | MLWSPBRNN | 1070001 | 2022-11-29 | 14881.31 | 8282.67 | 6125.06 | 473.58
MLP | CLOSE | MLU1 PLANT AIR DRYER INSTALLATION | E10539537 | MLWSPBRNN | 1070001 | 2023-06-16 | 568108.96 | 240493.94 | 298216.84 | 29398.18
MLP | CLOSE | MLU2 BURNER NOZZLE PURCHASE | E10539485 | MLWSPBRNN | 1070001 | 2022-12-21 | 550547.76 | 196937.65 | 319964.31 | 33645.8
MLP | COMP | MLP U1: SGC DEWATERING & COLLECTION CHAIN REPLACEMENT | E10840742 | MLWSPCCHN | 1070001 | 2025-05-13 | 501185.07 | 388431.61 | 72129.95 | 40623.51
MLP | CLOSE | MLP U2: BOX 3 TRANSFER STATION C FILTER BAG REPLACE | E10814246 | MLWSPDFAF | 1070001 | 2024-09-25 | 3114.01 | 1632 | 1370.53 | 111.48
MLP | CLOSE | MLP U2: BOX 3 TRANSFER STATION D FILTER BAG REPLACE | E10814245 | MLWSPDFAF | 1070001 | 2024-09-25 | 11963.88 | 10458 | 1010.08 | 495.8
MLP | CLOSE | MLU2 3D DFA FILTER BAG REPLACEMENT | E10539608 | MLWSPDFAF | 1070001 | 2022-11-05 | 8635.87 | 8055 | 147.92 | 432.95
MLP | CLOSE | MLU2 3C DFA FILTER BAG REPLACEMENT | E10539607 | MLWSPDFAF | 1070001 | 2022-09-23 | 12219.31 | 5619.6 | 6017.17 | 582.54
MLP | CLOSE | MLU1 2D DFA FILTER BAG REPLACEMENT | E10539606 | MLWSPDFAF | 1070001 | 2022-10-18 | 8764.52 | 5619.6 | 2746.54 | 398.38
MLP | CLOSE | MLU1 DFA FILTER BAG 1B REPLACEMENT | E10539605 | MLWSPDFAF | 1070001 | 2022-10-17 | 11001.9 | 9189.6 | 1383.45 | 428.85
MLP | CLOSE | MLU1 PENTHOUSE CASING INSULATION | E10584607 | MLWSPDUCT | 1070001 | 2023-02-15 | 141508.66 | 9198.22 | 126759.11 | 5551.33
MLP | COMP | MLP U1: TWO #16 PULV EXP JOINTS | E10843211 | MLWSPEJNT | 1070001 | 2025-05-13 | 77532.06 | 33217.61 | 39948.93 | 4365.52
MLP | CLOSE | MLP U2: ABSORBER OUTLET EXP JNT REPLACEMENT | E10840520 | MLWSPEJNT | 1070001 | 2024-12-19 | 25498.32 | 24880 | 0 | 618.32
MLP | CLOSE | MLP U2: MECHANICAL EXHAUSTER 1 EXP JOINT | E10804072 | MLWSPEJNT | 1070001 | 2024-09-25 | 3078.83 | 2954 | 0 | 124.83
MLP | CLOSE | MLP - U1 #12 ID FAN INLET HORIZONATAL EXP JOINT | E10690975 | MLWSPEJNT | 1070001 | 2023-11-04 | 45734.74 | 17391 | 26952.14 | 1391.6
MLP | CLOSE | MLU1 #12A BURNER SLIP JOINT | E10649003 | MLWSPEJNT | 1070001 | 2023-07-20 | 19122.36 | 9320 | 8253.23 | 1549.13
MLP | CLOSE | MLU1 FGX-72009 EJ & FRAME DOWNSTREAM OF ID FANS | E10648181 | MLWSPEJNT | 1070001 | 2024-10-14 | 237486.23 | 70143.15 | 154924.88 | 12418.2
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ1 JOINT & FRAME ON 1A | E10648179 | MLWSPEJNT | 1070001 | 2023-11-11 | 395857.38 | 78427.64 | 303794.68 | 13635.06
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ2 JOINT & FRAME ON 1B | E10648178 | MLWSPEJNT | 1070001 | 2023-11-11 | 309475.75 | 82842.82 | 213916.18 | 12716.75
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ3 JOINT & FRAME ON 2A | E10648177 | MLWSPEJNT | 1070001 | 2023-11-11 | 421966.88 | 136849.59 | 270461.92 | 14655.37
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ4 JOINT & FRAME ON 2B | E10648174 | MLWSPEJNT | 1070001 | 2023-11-11 | 429565.87 | 82403.58 | 317053.24 | 30109.05
MLP | CLOSE | ML U2A AR PUMP DISCHARGE EXP JOINT REPLACE | E10552765 | MLWSPEJNT | 1070001 | 2022-12-07 | 14043.76 | 13617.22 | 0 | 426.54
MLP | CLOSE | MLU1 AR PUMP DISCHARGE EXP JOINT REPLACE | E10552039 | MLWSPEJNT | 1070001 | 2022-12-01 | 13470.98 | 13060 | 0 | 410.98
MLP | CLOSE | MLU0 AUX BOILER FD FAN EXPANSION JOINT - EJ1 | E10539636 | MLWSPEJNT | 1070001 | 2022-11-20 | 34263.63 | 429.44 | 32809.13 | 1025.06
MLP | CLOSE | MLU0 Replace #3 RWMU Discharge expansion joint | E10539633 | MLWSPEJNT | 1070001 | 2023-04-26
MLP | CLOSE | MLU2 PENTHOUSE SEAL AIR FAN OUTLET EXP JNT REPLACE | E10539566 | MLWSPEJNT | 1070001 | 2022-12-01 | 44529.1 | 19207 | 23916.99 | 1405.11
MLP | CLOSE | MLU2 SCR EXP JNTS EJF01, EJF02, EJF05, EJF15, EJF16, EJF25 REPLACE | E10539565 | MLWSPEJNT | 1070001 | 2022-12-01 | 473340.22 | 116938.77 | 335230.74 | 21170.71
MLP | CLOSE | MLU1 PENTHOUSE SEAL AIR FAN EJ'S (2 INLET/1 OUTLET REPLACE | E10539564 | MLWSPEJNT | 1070001 | 2022-12-01 | 50742.59 | 15784.05 | 33005.34 | 1953.2
MLP | CLOSE | MLU1 SCR EXP JNTS EJF14, EJF15, EJ115 REPLACE | E10539563 | MLWSPEJNT | 1070001 | 2022-12-01 | 198778.73 | 61344.82 | 129244.47 | 8189.44
MLP | CLOSE | MLU1 FGD EXP JNTS EJ-FGX-71009 ID FAN TO ABSORBER INLET | E10539562 | MLWSPEJNT | 1070001 | 2022-12-01 | 196439.56 | 78005.63 | 110630.83 | 7803.1
MLP | CLOSE | MLP - U2: 22 AIR HEATER MOTOR REPLACEMENT | E10736911 | MLWSPFANS | 1070001 | 2024-03-05 | 6791.54 | 600 | 6846.83 | -655.29
MLP | CLOSE | MLU2 #23 DFA MECHANICAL EXHAUSTER REPLACEMENT | E10539502 | MLWSPFANS | 1070001 | 2023-04-26
MLP | COMP | MLP U1: 2-A6 CS RAPPER GEAR BOX REPLACEMENT | E10901921 | MLWSPGRBX | 1070001 | 2025-04-29 | 3299.1 | 3145.57 | 0 | 153.53
MLP | COMP | MLP U1: CS RAPPER S-B3 GEARBOX REPLACEMENT | E10890747 | MLWSPGRBX | 1070001 | 2025-04-15 | 4040.42 | 3769.19 | 78.9 | 192.33
MLP | CLOSE | MLP U2: PRECIP CS RAPPER GEARBOX REPLACEMENT | E10879852 | MLWSPGRBX | 1070001 | 2025-02-18 | 3506.85 | 3145.57 | 169.54 | 191.74
MLP | CLOSE | MLU1 REPLACE SPEED REDUCER ON CS RAPPER | E10692796 | MLWSPGRBX | 1070001 | 2023-11-03 | 3186.73 | 3101.48 | 0 | 85.25
MLP | CLOSE | MLP U1: 13 PA DIFF TRANSMITTER REPLACEMENT | E10784145 | MLWSPNPPB | 1070001 | 2024-07-14 | 2393.72 | 2220.71 | 0 | 173.01
MLP | CLOSE | MLU2 - oil skid compressed air pre-filters and burner deck corner filters | E10633321 | MLWSPNPPB | 1070001 | 2024-05-15 | 171208.2 | 45582.92 | 111551.46 | 14073.82
MLP | CLOSE | MLU1 - oil skid compressed air pre-filters and burner deck corner filters | E10633316 | MLWSPNPPB | 1070001 | 2024-05-28 | 181453.48 | 56401.85 | 111838.44 | 13213.19
MLP | CLOSE | MLP: U2 I/R BOX 3 HOPPER 2-3 DIFFUSER FEEDER SWING GATE VALVE | E10821992 | MLWSPPHCH | 1070001 | 2024-09-25 | 6711.66 | 6439.55 | 0 | 272.11
MLP | COMP | MLP U1: PURCHASE 16 PA CAPACITY DAMPER | E10834367 | MLWSPPULV | 1070001 | 2025-05-01 | 38096.88 | 29826 | 765.53 | 7505.35
MLP | COMP | MLP U1: PURCHASE 16 PA CAPACITY DAMPER | E10834367 | MLWSPPULV | 1070001 | 2025-05-01 | 76856.67 | 6406.45 | 70425.76 | 24.46
MLP | COMP | MLP U1: PURCHASE 16 PA SHUTOFF DAMPER | E10834365 | MLWSPPULV | 1070001 | 2025-05-01 | 77737.19 | 38374.94 | 34034.73 | 5327.52
MLP | CLOSE | MLP U2: 21 PULVERIZER MOTOR REBUILD | E10814282 | MLWSPPULV | 1070001 | 2025-01-21 | 94354.6 | 61055.81 | 16415.92 | 16882.87
MLP | CLOSE | MLP U2: 21 PULV MOTOR REPLACE (CSP) | E10800647 | MLWSPPULV | 1070001 | 2024-08-02 | 10816.1 | 4199.35 | 6028.5 | 588.25
MLP | CLOSE | MLP U1: #16 PULVERIZER MOTOR REWIND | E10745313 | MLWSPPULV | 1070001 | 2024-08-12 | 188938.24 | 52430.76 | 61457 | 75050.48
MLP | CLOSE | MLP - PURCHASE PULV CAPACITY DAMPER | E10743063 | MLWSPPULV | 1070001 | 2024-10-01 | 84530.05 | 33315.88 | 47339.08 | 3875.09
MLP | CLOSE | MLP - U1 PURCHASE PA SHUT OFF DAMPER | E10736512 | MLWSPPULV | 1070001 | 2024-10-01 | 71026.91 | 32453.09 | 34968.71 | 3605.11
MLP | CLOSE | MLU2 REPLACE #25 PULVERIZER GEAR BOX | E10688266 | MLWSPPULV | 1070001 | 2023-11-19 | 323285.4 | 274627.28 | 38451.4 | 10206.72
MLP | COMP | MLU2 - Feeder Discharge chutes & plugged feeder capacitance probes | E10633286 | MLWSPPULV | 1070001 | 2024-05-17 | 259303.5 | 121723.6 | 106261.53 | 31318.37
MLP | CLOSE | MLU1 - Feeder Discharge chutes & plugged feeder capacitance probes | E10633277 | MLWSPPULV | 1070001 | 2023-12-15 | 214991.1 | 100573.62 | 106656.7 | 7760.78
MLP | CLOSE | MLU2 REPLACE #24 COAL GATE | E10615067 | MLWSPPULV | 1070001 | 2023-11-19 | 17920.59 | 17346 | 0 | 574.59
MLP | CLOSE | MLP PULV REBUILD (CORRECTION) | E10574714 | MLWSPPULV | 1070001 | 2023-02-01 | 358666.94 | 345562.22 | 0 | 13104.72
MLP | CLOSE | MLU1 PULVERIZER REBUILD | E10573698 | MLWSPPULV | 1070001 | 2024-03-11 | 280170.55 | 253843.45 | 0 | 26327.1
MLP | CLOSE | MLU2 #26 PULVERIZER REBUILD | E10539582 | MLWSPPULV | 1070001 | 2022-10-22 | 783951.64 | 662780.39 | 85652.44 | 35518.81
MLP | COMP | MLU2 #25 PULVERIZER REBUILD | E10539581 | MLWSPPULV | 1070001 | 2022-10-22 | 221649.64 | 91578.76 | 120671.65 | 9399.23
MLP | COMP | MLP U1: STACK BREACHING CASING REPLACEMENT | E10840773 | MLWSPSBSR | 1070001 | 2025-05-07 | 430189.09 | 18836.52 | 388458.1 | 22894.47
MLP | CLOSE | MLP U1: SOOTBLOWER ASSEMBLY (STOCK ADJ) | E10835892 | MLWSPSOOT | 1070001 | 2024-11-13 | 46413.39 | 44200 | 131.49 | 2081.9
MLP | CLOSE | MLU2 WATER CANNON SYSTEM UPGRADE | E10539579 | MLWSPSOOT | 1070001 | 2023-11-16 | 655757.24 | 54623.99 | 546079.39 | 55053.86
MLP | CLOSE | MLU1 WATER CANNON SYSTEM UPGRADE | E10539578 | MLWSPSOOT | 1070001 | 2023-12-01 | 627698.34 | 52348.18 | 521371.61 | 53978.55
MLP | COMP | MLP U1: BOX 2 HOPPER 1-1 RECEIVING HOPPER GATE | E10933966 | MLWSPVALV | 1070001 | 2025-07-15 | 8574.15 | 6958.29 | 767.98 | 847.88
MLP | COMP | MLP U1: #12 ASH WATER ISOLATION VALVES REPLACEMENT | E10896492 | MLWSPVALV | 1070001 | 2025-06-12 | 20011.11 | 17915.42 | 806.34 | 1289.35
MLP | CLOSE | MLP U2: 22 ASH WATER PUMP SUCTION CHECK VALVE | E10877836 | MLWSPVALV | 1070001 | 2025-03-07 | 6218.91 | 3819 | 1473.41 | 926.5
MLP | COMP | MLP U2: ASH PIT SUMP PUMP CHECK VALVE REPLACEMENT | E10865610 | MLWSPVALV | 1070001 | 2025-04-15 | 7944.43 | 7304 | 0 | 640.43
MLP | CLOSE | MLP U1 BOX 2 HOPPER 1-2 RECEIVING HOPPER & TEE REPLACEMENT | E10843413 | MLWSPVALV | 1070001 | 2025-04-15 | 9130.55 | 7936 | 681.59 | 512.96
MLP | COMP | MLP U1: BOX 1 HOPPER 1 RECEIVING HOPPER REPLACEMENT | E10843412 | MLWSPVALV | 1070001 | 2025-04-29 | 8490.46 | 6942.16 | 1124.16 | 424.14
MLP | CLOSE | MLP U2: 24E BURNER SHUT OFF REPLACEMENT | E10756547 | MLWSPVALV | 1070001 | 2024-05-08 | 14871.76 | 9640.88 | 3831 | 1399.88
MLP | CLOSE | MLP U2: 22 ASH WATER PUMP SUCTION/DISCHARGE VALVES REPLACEMENT | E10748971 | MLWSPVALV | 1070001 | 2025-02-08 | 18371.98 | 12851.61 | 2990.31 | 2530.06
MLP | CLOSE | MLP U2: 26C BURNER SHUT OFF REPLACEMENT | E10748686 | MLWSPVALV | 1070001 | 2024-02-21 | 15443.92 | 9906.73 | 4524.67 | 1012.52
MLP | CLOSE | MLP - U2 ASH PIT SUMP PUMP | E10711029 | MLWSPVALV | 1070001 | 2023-12-10 | 28157.1 | 27324 | 0 | 833.1
MLP | CLOSE | MLU1 ASH JET VALVE 802 | E10643414 | MLWSPVALV | 1070001 | 2023-05-26 | 2587.09 | 2338.94 | 293.58 | -45.43
MLP | CLOSE | MLU2 PRECIP - REPLACE GEARBOX ON CS RAPPER | E10586150 | MLWSPVALV | 1070001 | 2023-02-15 | 2457.41 | 2387.09 | 0 | 70.32
MLP | CLOSE | MLU2 Replace Safety Valve #54 | E10541089 | MLWSPVALV | 1070001 | 2022-03-07 | 58441.73 | 10147.5 | 45397.13 | 2897.1
MLP | CLOSE | MLU1 BOX 2 XFER STA C NUVA FEEDER 12B LOWER HSO | E10539624 | MLWSPVALV | 1070001 | 2022-11-01 | 2312.73 | 2196 | 0 | 116.73
MLP | CLOSE | MLU2 #24 BURNER SHUT OFF REPLACEMENT | E10539597 | MLWSPVALV | 1070001 | 2024-03-12 | 4.02 | 0 | 1.1768e-14 | 4.02
MLP | CLOSE | MLU2 NUVA FEEDER LOWER HSO REPLACEMENT | E10539503 | MLWSPVALV | 1070001 | 2022-09-22 | 35608.72 | 31814.9 | 2129.94 | 1663.88
MLP | CLOSE | MLU1 #25 SAFETY VALVE REPLACEMENT | E10539463 | MLWSPVALV | 1070001 | 2023-11-07 | 68624.9 | 41207.73 | 17136.21 | 10280.96
MLP | CLOSE | MITCHELL-STORE TOOLS GEN PLT BLKT WHLG 413 -PORTA COOL JETSTREAM 260 VARIABLE SPD EVAPORATOR COOLER | E10541381 | MLWSTORB | 1070001 | 2023-07-05
MLP | INSERV | MLP U1: SCR CATALYST LAYER 1 REPLACEMENT | E10809719 | MLWVC1CL1 | 1070001 | 2025-04-25 | 2850642.29 | 2058186.84 | 547757.46 | 244697.99
MLP | CLOSE | ML2 SCR | E10539468 | MLWVC2CL4 | 1070001 | 2022-12-13 | 3430819.38 | 88004.19 | 2946148.83 | 396666.36
MLP | CLOSE | MLP U1: 11 ID FAN MOTOR REBUILD | E10809718 | MLWVIDFMR | 1070001 | 2024-12-19 | 183798.82 | 118829.2 | 37793.97 | 27175.65
MLP | CLOSE | MLP U0: Replace #11 ID fan motor due to EMI indication of broken rotor bar(s) | E10773943 | MLWVIDFMR | 1070001 | 2024-06-07 | 159429.36 | 3160.03 | 136323.49 | 19945.84
MLP | COMP | MLP U1: 11 DE AND RE HUB REPLACEMENT | E10867749 | MLWVP11ID | 1070001 | 2025-04-30 | 382004.04 | 94806.59 | 267741.33 | 19456.12
MLP | COMP | MLP U2: #21 ID FAN DRIVE END HUB REPLACEMENT | E10865891 | MLWVP21ID | 1070001 | 2025-02-15 | 383037.57 | 71284.41 | 281845.31 | 29907.85
MLP | COMP | MLP U0: 2 AR Pump Discharge Expansion Joints | E10841252 | MLWVPABEJ | 1070001 | 2025-02-05 | 25499.6 | 24500 | 0 | 999.6
MLP | CLOSE | MLP U0: CPS AIR COMPRESSOR REPLACEMENT | E10840418 | MLWVPAIRC | 1070001 | 2024-12-17 | 65167.31 | 63587 | 0 | 1580.31
MLP | CLOSE | MLU0 REPLACE FGD SERVICE AIR COMPRESSOR #2 | E10539476 | MLWVPAIRC | 1070001 | 2022-10-20 | 307049.6 | 245065.02 | 45668.36 | 16316.22
MLP | CLOSE | MLU2 FGD BATTERY REPLACEMENT | E10539527 | MLWVPBATT | 1070001 | 2022-10-25 | 146983.25 | 105136.1 | 35474.14 | 6373.01
MLP | CLOSE | MLU1 FGD BATTERY REPLACEMENT | E10539526 | MLWVPBATT | 1070001 | 2022-10-19 | 160977.54 | 111214.38 | 44734.52 | 5028.64
MLP | COMP | MLP U0: BALL MILL B LINER REPLACEMENT | E10840516 | MLWVPBLML | 1070001 | 2025-04-24 | 216424.69 | 132712.6 | 72475.67 | 11236.42
MLP | CLOSE | MLP U0: LIME SILO LEVEL INDICATION REPLACEMENT | E10834354 | MLWVPCNTM | 1070001 | 2024-11-20 | 5685.22 | 3781 | 1515.34 | 388.88
MLP | CLOSE | MLP U0: DSI BLOWER 2 DEWPOINT SENSOR REPLACEMENT | E10797764 | MLWVPDSIN | 1070001 | 2024-09-07 | 3399.26 | 2369.07 | 850.97 | 179.22
MLP | CLOSE | MLP - U2 DSI CONV BLWR #2 REPLACEMENT | E10691563 | MLWVPDSIN | 1070001 | 2023-11-02 | 21674.04 | 20193.63 | 1021.16 | 459.25
MLP | CLOSE | MLP - U0 PURCHASE NEW DSI SYSTEM SPARE PARTS | E10669347 | MLWVPDSIN | 1070001 | 2024-05-09 | 2646.13 | 2967.72 | 0 | -321.59
MLP | CLOSE | MLU2 DSI #2 SILO ISOLATION HAMMER GATE VALVE - INSTALL | E10650122 | MLWVPDSIN | 1070001 | 2023-10-27 | 33688.4 | 13856.55 | 19099.23 | 732.62
MLP | COMP | MLP U1: 11 ID FAN INLET EXP JNT EJ-71006 REPLACE | E10879891 | MLWVPEJNT | 1070001 | 2025-04-30 | 49798.62 | 25392.9 | 21733.86 | 2671.86
MLP | CLOSE | MLP U2: 21 ID FAN INLET EXP JOINT EJ-72006 REPLACEMENT | E10866269 | MLWVPEJNT | 1070001 | 2025-02-18 | 79842.73 | 24948.38 | 50346.56 | 4547.79
MLP | CLOSE | MLP U1: DSI SILO 1 - UPGRADE SILO BOOT | E10815916 | MLWVPEJNT | 1070001 | 2025-04-04 | 53095.16 | 27218.8 | 22684.91 | 3191.45
MLP | CLOSE | MLU2 Replace Oxidation Air Blower C Discharge Expansion Joint | E10793958 | MLWVPEJNT | 1070001 | 2024-07-11 | 10202.09 | 1675 | 7516.32 | 1010.77
MLP | CLOSE | MLP U2: 2C AR PUMP DISCHARGE EJ Q2-ZRX-80051 | E10768523 | MLWVPEJNT | 1070001 | 2024-10-14 | 59811.81 | 22307.83 | 34917.6 | 2586.38
MLP | CLOSE | MLP U1 BLEED PUMP 1A SUCTION PIPING & EXP JOINT | E10752244 | MLWVPEJNT | 1070001 | 2024-04-05 | 7692.81 | 3905.2 | 2857.08 | 930.53
MLP | CLOSE | MLP OVATION OPERATION STATION | E10788741 | MLWVPELGC | 1070001 | 2024-12-20 | 30028.01 | 28255.89 | 783.18 | 988.94
MLP | COMP | MLP U0: 24B BUS MULTILIN RELAY REPLACEMENT | E10890161 | MLWVPFGDN | 1070001 | 2025-05-13 | 9377.87 | 7975 | 839.37 | 563.5
MLP | INPRG | MLP U0: 22A BUS MULTILIN RELAY REPLACEMENT | E10890160 | MLWVPFGDN | 1070001 |  | 838.87 | 0 | 839.58 | -0.71
MLP | CLOSE | MLP U0: CPS PRESS #2 CLOTH REPLACEMENT | E10867837 | MLWVPFGDN | 1070001 | 2025-02-28 | 97351.11 | 21612.17 | 6930.12 | 68808.82
MLP | CLOSE | MLP U0: VAC BELT A FILTER CLOTH REPLACEMENT | E10843483 | MLWVPFGDN | 1070001 | 2024-11-26 | 14230.73 | 10037 | 3358.18 | 835.55
MLP | CLOSE | MLP U0: VAC BELT A VFD REPLACEMENT | E10815920 | MLWVPFGDN | 1070001 | 2024-10-18 | 17312.39 | 5965.83 | 9236.64 | 2109.92
MLP | CLOSE | MLP U0: CPS AIR COMPRESSOR 2 BREAKER REPLACE | E10795965 | MLWVPFGDN | 1070001 | 2024-08-05 | 3010.17 | 2189.62 | 537.23 | 283.32
MLP | CLOSE | MLP U0: CPS FEED BREAKER REPLACEMENT | E10762571 | MLWVPFGDN | 1070001 | 2024-03-28 | 1466.82 | 1373.48 | 0 | 93.34
MLP | CLOSE | MLP U0: UPGRADE LIME SILO 2 PANEL VIER HMI | E10762567 | MLWVPFGDN | 1070001 | 2024-06-11 | 9453.31 | 7618.32 | 155.96 | 1679.03
MLP | CLOSE | MLP U0: LABOR TO I/R FGD INST AIR DRYERS | E10750727 | MLWVPFGDN | 1070001 | 2024-09-06 | 123374.11 | 14938.54 | 93696.02 | 14739.55
MLP | CLOSE | MLP U0: ABSORBER AGITATOR 2F MOTOR REPLACEMENT | E10748211 | MLWVPFGDN | 1070001 | 2024-05-15 | 13848.84 | 10579.09 | 757.54 | 2512.21
MLP | CLOSE | MLP - U0: REPLACE GRV-9143 LIMIT SWITCH | E10728262 | MLWVPFGDN | 1070001 | 2024-04-04 | 3407.6 | 2648 | 494.64 | 264.96
MLP | COMP | MLP - U0: PURCHASE 2 FGD INST AIR DRYERS | E10719630 | MLWVPFGDN | 1070001 | 2024-07-05 | 228000.83 | 210812.76 | 0 | 17188.07
MLP | CLOSE | MLP - U2: 21 ID FAN DRIVE END BEARING LINER | E10706085 | MLWVPFGDN | 1070001 | 2023-11-04 | 20228.39 | 19693.27 | 0 | 535.12
MLP | CLOSE | MLU0 HYDROLYZER 2 GRV-9769 DXP REPLACE | E10700678 | MLWVPFGDN | 1070001 | 2024-09-30
MLP | CLOSE | MLU1 PURCHASE ABSORBER RECYCLE PUMP | E10646180 | MLWVPFGDN | 1070001 | 2024-07-19 | 198884.41 | 168750 | 0 | 30134.41
MLP | CLOSE | MLU0 Replace FGD Water Heater | E10645236 | MLWVPFGDN | 1070001 | 2024-06-26 | 12345.42 | 8518.42 | 2788.33 | 1038.67
MLP | CLOSE | MLU0 Fabricate new insulation enclosure for FGD tank level instruments | E10632479 | MLWVPFGDN | 1070001 | 2023-06-21 | 20151.94 | 813.07 | 19278.74 | 60.13
MLP | CLOSE | MLU0 PURCHASE AR PUMP MOTORS (CSP) | E10568752 | MLWVPFGDN | 1070001 | 2023-09-29 | 347386.06 | 319190 | 0 | 28196.06
MLP | CLOSE | MLU0 CPS FILTER PRESS BOMBAY DOOR LIMITS | E10567474 | MLWVPFGDN | 1070001 | 2023-11-05 | 12905.1 | 9251.68 | 2728.04 | 925.38
MLP | CLOSE | MLU0 FGD ELEVATOR POWER FEED CONDITIONER | E10564206 | MLWVPFGDN | 1070001 | 2023-03-29 | 56084.13 | 40967.58 | 12685.57 | 2430.98
MLP | CLOSE | MLU0 FGD VAC BELT C REPLACEMENT | E10541699 | MLWVPFGDN | 1070001 | 2022-10-06 | 22315.52 | 21250.73 | 0 | 1064.79
MLP | CLOSE | MLU0 Replace section of storm sewer pipe from North Coal Yard treatment pond to the Kammer Pond | E10539631 | MLWVPFGDN | 1070001 | 2023-06-07 | 19342.69 | 12490.54 | 6516.43 | 335.72
MLP | CLOSE | MLU2 REPLACE U2A CONDENSATE RETURN LINE | E10539619 | MLWVPFGDN | 1070001 | 2023-07-30 | 321874.44 | 96341.27 | 205949.75 | 19583.42
MLP | CLOSE | MLU0 ID fan #21 thrust bearing replacement | E10539613 | MLWVPFGDN | 1070001 | 2022-10-31 | 61115.41 | 39651 | 16419.59 | 5044.82
MLP | CLOSE | MLU2 CEMS MONITORS REPLACEMENT | E10539601 | MLWVPFGDN | 1070001 | 2023-03-01 | 92820 | 92820 | 0 | 0
MLP | CLOSE | MLU0 OXIDATION AIR BLOWER MOTOR C (CSP) REPLACEMENT | E10539592 | MLWVPFGDN | 1070001 | 2023-06-15 | 48868.43 | 14299.68 | 31790.44 | 2778.31
MLP | COMP | MLU0 CPS FILTER PRESS B BOMBAY DOOR LIMITS UPGRADE | E10539532 | MLWVPFGDN | 1070001 | 2022-10-06 | 13149.02 | 4023 | 8293.06 | 832.96
MLP | CLOSE | MLU0 BALL MILL A SLURRY TANK AGITATOR GEARBOX REPLACE | E10539519 | MLWVPFGDN | 1070001 | 2023-09-21 | 1.44 | 0 | 0 | 1.44
MLP | CLOSE | MLP U2: 2C AR PUMP GEARBOX COUPLING KIT | E10823089 | MLWVPGRBX | 1070001 | 2024-12-20 | 9598.16 | 9153.86 | 0 | 444.3
MLP | CLOSE | MLU0 Vacuum Belt B Pump Speed Reducer Replacement | E10660255 | MLWVPGRBX | 1070001 | 2023-08-09 | 34723.43 | 25814.19 | 6763.59 | 2145.65
MLP | CLOSE | MLU0 HYDROCLONE FEEDTANK B AGITATOR GEARBOX REPLACEMENT | E10591691 | MLWVPGRBX | 1070001 | 2023-11-18 | 139983.69 | 99699.13 | 35850.38 | 4434.18
MLP | CLOSE | MLU0 PURCH 6 30 KW 480 V PORTABLE HEATERS FOR FGD BUILDING | E10585788 | MLWVPHEAT | 1070001 | 2023-07-25 | 19980.5 | 16805.32 | 1616.56 | 1558.62
MLP | CLOSE | MLU0 PURCHASE & INSTALL HEATER ON TRAVELING TRIPPER | E10539494 | MLWVPHEAT | 1070001 | 2024-03-13 | 1.9951e-13 | 0 | 0 | -1.279e-13
MLP | CLOSE | MLU1 1E AR PUMP DISCHARGE EXP JOINT REPLACE | E10539598 | MLWVPIDEJ | 1070001 | 2022-12-16 | 28895.38 | 22782.6 | 4208.63 | 1904.15
MLP | CLOSE | MLU1 1F AR PUMP SUCTION SIDE EJ REPLACEMENT | E10539480 | MLWVPIDEJ | 1070001 | 2022-10-31 | 11444.04 | 6239.19 | 3624.09 | 1580.76
MLP | INPRG | MLP U1: HYDRAULIC CYLINDER CSP REBUILD | E10868490 | MLWVPIDHY | 1070001 |  | 75365.37 | 68912.65 | 0 | 6452.72
MLP | COMP | MLP U1: 11 ID FAN HYDRAULIC CYLINDER REPLACEMENT | E10867843 | MLWVPIDHY | 1070001 | 2025-04-30 | 65235.55 | 7354.84 | 54296.81 | 3583.9
MLP | CLOSE | MLP U2: ION METER ETHERNET SWITCH REPLACEMENT | E10777438 | MLWVPMONS | 1070001 | 2024-05-17 | 6495.34 | 3330 | 2040.63 | 1124.71
MLP | CLOSE | MLU0 REPLACE REAGENT LOOP B | E10677794 | MLWVPOPIP | 1070001 | 2023-11-07 | 1262900.21 | 29926.84 | 1193019.42 | 39953.95
MLP | CLOSE | MLU0 Replace Reagent Loop B | E10644745 | MLWVPOPIP | 1070001 | 2023-11-17 | 138859.23 | 120565.11 | 11322.02 | 6972.1
MLP | CLOSE | MLU0 REPLACE REAGENT LOOP A | E10677787 | MLWVPPIPE | 1070001 | 2023-11-07 | 1228464.77 | 6863.31 | 1188292.4 | 33309.06
MLP | CLOSE | MLU0 Replace Reagent Loop A | E10644741 | MLWVPPIPE | 1070001 | 2023-11-17 | 91950.7 | 67188.06 | 13180.83 | 11581.81
MLP | INPRG | MLP U0: SLUDGE PUMP 3 VFD REPLACEMENT | E10895086 | MLWVPPUMP | 1070001 |  | 15605.86 | 11279.23 | 3167.41 | 1159.22
MLP | INSERV | MLP U0: BALL MILL A REBUILD | E10887198 | MLWVPPUMP | 1070001 | 2025-06-20 | 7141.99 | 5733.25 | 842.92 | 565.82
MLP | COMP | MLP U2: LABOR TO I/R 2F AR PUMP MOTOR | E10877523 | MLWVPPUMP | 1070001 | 2025-04-02 | 91072.56 | 9411.82 | 64646.15 | 17014.59
MLP | CLOSE | MLP U0: FILTRATE PUMP C REPLACEMENT | E10863842 | MLWVPPUMP | 1070001 | 2025-01-13 | 25295.6 | 21617.87 | 1732.17 | 1945.56
MLP | CLOSE | MLP U0: MIST ELIMINATOR PUMP B REPLACEMENT | E10850668 | MLWVPPUMP | 1070001 | 2024-12-10 | 39856.32 | 37295 | 1566.34 | 994.98
MLP | CLOSE | MLP U1: LABOR TO I/R RECLAIM WATER PUMP A CSP | E10850094 | MLWVPPUMP | 1070001 | 2024-12-10 | 6258.35 | 686.2 | 5322.12 | 250.03
MLP | CLOSE | MLP U0: HYDROCLONE FEED PUMP A CSP REPLACEMENT | E10843260 | MLWVPPUMP | 1070001 | 2024-12-19 | 1533.03 | 0 | 1468.23 | 64.8
MLP | COMP | MLP U2: AR Pump 1F Motor & Pump Replacement/Gearbox Rebuild | E10840764 | MLWVPPUMP | 1070001 | 2025-05-13 | 500190.41 | 335143.23 | 135579.53 | 29467.65
MLP | CLOSE | MLP U2: LABOR TO I/R 2A BLEED PUMP CSP | E10832916 | MLWVPPUMP | 1070001 | 2024-11-07 | 6885.81 | 605.89 | 4922.51 | 1357.41
MLP | CLOSE | MLP U0: PURCHASE SERVICE WATER PUMP | E10822808 | MLWVPPUMP | 1070001 | 2024-12-09
MLP | CLOSE | MLP U0: RECLAIM WATER PUMP A | E10798038 | MLWVPPUMP | 1070001 | 2024-07-22 | 34664.01 | 26860.37 | 4648.52 | 3155.12
MLP | CLOSE | MLP U0: FGD SERVICE WATER PUMP A - REPLACEMENT | E10785753 | MLWVPPUMP | 1070001 | 2024-06-14 | 12223.87 | 10619 | 778.49 | 826.38
MLP | CLOSE | MLP U0: PURCHASE FGD EMERGENCY QUENCH PUMP | E10777434 | MLWVPPUMP | 1070001 | 2024-08-13 | 22715.53 | 19088.63 | 2524.25 | 1102.65
MLP | CLOSE | MLU0 LP SLUDGE PUMP #3 18 PULSE RECTIFIER | E10765291 | MLWVPPUMP | 1070001 | 2024-09-14 | 5698.2 | 3840 | 1308.81 | 549.39
MLP | CLOSE | MLP U0: CPS LP & HP SLUDGE PUMP VFD REPLACEMENTS | E10759743 | MLWVPPUMP | 1070001 | 2024-08-05 | 56459.8 | 38183.9 | 7231.92 | 11043.98
MLP | CLOSE | MLP U0: PURCHASE FGD HYDROCLONE OVERFLOW BLOWDOWN PUMP | E10745796 | MLWVPPUMP | 1070001 | 2024-07-25 | 44193.48 | 39815 | 0 | 4378.48
MLP | CLOSE | MLU0 REPLACE BALL MILL SLURRY PUMP A2 | E10717834 | MLWVPPUMP | 1070001 | 2023-12-19 | 53027.71 | 48249 | 2931.52 | 1847.19
MLP | CLOSE | MLU1 LABOR TO I/R 1D AR PUMP MOTOR (CSP) | E10693663 | MLWVPPUMP | 1070001 | 2023-12-02 | 36865.12 | 468.94 | 35235.21 | 1160.97
MLP | CLOSE | MLU0 Replace spare hydroclone feedpump shaft and impeller due to damage | E10687363 | MLWVPPUMP | 1070001 | 2023-11-15 | 19267.77 | 18650 | 0 | 617.77
MLP | CLOSE | MLU0 #3 PRIMARY CLARIFIER SLUDGE PUMP REPLACEMENT | E10664892 | MLWVPPUMP | 1070001 | 2023-08-08 | 14410.52 | 11326 | 2337.56 | 746.96
MLP | CLOSE | MLU0 LABOR TO I/R FGD HYDROCLONE FEEDPUMP C (CSP 9900116538) | E10655584 | MLWVPPUMP | 1070001 | 2023-07-17 | 1406.53 | 0 | 1318.31 | 88.22
MLP | CLOSE | MLP - MLU0 PURCHASE HYDROCLONE OVERFLOW BLOWDOWN PUMP | E10647482 | MLWVPPUMP | 1070001 | 2023-11-07 | 55173.83 | 48853.41 | 5144.11 | 1176.31
MLP | CLOSE | MLU0 - MIST ELIMINATOR PUMP A REPLACEMENT | E10635305 | MLWVPPUMP | 1070001 | 2023-05-03 | 20213.22 | 19133.06 | 1503.63 | -423.47
MLP | CLOSE | MLU0 MIST ELIMINATOR PUMP B - REPLACEMENT | E10617641 | MLWVPPUMP | 1070001 | 2024-09-02
MLP | CLOSE | MLU0 MIST ELIMINATOR PUMP A - REPLACE | E10611115 | MLWVPPUMP | 1070001 | 2023-03-16 | 23167.4 | 19101 | 2576.3 | 1490.1
MLP | CLOSE | MLU0 CPS CLOTH WASH PUMP REPLACEMENT | E10585887 | MLWVPPUMP | 1070001 | 2023-02-08 | 24774.96 | 22043 | 1972.77 | 759.19
MLP | CLOSE | MLU2 REPLACE 2F AR PUMP LOW SPEED COUPLING | E10560742 | MLWVPPUMP | 1070001 | 2022-12-01 | 3635.5 | 3543.15 | 0 | 92.35
MLP | CLOSE | MLU0 PURCHASE RECLAIM WATER PUMP CSP | E10554146 | MLWVPPUMP | 1070001 | 2023-11-28 | 86010 | 83768.42 | 0 | 2241.58
MLP | CLOSE | MLU0 - LABOR TI I/R #1 EFFLUENT SUMP PUMP | E10539627 | MLWVPPUMP | 1070001 | 2022-09-30 | 5083.08 | 0 | 4131.6 | 951.48
MLP | CLOSE | MLU0 MIST ELIMINATOR WAS PUMP B - REPLACE | E10539575 | MLWVPPUMP | 1070001 | 2022-10-01 | 34244.04 | 30901 | 1941.34 | 1401.7
MLP | CLOSE | MLU0 REPLACE HYDROCLONE FEEDPUMP A | E10539571 | MLWVPPUMP | 1070001 | 2022-06-13 | 2351.56 | 0 | 2142.07 | 209.49
MLP | COMP | MLU2 2C AR PUMP IMPELLER / PUMP RUNNER | E10539556 | MLWVPPUMP | 1070001 | 2023-05-31 | 143549.09 | 123561.61 | 14079.89 | 5907.59
MLP | CLOSE | MLU0 LABOR TO I/R REAGENT PUMP B (CSP) | E10539545 | MLWVPPUMP | 1070001 | 2023-04-26
MLP | CLOSE | MLU0 PURCHASE CPS EFFLUENT PUMP | E10539466 | MLWVPPUMP | 1070001 | 2023-04-26
MLP | CLOSE | MLU0 HYDROCLONE FEEDPUMP C - PURCHASE | E10539462 | MLWVPPUMP | 1070001 | 2022-09-30 | 70821.96 | 65506 | 0 | 5315.96
MLP | CLOSE | MLP U0: LABOR TO I/R MOISTURE SEPARATOR COLLECTION POT | E10872638 | MLWVPTANK | 1070001 | 2025-03-28 | 6016.61 | 494.43 | 5522.18 | 0
MLP | CLOSE | MLP U0: MOISTURE SEPARATOR COLLECTION POT - FAB & INSTALL | E10797221 | MLWVPTANK | 1070001 | 2024-10-30 | 12161.26 | 6052.05 | 6109.21 | 0
MLP | CLOSE | MLP - U0 CPS PRIMARY CLARIFIER TANK SLUDGE LEVEL PROBE | E10731778 | MLWVPTANK | 1070001 | 2024-04-04 | 7827.34 | 4687.24 | 2652.02 | 488.08
MLP | INPRG | MLP U1: Install two CEMS ports on FGD stack for installation of monitors | E10900953 | MLWVPTRMT | 1070001 |  | 6875.03 | 2401.84 | 3501.92 | 971.27
MLP | INPRG | MLP U1: Install two CEMS ports on FGD stack for installation of monitors | E10900953 | MLWVPTRMT | 1070001 |  | 6280.52 | 0 | 6280.52 | 0
MLP | CLOSE | MLP U0: BIOREACTOR 2C LEVEL TRANSMITTER/PROBE REPLACE | E10890325 | MLWVPTRMT | 1070001 | 2025-03-27 | 8147.28 | 7432 | 334.36 | 380.92
MLP | COMP | MLP U1: ABSORBER LEVEL TRANSMITTER REPLACEMENT | E10886937 | MLWVPTRMT | 1070001 | 2025-03-27 | 5750.62 | 3638.34 | 1730.09 | 382.19
MLP | COMP | MLP U1: SLURRY HOUSE SUMP ALARM TRANSMITTER REPLACE | E10868945 | MLWVPTRMT | 1070001 | 2025-05-05 | 1638.36 | 1132 | 404.81 | 101.55
MLP | CLOSE | MLP U0: REPLACE POSITIONER ON ZEAR 8003 | E10853343 | MLWVPTRMT | 1070001 | 2024-12-17 | 2714.61 | 2107.66 | 519.44 | 87.51
MLP | CLOSE | MLP U0: REPLACE POSITIONER ON ZEAR 8003 | E10853331 | MLWVPTRMT | 1070001 | 2024-12-13 | 3328.93 | 2228 | 1020.2 | 80.73
MLP | CLOSE | MLP U2: DSI SILO 2 PRESSURE TRANSMITTER | E10795318 | MLWVPTRMT | 1070001 | 2024-08-06 | 3353.03 | 2676.94 | 509.31 | 166.78
MLP | CLOSE | MLP U0: CLOTH WASH PUMP DCHG PRESSURE TRANSMITTER | E10785822 | MLWVPTRMT | 1070001 | 2024-08-09 | 3618.76 | 2183.94 | 1243.02 | 191.8
MLP | CLOSE | MLU2 - RX 22 Coriolis Flowmeter "A" Replacement | E10778667 | MLWVPTRMT | 1070001 | 2024-06-11 | 30691.91 | 24488.29 | 624.49 | 5579.13
MLP | CLOSE | MLP U0: CPS FILTER PRESS 3 BOMBAY DOOR LIMIT UPGRADE | E10767903 | MLWVPTRMT | 1070001 | 2024-06-11 | 6135.11 | 5497.4 | 0 | 637.71
MLP | CLOSE | MLU0 FGD - 869 Multilin Replacement for Spare Compartments | E10765527 | MLWVPTRMT | 1070001 | 2024-05-30 | 58396.98 | 48247.31 | 85.08 | 10064.59
MLP | CLOSE | MLU0 U2A HYDROLYZER BLOWDOWN SPARGING VESSEL LEVEL PROBE REPLACEMENT | E10765398 | MLWVPTRMT | 1070001 | 2024-10-17 | 9032.26 | 6584.09 | 751.03 | 1697.14
MLP | CLOSE | MLP U1: CEMS NOX MONITOR OZONE GENERATOR | E10758986 | MLWVPTRMT | 1070001 | 2024-04-25 | 2085.14 | 1944.32 | 0 | 140.82
MLP | CLOSE | MLP U2: AMMONIA INJECTION FLOW METER REACTOR 22 | E10757536 | MLWVPTRMT | 1070001 | 2024-07-04 | 10925.47 | 7424.07 | 1427.72 | 2073.68
MLP | CLOSE | MLP U1: ID FAN INLET PRESSURE INDICATOR PROBE B | E10748867 | MLWVPTRMT | 1070001 | 2024-02-29 | 3689.63 | 2589.24 | 810.05 | 290.34
MLP | CLOSE | MLP U1: DSI BLOWER 1 DISCHARGE DEWPOINT SENSOR | E10739049 | MLWVPTRMT | 1070001 | 2024-03-22 | 3373.95 | 2425.94 | 751.03 | 196.98
MLP | CLOSE | MLP - U0 FGD AIR DRYER SKID 2 DEWPOINT MONITOR | E10691873 | MLWVPTRMT | 1070001 | 2023-11-15 | 12755.97 | 3224.96 | 9181.02 | 349.99
MLP | CLOSE | MLU0 FGD MIMIC PANEL GAUGE REPLACEMENTS | E10679218 | MLWVPTRMT | 1070001 | 2024-01-29 | 26828.37 | 18400 | 7121.35 | 1307.02
MLP | CLOSE | MLU0 RECLAIM H2O HEADER DCHG PRESSURE TRANSMITTER | E10654009 | MLWVPTRMT | 1070001 | 2024-01-11 | 4308.38 | 4048.89 | 0 | 259.49
MLP | CLOSE | MLU2 Replace SCR #21 inlet probe | E10640724 | MLWVPTRMT | 1070001 | 2024-04-30 | 19358.13 | 18393 | 0 | 965.13
MLP | CLOSE | MLU0 FGD BALL MILL A SLURRY PUMP DCHG TRANSMITTER | E10621058 | MLWVPTRMT | 1070001 | 2023-10-26 | 5803.81 | 5351.75 | 317.16 | 134.9
MLP | CLOSE | MLU0 CLEAN AIR MERCURY SAMPLE SYSTEM PROBE | E10617642 | MLWVPTRMT | 1070001 | 2023-06-22 | 16826.67 | 16460 | 0 | 366.67
MLP | CLOSE | MLU0 INSTALL PERM PWR - FGD BLD TO REAGENT TANK A XMITTER | E10617457 | MLWVPTRMT | 1070001 | 2023-07-19 | 12948.42 | 544.24 | 11937.36 | 466.82
MLP | CLOSE | MLU0 CPS LIME SILO 1 HMI UPGRADE | E10615975 | MLWVPTRMT | 1070001 | 2023-05-02 | 10273.87 | 8195 | 1455.06 | 623.81
MLP | CLOSE | MLU0 FGD OXIDATION AIR BLOWER C MULTILIN RELAY (469( REPLACEMENT | E10539574 | MLWVPTRMT | 1070001 | 2022-06-09 | 996.15 | 0 | 971.89 | 24.26
MLP | CLOSE | MLU0 FGD REAGENT TANK A LEVEL TRANSMITTER | E10539484 | MLWVPTRMT | 1070001 | 2022-12-13 | 1915.04 | 1525.6 | 169.5 | 219.94
MLP | CLOSE | MLU0 Hydroclone Feedpump Bypass Valves | E10539458 | MLWVPTRMT | 1070001 | 2022-12-13 | 56725.18 | 37379.89 | 0 | 19345.29
MLP | CLOSE | MLP U0: HYDROLYZER VALVE REPLACEMENT | E10852390 | MLWVPVALV | 1070001 | 2024-12-13 | 4576.07 | 3122.86 | 1315.6 | 137.61
MLP | CLOSE | MLP U0: PURCHASE TUNGSTON LINED ROTARY AIRLOCKS | E10798029 | MLWVPVALV | 1070001 | 2025-01-17 | 58253.4 | 45279.5 | 10112.59 | 2861.31
MLP | CLOSE | MLP U0: 10-IN BRAY VLV ON OAB A BLOWOFF VLV | E10785774 | MLWVPVALV | 1070001 | 2024-07-08 | 5426.74 | 1433 | 3456.1 | 537.64
MLP | CLOSE | MLP U0: FGD ZDAR-8328 CONTROLLER | E10757532 | MLWVPVALV | 1070001 | 2024-05-02 | 2333.7 | 2164.06 | 0 | 169.64
MLP | CLOSE | MLP U0: REAGENT SLURRY LOOP DOSING VLV ZFAR-8111 POSITIONER | E10739024 | MLWVPVALV | 1070001 | 2024-02-03 | 3279.25 | 3140.05 | 0 | 139.2
MLP | CLOSE | MLU0 BALL MILL SLURRY PUMP A2 DCHG VLV ZPAS-8163 | E10648463 | MLWVPVALV | 1070001 | 2023-07-21 | 8515.49 | 4757 | 3419.98 | 338.51
MLP | CLOSE | MLU0 Replace FeCl Mix Tank Discharge Valves | E10631573 | MLWVPVALV | 1070001 | 2023-06-28 | 28168.8 | 20709.51 | 8044.01 | -584.72
MLP | CLOSE | MLU0 PURCHASE AR PUMP SUCTION VLV | E10617446 | MLWVPVALV | 1070001 | 2024-03-01 | 41802.97 | 38986.11 | 0 | 2816.86
MLP | CLOSE | MLU0 REPLACE 2 UREA STORAGE TANK VALVES | E10590269 | MLWVPVALV | 1070001 | 2023-10-30 | 5461.67 | 4613.5 | 540.59 | 307.58
MLP | CLOSE | MLU0 Replace U2A U1 GRV-9187 valve and actuator assembly with one from storeroom - 6 inch valve | E10567922 | MLWVPVALV | 1070001 | 2023-10-20 | 8492.57 | 7441.94 | 801.86 | 248.77
MLP | CLOSE | MLU2 2A AR PUMP VALVE (ZTAS-810) REPLACE | E10567466 | MLWVPVALV | 1070001 | 2022-12-05 | 8579.2 | 7324 | 1029.15 | 226.05
MLP | CLOSE | MLU0 REPLACE CPS TANK VALVES (7) | E10554815 | MLWVPVALV | 1070001 | 2023-11-07 | 237803.91 | 165654.33 | 54784.39 | 17365.19
MLP | CLOSE | MLU1 1E AR PUMP SUCTION VALVE REPLACE | E10539604 | MLWVPVALV | 1070001 | 2022-12-01 | 53517.5 | 0 | 52202.19 | 1315.31
MLP | COMP | MLU0 VACUUM BELT SERVICE WATER STRAINER REPLACEMENT | E10539478 | MLWVPVALV | 1070001 | 2022-12-01 | 96318.04 | 68251.94 | 12391.51 | 15674.59

## Capital Removal Dates
Site ID | Status | WO Description | Maximo Work Order Number | GL Project | GL Account | In Service Date | Actual Dollars | Material Cost | Labor Cost | Other Cost
MLP | INSERV | MLP U1: CLINKER GRINDER, MOTOR, & GATE UPGRADE | E10712699 | MLW1CGRPL | 1080005 | 2025-05-13 | 640248.88 | 34404.8 | 605521.05 | 323.03
MLP | INSERV | ML U1 Cooling Tower | E10608669 | MLWEC1CTF | 1080005 | 2023-12-06 | 1637089.49 | 27366.74 | 1487085.89 | 122636.86
MLP | CLOSE | MLU1 HP/VHP TURBINE ROTOR INSP & REPLACEMENT | E10634457 | MLWEC1VHL | 1080005 | 2024-01-29 | 771568.35 | 16400.01 | 393857.29 | 361311.05
MLP | CLOSE | MLU1 LPA TURBINE ROTOR INSP & REPLACEMENT | E10634268 | MLWEC1VHL | 1080005 | 2024-01-29 | 774894.48 | 71265.65 | 414909.69 | 288719.14
MLP | CLOSE | MLU0 OVATION DCS UPGRADE | E10539567 | MLWEP0DCS | 1080005 | 2022-12-14 | 1455.19 | 0 | 0 | 1455.19
MLP | CLOSE | MLU1 OVATION DCS UPGRADE | E10539568 | MLWEP1DCS | 1080005 | 2022-12-14
MLP | COMP | MLP U1: Generator Gas Baffles Purchase | E10840929 | MLWEP1GGB | 1080005 | 2025-05-09 | 185137.48 | 12731.52 | 20200.36 | 152205.6
MLP | INSERV | MLP U1: GENERATOR FIELD OUT INSPECTION | E10863838 | MLWEP1GNI | 1080005 | 2025-06-10 | 894796.67 | 14222.08 | 330609.07 | 549965.52
MLP | CLOSE | MLU2 OVATION DCS UPGRADE | E10539569 | MLWEP2DCS | 1080005 | 2022-12-14
MLP | CLOSE | MLU2 LPA DOGBONE EXPANSION JOINTS (4) REPLACE | E10539548 | MLWEP2LAI | 1080005 | 2022-11-30 | 37374.86 | 0 | 37281.46 | 93.4
MLP | CLOSE | MLU2 LPA TURBINE ROTOR INSP & REPLACEMENT | E10539524 | MLWEP2LAI | 1080005 | 2022-12-01 | 578292.12 | 9919 | 179830.51 | 388542.61
MLP | CLOSE | MLU2 LPB DOGBONE EXPANSION JOINTS (4) REPLACE | E10539549 | MLWEP2LBI | 1080005 | 2022-11-30 | 31249.25 | 0 | 31172.2 | 77.05
MLP | CLOSE | MLU2 LPB TURBINE ROTOR INSP & REPLACEMENT | E10539525 | MLWEP2LBI | 1080005 | 2022-12-01 | 635744.26 | 6106.44 | 304225.24 | 325412.58
MLP | COMP | MLP U1: CONTROL AIR DRYER | E10840169 | MLWEPAIRD | 1080005 | 2025-05-19 | 14445.16 | 71.66 | 14373.38 | 0.12
MLP | COMP | MLP - U2: BFP ROTATING ELEMENT REBUILD | E10712686 | MLWEPBFPB | 1080005 | 2024-12-19 | 3009.88 | 0 | 1752.08 | 1257.8
MLP | CLOSE | MLU1 Replace Shaft & 1st Stage Impellor on BFP Element removed in 2021 | E10539510 | MLWEPBFPB | 1080005 | 2022-11-09 | 27025.65 | 0 | 19730.49 | 7295.16
MLP | CLOSE | MLU2 BFP ROTATING ELEMENT (CSP) REPLACEMENT | E10539547 | MLWEPBFPE | 1080005 | 2022-11-01 | 26446.06 | 412.72 | 9133.91 | 16899.43
MLP | CLOSE | MLP - U1: PULL NEW CABLE TO KINNEAR DOOR 69 ON TBG-B | E10736536 | MLWEPCABL | 1080005 | 2024-05-01
MLP | CLOSE | MLU0 INSTALL PWR SUPPLY EMERGENCY FUEL TANK SHUT OFF'S | E10680559 | MLWEPCABL | 1080005 | 2023-09-22 | 3799.71 | 110.48 | 3689.22 | 0.01
MLP | CLOSE | MLU1 HYDROGEN SEAL OIL PP WIRE PULL | E10648477 | MLWEPCABL | 1080005 | 2024-03-13
MLP | CLOSE | MLU2 Pull New Cable to Generator Bus Duct Fan 2 From MCC | E10641262 | MLWEPCABL | 1080005 | 2023-05-21 | 2371.95 | 0 | 2378.4 | -6.45
MLP | CLOSE | MLU2 HOTWELL SUBPANEL CONDUCTIVITY TRANSMITTERS | E10634843 | MLWEPCABL | 1080005 | 2023-11-01
MLP | CLOSE | MLU2 FFC-1 SENSING LINES HEAT TRACE CABLE REPLACE | E10539530 | MLWEPCABL | 1080005 | 2022-12-28 | 2151.83 | 132.5 | 2019.28 | 0.05
MLP | CLOSE | MLU1 FFC-1 SENSING LINES HEAT TRACE CABLE REPLACE | E10539529 | MLWEPCABL | 1080005 | 2022-12-28 | 2498.64 | 142.7 | 2355.88 | 0.06
MLP | INPRG | MLP U2: SLAGBLOWER PLC CONTROLLER REPLACEMENT | E10925653 | MLWEPCTRL | 1080005 |  | 422.09 | 0 | 417.66 | 4.43
MLP | COMP | MLP U2: Replace Dewpoint Transmitter | E10908710 | MLWEPCTRL | 1080005 | 2025-05-27
MLP | INPRG | MLP U2: KRV-521 CONTROLLER REPLACEMENT | E10899429 | MLWEPCTRL | 1080005 |  | 2509.33 | 0 | 2475.12 | 34.21
MLP | COMP | MLP U2: #21 NASH PUMP MAGNETROL REPLACEMENT | E10894359 | MLWEPCTRL | 1080005 | 2025-06-10 | 458.58 | 0 | 451.65 | 6.93
MLP | COMP | MLP U2: KRV-541 CONTROLLER REPLACEMENT | E10894358 | MLWEPCTRL | 1080005 | 2025-05-27 | 2446.92 | 0 | 2423.48 | 23.44
MLP | CLOSE | MLP U0: BACKUP COMMUNICATION MODULE REPLACE | E10879559 | MLWEPCTRL | 1080005 | 2025-03-04 | 386.14 | 0 | 378.01 | 8.13
MLP | COMP | MLP U0: OX AIR BLOWER A PLC REPLACEMENT | E10872917 | MLWEPCTRL | 1080005 | 2025-05-01
MLP | CLOSE | MLP U2: DBA TRAIN 2 PLUGGED CHUTE ALARM | E10869736 | MLWEPCTRL | 1080005 | 2025-02-10 | 809.31 | 0 | 796.68 | 12.63
MLP | CLOSE | MLP U1: ASH PIT SUMP LEVEL CONTROL UPGRADE | E10868092 | MLWEPCTRL | 1080005 | 2025-02-26 | 3458.62 | 0 | 3392.29 | 66.33
MLP | CLOSE | MLP U0: REPLACE FILTER PRESS 3 HMI | E10841270 | MLWEPCTRL | 1080005 | 2024-12-12 | 1314.99 | 0 | 1290.81 | 24.18
MLP | CLOSE | MLP U2: RRV520 CONTROLLER REPLACEMENT | E10835886 | MLWEPCTRL | 1080005 | 2025-03-04 | 414.41 | 0 | 408.43 | 5.98
MLP | CLOSE | MLP U1: Upgrade DBA Sump Pump Level Controls | E10830310 | MLWEPCTRL | 1080005 | 2025-01-21 | 2107.04 | 0 | 2078.34 | 28.7
MLP | CLOSE | MLP U1 GRV-9092: REPLACE INDICATION | E10823805 | MLWEPCTRL | 1080005 | 2024-10-29 | 645.75 | 0 | 636.89 | 8.86
MLP | CLOSE | MLP U1: Replace Touch Screen on Air Compressor #13 | E10820964 | MLWEPCTRL | 1080005 | 2024-10-15
MLP | CLOSE | MLU1 REPLACE DBA Sump PP 3 Controller | E10796968 | MLWEPCTRL | 1080005 | 2024-08-05 | 212.47 | 0 | 210.36 | 2.11
MLP | CLOSE | MLP U2: SILICA ANALYZER REPLACEMENT | E10769856 | MLWEPCTRL | 1080005 | 2024-11-26 | 1000.01 | 0 | 1000 | 0.01
MLP | CLOSE | MLP U2: EHC CONDITIONING UNIT INSTALL | E10754872 | MLWEPCTRL | 1080005 | 2024-06-03
MLP | CLOSE | MLP - MLU1 LABOR TO INSTALL EHC CONDITIONING UNIT | E10736638 | MLWEPCTRL | 1080005 | 2024-06-03 | 1641.79 | 753.78 | 888.01 | 0
MLP | CLOSE | MLP - U1 RRV-1 DVC POSITIONER REPLACEMENT | E10735747 | MLWEPCTRL | 1080005 | 2024-06-11 | 1686.2 | 0 | 1669.5 | 16.7
MLP | CLOSE | MLP - U0: DFA SILO PANEL VIEW REPLACEMENT | E10710530 | MLWEPCTRL | 1080005 | 2024-04-05 | 673.26 | 0 | 661.88 | 11.38
MLP | CLOSE | MLU0 FILTER PRESS 1 HMI REPLACEMENT | E10690099 | MLWEPCTRL | 1080005 | 2024-02-05 | 652.67 | 0 | 646.1 | 6.57
MLP | CLOSE | MLU2 Well Water Head Tank Level Indication Replace | E10687111 | MLWEPCTRL | 1080005 | 2023-09-25 | 378.43 | 0 | 368.5 | 9.93
MLP | CLOSE | MLU1 - Replace BMO-4 Indication Bargraph | E10678168 | MLWEPCTRL | 1080005 | 2024-08-26 | 433.06 | 0 | 424.15 | 8.91
MLP | CLOSE | MLU1 Replace Stepdown Transformer for GSU Cooling Fans | E10649402 | MLWEPCTRL | 1080005 | 2023-06-22 | 2616.45 | 51.36 | 2565.09 | 0
MLP | CLOSE | MLU2 EHC TRIP HEADER PRESSURE TRANSMITTER REPLACE | E10647864 | MLWEPCTRL | 1080005 | 2023-10-26 | 378.58 | 0 | 373.74 | 4.84
MLP | CLOSE | MLU2 PRECIP CONTROL AIR HEAT TRACE INSTALL | E10643899 | MLWEPCTRL | 1080005 | 2023-11-03 | 14855.82 | 0 | 14855.82 | 0
MLP | CLOSE | MLU0 Replace Temperature Monitor on 51A Transformer | E10633409 | MLWEPCTRL | 1080005 | 2023-10-09 | 1604.6 | 0 | 1575.33 | 29.27
MLP | CLOSE | MLU2 PRECIP TR SET CONTROL MODULE | E10593837 | MLWEPCTRL | 1080005 | 2023-05-04
MLP | CLOSE | MLU0 INSTALL NEW VFD'S ON HS BELTS | E10567471 | MLWEPCTRL | 1080005 | 2023-12-05 | 686.55 | 0 | 678.81 | 7.74
MLP | CLOSE | MLU0 FGD VAC BELT A VFD REPLACEMENT | E10549400 | MLWEPCTRL | 1080005 | 2023-04-26
MLP | CLOSE | MLU0 CPS #3 LP & HP SLUDGE PUMPS VFD UPGRADES | E10549388 | MLWEPCTRL | 1080005 | 2023-10-27 | 1150.14 | 0 | 1135.71 | 14.43
MLP | CLOSE | MLU0 FGD VAC BELT #3 VFD REPLACEMENT | E10545020 | MLWEPCTRL | 1080005 | 2022-12-21 | 412.99 | 0 | 404.57 | 8.42
MLP | CLOSE | MLU0 DROP 122 POWER SUPPLY | E10539511 | MLWEPCTRL | 1080005 | 2022-10-01 | 0 | 0 | 0 | 0
MLP | CLOSE | MLU0 Install 4-East and 4-West Coal Conveyor Soft Starters | E10539500 | MLWEPCTRL | 1080005 | 2023-11-17 | 37762.91 | 1572.17 | 35945.05 | 245.69
MLP | CLOSE | MLU0 FUEL OIL STORAGE TANK LEVEL PROBE/PROCESSOR | E10539473 | MLWEPCTRL | 1080005 | 2023-11-21
MLP | CLOSE | MLU2 #23 AIR COMP INNER STAGE COOLERS REPLACEMENT | E10539472 | MLWEPCTRL | 1080005 | 2022-12-14 | 10171.17 | 0 | 10049.8 | 121.37
MLP | CLOSE | MLP U2: 22B CIRC WATER PUMP REBUILD | E10797898 | MLWEPCWPM | 1080005 | 2024-10-14 | 6506.57 | 60.7 | 6356.37 | 89.5
MLP | CLOSE | MLP U2: 22A CIRC WATER PUMP REBUILD | E10797890 | MLWEPCWPM | 1080005 | 2024-10-14 | 4838.8 | 0 | 4770.47 | 68.33
MLP | CLOSE | MLP - 12A CIRCULATING WATER PUMP | E10747369 | MLWEPCWPM | 1080005 | 2024-05-27 | 11396.96 | 395.35 | 10924.06 | 77.55
MLP | CLOSE | MLP - 12B CIRCULATING WATER PUMP | E10732312 | MLWEPCWPM | 1080005 | 2024-02-27 | 6228.8 | 0 | 6024.22 | 204.58
MLP | CLOSE | MLU2 21B CIRC WATER PUMP SHAFT REPLACEMENT | E10601053 | MLWEPCWPM | 1080005 | 2023-05-05 | 925.78 | 0 | 925.78 | 0
MLP | CLOSE | MLU1 11B CIRC WATER PUMP SHAFT REPLACEMENT | E10601045 | MLWEPCWPM | 1080005 | 2023-05-05
MLP | COMP | MLU2 DIESEL ENGINE FIRE PUMP & MOTOR REPLACE | E10611410 | MLWEPDFPM | 1080005 | 2025-05-27 | 19387.91 | 400.07 | 18857.54 | 130.3
MLP | COMP | MLU2 DIESEL ENGINE FIRE PUMP FUEL TANK REPLACE | E10611402 | MLWEPDFPM | 1080005 | 2025-05-27 | 36165.83 | 2158.53 | 34006.75 | 0.55
MLP | COMP | MLU1 DIESEL FIRE PUMP & MOTOR REPLACEMENT | E10539513 | MLWEPDFPM | 1080005 | 2024-07-25 | 29863.81 | 2018.85 | 26515.36 | 1329.6
MLP | CLOSE | MLU2 RECTIFIER BRIDGE REPLACEMENT | E10539544 | MLWEPDGHR | 1080005 | 2023-02-02 | 13257.27 | 312.5 | 12927.08 | 17.69
MLP | CLOSE | MLU2 SLAG BLOWER PLC AND FIBER PULLS | E10539515 | MLWEPFTCL | 1080005 | 2024-10-10 | 3149.97 | 0 | 3110.18 | 39.79
MLP | CLOSE | MLU1 SLAG BLOWER PLC & FIBER PULLS | E10539514 | MLWEPFTCL | 1080005 | 2024-05-31 | 5803.18 | 219.17 | 5568.3 | 15.71
MLP | INPRG | MLP U0: FGD ELEVATOR RM HVAC REPLACEMENT | E10888121 | MLWEPHVAC | 1080005 |  | 2810.93 | 695.5 | 2115.42 | 0.01
MLP | INPRG | MLP U0: REPLACE HEAT PUMP AT CFB | E10878577 | MLWEPHVAC | 1080005 |  | 4346.67 | 2003.8 | 2342.82 | 0.05
MLP | COMP | MLP U0: WINDOW HVAC UNIT - CONEX RR - OLD TRLR PARK | E10869749 | MLWEPHVAC | 1080005 | 2025-03-10 | 353.1 | 0 | 353.1 | 0
MLP | COMP | MLP U0: OFFICE ZONE 2 UNIT 24 HVAC REPLACEMENT | E10829676 | MLWEPHVAC | 1080005 | 2025-05-09 | 7714.34 | 3472.12 | 4242.11 | 0.11
MLP | CLOSE | MLP U0: GAURD HOUSE HVAC REPLACEMENT | E10824558 | MLWEPHVAC | 1080005 | 2024-11-05 | 420 | 0 | 420 | 0
MLP | CLOSE | MLP U0: SERVICE BLDG 2ND FLOOR HVAC UNIT REPLACE | E10795823 | MLWEPHVAC | 1080005 | 2024-11-07 | 11827.69 | 6888.45 | 4939.08 | 0.16
MLP | CLOSE | MLP U1: AUX BOILER MCC AC COND UNIT REPLACEMENT | E10779543 | MLWEPHVAC | 1080005 | 2024-10-25 | 1722.04 | 1102.03 | 620 | 0.01
MLP | CLOSE | MLP U0: UREA BLDG MCC RM MARVAIR AC UNIT REPLACE | E10779541 | MLWEPHVAC | 1080005 | 2024-10-15 | 1090.01 | 250 | 840 | 0.01
MLP | CLOSE | MLP U2: LABOR TO I/R CR & DCS RM HVAC | E10750208 | MLWEPHVAC | 1080005 | 2024-05-13 | 39422.48 | 4399.09 | 35023.05 | 0.34
MLP | COMP | MLP U1: LABOR TO I/R CR & DCS RM HVAC | E10750190 | MLWEPHVAC | 1080005 | 2024-05-23 | 27928.02 | 1069.21 | 26858.55 | 0.26
MLP | CLOSE | MLP - U0: LABOR TO I/R RSO BREAK ROOM HVAC | E10750182 | MLWEPHVAC | 1080005 | 2024-09-17 | 2498.54 | 1658.5 | 840 | 0.04
MLP | CLOSE | MLU2 CR & DCS RM HVAC UNIT REPLACEMENT | E10572732 | MLWEPHVAC | 1080005 | 2023-11-15
MLP | CLOSE | MLU0 RSO BREAK ROOM HVAC REPLACEMENT | E10572455 | MLWEPHVAC | 1080005 | 2023-11-15
MLP | CLOSE | MLU1 CR & DCS ROOM HVAC UNIT REPLACEMENT | E10572451 | MLWEPHVAC | 1080005 | 2023-11-15
MLP | CLOSE | MLU0 PLANT JANITOR ROOM / SHOWER HVAC REPLACEMENT | E10539546 | MLWEPHVAC | 1080005 | 2022-09-26 | 974.31 | 0 | 963.04 | 11.27
MLP | CLOSE | MLU0 PURCH & INST NEW AC/HEATPUMP ON RIVER BARGE CRANE | E10539475 | MLWEPHVAC | 1080005 | 2022-10-05 | 999.95 | 0 | 1000 | -0.05
MLP | INPRG | MLP U0: EMERGENCY LIGHTING BATTERY BANK REPLACEMENT | E10802604 | MLWEPLGHT | 1080005 |  | 7861.57 | 261.56 | 7599.8 | 0.21
MLP | CLOSE | MLU1 PRECIP LIGHTING UPGRADES | E10646178 | MLWEPLGHT | 1080005 | 2023-09-21 | 1030.38 | 0 | 1030.38 | 0
MLP | CLOSE | MLU0 Replace Stacker MCC Lighting (New conduit, receptables, lights, and wiring) | E10633395 | MLWEPLGHT | 1080005 | 2023-06-09
MLP | COMP | MLP U2: LABOR TO I/R 23 CONDENSATE BOOSTER PUMP MOTOR (CSP) | E10899661 | MLWEPMOTR | 1080005 | 2025-05-13 | 7642.6 | 0 | 7619.98 | 22.62
MLP | CLOSE | MLP U2: 22 ASH WATER PUMP MOTOR REPLACE | E10879889 | MLWEPMOTR | 1080005 | 2025-03-07 | 1445.35 | 0 | 1415.33 | 30.02
MLP | CLOSE | MLP FGD: Replace Ball Mill A Reducer Skid Motor | E10876094 | MLWEPMOTR | 1080005 | 2025-02-07 | 886.79 | 0 | 875.24 | 11.55
MLP | CLOSE | MLP U1: #13 FILTERED WATER PUMP MOTOR REPLACEMENT | E10863802 | MLWEPMOTR | 1080005 | 2025-01-10 | 1533.14 | 0 | 1498.92 | 34.22
MLP | CLOSE | MLP U2: #21 AIR COMPRESSOR MOTOR REPLACEMENT | E10838769 | MLWEPMOTR | 1080005 | 2025-03-18 | 10837.92 | 0 | 10837.82 | 0.1
MLP | CLOSE | MLP U2: 22 BOOSTER PUMP MOTOR REBUILD | E10834708 | MLWEPMOTR | 1080005 | 2024-12-17
MLP | CLOSE | MLP U2: 22 CLINKER GRINGER MOTOR REPLACEMENT | E10834333 | MLWEPMOTR | 1080005 | 2024-11-01 | 868.85 | 0 | 858.04 | 10.81
MLP | CLOSE | MLP U2: 21 CLINKER GRINDER MOTOR REPLACEMENT | E10834309 | MLWEPMOTR | 1080005 | 2024-11-01 | 720.18 | 0 | 709.43 | 10.75
MLP | CLOSE | MLP U1: REPLACE #12 CONDENSATE BOOSTER PUMP MOTOR | E10830305 | MLWEPMOTR | 1080005 | 2024-10-09 | 4720.89 | 0 | 4643.47 | 77.42
MLP | CLOSE | MLP U1: UMO-1 MOTOR REPLACMENT | E10823427 | MLWEPMOTR | 1080005 | 2024-10-02
MLP | CLOSE | MLP U1: 13 SOFTENED WATER BOOSTER PUMP MOTOR | E10795548 | MLWEPMOTR | 1080005 | 2024-07-23 | 1582.47 | 0 | 1552.5 | 29.97
MLP | CLOSE | MLP U1: REPLACE 13 CONDENSATE BOOSTER PUMP MOTOR | E10794526 | MLWEPMOTR | 1080005 | 2024-08-02 | 3867.3 | 0 | 3794.24 | 73.06
MLP | CLOSE | MLP U2: 21 AIR HEATER WASH MOTOR REWIND | E10756001 | MLWEPMOTR | 1080005 | 2024-09-14 | 511.4 | 0 | 511.4 | 0
MLP | CLOSE | MLP U1: 11 ASH WATER PUMP MOTOR/VALVES | E10749873 | MLWEPMOTR | 1080005 | 2024-05-07 | -53584.32 | -55985 | 2366.79 | 33.89
MLP | CLOSE | MLP U1: REPLACE 12 ASH H20 PP MOTOR | E10749160 | MLWEPMOTR | 1080005 | 2024-02-16 | -55332.48 | -55985 | 639.48 | 13.04
MLP | CLOSE | MLP - U1 #11 SOFTENED WATER BOOSTER PUMP MOTOR | E10747123 | MLWEPMOTR | 1080005 | 2024-03-07
MLP | CLOSE | MLP - U1: #13 SOFTENED WATER BOOSTER PUMP MOTOR | E10746792 | MLWEPMOTR | 1080005 | 2024-03-05 | 2104.23 | 0 | 2074.47 | 29.76
MLP | CLOSE | MLP - U0: ABSORBER AGITATOR 2H MOTOR REPLACEMENT | E10731467 | MLWEPMOTR | 1080005 | 2024-02-20 | 4056.04 | 0 | 3969.12 | 86.92
MLP | CLOSE | MLP U1: LABOR TO I/R 16 PULV MOTOR CSP | E10720449 | MLWEPMOTR | 1080005 | 2023-12-15 | 16278.96 | 0 | 12223.3 | 4055.66
MLP | CLOSE | MLP U1: 13 COOLING WATER PUMP MOTOR REPLACE | E10720127 | MLWEPMOTR | 1080005 | 2024-01-19 | 683.78 | 0 | 666.31 | 17.47
MLP | CLOSE | MLP - U0 RO SKID A 2ND STAGE MOTOR REPLACEMENT | E10691062 | MLWEPMOTR | 1080005 | 2023-10-24 | 2732.91 | 0 | 2693.66 | 39.25
MLP | CLOSE | MLU2 - REPLACE HD FIRE PUMP MOTOR | E10689498 | MLWEPMOTR | 1080005 | 2023-09-10 | 2291.36 | 0 | 2273 | 18.36
MLP | CLOSE | MLU1 - Replace East Clinker Grinder Motor | E10666372 | MLWEPMOTR | 1080005 | 2023-08-11 | 2062.31 | -1091.87 | 3137.49 | 16.69
MLP | CLOSE | MLU1 - Replace West Clinker Grinder Motor | E10666370 | MLWEPMOTR | 1080005 | 2023-08-11 | 3651.06 | 0 | 3624.28 | 26.78
MLP | CLOSE | MLU0 R1 CONVEYOR MOTOR REPLACEMENT | E10665586 | MLWEPMOTR | 1080005 | 2023-07-25 | 2553.84 | 0 | 2517.42 | 36.42
MLP | CLOSE | MLU2 - #21 WWS SUMP PUMP MOTOR REPLACEMENT | E10661299 | MLWEPMOTR | 1080005 | 2023-08-07 | 2829.36 | 0 | 2798.33 | 31.03
MLP | CLOSE | MLU1 - Replace Ash PP 12 Motor | E10649410 | MLWEPMOTR | 1080005 | 2023-06-27
MLP | CLOSE | MLU1 - Replace Service Water Pump 11 | E10644851 | MLWEPMOTR | 1080005 | 2023-07-18
MLP | CLOSE | MLU1 - 13 ASH WATER SUMP PUMP MOTOR REPLACE | E10634250 | MLWEPMOTR | 1080005 | 2024-03-13
MLP | CLOSE | MLU1 #12 COOLING WATER PUMP MOTOR REPLACE | E10593302 | MLWEPMOTR | 1080005 | 2023-02-02 | 1426.27 | 0 | 1414.24 | 12.03
MLP | CLOSE | MLU1 Replace the Burnt Up Motor _ UMO 1 Super Heater Bypass Block Valve | E10593105 | MLWEPMOTR | 1080005 | 2023-02-02
MLP | CLOSE | MLU1 Replace #11 ash pit sump pump | E10539630 | MLWEPMOTR | 1080005 | 2023-03-14
MLP | CLOSE | MLU1 #11 WASTE WATER SUMP PUMP MOTOR | E10539614 | MLWEPMOTR | 1080005 | 2023-03-14 | 2503.32 | 1699.82 | 793.15 | 10.35
MLP | CLOSE | MLU0 R10 FAN MOTOR REPLACEMENT | E10539508 | MLWEPMOTR | 1080005 | 2022-09-30 | 3275.08 | 0 | 3223.62 | 51.46
MLP | CLOSE | MLU0 MH #1 CONVEYOR MOTOR REPLACEMENT | E10539453 | MLWEPMOTR | 1080005 | 2024-03-12
MLP | CLOSE | MLU0 REPLACE 5 FGD EJ FOR NON UNIT PUMPS/TANKS | E10539623 | MLWEPMTRL | 1080005 | 2023-10-09 | 3555.01 | 0 | 3500.42 | 54.59
MLP | CLOSE | MLU1 REPLACE 1A BLEED PUMP EJ | E10539622 | MLWEPMTRL | 1080005 | 2023-05-03 | 637.58 | 0 | 279.79 | 357.79
MLP | CLOSE | MLU2 DEMIN FILTER PLC UPGRADE | E10539535 | MLWEPMTRL | 1080005 | 2023-11-22 | 1212.88 | 528 | 684.86 | 0.02
MLP | CLOSE | MLU2 PRECIP POWER FEED | E10539540 | MLWEPPTPF | 1080005 | 2022-12-01 | 11580.05 | 1105.6 | 10471.65 | 2.8
MLP | COMP | MLP U2: 21 CONDENSATE BOOSTER PUMP REPLACE | E10899431 | MLWEPPUMP | 1080005 | 2025-04-28
MLP | INPRG | MLP U1: 11A CIRCULATING WATER PUMP REBUILD | E10898933 | MLWEPPUMP | 1080005 |  | 7624.76 | 460.33 | 3954.26 | 3210.17
MLP | COMP | MLP U2: 22B CIRC WATER PUMP REBUILD | E10881140 | MLWEPPUMP | 1080005 | 2025-05-13 | 57464.97 | 33044.07 | 16560.83 | 7860.07
MLP | COMP | MLP U0: LABOR TO I/R CSP RO SKID A 1ST STAGE FEED PUMP | E10869619 | MLWEPPUMP | 1080005 | 2025-01-30 | 2921.36 | 0 | 2921.36 | 0
MLP | CLOSE | MLP U2: #3 ASH PIT SUMP PUMP REPLACEMENT | E10834360 | MLWEPPUMP | 1080005 | 2024-11-15 | 28864.34 | 17825.4 | 11035.96 | 2.98
MLP | CLOSE | MLP U2 ASH PIT SUMP PUMP 1 REPLACEMENT | E10834344 | MLWEPPUMP | 1080005 | 2025-04-15 | 7452.9 | 7452.9 | 0 | 0
MLP | CLOSE | MLP U2: STATOR WATER PUMP REPLACEMENT | E10829951 | MLWEPPUMP | 1080005 | 2024-12-17 | 0 | 0 | 0 | 0
MLP | CLOSE | MLP U1: LABOR TO MOVE ASH PIT SUMP PUMP U2 TO U1 | E10820742 | MLWEPPUMP | 1080005 | 2024-09-05 | 3998.74 | 0 | 3984.09 | 14.65
MLP | CLOSE | MLU1 Ash Pit Sump Pump 2 Replacement | E10796846 | MLWEPPUMP | 1080005 | 2024-12-04 | 351.39 | 0 | 343.85 | 7.54
MLP | CLOSE | MLU1 Ash Pit Sump Pump 1 Replacement | E10796845 | MLWEPPUMP | 1080005 | 2024-11-13 | 2339.57 | 0 | 2334.12 | 5.45
MLP | CLOSE | MLP U2: #23 RDV PUMP REPLACEMENT | E10783909 | MLWEPPUMP | 1080005 | 2024-07-10 | 332.31 | 0 | 327.43 | 4.88
MLP | CLOSE | MLU0 Station 1A Sump Pump Replacement | E10764089 | MLWEPPUMP | 1080005 | 2024-04-05 | 4910.05 | 0 | 4826.85 | 83.2
MLP | COMP | MLP U2: AT2006E NASH VACUUM PUMP SKID | E10714209 | MLWEPPUMP | 1080005 | 2024-10-17 | 63997.34 | 12264.53 | 51729.9 | 2.91
MLP | CLOSE | MLU1 #12 HOTWELL PUMP REPLACEMENT | E10683303 | MLWEPPUMP | 1080005 | 2023-10-02 | 3416.67 | 0 | 3359.93 | 56.74
MLP | CLOSE | MLU0 RO SKID B 2ND STAGE PUMP REPLACEMENT | E10680567 | MLWEPPUMP | 1080005 | 2023-09-21 | -0.78 | 0 | 0 | -0.78
MLP | CLOSE | MLU2 WASTE WATER PUMP REPLACEMENT | E10639423 | MLWEPPUMP | 1080005 | 2023-10-31 | 11996.04 | 2663.46 | 9207.33 | 125.25
MLP | CLOSE | MLU1 #12 GLSO Fan replacement | E10630360 | MLWEPPUMP | 1080005 | 2023-08-15
MLP | CLOSE | MLU2 22 EHC PUMP REPLACEMENT | E10618865 | MLWEPPUMP | 1080005 | 2024-10-24 | 629.39 | 0 | 616.47 | 12.92
MLP | CLOSE | MLU1 REPLACE #11 GSLO FAN | E10615599 | MLWEPPUMP | 1080005 | 2023-03-08 | -1527.89 | -1824 | 278.3 | 17.81
MLP | CLOSE | MLP - MLU1 - Replace check valves on Waste Water Sump Pumps #11, #12, and #13 | E10610281 | MLWEPPUMP | 1080005 | 2023-04-26 | 288.75 | 0 | 286.89 | 1.86
MLP | CLOSE | MLU0 Install 3" sump pump in HS tunnel | E10605002 | MLWEPPUMP | 1080005 | 2023-06-30
MLP | CLOSE | MLU0 1ST STAGE REVERSE OSMOSIS SYSTEM PUMP CAP SPARE | E10593846 | MLWEPPUMP | 1080005 | 2023-10-26 | 2649.1 | 58.96 | 2590.14 | 0
MLP | CLOSE | MLU2 REPLACE #2 ASH PIT SUMP PUMP | E10590875 | MLWEPPUMP | 1080005 | 2023-01-26 | 865.88 | 0 | 858.54 | 7.34
MLP | CLOSE | MLP REPLACE 4 RIVER WTR ROOT VLVS BTTM ASH CNVSN PRJCT BOTH UNITS | E10552396 | MLWEPPUMP | 1080005 | 2022-10-13 | 3260.03 | 3260.03 | 0 | 0
MLP | CLOSE | MLU0 Replace #1 RWMU Pump | E10539632 | MLWEPPUMP | 1080005 | 2022-11-01 | 34451.4 | 17789.89 | 13525.48 | 3136.03
MLP | CLOSE | MLU1 #11 FILTERED WATER PUMP REPLACEMENT | E10539628 | MLWEPPUMP | 1080005 | 2023-05-05 | 3935.35 | 0 | 3875.77 | 59.58
MLP | CLOSE | MLU2 #21 COOLING WATER BLOWDOWN PUMP REPLACE | E10539618 | MLWEPPUMP | 1080005 | 2023-07-19 | 15.29 | 15.29 | 0 | 0
MLP | CLOSE | MLU0 DFA SILO AREA B SUMP PUMP REPLACEMENT | E10539611 | MLWEPPUMP | 1080005 | 2022-09-29 | 3031.38 | 855.03 | 2067.29 | 109.06
MLP | CLOSE | MLU2 DEMIN ACID PUMP/PIPING UPGRADE | E10539489 | MLWEPPUMP | 1080005 | 2023-11-14 | 2357.96 | 0 | 2357.96 | 0
MLP | CLOSE | MLU1 DEMIN ACID PUMP/PIPING UPGRADE | E10539488 | MLWEPPUMP | 1080005 | 2022-11-19
MLP | CLOSE | MLU2 26 ASH WATER PUMP REPLACEMENT | E10539470 | MLWEPPUMP | 1080005 | 2022-11-30 | 1096.01 | 0 | 1082.94 | 13.07
MLP | CLOSE | MLU1 #12 ASH WATER PUMP REPLACEMENT | E10539461 | MLWEPPUMP | 1080005 | 2023-04-26
MLP | CLOSE | MLU2 DEMINERALIZER RESIN REPLACEMENT (5 YR) | E10614270 | MLWEPRESN | 1080005 | 2023-10-29 | 35431.15 | 7258.55 | 27985.9 | 186.7
MLP | CLOSE | MLU2 REPLACE SECURITY APPLIANCE SERVER | E10539591 | MLWEPSERV | 1080005 | 2022-10-11
MLP | CLOSE | MLU1 REPLACE SECURITY APPLIANCE SERVER | E10539590 | MLWEPSERV | 1080005 | 2022-10-11
MLP | CLOSE | MLU0 REPLACE SECURITY APPLIANCE SERVER | E10539589 | MLWEPSERV | 1080005 | 2022-10-11
MLP | CLOSE | MLU2 Replace OPC Server Unit 2 | E10539522 | MLWEPSERV | 1080005 | 2022-10-11
MLP | CLOSE | MLU1 Replace OPC Server Unit 1 | E10539521 | MLWEPSERV | 1080005 | 2022-10-11
MLP | CLOSE | MLU0 Replace OPC Server Unit 0 | E10539520 | MLWEPSERV | 1080005 | 2022-10-11
MLP | COMP | MLP U2: TR SET 4-17B BREAKER REPLACEMENT | E10906936 | MLWEPSWGR | 1080005 | 2025-05-08 | 406.11 | 0 | 402.17 | 3.94
MLP | CLOSE | MLU0 TRANSFORMER 14A HYDRAN MONITOR REPLACE | E10665203 | MLWEPSWGR | 1080005 | 2024-02-22 | 2957.41 | 0 | 2918.45 | 38.96
MLP | CLOSE | MLU0 TRANSFORMER 12B HYDRAN MONITOR REPLACE | E10665196 | MLWEPSWGR | 1080005 | 2024-02-07 | 1583.84 | 0 | 1561.49 | 22.35
MLP | CLOSE | MLU0 HVF-4 BREAKER REPLACEMENT | E10643882 | MLWEPSWGR | 1080005 | 2023-06-05
MLP | CLOSE | MLU2 TURBINE ROOM LIGHTING BREAKER UPGRADE | E10615977 | MLWEPSWGR | 1080005 | 2023-04-25
MLP | CLOSE | MLU1 FGD OXIDATION AIR BLOWER A MULTILIN RELAY 869 | E10611125 | MLWEPSWGR | 1080005 | 2023-10-26 | 429.98 | 0 | 421.88 | 8.1
MLP | CLOSE | MLU2 OXIDATION AIR BLOWER C MULTILIN RELAY 869 | E10611120 | MLWEPSWGR | 1080005 | 2023-10-26 | 1757.93 | 0 | 1717.98 | 39.95
MLP | CLOSE | MLU0 CPS LIME VALVE LSAR 7104B & LSAR 7204B POSITIONER | E10610709 | MLWEPSWGR | 1080005 | 2023-06-15
MLP | CLOSE | MLU2 Replace CC2S2 Line Breaker Disconnect | E10539617 | MLWEPSWGR | 1080005 | 2023-12-21 | 38954.57 | 0 | 55.76 | 38898.81
MLP | CLOSE | MLU0 TSFMR 12A/12B TIE BREAKER GE MULTILIN RELAY REPLACE | E10539600 | MLWEPSWGR | 1080005 | 2024-06-26 | 67.85 | 0 | 67.85 | 0
MLP | CLOSE | MLU0 CPS REGULATING TRANSFORMER REPLACE | E10539580 | MLWEPSWGR | 1080005 | 2023-02-02 | 13191.14 | 206.78 | 12853.78 | 130.58
MLP | CLOSE | MLU0 STATION 2 TRANSFORMER REPLACEMENT | E10539499 | MLWEPSWGR | 1080005 | 2024-03-08
MLP | CLOSE | MLU1 REPLACE ID FAN 12 PROTECTIVE RELAY | E10539486 | MLWEPSWGR | 1080005 | 2022-10-01 | -7905 | -7905 | 0 | 0
MLP | COMP | MLP U0: RETIRE CSP 0171606015 - BUSHING | E10896797 | MLWEPTFRM | 1080005 | 2025-06-03 | -6976.26 | 0 | 0 | -6976.26
MLP | COMP | MLP U1: U1 EXCITER POWER POTENTIAL TRANSFORMER | E10749172 | MLWEPTFRM | 1080005 | 2025-05-08 | 25212.2 | 1543.48 | 23668.65 | 0.07
MLP | COMP | MLP U2: ECON PRESSURE PROBE C ROSEMOUNT TRANSMITTER | E10910456 | MLWEPTRMT | 1080005 | 2025-05-30 | 435.54 | 0 | 429.03 | 6.51
MLP | COMP | MLP U1: REPLACE DVC ON IRV-20 | E10902811 | MLWEPTRMT | 1080005 | 2025-05-13 | 4523.83 | 0 | 4511.95 | 11.88
MLP | COMP | MLP U2: 22 DEMIN ROSEMOUNT TRANSMITTER REPLACE | E10887734 | MLWEPTRMT | 1080005 | 2025-05-13 | 4125.38 | 0 | 4117.59 | 7.79
MLP | CLOSE | MLP U1: FURNACE PRESSURE TRANSMITTER A REPLACE | E10887155 | MLWEPTRMT | 1080005 | 2025-03-19 | 337.38 | 0 | 324.35 | 13.03
MLP | CLOSE | MLP U1: 14 LP HEATER LEVEL TRANSMITTER REPLACEMENT | E10881046 | MLWEPTRMT | 1080005 | 2025-03-31 | 1634.73 | 0 | 1585.36 | 49.37
MLP | CLOSE | MLP U2: Replace Furnace Pressure Transmitter | E10876332 | MLWEPTRMT | 1080005 | 2025-02-07 | 422.61 | 0 | 406.33 | 16.28
MLP | CLOSE | MLP U1: CONDENSATE TANK LEVEL TRANSMITTER REPLACE | E10860947 | MLWEPTRMT | 1080005 | 2024-12-26 | 313.93 | 0 | 307.89 | 6.04
MLP | COMP | MLP U1: CR PRESSURE GAUGE REPLACEMENT | E10859355 | MLWEPTRMT | 1080005 | 2025-05-07 | 8182.39 | 0 | 8151.12 | 31.27
MLP | INPRG | MLP U1: HYDROGEN DEWPOINT METER REPLACEMENT | E10858459 | MLWEPTRMT | 1080005 |  | 5313.45 | 217 | 5036.74 | 59.71
MLP | CLOSE | MLP U1: FUEL OIL CORIOLIS FLOWMETER | E10800644 | MLWEPTRMT | 1080005 | 2024-09-12 | 2098.98 | 0 | 2069.33 | 29.65
MLP | CLOSE | MLP U1: WATER CANNON SKID DCHG FLOW TRANSMITTER | E10797763 | MLWEPTRMT | 1080005 | 2024-10-17 | 237.68 | 0 | 233.17 | 4.51
MLP | CLOSE | MLP U2: WATER CANNON STRAINER DIFF PRESSURE TRANSMITTER | E10797755 | MLWEPTRMT | 1080005 | 2024-09-25
MLP | CLOSE | MLP U2: WATER CANNON SKID DCHG FLOW TRANSMITTER | E10797750 | MLWEPTRMT | 1080005 | 2024-10-17 | 316.93 | 0 | 310.96 | 5.97
MLP | CLOSE | MLP U2: 21 HOTWELL PUMP DISCHARGE TRANSMITTER | E10756193 | MLWEPTRMT | 1080005 | 2024-03-08 | 867.79 | 0 | 856.94 | 10.85
MLP | CLOSE | MLP U0: NORTH CY CAUSTIC SYSTEM ECD TRANSMITTERS | E10710681 | MLWEPTRMT | 1080005 | 2024-02-21
MLP | CLOSE | MLP U1 - HP Heater 7B Lvl Probe A - Reading Erratic | E10709392 | MLWEPTRMT | 1080005 | 2023-11-15 | 342.83 | 0 | 338.95 | 3.88
MLP | CLOSE | MLU0 DSI CONV AIR BLWR 1 PRESSURE TRANSMITTER REPLACEMENT | E10665719 | MLWEPTRMT | 1080005 | 2023-08-11 | 621.85 | 0 | 613 | 8.85
MLP | CLOSE | MLU0 FGD VAC BELT C TRANSMITTER REPLACE | E10650484 | MLWEPTRMT | 1080005 | 2023-06-22 | 836.01 | 0 | 830.73 | 5.28
MLP | CLOSE | MLU1 HOTWELL SUBPANEL CONDUCTIVITY TRANSMITTERS | E10634834 | MLWEPTRMT | 1080005 | 2023-11-01
MLP | CLOSE | MLU0 CPS EFFLUENT SUMP PH TRANSMITTERS REPLACE | E10633642 | MLWEPTRMT | 1080005 | 2023-11-01
MLP | CLOSE | MLU1 SCR DISCHARGE TRIP PRESSURE TRANSMITTER | E10567555 | MLWEPTRMT | 1080005 | 2023-10-26 | 378.58 | 0 | 373.74 | 4.84
MLP | CLOSE | MLU2 HYDROGEN PURITY METER REPLACEMENT | E10557783 | MLWEPTRMT | 1080005 | 2023-03-29 | 1289.59 | 0 | 1282.71 | 6.88
MLP | CLOSE | MLU1 HIGH DEMAND FIRE PMP DSCHG PRESSURE XMTR | E10549384 | MLWEPTRMT | 1080005 | 2023-02-15 | 404.13 | 0 | 400.64 | 3.49
MLP | CLOSE | MLU2 #2 & #4 FFC TRANSMITTER REPLACEMENT | E10539625 | MLWEPTRMT | 1080005 | 2022-12-22 | 6741.22 | 1046.84 | 5594.58 | 99.8
MLP | CLOSE | MLU2 YOKOGAWA DISSOLVED OXYGEN TRANSMITTER | E10539517 | MLWEPTRMT | 1080005 | 2023-04-06
MLP | CLOSE | MLU1 YOKOGAWA DISSOLVED OXYGEN TRANSMITTER | E10539516 | MLWEPTRMT | 1080005 | 2023-04-25 | 248 | 248 | 0 | 0
MLP | CLOSE | MLU2 DA TANK LEVEL TRANSMITTER REPLACEMENT | E10539512 | MLWEPTRMT | 1080005 | 2023-04-26
MLP | CLOSE | MLU0 CPS FERRIC CHLORIDE MIX TANK 2 ECD PH TRANSMITTER REPLACEMENT | E10539509 | MLWEPTRMT | 1080005 | 2022-11-09 | -1005 | -1005 | 0 | 0
MLP | COMP | MLU2 CIRC WATER PH TRANSMITTER REPLACEMENT | E10539507 | MLWEPTRMT | 1080005 | 2023-07-31
MLP | COMP | MLU1 CIRC WATER PH TRANSMITTER REPLACEMENT | E10539506 | MLWEPTRMT | 1080005 | 2023-07-31 | 44.48 | 0 | 38.06 | 6.42
MLP | CLOSE | MLU1 CIRC WATER DCHG PRESSURE TRANSMITTER REPLACEMENT | E10539496 | MLWEPTRMT | 1080005 | 2023-12-21 | 3076.5 | 0 | 3039.28 | 37.22
MLP | CLOSE | MLU1 TURB RM COMB COIL PRESSURE TRANSMITTER | E10539495 | MLWEPTRMT | 1080005 | 2023-11-21 | 1149.57 | 0 | 1138.29 | 11.28
MLP | CLOSE | MLU2 COOLING TWR LEVEL STILLWELL & LEVEL TRANSMITTER | E10539459 | MLWEPTRMT | 1080005 | 2024-01-01 | 4547.86 | 0 | 4525.76 | 22.1
MLP | COMP | MLP U1: TURBINE CROSSOVER BELLOWS REPLACEMENT | E10878682 | MLWEPTURB | 1080005 | 2025-04-24 | 3285.62 | 0 | 3285.6 | 0.02
MLP | CLOSE | MLP U2: #24 CLARITE FILTER INLET HSO REPLACE | E10838901 | MLWEPVALV | 1080005 | 2025-01-31 | 3655.45 | 0 | 3655.44 | 0.01
MLP | CLOSE | MLP U2: #22 CLARITE FILTER INLET HSO REPLACE | E10838885 | MLWEPVALV | 1080005 | 2025-01-31 | 3532.25 | 0 | 3532.24 | 0.01
MLP | CLOSE | MLP U2: #22 HYDROGEN COOLING PUMP SUCTION HSO | E10821720 | MLWEPVALV | 1080005 | 2024-12-17 | 0 | 0 | 0 | 0
MLP | COMP | MLP U1: REMOVE CLARITE FLTR 11, 12, 13, &14 INTERNALS | E10821719 | MLWEPVALV | 1080005 | 2025-02-05 | 309798.87 | 60674.93 | 248569.58 | 554.36
MLP | COMP | MLP U2: 21, 22, 23, 24 CLARITE FILTER INTERNALS REMOVAL | E10797765 | MLWEPVALV | 1080005 | 2024-12-09 | 318004.95 | 32927.87 | 284847.56 | 229.52
MLP | CLOSE | MLP U1: 13 CLARITE FILTER VALVE (KMO-532) REPLACE | E10779325 | MLWEPVALV | 1080005 | 2024-05-24
MLP | CLOSE | MLP U2 COOLING TOWER DELUGE DEMO | E10752097 | MLWEPVALV | 1080005 | 2024-05-03 | 31648.83 | 963.6 | 30685.08 | 0.15
MLP | CLOSE | MLP U1 COOLING TOWER DELUGE DEMO | E10752096 | MLWEPVALV | 1080005 | 2024-05-03 | 44800.91 | 6475.22 | 38325.5 | 0.19
MLP | CLOSE | MLP - U0: STATION 3 HEADER AND DELUGE REPLACEMENT | E10745800 | MLWEPVALV | 1080005 | 2024-07-01 | 96054.21 | 4467.69 | 91585.68 | 0.84
MLP | CLOSE | MLP U1: Replace ARV-706 Valve | E10730016 | MLWEPVALV | 1080005 | 2024-01-03 | 2296.42 | 0 | 2272.56 | 23.86
MLP | CLOSE | MLP U2: REPLACE Valve, Gate, 6 IN 300 LB Bolted Bonnet | E10730011 | MLWEPVALV | 1080005 | 2024-01-10 | 912.65 | 0 | 889.34 | 23.31
MLP | CLOSE | MLP U1: #12 WWS PUMP CHECK VALVE REPLACE | E10721082 | MLWEPVALV | 1080005 | 2023-12-20 | 241.61 | 0 | 238.41 | 3.2
MLP | CLOSE | MLP U1: UPPER S. COMBUSTION COIL HSO REPLACE | E10719985 | MLWEPVALV | 1080005 | 2024-01-10
MLP | CLOSE | MLU0 - H2 BULK STORAGE TANK SAFETY VALVE REPLACE | E10695080 | MLWEPVALV | 1080005 | 2023-12-01
MLP | CLOSE | MLU1 #12 ASH WATER PUMP DISCHARGE VALVE REPLACE | E10656180 | MLWEPVALV | 1080005 | 2023-06-20
MLP | CLOSE | MLU2 REPLACE WW SUMP PIPING SUCTION / DCHG VALVES | E10646779 | MLWEPVALV | 1080005 | 2023-10-24 | 2388.34 | 0 | 2379.16 | 9.18
MLP | CLOSE | MLU0 MAINT SHOP DOOR FIRE HEADER REPLACEMENT | E10644246 | MLWEPVALV | 1080005 | 2023-08-15 | 4983.43 | 0 | 4892.61 | 90.82
MLP | CLOSE | MLU2 #23 Waste Water Sump Check Valve Replacement | E10642245 | MLWEPVALV | 1080005 | 2023-05-31 | 945.3 | 0 | 939.44 | 5.86
MLP | CLOSE | MLU2 6TH FLOOR FIRE HEADER REPLACEMENT | E10640690 | MLWEPVALV | 1080005 | 2023-08-15 | 5736.6 | 0 | 5736.6 | 0
MLP | CLOSE | MLU1 6TH FLOOR FIRE HEADER REPLACEMENT | E10640685 | MLWEPVALV | 1080005 | 2023-08-04 | 10870.8 | 0 | 10870.8 | 0
MLP | CLOSE | MLU1 REPLACE FIRE ISOLATION VALVE 50 | E10611094 | MLWEPVALV | 1080005 | 2023-04-26 | 673.64 | 0 | 665.81 | 7.83
MLP | CLOSE | MLU1 REPLACE RMO 8 VALVE | E10584145 | MLWEPVALV | 1080005 | 2023-01-16 | 7626.72 | 15.01 | 7533.15 | 78.56
MLP | CLOSE | MLU1 7A HP Heater safety replacement | E10582090 | MLWEPVALV | 1080005 | 2023-01-02 | 1117.69 | 0 | 1117.69 | 0
MLP | CLOSE | MLU1 REPLACE PLANT AIR RISER 8 IN ROOT VALVE | E10558775 | MLWEPVALV | 1080005 | 2022-11-05 | 1747.69 | 0 | 1736.77 | 10.92
MLP | CLOSE | MLU2 #22 CONDENSATE BOOSTER PUMP 12" GATE VALVE | E10552741 | MLWEPVALV | 1080005 | 2022-10-21 | 854.17 | 0 | 836.75 | 17.42
MLP | CLOSE | MLU1 REPLACE THE 12" GATE VALVE ON #13 CLARITE FILTER H.S.O | E10539629 | MLWEPVALV | 1080005 | 2023-01-11 | 448.4 | 0 | 443.44 | 4.96
MLP | CLOSE | MLU1 #12 WASTE WATER SUMP PUMP CHECK VALVE | E10539616 | MLWEPVALV | 1080005 | 2022-09-28 | 2994.68 | 1976.36 | 1006.8 | 11.52
MLP | COMP | MLP U1: BFPT INSPECTION | E10863835 | MLWES1BTI | 1080005 | 2025-05-05 | 315218.92 | 2872.83 | 45641.91 | 266704.18
MLP | CLOSE | MLU1 - 2 LPA DOGBONE EJ REPLACEMENT | E10634778 | MLWES1BTI | 1080005 | 2023-12-31 | 11148.92 | 0 | 11148.92 | 0
MLP | INPRG | MLP U0: HBF-1B CONVEYOR BELT REPLACEMENT | E10927880 | MLWMPBELT | 1080005 |  | 513.83 | 0 | 504.48 | 9.35
MLP | CLOSE | MLP U0: LABOR TO I/R 4 W BELT MOTOR & GEARBOX CSP'S | E10870483 | MLWMPBELT | 1080005 | 2025-02-17 | 8082.5 | 128.8 | 7836.52 | 117.18
MLP | COMP | MLP U0: R6 CONVEYOR MOTOR REPLACEMENT | E10861850 | MLWMPBELT | 1080005 | 2025-05-13 | 4858.48 | 0 | 4816.15 | 42.33
MLP | INPRG | MLP U0: BC9 BELT REPLACEMENT | E10840412 | MLWMPBELT | 1080005 |  | 4193.12 | 1335 | 2858.1 | 0.02
MLP | CLOSE | MLP U0: BF-1 GYPSUM FEEDER BELT REPLACEMENT | E10835360 | MLWMPBELT | 1080005 | 2024-12-04 | 3127.76 | 0 | 3116.49 | 11.27
MLP | CLOSE | MLP U0: BC-8 CONVEYOR BELT REPLACEMENT | E10768566 | MLWMPBELT | 1080005 | 2024-05-09 | 2490.06 | 2490 | 0 | 0.06
MLP | CLOSE | MLP U0: HSC3 CONVEYOR BELT REPLACEMENT | E10756194 | MLWMPBELT | 1080005 | 2024-03-27 | 5553.65 | 0 | 5553.6 | 0.05
MLP | CLOSE | MLP U1: CONVEYOR BELT 8 REPLACEMENT | E10754866 | MLWMPBELT | 1080005 | 2024-03-06 | 3106.01 | 0 | 3106 | 0.01
MLP | CLOSE | MLP - U0: HBF-1A FEEDER BELT REPLACEMENT | E10743670 | MLWMPBELT | 1080005 | 2024-02-08 | 4653.58 | 373.3 | 4218.73 | 61.55
MLP | CLOSE | MLP - U0: BC-20 CONVEYOR BELT REPLACEMENT | E10736916 | MLWMPBELT | 1080005 | 2024-01-25 | 12128.52 | 0 | 12128.52 | 0
MLP | CLOSE | MLP - U0 HSC-2 SNUB PULLEY & BEARINGS | E10736865 | MLWMPBELT | 1080005 | 2024-02-01 | 6533.1 | 0 | 6533.1 | 0
MLP | CLOSE | MLP U0 - HRC2 CONV BELT REPLACE | E10736545 | MLWMPBELT | 1080005 | 2024-02-27 | 8398.53 | 0 | 8398.5 | 0.03
MLP | CLOSE | MLU0 HIGH SULFUR FEEDER BELT BF-1A REPLACE | E10693655 | MLWMPBELT | 1080005 | 2024-04-11
MLP | CLOSE | MLU0 REPLACE CONVEYOR BC21 | E10688609 | MLWMPBELT | 1080005 | 2023-09-22 | 6790.8 | 0 | 6790.8 | 0
MLP | CLOSE | MLU0 REPLACE CONVEYOR BC14 | E10688600 | MLWMPBELT | 1080005 | 2023-09-22 | 8138.1 | 0 | 8138.1 | 0
MLP | CLOSE | MLU0 BF1 CONV BELT REPLACEMENT | E10682682 | MLWMPBELT | 1080005 | 2023-08-29 | 1525 | 0 | 1525 | 0
MLP | CLOSE | MLU0 HRC-2 CONVEYOR SNUB PULLEY REPLACEMENT | E10680731 | MLWMPBELT | 1080005 | 2023-10-11 | 11501.06 | 0 | 11424.5 | 76.56
MLP | CLOSE | MLU0 BEND PULLEY ON 4E CONV. REPLACEMENT | E10679246 | MLWMPBELT | 1080005 | 2023-08-18 | 1911.71 | 0 | 1885.34 | 26.37
MLP | CLOSE | MLU0 R2 CONVEYOR BELT REPLACEMENT | E10630106 | MLWMPBELT | 1080005 | 2023-10-18 | 3631.32 | 0 | 3631.32 | 0
MLP | CLOSE | MLU0 BF1 FEEDER BELT REPLACEMENT | E10610957 | MLWMPBELT | 1080005 | 2023-03-03 | 2255.6 | 0 | 2255.6 | 0
MLP | CLOSE | MLU0 REPLACE BELT SCRAPERS FROM 4E/W TO SILOS | E10576378 | MLWMPBELT | 1080005 | 2022-12-31
MLP | CLOSE | MLU0 REPLACE HRC-1 CONVEYOR BELT | E10575679 | MLWMPBELT | 1080005 | 2023-01-12 | 0 | 0 | 0 | 0
MLP | CLOSE | MLU0 BC-17 CONVEYOR BELT REPLACEMENT | E10571222 | MLWMPBELT | 1080005 | 2023-01-31 | 9555.08 | 0 | 9492.6 | 62.48
MLP | CLOSE | MLU0 REPLACE R6 CONVEYOR BELT | E10557598 | MLWMPBELT | 1080005 | 2022-11-18 | 2731.21 | 0 | 2723.44 | 7.77
MLP | CLOSE | MLU0 REPLACE R8 CONVEYOR BELT | E10544982 | MLWMPBELT | 1080005 | 2022-12-16 | 3351.69 | 0 | 3351.6 | 0.09
MLP | CLOSE | MLU0 4E CONVEYOR BELT REPLACEMENT | E10542785 | MLWMPBELT | 1080005 | 2022-11-23 | 1935.2 | 0 | 1935.15 | 0.05
MLP | CLOSE | MLU0 ROTOCLONE BOOSTER FAN REPLACEMENT | E10539620 | MLWMPBELT | 1080005 | 2023-02-01
MLP | CLOSE | MLU0 BF1 FEEDER BELT REPLACEMENT | E10539603 | MLWMPBELT | 1080005 | 2022-09-29 | 5494.77 | 0 | 5473.94 | 20.83
MLP | CLOSE | MLU0 Change BC-10 conveyor | E10539572 | MLWMPBELT | 1080005 | 2022-10-04 | 13888.83 | 1754 | 11862.48 | 272.35
MLP | CLOSE | MLU0 #3 HSF VFD REPLACEMENT | E10539557 | MLWMPBELT | 1080005 | 2023-09-21
MLP | CLOSE | MLU0 REPLACE R5 HEAD CHUTE | E10630103 | MLWMPCHUT | 1080005 | 2023-11-14 | 54968.5 | 44304 | 10664.5 | 0
MLP | CLOSE | MLU0 R6 Head Chute | E10574868 | MLWMPCHUT | 1080005 | 2023-11-14 | 61078.37 | 36343.84 | 24734.53 | 0
MLP | CLOSE | MLU0 R9 CONVEYOR CHUTE REPLACEMENT | E10539552 | MLWMPCHUT | 1080005 | 2022-12-01 | 222678.53 | 99228 | 121819.63 | 1630.9
MLP | CLOSE | MLU0 REPLACE 3B & 3C CHUTES | E10539523 | MLWMPCHUT | 1080005 | 2022-12-31 | 39665.04 | 24528 | 15095.35 | 41.69
MLP | COMP | MLP U0: HSC-3 GEARBOX REPLACEMENT | E10850821 | MLWMPCOMP | 1080005 | 2025-04-30 | 21287.53 | 79.4 | 20969.36 | 238.77
MLP | COMP | MLP U0: PORTAL RECLAIMER SCRAPPER REMOVAL | E10841688 | MLWMPCOMP | 1080005 | 2025-06-09 | 109431.89 | 3960.05 | 105415.76 | 56.08
MLP | CLOSE | MLP U0: BC12 TAIL PULLEY REPLACEMENT | E10840400 | MLWMPCOMP | 1080005 | 2025-01-03 | 1418.69 | 0 | 1418.68 | 0.01
MLP | CLOSE | MLP U0: BF1 GYPSUM FEEDER MOTOR & GEARBOX REPLACEMENT | E10833899 | MLWMPCOMP | 1080005 | 2024-12-14 | 6706.7 | 0 | 6612.47 | 94.23
MLP | CLOSE | MLP U0: SILO A FLUIDIZING AIR BLOWER B REPLACEMENT | E10829678 | MLWMPCOMP | 1080005 | 2024-10-29 | 758.3 | 0 | 748.03 | 10.27
MLP | CLOSE | MLP U0: SILO A FLUIDIZING AIR BLOWER A REPLACE | E10819465 | MLWMPCOMP | 1080005 | 2024-09-12 | 396.02 | 0 | 391.36 | 4.66
MLP | COMP | MLP U0: REMOVE CONV 4 EAST & WEST FIRE PROTECTION SYSTEM | E10811550 | MLWMPCOMP | 1080005 | 2024-09-27 | 20454.15 | 852.27 | 19600.4 | 1.48
MLP | CLOSE | MLP U0: BC 12 BEND PULLEY REPLACEMENT | E10798759 | MLWMPCOMP | 1080005 | 2024-08-09 | 3074 | 0 | 3073.99 | 0.01
MLP | CLOSE | MLP U0: R4 TAIL PULLEY REPLACEMENT | E10769848 | MLWMPCOMP | 1080005 | 2024-06-26 | 1805.32 | 0 | 1805.31 | 0.01
MLP | CLOSE | MLP U0: STAMLER CONV CHAIN REPLACEMENT | E10768670 | MLWMPCOMP | 1080005 | 2024-05-28 | 15529.15 | 740 | 14788.96 | 0.19
MLP | CLOSE | MLP U0: R2 CONVEYOR ROLLER REPLACEMENT | E10768525 | MLWMPCOMP | 1080005 | 2024-06-14
MLP | CLOSE | MLP - U0: HRC-3 Gearbox Replacement/Rebuild | E10747400 | MLWMPCOMP | 1080005 | 2024-03-01 | 2576.07 | -996.25 | 2618.34 | 953.98
MLP | CLOSE | MLP U0: HBF-1 VFD REPLACEMENT PF70 & SPARE 753 | E10802758 | MLWMPCTRL | 1080005 | 2024-09-07 | 675.45 | 0 | 666.02 | 9.43
MLP | COMP | MLP U0: FUEL OIL TANK LEVEL INDICATION AND CABLE/CONDUIT REPLACEMENT | E10773078 | MLWMPCTRL | 1080005 | 2025-03-03 | 18448.25 | 3440.94 | 15000.11 | 7.2
MLP | CLOSE | MLU0 Clearwater Pond Upper Outfall Line Replacement | E10645214 | MLWMPDRNG | 1080005 | 2023-11-10 | 13615.77 | 4480.28 | 9135.49 | 0
MLP | CLOSE | MLU0 REPLACE ECRANE SWING MOTORS | E10539621 | MLWMPECRN | 1080005 | 2022-09-29 | 3156.48 | 0 | 3000 | 156.48
MLP | CLOSE | MLU0 E-CRANE BARGE HAUL MOTOR REPLACEMENT | E10539577 | MLWMPECRN | 1080005 | 2022-09-29 | 4827.72 | 73.92 | 4598.92 | 154.88
MLP | COMP | MLP U0: REPLACE HEATERS IN TRACTOR SHED | E10840336 | MLWMPHEAT | 1080005 | 2025-03-04 | 4170.85 | 241.13 | 3929.72 | 0
MLP | CLOSE | MLU0 MAC950F HEATER RETIREMENT | E10695365 | MLWMPHEAT | 1080005 | 2023-12-18
MLP | CLOSE | MLU0 REMOVE AND INSTALL 480V HEATERS IN SILO B | E10574851 | MLWMPHEAT | 1080005 | 2023-11-29
MLP | CLOSE | MLU0 PURCHASE & INSTALL HEATERS IN DTE BUILDING | E10557530 | MLWMPHEAT | 1080005 | 2023-01-05 | 805.34 | 0 | 805.32 | 0.02
MLP | CLOSE | MLP U0: CAT D10T RJG00726 FINAL DRIVE | E10840395 | MLWMPHEVY | 1080005 | 2024-11-20
MLP | COMP | MLP U0: HS COAL TUNNERL CABLE TRAY EXP JOINT | E10868680 | MLWMPHSTF | 1080005 | 2025-01-28 | 291.81 | 22.4 | 269.41 | 0
MLP | CLOSE | MLP U0: REPLACE MSA GAS MONITORS IN HS COAL TUNNEL | E10867492 | MLWMPHSTF | 1080005 | 2025-02-01 | 10390.12 | 172.57 | 10217.55 | 0
MLP | COMP | MLP U0: Replace HRC-1 Conveyor Pulleys (Total 4) | E10861471 | MLWMPHSTF | 1080005 | 2025-02-14 | 12155.04 | 0 | 12154.97 | 0.07
MLP | CLOSE | MLP U0: HRC-1 CONVEYOR BELT REPLACEMENT | E10861003 | MLWMPHSTF | 1080005 | 2025-03-05 | 9652.11 | 0 | 9652.06 | 0.05
MLP | COMP | MLP U0: HSC3 MOTOR REPLACEMENT | E10866024 | MLWMPMOTR | 1080005 | 2025-05-13 | 799.42 | 0 | 791.86 | 7.56
MLP | CLOSE | MLP U2: HVF-2 MOTOR REPLACEMENT | E10814247 | MLWMPMOTR | 1080005 | 2024-10-25 | 16442.66 | 13600 | 2842.43 | 0.23
MLP | COMP | MLP U0: Replace Shaft, Sprockets, Bearings and Wheels on Barge Unloader Bucket Drive | E10844462 | MLWMPOTHR | 1080005 | 2025-05-13 | 49441.62 | 27322.18 | 22119.28 | 0.16
MLP | CLOSE | MLP U0: DTE BLDG AIR COMP CONTROL SCREEN REPLACEMENT | E10835420 | MLWMPOTHR | 1080005 | 2025-01-16 | 2230.01 | 0 | 2230.01 | 0
MLP | CLOSE | MLP U0 DFA SILO B FLUIDIZING CLOTH REPLACEMENT | E10804050 | MLWMPOTHR | 1080005 | 2024-10-15 | 1387.85 | 61.88 | 1325.96 | 0.01
MLP | CLOSE | MLP U0: REPLACE DFA SCALE MOXA TOUCH SCREEN DISPLAY | E10746661 | MLWMPOTHR | 1080005 | 2024-03-01 | 956.12 | 0 | 956.11 | 0.01
MLP | COMP | MLP U1: SERV WTR PMP A SWING CK VLV REPLACE | E10914135 | MLWMPPUMP | 1080005 | 2025-06-10 | 331.52 | 0 | 326.41 | 5.11
MLP | COMP | MLP U0: LEACHATE HIGH FLOW SUMP PUMP REPLACE | E10884193 | MLWMPPUMP | 1080005 | 2025-05-08 | 3485.87 | 0 | 3452.34 | 33.53
MLP | CLOSE | MLP U0: 3B SUMP PUMP REPLACEMENT | E10850670 | MLWMPPUMP | 1080005 | 2025-01-08 | 1815.83 | 0 | 1785.58 | 30.25
MLP | CLOSE | MLU0 Replace Leachate High Flow Sump Pump | E10775686 | MLWMPPUMP | 1080005 | 2024-07-16 | 3728.3 | 0 | 3658.1 | 70.2
MLP | CLOSE | MLU0 Remove and replace 3B Sump Pump | E10633400 | MLWMPPUMP | 1080005 | 2024-02-20 | 1368.58 | 0 | 1368.58 | 0
MLP | CLOSE | MLU0 Remove and replace 3C West Sump Pump | E10633391 | MLWMPPUMP | 1080005 | 2024-02-28 | 3108.58 | 0 | 3108.58 | 0
MLP | CLOSE | MLU0 Remove and replace 3C East sump pump | E10631584 | MLWMPPUMP | 1080005 | 2024-02-08 | 2422.53 | 0 | 2416.35 | 6.18
MLP | CLOSE | MLU0 SILO B FLUIDIZING AIR BLOWER A REPLACEMENT | E10614280 | MLWMPPUMP | 1080005 | 2023-04-27 | 781.25 | 0 | 734.83 | 46.42
MLP | CLOSE | MLU0 4E & 4W TUNNEL SUMP PUMP REPLACEMENT | E10539501 | MLWMPPUMP | 1080005 | 2023-01-31 | 4962.77 | 0 | 4741.96 | 220.81
MLP | CLOSE | MLU0 REPLACE LEACHATE POND PUMP | E10539497 | MLWMPPUMP | 1080005 | 2022-09-29
MLP | INPRG | MLP U0: REMOVE COAL TROL TANK - NORTH YARD | E10906574 | MLWMPREMV | 1080005 |  | 12639.84 | 375.68 | 12263.96 | 0.2
MLP | INPRG | MLP U0: RETIRE 1999 CATERPILLAR 834B ARTICULATING RUBBER TIRED WHEEL DOZER | E10830121 | MLWMPREMV | 1080005
MLP | CLOSE | MLP U0: RETIRE 2007 KOMATSU D3745A-5E0 CRAWLER TRACTOR | E10830116 | MLWMPREMV | 1080005 | 2025-02-24 | 11234.04 | 1078.65 | 10154.99 | 0.4
MLP | CLOSE | MLU0 DEMO/REMOVE CHEMICAL ADDITIVE SYSTEM IN SILO B | E10563602 | MLWMPREMV | 1080005 | 2022-12-16 | 9847.61 | 176.34 | 9603.38 | 67.89
MLP | COMP | MLP U0: BAG HOUSE/COAL DUST COLLECTOR REMOVAL | E10842296 | MLWMPROTO | 1080005 | 2024-12-19 | 171227.04 | 68322.68 | 102827.42 | 76.94
MLP | COMP | MLP U1: ROTOCLONES REPLACEMENT | E10840408 | MLWMPROTO | 1080005 | 2025-05-28 | 35646.56 | 346.19 | 35300.18 | 0.19
MLP | COMP | MLP U0: LABOR TO INSTALL / REMOVE BC-20 GEARBOX | E10907143 | MLWMPVALV | 1080005 | 2025-05-27 | 3066.3 | 100 | 2966.29 | 0.01
MLP | COMP | MLP U0: LABOR TO INSTALL / REMOVE BC-19 GEARBOX | E10907142 | MLWMPVALV | 1080005 | 2025-05-16 | 3954.05 | 0 | 3954.02 | 0.03
MLP | CLOSE | MLU0 REPLACE Silo Side Service Water Pump A Check Valve | E10786757 | MLWMPVALV | 1080005 | 2024-06-21 | 2894.57 | 0 | 2850 | 44.57
MLP | CLOSE | MLP UO: BF-1 GEARBOX REPLACEMENT | E10720305 | MLWMPVALV | 1080005 | 2024-01-05 | 2416.12 | 0 | 2384.11 | 32.01
MLP | CLOSE | MLU0 REBUILD TWO 514C GEARBOXES ON WM ROBINSON | E10642663 | MLWMPVALV | 1080005 | 2023-12-13 | 4878.39 | 0 | 4816.75 | 61.64
MLP | CLOSE | MLU0 DFA SILOS BACK PRESSURE REGULATING VLV REPLACE | E10539534 | MLWMPVALV | 1080005 | 2022-11-15 | 0 | 0 | 0 | 0
MLP | COMP | MLP U0: CFB 1ST FLOOR WATER HEATER REPLACEMENT | E10867127 | MLWNPBLDG | 1080005 | 2025-03-27 | 1683 | 0 | 1683 | 0
MLP | COMP | MLP U0: SERVICE BLDG 2ND FLOOR OFFICES | E10865858 | MLWNPBLDG | 1080005 | 2025-03-07 | 8168.02 | 845.07 | 7318.22 | 4.73
MLP | CLOSE | RETIRE GSU TRANSFORMER S/N 6213486 - SEE NOTES | E10846966 | MLWNPBLDG | 1080005 | 2024-12-19 | -139615.32 | 0 | 6154.61 | -145769.93
MLP | CLOSE | MLP U0: PLANT PARKING LOT PAVING | E10799122 | MLWNPBLDG | 1080005 | 2024-09-05 | 69964.26 | 0 | 69963.72 | 0.54
MLP | CLOSE | MLP U0: REMOVE CHLORINE HOUSE SERVICE WATER LINE | E10785786 | MLWNPBLDG | 1080005 | 2024-07-24 | 19209.72 | 12529.73 | 6640.11 | 39.88
MLP | CLOSE | MLP - U0: ADDITIONAL INSTALL/RETIREMENT | E10752190 | MLWNPBLDG | 1080005 | 2024-09-30
MLP | CLOSE | MLP U0: CABLE PULL FOR STATOR HEATERS WH7 | E10750771 | MLWNPBLDG | 1080005 | 2024-04-04 | 3677.52 | 181.4 | 3496.11 | 0.01
MLP | CLOSE | MLP U0: OLD STACK MAN DOOR REPLACEMENT | E10734260 | MLWNPBLDG | 1080005 | 2024-06-21 | 1366.72 | 30.22 | 1336.5 | 0
MLP | CLOSE | MLU2 Replace Pulverizer Access Platforms | E10719387 | MLWNPBLDG | 1080005 | 2024-02-15 | 0 | 0 | 0 | 0
MLP | CLOSE | MLU1 Replace Pulverizer Access Platforms | E10719385 | MLWNPBLDG | 1080005 | 2024-01-05 | 781.82 | 0 | 781.82 | 0
MLP | CLOSE | MLU0 REPLACE WATER SOFTENER IN HRLY SHOWERHOUSE | E10646625 | MLWNPBLDG | 1080005 | 2023-08-10 | 3976.81 | 0 | 3976.8 | 0.01
MLP | CLOSE | MLU1 WASTE WATER SUMP PUMP MONORAIL | E10635551 | MLWNPBLDG | 1080005 | 2024-05-31
MLP | CLOSE | MLU0 N CY RUN OFF POND - PLATFORM FOR LAB SAMPLES | E10611100 | MLWNPBLDG | 1080005 | 2023-07-14
MLP | CLOSE | MLU2 ALIMANK RAMP AND PLATFORM REPLACE | E10539584 | MLWNPBLDG | 1080005 | 2023-01-31 | 11446.26 | 0 | 11446.25 | 0.01
MLP | CLOSE | MLU0 CHLORINE BUILDING ROOF AND SIDING | E10539531 | MLWNPBLDG | 1080005 | 2022-09-30 | 25242.44 | 203.61 | 24955.94 | 82.89
MLP | CLOSE | MLU0 PURCH 2 CONNEX TRAILERS FOR OPER BRKRMS | E10539498 | MLWNPBLDG | 1080005 | 2022-11-05 | 15806.91 | 221.32 | 15585.59 | 0
MLP | CLOSE | MLU2 REPLACE PULVERIZER ACCESS PLATFORMS | E10539491 | MLWNPBLDG | 1080005 | 2023-03-07
MLP | CLOSE | MLU1 REPLACE PULVERIZER ACCESS PLATFORMS | E10539490 | MLWNPBLDG | 1080005 | 2023-03-07 | 2525.51 | 0 | 2525.48 | 0.03
MLP | INPRG | MLP U2: FIRE HEADER & VALVE REPLACEMENT | E10910686 | MLWNPFIRE | 1080005
MLP | CLOSE | MLU0 DFA Silo B Bin Vent Filter Bag Replacement | E10641321 | MLWNPINSL | 1080005 | 2023-11-10 | 9686.43 | 0 | 9686.43 | 0
MLP | INPRG | ML HAUL ROAD RELOCATION PRELIMINARY ENGINEERING | E10539448 | MLWNPROAD | 1080005 |  | -17.85 | 0 | -17.85 | 0
MLP | CLOSE | MLP U0: Coping power generator battery replacement | E10840846 | MLWNPTOOL | 1080005 | 2024-12-19 | 499.63 | 90 | 409.63 | 0
MLP | CLOSE | MLP U0: FGD JLG BATTERY REPLACMENT | E10840845 | MLWNPTOOL | 1080005 | 2025-01-08 | 333.68 | 112.5 | 221.18 | 0
MLP | CLOSE | MLP CAP SPARE RETIREMENTS/WRITE OFF | E10539635 | MLWNPTOOL | 1080005 | 2024-12-09 | 58.52 | 0 | 58.52 | 0
MLP | CLOSE | MLP CP WO MATERIAL CORRECTIONS | E10539634 | MLWNPTOOL | 1080005 | 2024-09-30 | -172676.35 | -172676.35 | 0 | 0
MLP | CLOSE | MLU0 ELECTRIC STACKER BATTERY REPLACEMENT | E10539528 | MLWNPTOOL | 1080005 | 2022-11-13 | 271.66 | 0 | 268.49 | 3.17
MLP | CLOSE | MLU0 HAWKER FORK TRUCK BATTERY REPLACEMENT | E10539493 | MLWNPTOOL | 1080005 | 2022-11-07
MLP | CLOSE | MLP U0: MAINT STORAGE BLDG HEATER REPLACEMENT | E10870486 | MLWNPWINT | 1080005 | 2025-03-04 | 635.66 | 0 | 622.56 | 13.1
MLP | CLOSE | MLP U0: REPLACE DOORS AT DELUGE HOUSES & TRANSFER STATION | E10869634 | MLWNPWINT | 1080005 | 2025-03-18 | 1857.48 | 38.69 | 1818.78 | 0.01
MLP | CLOSE | MLP U2: ID FAN WINTERIZATION HEATERS | E10842345 | MLWNPWINT | 1080005 | 2024-12-09 | 1356.62 | 0 | 1356.61 | 0.01
MLP | CLOSE | MLP U1: ID FAN WINTERIZATION HEATERS | E10842342 | MLWNPWINT | 1080005 | 2024-12-09 | 1356.61 | 0 | 1356.6 | 0.01
MLP | CLOSE | MLP - U2 CONTROL AIR DEWPOINT MONITOR & WIRE RUN | E10702189 | MLWNPWINT | 1080005 | 2023-11-20 | 2943.82 | 0 | 2943.82 | 0
MLP | CLOSE | MLP - U1 CONTROL AIR DEWPOINT MONITOR & WIRE RUN | E10702188 | MLWNPWINT | 1080005 | 2023-12-01 | 3934.7 | 0 | 3934.7 | 0
MLP | CLOSE | MLP U1: #12 ID FAN REG END HUB W/ NEW SHELL & INTERNALS | E10757760 | MLWOPFGDP | 1080005 | 2024-06-07 | 77804.73 | 1690 | 75693.16 | 421.57
MLP | CLOSE | MLP U0: RECLAIM TANK B - INTERNAL COATING | E10755142 | MLWOPFGDP | 1080005 | 2024-06-07 | 221564.28 | 74984 | 144655.79 | 1924.49
MLP | CLOSE | MLP U2: #21 ID FAN HYDRAULIC CYLINDER | E10755119 | MLWOPFGDP | 1080005 | 2024-05-17 | 28440.17 | 740 | 27693.46 | 6.71
MLP | CLOSE | MLP - U2: DSI DIVERTER GATE REPLACEMENT | E10755063 | MLWOPFGDP | 1080005 | 2024-06-06 | 5372.31 | 1059 | 4313.28 | 0.03
MLP | CLOSE | MLP -U1: DSI DIVERTER GATE REPLACEMENT | E10755046 | MLWOPFGDP | 1080005 | 2024-05-23 | 8732.24 | 138.1 | 8594.04 | 0.1
MLP | CLOSE | MLP 2F ABSORBER AGITATOR GEARBOX REPLACEMENT | E10752121 | MLWOPFGDP | 1080005 | 2024-05-17
MLP | CLOSE | MLP U1: #12 ID FAN HYDRAULIC CYLINDER (CSP) | E10749162 | MLWOPFGDP | 1080005 | 2024-06-03 | 38725.9 | 153.81 | 38567.45 | 4.64
MLP | CLOSE | MLP - U0: PRIMARY CLARIFIER SLUDGE PUMP #3 | E10710362 | MLWOPFGDP | 1080005 | 2023-11-15 | -9921.03 | -11326 | 1388.67 | 16.3
MLP | CLOSE | MLU0 FGD SERVICE WATER PUMP A | E10705652 | MLWOPFGDP | 1080005 | 2023-11-03 | 1416.66 | 0 | 1395.47 | 21.19
MLP | CLOSE | MLU2 #22 ID FAN HYDRAULIC CYLINDER | E10683308 | MLWOPFGDP | 1080005 | 2023-11-05 | 69548.43 | 3065.36 | 66482.97 | 0.1
MLP | CLOSE | MLU0 RECLAIM TANK A INTERNAL COATING | E10648184 | MLWOPFGDP | 1080005 | 2023-12-07 | 291138.94 | 54358.44 | 236780.19 | 0.31
MLP | CLOSE | MLU0 OXIDATION AIR BLOWER DSCHGE VLV ZOAS 8001 | E10615470 | MLWOPFGDP | 1080005 | 2023-05-14 | 5474.74 | 0 | 5474.74 | 0
MLP | CLOSE | MLU2 PLANT AIR DRYER INSTALLATION | E10539538 | MLWOPFGDP | 1080005 | 2023-06-16 | 15212.55 | 1109.3 | 13758.41 | 344.84
MLP | CLOSE | MLP U2: 21 PENTHOUSE SEAL AIR FAN EXP JOINT | E10802595 | MLWOPNONP | 1080005 | 2024-10-02 | 3447.66 | 0 | 3447.38 | 0.28
MLP | CLOSE | MLP U2: CIRC WATER & RIVER WATER SUPPLY HSO | E10777070 | MLWOPNONP | 1080005 | 2025-02-10 | 3856.14 | 543.15 | 3260.49 | 52.5
MLP | CLOSE | MLU2 NERC Protective Relay Replacement | E10775734 | MLWOPNONP | 1080005 | 2024-07-03
MLP | CLOSE | MLU1 7B heater safety valve replacement | E10764279 | MLWOPNONP | 1080005 | 2024-05-18 | 1938.09 | 0 | 1928.88 | 9.21
MLP | CLOSE | MLU1 7A heater safety valve replacement | E10764074 | MLWOPNONP | 1080005 | 2024-05-18 | 1290.06 | 0 | 1290.02 | 0.04
MLP | CLOSE | MLP U2: #22 RAW COAL CHUTE AND SILO GATE | E10762667 | MLWOPNONP | 1080005 | 2024-06-05 | 3759.64 | 0 | 3759.6 | 0.04
MLP | CLOSE | MLP U1: WASTE WATER SUMP PUMP REPLACE | E10754721 | MLWOPNONP | 1080005 | 2024-05-24 | 6368.84 | 0 | 6298.7 | 70.14
MLP | CLOSE | MLP U2: BRV-5 POWER RELIEF VALVE REPLACE | E10746723 | MLWOPNONP | 1080005 | 2024-10-14 | 23754.53 | 9504.98 | 14248.78 | 0.77
MLP | CLOSE | MLP U1: BRV-5 POWER RELIEF VALVE REPLACE | E10746719 | MLWOPNONP | 1080005 | 2024-09-15 | 17510.15 | 3241.6 | 14267.47 | 1.08
MLP | CLOSE | MLU1 #8 CONVEYOR GEARBOX REPLACEMENT | E10711973 | MLWOPNONP | 1080005 | 2023-11-27 | 2014.23 | 0 | 1990.86 | 23.37
MLP | CLOSE | MLP - U0 AUX BOILER TIE HEADER BYPASS VALVE | E10708155 | MLWOPNONP | 1080005 | 2023-11-08 | 255.06 | 0 | 251.87 | 3.19
MLP | CLOSE | MLP - U2: PRECIP BOX 4 HOPPER 1-5 | E10706078 | MLWOPNONP | 1080005 | 2023-11-09
MLP | CLOSE | MLP - U2 PRECIP BOX 4 HOPPER 1-4 VALVE REPLACE | E10705649 | MLWOPNONP | 1080005 | 2023-11-02 | 580.26 | 0 | 573.12 | 7.14
MLP | CLOSE | MLU1 BOX 2 ROW 2 HOPPER 1 GATE VALVE REPLACEMENT | E10695671 | MLWOPNONP | 1080005 | 2023-11-09 | 1013.85 | 0 | 996.12 | 17.73
MLP | CLOSE | MLU2 AIR COMPRESSOR HSO - REPLACEMENT | E10695573 | MLWOPNONP | 1080005 | 2023-10-13 | 764.6 | 0 | 750.48 | 14.12
MLP | CLOSE | MLU1 BOX 1 ROW 1 HOPPER 2 GATE VALVE REPLACEMENT | E10695550 | MLWOPNONP | 1080005 | 2023-10-06 | 704.34 | 0 | 691.29 | 13.05
MLP | CLOSE | MLU2 BOX 3 ROW 1 HOPPER 1 RECEIVING GATE | E10677489 | MLWOPNONP | 1080005 | 2023-10-30
MLP | CLOSE | MLU1 #50 SAFETY VALVE REPLACEMENT (CSP) | E10648483 | MLWOPNONP | 1080005 | 2023-11-07 | 18569.2 | 1036.07 | 17533.13 | 0
MLP | CLOSE | MLU2 BOX 4 TRANSFER STATION A & B BAG REPLACEMENT 1 SET EA | E10635698 | MLWOPNONP | 1080005 | 2023-10-11 | 2212.53 | 0 | 2171.29 | 41.24
MLP | CLOSE | MLU2 26F BURNER SLIP JOINT REPLACEMENT | E10635597 | MLWOPNONP | 1080005 | 2023-11-03 | -4427.69 | -9320 | 4892.31 | 0
MLP | CLOSE | MLU2 RRV-01 ACTUATOR REPLACEMENT | E10635257 | MLWOPNONP | 1080005 | 2023-06-20
MLP | CLOSE | MLU2 - 24 & 25 COAL SILO RAW COAL CHUTE REPLACEMENT | E10630134 | MLWOPNONP | 1080005 | 2023-11-19 | 9051.41 | 0 | 9051.41 | 0
MLP | CLOSE | MLU1 12, 14, & 15 COAL SILO RAW COAL CHUTE REPLACE | E10630129 | MLWOPNONP | 1080005 | 2023-11-30 | 19476.85 | 0 | 19471.22 | 5.63
MLP | CLOSE | MLU2 Replace Boiler Feed Pump Rotating Element (CSP) | E10619554 | MLWOPNONP | 1080005 | 2023-04-05 | 58170.32 | 0 | 25684.35 | 32485.97
MLP | CLOSE | MLU2 BFP ROTATING ELEMENT REBUILD | E10619232 | MLWOPNONP | 1080005 | 2023-12-01 | 24697.17 | 0 | 17229.13 | 7468.04
MLP | CLOSE | MLU2 UPGRADE ION METERS TO ION 9000 | E10610217 | MLWOPNONP | 1080005 | 2023-11-02 | 2802.52 | 64.2 | 2738.32 | 0
MLP | CLOSE | MLU1 UPGRADE ION METERS TO ION 9000 | E10610215 | MLWOPNONP | 1080005 | 2023-11-02 | 4776.72 | 149.7 | 4627.02 | 0
MLP | CLOSE | MLU1 PURCHASE #58 SAFETY VALVE | E10601145 | MLWOPNONP | 1080005 | 2023-11-22 | 5162.25 | 0 | 5127.52 | 34.73
MLP | CLOSE | MLU1 PURCHASE BRV-5 VALVES | E10601144 | MLWOPNONP | 1080005 | 2023-12-04 | 20306.32 | 2247.3 | 18059.02 | 0
MLP | CLOSE | MLU2 22 AIR HEATER GEARBOX REPLACE | E10567475 | MLWOPNONP | 1080005 | 2023-06-06 | 14923.39 | 75 | 14848.39 | 0
MLP | CLOSE | MLU2 CORESENSE M10 REPLACEMENT | E10539602 | MLWOPNONP | 1080005 | 2022-11-30 | 2557.46 | 0 | 2135.19 | 422.27
MLP | CLOSE | MLU2 RAW COAL CHUTE REPLACEMENT | E10539596 | MLWOPNONP | 1080005 | 2022-12-22
MLP | CLOSE | MLU1 RAW COAL CHUTE REPLACEMENT | E10539593 | MLWOPNONP | 1080005 | 2022-12-22 | 959.76 | 959.76 | 0 | 0
MLP | CLOSE | MLU2 Install Turbine Room Lights | E10539559 | MLWOPNONP | 1080005 | 2022-09-30 | 25536.46 | 0 | 25536.18 | 0.28
MLP | CLOSE | MLU1 PHASE 3 CORESENSE M10 MONITOR | E10539542 | MLWOPNONP | 1080005 | 2022-11-30
MLP | CLOSE | MLU1 PRECIP PWER FEED | E10539539 | MLWOPNONP | 1080005 | 2022-12-01 | 7480.8 | 910.3 | 6570.5 | 0
MLP | CLOSE | MLU122 HIGH ENERGY PIPING INSPECTION | E10539536 | MLWOPNONP | 1080005 | 2022-11-11 | 396846.92 | 30802.34 | 365988.83 | 55.75
MLP | CLOSE | MLU2 CIRC WATER RELAY UPGRADE | E10539504 | MLWOPNONP | 1080005 | 2023-11-22 | 2939.26 | 83.4 | 2855.86 | 0
MLP | CLOSE | MLP U2: INFRA-VIEW STARTUP PROBE REPLACEMENT | E10794205 | MLWOPSOOT | 1080005 | 2024-09-12 | 3898.44 | 0 | 0 | 3898.44
MLP | INSERV | ML0 CCR Compliance | E10567546 | MLWPC0ELG | 1080005 | 2024-09-10 | 918880.7 | 999 | 546499.39 | 371382.31
MLP | INSERV | ML0 CCR Compliance | E10539454 | MLWPC0ELG | 1080005 | 2024-09-10 | 25.6 | 0 | 0 | 25.6
MLP | INSERV | ML ELG Cmplianc Bottom Ash Pond | E10539452 | MLWPC0ELG | 1080005 | 2023-11-18 | 2216739.58 | 11132.9 | 1769666 | 435940.68
MLP | CLOSE | ML2 Hydrated Lime Conversion Project | E10539450 | MLWPC0LIM | 1080005 | 2022-12-14 | 372627.18 | 1300 | 342779.45 | 28547.73
MLP | CLOSE | ML1 Hydrated Lime Conversion Prj | E10539449 | MLWPC0LIM | 1080005 | 2023-05-30 | 324429.51 | 13166.35 | 292869.38 | 18393.78
MLP | CLOSE | ML1 Catalyst Replacement | E10539460 | MLWPC1CL4 | 1080005 | 2021-12-15 | 118968.13 | 0 | 90282.59 | 28685.54
MLP | CLOSE | ML2 E Cooling Tower Components | E10539477 | MLWPC2CTC | 1080005 | 2022-12-16 | 1227960.79 | 0 | 1153905.01 | 74055.78
MLP | CLOSE | ML2 ESP PURGE AIR HEATER | E10539465 | MLWPC2ESP | 1080005 | 2022-12-17 | 1192178.01 | -5087 | 1121629.79 | 75635.22
MLP | COMP | ML U1 Cooling Twr Canopy Rep | E10745400 | MLWPCT1BP | 1080005 | 2024-05-31 | 153277.85 | 18915.31 | 133819 | 543.54
MLP | CLOSE | ML U1 Air Heater Basket | E10539599 | MLWSC1AHB | 1080005 | 2023-12-30 | 1558761.75 | 77654.32 | 1395122.8 | 85984.63
MLP | CLOSE | ML2 AIR HEATER BASKET REPLACEMENT | E10539464 | MLWSC2AHB | 1080005 | 2022-12-13 | 69232.5 | 66924.84 | 2307.6 | 0.06
MLP | CLOSE | MLP U2: ASH PIT SUMP LEVEL CONTROL UPGRADE | E10878775 | MLWSPASHL | 1080005 | 2025-03-05 | 2420.06 | 0 | 2370.45 | 49.61
MLP | CLOSE | MLU2 ASKERAL TANK FOUNDATION & MISC. 6" PIPING REMOVAL | E10539610 | MLWSPASHL | 1080005 | 2023-06-06 | 42565.42 | 15178.81 | 26752.38 | 634.23
MLP | CLOSE | MLU1 REMOVE ASKERAL TANK FOUNDATION | E10539609 | MLWSPASHL | 1080005 | 2022-10-01 | 14293.65 | 791.8 | 13501.85 | 0
MLP | CLOSE | MLU2 HYDROVEYOR PIPING REMOVAL | E10539487 | MLWSPASHL | 1080005 | 2022-09-16 | 325147.75 | 22172.28 | 302924.26 | 51.21
MLP | CLOSE | MLU1 HYDROVEYOR PIPING REMOVAL | E10539481 | MLWSPASHL | 1080005 | 2022-12-08 | 430832.17 | 38580.91 | 392084.45 | 166.81
MLP | CLOSE | MLU2 PRECIP NEUNDORFER POS REPLACEMENT | E10539474 | MLWSPASHL | 1080005 | 2022-10-01
MLP | CLOSE | MLU2 22A BURNER SLIP JOINT REPLACEMENT | E10539615 | MLWSPBRNE | 1080005 | 2022-11-20 | 10125.67 | 10125.67 | 0 | 0
MLP | COMP | MLP U1: #12 COAL SILO GATE REPLACEMENT | E10840522 | MLWSPBRNN | 1080005 | 2025-05-01 | 2387.91 | 0 | 2387.89 | 0.02
MLP | COMP | MLP U1: PULV CAPACITY DAMPER REPLACEMENT | E10840385 | MLWSPBRNN | 1080005 | 2025-05-07 | 10742.99 | 0 | 10742.94 | 0.05
MLP | COMP | MLP U1: PULV PA DAMPER REPLACEMENT | E10840380 | MLWSPBRNN | 1080005 | 2025-05-07 | 22128.77 | 469.26 | 21659.44 | 0.07
MLP | COMP | MLP U1: 48 OIL LIGHTER ASSEMBLIES | E10840298 | MLWSPBRNN | 1080005 | 2025-05-13 | 37264.18 | 0 | 37224.41 | 39.77
MLP | COMP | MLP U1: #12 RAW COAL PIPE REPLACEMENT | E10840297 | MLWSPBRNN | 1080005 | 2025-05-01 | 2804.77 | 0 | 2804.75 | 0.02
MLP | COMP | MLP U1 & U2: SLIP JOINT REPLACEMENTS | E10840191 | MLWSPBRNN | 1080005 | 2025-05-03 | 23584.55 | 1333.91 | 22250.54 | 0.1
MLP | CLOSE | MLP U2: 26F BURNER SLIP JOINT REPLACEMENT | E10786930 | MLWSPBRNN | 1080005 | 2024-10-09
MLP | CLOSE | MLP U2: 22E BURNER SLIP JOINT REPLACEMENT | E10766902 | MLWSPBRNN | 1080005 | 2024-05-08 | 7109.52 | 740 | 6369.44 | 0.08
MLP | CLOSE | MLP U1: 16A, 16B, 16C BURNER SLIP JOINT REPLACEMENT | E10754728 | MLWSPBRNN | 1080005 | 2024-06-05 | 18192.84 | 1718.47 | 16474.1 | 0.27
MLP | CLOSE | MLP U2: 26A, 26B, 26F BURNER SLIP JOINT REPLACEMENT | E10754723 | MLWSPBRNN | 1080005 | 2024-10-13 | 70622.44 | 11675.01 | 58936.64 | 10.79
MLP | CLOSE | MLP U1: #16 COAL SILO GATE REPLACEMENT | E10754717 | MLWSPBRNN | 1080005 | 2024-06-05 | 5240.22 | 0 | 5240.16 | 0.06
MLP | CLOSE | MLP U1 REPLACE 12 BURNER OIL LIGHTER ASSEMBLIES | E10752248 | MLWSPBRNN | 1080005 | 2024-06-05 | 10022.41 | 76.54 | 9945.76 | 0.11
MLP | CLOSE | MLP U2: REPLACE 13 BURNER NOZZLES | E10752098 | MLWSPBRNN | 1080005 | 2024-10-01 | 155059.62 | 21415.51 | 133579.8 | 64.31
MLP | CLOSE | MLU1 - #16 COAL FEEDER RAW COAL CHUTE | E10751276 | MLWSPBRNN | 1080005 | 2024-06-05 | 1329.72 | 0 | 1329.68 | 0.04
MLP | CLOSE | MLU2 - #25 COAL FEEDER RAW COAL CHUTE | E10751271 | MLWSPBRNN | 1080005 | 2024-06-05 | 2159.77 | 0 | 2159.75 | 0.02
MLP | CLOSE | MLU1 LABOR TO I/R 24 BURNER NOZZLES | E10677431 | MLWSPBRNN | 1080005 | 2023-11-24 | 236758.09 | 2033.87 | 234661.88 | 62.34
MLP | CLOSE | MLU1 PURCHASE 24 BURNER NOZZLES | E10573704 | MLWSPBRNN | 1080005 | 2023-08-08
MLP | CLOSE | MLU1 11F BURNER NOZZLE TIP & THERMOCOUPLE REPLACEMENT | E10555517 | MLWSPBRNN | 1080005 | 2022-11-29 | 1569.94 | 0 | 1569.94 | 0
MLP | CLOSE | MLU1 PLANT AIR DRYER INSTALLATION | E10539537 | MLWSPBRNN | 1080005 | 2023-06-16 | 9453.29 | 474.34 | 8854.77 | 124.18
MLP | CLOSE | MLU2 BURNER NOZZLE PURCHASE | E10539485 | MLWSPBRNN | 1080005 | 2022-12-21 | 129516.82 | 9459.77 | 119986.08 | 70.97
MLP | COMP | MLP U1: SGC DEWATERING & COLLECTION CHAIN REPLACEMENT | E10840742 | MLWSPCCHN | 1080005 | 2025-05-13 | 44116.05 | 0 | 44100.05 | 16
MLP | CLOSE | MLP U2: BOX 3 TRANSFER STATION C FILTER BAG REPLACE | E10814246 | MLWSPDFAF | 1080005 | 2024-09-25 | 2070.67 | 684 | 1370.53 | 16.14
MLP | CLOSE | MLP U2: BOX 3 TRANSFER STATION D FILTER BAG REPLACE | E10814245 | MLWSPDFAF | 1080005 | 2024-09-25 | 1021.92 | 0 | 1010.08 | 11.84
MLP | CLOSE | MLU2 3D DFA FILTER BAG REPLACEMENT | E10539608 | MLWSPDFAF | 1080005 | 2022-11-05 | 99.09 | 0 | 98.62 | 0.47
MLP | CLOSE | MLU2 3C DFA FILTER BAG REPLACEMENT | E10539607 | MLWSPDFAF | 1080005 | 2022-09-23
MLP | CLOSE | MLU1 2D DFA FILTER BAG REPLACEMENT | E10539606 | MLWSPDFAF | 1080005 | 2022-10-18 | 1199.36 | 0 | 1174.95 | 24.41
MLP | CLOSE | MLU1 DFA FILTER BAG 1B REPLACEMENT | E10539605 | MLWSPDFAF | 1080005 | 2022-10-17 | 1412.25 | 0 | 1383.45 | 28.8
MLP | CLOSE | MLU1 PENTHOUSE CASING INSULATION | E10584607 | MLWSPDUCT | 1080005 | 2023-02-15 | 12545.92 | 0 | 12545.91 | 0.01
MLP | COMP | MLP U1: TWO #16 PULV EXP JOINTS | E10843211 | MLWSPEJNT | 1080005 | 2025-05-13 | 1598.2 | 0 | 1598.2 | 0
MLP | CLOSE | MLP U2: MECHANICAL EXHAUSTER 1 EXP JOINT | E10804072 | MLWSPEJNT | 1080005 | 2024-09-25
MLP | CLOSE | MLP - U1 #12 ID FAN INLET HORIZONATAL EXP JOINT | E10690975 | MLWSPEJNT | 1080005 | 2023-11-04 | 11269.04 | 0 | 11269.04 | 0
MLP | CLOSE | MLU1 #12A BURNER SLIP JOINT | E10649003 | MLWSPEJNT | 1080005 | 2023-07-20 | 4750.27 | 110.25 | 4640.02 | 0
MLP | CLOSE | MLU1 FGX-72009 EJ & FRAME DOWNSTREAM OF ID FANS | E10648181 | MLWSPEJNT | 1080005 | 2024-10-14 | 117099.67 | 3043.15 | 114050.65 | 5.87
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ1 JOINT & FRAME ON 1A | E10648179 | MLWSPEJNT | 1080005 | 2023-11-11 | 253670.97 | 9626.14 | 244044.74 | 0.09
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ2 JOINT & FRAME ON 1B | E10648178 | MLWSPEJNT | 1080005 | 2023-11-11 | 545735.82 | 4590.02 | 541145.75 | 0.05
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ3 JOINT & FRAME ON 2A | E10648177 | MLWSPEJNT | 1080005 | 2023-11-11 | 224029.17 | 12862.54 | 211166.59 | 0.04
MLP | CLOSE | MLU1 PRECIP INLET NOZZLE EJ4 JOINT & FRAME ON 2B | E10648174 | MLWSPEJNT | 1080005 | 2023-11-11 | 667449.81 | 109285.84 | 558163.93 | 0.04
MLP | CLOSE | ML U2A AR PUMP DISCHARGE EXP JOINT REPLACE | E10552765 | MLWSPEJNT | 1080005 | 2022-12-07
MLP | CLOSE | MLU1 AR PUMP DISCHARGE EXP JOINT REPLACE | E10552039 | MLWSPEJNT | 1080005 | 2022-12-01
MLP | CLOSE | MLU0 AUX BOILER FD FAN EXPANSION JOINT - EJ1 | E10539636 | MLWSPEJNT | 1080005 | 2022-11-20 | 3404.35 | 64.2 | 3340.06 | 0.09
MLP | CLOSE | MLU0 Replace #3 RWMU Discharge expansion joint | E10539633 | MLWSPEJNT | 1080005 | 2023-04-26
MLP | CLOSE | MLU2 PENTHOUSE SEAL AIR FAN OUTLET EXP JNT REPLACE | E10539566 | MLWSPEJNT | 1080005 | 2022-12-01 | 24174.95 | 0 | 24174.88 | 0.07
MLP | CLOSE | MLU2 SCR EXP JNTS EJF01, EJF02, EJF05, EJF15, EJF16, EJF25 REPLACE | E10539565 | MLWSPEJNT | 1080005 | 2022-12-01 | 164310.8 | 10664.49 | 153580.92 | 65.39
MLP | CLOSE | MLU1 PENTHOUSE SEAL AIR FAN EJ'S (2 INLET/1 OUTLET REPLACE | E10539564 | MLWSPEJNT | 1080005 | 2022-12-01 | 32643.29 | 576.02 | 31945.7 | 121.57
MLP | CLOSE | MLU1 SCR EXP JNTS EJF14, EJF15, EJ115 REPLACE | E10539563 | MLWSPEJNT | 1080005 | 2022-12-01 | 110073.01 | 9558.23 | 100281.51 | 233.27
MLP | CLOSE | MLU1 FGD EXP JNTS EJ-FGX-71009 ID FAN TO ABSORBER INLET | E10539562 | MLWSPEJNT | 1080005 | 2022-12-01 | 75373.86 | 1152.03 | 73989.31 | 232.52
MLP | CLOSE | MLP - U2: 22 AIR HEATER MOTOR REPLACEMENT | E10736911 | MLWSPFANS | 1080005 | 2024-03-05 | 9118.73 | 4880.72 | 4156.63 | 81.38
MLP | CLOSE | MLU2 #23 DFA MECHANICAL EXHAUSTER REPLACEMENT | E10539502 | MLWSPFANS | 1080005 | 2023-04-26
MLP | COMP | MLP U1: 2-A6 CS RAPPER GEAR BOX REPLACEMENT | E10901921 | MLWSPGRBX | 1080005 | 2025-04-29
MLP | COMP | MLP U1: CS RAPPER S-B3 GEARBOX REPLACEMENT | E10890747 | MLWSPGRBX | 1080005 | 2025-04-15
MLP | CLOSE | MLP U2: PRECIP CS RAPPER GEARBOX REPLACEMENT | E10879852 | MLWSPGRBX | 1080005 | 2025-02-18
MLP | CLOSE | MLU1 REPLACE SPEED REDUCER ON CS RAPPER | E10692796 | MLWSPGRBX | 1080005 | 2023-11-03
MLP | COMP | MLP U1: LOAD OUT RETIRED LIME INJ EQUIP | E10858457 | MLWSPLIME | 1080005 | 2025-05-05 | 11310.76 | 0 | 11310.7 | 0.06
MLP | CLOSE | MLU1 REMOVE LIME PIG | E10633657 | MLWSPLIME | 1080005 | 2023-07-19 | 89762.35 | 25986.97 | 63948.59 | -173.21
MLP | COMP | MLP U2: REMOVE OLD PULVERIZER HOIST | E10912142 | MLWSPNPPB | 1080005 | 2025-06-13 | 30656.43 | 147.06 | 30508.6 | 0.77
MLP | INPRG | MLP U1: REMOVE OLD PULVERIZER HOIST | E10912139 | MLWSPNPPB | 1080005 |  | 34403.33 | 3491 | 30911.47 | 0.86
MLP | CLOSE | MLP U1: 13 PA DIFF TRANSMITTER REPLACEMENT | E10784145 | MLWSPNPPB | 1080005 | 2024-07-14
MLP | CLOSE | MLU0 REMOVE OLD FUEL OIL PUMP SKID | E10639045 | MLWSPNPPB | 1080005 | 2023-07-19 | 110114.49 | 1381.32 | 108250.23 | 482.94
MLP | CLOSE | MLU2 - oil skid compressed air pre-filters and burner deck corner filters | E10633321 | MLWSPNPPB | 1080005 | 2024-05-15 | 4900.06 | 2244.13 | 2655.91 | 0.02
MLP | CLOSE | MLU1 - oil skid compressed air pre-filters and burner deck corner filters | E10633316 | MLWSPNPPB | 1080005 | 2024-05-28 | 4877.14 | 2011.96 | 2865.15 | 0.03
MLP | CLOSE | MLP: U2 I/R BOX 3 HOPPER 2-3 DIFFUSER FEEDER SWING GATE VALVE | E10821992 | MLWSPPHCH | 1080005 | 2024-09-25 | 2488.14 | 0 | 2488.12 | 0.02
MLP | COMP | MLP U1: PURCHASE 16 PA CAPACITY DAMPER | E10834367 | MLWSPPULV | 1080005 | 2025-05-01 | 37316.69 | 9870.23 | 27446.36 | 0.1
MLP | COMP | MLP U1: PURCHASE 16 PA SHUTOFF DAMPER | E10834365 | MLWSPPULV | 1080005 | 2025-05-01 | 43826.25 | 479.56 | 43346.56 | 0.13
MLP | CLOSE | MLP U2: 21 PULVERIZER MOTOR REBUILD | E10814282 | MLWSPPULV | 1080005 | 2025-01-21 | 68107.19 | 288.45 | 40653.67 | 27165.07
MLP | CLOSE | MLP U2: 21 PULV MOTOR REPLACE (CSP) | E10800647 | MLWSPPULV | 1080005 | 2024-08-02 | 6741.5 | 0 | 6671.73 | 69.77
MLP | CLOSE | MLP U1: #16 PULVERIZER MOTOR REWIND | E10745313 | MLWSPPULV | 1080005 | 2024-08-12 | 47076.2 | 3969.66 | 27938.48 | 15168.06
MLP | CLOSE | MLP - PURCHASE PULV CAPACITY DAMPER | E10743063 | MLWSPPULV | 1080005 | 2024-10-01 | 64687.73 | 11159.14 | 53526.83 | 1.76
MLP | CLOSE | MLP - U1 PURCHASE PA SHUT OFF DAMPER | E10736512 | MLWSPPULV | 1080005 | 2024-10-01 | 48904.32 | 4007.36 | 44896.55 | 0.41
MLP | CLOSE | MLU2 REPLACE #25 PULVERIZER GEAR BOX | E10688266 | MLWSPPULV | 1080005 | 2023-11-19 | 35744.51 | 89.64 | 35612.26 | 42.61
MLP | COMP | MLU2 - Feeder Discharge chutes & plugged feeder capacitance probes | E10633286 | MLWSPPULV | 1080005 | 2024-05-17 | 34140 | 799.12 | 33340.53 | 0.35
MLP | CLOSE | MLU1 - Feeder Discharge chutes & plugged feeder capacitance probes | E10633277 | MLWSPPULV | 1080005 | 2023-12-15 | 35218.66 | 65.5 | 35127.95 | 25.21
MLP | CLOSE | MLU2 REPLACE #24 COAL GATE | E10615067 | MLWSPPULV | 1080005 | 2023-11-19 | 515.2 | 0 | 515.2 | 0
MLP | CLOSE | MLP PULV REBUILD (CORRECTION) | E10574714 | MLWSPPULV | 1080005 | 2023-02-01
MLP | CLOSE | MLU2 #26 PULVERIZER REBUILD | E10539582 | MLWSPPULV | 1080005 | 2022-10-22 | 51938.77 | 0 | 51922.64 | 16.13
MLP | COMP | MLU2 #25 PULVERIZER REBUILD | E10539581 | MLWSPPULV | 1080005 | 2022-10-22 | 50931.59 | 4888.12 | 44975.13 | 1068.34
MLP | COMP | MLP U1: STACK BREACHING CASING REPLACEMENT | E10840773 | MLWSPSBSR | 1080005 | 2025-05-07 | 28977.9 | 174.21 | 28803.49 | 0.2
MLP | COMP | MLP U1: REMOVE SOOTBLOWER SEAL AIR FANS | E10848114 | MLWSPSOOT | 1080005 | 2025-01-09 | 48317.46 | 0 | 48282.29 | 35.17
MLP | COMP | MLP U2: REMOVE SOOTBLOWER SEAL AIR FANS | E10842340 | MLWSPSOOT | 1080005 | 2024-12-24 | 78227.3 | 4464.86 | 73680.7 | 81.74
MLP | CLOSE | MLU2 WATER CANNON SYSTEM UPGRADE | E10539579 | MLWSPSOOT | 1080005 | 2023-11-16 | 40662.09 | 3364.82 | 37237.16 | 60.11
MLP | CLOSE | MLU1 WATER CANNON SYSTEM UPGRADE | E10539578 | MLWSPSOOT | 1080005 | 2023-12-01 | 48759.26 | 5371.06 | 43252.05 | 136.15
MLP | CLOSE | MLP U2: IR SOOTBLOWER REMOVAL | E10756796 | MLWSPSOTO | 1080005 | 2024-06-05 | 7519.68 | 0 | 7455.44 | 64.24
MLP | CLOSE | MLU2 IR SOOTBLOWER REMOVAL | E10615058 | MLWSPSOTO | 1080005 | 2023-11-19 | 222233.09 | 16091.3 | 205713.11 | 428.68
MLP | CLOSE | MLU1 IR SOOTBLOWER REMOVAL | E10554756 | MLWSPSOTO | 1080005 | 2022-12-01 | 126475.35 | 0 | 126472.43 | 2.92
MLP | COMP | MLP U1: BOX 2 HOPPER 1-1 RECEIVING HOPPER GATE | E10933966 | MLWSPVALV | 1080005 | 2025-07-15 | 777.23 | 0 | 767.98 | 9.25
MLP | COMP | MLP U1: #12 ASH WATER ISOLATION VALVES REPLACEMENT | E10896492 | MLWSPVALV | 1080005 | 2025-06-12
MLP | CLOSE | MLP U2: 22 ASH WATER PUMP SUCTION CHECK VALVE | E10877836 | MLWSPVALV | 1080005 | 2025-03-07 | 1366.87 | 0 | 1338.43 | 28.44
MLP | COMP | MLP U2: ASH PIT SUMP PUMP CHECK VALVE REPLACEMENT | E10865610 | MLWSPVALV | 1080005 | 2025-04-15
MLP | CLOSE | MLP U1 BOX 2 HOPPER 1-2 RECEIVING HOPPER & TEE REPLACEMENT | E10843413 | MLWSPVALV | 1080005 | 2025-04-15 | 709.28 | 0 | 681.59 | 27.69
MLP | COMP | MLP U1: BOX 1 HOPPER 1 RECEIVING HOPPER REPLACEMENT | E10843412 | MLWSPVALV | 1080005 | 2025-04-29 | 1135.04 | 0 | 1124.16 | 10.88
MLP | CLOSE | MLP U2: 24E BURNER SHUT OFF REPLACEMENT | E10756547 | MLWSPVALV | 1080005 | 2024-05-08 | 3880.02 | 0 | 3829.09 | 50.93
MLP | CLOSE | MLP U2: 22 ASH WATER PUMP SUCTION/DISCHARGE VALVES REPLACEMENT | E10748971 | MLWSPVALV | 1080005 | 2025-02-08 | 1794.56 | 0 | 1761.71 | 32.85
MLP | CLOSE | MLP U2: 26C BURNER SHUT OFF REPLACEMENT | E10748686 | MLWSPVALV | 1080005 | 2024-02-21 | 1239.62 | 0 | 1222.13 | 17.49
MLP | CLOSE | MLP - U2 ASH PIT SUMP PUMP | E10711029 | MLWSPVALV | 1080005 | 2023-12-10
MLP | CLOSE | MLU1 ASH JET VALVE 802 | E10643414 | MLWSPVALV | 1080005 | 2023-05-26 | 295.42 | 0 | 293.58 | 1.84
MLP | CLOSE | MLU2 PRECIP - REPLACE GEARBOX ON CS RAPPER | E10586150 | MLWSPVALV | 1080005 | 2023-02-15
MLP | CLOSE | MLU2 Replace Safety Valve #54 | E10541089 | MLWSPVALV | 1080005 | 2022-03-07 | 15066.69 | 62.49 | 14958.93 | 45.27
MLP | CLOSE | MLU1 BOX 2 XFER STA C NUVA FEEDER 12B LOWER HSO | E10539624 | MLWSPVALV | 1080005 | 2022-11-01 | 905.76 | 0 | 897.36 | 8.4
MLP | CLOSE | MLU2 #24 BURNER SHUT OFF REPLACEMENT | E10539597 | MLWSPVALV | 1080005 | 2024-03-12 | -0.88 | 0 | 0 | -0.88
MLP | CLOSE | MLU2 NUVA FEEDER LOWER HSO REPLACEMENT | E10539503 | MLWSPVALV | 1080005 | 2022-09-22 | 971.92 | 0 | 962.96 | 8.96
MLP | CLOSE | MLU1 #25 SAFETY VALVE REPLACEMENT | E10539463 | MLWSPVALV | 1080005 | 2023-11-07 | 9784.03 | 133.18 | 9650.85 | 0
MLP | INSERV | MLP U1: SCR CATALYST LAYER 1 REPLACEMENT | E10809719 | MLWVC1CL1 | 1080005 | 2025-04-25 | 670403.78 | 85672.32 | 559911.46 | 24820
MLP | CLOSE | ML2 SCR | E10539468 | MLWVC2CL4 | 1080005 | 2022-12-13 | 24706.05 | 0 | 2106.72 | 22599.33
MLP | CLOSE | MLP U0: Replace #11 ID fan motor due to EMI indication of broken rotor bar(s) | E10773943 | MLWVIDFMR | 1080005 | 2024-06-07 | 69288.28 | 3350.47 | 65880.96 | 56.85
MLP | COMP | MLP U1: 11 DE AND RE HUB REPLACEMENT | E10867749 | MLWVP11ID | 1080005 | 2025-04-30 | 210726.8 | 14015.5 | 196187.08 | 524.22
MLP | COMP | MLP U2: #21 ID FAN DRIVE END HUB REPLACEMENT | E10865891 | MLWVP21ID | 1080005 | 2025-02-15 | 248914.37 | 76305.18 | 153613.97 | 18995.22
MLP | CLOSE | MLU0 REPLACE FGD SERVICE AIR COMPRESSOR #2 | E10539476 | MLWVPAIRC | 1080005 | 2022-10-20 | 67584.65 | 19737.92 | 47846.52 | 0.21
MLP | CLOSE | MLU2 FGD BATTERY REPLACEMENT | E10539527 | MLWVPBATT | 1080005 | 2022-10-25 | 20317.31 | 384.79 | 19894.28 | 38.24
MLP | CLOSE | MLU1 FGD BATTERY REPLACEMENT | E10539526 | MLWVPBATT | 1080005 | 2022-10-19 | 32854.35 | 0 | 32814.34 | 40.01
MLP | COMP | MLP U0: BALL MILL B LINER REPLACEMENT | E10840516 | MLWVPBLML | 1080005 | 2025-04-24 | 53951.49 | 864.8 | 53086.42 | 0.27
MLP | CLOSE | MLP U0: LIME SILO LEVEL INDICATION REPLACEMENT | E10834354 | MLWVPCNTM | 1080005 | 2024-11-20 | 761.21 | 0 | 750.22 | 10.99
MLP | CLOSE | MLP U0: DSI BLOWER 2 DEWPOINT SENSOR REPLACEMENT | E10797764 | MLWVPDSIN | 1080005 | 2024-09-07 | 846.53 | 0 | 834.41 | 12.12
MLP | CLOSE | MLP - U2 DSI CONV BLWR #2 REPLACEMENT | E10691563 | MLWVPDSIN | 1080005 | 2023-11-02 | 357.55 | 0 | 353.18 | 4.37
MLP | COMP | MLP U1: 11 ID FAN INLET EXP JNT EJ-71006 REPLACE | E10879891 | MLWVPEJNT | 1080005 | 2025-04-30 | 10134.48 | 0 | 10134.42 | 0.06
MLP | CLOSE | MLP U2: 21 ID FAN INLET EXP JOINT EJ-72006 REPLACEMENT | E10866269 | MLWVPEJNT | 1080005 | 2025-02-18 | 33477.25 | 0 | 33477.1 | 0.15
MLP | CLOSE | MLP U1: DSI SILO 1 - UPGRADE SILO BOOT | E10815916 | MLWVPEJNT | 1080005 | 2025-04-04 | 9585.59 | 0 | 9585.57 | 0.02
MLP | CLOSE | MLU2 Replace Oxidation Air Blower C Discharge Expansion Joint | E10793958 | MLWVPEJNT | 1080005 | 2024-07-11 | 4615.9 | 0 | 4615.89 | 0.01
MLP | CLOSE | MLP U2: 2C AR PUMP DISCHARGE EJ Q2-ZRX-80051 | E10768523 | MLWVPEJNT | 1080005 | 2024-10-14 | 31260.03 | 0 | 31259.79 | 0.24
MLP | CLOSE | MLP U1 BLEED PUMP 1A SUCTION PIPING & EXP JOINT | E10752244 | MLWVPEJNT | 1080005 | 2024-04-05 | 972.6 | 0 | 972.59 | 0.01
MLP | COMP | MLP U0: 24B BUS MULTILIN RELAY REPLACEMENT | E10890161 | MLWVPFGDN | 1080005 | 2025-05-13 | 847.67 | 0 | 839.58 | 8.09
MLP | INPRG | MLP U0: 22A BUS MULTILIN RELAY REPLACEMENT | E10890160 | MLWVPFGDN | 1080005 |  | 847.67 | 0 | 839.58 | 8.09
MLP | CLOSE | MLP U0: CPS PRESS #2 CLOTH REPLACEMENT | E10867837 | MLWVPFGDN | 1080005 | 2025-02-28 | 5404.32 | 567.88 | 4836.43 | 0.01
MLP | CLOSE | MLP U0: VAC BELT A FILTER CLOTH REPLACEMENT | E10843483 | MLWVPFGDN | 1080005 | 2024-11-26 | 2150.09 | 0 | 2110.54 | 39.55
MLP | CLOSE | MLP U0: VAC BELT A VFD REPLACEMENT | E10815920 | MLWVPFGDN | 1080005 | 2024-10-18 | -17985.28 | -19926.87 | 1915.11 | 26.48
MLP | CLOSE | MLP U0: CPS AIR COMPRESSOR 2 BREAKER REPLACE | E10795965 | MLWVPFGDN | 1080005 | 2024-08-05 | 1291.17 | 0 | 1278.65 | 12.52
MLP | CLOSE | MLP U0: CPS FEED BREAKER REPLACEMENT | E10762571 | MLWVPFGDN | 1080005 | 2024-03-28
MLP | CLOSE | MLP U0: UPGRADE LIME SILO 2 PANEL VIER HMI | E10762567 | MLWVPFGDN | 1080005 | 2024-06-11 | 155.97 | 0 | 155.96 | 0.01
MLP | CLOSE | MLP U0: LABOR TO I/R FGD INST AIR DRYERS | E10750727 | MLWVPFGDN | 1080005 | 2024-09-06 | 66048.6 | 42385.13 | 23663.23 | 0.24
MLP | CLOSE | MLP U0: ABSORBER AGITATOR 2F MOTOR REPLACEMENT | E10748211 | MLWVPFGDN | 1080005 | 2024-05-15 | 768.32 | 0 | 757.52 | 10.8
MLP | CLOSE | MLP - U0: REPLACE GRV-9143 LIMIT SWITCH | E10728262 | MLWVPFGDN | 1080005 | 2024-04-04 | 460.75 | 0 | 449.66 | 11.09
MLP | CLOSE | MLP - U2: 21 ID FAN DRIVE END BEARING LINER | E10706085 | MLWVPFGDN | 1080005 | 2023-11-04 | 1902.89 | 1902.89 | 0 | 0
MLP | CLOSE | MLU0 HYDROLYZER 2 GRV-9769 DXP REPLACE | E10700678 | MLWVPFGDN | 1080005 | 2024-09-30
MLP | CLOSE | MLU0 REMOVE UREA STORAGE TANK VENT CHILLER & CONDENSER | E10690413 | MLWVPFGDN | 1080005 | 2024-01-10 | 20749.21 | 1401.84 | 19347.37 | 0
MLP | CLOSE | MLU0 Replace FGD Water Heater | E10645236 | MLWVPFGDN | 1080005 | 2024-06-26 | 964 | 0 | 936.17 | 27.83
MLP | CLOSE | MLU1 & MLU2 - REMOVE #11, #12, #21 & #22 ID fan outlet guillotine dampers & framework | E10644675 | MLWVPFGDN | 1080005 | 2024-06-21 | 464745.41 | 106661.92 | 358068.84 | 14.65
MLP | CLOSE | MLU1 & MLU2 - REMOVE SEAL AIR PIPING | E10643403 | MLWVPFGDN | 1080005 | 2024-06-10 | 291896.35 | 16622.94 | 275271.25 | 2.16
MLP | CLOSE | MLU0 CPS FILTER PRESS BOMBAY DOOR LIMITS | E10567474 | MLWVPFGDN | 1080005 | 2023-11-05 | 585.28 | 0 | 577.72 | 7.56
MLP | CLOSE | MLU0 FGD VAC BELT C REPLACEMENT | E10541699 | MLWVPFGDN | 1080005 | 2022-10-06 | 147.82 | 0 | 147.12 | 0.7
MLP | CLOSE | MLU0 Replace section of storm sewer pipe from North Coal Yard treatment pond to the Kammer Pond | E10539631 | MLWVPFGDN | 1080005 | 2023-06-07 | 1059.4 | 0 | 1062.28 | -2.88
MLP | CLOSE | MLU2 REPLACE U2A CONDENSATE RETURN LINE | E10539619 | MLWVPFGDN | 1080005 | 2023-07-30 | 375876.24 | 76293.32 | 299172.06 | 410.86
MLP | CLOSE | MLU0 ID fan #21 thrust bearing replacement | E10539613 | MLWVPFGDN | 1080005 | 2022-10-31 | 17276.04 | 0 | 16419.59 | 856.45
MLP | CLOSE | MLU0 OXIDATION AIR BLOWER MOTOR C (CSP) REPLACEMENT | E10539592 | MLWVPFGDN | 1080005 | 2023-06-15 | 45237.13 | 24499 | 17668.23 | 3069.9
MLP | COMP | MLU0 CPS FILTER PRESS B BOMBAY DOOR LIMITS UPGRADE | E10539532 | MLWVPFGDN | 1080005 | 2022-10-06 | 9319.55 | 0 | 9218.12 | 101.43
MLP | CLOSE | MLU0 BALL MILL A SLURRY TANK AGITATOR GEARBOX REPLACE | E10539519 | MLWVPFGDN | 1080005 | 2023-09-21
MLP | CLOSE | MLU1 DISPOSAL OF SCR CATALYST U1, LAYER 3 | E10539518 | MLWVPFGDN | 1080005 | 2023-04-17 | 590671.07 | 0 | 590671.07 | 0
MLP | CLOSE | MLU0 Vacuum Belt B Pump Speed Reducer Replacement | E10660255 | MLWVPGRBX | 1080005 | 2023-08-09 | 782.71 | 0 | 771.62 | 11.09
MLP | CLOSE | MLU0 HYDROCLONE FEEDTANK B AGITATOR GEARBOX REPLACEMENT | E10591691 | MLWVPGRBX | 1080005 | 2023-11-18 | 10726.71 | 0 | 10726.71 | 0
MLP | CLOSE | MLU0 PURCHASE & INSTALL HEATER ON TRAVELING TRIPPER | E10539494 | MLWVPHEAT | 1080005 | 2024-03-13 | 0 | 0 | 0 | 0
MLP | CLOSE | MLU1 1E AR PUMP DISCHARGE EXP JOINT REPLACE | E10539598 | MLWVPIDEJ | 1080005 | 2022-12-16 | 3456.99 | 0 | 3456.9 | 0.09
MLP | CLOSE | MLU1 1F AR PUMP SUCTION SIDE EJ REPLACEMENT | E10539480 | MLWVPIDEJ | 1080005 | 2022-10-31 | 4333.78 | 0 | 4333.78 | 0
MLP | COMP | MLP U1: 11 ID FAN HYDRAULIC CYLINDER REPLACEMENT | E10867843 | MLWVPIDHY | 1080005 | 2025-04-30 | 53263.79 | 24670.5 | 28593.22 | 0.07
MLP | CLOSE | MLP U2: ION METER ETHERNET SWITCH REPLACEMENT | E10777438 | MLWVPMONS | 1080005 | 2024-05-17 | 861.95 | 0 | 853.55 | 8.4
MLP | CLOSE | MLU0 REPLACE REAGENT LOOP B | E10677794 | MLWVPOPIP | 1080005 | 2023-11-07 | 523902.26 | 1289 | 522538.78 | 74.48
MLP | CLOSE | MLU0 Replace Reagent Loop B | E10644745 | MLWVPOPIP | 1080005 | 2023-11-17 | 28170.51 | 1688.84 | 26502 | -20.33
MLP | CLOSE | MLU0 REPLACE REAGENT LOOP A | E10677787 | MLWVPPIPE | 1080005 | 2023-11-07 | 518953.2 | 2418.28 | 516534.71 | 0.21
MLP | CLOSE | MLU0 Replace Reagent Loop A | E10644741 | MLWVPPIPE | 1080005 | 2023-11-17 | 36804.86 | 644.5 | 33517.82 | 2642.54
MLP | INPRG | MLP U0: SLUDGE PUMP 3 VFD REPLACEMENT | E10895086 | MLWVPPUMP | 1080005 |  | 1598.97 | 0 | 1583.69 | 15.28
MLP | INSERV | MLP U0: BALL MILL A REBUILD | E10887198 | MLWVPPUMP | 1080005 | 2025-06-20 | 851.01 | 0 | 842.92 | 8.09
MLP | COMP | MLP U2: LABOR TO I/R 2F AR PUMP MOTOR | E10877523 | MLWVPPUMP | 1080005 | 2025-04-02 | 18666.05 | 0 | 18666.04 | 0.01
MLP | CLOSE | MLP U0: FILTRATE PUMP C REPLACEMENT | E10863842 | MLWVPPUMP | 1080005 | 2025-01-13 | 1664.34 | 0 | 1637.32 | 27.02
MLP | CLOSE | MLP U0: MIST ELIMINATOR PUMP B REPLACEMENT | E10850668 | MLWVPPUMP | 1080005 | 2024-12-10 | 1503.58 | 0 | 1478.53 | 25.05
MLP | CLOSE | MLP U1: LABOR TO I/R RECLAIM WATER PUMP A CSP | E10850094 | MLWVPPUMP | 1080005 | 2024-12-10 | 18452.52 | 16804 | 1618.08 | 30.44
MLP | CLOSE | MLP U0: HYDROCLONE FEED PUMP A CSP REPLACEMENT | E10843260 | MLWVPPUMP | 1080005 | 2024-12-19 | 977.39 | 0 | 959.48 | 17.91
MLP | COMP | MLP U2: AR Pump 1F Motor & Pump Replacement/Gearbox Rebuild | E10840764 | MLWVPPUMP | 1080005 | 2025-05-13 | 32170.02 | 3249.93 | 28919.98 | 0.11
MLP | CLOSE | MLP U2: LABOR TO I/R 2A BLEED PUMP CSP | E10832916 | MLWVPPUMP | 1080005 | 2024-11-07 | 2350.03 | 0 | 2312.62 | 37.41
MLP | CLOSE | MLP U0: RECLAIM WATER PUMP A | E10798038 | MLWVPPUMP | 1080005 | 2024-07-22 | 3081.23 | 0 | 3050.19 | 31.04
MLP | CLOSE | MLP U0: FGD SERVICE WATER PUMP A - REPLACEMENT | E10785753 | MLWVPPUMP | 1080005 | 2024-06-14 | -9660.98 | -10619 | 948.75 | 9.27
MLP | CLOSE | MLU0 LP SLUDGE PUMP #3 18 PULSE RECTIFIER | E10765291 | MLWVPPUMP | 1080005 | 2024-09-14 | 1171.6 | 0 | 1160.1 | 11.5
MLP | CLOSE | MLP U0: CPS LP & HP SLUDGE PUMP VFD REPLACEMENTS | E10759743 | MLWVPPUMP | 1080005 | 2024-08-05 | 3411.48 | 0 | 3352.18 | 59.3
MLP | CLOSE | MLU0 REPLACE BALL MILL SLURRY PUMP A2 | E10717834 | MLWVPPUMP | 1080005 | 2023-12-19 | 6345.19 | 0 | 6273.68 | 71.51
MLP | CLOSE | MLU1 LABOR TO I/R 1D AR PUMP MOTOR (CSP) | E10693663 | MLWVPPUMP | 1080005 | 2023-12-02 | 7947.54 | 0 | 7947.54 | 0
MLP | CLOSE | MLU0 #3 PRIMARY CLARIFIER SLUDGE PUMP REPLACEMENT | E10664892 | MLWVPPUMP | 1080005 | 2023-08-08 | -10297.32 | -11326 | 1013.96 | 14.72
MLP | CLOSE | MLU0 LABOR TO I/R FGD HYDROCLONE FEEDPUMP C (CSP 9900116538) | E10655584 | MLWVPPUMP | 1080005 | 2023-07-17 | 1355.82 | 0 | 1318.31 | 37.51
MLP | CLOSE | MLP - MLU0 PURCHASE HYDROCLONE OVERFLOW BLOWDOWN PUMP | E10647482 | MLWVPPUMP | 1080005 | 2023-11-07 | 1955.88 | 0 | 1931.82 | 24.06
MLP | CLOSE | MLU0 - MIST ELIMINATOR PUMP A REPLACEMENT | E10635305 | MLWVPPUMP | 1080005 | 2023-05-03 | 829.04 | 0 | 812.09 | 16.95
MLP | CLOSE | MLU0 MIST ELIMINATOR PUMP B - REPLACEMENT | E10617641 | MLWVPPUMP | 1080005 | 2024-09-02
MLP | CLOSE | MLU0 MIST ELIMINATOR PUMP A - REPLACE | E10611115 | MLWVPPUMP | 1080005 | 2023-03-16 | 1061.84 | 0 | 998.6 | 63.24
MLP | CLOSE | MLU0 CPS CLOTH WASH PUMP REPLACEMENT | E10585887 | MLWVPPUMP | 1080005 | 2023-02-08 | 1989.82 | 0 | 1972.77 | 17.05
MLP | CLOSE | MLU2 REPLACE 2F AR PUMP LOW SPEED COUPLING | E10560742 | MLWVPPUMP | 1080005 | 2022-12-01
MLP | CLOSE | MLU0 - LABOR TI I/R #1 EFFLUENT SUMP PUMP | E10539627 | MLWVPPUMP | 1080005 | 2022-09-30 | 10227.13 | 0 | 8672.43 | 1554.7
MLP | CLOSE | MLU0 MIST ELIMINATOR WAS PUMP B - REPLACE | E10539575 | MLWVPPUMP | 1080005 | 2022-10-01 | 667.47 | 0 | 660.12 | 7.35
MLP | CLOSE | MLU0 REPLACE HYDROCLONE FEEDPUMP A | E10539571 | MLWVPPUMP | 1080005 | 2022-06-13 | 1444.2 | 0 | 1425.24 | 18.96
MLP | COMP | MLU2 2C AR PUMP IMPELLER / PUMP RUNNER | E10539556 | MLWVPPUMP | 1080005 | 2023-05-31 | 15588.07 | 0 | 15446.88 | 141.19
MLP | CLOSE | MLU0 LABOR TO I/R REAGENT PUMP B (CSP) | E10539545 | MLWVPPUMP | 1080005 | 2023-04-26 | 305.98 | 0 | 0 | 305.98
MLP | CLOSE | MLP U0: LABOR TO I/R MOISTURE SEPARATOR COLLECTION POT | E10872638 | MLWVPTANK | 1080005 | 2025-03-28 | 611.58 | 0 | 611.58 | 0
MLP | CLOSE | MLP U0: MOISTURE SEPARATOR COLLECTION POT - FAB & INSTALL | E10797221 | MLWVPTANK | 1080005 | 2024-10-30 | 9614 | 100.29 | 9513.71 | 0
MLP | CLOSE | MLP - U0 CPS PRIMARY CLARIFIER TANK SLUDGE LEVEL PROBE | E10731778 | MLWVPTANK | 1080005 | 2024-04-04 | 2685.81 | 0 | 2652.02 | 33.79
MLP | CLOSE | MLP U0: BIOREACTOR 2C LEVEL TRANSMITTER/PROBE REPLACE | E10890325 | MLWVPTRMT | 1080005 | 2025-03-27 | 347.79 | 0 | 334.36 | 13.43
MLP | COMP | MLP U1: ABSORBER LEVEL TRANSMITTER REPLACEMENT | E10886937 | MLWVPTRMT | 1080005 | 2025-03-27 | 1798.85 | 0 | 1730.09 | 68.76
MLP | COMP | MLP U1: SLURRY HOUSE SUMP ALARM TRANSMITTER REPLACE | E10868945 | MLWVPTRMT | 1080005 | 2025-05-05 | 408.78 | 0 | 404.81 | 3.97
MLP | CLOSE | MLP U0: REPLACE POSITIONER ON ZEAR 8003 | E10853343 | MLWVPTRMT | 1080005 | 2024-12-17 | 352.28 | 0 | 345.91 | 6.37
MLP | CLOSE | MLP U0: REPLACE POSITIONER ON ZEAR 8003 | E10853331 | MLWVPTRMT | 1080005 | 2024-12-13 | 510.1 | 0 | 510.1 | 0
MLP | CLOSE | MLP U2: DSI SILO 2 PRESSURE TRANSMITTER | E10795318 | MLWVPTRMT | 1080005 | 2024-08-06 | 645.41 | 0 | 639.32 | 6.09
MLP | CLOSE | MLP U0: CLOTH WASH PUMP DCHG PRESSURE TRANSMITTER | E10785822 | MLWVPTRMT | 1080005 | 2024-08-09 | 411.12 | 0 | 407.07 | 4.05
MLP | CLOSE | MLU2 - RX 22 Coriolis Flowmeter "A" Replacement | E10778667 | MLWVPTRMT | 1080005 | 2024-06-11 | 155.97 | 0 | 155.96 | 0.01
MLP | CLOSE | MLP U0: CPS FILTER PRESS 3 BOMBAY DOOR LIMIT UPGRADE | E10767903 | MLWVPTRMT | 1080005 | 2024-06-11
MLP | CLOSE | MLU0 FGD - 869 Multilin Replacement for Spare Compartments | E10765527 | MLWVPTRMT | 1080005 | 2024-05-30 | 85.08 | 0 | 85.08 | 0
MLP | CLOSE | MLU0 U2A HYDROLYZER BLOWDOWN SPARGING VESSEL LEVEL PROBE REPLACEMENT | E10765398 | MLWVPTRMT | 1080005 | 2024-10-17 | 436.59 | 0 | 424.07 | 12.52
MLP | CLOSE | MLP U2: AMMONIA INJECTION FLOW METER REACTOR 22 | E10757536 | MLWVPTRMT | 1080005 | 2024-07-04 | 250.08 | 0 | 247.82 | 2.26
MLP | CLOSE | MLP U1: ID FAN INLET PRESSURE INDICATOR PROBE B | E10748867 | MLWVPTRMT | 1080005 | 2024-02-29 | 692.52 | 0 | 682.78 | 9.74
MLP | CLOSE | MLP U1: DSI BLOWER 1 DISCHARGE DEWPOINT SENSOR | E10739049 | MLWVPTRMT | 1080005 | 2024-03-22 | 316.92 | 0 | 310.95 | 5.97
MLP | CLOSE | MLP - U0 FGD AIR DRYER SKID 2 DEWPOINT MONITOR | E10691873 | MLWVPTRMT | 1080005 | 2023-11-15
MLP | CLOSE | MLU0 FGD MIMIC PANEL GAUGE REPLACEMENTS | E10679218 | MLWVPTRMT | 1080005 | 2024-01-29 | 1876.5 | 0 | 1849.74 | 26.76
MLP | CLOSE | MLU0 RECLAIM H2O HEADER DCHG PRESSURE TRANSMITTER | E10654009 | MLWVPTRMT | 1080005 | 2024-01-11
MLP | CLOSE | MLU2 Replace SCR #21 inlet probe | E10640724 | MLWVPTRMT | 1080005 | 2024-04-30
MLP | CLOSE | MLU0 FGD BALL MILL A SLURRY PUMP DCHG TRANSMITTER | E10621058 | MLWVPTRMT | 1080005 | 2023-10-26 | 293.75 | 0 | 288.32 | 5.43
MLP | CLOSE | MLU0 CPS LIME SILO 1 HMI UPGRADE | E10615975 | MLWVPTRMT | 1080005 | 2023-05-02 | 1485.49 | 0 | 1455.2 | 30.29
MLP | CLOSE | MLU0 FGD OXIDATION AIR BLOWER C MULTILIN RELAY (469( REPLACEMENT | E10539574 | MLWVPTRMT | 1080005 | 2022-06-09 | 64.29 | 0 | 64.29 | 0
MLP | CLOSE | MLU0 FGD REAGENT TANK A LEVEL TRANSMITTER | E10539484 | MLWVPTRMT | 1080005 | 2022-12-13 | 174.55 | 0 | 169.5 | 5.05
MLP | CLOSE | MLP U0: HYDROLYZER VALVE REPLACEMENT | E10852390 | MLWVPVALV | 1080005 | 2024-12-13 | 1338.08 | 0 | 1315.6 | 22.48
MLP | CLOSE | MLP U0: 10-IN BRAY VLV ON OAB A BLOWOFF VLV | E10785774 | MLWVPVALV | 1080005 | 2024-07-08 | 3219.72 | 0 | 3219.71 | 0.01
MLP | CLOSE | MLP U0: FGD ZDAR-8328 CONTROLLER | E10757532 | MLWVPVALV | 1080005 | 2024-05-02
MLP | CLOSE | MLP U0: REAGENT SLURRY LOOP DOSING VLV ZFAR-8111 POSITIONER | E10739024 | MLWVPVALV | 1080005 | 2024-02-03 | 894.37 | 0 | 876.48 | 17.89
MLP | CLOSE | MLU0 BALL MILL SLURRY PUMP A2 DCHG VLV ZPAS-8163 | E10648463 | MLWVPVALV | 1080005 | 2023-07-21 | 3301.45 | 0 | 3256.64 | 44.81
MLP | CLOSE | MLU0 Replace FeCl Mix Tank Discharge Valves | E10631573 | MLWVPVALV | 1080005 | 2023-06-28 | 18353.67 | 0 | 18403.64 | -49.97
MLP | CLOSE | MLU0 REPLACE 2 UREA STORAGE TANK VALVES | E10590269 | MLWVPVALV | 1080005 | 2023-10-30 | 547.73 | 0 | 540.59 | 7.14
MLP | CLOSE | MLU0 Replace U2A U1 GRV-9187 valve and actuator assembly with one from storeroom - 6 inch valve | E10567922 | MLWVPVALV | 1080005 | 2023-10-20 | 812.53 | 0 | 801.86 | 10.67
MLP | CLOSE | MLU2 2A AR PUMP VALVE (ZTAS-810) REPLACE | E10567466 | MLWVPVALV | 1080005 | 2022-12-05 | 1041.19 | 0 | 1029.15 | 12.04
MLP | CLOSE | MLU0 REPLACE CPS TANK VALVES (7) | E10554815 | MLWVPVALV | 1080005 | 2023-11-07 | 67919.49 | 7929.07 | 59990.08 | 0.34
MLP | CLOSE | MLU1 1E AR PUMP SUCTION VALVE REPLACE | E10539604 | MLWVPVALV | 1080005 | 2022-12-01 | 32102.05 | 11590.38 | 20474.53 | 37.14
MLP | COMP | MLU0 VACUUM BELT SERVICE WATER STRAINER REPLACEMENT | E10539478 | MLWVPVALV | 1080005 | 2022-12-01 | 87495 | 1320.87 | 86085.75 | 88.38