## Figure MR-1
Year | SAIFI | CAIDI | SAIDI | 3-Yr SAIFI | 3-Yr CAIDI | 3-Yr SAIDI | Year | 3-Yr SAIFI Average | 3-Yr CAIDI Average | 3-Yr SAIDI Average
2010 | 2.47 | 169.4 | 418.4 |  |  |  | 2012 | 2.66 | 184.8 | 493.1
2011 | 3.09 | 195.4 | 602.8 |  |  |  | 2013 | 2.55 | 187.8 | 481.2
2012 | 2.42 | 189.5 | 458 | 2.66 | 184.7667 | 493.0667 | 2014 | 2.31 | 193.6 | 448.7
2013 | 2.14 | 178.5 | 382.7 | 2.55 | 187.8 | 481.1667 | 2015 | 2.33 | 193.7 | 452
2014 | 2.37 | 212.9 | 505.3 | 2.31 | 193.6333 | 448.6667 | 2016 | 2.34 | 202.8 | 473.1
2015 | 2.47 | 189.8 | 468.1 | 2.3267 | 193.7333 | 452.0333 | 2017 | 2.27 | 194.3 | 440.1
2016 | 2.17 | 205.7 | 445.8 | 2.3367 | 202.8 | 473.0667 | 2018 | 2.23 | 199.9 | 445.4
2017 | 2.17 | 187.3 | 406.3 | 2.27 | 194.2667 | 440.0667 | 2019 | 2.33 | 196.4 | 458.5
2018 | 2.34 | 206.8 | 484.2 | 2.2267 | 199.9333 | 445.4333 | 2020 | 2.28 | 199.9 | 455.5
2019 | 2.49 | 195.2 | 485 | 2.3333 | 196.4333 | 458.5 | 2021 | 2.12 | 203.3 | 428.2
2020 | 2.01 | 197.7 | 397.4 | 2.28 | 199.9 | 455.5333 | 2022 | 2.05 | 209.7 | 430
2021 | 1.85 | 217.1 | 402.1 | 2.1167 | 203.3333 | 428.1667 | 2023 | 2 | 203.7 | 408.2
2022 | 2.29 | 214.3 | 490.6 | 2.05 | 209.7 | 430.0333 | 2024 | 2.1 | 193.6 | 409.4
2023 | 1.85 | 179.6 | 331.8 | 1.9967 | 203.6667 | 408.1667
2024 | 2.17 | 187 | 405.8 | 2.1033 | 193.6333 | 409.4

## Total Indices
Exclude Major Event |  | 12 Rolling Mths | [7 empty] | YTD March & May 2025 |  | Exclude MED
OpUnit | MthEndDt | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2020-12-31 | 165077 | 9165 | 331826 | 65600673 | 397.3944 | 2.0101 | 197.696
AEP-KYP | 2021-12-31 | 164021 | 8435 | 303745 | 65956314 | 402.1212 | 1.8519 | 217.1437
AEP-KYP | 2022-12-31 | 162018 | 9704 | 370882 | 79488727 | 490.6166 | 2.2891 | 214.3235
AEP-KYP | 2023-12-31 | 161642 | 8755 | 298663 | 53625916 | 331.7573 | 1.8477 | 179.5533
AEP-KYP | 2024-12-31 | 161599 | 9537 | 350744 | 65584414 | 405.8467 | 2.1705 | 186.9866 |  | OpUnit | MthEndDt | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2025-03-31 | 161599 | 9505 | 345197 | 65904361 | 407.8265 | 2.1361 | 190.9181 | updated 3/31 in case needed to | AEP-KYP | 2025-03-31 | 161599 | 2074 | 74365 | 14451978 | 89.4311 | 0.46018 | 194.3384
AEP-KYP | 2025-05-31 | 161599 | 9583 | 356135 | 66121988 | 409.1732 | 2.2038 | 185.6655 |  | AEP-KYP | 2025-05-31 | 161599 | 3869 | 151702 | 30008172 | 185.6953 | 0.93876 | 197.81
Include Major Events |  | 12 Rolling Mths | [7 empty] | YTD March & May 2025 |  | Include MED
OpUnit | MthEndDt | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2020-12-31 | 165077 | 10522 | 434145 | 285558332 | 1729.8493 | 2.63 | 657.7488
AEP-KYP | 2021-12-31 | 164021 | 10579 | 433218 | 465666241 | 2839.0648 | 2.6412 | 1074.9005
AEP-KYP | 2022-12-31 | 162018 | 10810 | 459630 | 277149229 | 1710.6076 | 2.8369 | 602.9833
AEP-KYP | 2023-12-31 | 161642 | 9869 | 379369 | 116110640 | 718.3197 | 2.347 | 306.0625
AEP-KYP | 2024-12-31 | 161599 | 11027 | 448347 | 203003497 | 1256.2175 | 2.7744 | 452.7821 |  | OpUnit | MthEndDt | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2025-03-31 | 161599 | 11708 | 491218 | 260882730 | 1614.3833 | 3.0397 | 531.0936 |  | AEP-KYP | 2025-03-31 | 161599 | 2787 | 122569 | 71685476 | 443.601 | 0.75848 | 584.8581
AEP-KYP | 2025-03-31 | 161599 | 11708 | 491004 | 260556942 | 1612.3673 | 3.0384 | 530.6615 | updated 3/31 in case needed to | AEP-KYP | 2025-05-31 | 161599 | 4981 | 225289 | 106005235 | 655.977 | 1.3941 | 470.53
AEP-KYP | 2025-05-31 | 161599 | 11625 | 489384 | 235726199 | 1458.7108 | 3.0284 | 481.6794

## 12Mth Maj&MinExcl MED Pivot
Major Cause Name | (All)
OpUnit | AEP-KYP
Sum of SAIDI | Column Labels
Row Labels | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-03-31 | 2025-05-31
OTHER | 4.3084 | 2.3629 | 3.745 | 1.7189 | 1.7171 | 0.63897 | 0.89531
ABNORMAL FEED | 0.30585 |  |  |  |  | 0.045638 | 0.045638
ANIMAL - BIRD | 3.2704 | 0.35769 | 1.7676 | 1.444 | 0.16787 | 0.68679 | 0.67768
ANIMAL - NON BIRD | 1.7603 | 1.2154 | 0.9802 | 0.79393 | 1.918 | 0.89731 | 0.97535
ANIMAL - OTHER | 1.7989
ANIMAL BUS | 1.4449 | 1.1788 |  | 0.63053
ANIMAL BUSHING XFMR | 0.38064
BLAST/EXPLOSION (NON AEP) |  |  | 0.0038885 |  |  |  | 0.0014728
CONTAMINATION/FLASHOVER | 0.031301 | 0.33859 | 0.092268 | 0.23254
CORROSION | 0.029423 | 0.12967 | 0.17241 | 0.54211 | 0.40914 | 0.36023 | 0.071003
CUST. EQUIPMENT > 1 CUSTOMER | 0.63146 | 0.94406 | 0.40555 | 0.0088405 | 0.10068 | 0.10378 | 0.11878
EQUIPMENT FAILURE | 87.0841 | 71.9596 | 108.9066 | 47.6055 | 62.1571 | 68.8156 | 83.5411
ERROR - FIELD | 0.1451 | 0.16334 | 0.34752 | 0.5605 | 0.23912 | 1.936 | 2.9385
ERROR - OPERATIONS | 0.00069059 | 0.19765 | 0.030737 | 1.6994 | 4.4234 | 4.4199 | 4.8305
ERROR-FIELD | 0.0066757 | 0.0012011 | 0.021775 | 0.0016456 | 0.003682 | 0.003682 | 0.0027847
FACILITATION OF WORK | 2.9236 | 2.5104 | 4.8038 | 3.8829 | 3.6753 | 2.8754 | 2.2603
FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 0.7811 | 2.7003 | 2.6643 | 7.0256 | 1.9756 | 3.0244 | 3.1869
FOREIGN OBJECT (NON ANIMAL) | 0.41624 | 0.26474 | 0.049427 | 0.3458 | 0.16307 | 0.16092 | 0.23537
OTHER UTILITY | 0.44535 | 6.033 | 0.040298 | 0.098236 | 2.2443 | 1.9479 | 2.1248
OVERLOAD | 0.078842 | 0.095006 | 0.13237 | 0.62088 | 0.37919 | 0.37689 | 0.37689
SCHEDULED COMPANY | 26.911 | 43.31 | 34.9697 | 30.4135 | 27.4858 | 25.4685 | 26.6528
SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 1.4402 | 0.58071 | 0.69643 | 0.72977 | 0.19569 | 0.32383 | 0.25246
TREE INSIDE ROW | 16.9604 | 9.6825 | 12.9006 | 6.9945 | 8.5499 | 8.9261 | 9.1186
TREE OUT OF ROW | 183.2794 | 185.797 | 225.279 | 177.5376 | 224.7798 | 214.639 | 199.2993
TREE REMOVAL (NON AEP) | 1.5947 | 4.0997 | 4.4411 | 2.0808 | 1.4516 | 1.351 | 0.47995
UG CONST. /DIG-INS (NON AEP) | 0.80528 | 0.054469 | 0.074695 | 0.083543 | 0.026114 | 0.02422 | 0.02422
UNBALANCE | 0.3855 | 0.53344
UNKNOWN (NON WEATHER) | 16.7469 | 16.0125 | 21.8844 | 14.2791 | 17.9204 | 19.1763 | 19.799
VANDALISM | 0.95623 | 0.33349 | 0.14582 | 0.017947 | 0.99164 | 1.185 | 2.1655
VEHICLE ACCIDENT (NON AEP) | 9.726 | 10.8935 | 10.6917 | 10.2752 | 18.8157 | 18.8848 | 16.7058
VINE | 1.2854 | 1.4197 | 3.8826 | 1.931 | 1.262 | 1.2006 | 1.291
WEATHER - FLOOD/SLIDE | 3.2931 | 7.4098 | 16.8438 | 0.21818 | 1.1855 | 3.5988 | 5.9725
WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 5.5732 | 0.69925 | 3.4566 | 2.9277 | 8.3763 | 8.3151 | 5.5994
WEATHER - HURRICANE |  |  | 0.00098137 |  | 0.0038057 | 0.0038057 | 0.0038057
WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 4.9735 | 18.8106 | 8.9317 |  | 0.0094864 | 1.9714 | 1.9714
WEATHER - LIGHTNING | 1.1928 | 1.8193 | 2.1462 | 1.2813 | 1.6959 | 1.6795 | 2.7416
WEATHER - TORNADO |  |  |  | 0.048997 | 0.0063986 | 1.3611 | 1.3547
WEATHER - UNKNOWN | 16.4276 | 10.2129 | 19.874 | 15.7262 | 13.5168 | 13.424 | 13.4588
WEATHER-FLOOD/SLIDE |  |  | 0.23359 | 0.00033407
Grand Total | 397.3944 | 402.1212 | 490.6166 | 331.7573 | 405.8467 | 407.8265 | 409.1732

## 12Mth Maj&Min Incl MED Pivot
OpUnit | AEP-KYP
Sum of SAIDI | Column Labels
Row Labels | 2020-12-31 | 2021-12-31 | 2022-12-31 | 2023-12-31 | 2024-12-31 | 2025-03-31 | 2025-05-31
OTHER | 4.4156 | 13.897 | 7.8087 | 3.2845 | 7.5281 | 6.6803 | 4.8129
ABNORMAL FEED | 3.5795 | 8.5466 |  |  |  | 0.045638 | 0.045638
ANIMAL - BIRD | 3.2704 | 0.35769 | 1.7676 | 1.444 | 0.16787 | 0.68679 | 0.67768
ANIMAL - NON BIRD | 1.7816 | 1.2154 | 1.0691 | 0.79709 | 1.928 | 0.90731 | 0.97782
ANIMAL - OTHER | 1.7989
ANIMAL BUS | 1.4449 | 1.1788 |  | 0.63053
ANIMAL BUSHING XFMR | 0.38064
BLAST/EXPLOSION (NON AEP) |  |  | 0.0038885 |  |  |  | 0.0014728
CONTAMINATION/FLASHOVER | 0.031301 | 0.33859 | 0.092268 | 0.23254
CORROSION | 0.66599 | 0.14213 | 0.17241 | 0.57437 | 0.44087 | 0.39196 | 0.071003
CUST. EQUIPMENT > 1 CUSTOMER | 0.72103 | 1.5541 | 0.64111 | 0.0088405 | 0.15055 | 0.15365 | 0.18116
EQUIPMENT FAILURE | 110.2858 | 111.6479 | 134.147 | 56.7239 | 147.8886 | 175.8721 | 172.1236
ERROR - FIELD | 0.15286 | 0.16334 | 0.34752 | 0.63863 | 0.23912 | 2.6287 | 3.6312
ERROR - OPERATIONS | 0.00069059 | 0.19765 | 0.030737 | 1.6994 | 4.4234 | 4.4199 | 4.8305
ERROR-FIELD | 0.0066757 | 0.0012011 | 0.021775 | 0.0016456 | 0.003682 | 0.003682 | 0.0027847
FACILITATION OF WORK | 3.2708 | 9.2372 | 5.7579 | 3.892 | 5.2136 | 4.4137 | 3.8029
FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 0.7811 | 2.7003 | 2.7687 | 7.0256 | 1.9756 | 3.0244 | 3.1869
FOREIGN OBJECT (NON ANIMAL) | 1.1333 | 1.7595 | 1.8368 | 0.37822 | 0.16307 | 0.176 | 0.26092
OTHER UTILITY | 0.44535 | 6.033 | 0.040298 | 0.098236 | 2.4401 | 2.1438 | 2.304
OVERLOAD | 0.078842 | 2.4887 | 0.13237 | 0.62088 | 0.37919 | 0.37689 | 0.37689
SCHEDULED COMPANY | 26.9794 | 44.7652 | 53.3408 | 30.4478 | 27.531 | 26.2536 | 27.4442
SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 1.6724 | 1.02 | 0.69643 | 1.1425 | 0.19569 | 0.32383 | 0.25246
TREE INSIDE ROW | 38.3709 | 101.7302 | 31.8485 | 18.8361 | 74.6439 | 87.8828 | 78.374
TREE OUT OF ROW | 738.7003 | 957.0163 | 775.3229 | 449.1147 | 705.4624 | 892.55 | 800.6066
TREE REMOVAL (NON AEP) | 5.8403 | 4.3962 | 4.6819 | 5.1412 | 1.8367 | 1.736 | 0.49472
UG CONST. /DIG-INS (NON AEP) | 0.80528 | 0.054469 | 0.074695 | 0.083543 | 0.026114 | 0.02422 | 0.02422
UNBALANCE | 0.3855 | 1.5873
UNKNOWN (NON WEATHER) | 25.5055 | 19.0479 | 24.4591 | 19.0458 | 22.6141 | 24.7892 | 25.8308
VANDALISM | 0.95623 | 0.33349 | 0.14582 | 0.017947 | 0.99164 | 1.185 | 2.1695
VEHICLE ACCIDENT (NON AEP) | 9.7662 | 11.4513 | 12.1853 | 10.2752 | 18.8157 | 18.9253 | 16.7463
VINE | 5.3806 | 1.7219 | 4.4654 | 2.0376 | 2.8393 | 2.7786 | 2.8821
WEATHER - FLOOD/SLIDE | 4.1596 | 57.4953 | 522.3939 | 0.21818 | 1.7509 | 88.3557 | 91.1591
WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 513.3498 | 0.73354 | 40.4327 | 62.9015 | 152.6256 | 156.498 | 112.6387
WEATHER - HURRICANE | 0.065448 |  | 0.00098137 |  | 12.6721 | 12.6721 | 12.9116
WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 13.538 | 1369.0325 | 8.9317 |  | 0.0094864 | 19.5178 | 19.5178
WEATHER - LIGHTNING | 2.1415 | 4.3875 | 4.7104 | 1.3364 | 2.4166 | 2.4123 | 2.9207
WEATHER - TORNADO | 0.025503 |  | 0.65236 | 0.048997 | 0.076875 | 1.4315 | 1.3547
WEATHER - UNKNOWN | 207.9615 | 102.8327 | 69.2668 | 39.6213 | 58.768 | 73.1067 | 66.096
WEATHER-FLOOD/SLIDE |  |  | 0.35998 | 0.00033407
Grand Total | 1729.8493 | 2839.0648 | 1710.6076 | 718.3197 | 1256.2175 | 1612.3673 | 1458.7108

## Figure MR-2
MINOR CAUSE NAME | 2024 CMI | % of 2024 CMI | Outage Cause | Percent of 2024 CMI | 2024 CMI
ABNORMAL FEED | 0 | 0% | Tree Outside of ROW | 55.39% | 36324190
ANIMAL - BIRD | 27128 | 0.04136% | Equipment Failure | 15.32% | 10044529 | 61666487
ANIMAL - NON BIRD | 309950 | 0.4726% | Scheduled Company | 6.77% | 4441685 | 65584414
ANIMAL - OTHER | 0 | 0% | Vehicle Accident (Non-AEP) | 4.64% | 3040593 | 3917927
ANIMAL BUS | 0 | 0% | Unknown (Non-weather) | 4.42% | 2895925
ANIMAL BUSHING XFMR | 0 | 0% | Weather - Unknown | 3.33% | 2184305
BLAST/EXPLOSION (NON AEP) | 0 | 0% | Tree Inside of ROW | 2.11% | 1381654
CONTAMINATION/FLASHOVER | 0 | 0% | Weather - High Winds (Exceeding 60mph) | 2.06% | 1353606
CORROSION | 66116 | 0.1008% | All Other Causes (31 unique causes) | 5.96% | 3917927
CUST. EQUIPMENT > 1 CUSTOMER | 16270 | 0.02481%
EQUIPMENT FAILURE | 10044529 | 15.32%
ERROR - FIELD | 38641 | 0.05892%
ERROR - OPERATIONS | 714819 | 1.09%
ERROR-FIELD | 595 | 0.0009072%
FACILITATION OF WORK | 593925 | 0.9056%
FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 319263 | 0.4868%
FOREIGN OBJECT (NON ANIMAL) | 26352 | 0.04018%
OTHER | 277484 | 0.4231%
OTHER UTILITY | 362673 | 0.553%
OVERLOAD | 61277 | 0.09343%
SCHEDULED COMPANY | 4441685 | 6.772%
SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 31624 | 0.04822%
TREE INSIDE ROW | 1381654 | 2.107%
TREE OUT OF ROW | 36324190 | 55.39%
TREE REMOVAL (NON AEP) | 234581 | 0.3577%
UG CONST. /DIG-INS (NON AEP) | 4220 | 0.006434%
UNBALANCE | 0 | 0%
UNKNOWN (NON WEATHER) | 2895925 | 4.416%
VANDALISM | 160248 | 0.2443%
VEHICLE ACCIDENT (NON AEP) | 3040593 | 4.636%
VINE | 203936 | 0.311%
WEATHER - FLOOD/SLIDE | 191583 | 0.2921%
WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 1353606 | 2.064%
WEATHER - HURRICANE | 615 | 0.0009377%
WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 1533 | 0.002337%
WEATHER - LIGHTNING | 274060 | 0.4179%
WEATHER - TORNADO | 1034 | 0.001577%
WEATHER - UNKNOWN | 2184305 | 3.331%
WEATHER-FLOOD/SLIDE | 0 | 0%
TOTAL CMI | 65584414

## Minor Cause MED Excluded Pivot
OpUnit | (All)
Sum of CMI | Column Labels
Row Labels | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | Grand Total
ABNORMAL FEED | 50488 |  |  |  |  | 14750 | 65238
ANIMAL - BIRD | 539875 | 58669 | 286376 | 233417 | 27128 | 220497 | 1365962
ANIMAL - NON BIRD | 290583 | 199355 | 158810 | 128333 | 309950 | 302621 | 1389652
ANIMAL - OTHER | 296961 | [5 empty] | 296961
ANIMAL BUS | 238526 | 193340 |  | 101920 |  |  | 533786
ANIMAL BUSHING XFMR | 62835 | [5 empty] | 62835
BLAST/EXPLOSION (NON AEP) |  |  | 630 |  |  | 238 | 868
CONTAMINATION/FLASHOVER | 5167 | 55536 | 14949 | 37589 |  |  | 113241
CORROSION | 4857 | 21269 | 27934 | 87628 | 66116 | 69687 | 277491
CUST. EQUIPMENT > 1 CUSTOMER | 104239 | 154845 | 65707 | 1429 | 16270 | 35966 | 378456
EQUIPMENT FAILURE | 14375575 | 11802883 | 17644837 | 7695056 | 10044529 | 24620697 | 86183577
ERROR - FIELD | 23953 | 26791 | 56304 | 90600 | 38641 | 787705 | 1023994
ERROR - OPERATIONS | 114 | 32419 | 4980 | 274699 | 714819 | 1494856 | 2521887
ERROR-FIELD | 1102 | 197 | 3528 | 266 | 595 | 1045 | 6733
FACILITATION OF WORK | 482611 | 411751 | 778300 | 627644 | 593925 | 829932 | 3724163
FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 128942 | 442903 | 431660 | 1135633 | 319263 | 1003740 | 3462141
FOREIGN OBJECT (NON ANIMAL) | 68712 | 43423 | 8008 | 55896 | 26352 | 64039 | 266430
OTHER | 711219 | 387571 | 606760 | 277851 | 277484 | 247938 | 2508823
OTHER UTILITY | 73517 | 989535 | 6529 | 15879 | 362673 | 658144 | 2106277
OVERLOAD | 13015 | 15583 | 21446 | 100360 | 61277 | 121810 | 333491
SCHEDULED COMPANY | 4442381 | 7103757 | 5665724 | 4916096 | 4441685 | 8422750 | 34992393
SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 237737 | 95248 | 112835 | 117961 | 31624 | 93127 | 688532
TREE INSIDE ROW | 2799778 | 1588134 | 2090125 | 1130606 | 1381654 | 2916004 | 11906301
TREE OUT OF ROW | 30255212 | 30474613 | 36499258 | 28697536 | 36324190 | 66892016 | 229142825
TREE REMOVAL (NON AEP) | 263255 | 672433 | 719539 | 336346 | 234581 | 295876 | 2522030
UG CONST. /DIG-INS (NON AEP) | 132933 | 8934 | 12102 | 13504 | 4220 | 7828 | 179521
UNBALANCE | 63638 | 87496 |  |  |  |  | 151134
UNKNOWN (NON WEATHER) | 2764524 | 2626390 | 3545659 | 2308103 | 2895925 | 6298377 | 20438978
VANDALISM | 157852 | 54700 | 23626 | 2901 | 160248 | 541439 | 940766
VEHICLE ACCIDENT (NON AEP) | 1605531 | 1786764 | 1732245 | 1660907 | 3040593 | 5751408 | 15577448
VINE | 212182 | 232858 | 629054 | 312135 | 203936 | 402639 | 1992804
WEATHER - FLOOD/SLIDE | 543619 | 1215368 | 2729006 | 35267 | 191583 | 1546720 | 6261563
WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 920007 | 114691 | 560024 | 473243 | 1353606 | 2248567 | 5670138
WEATHER - HURRICANE |  |  | 159 |  | 615 | 1230 | 2004
WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 821018 | 3085340 | 1447094 |  | 1533 | 637160 | 5992145
WEATHER - LIGHTNING | 196896 | 298396 | 347728 | 207116 | 274060 | 714438 | 2038634
WEATHER - TORNADO |  |  |  | 7920 | 1034 | 438862 | 447816
WEATHER - UNKNOWN | 2711819 | 1675122 | 3219945 | 2542021 | 2184305 | 4344243 | 16677455
WEATHER-FLOOD/SLIDE |  |  | 37846 | 54 |  |  | 37900
Grand Total | 65600673 | 65956314 | 79488727 | 53625916 | 65584414 | 132026349 | 462282393

## 12Mth Maj&Min Cause Excl MED
OpUnit | MthEndDt | Cause Grouping | Major Cause Code | Major Cause Name | Minor Cause Code | Minor Cause Name | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2020-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 165077 | 4 | 6 | 198 | 0.0011994 | 3.6347e-05 | 33
AEP-KYP | 2020-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 165077 | 361 | 3386 | 290385 | 1.7591 | 0.020512 | 85.7605
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AB | ANIMAL BUS | 165077 | 2 | 1325 | 238526 | 1.4449 | 0.0080266 | 180.0196
AEP-KYP | 2020-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 165077 | 84 | 4533 | 538658 | 3.2631 | 0.02746 | 118.8304
AEP-KYP | 2020-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 165077 | 6 | 20 | 1217 | 0.0073723 | 0.00012116 | 60.85
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | ABX | ANIMAL BUSHING XFMR | 165077 | 1 | 355 | 62835 | 0.38064 | 0.0021505 | 177
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 165077 | 4 | 101 | 41488 | 0.25133 | 0.00061184 | 410.7723
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AF | ABNORMAL FEED | 165077 | 1 | 45 | 9000 | 0.05452 | 0.0002726 | 200
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AO | ANIMAL - OTHER | 165077 | 1 | 1659 | 296961 | 1.7989 | 0.01005 | 179
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 165077 | 1 | 1 | 261 | 0.0015811 | 6.0578e-06 | 261
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 165077 | 32 | 484 | 103978 | 0.62988 | 0.002932 | 214.8306
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 165077 | 4 | 22 | 5167 | 0.031301 | 0.00013327 | 234.8636
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 165077 | 3 | 20 | 3633 | 0.022008 | 0.00012116 | 181.65
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 165077 | 3 | 4 | 1224 | 0.0074147 | 2.4231e-05 | 306
AEP-KYP | 2020-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 165077 | 201 | 567 | 66125 | 0.40057 | 0.0034348 | 116.6226
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 165077 | 8 | 3408 | 616243 | 3.7331 | 0.020645 | 180.8225
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 165077 | 15 | 10453 | 2210705 | 13.392 | 0.063322 | 211.49
AEP-KYP | 2020-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 165077 | 1298 | 68006 | 10051463 | 60.8895 | 0.41197 | 147.8026
AEP-KYP | 2020-12-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 165077 | 7 | 5619 | 1431039 | 8.6689 | 0.034039 | 254.6786
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 165077 | 2 | 10 | 1102 | 0.0066757 | 6.0578e-05 | 110.2
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 165077 | 19 | 595 | 23953 | 0.1451 | 0.0036044 | 40.2571
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 165077 | 2 | 2 | 114 | 0.00069059 | 1.2116e-05 | 57
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 165077 | 39 | 593 | 128942 | 0.7811 | 0.0035923 | 217.4401
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 165077 | 2 | 2 | 236 | 0.0014296 | 1.2116e-05 | 118
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 165077 | 17 | 536 | 68476 | 0.41481 | 0.003247 | 127.7537
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 165077 | 1 | 12 | 3850 | 0.023322 | 7.2693e-05 | 320.8333
AEP-KYP | 2020-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 165077 | 341 | 6378 | 478761 | 2.9002 | 0.038637 | 75.0644
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 165077 | 4 | 9 | 953 | 0.0057731 | 5.452e-05 | 105.8889
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | O | OTHER | 165077 | 2 | 3254 | 292860 | 1.7741 | 0.019712 | 90
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 165077 | 46 | 2373 | 410559 | 2.4871 | 0.014375 | 173.0126
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 165077 | 3 | 38 | 6847 | 0.041478 | 0.0002302 | 180.1842
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 165077 | 6 | 103 | 13015 | 0.078842 | 0.00062395 | 126.3592
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | OU | OTHER UTILITY | 165077 | 1 | 20 | 21080 | 0.1277 | 0.00012116 | 1054
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 165077 | 9 | 669 | 52150 | 0.31591 | 0.0040527 | 77.9522
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 165077 | 1 | 1 | 287 | 0.0017386 | 6.0578e-06 | 287
AEP-KYP | 2020-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 165077 | 1735 | 29263 | 4394518 | 26.621 | 0.17727 | 150.1732
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 165077 | 3 | 114 | 4157 | 0.025182 | 0.00069059 | 36.4649
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 165077 | 3 | 4006 | 43706 | 0.26476 | 0.024267 | 10.9101
AEP-KYP | 2020-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 165077 | 36 | 1836 | 237737 | 1.4402 | 0.011122 | 129.4864
AEP-KYP | 2020-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 165077 | 7 | 18 | 4160 | 0.0252 | 0.00010904 | 231.1111
AEP-KYP | 2020-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 165077 | 287 | 10549 | 2795618 | 16.9352 | 0.063904 | 265.0126
AEP-KYP | 2020-12-31 | T&G | ST | SUBTRANSMISSION LINE | TOR | TREE OUT OF ROW | 165077 | 1 | 490 | 126588 | 0.76684 | 0.0029683 | 258.3429
AEP-KYP | 2020-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 165077 | 2003 | 107305 | 30053870 | 182.0597 | 0.65003 | 280.0789
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 165077 | 1 | 19 | 33991 | 0.20591 | 0.0001151 | 1789
AEP-KYP | 2020-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 165077 | 39 | 97 | 40763 | 0.24693 | 0.0005876 | 420.2371
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 165077 | 5 | 12 | 1167 | 0.0070694 | 7.2693e-05 | 97.25
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 165077 | 77 | 1954 | 262088 | 1.5877 | 0.011837 | 134.129
AEP-KYP | 2020-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 165077 | 1444 | 27433 | 2687186 | 16.2784 | 0.16618 | 97.9545
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | U | UNKNOWN (NON WEATHER) | 165077 | 2 | 847 | 58616 | 0.35508 | 0.0051309 | 69.2043
AEP-KYP | 2020-12-31 | Unknown | DIS | DISTRIBUTION SOURCE | U | UNKNOWN (NON WEATHER) | 165077 | 1 | 6 | 696 | 0.0042162 | 3.6347e-05 | 116
AEP-KYP | 2020-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 165077 | 48 | 175 | 18026 | 0.1092 | 0.0010601 | 103.0057
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | UB | UNBALANCE | 165077 | 3 | 258 | 63638 | 0.3855 | 0.0015629 | 246.6589
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 165077 | 1 | 3 | 1407 | 0.0085233 | 1.8173e-05 | 469
AEP-KYP | 2020-12-31 | T&G | TS | TRANSMISSION STATION | UG | UG CONST. /DIG-INS (NON AEP) | 165077 | 1 | 486 | 128790 | 0.78018 | 0.0029441 | 265
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 165077 | 8 | 17 | 2736 | 0.016574 | 0.00010298 | 160.9412
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 165077 | 18 | 747 | 157852 | 0.95623 | 0.0045252 | 211.3146
AEP-KYP | 2020-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 165077 | 1 | 1 | 104 | 0.00063001 | 6.0578e-06 | 104
AEP-KYP | 2020-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 165077 | 86 | 12749 | 1604614 | 9.7204 | 0.077231 | 125.8619
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 165077 | 2 | 5 | 813 | 0.004925 | 3.0289e-05 | 162.6
AEP-KYP | 2020-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 165077 | 5 | 8 | 896 | 0.0054278 | 4.8462e-05 | 112
AEP-KYP | 2020-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 165077 | 300 | 1652 | 211286 | 1.2799 | 0.010007 | 127.8971
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 165077 | 27 | 2476 | 543619 | 3.2931 | 0.014999 | 219.5553
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 165077 | 40 | 904 | 723332 | 4.3818 | 0.0054762 | 800.146
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 165077 | 1 | 603 | 97686 | 0.59176 | 0.0036528 | 162
AEP-KYP | 2020-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 165077 | 1 | 4 | 588 | 0.003562 | 2.4231e-05 | 147
AEP-KYP | 2020-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 165077 | 51 | 1661 | 196308 | 1.1892 | 0.010062 | 118.1866
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WU | WEATHER - UNKNOWN | 165077 | 1 | 905 | 83260 | 0.50437 | 0.0054823 | 92
AEP-KYP | 2020-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 165077 | 297 | 9246 | 2624957 | 15.9014 | 0.05601 | 283.9019
AEP-KYP | 2020-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 165077 | 4 | 16 | 3602 | 0.02182 | 9.6924e-05 | 225.125
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 165077 | 95 | 1352 | 920007 | 5.5732 | 0.0081901 | 680.4786
AEP-KYP | 2021-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 164021 | 240 | 1901 | 198426 | 1.2098 | 0.01159 | 104.3798
AEP-KYP | 2021-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 164021 | 6 | 10 | 929 | 0.0056639 | 6.0968e-05 | 92.9
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AB | ANIMAL BUS | 164021 | 2 | 1106 | 193340 | 1.1788 | 0.006743 | 174.8101
AEP-KYP | 2021-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 164021 | 63 | 410 | 58568 | 0.35708 | 0.0024997 | 142.8488
AEP-KYP | 2021-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 164021 | 1 | 1 | 101 | 0.00061577 | 6.0968e-06 | 101
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 164021 | 13 | 83 | 9111 | 0.055548 | 0.00050603 | 109.7711
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 164021 | 5 | 13 | 2079 | 0.012675 | 7.9258e-05 | 159.9231
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 164021 | 1 | 785 | 143655 | 0.87583 | 0.004786 | 183
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 164021 | 4 | 198 | 54954 | 0.33504 | 0.0012072 | 277.5455
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | CF | CONTAMINATION/FLASHOVER | 164021 | 1 | 3 | 582 | 0.0035483 | 1.829e-05 | 194
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 164021 | 15 | 31 | 5559 | 0.033892 | 0.000189 | 179.3226
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 164021 | 14 | 103 | 15710 | 0.09578 | 0.00062797 | 152.5243
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 164021 | 10 | 5398 | 343608 | 2.0949 | 0.03291 | 63.6547
AEP-KYP | 2021-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 164021 | 161 | 444 | 85704 | 0.52252 | 0.002707 | 193.027
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 164021 | 7 | 4935 | 2468675 | 15.051 | 0.030088 | 500.2381
AEP-KYP | 2021-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 164021 | 1163 | 49351 | 8904896 | 54.2912 | 0.30088 | 180.44
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 164021 | 1 | 1 | 197 | 0.0012011 | 6.0968e-06 | 197
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 164021 | 14 | 81 | 26791 | 0.16334 | 0.00049384 | 330.7531
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 164021 | 9 | 126 | 32419 | 0.19765 | 0.00076819 | 257.2937
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 164021 | 2 | 1212 | 391563 | 2.3873 | 0.0073893 | 323.0718
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 164021 | 43 | 340 | 51340 | 0.31301 | 0.0020729 | 151
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 164021 | 23 | 625 | 40134 | 0.24469 | 0.0038105 | 64.2144
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 164021 | 2 | 4 | 3289 | 0.020052 | 2.4387e-05 | 822.25
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | FW | FACILITATION OF WORK | 164021 | 1 | 777 | 13986 | 0.08527 | 0.0047372 | 18
AEP-KYP | 2021-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 164021 | 317 | 4934 | 376925 | 2.298 | 0.030082 | 76.3934
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 164021 | 1 | 1042 | 20840 | 0.12706 | 0.0063528 | 20
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 164021 | 8 | 10 | 2834 | 0.017278 | 6.0968e-05 | 283.4
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 164021 | 60 | 1438 | 281174 | 1.7143 | 0.0087672 | 195.5313
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 164021 | 3 | 822 | 13257 | 0.080825 | 0.0050116 | 16.1277
AEP-KYP | 2021-12-31 | Remaining | DIS | DISTRIBUTION SOURCE | O | OTHER | 164021 | 1 | 1038 | 90306 | 0.55058 | 0.0063285 | 87
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 164021 | 8 | 86 | 15397 | 0.093872 | 0.00052432 | 179.0349
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | OL | OVERLOAD | 164021 | 1 | 2 | 186 | 0.001134 | 1.2194e-05 | 93
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 164021 | 10 | 314 | 76239 | 0.46481 | 0.0019144 | 242.7994
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | OU | OTHER UTILITY | 164021 | 3 | 3984 | 913054 | 5.5667 | 0.02429 | 229.1802
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 164021 | 2 | 2 | 242 | 0.0014754 | 1.2194e-05 | 121
AEP-KYP | 2021-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 164021 | 1802 | 51903 | 6647720 | 40.5297 | 0.31644 | 128.0797
AEP-KYP | 2021-12-31 | Scheduled | DIS | DISTRIBUTION SOURCE | SCO | SCHEDULED COMPANY | 164021 | 1 | 24 | 2040 | 0.012437 | 0.00014632 | 85
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 164021 | 9 | 8628 | 441259 | 2.6903 | 0.052603 | 51.1427
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 164021 | 6 | 59 | 12738 | 0.077661 | 0.00035971 | 215.8983
AEP-KYP | 2021-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 164021 | 26 | 457 | 95248 | 0.58071 | 0.0027862 | 208.4201
AEP-KYP | 2021-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 164021 | 7 | 17 | 2801 | 0.017077 | 0.00010365 | 164.7647
AEP-KYP | 2021-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 164021 | 242 | 7550 | 1585333 | 9.6654 | 0.046031 | 209.9779
AEP-KYP | 2021-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 164021 | 1837 | 96564 | 30402551 | 185.3577 | 0.58873 | 314.8435
AEP-KYP | 2021-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 164021 | 48 | 126 | 72062 | 0.43935 | 0.00076819 | 571.9206
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 164021 | 62 | 2766 | 672239 | 4.0985 | 0.016864 | 243.0365
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 164021 | 1 | 1 | 194 | 0.0011828 | 6.0968e-06 | 194
AEP-KYP | 2021-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 164021 | 47 | 105 | 9646 | 0.05881 | 0.00064016 | 91.8667
AEP-KYP | 2021-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 164021 | 1230 | 22242 | 2440740 | 14.8807 | 0.1356 | 109.7356
AEP-KYP | 2021-12-31 | Unknown | DIS | DISTRIBUTION SOURCE | U | UNKNOWN (NON WEATHER) | 164021 | 1 | 2 | 108 | 0.00065845 | 1.2194e-05 | 54
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 164021 | 2 | 2233 | 175896 | 1.0724 | 0.013614 | 78.7712
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | UB | UNBALANCE | 164021 | 1 | 10 | 2680 | 0.016339 | 6.0968e-05 | 268
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | UB | UNBALANCE | 164021 | 2 | 248 | 84816 | 0.5171 | 0.001512 | 342
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 164021 | 2 | 2 | 598 | 0.0036459 | 1.2194e-05 | 299
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 164021 | 5 | 70 | 8336 | 0.050823 | 0.00042677 | 119.0857
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 164021 | 21 | 131 | 54645 | 0.33316 | 0.00079868 | 417.1374
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | V | VANDALISM | 164021 | 1 | 1 | 55 | 0.00033532 | 6.0968e-06 | 55
AEP-KYP | 2021-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 164021 | 3 | 7 | 1799 | 0.010968 | 4.2677e-05 | 257
AEP-KYP | 2021-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 164021 | 81 | 9785 | 1784965 | 10.8825 | 0.059657 | 182.4185
AEP-KYP | 2021-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 164021 | 263 | 1447 | 230785 | 1.407 | 0.008822 | 159.4921
AEP-KYP | 2021-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 164021 | 6 | 23 | 2073 | 0.012639 | 0.00014023 | 90.1304
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | WFS | WEATHER - FLOOD/SLIDE | 164021 | 1 | 45 | 21285 | 0.12977 | 0.00027436 | 473
AEP-KYP | 2021-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 164021 | 29 | 1345 | 1194083 | 7.2801 | 0.0082002 | 887.7941
AEP-KYP | 2021-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 3 | 11 | 8101 | 0.04939 | 6.7065e-05 | 736.4545
AEP-KYP | 2021-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 160 | 2683 | 2975935 | 18.1436 | 0.016358 | 1109.1819
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 1 | 804 | 101304 | 0.61763 | 0.0049018 | 126
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WL | WEATHER - LIGHTNING | 164021 | 1 | 409 | 95706 | 0.5835 | 0.0024936 | 234
AEP-KYP | 2021-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 164021 | 2 | 11 | 1160 | 0.0070723 | 6.7065e-05 | 105.4545
AEP-KYP | 2021-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 164021 | 77 | 2017 | 201530 | 1.2287 | 0.012297 | 99.9157
AEP-KYP | 2021-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 164021 | 4 | 34 | 1677 | 0.010224 | 0.00020729 | 49.3235
AEP-KYP | 2021-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 164021 | 219 | 9402 | 1673445 | 10.2026 | 0.057322 | 177.9882
AEP-KYP | 2021-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 164021 | 17 | 973 | 114691 | 0.69925 | 0.0059322 | 117.8736
AEP-KYP | 2022-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 162018 | 5 | 9 | 713 | 0.0044007 | 5.5549e-05 | 79.2222
AEP-KYP | 2022-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 162018 | 260 | 1364 | 158097 | 0.9758 | 0.0084188 | 115.9069
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | ABI | ANIMAL - BIRD | 162018 | 2 | 1563 | 203705 | 1.2573 | 0.0096471 | 130.3295
AEP-KYP | 2022-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 162018 | 1 | 1 | 61 | 0.0003765 | 6.1722e-06 | 61
AEP-KYP | 2022-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 162018 | 55 | 654 | 82610 | 0.50988 | 0.0040366 | 126.315
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | BE | BLAST/EXPLOSION (NON AEP) | 162018 | 1 | 6 | 630 | 0.0038885 | 3.7033e-05 | 105
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 162018 | 2 | 5 | 620 | 0.0038267 | 3.0861e-05 | 124
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 162018 | 26 | 244 | 65087 | 0.40173 | 0.001506 | 266.75
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | CF | CONTAMINATION/FLASHOVER | 162018 | 2 | 37 | 1604 | 0.0099001 | 0.00022837 | 43.3514
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 162018 | 3 | 12 | 13345 | 0.082367 | 7.4066e-05 | 1112.0833
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 162018 | 24 | 61 | 8723 | 0.05384 | 0.0003765 | 143
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 162018 | 16 | 178 | 19211 | 0.11857 | 0.0010986 | 107.927
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 162018 | 6 | 5455 | 1277388 | 7.8842 | 0.033669 | 234.1683
AEP-KYP | 2022-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 162018 | 1387 | 75423 | 16127263 | 99.5399 | 0.46552 | 213.8242
AEP-KYP | 2022-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 162018 | 152 | 413 | 84120 | 0.5192 | 0.0025491 | 203.6804
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 162018 | 5 | 1281 | 156066 | 0.96326 | 0.0079065 | 121.8314
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 162018 | 1 | 3 | 3528 | 0.021775 | 1.8516e-05 | 1176
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 162018 | 19 | 981 | 42048 | 0.25953 | 0.0060549 | 42.8624
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | ERF | ERROR - FIELD | 162018 | 1 | 264 | 14256 | 0.08799 | 0.0016294 | 54
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 162018 | 2 | 298 | 4980 | 0.030737 | 0.0018393 | 16.7114
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 162018 | 64 | 4039 | 431660 | 2.6643 | 0.024929 | 106.873
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 162018 | 10 | 63 | 7944 | 0.049032 | 0.00038885 | 126.0952
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 162018 | 1 | 1 | 64 | 0.00039502 | 6.1722e-06 | 64
AEP-KYP | 2022-12-31 | T&G | TS | TRANSMISSION STATION | FW | FACILITATION OF WORK | 162018 | 3 | 1711 | 22747 | 0.1404 | 0.010561 | 13.2946
AEP-KYP | 2022-12-31 | Work Facilitation | PP | PARTIAL POWER | FW | FACILITATION OF WORK | 162018 | 1 | 5 | 380 | 0.0023454 | 3.0861e-05 | 76
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 162018 | 1 | 335 | 2345 | 0.014474 | 0.0020677 | 7
AEP-KYP | 2022-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 162018 | 369 | 9511 | 752828 | 4.6466 | 0.058703 | 79.1534
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 162018 | 3 | 2630 | 205625 | 1.2691 | 0.016233 | 78.1844
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 162018 | 4 | 10 | 3376 | 0.020837 | 6.1722e-05 | 337.6
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 162018 | 66 | 2727 | 397759 | 2.455 | 0.016831 | 145.8596
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 162018 | 13 | 141 | 20948 | 0.12929 | 0.00087027 | 148.5674
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | OL | OVERLOAD | 162018 | 2 | 8 | 498 | 0.0030737 | 4.9377e-05 | 62.25
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 162018 | 7 | 48 | 6229 | 0.038446 | 0.00029626 | 129.7708
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 162018 | 1 | 1 | 300 | 0.0018516 | 6.1722e-06 | 300
AEP-KYP | 2022-12-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 162018 | 3 | 1581 | 85655 | 0.52868 | 0.0097582 | 54.1777
AEP-KYP | 2022-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 162018 | 2012 | 36772 | 5501568 | 33.9565 | 0.22696 | 149.613
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 162018 | 4 | 208 | 33141 | 0.20455 | 0.0012838 | 159.3317
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 162018 | 1 | 1296 | 45360 | 0.27997 | 0.0079991 | 35
AEP-KYP | 2022-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 162018 | 17 | 1138 | 112835 | 0.69643 | 0.0070239 | 99.152
AEP-KYP | 2022-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 162018 | 8 | 16 | 4112 | 0.02538 | 9.8754e-05 | 257
AEP-KYP | 2022-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 162018 | 237 | 8114 | 2014685 | 12.4349 | 0.050081 | 248.2974
AEP-KYP | 2022-12-31 | TIR | DIS | DISTRIBUTION SOURCE | TIR | TREE INSIDE ROW | 162018 | 1 | 924 | 71328 | 0.44025 | 0.0057031 | 77.1948
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 162018 | 7 | 3253 | 473896 | 2.925 | 0.020078 | 145.6797
AEP-KYP | 2022-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 162018 | 47 | 85 | 27915 | 0.1723 | 0.00052463 | 328.4118
AEP-KYP | 2022-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 162018 | 2251 | 126105 | 35997447 | 222.1818 | 0.77834 | 285.4561
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 162018 | 54 | 3724 | 719479 | 4.4407 | 0.022985 | 193.2006
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 162018 | 1 | 1 | 60 | 0.00037033 | 6.1722e-06 | 60
AEP-KYP | 2022-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 162018 | 39 | 77 | 12532 | 0.077349 | 0.00047526 | 162.7532
AEP-KYP | 2022-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 162018 | 1254 | 24723 | 2847199 | 17.5733 | 0.15259 | 115.164
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | U | UNKNOWN (NON WEATHER) | 162018 | 1 | 1007 | 187193 | 1.1554 | 0.0062154 | 185.8918
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 162018 | 9 | 7424 | 498735 | 3.0783 | 0.045822 | 67.1787
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 162018 | 9 | 60 | 11939 | 0.073689 | 0.00037033 | 198.9833
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 162018 | 1 | 1 | 163 | 0.0010061 | 6.1722e-06 | 163
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 162018 | 22 | 61 | 23626 | 0.14582 | 0.0003765 | 387.3115
AEP-KYP | 2022-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 162018 | 3 | 6 | 620 | 0.0038267 | 3.7033e-05 | 103.3333
AEP-KYP | 2022-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 162018 | 100 | 11471 | 1731625 | 10.6879 | 0.070801 | 150.9568
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | VIN | VINE | 162018 | 3 | 2371 | 231789 | 1.4306 | 0.014634 | 97.76
AEP-KYP | 2022-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 162018 | 372 | 2135 | 391615 | 2.4171 | 0.013178 | 183.4262
AEP-KYP | 2022-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 162018 | 12 | 29 | 5650 | 0.034873 | 0.00017899 | 194.8276
AEP-KYP | 2022-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WFS | WEATHER-FLOOD/SLIDE | 162018 | 3 | 14 | 37846 | 0.23359 | 8.641e-05 | 2703.2857
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 162018 | 143 | 2424 | 2729006 | 16.8438 | 0.014961 | 1125.8276
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 162018 | 1 | 3 | 159 | 0.00098137 | 1.8516e-05 | 53
AEP-KYP | 2022-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 162018 | 3 | 18 | 4464 | 0.027552 | 0.0001111 | 248
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 162018 | 57 | 4265 | 1442630 | 8.9041 | 0.026324 | 338.2485
AEP-KYP | 2022-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 162018 | 81 | 2151 | 347156 | 2.1427 | 0.013276 | 161.3928
AEP-KYP | 2022-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 162018 | 1 | 2 | 572 | 0.0035305 | 1.2344e-05 | 286
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 162018 | 6 | 3393 | 330691 | 2.0411 | 0.020942 | 97.4627
AEP-KYP | 2022-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 162018 | 375 | 15001 | 2885208 | 17.8079 | 0.092588 | 192.3344
AEP-KYP | 2022-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 162018 | 9 | 25 | 4046 | 0.024973 | 0.0001543 | 161.84
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 162018 | 42 | 1522 | 560024 | 3.4566 | 0.009394 | 367.9527
AEP-KYP | 2023-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161642 | 2 | 6 | 754 | 0.0046646 | 3.7119e-05 | 125.6667
AEP-KYP | 2023-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161642 | 321 | 1329 | 127579 | 0.78927 | 0.0082219 | 95.9962
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AB | ANIMAL BUS | 161642 | 2 | 1040 | 101920 | 0.63053 | 0.006434 | 98
AEP-KYP | 2023-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161642 | 67 | 1713 | 232796 | 1.4402 | 0.010597 | 135.8996
AEP-KYP | 2023-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161642 | 6 | 8 | 621 | 0.0038418 | 4.9492e-05 | 77.625
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161642 | 4 | 11 | 319 | 0.0019735 | 6.8052e-05 | 29
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161642 | 1 | 3 | 1110 | 0.006867 | 1.856e-05 | 370
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 161642 | 2 | 216 | 37589 | 0.23254 | 0.0013363 | 174.0231
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161642 | 9 | 13 | 1457 | 0.0090137 | 8.0425e-05 | 112.0769
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161642 | 13 | 735 | 86171 | 0.5331 | 0.0045471 | 117.2395
AEP-KYP | 2023-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161642 | 1167 | 44354 | 6395450 | 39.5655 | 0.2744 | 144.1911
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161642 | 3 | 1929 | 254869 | 1.5767 | 0.011934 | 132.1249
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161642 | 3 | 1911 | 406418 | 2.5143 | 0.011822 | 212.6729
AEP-KYP | 2023-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161642 | 166 | 895 | 54140 | 0.33494 | 0.0055369 | 60.4916
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161642 | 11 | 8234 | 584179 | 3.614 | 0.05094 | 70.9472
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161642 | 14 | 448 | 46069 | 0.28501 | 0.0027716 | 102.8326
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | ERF | ERROR - FIELD | 161642 | 4 | 3112 | 44531 | 0.27549 | 0.019252 | 14.3094
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161642 | 2 | 2 | 266 | 0.0016456 | 1.2373e-05 | 133
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161642 | 3 | 3 | 151 | 0.00093416 | 1.856e-05 | 50.3333
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | ERO | ERROR - OPERATIONS | 161642 | 1 | 1644 | 274548 | 1.6985 | 0.010171 | 167
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161642 | 9 | 3186 | 346622 | 2.1444 | 0.01971 | 108.7954
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161642 | 44 | 4294 | 789011 | 4.8812 | 0.026565 | 183.7473
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161642 | 2 | 2 | 280 | 0.0017322 | 1.2373e-05 | 140
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161642 | 22 | 881 | 55616 | 0.34407 | 0.0054503 | 63.1283
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | FW | FACILITATION OF WORK | 161642 | 7 | 3061 | 70593 | 0.43672 | 0.018937 | 23.0621
AEP-KYP | 2023-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161642 | 506 | 6302 | 526781 | 3.2589 | 0.038987 | 83.5895
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | FW | FACILITATION OF WORK | 161642 | 1 | 2018 | 30270 | 0.18727 | 0.012484 | 15
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161642 | 37 | 1389 | 264521 | 1.6365 | 0.0085931 | 190.4399
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 161642 | 2 | 118 | 10842 | 0.067074 | 0.00073001 | 91.8814
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161642 | 5 | 13 | 2488 | 0.015392 | 8.0425e-05 | 191.3846
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161642 | 5 | 611 | 99892 | 0.61798 | 0.00378 | 163.4894
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | OL | OVERLOAD | 161642 | 3 | 6 | 468 | 0.0028953 | 3.7119e-05 | 78
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161642 | 1 | 1 | 129 | 0.00079806 | 6.1865e-06 | 129
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161642 | 8 | 246 | 15750 | 0.097438 | 0.0015219 | 64.0244
AEP-KYP | 2023-12-31 | T&G | ST | SUBTRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161642 | 3 | 12 | 632 | 0.0039099 | 7.4238e-05 | 52.6667
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161642 | 5 | 2853 | 191633 | 1.1855 | 0.01765 | 67.1689
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161642 | 4 | 1045 | 17302 | 0.10704 | 0.0064649 | 16.5569
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161642 | 3 | 3140 | 349252 | 2.1607 | 0.019426 | 111.2268
AEP-KYP | 2023-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161642 | 2279 | 35649 | 4357277 | 26.9563 | 0.22054 | 122.2272
AEP-KYP | 2023-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161642 | 25 | 390 | 117961 | 0.72977 | 0.0024127 | 302.4641
AEP-KYP | 2023-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161642 | 191 | 5366 | 1124541 | 6.957 | 0.033197 | 209.5678
AEP-KYP | 2023-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161642 | 10 | 36 | 6065 | 0.037521 | 0.00022271 | 168.4722
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161642 | 3 | 2247 | 189944 | 1.1751 | 0.013901 | 84.5323
AEP-KYP | 2023-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161642 | 1729 | 98653 | 28466781 | 176.1101 | 0.61032 | 288.5546
AEP-KYP | 2023-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161642 | 35 | 71 | 40811 | 0.25248 | 0.00043924 | 574.8028
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161642 | 46 | 2026 | 335488 | 2.0755 | 0.012534 | 165.5913
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161642 | 4 | 4 | 858 | 0.005308 | 2.4746e-05 | 214.5
AEP-KYP | 2023-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161642 | 32 | 83 | 7017 | 0.043411 | 0.00051348 | 84.5422
AEP-KYP | 2023-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161642 | 1107 | 18951 | 2230592 | 13.7996 | 0.11724 | 117.7031
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161642 | 1 | 379 | 70494 | 0.43611 | 0.0023447 | 186
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161642 | 4 | 30 | 13504 | 0.083543 | 0.0001856 | 450.1333
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161642 | 17 | 39 | 2901 | 0.017947 | 0.00024127 | 74.3846
AEP-KYP | 2023-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161642 | 96 | 11681 | 1660907 | 10.2752 | 0.072265 | 142.1888
AEP-KYP | 2023-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161642 | 295 | 1993 | 307826 | 1.9044 | 0.01233 | 154.4536
AEP-KYP | 2023-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161642 | 8 | 32 | 4309 | 0.026658 | 0.00019797 | 134.6562
AEP-KYP | 2023-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161642 | 2 | 57 | 35267 | 0.21818 | 0.00035263 | 618.7193
AEP-KYP | 2023-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WFS | WEATHER-FLOOD/SLIDE | 161642 | 1 | 1 | 54 | 0.00033407 | 6.1865e-06 | 54
AEP-KYP | 2023-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161642 | 65 | 2078 | 207116 | 1.2813 | 0.012856 | 99.6708
AEP-KYP | 2023-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161642 | 1 | 16 | 7920 | 0.048997 | 9.8984e-05 | 495
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 161642 | 11 | 9322 | 849703 | 5.2567 | 0.057671 | 91.1503
AEP-KYP | 2023-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161642 | 3 | 8 | 813 | 0.0050296 | 4.9492e-05 | 101.625
AEP-KYP | 2023-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161642 | 258 | 10160 | 1691505 | 10.4645 | 0.062855 | 166.4867
AEP-KYP | 2023-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161642 | 63 | 2606 | 472466 | 2.9229 | 0.016122 | 181.2993
AEP-KYP | 2023-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161642 | 1 | 1 | 777 | 0.0048069 | 6.1865e-06 | 777
AEP-KYP | 2024-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 2 | 2 | 319 | 0.001974 | 1.2376e-05 | 159.5
AEP-KYP | 2024-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 433 | 3239 | 309631 | 1.916 | 0.020043 | 95.5946
AEP-KYP | 2024-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 80 | 221 | 26327 | 0.16292 | 0.0013676 | 119.1267
AEP-KYP | 2024-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 6 | 10 | 801 | 0.0049567 | 6.1882e-05 | 80.1
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 18 | 125 | 16270 | 0.10068 | 0.00077352 | 130.16
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161599 | 7 | 39 | 8885 | 0.054982 | 0.00024134 | 227.8205
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 12 | 82 | 57231 | 0.35415 | 0.00050743 | 697.939
AEP-KYP | 2024-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 156 | 784 | 112641 | 0.69704 | 0.0048515 | 143.6747
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 3 | 3382 | 501928 | 3.106 | 0.020928 | 148.4116
AEP-KYP | 2024-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 1403 | 61447 | 8791670 | 54.4042 | 0.38024 | 143.0773
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 5 | 1308 | 0.0080941 | 3.0941e-05 | 261.6
AEP-KYP | 2024-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 8 | 5479 | 636982 | 3.9417 | 0.033905 | 116.2588
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 27 | 701 | 38641 | 0.23912 | 0.0043379 | 55.1227
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 4 | 5 | 595 | 0.003682 | 3.0941e-05 | 119
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 13 | 2209 | 341594 | 2.1138 | 0.01367 | 154.6374
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | ERO | ERROR - OPERATIONS | 161599 | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 42 | 1519 | 244274 | 1.5116 | 0.0093998 | 160.8124
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 2 | 929 | 19717 | 0.12201 | 0.0057488 | 21.2239
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 16 | 132 | 25500 | 0.1578 | 0.00081684 | 193.1818
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 1 | 6 | 852 | 0.0052723 | 3.7129e-05 | 142
AEP-KYP | 2024-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 375 | 8339 | 582907 | 3.6071 | 0.051603 | 69.9013
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 1 | 252 | 11018 | 0.068181 | 0.0015594 | 43.7222
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 4 | 5 | 2223 | 0.013756 | 3.0941e-05 | 444.6
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 31 | 2034 | 120495 | 0.74564 | 0.012587 | 59.2404
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 161599 | 3 | 1612 | 154766 | 0.95772 | 0.0099753 | 96.0087
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161599 | 6 | 557 | 61277 | 0.37919 | 0.0034468 | 110.0126
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 8 | 2835 | 361945 | 2.2398 | 0.017543 | 127.6702
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161599 | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2024-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 3 | 855 | 6982 | 0.043206 | 0.0052909 | 8.1661
AEP-KYP | 2024-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 2001 | 33367 | 4280204 | 26.4866 | 0.20648 | 128.2766
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 4 | 330 | 31959 | 0.19777 | 0.0020421 | 96.8455
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161599 | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2024-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 13 | 95 | 31624 | 0.19569 | 0.00058787 | 332.8842
AEP-KYP | 2024-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 9 | 25 | 5706 | 0.03531 | 0.0001547 | 228.24
AEP-KYP | 2024-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 195 | 6598 | 1375698 | 8.513 | 0.040829 | 208.5023
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | TIR | TREE INSIDE ROW | 161599 | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2024-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 2361 | 130360 | 33613694 | 208.0068 | 0.80669 | 257.8528
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 18 | 11259 | 2660779 | 16.4653 | 0.069672 | 236.3246
AEP-KYP | 2024-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 40 | 94 | 49717 | 0.30766 | 0.00058169 | 528.9043
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 40 | 1746 | 233670 | 1.446 | 0.010805 | 133.8316
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 3 | 7 | 911 | 0.0056374 | 4.3317e-05 | 130.1429
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 2626 | 52005 | 0.32182 | 0.01625 | 19.8039
AEP-KYP | 2024-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 1252 | 25409 | 2821234 | 17.4582 | 0.15723 | 111.0329
AEP-KYP | 2024-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 35 | 83 | 13782 | 0.085285 | 0.00051362 | 166.0482
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | U | UNKNOWN (NON WEATHER) | 161599 | 1 | 42 | 8904 | 0.055099 | 0.0002599 | 212
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 3 | 32 | 3556 | 0.022005 | 0.00019802 | 111.125
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 19 | 1060 | 156744 | 0.96996 | 0.0065594 | 147.8717
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | V | VANDALISM | 161599 | 1 | 12 | 3504 | 0.021683 | 7.4258e-05 | 292
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2024-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 5 | 586 | 0.0036263 | 3.0941e-05 | 117.2
AEP-KYP | 2024-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 93 | 12602 | 2687209 | 16.6289 | 0.077983 | 213.2367
AEP-KYP | 2024-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161599 | 4 | 14 | 2074 | 0.012834 | 8.6634e-05 | 148.1429
AEP-KYP | 2024-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 297 | 1401 | 201862 | 1.2492 | 0.0086696 | 144.0842
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 9 | 1432 | 191583 | 1.1855 | 0.0088614 | 133.787
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 3 | 7 | 615 | 0.0038057 | 4.3317e-05 | 87.8571
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 2 | 12 | 1533 | 0.0094864 | 7.4258e-05 | 127.75
AEP-KYP | 2024-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 67 | 1585 | 273349 | 1.6915 | 0.0098082 | 172.4599
AEP-KYP | 2024-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 3 | 8 | 711 | 0.0043998 | 4.9505e-05 | 88.875
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 11 | 1034 | 0.0063986 | 6.807e-05 | 94
AEP-KYP | 2024-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 279 | 13482 | 2152086 | 13.3174 | 0.083429 | 159.6266
AEP-KYP | 2024-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 3 | 3 | 341 | 0.0021102 | 1.8564e-05 | 113.6667
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 161599 | 1 | 414 | 31878 | 0.19727 | 0.0025619 | 77
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 94 | 2619 | 1350401 | 8.3565 | 0.016207 | 515.617
AEP-KYP | 2024-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 2 | 5 | 3205 | 0.019833 | 3.0941e-05 | 641
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 3 | 2229 | 49486 | 0.30623 | 0.013793 | 22.201
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 366 | 1482 | 156927 | 0.97109 | 0.0091708 | 105.8887
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 3 | 7 | 615 | 0.0038057 | 4.3317e-05 | 87.8571
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 208 | 5537 | 1466688 | 9.0761 | 0.034264 | 264.8886
AEP-KYP | 2025-03-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 2325 | 118881 | 31973301 | 197.8558 | 0.73565 | 268.9522
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 25 | 1220 | 191493 | 1.185 | 0.0075496 | 156.9615
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 2 | 255 | 11834 | 0.073231 | 0.001578 | 46.4078
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161599 | 5 | 17 | 5127 | 0.031727 | 0.0001052 | 301.5882
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 1 | 252 | 11018 | 0.068181 | 0.0015594 | 43.7222
AEP-KYP | 2025-05-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 1 | 1 | 46 | 0.00028466 | 6.1882e-06 | 46
AEP-KYP | 2025-03-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 5 | 11 | 2320 | 0.014357 | 6.807e-05 | 210.9091
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 1201 | 25072 | 3161080 | 19.5613 | 0.15515 | 126.0801
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 378 | 1378 | 144587 | 0.89473 | 0.0085273 | 104.9253
AEP-KYP | 2025-03-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 3 | 8 | 711 | 0.0043998 | 4.9505e-05 | 88.875
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 11 | 2749 | 342635 | 2.1203 | 0.017011 | 124.6399
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 8 | 5524 | 589332 | 3.6469 | 0.034183 | 106.6857
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 35 | 1480 | 312851 | 1.936 | 0.0091585 | 211.3858
AEP-KYP | 2025-05-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 2427 | 125176 | 31799861 | 196.7825 | 0.77461 | 254.0412
AEP-KYP | 2025-05-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161599 | 3 | 7 | 691 | 0.004276 | 4.3317e-05 | 98.7143
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 4 | 5 | 595 | 0.003682 | 3.0941e-05 | 119
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 2005 | 34312 | 4108293 | 25.4228 | 0.21233 | 119.7334
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 1235 | 24899 | 3015609 | 18.6611 | 0.15408 | 121.1137
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 4 | 185 | 26746 | 0.16551 | 0.0011448 | 144.573
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 11 | 75 | 49328 | 0.30525 | 0.00046411 | 657.7067
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | BE | BLAST/EXPLOSION (NON AEP) | 161599 | 1 | 2 | 238 | 0.0014728 | 1.2376e-05 | 119
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 291 | 1373 | 191948 | 1.1878 | 0.0084963 | 139.8019
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 61 | 2710 | 904771 | 5.5989 | 0.01677 | 333.8638
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 86 | 1239 | 108659 | 0.6724 | 0.0076671 | 87.699
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 3 | 8 | 1119 | 0.0069245 | 4.9505e-05 | 139.875
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-03-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161599 | 4 | 14 | 2074 | 0.012834 | 8.6634e-05 | 148.1429
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161599 | 7 | 39 | 8885 | 0.054982 | 0.00024134 | 227.8205
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 32 | 130 | 30800 | 0.1906 | 0.00080446 | 236.9231
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 202 | 5238 | 1436115 | 8.8869 | 0.032414 | 274.1724
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 2 | 31 | 3250 | 0.020112 | 0.00019183 | 104.8387
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 161599 | 1 | 414 | 31878 | 0.19727 | 0.0025619 | 77
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 3 | 183 | 26226 | 0.16229 | 0.0011324 | 143.3115
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 7 | 6868 | 1033042 | 6.3926 | 0.0425 | 150.4138
AEP-KYP | 2025-03-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 1446 | 63179 | 9392816 | 58.1242 | 0.39096 | 148.6699
AEP-KYP | 2025-03-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 10 | 27 | 6088 | 0.037674 | 0.00016708 | 225.4815
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 3 | 8 | 1119 | 0.0069245 | 4.9505e-05 | 139.875
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161599 | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2025-05-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 167 | 543 | 83154 | 0.51457 | 0.0033602 | 153.1381
AEP-KYP | 2025-03-31 | T&G | TS | TRANSMISSION STATION | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2025-05-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 1 | 1 | 85 | 0.00052599 | 6.1882e-06 | 85
AEP-KYP | 2025-03-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 71 | 1693 | 270693 | 1.6751 | 0.010477 | 159.8895
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 19 | 1134 | 160328 | 0.99213 | 0.0070174 | 141.3827
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 2 | 1038 | 219948 | 1.3611 | 0.0064233 | 211.896
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 3 | 7 | 615 | 0.0038057 | 4.3317e-05 | 87.8571
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 7 | 11 | 854 | 0.0052847 | 6.807e-05 | 77.6364
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 15 | 1387 | 318580 | 1.9714 | 0.008583 | 229.69
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 3 | 4 | 450 | 0.0027847 | 2.4753e-05 | 112.5
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | ERO | ERROR - OPERATIONS | 161599 | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2025-05-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 61 | 1774 | 262796 | 1.6262 | 0.010978 | 148.1375
AEP-KYP | 2025-05-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 84 | 12528 | 2344530 | 14.5083 | 0.077525 | 187.1432
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 4 | 3004 | 375830 | 2.3257 | 0.018589 | 125.1099
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 21 | 151 | 19195 | 0.11878 | 0.00093441 | 127.1192
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 10 | 2535 | 314053 | 1.9434 | 0.015687 | 123.8868
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 21 | 133 | 16771 | 0.10378 | 0.00082302 | 126.0977
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 2626 | 52005 | 0.32182 | 0.01625 | 19.8039
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 2 | 2 | 187 | 0.0011572 | 1.2376e-05 | 93.5
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 4 | 34 | 7622 | 0.047166 | 0.0002104 | 224.1765
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 72 | 3008 | 581562 | 3.5988 | 0.018614 | 193.3384
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 3 | 2169 | 386742 | 2.3932 | 0.013422 | 178.3043
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 320 | 13286 | 2134918 | 13.2112 | 0.082216 | 160.6893
AEP-KYP | 2025-05-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 1457 | 64216 | 10264670 | 63.5194 | 0.39738 | 159.846
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 18 | 11259 | 2660779 | 16.4653 | 0.069672 | 236.3246
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161599 | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2025-03-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 91 | 13243 | 2696642 | 16.6872 | 0.08195 | 203.6277
AEP-KYP | 2025-05-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 37 | 84 | 30881 | 0.1911 | 0.00051981 | 367.631
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 4 | 1916 | 127687 | 0.79015 | 0.011857 | 66.6425
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | TIR | TREE INSIDE ROW | 161599 | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 32 | 833 | 77373 | 0.4788 | 0.0051547 | 92.8848
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 15 | 1387 | 318580 | 1.9714 | 0.008583 | 229.69
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 31 | 1861 | 142679 | 0.88292 | 0.011516 | 76.6679
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 4 | 6 | 2637 | 0.016318 | 3.7129e-05 | 439.5
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 13 | 96 | 40797 | 0.25246 | 0.00059406 | 424.9688
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 4 | 4 | 689 | 0.0042636 | 2.4753e-05 | 172.25
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 3 | 3 | 418 | 0.0025866 | 1.8564e-05 | 139.3333
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 4 | 1916 | 127687 | 0.79015 | 0.011857 | 66.6425
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 2 | 31 | 3250 | 0.020112 | 0.00019183 | 104.8387
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161599 | 5 | 551 | 60905 | 0.37689 | 0.0034097 | 110.5354
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 11 | 34 | 6347 | 0.039276 | 0.0002104 | 186.6765
AEP-KYP | 2025-05-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 10 | 27 | 6613 | 0.040922 | 0.00016708 | 244.9259
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 3 | 7 | 911 | 0.0056374 | 4.3317e-05 | 130.1429
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 1399 | 283997 | 1.7574 | 0.0086572 | 203
AEP-KYP | 2025-05-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 5 | 11 | 2320 | 0.014357 | 6.807e-05 | 210.9091
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 18 | 122 | 24885 | 0.15399 | 0.00075496 | 203.9754
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 34 | 133 | 31261 | 0.19345 | 0.00082302 | 235.0451
AEP-KYP | 2025-03-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 2 | 5 | 3205 | 0.019833 | 3.0941e-05 | 641
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 20 | 16167 | 2481599 | 15.3565 | 0.10004 | 153.4978
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 14 | 117 | 52330 | 0.32383 | 0.00072401 | 447.265
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 339 | 15998 | 2172298 | 13.4425 | 0.098998 | 135.7856
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WL | WEATHER - LIGHTNING | 161599 | 1 | 1232 | 180192 | 1.1151 | 0.0076238 | 146.2597
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 43 | 1441 | 305785 | 1.8922 | 0.0089171 | 212.2033
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | ERO | ERROR - OPERATIONS | 161599 | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161599 | 5 | 551 | 60905 | 0.37689 | 0.0034097 | 110.5354
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 4 | 5 | 2002 | 0.012389 | 3.0941e-05 | 400.4
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 37 | 1758 | 217405 | 1.3453 | 0.010879 | 123.6661
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 88 | 1233 | 110130 | 0.6815 | 0.00763 | 89.3187
AEP-KYP | 2025-03-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 169 | 589 | 105345 | 0.65189 | 0.0036448 | 178.854
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 49 | 2180 | 332037 | 2.0547 | 0.01349 | 152.3106
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 36 | 2130 | 474854 | 2.9385 | 0.013181 | 222.9362
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 32 | 1694 | 101034 | 0.62521 | 0.010483 | 59.6423
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 7 | 11 | 854 | 0.0052847 | 6.807e-05 | 77.6364
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 1909 | 33660 | 3959937 | 24.5047 | 0.20829 | 117.6452
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 92 | 3153 | 1340506 | 8.2953 | 0.019511 | 425.1526
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 3 | 855 | 6982 | 0.043206 | 0.0052909 | 8.1661
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 83 | 3896 | 965158 | 5.9725 | 0.024109 | 247.7305
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 22 | 341 | 36916 | 0.22844 | 0.0021102 | 108.2581
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 269 | 1351 | 207926 | 1.2867 | 0.0083602 | 153.9053
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 13 | 2809 | 407379 | 2.5209 | 0.017383 | 145.0263
AEP-KYP | 2025-03-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 341 | 7117 | 453651 | 2.8073 | 0.044041 | 63.7419
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2025-05-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 303 | 6002 | 353429 | 2.1871 | 0.037141 | 58.8852
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | V | VANDALISM | 161599 | 1 | 869 | 189618 | 1.1734 | 0.0053775 | 218.2025
AEP-KYP | 2025-03-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 38 | 94 | 51364 | 0.31785 | 0.00058169 | 546.4255
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 11 | 2207 | 341027 | 2.1103 | 0.013657 | 154.5206
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 4 | 5 | 2223 | 0.013756 | 3.0941e-05 | 444.6
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161599 | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | TIR | TREE INSIDE ROW | 161599 | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2025-03-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161599 | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 3 | 5 | 2512 | 0.015545 | 3.0941e-05 | 502.4

## 12Mth Maj&Min Cause Incl MED
OpUnit | MthEndDt | Cause Grouping | Major Cause Code | Major Cause Name | Minor Cause Code | Minor Cause Name | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2020-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 165077 | 4 | 6 | 198 | 0.0011994 | 3.6347e-05 | 33
AEP-KYP | 2020-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 165077 | 363 | 3415 | 293904 | 1.7804 | 0.020687 | 86.0627
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AB | ANIMAL BUS | 165077 | 2 | 1325 | 238526 | 1.4449 | 0.0080266 | 180.0196
AEP-KYP | 2020-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 165077 | 84 | 4533 | 538658 | 3.2631 | 0.02746 | 118.8304
AEP-KYP | 2020-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 165077 | 6 | 20 | 1217 | 0.0073723 | 0.00012116 | 60.85
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | ABX | ANIMAL BUSHING XFMR | 165077 | 1 | 355 | 62835 | 0.38064 | 0.0021505 | 177
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | AF | ABNORMAL FEED | 165077 | 1 | 399 | 523887 | 3.1736 | 0.0024171 | 1313
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 165077 | 5 | 381 | 58008 | 0.3514 | 0.002308 | 152.252
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AF | ABNORMAL FEED | 165077 | 1 | 45 | 9000 | 0.05452 | 0.0002726 | 200
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AO | ANIMAL - OTHER | 165077 | 1 | 1659 | 296961 | 1.7989 | 0.01005 | 179
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 165077 | 1 | 1 | 261 | 0.0015811 | 6.0578e-06 | 261
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 165077 | 34 | 551 | 118765 | 0.71945 | 0.0033378 | 215.5445
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 165077 | 4 | 22 | 5167 | 0.031301 | 0.00013327 | 234.8636
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 165077 | 4 | 39 | 83053 | 0.50312 | 0.00023625 | 2129.5641
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 165077 | 4 | 10 | 26886 | 0.16287 | 6.0578e-05 | 2688.6
AEP-KYP | 2020-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 165077 | 206 | 583 | 101772 | 0.61651 | 0.0035317 | 174.566
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 165077 | 8 | 3408 | 616243 | 3.7331 | 0.020645 | 180.8225
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 165077 | 15 | 10453 | 2210705 | 13.392 | 0.063322 | 211.49
AEP-KYP | 2020-12-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 165077 | 7 | 5619 | 1431039 | 8.6689 | 0.034039 | 254.6786
AEP-KYP | 2020-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 165077 | 1362 | 74942 | 13845894 | 83.8754 | 0.45398 | 184.7548
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 165077 | 2 | 10 | 1102 | 0.0066757 | 6.0578e-05 | 110.2
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 165077 | 20 | 598 | 25234 | 0.15286 | 0.0036226 | 42.1973
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 165077 | 2 | 2 | 114 | 0.00069059 | 1.2116e-05 | 57
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 165077 | 39 | 593 | 128942 | 0.7811 | 0.0035923 | 217.4401
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 165077 | 3 | 3 | 579 | 0.0035075 | 1.8173e-05 | 193
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 165077 | 25 | 655 | 186505 | 1.1298 | 0.0039678 | 284.7405
AEP-KYP | 2020-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 165077 | 342 | 6392 | 536091 | 3.2475 | 0.038721 | 83.8691
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 165077 | 1 | 12 | 3850 | 0.023322 | 7.2693e-05 | 320.8333
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 165077 | 5 | 11 | 14559 | 0.088195 | 6.6636e-05 | 1323.5455
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 165077 | 47 | 2377 | 414647 | 2.5118 | 0.014399 | 174.4413
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | O | OTHER | 165077 | 2 | 3254 | 292860 | 1.7741 | 0.019712 | 90
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 165077 | 3 | 38 | 6847 | 0.041478 | 0.0002302 | 180.1842
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 165077 | 6 | 103 | 13015 | 0.078842 | 0.00062395 | 126.3592
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | OU | OTHER UTILITY | 165077 | 1 | 20 | 21080 | 0.1277 | 0.00012116 | 1054
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 165077 | 1 | 1 | 287 | 0.0017386 | 6.0578e-06 | 287
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 165077 | 9 | 669 | 52150 | 0.31591 | 0.0040527 | 77.9522
AEP-KYP | 2020-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 165077 | 1737 | 29282 | 4405813 | 26.6894 | 0.17738 | 150.4615
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 165077 | 3 | 114 | 4157 | 0.025182 | 0.00069059 | 36.4649
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 165077 | 3 | 4006 | 43706 | 0.26476 | 0.024267 | 10.9101
AEP-KYP | 2020-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 165077 | 37 | 1859 | 276078 | 1.6724 | 0.011261 | 148.5089
AEP-KYP | 2020-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 165077 | 345 | 14624 | 6329997 | 38.3457 | 0.088589 | 432.8499
AEP-KYP | 2020-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 165077 | 7 | 18 | 4160 | 0.0252 | 0.00010904 | 231.1111
AEP-KYP | 2020-12-31 | T&G | ST | SUBTRANSMISSION LINE | TOR | TREE OUT OF ROW | 165077 | 1 | 490 | 126588 | 0.76684 | 0.0029683 | 258.3429
AEP-KYP | 2020-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 165077 | 2694 | 151576 | 121723988 | 737.377 | 0.91821 | 803.0558
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 165077 | 1 | 19 | 33991 | 0.20591 | 0.0001151 | 1789
AEP-KYP | 2020-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 165077 | 46 | 125 | 57859 | 0.3505 | 0.00075722 | 462.872
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 165077 | 5 | 12 | 1167 | 0.0070694 | 7.2693e-05 | 97.25
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 165077 | 83 | 2087 | 962935 | 5.8332 | 0.012643 | 461.3967
AEP-KYP | 2020-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 165077 | 1473 | 28501 | 4132588 | 25.0343 | 0.17265 | 144.998
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | U | UNKNOWN (NON WEATHER) | 165077 | 2 | 847 | 58616 | 0.35508 | 0.0051309 | 69.2043
AEP-KYP | 2020-12-31 | Unknown | DIS | DISTRIBUTION SOURCE | U | UNKNOWN (NON WEATHER) | 165077 | 1 | 6 | 696 | 0.0042162 | 3.6347e-05 | 116
AEP-KYP | 2020-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 165077 | 49 | 176 | 18471 | 0.11189 | 0.0010662 | 104.9489
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | UB | UNBALANCE | 165077 | 3 | 258 | 63638 | 0.3855 | 0.0015629 | 246.6589
AEP-KYP | 2020-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 165077 | 1 | 3 | 1407 | 0.0085233 | 1.8173e-05 | 469
AEP-KYP | 2020-12-31 | T&G | TS | TRANSMISSION STATION | UG | UG CONST. /DIG-INS (NON AEP) | 165077 | 1 | 486 | 128790 | 0.78018 | 0.0029441 | 265
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 165077 | 8 | 17 | 2736 | 0.016574 | 0.00010298 | 160.9412
AEP-KYP | 2020-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 165077 | 18 | 747 | 157852 | 0.95623 | 0.0045252 | 211.3146
AEP-KYP | 2020-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 165077 | 1 | 1 | 104 | 0.00063001 | 6.0578e-06 | 104
AEP-KYP | 2020-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 165077 | 88 | 12785 | 1611250 | 9.7606 | 0.077449 | 126.0266
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 165077 | 2 | 5 | 813 | 0.004925 | 3.0289e-05 | 162.6
AEP-KYP | 2020-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 165077 | 305 | 3491 | 887311 | 5.3751 | 0.021148 | 254.171
AEP-KYP | 2020-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 165077 | 5 | 8 | 896 | 0.0054278 | 4.8462e-05 | 112
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 165077 | 30 | 2506 | 686655 | 4.1596 | 0.015181 | 274.0044
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 165077 | 1 | 2 | 10804 | 0.065448 | 1.2116e-05 | 5402
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 165077 | 59 | 1852 | 2137121 | 12.9462 | 0.011219 | 1153.953
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 165077 | 1 | 603 | 97686 | 0.59176 | 0.0036528 | 162
AEP-KYP | 2020-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 165077 | 1 | 4 | 588 | 0.003562 | 2.4231e-05 | 147
AEP-KYP | 2020-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 165077 | 55 | 1830 | 352921 | 2.1379 | 0.011086 | 192.853
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 165077 | 1 | 2 | 4210 | 0.025503 | 1.2116e-05 | 2105
AEP-KYP | 2020-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 165077 | 458 | 19572 | 30843451 | 186.8428 | 0.11856 | 1575.8967
AEP-KYP | 2020-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WU | WEATHER - UNKNOWN | 165077 | 3 | 1808 | 3481656 | 21.0911 | 0.010952 | 1925.6947
AEP-KYP | 2020-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 165077 | 5 | 17 | 4551 | 0.027569 | 0.00010298 | 267.7059
AEP-KYP | 2020-12-31 | T&G | ST | SUBTRANSMISSION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 165077 | 1 | 63 | 149436 | 0.90525 | 0.00038164 | 2372
AEP-KYP | 2020-12-31 | T&G | TL | TRANSMISSION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 165077 | 12 | 4522 | 7585395 | 45.9506 | 0.027393 | 1677.4425
AEP-KYP | 2020-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 165077 | 355 | 27317 | 77007410 | 466.4939 | 0.16548 | 2819.0288
AEP-KYP | 2021-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 164021 | 240 | 1901 | 198426 | 1.2098 | 0.01159 | 104.3798
AEP-KYP | 2021-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 164021 | 6 | 10 | 929 | 0.0056639 | 6.0968e-05 | 92.9
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AB | ANIMAL BUS | 164021 | 2 | 1106 | 193340 | 1.1788 | 0.006743 | 174.8101
AEP-KYP | 2021-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 164021 | 63 | 410 | 58568 | 0.35708 | 0.0024997 | 142.8488
AEP-KYP | 2021-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 164021 | 1 | 1 | 101 | 0.00061577 | 6.0968e-06 | 101
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 164021 | 3 | 1118 | 1401815 | 8.5466 | 0.0068162 | 1253.8596
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 164021 | 17 | 111 | 109164 | 0.66555 | 0.00067674 | 983.4595
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 164021 | 1 | 785 | 143655 | 0.87583 | 0.004786 | 183
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 164021 | 5 | 13 | 2079 | 0.012675 | 7.9258e-05 | 159.9231
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 164021 | 4 | 198 | 54954 | 0.33504 | 0.0012072 | 277.5455
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | CF | CONTAMINATION/FLASHOVER | 164021 | 1 | 3 | 582 | 0.0035483 | 1.829e-05 | 194
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 164021 | 16 | 32 | 6594 | 0.040202 | 0.0001951 | 206.0625
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 164021 | 15 | 104 | 16719 | 0.10193 | 0.00063407 | 160.7596
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 164021 | 10 | 5398 | 343608 | 2.0949 | 0.03291 | 63.6547
AEP-KYP | 2021-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 164021 | 171 | 505 | 208165 | 1.2691 | 0.0030789 | 412.2079
AEP-KYP | 2021-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 164021 | 1237 | 55642 | 11253592 | 68.6107 | 0.33924 | 202.25
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 164021 | 10 | 8196 | 6507232 | 39.6732 | 0.049969 | 793.9522
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 164021 | 1 | 1 | 197 | 0.0012011 | 6.0968e-06 | 197
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 164021 | 14 | 81 | 26791 | 0.16334 | 0.00049384 | 330.7531
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 164021 | 9 | 126 | 32419 | 0.19765 | 0.00076819 | 257.2937
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 164021 | 2 | 1212 | 391563 | 2.3873 | 0.0073893 | 323.0718
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 164021 | 43 | 340 | 51340 | 0.31301 | 0.0020729 | 151
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 164021 | 26 | 867 | 285298 | 1.7394 | 0.0052859 | 329.0634
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 164021 | 2 | 4 | 3289 | 0.020052 | 2.4387e-05 | 822.25
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | FW | FACILITATION OF WORK | 164021 | 1 | 777 | 13986 | 0.08527 | 0.0047372 | 18
AEP-KYP | 2021-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 164021 | 323 | 5663 | 1480275 | 9.0249 | 0.034526 | 261.3941
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 164021 | 1 | 1042 | 20840 | 0.12706 | 0.0063528 | 20
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 164021 | 9 | 13 | 14060 | 0.085721 | 7.9258e-05 | 1081.5385
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 164021 | 72 | 2376 | 2161773 | 13.1799 | 0.014486 | 909.8371
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 164021 | 3 | 822 | 13257 | 0.080825 | 0.0050116 | 16.1277
AEP-KYP | 2021-12-31 | Remaining | DIS | DISTRIBUTION SOURCE | O | OTHER | 164021 | 1 | 1038 | 90306 | 0.55058 | 0.0063285 | 87
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 164021 | 12 | 409 | 408015 | 2.4876 | 0.0024936 | 997.5917
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | OL | OVERLOAD | 164021 | 1 | 2 | 186 | 0.001134 | 1.2194e-05 | 93
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 164021 | 10 | 314 | 76239 | 0.46481 | 0.0019144 | 242.7994
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | OU | OTHER UTILITY | 164021 | 3 | 3984 | 913054 | 5.5667 | 0.02429 | 229.1802
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 164021 | 2 | 2 | 242 | 0.0014754 | 1.2194e-05 | 121
AEP-KYP | 2021-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 164021 | 1807 | 52648 | 6880868 | 41.9511 | 0.32098 | 130.6957
AEP-KYP | 2021-12-31 | Scheduled | DIS | DISTRIBUTION SOURCE | SCO | SCHEDULED COMPANY | 164021 | 1 | 24 | 2040 | 0.012437 | 0.00014632 | 85
AEP-KYP | 2021-12-31 | Scheduled | PP | PARTIAL POWER | SCO | SCHEDULED COMPANY | 164021 | 1 | 1 | 5524 | 0.033679 | 6.0968e-06 | 5524
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 164021 | 9 | 8628 | 441259 | 2.6903 | 0.052603 | 51.1427
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 164021 | 6 | 59 | 12738 | 0.077661 | 0.00035971 | 215.8983
AEP-KYP | 2021-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 164021 | 28 | 1082 | 167294 | 1.02 | 0.0065967 | 154.6155
AEP-KYP | 2021-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 164021 | 9 | 27 | 61705 | 0.3762 | 0.00016461 | 2285.3704
AEP-KYP | 2021-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 164021 | 349 | 12800 | 16624184 | 101.354 | 0.078039 | 1298.7644
AEP-KYP | 2021-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 164021 | 2591 | 134886 | 156068492 | 951.5153 | 0.82237 | 1157.04
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 164021 | 3 | 543 | 716065 | 4.3657 | 0.0033106 | 1318.7201
AEP-KYP | 2021-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 164021 | 56 | 153 | 186213 | 1.1353 | 0.00093281 | 1217.0784
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 164021 | 65 | 2909 | 720875 | 4.395 | 0.017736 | 247.8085
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 164021 | 1 | 1 | 194 | 0.0011828 | 6.0968e-06 | 194
AEP-KYP | 2021-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 164021 | 48 | 108 | 57520 | 0.35069 | 0.00065845 | 532.5926
AEP-KYP | 2021-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 164021 | 1255 | 22517 | 2890733 | 17.6242 | 0.13728 | 128.38
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 164021 | 2 | 2233 | 175896 | 1.0724 | 0.013614 | 78.7712
AEP-KYP | 2021-12-31 | Unknown | DIS | DISTRIBUTION SOURCE | U | UNKNOWN (NON WEATHER) | 164021 | 1 | 2 | 108 | 0.00065845 | 1.2194e-05 | 54
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | UB | UNBALANCE | 164021 | 1 | 10 | 2680 | 0.016339 | 6.0968e-05 | 268
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | UB | UNBALANCE | 164021 | 3 | 478 | 257674 | 1.571 | 0.0029143 | 539.0669
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 164021 | 2 | 2 | 598 | 0.0036459 | 1.2194e-05 | 299
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 164021 | 5 | 70 | 8336 | 0.050823 | 0.00042677 | 119.0857
AEP-KYP | 2021-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 164021 | 21 | 131 | 54645 | 0.33316 | 0.00079868 | 417.1374
AEP-KYP | 2021-12-31 | Remaining | PP | PARTIAL POWER | V | VANDALISM | 164021 | 1 | 1 | 55 | 0.00033532 | 6.0968e-06 | 55
AEP-KYP | 2021-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 164021 | 3 | 7 | 1799 | 0.010968 | 4.2677e-05 | 257
AEP-KYP | 2021-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 164021 | 85 | 10003 | 1876462 | 11.4404 | 0.060986 | 187.5899
AEP-KYP | 2021-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 164021 | 6 | 23 | 2073 | 0.012639 | 0.00014023 | 90.1304
AEP-KYP | 2021-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 164021 | 266 | 1459 | 280353 | 1.7093 | 0.0088952 | 192.1542
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WFS | WEATHER - FLOOD/SLIDE | 164021 | 1 | 928 | 64960 | 0.39605 | 0.0056578 | 70
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | WFS | WEATHER - FLOOD/SLIDE | 164021 | 1 | 45 | 21285 | 0.12977 | 0.00027436 | 473
AEP-KYP | 2021-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 164021 | 70 | 5760 | 9344192 | 56.9695 | 0.035117 | 1622.2556
AEP-KYP | 2021-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 6 | 19 | 101648 | 0.61973 | 0.00011584 | 5349.8947
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 5 | 2682 | 3100416 | 18.9026 | 0.016352 | 1156.0089
AEP-KYP | 2021-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 1146 | 57231 | 219030206 | 1335.379 | 0.34892 | 3827.1253
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 164021 | 1 | 557 | 2317815 | 14.1312 | 0.0033959 | 4161.2478
AEP-KYP | 2021-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WL | WEATHER - LIGHTNING | 164021 | 1 | 409 | 95706 | 0.5835 | 0.0024936 | 234
AEP-KYP | 2021-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 164021 | 80 | 2090 | 622773 | 3.7969 | 0.012742 | 297.9775
AEP-KYP | 2021-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 164021 | 2 | 11 | 1160 | 0.0070723 | 6.7065e-05 | 105.4545
AEP-KYP | 2021-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 164021 | 5 | 1434 | 994716 | 6.0646 | 0.0087428 | 693.6653
AEP-KYP | 2021-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 164021 | 277 | 15631 | 15870335 | 96.7579 | 0.095299 | 1015.3116
AEP-KYP | 2021-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 164021 | 4 | 34 | 1677 | 0.010224 | 0.00020729 | 49.3235
AEP-KYP | 2021-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 164021 | 18 | 976 | 120316 | 0.73354 | 0.0059505 | 123.2746
AEP-KYP | 2022-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 162018 | 5 | 9 | 713 | 0.0044007 | 5.5549e-05 | 79.2222
AEP-KYP | 2022-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 162018 | 265 | 1386 | 172493 | 1.0647 | 0.0085546 | 124.4538
AEP-KYP | 2022-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 162018 | 1 | 1 | 61 | 0.0003765 | 6.1722e-06 | 61
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | ABI | ANIMAL - BIRD | 162018 | 2 | 1563 | 203705 | 1.2573 | 0.0096471 | 130.3295
AEP-KYP | 2022-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 162018 | 55 | 654 | 82610 | 0.50988 | 0.0040366 | 126.315
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | BE | BLAST/EXPLOSION (NON AEP) | 162018 | 1 | 6 | 630 | 0.0038885 | 3.7033e-05 | 105
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 162018 | 30 | 271 | 103252 | 0.63729 | 0.0016727 | 381.0037
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 162018 | 2 | 5 | 620 | 0.0038267 | 3.0861e-05 | 124
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 162018 | 3 | 12 | 13345 | 0.082367 | 7.4066e-05 | 1112.0833
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | CF | CONTAMINATION/FLASHOVER | 162018 | 2 | 37 | 1604 | 0.0099001 | 0.00022837 | 43.3514
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 162018 | 24 | 61 | 8723 | 0.05384 | 0.0003765 | 143
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 162018 | 16 | 178 | 19211 | 0.11857 | 0.0010986 | 107.927
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 162018 | 6 | 5455 | 1277388 | 7.8842 | 0.033669 | 234.1683
AEP-KYP | 2022-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 162018 | 156 | 439 | 107935 | 0.66619 | 0.0027096 | 245.8656
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 162018 | 5 | 1281 | 156066 | 0.96326 | 0.0079065 | 121.8314
AEP-KYP | 2022-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 162018 | 1441 | 79615 | 20192835 | 124.6333 | 0.4914 | 253.631
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 162018 | 1 | 3 | 3528 | 0.021775 | 1.8516e-05 | 1176
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | ERF | ERROR - FIELD | 162018 | 1 | 264 | 14256 | 0.08799 | 0.0016294 | 54
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 162018 | 19 | 981 | 42048 | 0.25953 | 0.0060549 | 42.8624
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 162018 | 2 | 298 | 4980 | 0.030737 | 0.0018393 | 16.7114
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 162018 | 65 | 4049 | 448580 | 2.7687 | 0.024991 | 110.7878
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 162018 | 12 | 834 | 297534 | 1.8364 | 0.0051476 | 356.7554
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 162018 | 1 | 1 | 64 | 0.00039502 | 6.1722e-06 | 64
AEP-KYP | 2022-12-31 | T&G | TS | TRANSMISSION STATION | FW | FACILITATION OF WORK | 162018 | 3 | 1711 | 22747 | 0.1404 | 0.010561 | 13.2946
AEP-KYP | 2022-12-31 | Work Facilitation | PP | PARTIAL POWER | FW | FACILITATION OF WORK | 162018 | 1 | 5 | 380 | 0.0023454 | 3.0861e-05 | 76
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 162018 | 1 | 335 | 2345 | 0.014474 | 0.0020677 | 7
AEP-KYP | 2022-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 162018 | 374 | 9735 | 907414 | 5.6007 | 0.060086 | 93.2115
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 162018 | 4 | 10 | 3376 | 0.020837 | 6.1722e-05 | 337.6
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 162018 | 76 | 3116 | 1056144 | 6.5187 | 0.019232 | 338.9422
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 162018 | 3 | 2630 | 205625 | 1.2691 | 0.016233 | 78.1844
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 162018 | 13 | 141 | 20948 | 0.12929 | 0.00087027 | 148.5674
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | OL | OVERLOAD | 162018 | 2 | 8 | 498 | 0.0030737 | 4.9377e-05 | 62.25
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 162018 | 7 | 48 | 6229 | 0.038446 | 0.00029626 | 129.7708
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 162018 | 1 | 1 | 300 | 0.0018516 | 6.1722e-06 | 300
AEP-KYP | 2022-12-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 162018 | 3 | 1581 | 85655 | 0.52868 | 0.0097582 | 54.1777
AEP-KYP | 2022-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 162018 | 2022 | 37554 | 8478020 | 52.3276 | 0.23179 | 225.7554
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 162018 | 4 | 208 | 33141 | 0.20455 | 0.0012838 | 159.3317
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 162018 | 1 | 1296 | 45360 | 0.27997 | 0.0079991 | 35
AEP-KYP | 2022-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 162018 | 17 | 1138 | 112835 | 0.69643 | 0.0070239 | 99.152
AEP-KYP | 2022-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 162018 | 8 | 16 | 4112 | 0.02538 | 9.8754e-05 | 257
AEP-KYP | 2022-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 162018 | 295 | 10259 | 5084595 | 31.3829 | 0.06332 | 495.6229
AEP-KYP | 2022-12-31 | TIR | DIS | DISTRIBUTION SOURCE | TIR | TREE INSIDE ROW | 162018 | 1 | 924 | 71328 | 0.44025 | 0.0057031 | 77.1948
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 162018 | 7 | 3253 | 473896 | 2.925 | 0.020078 | 145.6797
AEP-KYP | 2022-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 162018 | 52 | 129 | 73814 | 0.45559 | 0.00079621 | 572.2016
AEP-KYP | 2022-12-31 | TOR | DIS | DISTRIBUTION SOURCE | TOR | TREE OUT OF ROW | 162018 | 1 | 71 | 656598 | 4.0526 | 0.00043822 | 9247.8592
AEP-KYP | 2022-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 162018 | 2791 | 175648 | 124411962 | 767.8898 | 1.0841 | 708.3028
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 162018 | 56 | 3781 | 758491 | 4.6815 | 0.023337 | 200.6059
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 162018 | 1 | 1 | 60 | 0.00037033 | 6.1722e-06 | 60
AEP-KYP | 2022-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 162018 | 40 | 80 | 12901 | 0.079627 | 0.00049377 | 161.2625
AEP-KYP | 2022-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 162018 | 1291 | 25492 | 3263983 | 20.1458 | 0.15734 | 128.0395
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | U | UNKNOWN (NON WEATHER) | 162018 | 1 | 1007 | 187193 | 1.1554 | 0.0062154 | 185.8918
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 162018 | 9 | 7424 | 498735 | 3.0783 | 0.045822 | 67.1787
AEP-KYP | 2022-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 162018 | 1 | 1 | 163 | 0.0010061 | 6.1722e-06 | 163
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 162018 | 9 | 60 | 11939 | 0.073689 | 0.00037033 | 198.9833
AEP-KYP | 2022-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 162018 | 22 | 61 | 23626 | 0.14582 | 0.0003765 | 387.3115
AEP-KYP | 2022-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 162018 | 3 | 6 | 620 | 0.0038267 | 3.7033e-05 | 103.3333
AEP-KYP | 2022-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 162018 | 102 | 11885 | 1973614 | 12.1814 | 0.073356 | 166.0592
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | VIN | VINE | 162018 | 3 | 2371 | 231789 | 1.4306 | 0.014634 | 97.76
AEP-KYP | 2022-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 162018 | 12 | 29 | 5650 | 0.034873 | 0.00017899 | 194.8276
AEP-KYP | 2022-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 162018 | 379 | 2190 | 486032 | 2.9999 | 0.013517 | 221.9324
AEP-KYP | 2022-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WFS | WEATHER - FLOOD/SLIDE | 162018 | 2 | 849 | 4114033 | 25.3924 | 0.0052402 | 4845.7397
AEP-KYP | 2022-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WFS | WEATHER-FLOOD/SLIDE | 162018 | 5 | 20 | 58324 | 0.35998 | 0.00012344 | 2916.2
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 162018 | 338 | 20288 | 80523175 | 497.0014 | 0.12522 | 3969.0051
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 162018 | 1 | 3 | 159 | 0.00098137 | 1.8516e-05 | 53
AEP-KYP | 2022-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 162018 | 3 | 18 | 4464 | 0.027552 | 0.0001111 | 248
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 162018 | 57 | 4265 | 1442630 | 8.9041 | 0.026324 | 338.2485
AEP-KYP | 2022-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 162018 | 99 | 2805 | 762598 | 4.7069 | 0.017313 | 271.8709
AEP-KYP | 2022-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 162018 | 1 | 2 | 572 | 0.0035305 | 1.2344e-05 | 286
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 162018 | 1 | 26 | 105694 | 0.65236 | 0.00016048 | 4065.1538
AEP-KYP | 2022-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 162018 | 7 | 3413 | 401631 | 2.4789 | 0.021066 | 117.6768
AEP-KYP | 2022-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 162018 | 9 | 25 | 4046 | 0.024973 | 0.0001543 | 161.84
AEP-KYP | 2022-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 162018 | 450 | 20159 | 10816786 | 66.7629 | 0.12442 | 536.5735
AEP-KYP | 2022-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 162018 | 106 | 6149 | 6550818 | 40.4327 | 0.037953 | 1065.3469
AEP-KYP | 2023-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161642 | 2 | 6 | 754 | 0.0046646 | 3.7119e-05 | 125.6667
AEP-KYP | 2023-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161642 | 322 | 1335 | 128089 | 0.79242 | 0.008259 | 95.9468
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | AB | ANIMAL BUS | 161642 | 2 | 1040 | 101920 | 0.63053 | 0.006434 | 98
AEP-KYP | 2023-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161642 | 67 | 1713 | 232796 | 1.4402 | 0.010597 | 135.8996
AEP-KYP | 2023-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161642 | 6 | 8 | 621 | 0.0038418 | 4.9492e-05 | 77.625
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161642 | 4 | 11 | 319 | 0.0019735 | 6.8052e-05 | 29
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161642 | 1 | 3 | 1110 | 0.006867 | 1.856e-05 | 370
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | CF | CONTAMINATION/FLASHOVER | 161642 | 2 | 216 | 37589 | 0.23254 | 0.0013363 | 174.0231
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161642 | 10 | 19 | 6671 | 0.04127 | 0.00011754 | 351.1053
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161642 | 13 | 735 | 86171 | 0.5331 | 0.0045471 | 117.2395
AEP-KYP | 2023-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161642 | 1217 | 47130 | 7413254 | 45.8622 | 0.29157 | 157.2937
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161642 | 3 | 1929 | 254869 | 1.5767 | 0.011934 | 132.1249
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161642 | 3 | 1911 | 406418 | 2.5143 | 0.011822 | 212.6729
AEP-KYP | 2023-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161642 | 171 | 906 | 55488 | 0.34328 | 0.005605 | 61.245
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161642 | 12 | 9299 | 1038934 | 6.4274 | 0.057528 | 111.7253
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161642 | 15 | 463 | 58699 | 0.36314 | 0.0028644 | 126.7797
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | ERF | ERROR - FIELD | 161642 | 4 | 3112 | 44531 | 0.27549 | 0.019252 | 14.3094
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161642 | 2 | 2 | 266 | 0.0016456 | 1.2373e-05 | 133
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | ERO | ERROR - OPERATIONS | 161642 | 1 | 1644 | 274548 | 1.6985 | 0.010171 | 167
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161642 | 3 | 3 | 151 | 0.00093416 | 1.856e-05 | 50.3333
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161642 | 9 | 3186 | 346622 | 2.1444 | 0.01971 | 108.7954
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161642 | 44 | 4294 | 789011 | 4.8812 | 0.026565 | 183.7473
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161642 | 2 | 2 | 280 | 0.0017322 | 1.2373e-05 | 140
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161642 | 23 | 884 | 60857 | 0.37649 | 0.0054689 | 68.8428
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | FW | FACILITATION OF WORK | 161642 | 7 | 3061 | 70593 | 0.43672 | 0.018937 | 23.0621
AEP-KYP | 2023-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161642 | 508 | 6304 | 528251 | 3.268 | 0.039 | 83.7962
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | FW | FACILITATION OF WORK | 161642 | 1 | 2018 | 30270 | 0.18727 | 0.012484 | 15
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161642 | 47 | 1520 | 395000 | 2.4437 | 0.0094035 | 259.8684
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 161642 | 3 | 595 | 133431 | 0.82547 | 0.003681 | 224.2538
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161642 | 5 | 13 | 2488 | 0.015392 | 8.0425e-05 | 191.3846
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161642 | 5 | 611 | 99892 | 0.61798 | 0.00378 | 163.4894
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | OL | OVERLOAD | 161642 | 3 | 6 | 468 | 0.0028953 | 3.7119e-05 | 78
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161642 | 1 | 1 | 129 | 0.00079806 | 6.1865e-06 | 129
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161642 | 8 | 246 | 15750 | 0.097438 | 0.0015219 | 64.0244
AEP-KYP | 2023-12-31 | T&G | ST | SUBTRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161642 | 3 | 12 | 632 | 0.0039099 | 7.4238e-05 | 52.6667
AEP-KYP | 2023-12-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161642 | 5 | 2853 | 191633 | 1.1855 | 0.01765 | 67.1689
AEP-KYP | 2023-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161642 | 2281 | 35730 | 4362821 | 26.9906 | 0.22104 | 122.1053
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161642 | 4 | 1045 | 17302 | 0.10704 | 0.0064649 | 16.5569
AEP-KYP | 2023-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161642 | 3 | 3140 | 349252 | 2.1607 | 0.019426 | 111.2268
AEP-KYP | 2023-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161642 | 26 | 877 | 184683 | 1.1425 | 0.0054256 | 210.5849
AEP-KYP | 2023-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161642 | 11 | 37 | 6728 | 0.041623 | 0.0002289 | 181.8378
AEP-KYP | 2023-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161642 | 227 | 7728 | 3037981 | 18.7945 | 0.047809 | 393.1135
AEP-KYP | 2023-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161642 | 44 | 83 | 57403 | 0.35512 | 0.00051348 | 691.6024
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161642 | 3 | 2247 | 189944 | 1.1751 | 0.013901 | 84.5323
AEP-KYP | 2023-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161642 | 2418 | 147673 | 72348449 | 447.5845 | 0.91358 | 489.9233
AEP-KYP | 2023-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161642 | 4 | 4 | 858 | 0.005308 | 2.4746e-05 | 214.5
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161642 | 51 | 2440 | 830174 | 5.1359 | 0.015095 | 340.2352
AEP-KYP | 2023-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161642 | 32 | 83 | 7017 | 0.043411 | 0.00051348 | 84.5422
AEP-KYP | 2023-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161642 | 1126 | 20025 | 3001098 | 18.5663 | 0.12388 | 149.8676
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161642 | 1 | 379 | 70494 | 0.43611 | 0.0023447 | 186
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161642 | 4 | 30 | 13504 | 0.083543 | 0.0001856 | 450.1333
AEP-KYP | 2023-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161642 | 17 | 39 | 2901 | 0.017947 | 0.00024127 | 74.3846
AEP-KYP | 2023-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161642 | 96 | 11681 | 1660907 | 10.2752 | 0.072265 | 142.1888
AEP-KYP | 2023-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161642 | 299 | 2018 | 325053 | 2.0109 | 0.012484 | 161.0768
AEP-KYP | 2023-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161642 | 8 | 32 | 4309 | 0.026658 | 0.00019797 | 134.6562
AEP-KYP | 2023-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161642 | 2 | 57 | 35267 | 0.21818 | 0.00035263 | 618.7193
AEP-KYP | 2023-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WFS | WEATHER-FLOOD/SLIDE | 161642 | 1 | 1 | 54 | 0.00033407 | 6.1865e-06 | 54
AEP-KYP | 2023-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161642 | 68 | 2215 | 216013 | 1.3364 | 0.013703 | 97.5228
AEP-KYP | 2023-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161642 | 1 | 16 | 7920 | 0.048997 | 9.8984e-05 | 495
AEP-KYP | 2023-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 161642 | 11 | 9322 | 849703 | 5.2567 | 0.057671 | 91.1503
AEP-KYP | 2023-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161642 | 345 | 19321 | 5552538 | 34.3508 | 0.11953 | 287.3836
AEP-KYP | 2023-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161642 | 4 | 9 | 2231 | 0.013802 | 5.5679e-05 | 247.8889
AEP-KYP | 2023-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161642 | 247 | 16045 | 10166754 | 62.8967 | 0.099263 | 633.64
AEP-KYP | 2023-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161642 | 1 | 1 | 777 | 0.0048069 | 6.1865e-06 | 777
AEP-KYP | 2024-12-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 2 | 2 | 319 | 0.001974 | 1.2376e-05 | 159.5
AEP-KYP | 2024-12-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 437 | 3263 | 311247 | 1.926 | 0.020192 | 95.3868
AEP-KYP | 2024-12-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 80 | 221 | 26327 | 0.16292 | 0.0013676 | 119.1267
AEP-KYP | 2024-12-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 6 | 10 | 801 | 0.0049567 | 6.1882e-05 | 80.1
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 20 | 128 | 24328 | 0.15055 | 0.00079208 | 190.0625
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161599 | 8 | 40 | 10555 | 0.065316 | 0.00024753 | 263.875
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 13 | 89 | 60689 | 0.37555 | 0.00055075 | 681.8989
AEP-KYP | 2024-12-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 158 | 787 | 121299 | 0.75062 | 0.0048701 | 154.1283
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 3 | 3382 | 501928 | 3.106 | 0.020928 | 148.4116
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 5 | 1308 | 0.0080941 | 3.0941e-05 | 261.6
AEP-KYP | 2024-12-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 1480 | 69308 | 22637125 | 140.0821 | 0.42889 | 326.6163
AEP-KYP | 2024-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 8 | 5479 | 636982 | 3.9417 | 0.033905 | 116.2588
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 27 | 701 | 38641 | 0.23912 | 0.0043379 | 55.1227
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 4 | 5 | 595 | 0.003682 | 3.0941e-05 | 119
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 13 | 2209 | 341594 | 2.1138 | 0.01367 | 154.6374
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | ERO | ERROR - OPERATIONS | 161599 | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 42 | 1519 | 244274 | 1.5116 | 0.0093998 | 160.8124
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 2 | 929 | 19717 | 0.12201 | 0.0057488 | 21.2239
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 16 | 132 | 25500 | 0.1578 | 0.00081684 | 193.1818
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 1 | 6 | 852 | 0.0052723 | 3.7129e-05 | 142
AEP-KYP | 2024-12-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 380 | 9979 | 831493 | 5.1454 | 0.061752 | 83.3243
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 1 | 252 | 11018 | 0.068181 | 0.0015594 | 43.7222
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 4 | 5 | 2223 | 0.013756 | 3.0941e-05 | 444.6
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 42 | 3372 | 1059541 | 6.5566 | 0.020866 | 314.2174
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | O | OTHER | 161599 | 3 | 1612 | 154766 | 0.95772 | 0.0099753 | 96.0087
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161599 | 6 | 557 | 61277 | 0.37919 | 0.0034468 | 110.0126
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 10 | 2868 | 393593 | 2.4356 | 0.017748 | 137.2361
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161599 | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2024-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 3 | 855 | 6982 | 0.043206 | 0.0052909 | 8.1661
AEP-KYP | 2024-12-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 2005 | 33379 | 4287494 | 26.5317 | 0.20655 | 128.4488
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 4 | 330 | 31959 | 0.19777 | 0.0020421 | 96.8455
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161599 | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2024-12-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 13 | 95 | 31624 | 0.19569 | 0.00058787 | 332.8842
AEP-KYP | 2024-12-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 12 | 32 | 16240 | 0.1005 | 0.00019802 | 507.5
AEP-KYP | 2024-12-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 303 | 12962 | 12045882 | 74.5418 | 0.080211 | 929.3228
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | TIR | TREE INSIDE ROW | 161599 | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2024-12-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 3228 | 180084 | 111256909 | 688.4752 | 1.1144 | 617.8056
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 19 | 11269 | 2662819 | 16.4779 | 0.069734 | 236.2959
AEP-KYP | 2024-12-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 44 | 101 | 82287 | 0.5092 | 0.000625 | 814.7228
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 43 | 1790 | 294812 | 1.8243 | 0.011077 | 164.6994
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 4 | 9 | 1995 | 0.012345 | 5.5693e-05 | 221.6667
AEP-KYP | 2024-12-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 1281 | 26958 | 3579718 | 22.1519 | 0.16682 | 132.7887
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 2626 | 52005 | 0.32182 | 0.01625 | 19.8039
AEP-KYP | 2024-12-31 | T&G | TS | TRANSMISSION STATION | U | UNKNOWN (NON WEATHER) | 161599 | 1 | 42 | 8904 | 0.055099 | 0.0002599 | 212
AEP-KYP | 2024-12-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 35 | 83 | 13782 | 0.085285 | 0.00051362 | 166.0482
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 3 | 32 | 3556 | 0.022005 | 0.00019802 | 111.125
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2024-12-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 19 | 1060 | 156744 | 0.96996 | 0.0065594 | 147.8717
AEP-KYP | 2024-12-31 | Remaining | PP | PARTIAL POWER | V | VANDALISM | 161599 | 1 | 12 | 3504 | 0.021683 | 7.4258e-05 | 292
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2024-12-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 5 | 586 | 0.0036263 | 3.0941e-05 | 117.2
AEP-KYP | 2024-12-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 93 | 12602 | 2687209 | 16.6289 | 0.077983 | 213.2367
AEP-KYP | 2024-12-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161599 | 4 | 14 | 2074 | 0.012834 | 8.6634e-05 | 148.1429
AEP-KYP | 2024-12-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 314 | 1524 | 456753 | 2.8265 | 0.0094308 | 299.7067
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 10 | 1487 | 282938 | 1.7509 | 0.0092018 | 190.2744
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | WH | WEATHER - HURRICANE | 161599 | 1 | 381 | 230886 | 1.4288 | 0.0023577 | 606
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 27 | 683 | 1816910 | 11.2433 | 0.0042265 | 2660.1903
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 2 | 12 | 1533 | 0.0094864 | 7.4258e-05 | 127.75
AEP-KYP | 2024-12-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 75 | 1746 | 389809 | 2.4122 | 0.010805 | 223.2583
AEP-KYP | 2024-12-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 3 | 8 | 711 | 0.0043998 | 4.9505e-05 | 88.875
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 2 | 18 | 12423 | 0.076875 | 0.00011139 | 690.1667
AEP-KYP | 2024-12-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 379 | 20120 | 9436499 | 58.3945 | 0.12451 | 469.0109
AEP-KYP | 2024-12-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 4 | 9 | 24461 | 0.15137 | 5.5693e-05 | 2717.8889
AEP-KYP | 2024-12-31 | Station - Distribution | DS | DISTRIBUTION STATION | WU | WEATHER - UNKNOWN | 161599 | 1 | 154 | 4004 | 0.024777 | 0.00095298 | 26
AEP-KYP | 2024-12-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 161599 | 1 | 414 | 31878 | 0.19727 | 0.0025619 | 77
AEP-KYP | 2024-12-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 303 | 23379 | 24619358 | 152.3485 | 0.14467 | 1053.0544
AEP-KYP | 2024-12-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 4 | 18 | 44780 | 0.27711 | 0.00011139 | 2487.7778
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 43 | 1441 | 305785 | 1.8922 | 0.0089171 | 212.2033
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 1399 | 283997 | 1.7574 | 0.0086572 | 203
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 4 | 5 | 2002 | 0.012389 | 3.0941e-05 | 400.4
AEP-KYP | 2025-05-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 5 | 11 | 2320 | 0.014357 | 6.807e-05 | 210.9091
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 34 | 133 | 31261 | 0.19345 | 0.00082302 | 235.0451
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 20 | 132 | 27322 | 0.16907 | 0.00081684 | 206.9848
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 37 | 2287 | 586795 | 3.6312 | 0.014152 | 256.5785
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 4 | 9 | 1995 | 0.012345 | 5.5693e-05 | 221.6667
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 40 | 1802 | 278547 | 1.7237 | 0.011151 | 154.5766
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 88 | 1233 | 110130 | 0.6815 | 0.00763 | 89.3187
AEP-KYP | 2025-03-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 4 | 18 | 44780 | 0.27711 | 0.00011139 | 2487.7778
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 49 | 2180 | 332037 | 2.0547 | 0.01349 | 152.3106
AEP-KYP | 2025-03-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 174 | 626 | 121837 | 0.75395 | 0.0038738 | 194.6278
AEP-KYP | 2025-05-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 1575 | 75344 | 24561562 | 151.9908 | 0.46624 | 325.9923
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 479 | 25267 | 10645709 | 65.8773 | 0.15636 | 421.3286
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WL | WEATHER - LIGHTNING | 161599 | 1 | 1232 | 180192 | 1.1151 | 0.0076238 | 146.2597
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 7 | 15 | 31342 | 0.19395 | 9.2822e-05 | 2089.4667
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 57 | 4815 | 3154051 | 19.5178 | 0.029796 | 655.0469
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 44 | 2914 | 775756 | 4.8005 | 0.018032 | 266.2169
AEP-KYP | 2025-05-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 13 | 34 | 17147 | 0.10611 | 0.0002104 | 504.3235
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 11 | 34 | 6347 | 0.039276 | 0.0002104 | 186.6765
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161599 | 5 | 551 | 60905 | 0.37689 | 0.0034097 | 110.5354
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | OL | OVERLOAD | 161599 | 5 | 551 | 60905 | 0.37689 | 0.0034097 | 110.5354
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 2 | 31 | 3250 | 0.020112 | 0.00019183 | 104.8387
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 3 | 3 | 418 | 0.0025866 | 1.8564e-05 | 139.3333
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 4 | 1916 | 127687 | 0.79015 | 0.011857 | 66.6425
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | WFS | WEATHER - FLOOD/SLIDE | 161599 | 2 | 698 | 968401 | 5.9926 | 0.0043193 | 1387.394
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | ERO | ERROR - OPERATIONS | 161599 | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 309 | 1497 | 446939 | 2.7657 | 0.0092637 | 298.5564
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 13 | 96 | 40797 | 0.25246 | 0.00059406 | 424.9688
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 45 | 3045 | 1077306 | 6.6665 | 0.018843 | 353.7951
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 7 | 11 | 854 | 0.0052847 | 6.807e-05 | 77.6364
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 4 | 4 | 689 | 0.0042636 | 2.4753e-05 | 172.25
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | WU | WEATHER - UNKNOWN | 161599 | 1 | 154 | 4004 | 0.024777 | 0.00095298 | 26
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 32 | 833 | 77373 | 0.4788 | 0.0051547 | 92.8848
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | TIR | TREE INSIDE ROW | 161599 | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 4 | 1916 | 127687 | 0.79015 | 0.011857 | 66.6425
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2025-03-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 92 | 13278 | 2703187 | 16.7277 | 0.082166 | 203.5839
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 20 | 16167 | 2481599 | 15.3565 | 0.10004 | 153.4978
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 14 | 117 | 52330 | 0.32383 | 0.00072401 | 447.265
AEP-KYP | 2025-05-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 43 | 102 | 45539 | 0.2818 | 0.00063119 | 446.4608
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161599 | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 28 | 696 | 1855611 | 11.4828 | 0.004307 | 2666.1078
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 19 | 11269 | 2662819 | 16.4779 | 0.069734 | 236.2959
AEP-KYP | 2025-05-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 2 | 3 | 492 | 0.0030446 | 1.8564e-05 | 164
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161599 | 5 | 17 | 5127 | 0.031727 | 0.0001052 | 301.5882
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 2 | 255 | 11834 | 0.073231 | 0.001578 | 46.4078
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 1 | 252 | 11018 | 0.068181 | 0.0015594 | 43.7222
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 57 | 4815 | 3154051 | 19.5178 | 0.029796 | 655.0469
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 7 | 11 | 854 | 0.0052847 | 6.807e-05 | 77.6364
AEP-KYP | 2025-03-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 5 | 11 | 2320 | 0.014357 | 6.807e-05 | 210.9091
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 1914 | 33729 | 4086813 | 25.2898 | 0.20872 | 121.1661
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 313 | 24361 | 25245135 | 156.2209 | 0.15075 | 1036.2931
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 86 | 1239 | 108659 | 0.6724 | 0.0076671 | 87.699
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 222 | 14714 | 18160648 | 112.3809 | 0.091053 | 1234.2428
AEP-KYP | 2025-03-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161599 | 4 | 14 | 2074 | 0.012834 | 8.6634e-05 | 148.1429
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 3 | 8 | 1119 | 0.0069245 | 4.9505e-05 | 139.875
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 1 | 2 | 664 | 0.0041089 | 1.2376e-05 | 332
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | CO | CORROSION | 161599 | 8 | 40 | 10555 | 0.065316 | 0.00024753 | 263.875
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 3 | 855 | 6982 | 0.043206 | 0.0052909 | 8.1661
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 350 | 13730 | 14184897 | 87.7784 | 0.084963 | 1033.1316
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 294 | 1477 | 465051 | 2.8778 | 0.0091399 | 314.8619
AEP-KYP | 2025-03-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 346 | 8757 | 702237 | 4.3456 | 0.05419 | 80.1915
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 167 | 10643 | 12505813 | 77.3879 | 0.065861 | 1175.0271
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 25 | 353 | 41045 | 0.25399 | 0.0021844 | 116.2748
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 7 | 6868 | 1033042 | 6.3926 | 0.0425 | 150.4138
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 32 | 130 | 30800 | 0.1906 | 0.00080446 | 236.9231
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 13 | 2809 | 407379 | 2.5209 | 0.017383 | 145.0263
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 3 | 183 | 26226 | 0.16229 | 0.0011324 | 143.3115
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | UG | UG CONST. /DIG-INS (NON AEP) | 161599 | 2 | 31 | 3250 | 0.020112 | 0.00019183 | 104.8387
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | WU | WEATHER - UNKNOWN | 161599 | 1 | 414 | 31878 | 0.19727 | 0.0025619 | 77
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 4 | 2270 | 352798 | 2.1832 | 0.014047 | 155.4176
AEP-KYP | 2025-03-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 1574 | 75288 | 26676538 | 165.0786 | 0.46589 | 354.3266
AEP-KYP | 2025-05-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 306 | 7191 | 602703 | 3.7296 | 0.044499 | 83.8135
AEP-KYP | 2025-03-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 13 | 34 | 16622 | 0.10286 | 0.0002104 | 488.8824
AEP-KYP | 2025-03-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 45 | 109 | 88668 | 0.54869 | 0.00067451 | 813.4679
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | ERO | ERROR - OPERATIONS | 161599 | 3 | 1810 | 373225 | 2.3096 | 0.011201 | 206.2017
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 3 | 4 | 450 | 0.0027847 | 2.4753e-05 | 112.5
AEP-KYP | 2025-05-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 85 | 12563 | 2351075 | 14.5488 | 0.077742 | 187.1428
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 382 | 1402 | 146203 | 0.90473 | 0.0086758 | 104.2817
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 1242 | 26292 | 4135812 | 25.5931 | 0.1627 | 157.3031
AEP-KYP | 2025-05-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 68 | 1825 | 291302 | 1.8026 | 0.011293 | 159.6175
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 24 | 157 | 29275 | 0.18116 | 0.00097154 | 186.465
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 12 | 2754 | 371595 | 2.2995 | 0.017042 | 134.9292
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 4 | 3004 | 375830 | 2.3257 | 0.018589 | 125.1099
AEP-KYP | 2025-03-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 3 | 8 | 711 | 0.0043998 | 4.9505e-05 | 88.875
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 8 | 5524 | 589332 | 3.6469 | 0.034183 | 106.6857
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | WU | WEATHER - UNKNOWN | 161599 | 1 | 154 | 4004 | 0.024777 | 0.00095298 | 26
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 12 | 2568 | 345701 | 2.1393 | 0.015891 | 134.6188
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 4 | 6 | 2573 | 0.015922 | 3.7129e-05 | 428.8333
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 36 | 1637 | 424792 | 2.6287 | 0.01013 | 259.4942
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 23 | 136 | 24829 | 0.15365 | 0.00084159 | 182.5662
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | WH | WEATHER - HURRICANE | 161599 | 1 | 381 | 230886 | 1.4288 | 0.0023577 | 606
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | OU | OTHER UTILITY | 161599 | 1 | 7 | 728 | 0.004505 | 4.3317e-05 | 104
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 11 | 2207 | 341027 | 2.1103 | 0.013657 | 154.5206
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 6 | 14 | 31217 | 0.19318 | 8.6634e-05 | 2229.7857
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 3 | 8 | 1119 | 0.0069245 | 4.9505e-05 | 139.875
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | TIR | TREE INSIDE ROW | 161599 | 1 | 2 | 250 | 0.001547 | 1.2376e-05 | 125
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 4 | 5 | 2223 | 0.013756 | 3.0941e-05 | 444.6
AEP-KYP | 2025-03-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161599 | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | SCO | SCHEDULED COMPANY | 161599 | 1 | 471 | 122540 | 0.7583 | 0.0029146 | 260.1699
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | V | VANDALISM | 161599 | 1 | 869 | 189618 | 1.1734 | 0.0053775 | 218.2025
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 369 | 1487 | 157325 | 0.97355 | 0.0092018 | 105.8003
AEP-KYP | 2025-05-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 176 | 600 | 101097 | 0.6256 | 0.0037129 | 168.495
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 27 | 683 | 1816910 | 11.2433 | 0.0042265 | 2660.1903
AEP-KYP | 2025-05-31 | Weather - Non Lightning | PP | PARTIAL POWER | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 3 | 14 | 41660 | 0.2578 | 8.6634e-05 | 2975.7143
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WH | WEATHER - HURRICANE | 161599 | 1 | 381 | 230886 | 1.4288 | 0.0023577 | 606
AEP-KYP | 2025-03-31 | T&G | TS | TRANSMISSION STATION | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 1 | 2632 | 55272 | 0.34203 | 0.016287 | 21
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 342 | 12687 | 12647757 | 78.2663 | 0.078509 | 996.9068
AEP-KYP | 2025-03-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 3603 | 194652 | 141483705 | 875.5234 | 1.2045 | 726.8546
AEP-KYP | 2025-03-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 81 | 1857 | 389109 | 2.4079 | 0.011491 | 209.5363
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 25 | 1220 | 191493 | 1.185 | 0.0075496 | 156.9615
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 20 | 1140 | 160976 | 0.99614 | 0.0070545 | 141.207
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 2626 | 52005 | 0.32182 | 0.01625 | 19.8039
AEP-KYP | 2025-05-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 3625 | 201937 | 128955859 | 797.9991 | 1.2496 | 638.5945
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 4 | 34 | 7622 | 0.047166 | 0.0002104 | 224.1765
AEP-KYP | 2025-05-31 | TIR | PP | PARTIAL POWER | VIN | VINE | 161599 | 3 | 7 | 691 | 0.004276 | 4.3317e-05 | 98.7143
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 151 | 9638 | 12052796 | 74.5846 | 0.059641 | 1250.5495
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 3 | 781 | 1257000 | 7.7785 | 0.004833 | 1609.475
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 4 | 5 | 595 | 0.003682 | 3.0941e-05 | 119
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 3 | 2169 | 386742 | 2.3932 | 0.013422 | 178.3043
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 463 | 23149 | 11746864 | 72.6914 | 0.14325 | 507.4459
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 2010 | 34396 | 4236182 | 26.2142 | 0.21285 | 123.1591
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 3 | 2229 | 49486 | 0.30623 | 0.013793 | 22.201
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 1277 | 26753 | 3922637 | 24.2739 | 0.16555 | 146.6242
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 12 | 82 | 52786 | 0.32665 | 0.00050743 | 643.7317
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 4 | 185 | 26746 | 0.16551 | 0.0011448 | 144.573
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 3 | 781 | 1257000 | 7.7785 | 0.004833 | 1609.475
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | WFS | WEATHER - FLOOD/SLIDE | 161599 | 2 | 698 | 968401 | 5.9926 | 0.0043193 | 1387.394
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | BE | BLAST/EXPLOSION (NON AEP) | 161599 | 1 | 2 | 238 | 0.0014728 | 1.2376e-05 | 119
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 3 | 1045 | 231337 | 1.4315 | 0.0064666 | 221.3751

## YTD Maj&Min Cause Excl MED
OpUnit | MthEndDt | Cause Grouping | Major Cause Code | Major Cause Name | Minor Cause Code | Minor Cause Name | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2025-03-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 58 | 296 | 44257 | 0.27387 | 0.0018317 | 149.5169
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 163 | 3819 | 628593 | 3.8898 | 0.023633 | 164.5962
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 415 | 4150 | 0.025681 | 0.0025681 | 10
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 26 | 128 | 9298 | 0.057537 | 0.00079208 | 72.6406
AEP-KYP | 2025-03-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 1 | 6 | 1734 | 0.01073 | 3.7129e-05 | 289
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 1 | 1 | 53 | 0.00032797 | 6.1882e-06 | 53
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 2 | 24 | 20748 | 0.12839 | 0.00014852 | 864.5
AEP-KYP | 2025-03-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 17 | 1973 | 173148 | 1.0715 | 0.012209 | 87.7587
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 15 | 1387 | 318580 | 1.9714 | 0.008583 | 229.69
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 18 | 372 | 133994 | 0.82918 | 0.002302 | 360.1989
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 2 | 2 | 267 | 0.0016522 | 1.2376e-05 | 133.5
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 29 | 1746 | 757803 | 4.6894 | 0.010805 | 434.0223
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 510 | 7891 | 745094 | 4.6108 | 0.048831 | 94.4233
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 5 | 317 | 32327 | 0.20004 | 0.0019616 | 101.9779
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 11 | 34 | 2357 | 0.014585 | 0.0002104 | 69.3235
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 2 | 987 | 107970 | 0.66814 | 0.0061077 | 109.3921
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 1 | 1 | 99 | 0.00061263 | 6.1882e-06 | 99
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 10 | 1017 | 84086 | 0.52034 | 0.0062934 | 82.6804
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 7 | 81 | 10661 | 0.065972 | 0.00050124 | 131.6173
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 67 | 19146 | 0.11848 | 0.00041461 | 285.7612
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 6 | 8 | 927 | 0.0057364 | 4.9505e-05 | 115.875
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 36 | 762 | 241587 | 1.495 | 0.0047154 | 317.0433
AEP-KYP | 2025-03-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 50 | 1193 | 124556 | 0.77077 | 0.0073825 | 104.4057
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 4 | 3486 | 531114 | 3.2866 | 0.021572 | 152.3563
AEP-KYP | 2025-03-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 395 | 16868 | 2284310 | 14.1357 | 0.10438 | 135.4227
AEP-KYP | 2025-03-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 7 | 14 | 5438 | 0.033651 | 8.6634e-05 | 388.4286
AEP-KYP | 2025-03-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 2 | 4 | 918 | 0.0056807 | 2.4753e-05 | 229.5
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 2 | 4 | 2470 | 0.015285 | 2.4753e-05 | 617.5
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 1 | 1 | 14 | 8.6634e-05 | 6.1882e-06 | 14
AEP-KYP | 2025-03-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 465 | 23336 | 6481437 | 40.1082 | 0.14441 | 277.7441
AEP-KYP | 2025-03-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 15 | 493 | 46695 | 0.28896 | 0.0030508 | 94.716
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 7 | 162 | 34895 | 0.21594 | 0.0010025 | 215.4012
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 8 | 22 | 2662 | 0.016473 | 0.00013614 | 121
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 3 | 6 | 456 | 0.0028218 | 3.7129e-05 | 76
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 66 | 2162 | 527617 | 3.265 | 0.013379 | 244.0412
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 112 | 3463 | 571559 | 3.5369 | 0.02143 | 165.0474
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 11 | 785 | 274669 | 1.6997 | 0.0048577 | 349.8968
AEP-KYP | 2025-05-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 628 | 29178 | 4670466 | 28.9016 | 0.18056 | 160.0681
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 1 | 2 | 520 | 0.0032178 | 1.2376e-05 | 260
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 1 | 1 | 74 | 0.00045792 | 6.1882e-06 | 74
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 15 | 1387 | 318580 | 1.9714 | 0.008583 | 229.69
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 1 | 3 | 816 | 0.0050495 | 1.8564e-05 | 272
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 17 | 12785 | 1979671 | 12.2505 | 0.079116 | 154.8433
AEP-KYP | 2025-05-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 12 | 19 | 6378 | 0.039468 | 0.00011757 | 335.6842
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 2 | 987 | 107970 | 0.66814 | 0.0061077 | 109.3921
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 13 | 482 | 38890 | 0.24066 | 0.0029827 | 80.6846
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 179 | 6906 | 891874 | 5.5191 | 0.042735 | 129.1448
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WL | WEATHER - LIGHTNING | 161599 | 1 | 1232 | 180192 | 1.1151 | 0.0076238 | 146.2597
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 3 | 5 | 2595 | 0.016058 | 3.0941e-05 | 519
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 9 | 526 | 80083 | 0.49557 | 0.003255 | 152.249
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 35 | 1799 | 786866 | 4.8693 | 0.011132 | 437.3908
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 20 | 1058 | 87361 | 0.5406 | 0.0065471 | 82.5718
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 2 | 2 | 370 | 0.0022896 | 1.2376e-05 | 185
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 5 | 38 | 23084 | 0.14285 | 0.00023515 | 607.4737
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 1 | 1 | 53 | 0.00032797 | 6.1882e-06 | 53
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 1 | 1 | 67 | 0.00041461 | 6.1882e-06 | 67
AEP-KYP | 2025-05-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 5 | 9 | 1832 | 0.011337 | 5.5693e-05 | 203.5556
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 1399 | 283997 | 1.7574 | 0.0086572 | 203
AEP-KYP | 2025-05-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 1 | 6 | 1734 | 0.01073 | 3.7129e-05 | 289
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 1 | 1 | 94 | 0.00058169 | 6.1882e-06 | 94
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 15 | 1459 | 438095 | 2.711 | 0.0090285 | 300.2707
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 31 | 1259 | 180010 | 1.1139 | 0.0077909 | 142.9786
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 13 | 272 | 23934 | 0.14811 | 0.0016832 | 87.9926
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 81 | 3858 | 955964 | 5.9157 | 0.023874 | 247.7875
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 63 | 559 | 87466 | 0.54125 | 0.0034592 | 156.4687
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 8 | 78 | 19768 | 0.12233 | 0.00048268 | 253.4359
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 4 | 606 | 67824 | 0.41971 | 0.00375 | 111.9208
AEP-KYP | 2025-05-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 75 | 1557 | 140162 | 0.86734 | 0.009635 | 90.0206
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 2 | 2 | 267 | 0.0016522 | 1.2376e-05 | 133.5
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | V | VANDALISM | 161599 | 1 | 869 | 189618 | 1.1734 | 0.0053775 | 218.2025
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 106 | 519 | 49391 | 0.30564 | 0.0032117 | 95.1657
AEP-KYP | 2025-05-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 83 | 340 | 51073 | 0.31605 | 0.002104 | 150.2147
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 72 | 1953 | 575859 | 3.5635 | 0.012085 | 294.8587
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 7 | 162 | 34895 | 0.21594 | 0.0010025 | 215.4012
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 11 | 47 | 5544 | 0.034307 | 0.00029084 | 117.9574
AEP-KYP | 2025-05-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 29 | 3109 | 323740 | 2.0034 | 0.019239 | 104.1299
AEP-KYP | 2025-05-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 26 | 676 | 75568 | 0.46763 | 0.0041832 | 111.787
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 5 | 258 | 35992 | 0.22272 | 0.0015965 | 139.5039
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 1 | 565 | 58760 | 0.36362 | 0.0034963 | 104
AEP-KYP | 2025-05-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 1036 | 50843 | 14174439 | 87.7137 | 0.31462 | 278.7884
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 20 | 7314 | 0.04526 | 0.00012376 | 365.7
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 415 | 4150 | 0.025681 | 0.0025681 | 10
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 883 | 13017 | 1567562 | 9.7003 | 0.080551 | 120.4242
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 2 | 1997 | 47746 | 0.29546 | 0.012358 | 23.9089
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | BE | BLAST/EXPLOSION (NON AEP) | 161599 | 1 | 2 | 238 | 0.0014728 | 1.2376e-05 | 119
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 354 | 8401 | 1202937 | 7.444 | 0.051987 | 143.1897

## YTD Maj&Min Cause Incl MED
OpUnit | MthEndDt | Cause Grouping | Major Cause Code | Major Cause Name | Minor Cause Code | Minor Cause Name | Served | Outages | CI | CMI | SAIDI | SAIFI | CAIDI
AEP-KYP | 2025-03-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 61 | 330 | 52091 | 0.32235 | 0.0020421 | 157.8515
AEP-KYP | 2025-03-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 1 | 6 | 1734 | 0.01073 | 3.7129e-05 | 289
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 1 | 1 | 53 | 0.00032797 | 6.1882e-06 | 53
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 2 | 24 | 20748 | 0.12839 | 0.00014852 | 864.5
AEP-KYP | 2025-03-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 18 | 2008 | 179693 | 1.112 | 0.012426 | 89.4885
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 57 | 4815 | 3154051 | 19.5178 | 0.029796 | 655.0469
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 18 | 372 | 133994 | 0.82918 | 0.002302 | 360.1989
AEP-KYP | 2025-03-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 511 | 7948 | 864680 | 5.3508 | 0.049183 | 108.7921
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 7 | 330 | 69553 | 0.4304 | 0.0020421 | 210.7667
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 12 | 35 | 2457 | 0.015204 | 0.00021659 | 70.2
AEP-KYP | 2025-03-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 1 | 1 | 99 | 0.00061263 | 6.1882e-06 | 99
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 2 | 987 | 107970 | 0.66814 | 0.0061077 | 109.3921
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 10 | 1017 | 84086 | 0.52034 | 0.0062934 | 82.6804
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 7 | 81 | 10661 | 0.065972 | 0.00050124 | 131.6173
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 67 | 19146 | 0.11848 | 0.00041461 | 285.7612
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 8 | 18 | 3364 | 0.020817 | 0.00011139 | 186.8889
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 41 | 2194 | 1393475 | 8.623 | 0.013577 | 635.1299
AEP-KYP | 2025-03-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 2 | 2 | 267 | 0.0016522 | 1.2376e-05 | 133.5
AEP-KYP | 2025-03-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 76 | 2890 | 2320185 | 14.3577 | 0.017884 | 802.8322
AEP-KYP | 2025-03-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 50 | 1193 | 124556 | 0.77077 | 0.0073825 | 104.4057
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 4 | 3486 | 531114 | 3.2866 | 0.021572 | 152.3563
AEP-KYP | 2025-03-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 446 | 21116 | 5722577 | 35.4122 | 0.13067 | 271.0067
AEP-KYP | 2025-03-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 10 | 22 | 10172 | 0.062946 | 0.00013614 | 462.3636
AEP-KYP | 2025-03-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 2 | 4 | 918 | 0.0056807 | 2.4753e-05 | 229.5
AEP-KYP | 2025-03-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 4 | 7 | 7055 | 0.043657 | 4.3317e-05 | 1007.8571
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 1 | 1 | 14 | 8.6634e-05 | 6.1882e-06 | 14
AEP-KYP | 2025-03-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 876 | 49383 | 38348626 | 237.3073 | 0.30559 | 776.5552
AEP-KYP | 2025-03-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 17 | 496 | 48651 | 0.30106 | 0.0030693 | 98.0867
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 7 | 162 | 34895 | 0.21594 | 0.0010025 | 215.4012
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2025-03-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 26 | 128 | 9298 | 0.057537 | 0.00079208 | 72.6406
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 415 | 4150 | 0.025681 | 0.0025681 | 10
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 8 | 22 | 2662 | 0.016473 | 0.00013614 | 121
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 12 | 942 | 386610 | 2.3924 | 0.0058292 | 410.414
AEP-KYP | 2025-03-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 3 | 6 | 456 | 0.0028218 | 3.7129e-05 | 76
AEP-KYP | 2025-03-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 144 | 8737 | 11907496 | 73.6855 | 0.054066 | 1362.8815
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 155 | 6688 | 2899092 | 17.94 | 0.041386 | 433.4767
AEP-KYP | 2025-03-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 176 | 4124 | 777137 | 4.809 | 0.02552 | 188.4425
AEP-KYP | 2025-03-31 | T&G | TL | TRANSMISSION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 3 | 781 | 1257000 | 7.7785 | 0.004833 | 1609.475
AEP-KYP | 2025-03-31 | Station - Distribution | DS | DISTRIBUTION STATION | WFS | WEATHER - FLOOD/SLIDE | 161599 | 2 | 698 | 968401 | 5.9926 | 0.0043193 | 1387.394
AEP-KYP | 2025-05-31 | Equipment | DL | DISTRIBUTION LINE | EQF | EQUIPMENT FAILURE | 161599 | 700 | 35300 | 8753485 | 54.1679 | 0.21844 | 247.9741
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | BE | BLAST/EXPLOSION (NON AEP) | 161599 | 1 | 2 | 238 | 0.0014728 | 1.2376e-05 | 119
AEP-KYP | 2025-05-31 | TOR | PP | PARTIAL POWER | TOR | TREE OUT OF ROW | 161599 | 16 | 35 | 13504 | 0.083565 | 0.00021659 | 385.8286
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | EQF | EQUIPMENT FAILURE | 161599 | 17 | 12785 | 1979671 | 12.2505 | 0.079116 | 154.8433
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 2 | 987 | 107970 | 0.66814 | 0.0061077 | 109.3921
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | TR | TREE REMOVAL (NON AEP) | 161599 | 13 | 482 | 38890 | 0.24066 | 0.0029827 | 80.6846
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | WU | WEATHER - UNKNOWN | 161599 | 254 | 10792 | 3608066 | 22.3273 | 0.066783 | 334.3278
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WL | WEATHER - LIGHTNING | 161599 | 1 | 1232 | 180192 | 1.1151 | 0.0076238 | 146.2597
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | O | OTHER | 161599 | 12 | 540 | 117369 | 0.7263 | 0.0033416 | 217.35
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | WU | WEATHER - UNKNOWN | 161599 | 5 | 8 | 7180 | 0.044431 | 4.9505e-05 | 897.5
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | A | ANIMAL - NON BIRD | 161599 | 2 | 2 | 370 | 0.0022896 | 1.2376e-05 | 185
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SO | SCHEDULED OUTSIDE REQUEST > 1 CUSTOMER | 161599 | 5 | 38 | 23084 | 0.14285 | 0.00023515 | 607.4737
AEP-KYP | 2025-05-31 | Animal | PP | PARTIAL POWER | ABI | ANIMAL - BIRD | 161599 | 1 | 1 | 53 | 0.00032797 | 6.1882e-06 | 53
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CO | CORROSION | 161599 | 1 | 1 | 67 | 0.00041461 | 6.1882e-06 | 67
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | WFS | WEATHER - FLOOD/SLIDE | 161599 | 2 | 698 | 968401 | 5.9926 | 0.0043193 | 1387.394
AEP-KYP | 2025-05-31 | TIR | PP | PARTIAL POWER | TIR | TREE INSIDE ROW | 161599 | 5 | 9 | 1832 | 0.011337 | 5.5693e-05 | 203.5556
AEP-KYP | 2025-05-31 | T&G | TS | TRANSMISSION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 1399 | 283997 | 1.7574 | 0.0086572 | 203
AEP-KYP | 2025-05-31 | Vehicle Accident | PP | PARTIAL POWER | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 1 | 6 | 1734 | 0.01073 | 3.7129e-05 | 289
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | O | OTHER | 161599 | 1 | 1 | 94 | 0.00058169 | 6.1882e-06 | 94
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERF | ERROR - FIELD | 161599 | 16 | 1616 | 550036 | 3.4037 | 0.01 | 340.3688
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | F | FIRE - AEP, OR AFFECTING > 1 CUSTOMER | 161599 | 31 | 1259 | 180010 | 1.1139 | 0.0077909 | 142.9786
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WW | WEATHER - HIGH WINDS (EXCEEDING 60 MPH) | 161599 | 76 | 3059 | 2553449 | 15.8011 | 0.01893 | 834.7332
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | AF | ABNORMAL FEED | 161599 | 1 | 5 | 7375 | 0.045638 | 3.0941e-05 | 1475
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | ABI | ANIMAL - BIRD | 161599 | 20 | 1058 | 87361 | 0.5406 | 0.0065471 | 82.5718
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | VIN | VINE | 161599 | 78 | 591 | 101153 | 0.62595 | 0.0036572 | 171.1557
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 164 | 10550 | 12405264 | 76.7657 | 0.065285 | 1175.8544
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 16 | 284 | 28063 | 0.17366 | 0.0017574 | 98.8134
AEP-KYP | 2025-05-31 | Unknown | PP | PARTIAL POWER | U | UNKNOWN (NON WEATHER) | 161599 | 8 | 78 | 19768 | 0.12233 | 0.00048268 | 253.4359
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | ERO | ERROR - OPERATIONS | 161599 | 4 | 606 | 67824 | 0.41971 | 0.00375 | 111.9208
AEP-KYP | 2025-05-31 | Work Facilitation | DL | DISTRIBUTION LINE | FW | FACILITATION OF WORK | 161599 | 76 | 1599 | 144446 | 0.89385 | 0.0098949 | 90.3352
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | FO | FOREIGN OBJECT (NON ANIMAL) | 161599 | 2 | 2 | 267 | 0.0016522 | 1.2376e-05 | 133.5
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WT | WEATHER - TORNADO | 161599 | 1 | 1027 | 218914 | 1.3547 | 0.0063552 | 213.1587
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | V | VANDALISM | 161599 | 1 | 869 | 189618 | 1.1734 | 0.0053775 | 218.2025
AEP-KYP | 2025-05-31 | Animal | DL | DISTRIBUTION LINE | A | ANIMAL - NON BIRD | 161599 | 109 | 524 | 49789 | 0.3081 | 0.0032426 | 95.0172
AEP-KYP | 2025-05-31 | Equipment | PP | PARTIAL POWER | EQF | EQUIPMENT FAILURE | 161599 | 90 | 394 | 60358 | 0.3735 | 0.0024381 | 153.1929
AEP-KYP | 2025-05-31 | TIR | DL | DISTRIBUTION LINE | TIR | TREE INSIDE ROW | 161599 | 128 | 4464 | 2929056 | 18.1255 | 0.027624 | 656.1505
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | V | VANDALISM | 161599 | 8 | 168 | 35543 | 0.21995 | 0.0010396 | 211.5655
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WH | WEATHER - HURRICANE | 161599 | 1 | 13 | 38701 | 0.23949 | 8.0446e-05 | 2977
AEP-KYP | 2025-05-31 | Lightning | PP | PARTIAL POWER | WL | WEATHER - LIGHTNING | 161599 | 1 | 2 | 446 | 0.0027599 | 1.2376e-05 | 223
AEP-KYP | 2025-05-31 | Weather - Non Lightning | DL | DISTRIBUTION LINE | WI | WEATHER - ICE (1/2 INCH OR > 6 " SNOW) | 161599 | 57 | 4815 | 3154051 | 19.5178 | 0.029796 | 655.0469
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | ERF | ERROR-FIELD | 161599 | 1 | 1 | 74 | 0.00045792 | 6.1882e-06 | 74
AEP-KYP | 2025-05-31 | Vehicle Accident | DL | DISTRIBUTION LINE | VA | VEHICLE ACCIDENT (NON AEP) | 161599 | 30 | 3144 | 330285 | 2.0439 | 0.019456 | 105.0525
AEP-KYP | 2025-05-31 | Unknown | DL | DISTRIBUTION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 378 | 8983 | 1605382 | 9.9344 | 0.055588 | 178.7133
AEP-KYP | 2025-05-31 | Lightning | DL | DISTRIBUTION LINE | WL | WEATHER - LIGHTNING | 161599 | 33 | 727 | 104074 | 0.64403 | 0.0044988 | 143.1554
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | CE | CUST. EQUIPMENT > 1 CUSTOMER | 161599 | 12 | 50 | 7566 | 0.04682 | 0.00030941 | 151.32
AEP-KYP | 2025-05-31 | Remaining | DL | DISTRIBUTION LINE | OU | OTHER UTILITY | 161599 | 5 | 258 | 35992 | 0.22272 | 0.0015965 | 139.5039
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | TOR | TREE OUT OF ROW | 161599 | 1 | 565 | 58760 | 0.36362 | 0.0034963 | 104
AEP-KYP | 2025-05-31 | Remaining | PP | PARTIAL POWER | TR | TREE REMOVAL (NON AEP) | 161599 | 1 | 2 | 1302 | 0.008057 | 1.2376e-05 | 651
AEP-KYP | 2025-05-31 | TOR | DL | DISTRIBUTION LINE | TOR | TREE OUT OF ROW | 161599 | 1694 | 97946 | 61948086 | 383.3445 | 0.60611 | 632.4718
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | U | UNKNOWN (NON WEATHER) | 161599 | 3 | 20 | 7314 | 0.04526 | 0.00012376 | 365.7
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | WFS | WEATHER - FLOOD/SLIDE | 161599 | 3 | 781 | 1257000 | 7.7785 | 0.004833 | 1609.475
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | EQF | EQUIPMENT FAILURE | 161599 | 1 | 415 | 4150 | 0.025681 | 0.0025681 | 10
AEP-KYP | 2025-05-31 | Scheduled | DL | DISTRIBUTION LINE | SCO | SCHEDULED COMPANY | 161599 | 887 | 13094 | 1688479 | 10.4486 | 0.081028 | 128.9506
AEP-KYP | 2025-05-31 | Station - Distribution | DS | DISTRIBUTION STATION | SCO | SCHEDULED COMPANY | 161599 | 2 | 1997 | 47746 | 0.29546 | 0.012358 | 23.9089
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | SCO | SCHEDULED COMPANY | 161599 | 1 | 2 | 520 | 0.0032178 | 1.2376e-05 | 260
AEP-KYP | 2025-05-31 | T&G | TL | TRANSMISSION LINE | FW | FACILITATION OF WORK | 161599 | 1 | 3 | 816 | 0.0050495 | 1.8564e-05 | 272