24607 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-09-29 20:59 | 2015-09-29 21:54 | 1 | 55 | 4292071 | 55 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 38820966A30695 LETTINGSOUCE SIDE RISER CONTACT CROSSARM REPLACED CUTOUT RESTORED POWER AT21:54 MAKE ADDITIONAL OUTAGE FROM ORIGINAL CUSTOMER OUT FROM 2059 TILL 2154 VER/SEF L3/DKG VERIFIED WITH ALARM HISTORY AND SWITCHING ORDER
24608 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-07-20 12:26 | 2016-07-20 13:21 | 1 | 55 | 4660581 | 55 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL PULLED OUT OF SLEEVE IN SERVICE DROP//I REPAIRED SERVICE DROP//COMPLETE//EM VER/CRB
24609 | Whitesburg | 3312901 | JENKINS | KONA | 2010-02-25 13:49 | 2010-02-25 14:43 | 1 | 54 | 60942-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPLACED SECONDARY SIDE OF TRANSFORMER// VER/DBM IDC XXXX
24610 | Hazard | 3310502 | HADDIX | CANOE | 2011-03-01 09:22 | 2011-03-01 09:40 | 3 | 18 | H65327-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OFF 9:22--ON 9:40 COD-4 ISO LF 37830169C00072 DUP IN HOIS THIS IS FOR THE FUSE OUTAGE 3 CUST FROM VER/HFP L3/HFP IDC XXXX
24611 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-05-04 11:50 | 2017-05-04 12:44 | 1 | 54 | 4744581 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD BROKE, REFUSED XMF APR AT 1244 CLOSE TICKET/ ISO 38830549000126/ COD1/ VER/BOW
24612 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-02-03 11:47 | 2016-02-03 12:05 | 3 | 18 | H4671831 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO AT POLE 398-374, OPENED STEPDOWN AT 11:47 TO ISOLATE..//COD 15 FROM BEGINNING OF OUTAGE//LOOP BURNT INTO AT POLE 398-374, OPENED STEPDOWN AT 11:47 TO ISOLATE..REPAIRED LOOP RESTORED POWER AT 12:05.. VER/CRB
24613 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-12 19:54 | 2010-12-12 20:48 | 1 | 54 | 65709-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | STS SERVIN PULL OUT VER/HFP L3/HFP IDC XXXX
24614 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-06-14 13:15 | 2019-06-14 13:42 | 2 | 27 | 4505581 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 120V ON 1LEG,128 0N THE OTHER,MAY HAVE XFR ISSUE.NEED 25KVA,MATERIAL HANDLER.TRUCK ACCESSABLE.ONE@SITE IS A CSP XFR. Opened up line fuse on pole 71-20 @ 12:55 no additional customers out.120V ON 1LEG,128 0N THE OTHER,MAY HAVE XFR ISSUE.NEED 25KVA,MATERIAL HANDLER.TRUCK ACCESSABLE.ONE@SITE IS A CSP XFR////////REPLACED XFR&RESTORED,124V EACH LEG AFTERWARDS//NO OUTAGE TILL L/F OPENED @ 1315
24615 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-05-18 13:01 | 2008-05-18 13:55 | 1 | 54 | 65457-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 SER. IN PULLED LOOSE VER/HFP IDC XXXX
24616 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-26 09:01 | 2011-01-26 09:55 | 1 | 54 | 64437-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BAD ON THE SECONDARY POLE. VER/HFP L3/HFP IDC XXXX
24617 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-06-10 09:06 | 2017-06-10 09:33 | 2 | 27 | H4928501 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE *** 2 CUST PART OUT ORIGINALLY/ OPENED XMF AT 0906 APR AT 0933 (2 ADD CUST)/, FOUND SEVERAL BAD CONN ON XMF, PLEASE SEND COPY TO STEVE M XMF AND RISER, ALSO A SHORT SPAN OF SEC NEEDS UPGRADED, POSSIBLY REPLACEING POLE ALSO. APR AT 0933 CLOSE TICKET/ ISO 38830428000180/ COD 4/ VER/BOW
24618 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-04-01 08:21 | 2015-04-01 09:15 | 1 | 54 | 4254001 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONE BAD SPLICE IN SINGLEPHASE SRVICEDROP MADE REPAIRES APR AT 0915 CLOSE TICKET// VER/ ADH L3/HFP XXX
24619 | Whitesburg | 3312901 | JENKINS | KONA | 2011-02-01 23:46 | 2011-02-02 00:40 | 1 | 54 | 52985-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKE,I REPAIRED VER/HFP L3/HFP IDCC PN52 XXXX
24620 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-06-24 02:48 | 2018-06-24 03:42 | 1 | 54 | 4655501 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replacing door
24621 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2015-12-07 13:40 | 2015-12-07 13:49 | 6 | 9 | 4516231 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED KVA PN 454-3615 IN ORDER TO CHANGE CUTOUT AT 13:40 RESTORED POWER AT 13:49 ALL POWER RESTORED PLEASE CLOSE TICKET THANKS DWW // COD-6 ISO TF 38830454B43615 VER/HFP L3/HFP
24622 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-06-21 23:33 | 2021-06-21 23:42 | 6 | 9 | 4787441 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Bad cutout gate on pole 248-A-653, power off at 23:33 back on at 23:42.
24623 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-05-23 13:40 | 2022-05-23 14:34 | 1 | 54 | 4933931 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | complete changed broke cutout
24624 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-03-05 18:55 | 2013-03-05 19:22 | 2 | 27 | 4873391 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830103000082 BAD XFMR C/O/// C/O CHANGED, POWER RESTORED. ///VER/CRB L/3 CRB IDCC TOF1819 ESTIMATED TIME OFF XXXX
24625 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-02-18 09:18 | 2019-02-18 10:12 | 1 | 54 | 4803051 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURT OFF @ POLE 38830182B10011,,,replaced burnt off stirrup and hot line clamp,,,customer restored @ 10:12 complete COD-1
24626 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-11-20 14:26 | 2014-11-20 15:20 | 1 | 54 | 4749621 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON WEATHERHEAD VER/CRB L3/DKGXXXX
24627 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-02-26 18:06 | 2015-02-26 19:00 | 1 | 54 | 4084551 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1099-158 6T TRANS FUSE MELTED OUT 25KVA SEND NOTE TO ENG. TRANS TO SMALL FOR 7 CUST. NEEDS 37.5 OR 50KVA NO TRUCK TO POLE/EMAILED TECH/ADH// VER/ ADH L3/DKGXXXX
24628 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-02-21 18:56 | 2012-02-21 19:50 | 1 | 54 | 4472861 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | LOOP BURNT ON POLE 37830223B00043,---- POWER RESTORED. CLOSE TICKET MWL //VER/GAH
24629 | Pikeville | 3402003 | KEYSER | MULLINS | 2020-12-02 15:43 | 2020-12-02 16:10 | 2 | 27 | 4739761 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1103-224, checking. Trans. fuse broke, refused @1610.
24630 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-03-15 13:06 | 2010-03-15 14:00 | 1 | 54 | 50280-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830375000103. VER/KEP L3/KEP IDC XXXX
24631 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-10-19 15:42 | 2011-10-19 16:00 | 3 | 18 | 4999701 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO 38821038A40130 // CREWS LIFTED HOTTAP IN ORDER TO REPAIR BAD CUTOUT ON ORDER 499261//COD 6// VER/DBM IDC XXXX
24632 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-03-23 15:29 | 2011-03-23 15:35 | 9 | 6 | 57149-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 39280435 //FOUNT BAD CUTOUT///REPLACED WITH NEW ONE//COD 9// VER/DBM IDC XXXX
24633 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2011-05-04 23:46 | 2011-05-05 00:40 | 1 | 54 | 4010431 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIREED REPLACED CUTOUT DOOR CUT VINES VER/PDP IDC XXXX
24634 | Hazard | 3302703 | HAZARD | HAZARD | 2013-02-28 13:18 | 2013-02-28 13:45 | 2 | 27 | 4862801 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLIT BOLT CONNECTOR FAILED AT WEATHER HEAD. OPENED TRANSFORMER AT 13:18, CLOSED AT 13:45, POWER RESTORED. ///VER/CRB L/3 CRB IDC XXXX
24635 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2019-05-29 12:21 | 2019-05-29 13:15 | 1 | 54 | 4360441 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken c/o, have replaced power is restored at this loc at 1315 by amg
24636 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-05-18 11:41 | 2021-05-18 12:35 | 1 | 54 | 4595841 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout
24637 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-05-13 16:46 | 2008-05-13 17:40 | 1 | 54 | 63658-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SERVE ENDS ON SERVICE DROP, RESQUEEZED ALL CONNECTION, EVERYTHING IS FINE HERE, NOW//3110902//VER/CRB IDCC CDC92 XXXX
24638 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2022-07-26 17:41 | 2022-07-26 18:35 | 1 | 54 | 4589141 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CUST METER MALFUCTION // REPAIRED @ 18:35
24639 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-02-15 15:21 | 2010-02-15 16:15 | 1 | 54 | 58048-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR FAILED ON SECONDARY RISER// VER/DBM IDC XXXX
24640 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-01-27 14:18 | 2016-01-27 15:12 | 1 | 54 | 4654641 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 397-26, REPLACED CUTOUT RESTORED POWER AT 15:12./ VER/AWD
24641 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-07-12 12:30 | 2010-07-12 12:57 | 2 | 27 | 65357-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT MIGHT BE BREAKING DOWN BASED ON WHAT CUST TOLD ME,WILL REPLACE IT////////REPLACED CUTOUT ALTHO IT APPEARED TO BE OK.OFF-12:30,ON 12:57 VER/HFP L3/HFP IDC XXXX
24642 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2021-08-24 10:48 | 2021-08-24 11:42 | 1 | 54 | 4143621 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse for xfmr had broke inside cutout door. I installed new fuse and restored @ 11:42
24643 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-10-11 14:28 | 2011-10-11 15:22 | 1 | 54 | 4965291 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// FUSE LINK APPEARED TO HAVE BROKEN//COD 1// VER/DBM IDC XXXX
24644 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-09-27 09:19 | 2010-09-27 09:25 | 9 | 6 | 53890-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE AREA SERVICER CHECK ON 9-28-10 AT REGULAR WORKTIME CUTOUT FAILURE IS CAUSING GUYWIRE TO ARC IN TREES, WAITING ON HELP TO CHANGE CUTOUT ,, WILL HAVE APPROX 10 CUST OFF, KNOCKED ON DOORS,1 ANSWERED,,TIME OFF 09:19TIME ON:0925//COD 9// VER/DBM IDC XXXX
24645 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-10-06 17:18 | 2014-10-06 18:12 | 1 | 54 | 4559621 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN THE SERVICE DROP, ONLY ONE CUSTOMER AFFECTED.// ISO 37820242000056// VER/BOW VER/DKG L3/DKG
24646 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-11-04 22:11 | 2012-11-04 23:05 | 1 | 54 | 4358581 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SQUEEZE ON AT XFMR POLE 55-95 .. REPAIRED AND COMPLETE.. XFMR ON THAT POLE WAS OFF FROM 22:48 TO 23:05 VER/ARN IDC CHANGED TIME OFF BACK TO CUSTOMER CALL. APPEARS THIS WAS A PART POWER XXXX
24647 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-06-04 14:56 | 2014-06-04 15:50 | 1 | 54 | 4973661 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT. VER/CRB
24648 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2018-06-23 23:11 | 2018-06-24 00:05 | 1 | 54 | 4655351 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv door
24649 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-01-22 18:57 | 2019-01-22 19:51 | 1 | 54 | 4705951 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad insulink. repairs made. all good. pls close. tre L3/HFP
24650 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-02-08 17:20 | 2022-02-08 18:14 | 1 | 54 | 4459401 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad conn. on transformer
24651 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-11-30 11:00 | 2013-11-30 11:54 | 1 | 54 | 4089091 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 1// VER/DBM
24652 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-05-21 23:51 | 2020-05-22 00:45 | 1 | 54 | 4883831 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Txmf riser had come loose from bottom of cutout, repaires made apr at 0045 close ticket/ ISO 38830477000301/ COD 1
24653 | Pikeville | 3421002 | BREAKS | GRASSY | 2013-05-20 16:06 | 2013-05-20 17:00 | 1 | 54 | 4140021 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON THE SECONDARY POLE ONE OF THE PHASE WIRES. ONLY ONE CUSTOMER AFFECTED. VER/HFP L3/HFP IDC XXXX
24654 | South Williamson | 3200302 | BELFRY | TOLER | 2011-01-24 09:46 | 2011-01-24 10:40 | 1 | 54 | 63834-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK CONNECTOR BURNT UP ON 1 HOT LEG, ON SEC RISER SERVICE LOOPS ON XFMR POLE....WILL REPLACE WITH SQUEESE-ON CONNECTOR.....//....REPLACED CNNECTION....VOLTAGE GOOD NOW....JRV....01/24/11//VER/CRB IDC XXXX
24655 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-10-29 19:45 | 2020-10-29 20:39 | 1 | 54 | 4602341 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Conductors burnt into in service drop/// Repaired service drop and restored service @ 20:39//Only 1 cutomer affected
24656 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-04-27 18:51 | 2014-04-27 19:45 | 1 | 54 | 4639831 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS OLD , AND BROKE.//COD 1// VER/DBM IDC XXXX
24657 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-02-13 14:19 | 2015-02-13 15:13 | 1 | 54 | 4013951 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE WILL REPLACE//// REPLACED BROKEN CUTOUT AND RESTORED SERVICE @ 15:13// VER/ ADH L3/HFP XXX
24658 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-03-04 17:03 | 2015-03-04 17:30 | 2 | 27 | 4101191 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CUTOUT DOOR REPLACED POWER RESTORED AT THIS LOC AT 1730/ ISO 39830902B00202/ COD 2 L3/DKGXXXX
24659 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-11-03 13:51 | 2008-11-03 14:00 | 6 | 9 | 61845-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP RELATED TO ORDER 61787-1 CREW OPENED TRANSFORMER TO ALLOW THEM TO SAFELY CHECK CONNECTION ON TRANSFOMRMER POLE.. COD-6 IDC XXXX
24660 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2020-12-15 17:21 | 2020-12-15 17:30 | 6 | 9 | 4772341 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing bad c/o////open@17:21 Closed @ 17:30///complete BR
24661 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-02-07 21:36 | 2011-02-07 22:30 | 1 | 54 | 55145-1 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE WEATHERHEAD ON ONE 120 VOLT PHASE.//VER/CRB IDC XXXX
24662 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-04-08 15:41 | 2008-04-08 16:35 | 1 | 54 | 65268-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NETURAL BROKE ON MID SPAN CLAMP COMMING OFF LONG SPAN OF LASH. ADD WIRE AND REPAIR WIRE VER/HFP IDC XXXX
24663 | Whitesburg | 3312901 | JENKINS | KONA | 2014-03-03 13:26 | 2014-03-03 14:20 | 1 | 54 | 4447721 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | RED TO RED SQUEEZE-ON PULLED OUT VER/SEF
24664 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-04-10 11:11 | 2009-04-10 11:29 | 3 | 18 | 51002-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | AT 1108 SERV OPENED TR TO INSTALL AUTO TR. (2) ADD. CUST. LINK TO 50934-1//VER/CRB IDC XXXX
24665 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-02-07 13:15 | 2017-02-07 13:33 | 3 | 18 | 4363741 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE HAD NEUTRAL BURNT OPEN.OPENED XFM. ON POLE 141-62 @ 13:15 AND MADE REPAIRS.CLOSED BACK @ 13:33.. VER/CRB L3/HFP XXXHFP
24666 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-04-12 19:56 | 2022-04-12 20:50 | 1 | 54 | 4755281 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 20:50
24667 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-10-18 18:25 | 2011-10-18 18:43 | 3 | 18 | 4995891 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE ON POLE 98-156 BROKE AND LAID OVER INTO TRANSFORMER. IT HIT LEAD GOING FROM BUSHING TO ARRESTER AND ARCED. I OPENED TRANS., REMOVED GUY WIRE, AND THEN CLOSED TRANSFORMER. ///VER/CRB IDC XXXX
24668 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-11-12 11:18 | 2014-11-12 12:12 | 1 | 54 | 4722481 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE...REPLACED TRANSFORMER FUSE.6T FUSE/ ISO 38830858C00031/ COD 1// VER/BOW
24669 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-10-09 09:18 | 2018-10-09 09:45 | 2 | 27 | 4211191 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | METERING CABLE BURNT INTO//OPENED TRANS @ 0918 CLOSED 0945 // PER VOICE RECORDER WE HAD METERING CABLE BURNT UP THAT WAS CHANGED OUT TO CORRECT THE CUSTOMERS BILL = L3/HFP
24670 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-11-10 15:22 | 2022-11-10 15:40 | 3 | 18 | 4122811 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout, apr at 1540 close ticket.
24671 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2012-07-13 20:31 | 2012-07-13 21:25 | 1 | 54 | 4718791 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 280-60 SERV TO CHANGE,ALL CUST RESTORED@2125 PLEASE CLOSE TICKET THANKS.BT COD-1 ISO TF 38830280000060 (*&(*&_)(*&)(*&)(*&()
24672 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-03-24 10:06 | 2015-03-24 11:00 | 1 | 54 | 4221961 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN AT THE XFMR ON ONE OF THE SECONDARY PHASES. ONLY ONE CUST AFFECTED./// VER/ ADH L3/DKGXXXX
24673 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-12-14 13:26 | 2010-12-14 14:20 | 1 | 54 | 50020-1 | 54 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL PULLED OUT OF SLEEVE AND MAY HAVE SHORTED OUT CAUSING XFMR FUSE TO BLOW. REPAIRING SERVICE AND WILL TRY XFMR. REPAIRED SERVICE AND RE-FUSED XFMR @ 14:20. SH//VER/CRB IDC XXXX
24674 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-07-18 14:51 | 2013-07-18 15:45 | 1 | 54 | 4549941 | 54 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | YARD TREE RUBBING AGAINST SERVICE CAUSED NEUTRAL TO BREAK.---- POWER RESTORED.----- ONLY 1 CUST. WITH PART POWER// VER/DBM
24675 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-05-25 11:27 | 2018-05-25 12:20 | 1 | 53 | 4495871 | 53 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | connections & wire melted, repairs made & restored
24676 | Pikeville | 3410602 | E.PRESTON | LANCER | 2013-09-02 11:12 | 2013-09-02 12:05 | 1 | 53 | 4813291 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN ON POLE 38830980000043 GOING TO CUT PATH UP HILL AND REFUSE APPEARS FUSE BROKE POWER RESTORED @ 12:05//COD 1 VER/HFP L3/HFP IDC XXXX
24677 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-03-28 18:27 | 2018-03-28 19:20 | 1 | 53 | 4142371 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout is burned into , no one living here , vacation home crew can change cutout in the morning. per customers brother .// ops order to change cutout 037461672// Released by crew 077S12
24678 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-04-24 14:17 | 2012-04-24 15:10 | 1 | 53 | 4703421 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSED ROTTED COD-1 ISO TF 37830338000029 VER/HFP L3/HFP IDC XXXX
24679 | South Williamson | 3200301 | BELFRY | BELFRY | 2018-12-14 07:52 | 2018-12-14 08:45 | 1 | 53 | 4563801 | 53 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | A phase trans fuse out on 1014-C1-3.refused trans cutout.restored power at 08:45. ¦¦¦¦¦ L3/HFP
24680 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2016-01-28 10:42 | 2016-01-28 11:35 | 1 | 53 | 4656181 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONN BURNT INTO @ WEATHER HEAD REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT. FAULT 38830206B02454/ VER/AWD
24681 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-10-30 08:37 | 2014-10-30 09:30 | 1 | 53 | 4673451 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BURNT OFF @ POLE 38830182B30155//BASKET BURNT OFF @ POLE 182B30155, REPAIRE MADE ALL CUST RESTORED @ 0930 PLEASE CLOSE TICKET THANKS.BT//ISO 38830182B10011//COD 1 VER/CRB
24682 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2016-04-18 08:27 | 2016-04-18 09:20 | 1 | 53 | 4098711 | 53 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRD REPAIR CONNECTION VER/CRB
24683 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-06-06 21:28 | 2017-06-06 22:21 | 1 | 53 | 4918031 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED 6T FUSE VER/CRB
24684 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2014-11-08 01:37 | 2014-11-08 02:30 | 1 | 53 | 4712581 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 94-192 6T TRANS FUSE BROKE VER/TOM L3/TOM
24685 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-12-20 10:07 | 2012-12-20 11:00 | 1 | 53 | 4485621 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE..REFUSED TRANSFORMER. VER/KEP
24686 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2012-08-14 20:12 | 2012-08-14 21:05 | 1 | 53 | 4937641 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK PULLED APART IN XFMR CUTOUT..//.REPLACED & RE-FUSED..JRV..08/14/12 //COD 1// VER/DBM IDC XXXX
24687 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-01-14 11:37 | 2017-01-14 12:30 | 1 | 53 | 4297411 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED XFMR CUTOUT . REPLACED 27KV CUTOUT , ALL WORK COMPLETE / GXJ/ ISO 38831125C40675/ COD 1/ VER/BOW L3/HFP XXXHFP
24688 | South Williamson | 3411401 | DEWEY | INEZ | 2015-01-29 16:17 | 2015-01-29 17:10 | 1 | 53 | 4973591 | 53 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT UP AT XFMR//MAKING REPAIRS//REPAIRS MADE//XFMR ON 769-166 NEEDS UPGRADED TO 25KVA//I WILL TALKTO TECHNICIAN TOMAORROW ABOUT IT//RETORED SERVICE AT 17:10//COMPLETE//EM VER/CRB L3/HFP XXX
24689 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-11-19 14:30 | 2021-11-19 15:23 | 1 | 53 | 4109101 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @46-52, checking. Trans. fuse melted, refused @1523.
24690 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-02-28 18:47 | 2011-02-28 19:40 | 1 | 53 | 65101-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT//VER/CRB IDC XXXX
24691 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-04-11 12:40 | 2016-04-11 13:33 | 1 | 53 | 4080081 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 166-213.WILL MAKE REPAIRS.REPAIRS MADE. VER/AWD
24692 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-09-17 08:07 | 2020-09-17 09:00 | 1 | 53 | 4470611 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke c/o--in at 09:00--allgood-ds091720
24693 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-07-24 22:12 | 2009-07-24 23:05 | 1 | 53 | 55862-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3003701// BROKEN FUSE LINK. VER/TOM L3/TOM IDC XXXX
24694 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-11-10 19:27 | 2008-11-10 20:20 | 1 | 53 | 63750-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP BAD FUSE LINK. COD-1 IDC XXXX
24695 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-03-08 09:14 | 2010-03-08 10:07 | 1 | 53 | 63695-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NETURAL BROKE IN SERVICE DROP WILL REPLACE SERVICE .REPLACED 4/3 SERVICE WITH 2/3 COMPLTED AT 10:07 VER/HFP L3/HFP IDC XXXX
24696 | Hazard | 3301401 | COMBS | COMBS | 2013-12-15 14:28 | 2013-12-15 15:21 | 1 | 53 | 4163551 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT AT WEATHERHEAD.------ REMADE CONNECTIONS, POWER RESTORED. VER/CRB L3/HFP
24697 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2013-12-03 14:00 | 2013-12-03 14:53 | 1 | 53 | 4096181 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING BAD TRANSFORMER, TCM/ VER/SEF L3/HFP
24698 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-12-22 11:37 | 2019-12-22 12:30 | 1 | 53 | 4176151 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | repaired cutout, power restored 12:30
24699 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-02-23 08:07 | 2022-02-23 09:00 | 1 | 53 | 4534561 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew requird/cutout replacement
24700 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-02-26 15:22 | 2008-02-26 16:15 | 1 | 53 | 50621-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000701// FOUND BAD LINE CUTOUT, ON POLE 927-25 HAVE CUTOUT CHANGED AT THIS TIME AND POWER IS RESTORED AT THIS LOC// VER/TOM IDC XXXX
24701 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-05-23 07:37 | 2011-05-23 08:30 | 1 | 53 | 4138551 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACE ARRESTOR COD-1 ISO TF 37830023000218 VER/HFP L3/HFP
24702 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-12-18 12:07 | 2016-12-18 13:00 | 1 | 53 | 4215331 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT AND ARRESTER ON POLE 182 91/ ISO 37830182A00091/ COD 1/ VER/BOW
24703 | Pikeville | 3402002 | KEYSER | STONECOAL | 2012-02-14 14:52 | 2012-02-14 15:45 | 1 | 53 | 4348571 | 53 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | B PHASE FUSE OUT ON URD RISER POLE 38831152C41769.EVERYTHING LOOKS OK IN PADMOUNT.GOING TO REFUSE.APPEARS FUSE BROKE.REFUSED AND EVERYTHING OK//COD 1// VER/DBM IDC XXXX
24704 | South Williamson | 3411401 | DEWEY | INEZ | 2013-01-07 13:37 | 2013-01-07 14:30 | 1 | 53 | 4575211 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | METER HAD MELTED ON 3 LUGS//I CHECKED VOLTAGEAND ALL WAS GOOD//CUSTOMER IS PULLING PRETTY GOD LOAD INSIDE//METER ELECTRICIAN SAID COULD PLACE HIGHER AMP METER HERE///I CHANGED TO NEW METER/ALSO PLEASE SEND TO CLIFF FREEMAN TO CHANGE OUT TO LARGER SERVICE DROP//COMPLETE//EM VER/KEP IDCC CNT2 XXXX
24705 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-12-13 10:03 | 2016-12-13 10:56 | 1 | 53 | 4191231 | 53 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD NU. CONN. ON POLE REPAIRED VER/AWD L3/HFP XXXHFP
24706 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-02-22 13:57 | 2010-02-22 14:50 | 1 | 53 | 59885-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#33967801 POLE 116-113 BAD 19.9 CUTOUT//VER/CRB IDC XXXX
24707 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2015-12-04 07:57 | 2015-12-04 08:50 | 1 | 53 | 4509131 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 448-560. REPLACED CUTOUT RESTORED POWER AT 08:50.// VER/ ADH
24708 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-11-28 12:57 | 2015-11-28 13:50 | 1 | 53 | 4489611 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE VER/CRB
24709 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-04-19 12:15 | 2008-04-19 13:08 | 1 | 53 | 52281-1 | 53 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE 113-79. I WILL HAVE TO CLIMB POLE WILL BE OUT OF TRUCK.CHANGED CUTOUT EVERYTHANG OK.//3407101//VER/CRB IDC XXXX
24710 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2020-08-24 10:23 | 2020-08-24 11:15 | 1 | 52 | 4363751 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse out on941-c3-83.no hazards seen.restored power at 11:45
24711 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-07-27 12:50 | 2009-07-27 13:03 | 4 | 13 | 60903-1 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLCED CONNECTIONS ON SEVICE VER/KEP L3/KEP IDCC TOF1010 XXXX
24712 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-08-30 12:15 | 2015-08-30 12:28 | 4 | 13 | 4183441 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PULLED XFMR OFF @ 12:15 & BACK ON @12:28 TO REPLACE SECONDARY CONNECTIONS./ ISO 38831151C00220/ COD 4/ VER/BOW L3/GSL
24713 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-01-29 13:54 | 2015-01-29 14:46 | 1 | 52 | 4973251 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | 1 CUSTOMER ORGINALLY, OPEN TRANS AT 1414 AND CLOSED AT 1446 1+2/FIX IT IN HOIS// VER/ ADH L3/HFP HFPC MCCDL CDC92
24714 | Hazard | 3309301 | VICCO | REDFOX | 2014-11-08 12:25 | 2014-11-08 12:51 | 2 | 26 | 4713631 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DIDNT OPEN XFMR, OPENED SEC. ON POLE 277-158, HAD TWO CUSTOMERS OFF. SEC. NEUTRAL HELD TOGETHER BY ONE STRAND, CUT AND SPLICED NEUTRAL. COMPLTED POWER BACK ON.// ONLY 2 CUST OFF ON POLE 158/ VER/BOW
24715 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-03-09 08:43 | 2008-03-09 09:35 | 1 | 52 | 55617-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001101//8T ME FUSE LINK BROKE//ISO//COD 1// VER/DBM IDC XXXX
24716 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-09-13 12:14 | 2013-09-13 13:06 | 1 | 52 | 4851131 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRING CONNECTION CUTTING TREE LIMBS/WAS JUST BAD CONNECTION NOT TREES VER/SEF L3/HFP HFPC CNT6
24717 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-08-20 19:33 | 2010-08-20 20:25 | 1 | 52 | 58878-1 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 36538915//POLE 92-234 HOT TAP BURNT OFF B PHASE REPAIRED VER/KEP L3/KEP IDC XXXX
24718 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-04-29 19:58 | 2017-04-29 20:50 | 1 | 52 | 4696091 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKE FUSE/ ISO 37830254D00150/ COD 1/ VER/BOW L3/HFP XXXHFP
24719 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-05-27 11:33 | 2010-05-27 12:25 | 1 | 52 | 51361-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD FROM ARRESTER FELL ON XFMR CLEARED UP AND RESTORED POWER VER/ARN IDC XXXX
24720 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-09-04 13:16 | 2014-09-04 14:08 | 1 | 52 | 4463321 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | JIM HOLLIDAY REPORTED CUSTOMER ONLY HAD PART POWER, ONE LEG DEAD.PART POWER BAD SERVE IN AT XFMR MADE REPAIRS RESTORED POWER AT 14:08.// COD 1// VER/ ADH
24721 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2012-11-14 14:59 | 2012-11-14 15:25 | 2 | 26 | 4397901 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I FOUND A CONNECTION GOING BAD AT SECONDARY POLE WHILE I WAS DOING A DNP CUT AT POLE. REPLACED CONNECTION. COD-2 VER/KEP IDC XXXX
24722 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-12-29 20:15 | 2014-12-29 21:07 | 1 | 52 | 4890791 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR. FUSE BLOWN // WILL REFUSE// FUSE LINK BROKE// POWER RESTORED @ 21:07/ ISO 37830024C01597/ COD 1/ VER/BOW
24723 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2021-08-12 19:43 | 2021-08-12 20:35 | 1 | 52 | 4048851 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse had pulled apart inside cutout door. I refused and restored @20:35
24724 | Pikeville | 3409502 | BURDINE | LEVISA | 2016-08-30 18:44 | 2016-08-30 19:10 | 2 | 26 | 4852681 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER COMPLAING OF HIGH BILL SAYS ELECTRICIAN CHECK THEIR EQUIPMENT AND SAID POWER WAS RUNNING BACKWARDS CUSTOMERS VOLTAGE CHECKED GOOD AT METER ADVISED CUSTOMER TO RECHECK THEIR EQUIPMENT REPAIRED BURNT UP SECONDARY CONNECTIONS ON TRANS POLE 312-47 OPENED TRANS UP AT 18:44 CLOSED AT 19:10/ ISO 37830312000047/ COD 2/ VER/BOW
24725 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-01-13 09:19 | 2009-01-13 10:11 | 1 | 52 | 54635-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP REPAIRED SERVICE DROP. L3/HFP IDC XXXX
24726 | Hazard | 3303901 | LESLIE | HYDEN | 2011-02-05 19:08 | 2011-02-05 20:00 | 1 | 52 | 54681-1 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON POLE NO OUTAGE ONLY 1 LEG//COD 1// VER/DBM IDC XXXX
24727 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-02-17 19:25 | 2012-02-17 20:17 | 1 | 52 | 4355751 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER ON POLE 37820146000089 IS LEAKING IN YARD.WILL NEED A 25KVA 7200, CUTOUT, AND BRACKET.STEEP TURN INTO DRIVEWAY /// RAY, RICHARD ECSP TRANSFORMER ON POLE 37820146000089 IS LEAKING IN YARD.WILL NEED A 25KVA 7200, CUTOUT, AND BRACKET.STEEP TURN INTO DRIVEWAY.BRING 700559 OR HYBRID BUCKET TO MAKE TURN AND 2 XFMR SACKS OFF @ 1925 ON @ 2017 COD-1 ISO TF 37820146000089 VER/HFP L3/HFP IDCC PN NULL XXXX
24728 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2008-08-10 10:28 | 2008-08-10 11:20 | 1 | 52 | 50672-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE LINK APPEARS TO HAVE JUST DETERRIORATED AND BROKE.//3308601//VER/CRB IDC XXXX
24729 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-01-04 20:10 | 2018-01-04 20:36 | 2 | 26 | 4707841 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse had broke, refused txmf apr at 2036 close ticket
24730 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-05-24 09:56 | 2009-05-24 10:22 | 2 | 26 | 62727-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3007904//,,,,BAD TRANSFORMER 25KVA 19.9 IT IS TRUCK ACCESSIBLE RELEASED BY CREW 078S02 VER/TOM IDC XXXX
24731 | Hazard | 3309003 | JEFF | VIPER | 2019-02-27 11:53 | 2019-02-27 12:45 | 1 | 52 | 4932681 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changing bad transformer power restored at12:45
24732 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-05-17 15:17 | 2009-05-17 16:09 | 1 | 52 | 61284-1 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD CALLED CUST, CAN WAIT UNTIL MONDAY MORNING GIVE TO LLOYD RAYBURN TO WORK FIRST THING IN MORNING 7200VOLT 15 KVA 1.9 IMP DOUBLE BUSHING Y-Y BANK 120/208 WORK ASAP IN MORNING RELEASED BY CREW 078S09//VER/CRB IDCC PN7543 XXXX
24733 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-05-28 12:27 | 2012-05-28 12:40 | 4 | 13 | 4837231 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ALLEN ANDERSON (LINE CREW SUPERVISOR IN GRUNDY. CELL 276-219-3230) WHILE AT PIKEVILLE RV FOUND A WIRE OFF THE INSULATOR AND LAYING UP AGAINST THE POLE ON 34KV AT POLE 1126-312 - TIE WIRE BROKE. IF IT RAINS THIS WILL CAUSE THE POLE TO CATCH FIRE AND BURN UP. // PRI. COND. IS OFF INSULATOR AT POLE 1126-312. I AM GOING TO OPEN LINE CUTOUT AT POLE 1126-298 SO I CAN TIE WIRE BACK ON INSULATOR. I OPENED LINE FUSE ON 1126-298 AT 12:27, AND CLOSED IT BACK AT 12:40.//COD 4 IDC XXXX
24734 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-04-13 09:30 | 2009-04-13 09:56 | 2 | 26 | 51724-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602// REPLACED CUTOUT COD-2 OPENED AT 0930 CLOSED 0956 VER/KEP L3/KEP IDC XXXX
24735 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2010-04-20 23:35 | 2010-04-21 00:01 | 2 | 26 | 65771-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT AND ARRESTER. OPENED XFMR ON 954-865 @ 23:35 AND CLOSED @ 00:00. SH VER/KEP L3/KEP IDCC PN153 XXXX
24736 | Hazard | 3311103 | STINNETT | WENDOVER | 2011-08-10 13:08 | 2011-08-10 14:00 | 1 | 52 | 4692791 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT 7.2KV VER/KEP IDC XXXX
24737 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2010-08-03 13:09 | 2010-08-03 13:35 | 2 | 26 | 60827-1 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | WR# 36271882 // POLE 68-4031 10T CHANCE FUSE BROKE//COD 2//ISO 38830068C04031// VER/DBM IDC XXXX
24738 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-09-15 13:44 | 2008-09-15 13:57 | 4 | 13 | 64200-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE BROKE.WILL REFUSE.I REFUSED THE CUTOUT WITH A 65T AND RESTORED POWER TO NORMAL THERE ARE 3-65TS ON THIS POLE AND A SINGLE PHASE LINE FUSE THAT FEEDS 2 SPANS BUT I DONT KNOW THE SIZE FUSE FOR THE SINGLE PHASE CUSTOMER THE MAP SHOWS THE 3-LINE FUSES WITH 65S BUT NO SINGLE PHASE FUSE.TIM MCCOY RELEASED BY CREW 074H10 CUSTOMER COUNT 4 VER/ARN IDC XXXX
24739 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2022-11-25 11:18 | 2022-11-25 12:10 | 1 | 52 | 4179531 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @22-243, checking. Trans. fuse melted out, refused @1210.
24740 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-11-17 17:11 | 2021-11-17 18:03 | 1 | 52 | 4102591 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke--replaced-allgood-ds111721
24741 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2020-06-22 15:17 | 2020-06-22 16:09 | 1 | 52 | 4060271 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections,,complete
24742 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2017-02-10 15:00 | 2017-02-10 15:52 | 1 | 52 | 4384241 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING NOW TCM/ ONLY ONE RED LIGHT OUT , FOUND BAD SERVIN ON HOT LEG TCM. VER/CRB L3/HFP HFPC CDC89
24743 | South Williamson | 3411401 | DEWEY | INEZ | 2012-06-28 21:28 | 2012-06-28 22:20 | 1 | 52 | 4973661 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 816-27//REPLACED AND RESTORED AT 2220//COMPLETE/EM ///VER/CRB L/3 CRB
24744 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-02-19 15:33 | 2019-02-19 16:25 | 1 | 52 | 4808041 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | restored 16:25
24745 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-07-29 18:18 | 2016-07-29 19:10 | 1 | 52 | 4710271 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED//CUT OUT BROKE AND BURNING INSIDE POLE. CHANGED CUTOUT AND RESTORED POWER AT 1910 VER/CRB
24746 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2014-07-11 15:03 | 2014-07-11 15:55 | 1 | 52 | 4230161 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THE NEUTRAL IN THE SERVICE DROP BURNED APART DUE TO A PHASE CONNECTION HEATING AND MELTING THE INSULATION BETWEEN THE PHASE AND THE NEUTRAL VER/CRB
24747 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-10 21:03 | 2011-06-10 21:55 | 1 | 52 | 4289611 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR. COD-1 ISO TF 38830165D00251 VER/HFP L3/HFP IDC XXXX
24748 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-10-10 10:38 | 2013-10-10 11:30 | 1 | 52 | 4927321 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE IN PROCESS OF CHANGING CUTOUT,POLE FIRE IN PROCESS OF CHANGING CUTOUT. PLEASE SEND TO TECH JOB NEEDS WRITTEN TO REPLACED BURNT POLE. VER/SEF L3/HFP
24749 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-11-22 15:30 | 2011-11-22 16:22 | 1 | 52 | 4100921 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTION ON POLE//COD 1// VER/DBM IDCC TOF1302 ESTIMATED TIME OFF FOR REPAIR XXXX
24750 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-08-18 18:38 | 2014-08-18 19:30 | 1 | 52 | 4381431 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T XFMR RESTORED @ 1930//COD 1// VER/DBM
24751 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2022-11-21 16:14 | 2022-11-21 17:06 | 1 | 52 | 4169711 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Pat Thovson reporting XFMR fuse open at this location per windstream tech.. transformer back in at 17:06.. complete
24752 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-01-30 12:58 | 2016-01-30 13:50 | 1 | 52 | 4660331 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED ALL CUST RESTORED @ 1350 PLEASE CLOSE TICKET THANKS.BT VER/CRB
24753 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-08-26 14:24 | 2010-08-26 15:16 | 1 | 52 | 60849-1 | 52 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEZED BAD CONNECTION VER/KEP L3/KEP IDC XXXX
24754 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-05-20 08:04 | 2009-05-20 08:56 | 1 | 52 | 51161-1 | 52 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WR#29905296//RESQUEZED BAD CONNECTION/VER/CRB
24755 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2018-03-31 18:24 | 2018-03-31 19:15 | 1 | 51 | 4159861 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Called customer numbers arent valid, bad 12kv c/o door/ ISO 39831147D10371/ COD 1
24756 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-01-12 19:14 | 2020-01-12 20:05 | 1 | 51 | 4294301 | 51 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER LUG WAS LOOSE CAUSING PART POWER, CUT BAD PART OF RISOR OFF AND RE-TIGHTEND
24757 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-05-28 19:49 | 2017-05-28 20:40 | 1 | 51 | 4877421 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN C/O, HAVE REPLACED POWER IS RESTORED AT THIS LOC AT 2040, BY AMG/// VER/DKM
24758 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-02-06 13:44 | 2017-02-06 14:35 | 1 | 51 | 4361661 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 471-95, REPLACED BAD CUTOUT RESTORED POWER AT 14:35.. NO METERED ACCTS VER/CRB L3/HFP XXXHFP
24759 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-09-21 14:31 | 2010-09-21 15:22 | 1 | 51 | 51925-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR HAD MELTED OUT//////CHANGED DOOR//RESTORED EM//ISO 38820746C00366//COD 1// VER/DBM IDCC CDC83 XXXX
24760 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-05-20 07:37 | 2013-05-20 08:28 | 1 | 51 | 4136371 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKE FUSE//COD 1// VER/DBM IDC XXXX
24761 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-12 18:24 | 2013-01-12 19:15 | 1 | 51 | 4598841 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. ///VER/CRB L/3 CRB IDC XXXX
24762 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-09-24 08:12 | 2009-09-24 09:03 | 1 | 51 | 61220-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110903//BURNT C DOOR REPLACED CUT OUT POWER RESTORED IDC XXXX
24763 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-02-03 09:52 | 2014-02-03 10:43 | 1 | 51 | 4343531 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT VER/SEF
24764 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-07-03 15:25 | 2009-07-03 15:42 | 3 | 17 | 63366-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3202201//...FOUND CORRODED NUETRAL CONNECTIONS IN MTR BASE....WILL CLEAN UP...NO OUTAGE...//..CLEANED C USTS BASE.....STILL HAVE ODD VOLTAGE (HIGH & LOW)....WILL HAVE TO OPEN XFRMER & CLIMB & CHECK ALL CONNECTIONS...// OPENED XFRMER @ 15:25....REPLACED OPEN NUETRAL CONNECTION ON LASH CABLE ON XFRMR POLE...CLOSED XFRMER @ 15:42.....VOLTAGE GOOD NOW....JRV...07/03/09//COD 3// VER/DBM IDC XXXX
24765 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-04-28 16:28 | 2013-04-28 16:45 | 3 | 17 | 4053981 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 423-304, OPENED LINE FUSE ON POLE 423-131 AT 16:28 TO ISOLATE , REPLACED CUTOUT RESTORED POWER AT 16:45 //////VER/CRB L/3 CRB. IDCC CDC92 XXXX
24766 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-05-06 14:44 | 2016-05-06 15:35 | 1 | 51 | 4182571 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING BAD TRANSFORMER/ ISO 37830154000144/ COD 1/ VER/BOW
24767 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-03-09 20:21 | 2014-03-09 21:12 | 1 | 51 | 4463421 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED BAD CONNECTION COD-1 VER/KEP
24768 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-08-06 15:18 | 2009-08-06 15:35 | 3 | 17 | 52265-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG ON TRANSFORMER HAD BEEN GETTING HOT AND MELTING CONNECTION. I OPENED TRANS. ON POLE 214-110 AT 15:18, FIXED CONNECTIONS AND CLOSED TRANS. BACK IN AT 15:35. CUSTOMER SAID THIS FIXED PROBLEM. VER/KEP L3/KEP IDC XXXX
24769 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-03-04 15:54 | 2010-03-04 16:45 | 1 | 51 | 62885-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
24770 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-12-23 15:28 | 2016-12-23 15:45 | 3 | 17 | 4230821 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT ON POLE 37830221000042/ OPENED LINE FUSE AND TRANSFORMER FUSE ON POLE 37830221000042 @ 1528 AND CLOSED BOTH AT 1545/ 12T LINE FUSE MD/ ISO 37830221000042/ COD 3/ VER/BOW
24771 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2021-12-20 13:31 | 2021-12-20 14:22 | 1 | 51 | 4214551 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link appears to have broke. Restored @ 14:22. sh
24772 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-04-14 22:29 | 2008-04-14 23:20 | 1 | 51 | 51159-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001102//WRONG ADDRESS WRONG POLE NUMBER COD-1 VER/LDA IDC XXXX
24773 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-10-27 12:14 | 2009-10-27 13:05 | 1 | 51 | 57583-1 | 51 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | #4/3 SERVICE DROP SHORTED OUT AT SPLICE IN MIDSPAN AND BURNED NEUTRAL INTO. I AM GOING TO CHANGE DROP TO A 2/3 DROP. I CHANGED S/DROP TO A 2/3. CUSTOMER SAID THEY COULD NOT FIND ANY DAMAGES. VER/KEP L3/KEP IDC XXXX
24774 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-04-08 10:29 | 2016-04-08 11:20 | 1 | 51 | 4070861 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | CREW ON SITE TO REPAIR UG SERVICE HOT LEG..FOUND BAD SPLICE ON BOTH HOT LEGS 4/0 WIRE.. WIRE HAS BEEN REPAIRED AND SERVICE RESTORED AT 1120.. JUST FED RESTROOMS AND CONCESSION STAND AT BALL FIELD.. PLEASE CLOSE TICKET..CY VER/HFP L3/HFP
24775 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-08-21 18:34 | 2009-08-21 19:25 | 1 | 51 | 60045-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING FUSE DOOR//COD 1// VER/DBM IDC XXXX
24776 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-07-14 14:31 | 2008-07-14 15:22 | 1 | 51 | 52540-1 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 3311101//XFMR FUSE BLOWN , GUY WIRE BROKE GOT INTO RISER. STAPLE GUY TO POLE REFUSED C/O POWER RESTORED. NEED TREE TICKET SENT TO CORY, TREE LAYING OVER TOP LINE, NEEDS REMOVED ASAP. IDC XXXX
24777 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2022-07-17 13:09 | 2022-07-17 14:00 | 1 | 51 | 4502701 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | burnt up hot tap in bank of transformers repairs made. complete
24778 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2021-06-10 17:02 | 2021-06-10 17:53 | 1 | 51 | 4708831 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | restored @1753
24779 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-12-27 11:15 | 2013-12-27 12:06 | 1 | 51 | 4204741 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE IS BURNED UP ON TOP OF TRANSFORMER. I AM GOING TO REFUSE TRANS. I REFUSED TRANS. AND IT STAYED. COD-1 VER/HFP L3/HFP
24780 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2017-09-19 15:54 | 2017-09-19 16:45 | 1 | 51 | 4374131 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 83-214/127--BROKE C/O--REPLACED-ALLGOOD--6T TRAN FUSE IN AT 16:45--DS091 VER/KEP L3/HFP XXXHFP
24781 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-03-17 18:59 | 2016-03-17 19:50 | 1 | 51 | 4860201 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 258-233. REPLACED AND RESTORED AT 1950. ISO 38830258C20233 COD 1 VER/AWD
24782 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-02-11 17:00 | 2011-02-11 17:51 | 1 | 51 | 56279-1 | 51 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | W IF ANYILL CHECK FOR PROBLEMSBAD SERVE-IN CONN AT XFR POLE CAUSING AN OCCASIONAL PARTIAL POWER,REPLACED BAD CONNECTIONS,ALL OK AFTERWARDS//VER/CRB IDC CHANGE START TIME FROM 1552 ESTIMATED TIME OFF XXXX
24783 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2014-04-23 15:24 | 2014-04-23 16:15 | 1 | 51 | 4628201 | 51 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1148-6516 BAD CUTOUT REPLACED VER/CRB
24784 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-12-08 14:05 | 2010-12-08 14:30 | 2 | 25 | H64396-1 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 64396-1//OPENED XFMR UP AT 14:05 TO REPAIR CONNECTION CLOSED AT 14:30 M.D.I.//COD 2// VER/DBM IDC XXXX
24785 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-08-21 11:45 | 2014-08-21 12:10 | 2 | 25 | 4394141 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACING LEAD ON POLE 37820073B00606. I OPENED TRANS. AT 11:45 AND CLOSED IN AT 12:10. SQUEEZE ON HAD BURNED INTO ON TRANS POLE.
24786 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-07-21 22:48 | 2017-07-21 23:38 | 1 | 50 | 4153531 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE JUST BROKE WAS NOT BLOWN REFUSED XMF APR AT 2338 CLOSE TICKET L3/HFP XXXHFP
24787 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2021-07-13 17:00 | 2021-07-13 17:50 | 1 | 50 | 4907541 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Customer having issue with Dead Phase fuse blowen in pad mount 272 c1 24 opened fuses onprimary under ground pole 1178 to replace fuse in transformer at 17:00 all pwer restored at 17:50
24788 | South Williamson | 3411401 | DEWEY | INEZ | 2013-09-05 22:15 | 2013-09-05 23:05 | 1 | 50 | 4824061 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED INTO//RESTORED AT 23:05//COMPLETE//EM VER/SEF L3/HFP HFPC FEC49 IDCC XXXX
24789 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2020-12-03 08:25 | 2020-12-03 09:15 | 1 | 50 | 4741051 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @24-B2-1543, checking. Fuse had melted, refused @0915.
24790 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-05-28 10:30 | 2019-05-28 11:20 | 1 | 50 | 4351991 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | secondary netural broke midspan,cutout is crack.will replace cutout,i have an observer coming to help//open transformer at 10:30 and close at 11:20
24791 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-11-06 08:20 | 2009-11-06 08:45 | 2 | 25 | 64866-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP REPAIRED CONNECTIONS AT ENTRANCE CABLE WHERE CABLE WAS DECADED. COUSTOMER IS TO HAVE ENTRANCE CHANGED SOON. OPENED TRANSFORMER AT 0820 ON AT 0845 COD-2 ISO TF 38831125C40087 L3/HFP IDCC CCO XXXX
24792 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2019-03-04 19:37 | 2019-03-04 20:27 | 1 | 50 | 4951731 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad insulink. all repairs made. pls close. tre L3/HFP
24793 | Paintsville | 3410602 | E.PRESTON | LANCER | 2021-07-07 14:20 | 2021-07-07 15:10 | 1 | 50 | 4865221 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | report of leaking transformer//xfmr leaking on pole 955-b-158//crew checking to see if we have a xfmr Released by crew 079S01.. opened @14:20 closed @ 15:10
24794 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-08-08 19:25 | 2009-08-08 19:50 | 2 | 25 | H64403-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR 31140255 OPEN TRANS. ON POLE 1123-4141 19.25 ON 19:50 4/3 SERVICE BURNT DOWN REPAIRED SEND NOTE TO TEC POLE 1123-4045 ROTTEN NEEDS LOOKED AT IDCC DUP TO OPEN TRANSFORMER XXXX
24795 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2011-02-02 18:45 | 2011-02-02 19:35 | 1 | 50 | 53620-1 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A BAD CONNECTION ON THE SECONDARY NEUTRAL AT THE TRANSFORMER. COD-1 ISO SO 37820125000045 VER/HFP L3/HFP IDCC TOF1754 XXXX
24796 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-16 13:50 | 2008-07-16 14:15 | 2 | 25 | 53247-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SECONDARY LEAD INTO ON POLE #181-76 WILL HAVE TO OPEN XFMR BANK TO MAKE REPAIRS ....REPAIRED SECONDARY RESTORED POWER AT 14:15 ...XFMR BUSHING IS LEAKING OIL , CREW WILL CHANGE//3308401//VER/CRB IDC XXXX
24797 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-11-14 21:47 | 2017-11-14 22:37 | 1 | 50 | 90003417 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH
24798 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2017-09-11 22:15 | 2017-09-11 23:05 | 1 | 50 | 4348201 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DUE TO BAD CUTOUT I OPENED TRANSFORMER UP AT 22:15 AND CLOSED TRANSFORMER BACK IN AT 23:05. CHANGED CUTOUT EVERYTHING OK 37830212D00167 VER/AWD L3/HFP XXXHFP
24799 | South Williamson | 3411401 | DEWEY | INEZ | 2021-07-08 16:20 | 2021-07-08 17:10 | 1 | 50 | 4874371 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | middle cutout breaking down on metering pole 861-a-69//going to open recloser on pole 861-70 to make repairs//going to replace all 3 cutouts//talked to federal prison they have switched over to generator for me to complete work//opened at 16:20//repairs made//restored at 17:10//complete//em
24800 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-04-25 20:20 | 2011-04-25 21:10 | 1 | 50 | 64872-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE TRANSFORMER CUTOUT FAILED I REPLACED IT. COD-1 ISO TF 37820150000030 VER/HFP L3/HFP IDC XXXX
24801 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2012-12-22 19:06 | 2012-12-22 19:16 | 5 | 10 | 4509431 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING. HOT LEG MELTED ON TRANS. AT POLE 448-88. I OPENED IT AT 1906 MADE REPAIRS CLOSED IT BACK IN AT 1916. ///VER/CRB L/3 CRB
24802 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-07-20 17:40 | 2010-07-20 18:30 | 1 | 50 | 53954-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT AND ARRESTOR VER/KEP L3/KEP IDCC TOF1430, ESTIMATED TIME OFF XXXX
24803 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-11-12 16:30 | 2011-11-12 17:20 | 1 | 50 | 4070471 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP CUTOUT GATE, ALL POWER RESTORED @ 17:20 HRS P.HICKS VER/KEP IDC XXXX
24804 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-07-07 13:10 | 2008-07-07 13:35 | 2 | 25 | H63668-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3110903//BAD 15 KVA 7.200 SINGLE BUSHING 3RD TIME IN 10 DAYS IT HAS WENT OUT NEED LINE CREW TO RE-PLACE GIVE TO BILL FRALEY//COD 2//-----TAP OFF FROM 13:10 TO 13:35//ADDITIONAL 2 CUSTOMERS OUT// VER/DBM IDC XXXX
24805 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-12-26 08:21 | 2017-12-26 08:46 | 2 | 25 | 4678551 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | no outage until opened,,opened @ 08:21 closed @ 08:46 and repaired secondary connections
24806 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-04-03 14:27 | 2009-04-03 14:37 | 5 | 10 | H64640-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 64640-1 //OPENED RECLOSER ON POLE 351-269 AT14:27 MADE LOOP UP IN POLE 351-63, CLOSED RECLOSER AT 14:37 RESTORING POWER// VER/DBM AJB
24807 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2021-07-10 22:20 | 2021-07-10 23:10 | 1 | 50 | 4888671 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Burnt up door, restored @ 23:10. Please send copy to forestry to spray vines on pole 38830044D37027*///emailed Dusty Roll for follow up
24808 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-12-07 16:05 | 2015-12-07 16:55 | 1 | 50 | H4515911 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEADEND INSULATOR ON POLE 37830096D00122 IS BAD AND CAUSING TRACKING DOWN POLE.TALKED TO TIM HALL AND HE HAS HELP ON WAY.//LIFTED HOT TAP ON POLE 96-D-271 @ 1605 CLOSED @ 1655 TO ISOLATE TROUBLE//DEADEND INSULATOR ON POLE 96D-122 IS BAD AND CAUSING TRACKING DOWN POLE.TALKED TO TIM HALL AND HE HAS HELP ON WAY. RELEASED BY CREW 074H21 VER/CRB
24809 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-12-19 19:45 | 2016-12-19 20:35 | 1 | 50 | 4221941 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKE XFR CUTOUT VER/CRB
24810 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-07-31 17:28 | 2019-07-31 18:18 | 1 | 50 | 4819071 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connections mid span tap service drop to cust. made repairs new connections everything ok
24811 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2021-03-22 12:15 | 2021-03-22 12:40 | 2 | 25 | 4360711 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad splice burnt one hot leg and neutral in 2, will be making repairs// opened XFM at 12:15 closed at 12:40
24812 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2021-06-15 15:30 | 2021-06-15 16:20 | 1 | 50 | 4754341 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Pole 38830503000085 broke at the neutral. Pole 503-122 will need deadended today to eliminate outage. Please tie conductor at phone level to keep out of feild untill decistion can be made to keep line or remove. Also please send copy to tech to look at this does not have to be looked at today. Crew required. Released by crew 078S11,repairs made open xfmr @ 1530 close @ 1620 please close ticket thanks.bt
24813 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-03-31 14:20 | 2008-03-31 15:10 | 1 | 50 | 62481-1 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3116703// BAD CONNECTION AT MAST// RESQUEZED CONNECTION// VER/DBM IDC XXXX
24814 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-12-25 16:09 | 2017-12-25 16:34 | 2 | 25 | 4677561 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr pole opened xfmr at 16:09 closed at 16:34
24815 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-08-03 21:58 | 2011-08-03 22:48 | 1 | 50 | 4661821 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED UP..CHANGED DOOR.//COD 1// VER/DBM IDC XXXX
24816 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-10-27 12:50 | 2018-10-27 13:15 | 2 | 25 | 4332091 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | will need big bucket to replace cutout and arrestor, complted//OFF 1250 L3/HFP
24817 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-11-28 08:25 | 2014-11-28 08:35 | 5 | 10 | 4813971 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMER, OFF @ 08:25, RESTORED @ 08:35 MP VER/ARN
24818 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-10-05 17:54 | 2013-10-05 18:44 | 1 | 50 | 4913371 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE SERV TO REPAIR,REPAIRS MADE ALL CUST RESTORED @ 1844 PLEASE CLOSE TICKET THANKS.BT VER/SEF L3/HFP IDC XXXX
24819 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2008-10-01 11:10 | 2008-10-01 12:00 | 1 | 50 | 52563-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP RELATED TO ORDER 52529-1 CREW OPENED TRANSFORMER TO REPAIR SECONDARY THAT IS DOWN (PER SERVICER THIS INTERRUPTS 1 ADDITIONAL CUSTOMER) THIS ORDER FOR THAT TRANSFORMER OUTAGE FOR 1 CUSTOMER. IDC XXXX
24820 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-08-19 17:25 | 2014-08-19 18:15 | 1 | 50 | 4385801 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE 1027-D-515/// ROBBIE WORRIX ENROUTE TO CHANGE TRANSFORMER/// OPENED TRANSFORMER UP @ 17:25 AND CHANGED TRANSFORMER CLOSED NEW TRANSFORMER IN @ 18:15 123/123/246 //COD 1// VER/DBM
24821 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-08-12 10:10 | 2017-08-12 11:00 | 1 | 50 | 4253021 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1.6T FUSE OUT LOOKS LIKE FUSE BROKE. FUSED UP EVERYTHING OK/ ISO 37830144A00089/ COD 1/ VER/BOW
24822 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-01-13 14:35 | 2015-01-13 14:45 | 5 | 10 | 4933281 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I OPENED THE XFMR AT 14:35 TO REPAIR SERVICE AND CLOSED BACK IN AT 14:45//SD HAD PLACES IN IT HAD TO OPEN TRANSFER TO FIX VER/CRB
24823 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-10-07 15:33 | 2009-10-07 16:23 | 1 | 50 | 60961-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE-JUST 1 CUSTOMER ON TRANSFORMER//VER/CRB IDC XXXX
24824 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-11-19 14:25 | 2014-11-19 14:35 | 5 | 10 | 4746581 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830046B12074 COD 5//BAD CUTOUT AND ARRESTOR FOUND DURING CIR INSP---BAD CUTOUT AND ARRESTOR FOUND DURING CIR INSP---OFF @ 14:25BAD CUTOUT AND ARRESTOR FOUND DURING CIR INSP---OFF @ 14:25---BACK ON @ 14:35---BL TKT COMP VER/CRB
24825 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2015-07-11 11:35 | 2015-07-11 12:25 | 1 | 50 | 4776571 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TAP FUSE AT POLE 1146-68 AT 11:35 TO ISOLATE BAD CUTOUT AT POLE 158, CLOSED LINE FUSE AT 12:25,ALL WORK COMPLETE / GXJ/ISO POLE 38831146000068/COD 1/MD MADE/ADH// VER/ ADH
24826 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-07-10 11:55 | 2011-07-10 12:20 | 2 | 25 | 4499031 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD BAD NEUTRAL CONNECTION ON XFMR POLE. CLEANED AND RECONNECTED SERVICE NEUTRAL, POWER SEEMED TO BE OK. // ADJUSTED TIME OFF TO ALLOW FOR OPENING TR AND MAKING REPAIRS // COD-2 ISO TF 37830130000016 VER/HFP L3/HFP IDC XXXX
24827 | South Williamson | 3411401 | DEWEY | INEZ | 2015-10-27 07:25 | 2015-10-27 08:15 | 1 | 50 | 4379121 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BROKEN CUTOUTCUTOUT BROKE ON 769-143//REPAIRS MADE//RESTORED AT 8:15//COMPLETE//EM/ ISO 38820769A00143/ COD 1/ VER/BOW
24828 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-08-02 12:30 | 2019-08-02 12:55 | 2 | 25 | 4832011 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | opened xfmr to change cutout and arrester tracking # KY050818-1244-9270 opened xfmr @ 12:30 in @ 12:55
24829 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-09-13 14:15 | 2012-09-13 14:40 | 2 | 25 | 4046091 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | TRANS. CUTOUT IS ARCING. I AM GOING TO OPEN TRANS. AND TIGHTEN CONNECTION. I REPLACED RISER FROM TRANS. TO BOTTOM OF TRANSFORMER. ///VER/CRB L/3 CRB IDC XXXX
24830 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-07-07 10:48 | 2022-07-07 11:38 | 1 | 50 | 4418561 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1129-D-60, checking. Trans. fuse melted out, refused @1138.
24831 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-03-21 09:40 | 2013-03-21 10:05 | 2 | 25 | 4944361 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED . REPLACED CURRENT LIMITING FUSE AND REFUSED TRANSFORMER , ALL WORK COMPLETE / GXJ VER/KEP IDCC 0831 ESTIMATED TIME OFF XXXX
24832 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-03-30 17:30 | 2008-03-30 18:20 | 1 | 50 | 62172-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602// BAD CUTOUT.// SERVICER DID NOT PROVIDE FETR// COD 1 ISO/FLT 37830422000113// // VER/TOM IDCC TOF1630 AS OF 1713 NO REPORT OF OUTAGE ESTIMATED TIME OFF XXXX
24833 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-05-23 09:15 | 2014-05-23 09:40 | 2 | 25 | 4744231 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER, OPENED TRANSFORMER AT 09:15, REPAIRED CONNECTION, CLOSED TRANSFORMER AT 09:40 COD-2 ISO SO @ 37830272C41270 VER/HFP L3/HFP
24834 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-08-26 10:30 | 2010-08-26 10:55 | 2 | 25 | H60650-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36610833 //,, BAD 50KVA 7200 CSP, NEED NEW XFMR, CUTOUT, POLE BRACKET, TRUCK OK RELEASED BY CREW 078S05 TOOK LINE FUSE OUT AT 10;30 BACK ON AT 10;55 OPENED TO DO REPAIRS ON 60650-1 VER/HFP L3/HFP IDC XXXX
24835 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-10-01 10:20 | 2012-10-01 10:45 | 2 | 25 | 4102081 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 078S08/// FETR 12:00 // JEH/ OPEN XFMER @ 10:20// CLOSED @10:45// REPLACED RISERS & SEC. CONNECTIONS/ REPAIRS COMP. POWER REST. @ 10:45 JEH //COD 2// VER/DBM IDC XXXX
24836 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-12-05 17:00 | 2018-12-05 17:50 | 1 | 50 | 4510871 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on pole. Repairs made and power restored. GH L3/HFP
24837 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2020-07-02 11:30 | 2020-07-02 11:55 | 2 | 25 | 4103681 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer open xfmr @ 1130 in @ 1155 please close ticket thanks.bt
24838 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-05-17 14:10 | 2016-05-17 15:00 | 1 | 50 | 4226331 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIR HOTAP VER/AWD L3/HFP XXXHFP
24839 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-09-05 15:10 | 2014-09-05 16:00 | 1 | 50 | 4469121 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078H12(OLD CSP XFORM NEEDS TO BE CHANGED OUT 25 KVA NO TR. CUST ALREADY HAS BEEN OUT OF POWER TWICE TODAY// BAD TRANSFORMER/// CLOSED IN FUSE// CHANGING TRANSFORMER OUT ON ANOTHER TICKET 4469461// VER/BOW
24840 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-03-19 14:00 | 2009-03-19 14:50 | 1 | 50 | 59976-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN 1/0 TWIST SECONDARY. NEED NEW RUN OF WIRE.APPROXIMATELY 125 FT. MAY BE ABLE TO PULL BACK TOGETHER. RELEASED BY CREW 078S04 // VER/TOM L3/TOM IDCC TOF0715 ESTIMATED TIME OFF XXXX
24841 | Hazard | 3303902 | LESLIE | WOOTON | 2012-11-19 13:10 | 2012-11-19 14:00 | 1 | 50 | 4408731 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE // COD-1 ISO TF 37830414000056 VER/HFP L3/HFP IDC XXXX
24842 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-04-03 09:15 | 2018-04-03 10:05 | 1 | 50 | 4167751 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse open on 38830044B00124, line fuse back in at 10:05
24843 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-11-23 13:22 | 2009-11-23 13:32 | 5 | 10 | 62545-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP SERVICER OPENED TRANSFORMER TO REPLACE BAD CONNECTION ON SECONDARY --- THIS ORDER CREATED TO REPAIR TROUBEL REPORTED IN ORDER 62462-1 L3/HFP IDC XXXX
24844 | Hazard | 3302703 | HAZARD | HAZARD | 2018-11-26 11:40 | 2018-11-26 12:30 | 1 | 50 | 4479081 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection failed on service pole,only 1 customer
24845 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-09-16 13:40 | 2019-09-16 14:05 | 2 | 25 | 4023951 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer had broke sec bushing. replaced transformer. opened @ 13:40 closed @ 14:05.. power restored
24846 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2008-10-16 14:25 | 2008-10-16 15:15 | 1 | 50 | 56219-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3400702// I REPLACED A BAD CONNECTION AT THE TRANSFORMER IDC XXXX
24847 | Hazard | 3303901 | LESLIE | HYDEN | 2014-01-15 12:30 | 2014-01-15 13:20 | 1 | 50 | 4284021 | 50 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | FUSE ROTTED OUT//COD 1// VER/DBM L3/HFP IDC XXXX
24848 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-03-05 16:40 | 2008-03-05 17:30 | 1 | 50 | 54046-1 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201//BROKE CUTOUT .. WILL REPLACE,,,REPLACE BROKE CUTOUT ,, THIS BAD CUTOUT MORE THAN LIKELY THE CAUSE OF THE FLICKERING LIGHT CALLS ON MORGANS CREEK RD.// NEED TO ADJUST TIMES IN HOIS// VER/TOM IDC NOT SURE WHEN OUTAGE ACTUALLY STARTED FIRST CALL WAS FULL POWER XXXX
24849 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2017-11-14 10:20 | 2017-11-14 10:45 | 2 | 25 | 4555341 | 50 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Related to 4554681/ crew required pole 270-18 broke at deadend shoe no trucks primary only 1 customer at 270-263/ will have to have outage on 270-18 line fuse to repair/ opened transformer on pole 38830270D00017/ ISO 38830270D00017/ COD 2/ 1020-1045
24850 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2015-01-29 13:46 | 2015-01-29 14:35 | 1 | 49 | 4973211 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 449-1489, REPLACED CUTOUT RESTORED POWER AT 14:35, ONLY ONE CUSTOMER AFFECTED//COD 1// VER/ ADH L3/HFP XXX
24851 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-09-02 15:40 | 2014-09-02 16:29 | 1 | 49 | 4449711 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN SEC. ON TRANS POLE SERVICER TO MAKE REPAIRS LRM 16:29 ALL PWR RESTORED PLEASE CLOSE TICKET LRM// CONNECTION ON SECONDARY BURNT/BROKE/// ISO 38830308000105// COD 1// VER/BOW
24852 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-11-30 19:21 | 2015-11-30 20:10 | 1 | 49 | 4496741 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-4535 BAD CUTOUT DOOR REPLACED 8T FUSE/ ISO 38830069C24535/ COD 1/ VER/BOW
24853 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-08-13 19:49 | 2021-08-13 20:38 | 1 | 49 | 4058621 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm fuse pulled into. restored 20:38
24854 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-01-05 10:53 | 2018-01-05 11:42 | 1 | 49 | 4709401 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | look like fuse pull into
24855 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2010-01-14 19:31 | 2010-01-14 20:20 | 1 | 49 | 54336-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR# 33450254 6T CHANCE FUSE BROKE//COD 1// VER/DBM IDC XXXX
24856 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-12-11 20:26 | 2017-12-11 21:15 | 1 | 49 | 4640161 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse broke into
24857 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-03-27 09:11 | 2009-03-27 10:00 | 1 | 49 | 62022-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29114198REPLACED CUTOUT POWER RESTORED L3/HFP IDCC SC NULL XXXX
24858 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-05-28 09:41 | 2015-05-28 10:30 | 1 | 49 | 4475581 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ 183A-162,REPLACED CUTOUT ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT
24859 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2020-04-28 12:26 | 2020-04-28 13:15 | 1 | 49 | 4761671 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o door. replaced door, restored
24860 | Hazard | 3420001 | SOFT SHELL | VEST | 2016-03-17 11:02 | 2016-03-17 11:51 | 1 | 49 | 4855521 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE RANDY FIELDS REPORTS THIS IS A BROKE CUTOUT THAT IS STILL ENERZGIZED. NEEDS CHANGED ASAP 3-17-16 ///SEE ORDER 4858541 FOR OUTAGE TO ISOLATE CUTOUT // DE-ENERGIZED TAP @ 1102 --- RESTORED @ 1120 CHANGED CUTOUT LEFT GROUNDED FOR TREE CUTTERS RELEASED BY CREW 077H02 RELEASED BY CREW 077S02 SEE 4858541 FOR REC OUTAGE TO ISOLATE TROUBLE VER/HFP L3/HFP
24861 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2022-07-26 15:56 | 2022-07-26 16:45 | 1 | 49 | 4587881 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | center phase fuse blown,by pass lead on center phase laying against pole causing pole to burn//opened 3 LF on pole 1107-2 to make repairs//restored @16:45
24862 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-07-18 13:01 | 2015-07-18 13:50 | 1 | 49 | 4906841 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | POLE 115-2053 6T FUSE BROKE REPLACED VER/KEP
24863 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-04-06 14:56 | 2011-04-06 15:45 | 1 | 49 | 50772-1 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION RESQUEEZED ONE HOT LEG FULL POWER CLOSE TICKET VER/HFP L3/HFP
24864 | South Williamson | 3411401 | DEWEY | INEZ | 2011-10-14 16:56 | 2011-10-14 17:45 | 1 | 49 | 4982731 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY METER# 532870245 AFFECTED// CONDUCTOR HAD PULLED OUT OF SERVE-IN IN MID SPAN SPLICE OF SERVICE DROP// REPAIRED//BACK ON AT 1745//COMPLETE//EM VER/HFP L3/HFP IDC XXXX
24865 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-24 01:16 | 2014-11-24 02:05 | 1 | 49 | 4759041 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED TO MAKE REPAIRS ON 4757821
24866 | South Williamson | 3411401 | DEWEY | INEZ | 2016-12-30 14:51 | 2016-12-30 15:40 | 1 | 49 | 4257151 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BROKEN XFMR CUTOUT FEEDING STREET LIGHTS.CREW ENROUTE TO HELP MAKE REPAIRS VER/CRB
24867 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-03-31 14:23 | 2014-03-31 14:30 | 7 | 7 | H4547221 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE RELEASED BY CREW 078S09/TRIED BREAKER IN @1220/CAME BACK OUT/THREE CREWS PATOLLING LINE/CAN FIND NO OBVIOUS TROUBLE/VEM FAILED CUTOUT ON POLE392-A-997PATROLING LINE RELEASED BY CREW 078S09/TRIED BREAKER IN @1220/CAME BACK OUT/THREE CREWS PATOLLING LINE/CAN FIND NO OBVIOUS TROUBLE/VEM/REMAINING CUST SHOULD BE RESTORED BY 1730/VEM RELEASED BY CREW 078H14 VER/KEP IDC XXXX
24868 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-09-04 22:30 | 2009-09-04 22:37 | 7 | 7 | 66185-1 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY NEUTRAL BROKE... REPAIRED NEUTRAL ,TOOK XFMR OFF AT 22:30 RESTORED POWER AT 22:37//COD 7// VER/DBM IDC XXXX
24869 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-02-27 10:11 | 2011-02-27 11:00 | 1 | 49 | 63416-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT INTO, REPLACED ENTIRE SERVICE DROP// VER/DBM IDC XXXX
24870 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2013-12-24 15:50 | 2013-12-24 16:39 | 1 | 49 | 4198981 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTOR VER/SEF L3/HFP
24871 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-02-02 19:21 | 2009-02-02 20:10 | 1 | 49 | 54896-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP FOUND A BAD HOT TAP, ON THIS TRANSFORMER, HAVE IT REPLACED AND POWER IS RESTORED AT THIS LOC L3/HFP
24872 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-09-07 08:41 | 2018-09-07 09:30 | 1 | 49 | 4052571 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | restored
24873 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2018-10-22 09:11 | 2018-10-22 10:00 | 1 | 49 | 4307611 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | restored 80t primary metering fuse on 45-5201, 10:00am L3/HFP
24874 | Whitesburg | 3401301 | FLEMING | NEON | 2013-06-25 11:36 | 2013-06-25 12:25 | 1 | 49 | 4396521 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE CHANGED XFMR CUTOUT AND CLEANED BRUSH AND TREES OFF OF POLE . THIS WAS FOR A NEW SERVICE VER/CRB L/3 CRB IDC XXXX
24875 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-05-01 20:11 | 2009-05-01 21:00 | 1 | 49 | 62747-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. VER/KEP L3/KEP IDC XXXX
24876 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-03-01 09:23 | 2009-03-01 10:12 | 1 | 49 | 52700-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE ON SERV. & SECONDARY FROZE OUT == THIS ON 1 OF THE HOT LEGS == REPAIRED == POWER OK VER/KEP L3/KEP IDC XXXX
24877 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2013-11-06 19:29 | 2013-11-06 20:18 | 1 | 49 | 4016861 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVEND BAD @ XFMR. REDONE XFMR CONNECTIONS VER/HFP L3/HFP
24878 | Whitesburg | 3312901 | JENKINS | KONA | 2009-02-24 09:56 | 2009-02-24 10:45 | 1 | 49 | 51012-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT VER/TOM L3/TOM IDC XXXX
24879 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-09-01 21:32 | 2014-09-01 22:21 | 1 | 49 | 4446371 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BURNT FUSE DOOR VER/SEF VER/DKG L3/DKG
24880 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2017-02-27 11:46 | 2017-02-27 12:35 | 1 | 49 | 4425781 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN REPLACED POWER IS RESTORED AT THIS LOC AT 1235 BY AMG VER/CRB L3/HFP XXXHFP
24881 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2022-11-18 09:48 | 2022-11-18 10:37 | 1 | 49 | 4158281 | 49 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service leg was burnt into. Made repairs. Restored at 10:37.
24882 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2009-03-26 13:35 | 2009-03-26 13:42 | 7 | 7 | 61743-1 | 49 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT,RESTORED,ALL OK AFTERWARDS.POLE BURNED OVER HALF INTO,MIGHT OUGHT TO REPLACE IT.SEND TO RON RYE TECH IN PVILLE.OFF-1300,ON-1339//COD 7// VER/DBM IDC XXXX
24883 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-03-05 21:52 | 2008-03-05 22:40 | 1 | 48 | 54112-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003701// BAD CUTOUT DOOR . VER/HFP IDC XXXX
24884 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-03-23 14:48 | 2008-03-23 15:36 | 1 | 48 | 60087-1 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION IS BURNED OFF AT TRANSFORMER VER/HFP IDC XXXX
24885 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-04-27 10:33 | 2016-04-27 10:57 | 2 | 24 | 4132021 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE WAS BROKE. REPLACED THE FUSE AND POWER IS RESTORED. ONLY TWO CUSTOMERS WERE OFF.
24886 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2016-07-26 20:31 | 2016-07-26 20:55 | 2 | 24 | 4683751 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOOKS LIKE HOT TAP BROKE CREW NEEDED NEED NEW CUTOUTS AND LA 45-381 1937 GREENUP AVE. RELEASED BY CREW 078S08--CREW ON SITE---OPENED BAND O XFMRS AT 20:31---CLOSED AT 20:55---CHANGED 3 CUTOUTS AND 3 ARRESTORS---TBL TKT COMP---RMV VER/CRB
24887 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-25 11:31 | 2019-06-25 11:55 | 2 | 24 | 4592741 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 767-662//replaced cutout//restored at 11:55/complete//em/ ISO 38830767D40662/ COD 2
24888 | Hazard | 3303901 | LESLIE | HYDEN | 2008-06-19 10:42 | 2008-06-19 11:30 | 1 | 48 | 50715-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED OUT REFUSED TRANSFORMER//3303901//VER/CRB//VER/CRB
24889 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2018-06-23 18:27 | 2018-06-23 18:51 | 2 | 24 | 4653501 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 68-1018, 30-6 rotted andlaying in tree, line crew, tech, truck to pole Released by crew 078S07--crew on site--changed pole--tbl tkt comp---rmv----xfmr open @ 18:27--closed @ 18:51/ ISO 38830068B01017/ COD 2
24890 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-03-13 13:50 | 2010-03-13 14:38 | 1 | 48 | 66401-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 353-264 WILL HAVE TO OPEN RECLOSER ON 353-245 TO ISOLATE ONLY SERVES COAL CO,OPENED RECLOSER AT 13:50 REPLACED CUTOUT RESTORED POWER AT 14:38//VER/CRB IDC XXXX
24891 | Hazard | 3309003 | JEFF | VIPER | 2017-02-11 13:32 | 2017-02-11 14:20 | 1 | 48 | 4386231 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE VER/CRB L3/HFP XXXHFP
24892 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-01-27 12:48 | 2020-01-27 13:36 | 1 | 48 | 4342351 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout on pole 1123-6598///opened at 12:48 closed at 13:36///complete BR//LIFTED CLAMP ON POLE 39831123D26597
24893 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2019-04-07 22:57 | 2019-04-07 23:13 | 3 | 16 | 4067641 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad transformer cutout. I opened the transformer at 22:57, and closed back at 23:13. Pole will need to be replaced, send a copy to Bill Johnson./ ISO 38821089A00043/ COD 3 L3/HFP
24894 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2016-02-22 10:15 | 2016-02-22 10:27 | 4 | 12 | 4746451 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON POLE 38830785D20587 TO REPLACE CUTOUT ON POLE 38830785D20772. RELATED TO OUTAGE 4746081.CLOSED 1015 ON 1027 VER/AWD
24895 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-07-21 20:01 | 2016-07-21 20:13 | 4 | 12 | 4665241 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ***SEE 4662931*** OPENING LINE FUSE SO TAP CAN BE MADE BACK UP IN TRANSFORMER ON POLE 39831148A00614/ ISO 39831148A00464/ COD 4/ 2001 TO 2013/ VER/BOW
24896 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-03-05 14:42 | 2018-03-05 15:30 | 1 | 48 | 4968041 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on transformer B phase,made new connection/ ISO 37830247C00261/ COD 1
24897 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-04-11 19:37 | 2016-04-11 20:25 | 1 | 48 | 4082401 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP @ POLE,REPAIRED VER/CRB
24898 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-12-07 11:15 | 2017-12-07 11:31 | 3 | 16 | 4628381 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED L/F 37830156000165 TO REPLACE INSULATER ON POLE 37830156000162//OPENED 1115 CLOSED 1131
24899 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2016-05-27 19:12 | 2016-05-27 20:00 | 1 | 48 | 4266311 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 357-238, MADE REPAIRS, GOT BACK ON AT 20:00. VER/CRB
24900 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2021-10-04 12:37 | 2021-10-04 13:25 | 1 | 48 | 4315221 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link had pulled apart in side cutout door. I installed new fuse and restored @ 13:25
24901 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-07-15 14:14 | 2014-07-15 14:38 | 2 | 24 | H4247061 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4247061//OPENED FUSE ON POLE 170-139 AT 14:14 AND CLOSED AT 14:38..SERVICE RESTORED.//COD 1// VER/DBM VER/DKG L3/DKG
24902 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-04-07 19:12 | 2013-04-07 20:00 | 1 | 48 | 4986141 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVEN FROZE OUT AT THE TRANSFORMER ON ON OF THE SECONDARY PHASE CONDUCTORS. ///VER/CRB L/3 CRB IDC XXXX
24903 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-08-08 14:56 | 2018-08-08 15:44 | 1 | 48 | 4927271 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I had to replace a bad connection at the weather head. Power is restored.//COD 1
24904 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-01-13 14:57 | 2021-01-13 15:45 | 1 | 48 | 4866911 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew requir4d bad connection
24905 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-03-29 15:48 | 2021-03-29 16:12 | 2 | 24 | 4400921 | 48 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | fuse pulled apart inside door, refused and restored
24906 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-04-12 16:36 | 2009-04-12 17:00 | 2 | 24 | 51661-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND FUSE LINK TO BE ROTTEN AND BROKEN, I REPLACED AND POWER IS RESTORED AT THIS LOC//3110903//VER/CRB IDC XXXX
24907 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-02-05 13:11 | 2008-02-05 13:27 | 3 | 16 | 66452-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000802RELEASED BY CREW 078H05//1311 OPENED REC TO MAKE REPAIRS ON BURNT CROSSARMS/VER/CRB IDCC PN93 XXXX
24908 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-09-03 20:55 | 2015-09-03 21:43 | 1 | 48 | 4196251 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | OLD FUSE BROKE, REFUSED XMF APR AT 2143 CLOSE TICKET// VER/ ADH
24909 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-06-30 11:54 | 2015-06-30 12:10 | 3 | 16 | 4696261 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | TOMMY OPENING LINE FUSE TO SAFELY TRANSFER WIRE//COD 3 VER/CRB
24910 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-06-29 12:13 | 2017-06-29 12:37 | 2 | 24 | 4057771 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED TRANSFORMER TO SAFELY REPLACE CUTOUT--CREW ON SITE--OPENED XFMR AT 12:13--REPAIRED CUTOUT CLOSED XFMR AT 12:37---TBL TKT COMP--RMV 38830069D16034 VER/AWD
24911 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-04-30 16:15 | 2008-04-30 16:39 | 2 | 24 | 55775-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRING NO. 4 COPPER BROKE AT CONNECTION OFF AT 1615 BACK ON AT 1639 VER/HFP IDC XXXX
24912 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-02-10 00:32 | 2011-02-10 01:20 | 1 | 48 | 55802-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE OR MELTED OUT. STAYED IN FOR ONE HOUR WHEN I FUSED IT UP AT 23:30 DUE TO FUSE TAIL BEING BROKE. MAY HAVE JUST GOTTEN A BAD FUSE. SERVICES LOOK OK - IF IT GOES OUT AGAIN WELL HAVE TO CHANGE XFMR. RE-FUSED @ 01:20. STILL IN 25 MINUTES LATER. SH VER/PDP IDC XXXX
24913 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-03-02 14:42 | 2010-03-02 15:30 | 1 | 48 | 62283-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUT OUT. VER/KEP L3/KEP IDC XXXX
24914 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-10-11 11:12 | 2016-10-11 12:00 | 1 | 48 | 4985121 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SQUEEZE ON COMPLETE// VER/ ADH L3/HFP XXXHFP
24915 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-04-14 15:22 | 2016-04-14 16:10 | 1 | 48 | 4091861 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUN OPEN SECONDARY DOWN ON GROUND HOT BETWEEN 205-77 &205-259 OPENED TRANSFORMER ON POLE 78 AT 15:51 REPAIRS MADE POWER RESTORED AT 16:10// VER/ ADH
24916 | Hazard | 3303902 | LESLIE | WOOTON | 2008-07-13 23:30 | 2008-07-14 00:18 | 1 | 48 | 52049-1 | 48 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL HAVE TO CHANGE XFMR 300 VOLTS ACROSS HOT LEADS ** AT 2202- JEFF BAKER ENROUTE TO REPLACE TR SERVICER OPENED TR AT 2330- CLOSED AT 2350. IDCC TOF2036 XXXX
24917 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-12-09 09:03 | 2011-12-09 09:50 | 1 | 47 | 4163901 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SERVICE DROP.. /// VER/CRB IDCC PN80 XXXX
24918 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-02-05 12:43 | 2015-02-05 13:30 | 1 | 47 | 4992891 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING A BAD CUTOUT/ ISO 38830258000007/ COD 1//COMPANY CREW CHANGING BAD CUTOUT ///FETR 14:00//RMV/ VER/BOW L3/HFP XXX
24919 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-10-20 17:28 | 2008-10-20 18:15 | 1 | 47 | 57451-1 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP PATROLING LINE-BROKEN FUSE COD-1 IDC XXXX
24920 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-07-13 21:43 | 2011-07-13 22:30 | 1 | 47 | 4544361 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO REPLACE DOOR. I CHANGED CUTOUT DOOR AND CLOSED TRANS. FUSE IN AND IT STAYED.//COD 1// VER/DBM IDC XXXX
24921 | Hazard | 3303902 | LESLIE | WOOTON | 2010-10-22 08:18 | 2010-10-22 09:05 | 1 | 47 | 62027-1 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE REPLACED IT//COD 1// VER/DBM IDC XXXX
24922 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-12-06 11:37 | 2010-12-06 12:24 | 1 | 47 | 63584-1 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-1 ISO TF 38830115C00343 VER/HFP L3/HFP IDC XXXX
24923 | South Williamson | 3200301 | BELFRY | BELFRY | 2014-01-07 18:28 | 2014-01-07 19:15 | 1 | 47 | 4255061 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. REPLACED FUSE AND POWER IS BACK ON. COD-1 ISO TF 38821014D10486 VER/HFP L3/HFP IDC XXXX
24924 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-01-17 15:58 | 2015-01-17 16:45 | 1 | 47 | 4941801 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE ON POLE 37830541000002//. WILL MAKE REPAIRS.CUT-OUT BROKE ON POLE 541-2. WILL MAKE REPAIRS. POWER RESTORED AT 16:45. 1/17/2015 VER/CRB L3/HFP XXX
24925 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-04-23 17:33 | 2022-04-23 18:20 | 1 | 47 | 4793481 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse burnt into// power restored 18:20
24926 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2015-03-01 22:53 | 2015-03-01 23:40 | 1 | 47 | 4089481 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | I REPLACED THE BROKE TRANSFORMER FUSE AND POWER IS BACK ON. VER/SEF L3/HFP XXX
24927 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-08-11 10:58 | 2015-08-11 11:45 | 1 | 47 | 4122521 | 47 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A BAD CONNECTION AT THE TRANSFORMER. VER/CRB
24928 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-07-08 14:40 | 2012-07-08 15:27 | 1 | 47 | 4599741 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CSP XFMR MAKING SIZZLING NOISE..TOOK XFMR OFF LINE..PRIMARY RISER ALMOST BURNT OUT OF PRI BUSHING.//.RETIGHTENED RISER..XFMR & VOLTAGE OK..JRV.07/08/12//COD 1
24929 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-02-13 16:35 | 2018-02-13 17:22 | 1 | 47 | 4838341 | 47 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad serve in @ pole/ ISO 38830070B43582/ COD 1
24930 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-12-24 01:13 | 2010-12-24 02:00 | 1 | 47 | 55419-1 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER BROKE. IDC XXXX
24931 | South Williamson | 3411401 | DEWEY | INEZ | 2019-07-11 16:13 | 2019-07-11 17:00 | 1 | 47 | 4696821 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFER , REPLACING OFF@ 1613 ON@ 1700
24932 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2016-03-03 10:13 | 2016-03-03 11:00 | 1 | 47 | 4806241 | 47 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER, REMADE CONNECTIONS, POWER RESTORED.,.... ONLY ONE CUST ITH PART POWER.// VER/ ADH
24933 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-10 15:29 | 2015-02-10 16:16 | 1 | 47 | 4006211 | 47 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | INSULINK PULLED APART AT WEATHERHEAD///I REPAIRED CONNECTION//RESTORED AT 16:16//COMPLETE//EM// VER/ ADH L3/HFP XXX
24934 | Hazard | 3310502 | HADDIX | CANOE | 2015-04-10 20:08 | 2015-04-10 20:55 | 1 | 47 | 4306671 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 51-129 VER/KEP
24935 | Paintsville | 3401802 | INDEX | HOSPITAL | 2022-07-17 09:58 | 2022-07-17 10:45 | 1 | 47 | 4502251 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken cutout fuse, replacing
24936 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-03-11 08:16 | 2008-03-11 09:03 | 1 | 47 | 56129-1 | 47 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK SERVICE FOR PROBLEMSFOUND LOOSE CONNECTION ON POLE(BAD SERVE-IN).REPLACED SERVE-INS WITH SQUEEZE-ONS,ALL OK AFTERWARDS VER/HFP IDC XXXX
24937 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-09-25 11:08 | 2018-09-25 11:55 | 1 | 47 | 4155081 | 47 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | insalink failed, resqueezed service
24938 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-04-12 18:30 | 2013-04-12 19:17 | 1 | 47 | 4005291 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA NEED UPGRADED TO A 25 TRUCKS OK/SEND TO MULLINS RELEASED BY CREW 078S03 // MULLINS & MORGAN & STONE & MCCANN/UPGRADING XFMR/VEM/OPEN XFMR1830/BACK IN AT1917/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO TF 38830250000237 VER/HFP L3/HFP IDC XXXX
24939 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2012-12-17 14:33 | 2012-12-17 15:20 | 1 | 47 | 4475401 | 47 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38820965D00090. I REPLACED CUTOUT BUT POLE IS BURNED AT THE CUTOUT BRACKET. POLE IS OK FOR NOW. PLEASE SEND TO CLIFF FREEMAN TO HAVE POLE REPLACED. ///VER/CRB L/3 CRB
24940 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-09-27 11:21 | 2009-09-27 12:07 | 1 | 46 | 65502-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/KEP L3/KEP IDC XXXX
24941 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-12-10 22:15 | 2009-12-10 22:38 | 2 | 23 | 50250-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ((((CREW REQUIRED)))) BOTTOM CONDUCTOR IN OPEN-WIRE SECONDARY BURNT DOWN. NEED 100 FEET OF #2 AA, THREE MEN AND A BUCKET. NEED TO RE-SAG OTHER HOT CONDUCTOR ALSO. SUPERVISOR NOTIFIED. ONLY AFFECTS 1 CUSTOMER//OPENED XFRMR @ 2215 CLOSED 2238//COD 2 IDC XXXX
24942 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-10-09 08:39 | 2020-10-09 09:25 | 1 | 46 | 4538881 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link for xfmr had pulled apart inside cutout door. I installed new fuse and restored @09:25
24943 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-03-23 15:11 | 2010-03-23 15:57 | 1 | 46 | 53302-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | RELATED TO ORDER 53148-1 CREW OPENED LINE FUSE TO STRAITEN POLE AND REPAIR BROKEN GUY VER/HFP L3/HFP IDC XXXX
24944 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-04-04 16:58 | 2012-04-04 17:21 | 2 | 23 | 4646931 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BAD CUTOUT CALLED FOR BIG BUCKET 1 MAN === TOOK POWER OFF AT 1658 BACK ON AT 1721 === CHANGE CUTOUT == POWER OK//COD 2// VER/DBM IDC XXXX
24945 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2015-04-15 12:55 | 2015-04-15 13:41 | 1 | 46 | 4322341 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PLACE LOOKS TO BE VACANT. TRANSFORMER FUSE HAS BROKE, ILL REPLACE THE FUSE. POWER HAS BEEN RESTORED.// VER/ ADH L3/DKGXXX
24946 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-03-17 10:24 | 2015-03-17 11:10 | 1 | 46 | 4203041 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4202811//OPENED FUSE IN ORDER TO REPAIR BAD CUTOUT ON POLE 37830448C10453//COD 1// VER/DBM
24947 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-06-30 17:57 | 2020-06-30 18:20 | 2 | 23 | 4096251 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | treee foreman call vernon, said buzzing was coming from transformer, up on arrival, found bad open gap arrester bad, open solid blade on 1098-519, then proceed to 1098-659, grd and tg to myself, and clear up bad arrester restored power at 1820 to all cust//MD AND DAE MADE
24948 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-01-18 16:09 | 2011-01-18 16:55 | 1 | 46 | 62361-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 38486275 // FUSE LINK FAILED, NOT OVERLOADED ... ALL WORK COMPLETE / GXJ COD-1 ISO TF 38831122A10460 VER/HFP L3/HFP IDC XXXX
24949 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-02-05 14:55 | 2016-02-05 15:41 | 1 | 46 | 4678321 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD XFMR CUTOUT ALL CUST RESTORED @ 1541 PLEASE CLOSE TICKET THANKS.BT VER/TOM L3/TOM
24950 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-05-16 14:14 | 2011-05-16 15:00 | 1 | 46 | 4101241 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND NO SQUIRREL, BUT DID FIND A BAD CUTOUT, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC//COD 1// VER/DBM
24951 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-12-31 13:59 | 2014-12-31 14:45 | 1 | 46 | 4895091 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD BAD CONNECTION ON SEC////// REPAIRED. VER/CRB
24952 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-03-01 08:37 | 2020-03-01 09:00 | 2 | 23 | 4441921 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411902/gaj/0839/all out disp A Sanders 3518/// CSP xfm was open due to fault on open wire secondary///Closed CSP in @ 09:00 and restored service
24953 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-06-07 22:06 | 2013-06-07 22:52 | 1 | 46 | 4238301 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULL INTO//COD 1// VER/DBM IDC XXXX
24954 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-11-16 16:19 | 2009-11-16 17:05 | 1 | 46 | 62101-1 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP SERVICE WIRE BURNT IN TO L3/HFP IDCC MCCDL XXXX
24955 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-01-14 13:02 | 2018-01-14 13:25 | 2 | 23 | 4746691 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burnt up ----- replaced
24956 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-28 19:19 | 2016-02-28 20:05 | 1 | 46 | 4784411 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 117-34 BAD CONN. REPAIRED// VER/ ADH
24957 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-04-06 14:14 | 2016-04-06 15:00 | 1 | 46 | 4058701 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE APPEARS TO HAVE BROKEN IN LINE FUSE THATS NOT ON FIELDVIEW. PHASE A ONLY AND THREE CUSTOMERS AFFECTED. RESTORED @ 15:00. ONLY ONE CUSTOMER AFFECTED (THREE PHASE CUST) OFF XFMR BANK 930-823. PLEASE ADD 3 20T LINE FUSES ON 930-822 TO MAPS. THEY ONLY FEED THE TWO POLE TAP TOWARD 823 & 844. SH//MADE MDC VER/CRB
24958 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-09-13 08:19 | 2018-09-13 09:05 | 1 | 46 | 4090881 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed and burnt service neutral in two. Opened xfmr @ 8:58, repaired and closed @ 9:05. sh
24959 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-09-26 15:54 | 2008-09-26 16:40 | 1 | 46 | 51010-1 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT. HAVE TO OPEN TRANSFORMER BANK. TRANSFORMER BANK OUTAGE IN ORDER 51029-1.....DAH THIS ORDER FOR THE PART POWER// IDC XXXX
24960 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2017-04-24 19:34 | 2017-04-24 20:20 | 1 | 46 | 4678451 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT LEG HAD BURNT IN THE CLEAR, SHORTED OUT AGAINST THE NEUTRAL, REPLACED A PEICE OF COPPER , APR AT 2020 CLOSE TICKET VER/CRB L3/HFP XXXHFP
24961 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2015-05-21 10:15 | 2015-05-21 11:01 | 1 | 46 | 4450551 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM ON POLE # 187-D-120 NEEDS CHANGED //// CUSTOMER REQUESTED THAT WE WAIT TILL IN THE MORNING TO CHANGE THIS IS TRUCK ACCESSIBLE/// MAP SHOWS 25 KVA BUT THIS NEEDS UPGRADED TO 50KVA 7200 ALREADY HAS NEW CUTOUT AND BRACKET/// PLEASE SEND COPY TO TIM HALL SO HE CAN HAVE CREW CHANGE THIS IN THE MORNING/ ARRIVED 09:52 FETR 11:30 R RAY/// OFF AT 10:15 ON AT 10:37
24962 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-08-28 07:07 | 2012-08-28 07:53 | 1 | 46 | 4979281 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | FUSE HAD PULLED LOOSE ON A PHASE. REFUSED XMF APR AT 0753 CLOSE TICKET. VER/KEP IDC XXXX
24963 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-09-13 18:56 | 2008-09-13 19:42 | 1 | 46 | 62248-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001102//BROKEN FUSE LINK // VER/TOM IDC XXXX
24964 | Hazard | 3302704 | HAZARD | KENMONT | 2009-01-05 13:15 | 2009-01-05 13:38 | 2 | 23 | 51576-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3302704//LINE FUSE WAS NEVER OUT//CURRENT LIMITER ON FIRE ON XFMR AT POLE 37830320C00058// REMOVED CURRENT LIMITER AND RESTORED POWER, XFMR ON POLE 37830320C00058 WAS THE ONLY OUTAGE//VER/CRB L3/KEP IDC FIRST 2 CALLS WERE NOT ALL OUTS ESTIMATED TIME OFF AND CHANGED FROM 1249 XXXX
24965 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-11-09 16:14 | 2010-11-09 17:00 | 1 | 46 | 54389-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE....REFUSED TRANSFORMER....6 T FUSE..BB COD-1 VER/HFP L3/HFP IDC XXXX
24966 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-12-02 12:32 | 2014-12-02 13:18 | 1 | 46 | 4826171 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE DOOR BURNED INTO ON LATERAL FUSE ON POLE 38820842A00015/NOTHING ON TAP//RESTORED AT 13:18 VER/CRB
24967 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2010-10-25 14:53 | 2010-10-25 15:39 | 1 | 46 | 63380-1 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S08 COD-11 VER/HFP L3/HFP IDCC PN1074, CNT11, MCCDL XXXX
24968 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-12-01 11:39 | 2009-12-01 12:25 | 1 | 46 | 53448-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS TRANSFORMER FUSE OUT, GOING TO REFUSE TRANSFORMER, LOOK LIKE FUSE PULL INTO IDC XXXX
24969 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-03-24 19:23 | 2020-03-24 20:09 | 1 | 46 | 4506971 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Replaced door that was burnt up. apr at 2009 close ticket
24970 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-07-19 14:49 | 2013-07-19 15:35 | 1 | 46 | 4555191 | 46 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 44-105 BAD CONN ON POLE REPAIRED VER/CRB L/3 CRB
24971 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-05-19 08:26 | 2009-05-19 09:12 | 1 | 46 | 64762-1 | 46 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP FUSE BROKEN , REFUSED TRANSFORMER ... ALL WORK COMPLETE / GXJ COD-1 ISO POLE 38831098C00771 L3/HFP IDC XXXX
24972 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-12-21 13:05 | 2010-12-21 13:20 | 3 | 15 | 54822-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 38177622 // BAD CUT OUT OFF 1;05 ON 1;20//COD 3// VER/DBM IDC XXXX
24973 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-03-29 13:50 | 2022-03-29 14:05 | 3 | 15 | 4687261 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Repaired connections in service drop. Opened transformer @ 13:50 Closed @ 14:05 (no outage till TR was opened)
24974 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-03-19 10:45 | 2010-03-19 11:30 | 1 | 45 | H51673-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF H51673-1//OPENED TRANSFORMER IN ORDER TO MAKE REPAIRS @ 1045//REPAIRED SERVICE DROP.//COD 1// VER/DBM IDC XXXX
24975 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-06-02 15:00 | 2013-06-02 15:45 | 1 | 45 | 4209921 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT COD 1 ISO TF 99-24 VER/SEF IDCC TOF1412, ESTIMATED TIME OFF XXXX
24976 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-01-26 11:15 | 2022-01-26 11:30 | 3 | 15 | 4406061 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Open TR 37840384000026 (3 COD) to repair neutral found broken in a service////Off at 1115 -- On at 1130
24977 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-04-18 20:10 | 2009-04-18 20:25 | 3 | 15 | 58280-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LIFTED HOT TAPS TO ISOLATE SWITCH AND MAKE REPAIRS ON 58270// RESTORED @ 2025 VER/KEP L3/KEP IDCC TOF1852 XXXX
24978 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-05-10 23:45 | 2020-05-11 | 3 | 15 | 4821701 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2345-0000 TR outage to replace failed cutout at 37840408C00141
24979 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2017-06-04 15:40 | 2017-06-04 15:55 | 3 | 15 | 4904191 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AT POLE 38820942B11401. I OPENED THE TRANSFORMER AT 15:40 AND CLOSE BACK IN AT 15:55. SEND TO CLIFF FREEMAN TO HAVE THIS POLE REPLACED. ITS BURNED OUT AT THE CUTOUT AND THE POLE TOPIS ROTTEN. 38820942B11401 SENT TO FREEMAN/AWD.MD ENTERED. VER/AWD
24980 | Hazard | 3309302 | VICCO | JEFF | 2015-02-20 14:55 | 2015-02-20 15:10 | 3 | 15 | 4054581 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON THE SECONDARY SIDE OF TRANSF === NEED CREW AND PICKUP TO GET HILL ==== MANUAL POLE AND SOME # 2 COPPER RELEASED BY CREW 077S03 REDONE CONNECTIONS POWER RESTORED/ 1455 TO 1510/ ISO 37830323D00595/ COD 3/ VER/BOW
24981 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-03-27 10:46 | 2019-03-27 10:55 | 5 | 9 | 4029891 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGING OUT ARRESTOR/// COD 5 /// ISO 38830182B43591,,replaced arrester,,,opened @ 10:46--closed @ 10:55 complete NOTE: I CHANGED TIME OFF ON THIS ONE IN POWERON
24982 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2010-05-16 22:45 | 2010-05-16 23:30 | 1 | 45 | 63493-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T ME FUSE BROKE IDC XXXX
24983 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-04-17 21:36 | 2010-04-17 22:21 | 1 | 45 | 64711-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ON SITE, XFORMER FUSE BLOWN, REFUSING IT, FUSE ROTTED OR BROKE INTO VER/LDA IDC XXXX
24984 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-09-12 13:35 | 2014-09-12 13:50 | 3 | 15 | 4493851 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPEN WIRE SECONDARY ON GROUND STILL ENERGIZED STEVE MARTIN ON SITE--- OPENED XFORMER ON POLE 118-4112 @ 13:35 ON @13:50 VER/KEP
24985 | Hazard | 3303902 | LESLIE | WOOTON | 2010-03-02 20:00 | 2010-03-02 20:45 | 1 | 45 | 62368-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE, C/O BAD/// PROBABLY WILL NEED TO BE CHANGED OUT, PUT FIRE OUT BUT POLE IS BURNT OVER HALFWAY INTO. IT ALSO HAS TAP AND GUY ABOVE BURNT SPOT. REPLACED C/O, POWER BACK ON. POLE IS 40 CL 4. TRUCK ACCESSABLE.//VER/CRB IDC CHANGED TIME OFF FROM 1833 XXXX
24986 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-05-21 10:40 | 2010-05-21 10:55 | 3 | 15 | 65957-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL ON 2/3 WIRE BROKE AT POLE 478/1056; OPENED TRANSFORMER AT POLE 478/1055 AT 1040 HRS; REPAIRS MADE; TRANSFORMER BACK IN AT 1055 HRS; CLOSE TICKET//VER/CRB IDC XXXX
24987 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-09-03 12:35 | 2014-09-03 13:20 | 1 | 45 | 4452691 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG SEC. CREW REQD.,NEED 25 KVA ADD A PHASE INSTALLED. CUSTOMER OK TO WAIT TILL MORN 1028 BRENTWOOD DR. RELEASED BY CREW 078H12//SERVICER OPENING TRANSFORMER 1147-D3-628 TO MAKE REPAIRS//BAD UG SEC. CREW REQD.,NEED 25 KVA ADD A PHASE INSTALLED. CUSTOMER OK TO WAIT TILL MORN 1028 BRENTWOOD DR. RELEASED BY CREW 078H12..SLPICED FAULTED UNDERGROUND SERVICE.BLR..OPENED TRANS @ 12:35 ALL POWER RESTORED @ 13:20// MADE DUPLICATE OUTAGE IN HOIS FOR PART POWER AND OPENING TRANSFORMER// VER/ ADH
24988 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2013-05-13 08:40 | 2013-05-13 09:25 | 1 | 45 | 4108761 | 45 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION AT THE ENTRANCE CABLE. VER/SEF IDC XXXX
24989 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-03-01 15:30 | 2012-03-01 16:15 | 1 | 45 | 4527621 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED XFMR FUSE .IT APPEARED TO HAVED PULLED APART VER/KEP IDCC CCU XXXX
24990 | Hazard | 3303902 | LESLIE | WOOTON | 2013-07-01 17:51 | 2013-07-01 18:06 | 3 | 15 | 4435181 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT , OPENED LINE AT 1751 AND RESTORED POWER AT 1806 VER/KEP IDC XXXX
24991 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-01-14 08:55 | 2010-01-14 09:40 | 1 | 45 | 53943-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED XFMR @ 09:40. <<<<ONLY ONE CUSTOMER AFFECTED>>>> SH VER/KEP L3/KEP IDC XXXX
24992 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-03-31 10:00 | 2015-03-31 10:45 | 1 | 45 | 4245881 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING TRANSFORMER 39831098A00818/ ISO 39831098A00818/ COD 1.. CREW ON SIGHT REPLACING B PHASE TRANSFORMER DUE TO SHORTED WINDINGS.. ETR AROUND 11:30 ATTEMPTING TO NOTIFY CUST.. OPENED XFMR BANK AT 10:00 CLOSED BACK IN AT 10:45 COMPLETE../ VER/BOW
24993 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-10-15 09:55 | 2018-10-15 10:40 | 1 | 45 | 4253671 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced broke fuse link and door also // Outage pole was 38830247A30179 L3/HFP
24994 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-11-08 11:30 | 2010-11-08 12:15 | 1 | 45 | 53803-1 | 45 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | PRIMARY METERING CUTOUT BAD--HELP ON WAY//COD 1// VER/DBM L3/ JKW IDC XXXX
24995 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-08-03 14:55 | 2012-08-03 15:10 | 3 | 15 | 4889201 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RIDE AROUND LOOP ON A DOUBLE-DEADEND POLE HAD FALLEN DOWN AND WAS ALMOST TOUCHING METAL CUTOUT BRACKET AND WAS ARCING. I OPENED LINE FUSE ON POLE 73-587 AT 14:55 , FIXED PROBLEM AND CLOSED IT BACK IN AT 15:10//COD 3// VER/DBM IDC XXXX
24996 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-07-02 14:15 | 2013-07-02 15:00 | 1 | 45 | 4447791 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE BROKE @CONN SERV TO REPAIR, REPAIRS MADE POWER RESTORED PLEASE CLOSE TICKET THANKS.BT VER/CRB L/3 CRB
24997 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2020-08-12 11:00 | 2020-08-12 11:45 | 1 | 45 | 4313931 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse out on 966A1333 refused cutout,restoredpower at 11:45.
24998 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2009-04-11 08:20 | 2009-04-11 09:05 | 1 | 45 | 51406-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3002105 - FOUND BROKEN FUSE LINK. POWER RESTORED AT 0905 //VER/GAH IDC XXXX
24999 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2017-04-18 11:30 | 2017-04-18 12:15 | 1 | 45 | 4654301 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICED OUT 4/0 SER. DROP BURN INTO ON POLE 21-6649 IN ALLEY MADE NEW CONNECTIONS OFF 11:30 ON 12:15 38830021D26649 VER/AWD L3/HFP XXXHFP
25000 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-04-25 10:06 | 2018-04-25 10:51 | 1 | 45 | 4276881 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke/ ISO 37830223D41184/ COD 1
25001 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-02-20 19:00 | 2015-02-20 19:45 | 1 | 45 | 4058171 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGED POWER INTERUPTED FROM 19;00 TO 19;45 PLEASE CLOSE TICKET THANKS DWW VER/CRB L3/DKGXXXX
25002 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-09-08 14:30 | 2018-09-08 15:15 | 1 | 45 | 4058031 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad neut connection, replaced service. off @ 1430 on @ 1515 pls cls tre
25003 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-02-14 11:30 | 2020-02-14 12:15 | 1 | 45 | 4405911 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | replaced 60 drop--11:30 to 12:15--dwds021420
25004 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-08-10 23:30 | 2009-08-11 00:15 | 1 | 45 | 61601-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN NEUTRAL *** 2321- GARY BENTLEY ENROUTE TO ASSIST.OPEN NEUTRAL, BAD CONNECTION IN METERBASE OPENED XFMER TO MAKE REPAIRS IDC XXXX
25005 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2017-01-05 08:55 | 2017-01-05 09:10 | 3 | 15 | 4270021 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPOKE WITH CUSTOMER OK WITH CHECKING IN THE MORNING BUT WONT BE HOME AFTER 9:30AM// BAD SQUEEZE @ RISER, REPLACED, XFMER OFF @ 8.55 ON @ 9.10 VER/CRB L3/HFP XXXHFP
25006 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2017-10-29 18:10 | 2017-10-29 18:55 | 1 | 45 | 4510261 | 45 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | REPLACED METER VER/AWD L3/HFP XXXHFP
25007 | Paintsville | 3410602 | E.PRESTON | LANCER | 2020-01-16 14:19 | 2020-01-16 15:04 | 1 | 45 | 4312881 | 45 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2431 s lake dr // meter 190916655 secondary netural between 955b00534 & 955B00271was burned in two. it had rubbed tape on squeezon .
25008 | Hazard | 3309003 | JEFF | VIPER | 2017-04-22 10:36 | 2017-04-22 11:21 | 1 | 45 | 4667261 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSEE BROKE 37830368D40191 VER/AWD L3/HFP XXXHFP
25009 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-10-28 15:27 | 2008-10-28 16:12 | 1 | 45 | 60189-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSETAIL BROKEN//3307302//VER/CRB IDC XXXX
25010 | Hazard | 3309302 | VICCO | JEFF | 2019-11-09 18:21 | 2019-11-09 19:06 | 1 | 45 | 4015611 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Open cutout on37830347A10616 to clear up fire service cutout broke replaced power ok
25011 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-11-30 03:21 | 2019-11-30 03:36 | 3 | 15 | 4106491 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT GOING BAD WILL NEED TO REPLACE 7200 CUST SAID WE COULD PULL IN YARD Released by crew 077S01/ ISO 37840336000047/ COD 3/ 0321 - 0336
25012 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-11-12 17:00 | 2010-11-12 17:45 | 1 | 45 | 55265-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER HAD BAD CONNECTION AT WEATHERHEAD, REWORKED CONNECTIONS, CUSTOMER CHECKED AND LIGHTS WERE BACK TO NORMAL///COMPLETE// EM VER/HFP L3/HFP IDCC TOF1609 XXXX
25013 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-08-16 13:25 | 2018-08-16 13:40 | 3 | 15 | 4960451 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Found a bad connector Off @ 1325 On @ 1340
25014 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-01-19 21:14 | 2017-01-19 21:59 | 1 | 45 | 4313601 | 45 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE 38830094D26586 VER/AWD L3/HFP XXXHFP
25015 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-04-19 16:00 | 2013-04-19 16:45 | 1 | 45 | 4025781 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH VOLTAGE 133--270--NEED TO CHANGE TRANSFORMER 15 KVA 7200 BIG BUCKET WILL WORK POLE RELEASED BY CREW 077S10 ///VER/CRB L/3 CRB IDCC TOF1128, ESTIMATED TIME OFF XXXX
25016 | Hazard | 3302704 | HAZARD | KENMONT | 2020-05-18 15:45 | 2020-05-18 16:00 | 3 | 15 | 4850161 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Outage to replace down guy Off at 1545 On at 1600
25017 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-07-01 14:45 | 2019-07-01 15:30 | 1 | 45 | 4625771 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 2 CUTOUTS AND LEADS TO MAKE NEW CONNECTIONS// OPENED XFMR @ 1445 AND CLOSED @ 1530
25018 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-06-30 16:30 | 2008-06-30 17:15 | 1 | 45 | 60245-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308402// BAD CUTOUT ON POLE 302-219, LINE FUSE BLOWN ON 302-216 // NEED TO UPDATE MAP// ENTERED MD - HFP COD-1 VER/HFP IDCC CNT3, PN175, TO1400 XXXX
25019 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-06-11 11:05 | 2011-06-11 11:20 | 3 | 15 | 4291851 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT GOING BAD..SERVICE DROP OK..WILL CHANGE CUTOUT...WILL NOTE OFF & ON TIMES..//COD 3//OPENED @ 1105 //CLOSED @ 1120// VER/DBM IDC XXXX
25020 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-14 07:15 | 2009-06-14 07:30 | 3 | 15 | 62073-1 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER PATROLLING CKT ..AT 0715 SERVICER OPENED TR TO MAKE REPAIRS. PP ON 1 CUSTOMER UNTIL SERV OPENED TR. SPLIT BOLT CONN BAD. CLOSED AT 0730. IDCC TONF0757 CHANGED FROM EQUIP FAILURE TO CUST EQUIPMENT AND COUNT FROM 4, AND TIME OFF FROM 0608 XXXX
25021 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-06-02 08:30 | 2013-06-02 09:15 | 1 | 45 | 4207711 | 45 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TRANSFORMER AT POLE 306 AT 08:30 AND ON AT 09:15, REPLACED TRANSFORMER CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ CCC COD-1 ISO TF 38831122000306 VER/HFP L3/HFP IDCC CNT2 XXXX
25022 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-06-18 13:48 | 2020-06-18 14:10 | 2 | 22 | 4041551 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Neutral splice on a secondary pulled apart on pole 318-A-123, waiting on help to arrive and will need to open this XFMR to make repairs. XFMR opened from 13:48 to 14:10.
25023 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-12-16 14:41 | 2016-12-16 15:03 | 2 | 22 | H4200141 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ***SEE 4200141*** ONE BAD SECONDARY UNDERGROUND LEG, SIZE OF COND IS 350. CREW REQUIRED/ ONLY 3 CUSTOMERS AFFECTED WITH PART POWER 38830478C20582 ORIGINALLY/ OPENED 38830478C20577 (2 CUST ADD.) @ 1441 TO MOVE CONDUCTOR CLOSED @ 1503 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD) @ 1531 TO DO SOME CONNECTIONS CLOSED @ 1543 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD.) @ 1722 TO FINISH WORK CLOSED @ 1740 (REST. ALL 5 CUST)/ VER/BOW
25024 | Hazard | 3308001 | JACKSON | S.JACKSON | 2022-01-11 12:37 | 2022-01-11 13:21 | 1 | 44 | 4336071 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad connection on weatherhead
25025 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-05-30 20:16 | 2019-05-30 21:00 | 1 | 44 | 4392661 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 25kv xfm on bank pole 96-271..please send to PR..building is vacant but has active meter..can work in a.m.
25026 | South Williamson | 3200302 | BELFRY | TOLER | 2008-08-26 20:40 | 2008-08-26 21:24 | 1 | 44 | 55285-1 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200302//, ON SITE, CHECKING TROUBLE, CUTOUT BREAKING DOWN , NEEDS REPLACED, CALLED R MARCUM RELASED BY CREW 080S01//VER/CRB IDCC TOF1902, ESTIMATED TIME OFF XXXX
25027 | Cannonsburg | 3001401 | LOUISA | CITY | 2021-07-21 10:18 | 2021-07-21 10:40 | 2 | 22 | 4941461 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 7.2 kv cutout, no trucks,,,off @10:18 on @ 10:40
25028 | Hazard | 3309302 | VICCO | JEFF | 2008-12-25 15:31 | 2008-12-25 16:15 | 1 | 44 | 63924-1 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CONNECTION AT TOP OF TRL POLE BAD == REPAIRED CONNECTION == POWER OK L3/HFP IDC XXXX
25029 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-11-05 10:25 | 2008-11-05 11:09 | 1 | 44 | 62352-1 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR, BARREL LINK BURN UP.//3116102//VER/CRB IDC XXXX
25030 | Hazard | 3309302 | VICCO | JEFF | 2011-08-16 13:28 | 2011-08-16 14:12 | 1 | 44 | 4717451 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | //VER/CRB IDCC FP NULL XXXX
25031 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-04-10 18:16 | 2013-04-10 19:00 | 1 | 44 | 4996651 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK ROTTED AND BROKE REPLACE FUSE AND POWER IS RESTORED AT THIS LOC AT 1900 COD-1 ISO TF 39831023000076 VER/HFP L3/HFP IDC XXXX
25032 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2010-10-05 12:14 | 2010-10-05 12:58 | 1 | 44 | 57019-1 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK ROTTEN AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC VER/KEP L3/KEP IDC XXXX
25033 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-09-20 17:00 | 2016-09-20 17:22 | 2 | 22 | 4912351 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S04 VER/AWD
25034 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-04-05 18:43 | 2010-04-05 19:27 | 1 | 44 | 59019-1 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS MEALTED OUT-- MADE TEMPOARY REPAIRS-E MAIL TO B FRALEY TO REPAIR TUESDAY MORNING-NEED 4/0 RISER AND 1/0 SECONDARY VER/LDA IDC XXXX
25035 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-12-04 08:37 | 2015-12-04 09:21 | 1 | 44 | 4509321 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNT UP// VER/ ADH
25036 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2019-02-12 19:17 | 2019-02-12 20:01 | 1 | 44 | 4783231 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad insulink at mast. replaced all connections. pls close tre.
25037 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-03-17 13:51 | 2018-03-17 14:35 | 1 | 44 | 4022411 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I replaced bad cutout cod 1 iso 37830472000053
25038 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-03-28 15:51 | 2011-03-28 16:35 | 1 | 44 | 60007-1 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON POLE 103-220 IS BROKEN INTO I AM GOING TO CHANGE CUTOUT.//VER/CRB IDC XXXX
25039 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-01-17 21:31 | 2009-01-17 22:15 | 1 | 44 | 57850-1 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR IS BURNED OFF AT TRANSFORMER. I WILL HAVE TO OPEN IT UP LONG ENOUGH TO MAKE REPAIRS. OPENED TRANSFORMER AT 2202 AND CLOSED BACK AT 2215 VER/LDA MADE DUP FOR TRANS OUTAGE L3/KEP AJB
25040 | Hazard | 3311103 | STINNETT | WENDOVER | 2015-03-06 13:46 | 2015-03-06 14:30 | 1 | 44 | 4147121 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT 19.9// VER/ ADH
25041 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2016-03-23 19:16 | 2016-03-23 20:00 | 1 | 44 | 4875651 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END IN SERVICE DROP HAVE REPAIRS MADE ALL IS GOOD HERE AT THIS TIME VER/AWD
25042 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-03-27 12:51 | 2011-03-27 13:35 | 1 | 44 | 59689-1 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD=1 ISO TF 38830020B20285 VER/HFP L3/HFP IDC XXXX
25043 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-03-29 16:51 | 2014-03-29 17:35 | 1 | 44 | 4535001 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT SERVICER TO REPAIR.. ALL PWR RESTORED @ 17:35 PLEASE CLOSE TICKET LRM VER/CRB
25044 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-10-28 10:54 | 2013-10-28 11:38 | 1 | 44 | 4968621 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD, CHANGING ALL THREE CUTOUTS, OPEN AT 1054//CUTOUT BAD, CHANGING ALL THREE CUTOUTS, OPEN AT 1054 AND CLOSED AT1138 VER/CRB L/3 CRB
25045 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-10-09 19:16 | 2014-10-09 20:00 | 1 | 44 | 4580681 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKEN.RE FUSED// ISO 38830874000064/// COD 1// VER/BOW
25046 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-06-11 12:11 | 2013-06-11 12:55 | 1 | 44 | 4258351 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTIONS AT THE CUSTOMERS SERVICE POLE. IDC XXXX
25047 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-05-18 12:50 | 2021-05-18 13:01 | 4 | 11 | 4595661 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | PRIMARY OFF INSULATOR @ 37830077000025. off at 12:50 back on at 13:01 Released by crew 077S10
25048 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-07-02 19:44 | 2015-07-02 20:28 | 1 | 44 | 4712221 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN/// FUSE BROKE, REFUSED POWER RESTORED.// VER/ ADH
25049 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-12-08 20:11 | 2012-12-08 20:55 | 1 | 44 | 4452641 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED BROKEN FUSE LINK//COD 1// VER/DBM IDC XXXX
25050 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-03-11 09:01 | 2014-03-11 09:45 | 1 | 44 | 4467211 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED BURNT UP CUTOUT DOOR COD-1 ISO TF 38830206C02440 VER/HFP L3/HFP
25051 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2021-02-06 15:17 | 2021-02-06 15:28 | 4 | 11 | 4941251 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | customer is claiming to have low primary voltage on one phase, spoke with alan in switching and he is going to send someone from station dept to check regulators in station// riser clamp fell off of load side on pole 79-175// will have to open recloser to put riser back on//no outage till recloser 37820079000175 opened 1517 closedcustomer is claiming to have low primary voltage on one phase, spoke with alan in switching and he is going to send someone from station dept to check regulators in st
25052 | Hazard | 3308001 | JACKSON | S.JACKSON | 2012-10-10 09:45 | 2012-10-10 10:29 | 1 | 44 | H4127531 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED AT REG WK TIME TODAY. STS POLE COMPLTED COVERED IN VINES AND LINE FUSE CUTOUT IS BROKE ,CALL JIM MULLINS AND HE IS GETTING ME ONE MAN TO HELP CHANGE CUTOUT OPEN LINE FUSE AT 0945 AND CLOSED AT1029 VER/KEP IDC XXXX
25053 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-01-10 10:02 | 2012-01-10 10:46 | 1 | 44 | 4244491 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER SERVICE DROP HAD PULLED APART ON HOT LEGS AT RED TO RED SPLICES// I HAVE DROP REPAIRED//ONLY ONE CUSTOMER AFFECTED//RESTORED AT 10:47//COMPLETE//EM VER/KEP IDC XXXX
25054 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2022-04-23 17:26 | 2022-04-23 18:10 | 1 | 44 | 4793441 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | had a bad lighting arrester on transformer pole 834-D-201.//// clearded up arrester and got restored at 18:10
25055 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2020-01-02 13:46 | 2020-01-02 14:30 | 1 | 44 | 4204211 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
25056 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-09-20 09:52 | 2021-09-20 10:36 | 1 | 44 | 4258181 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad cutout//repairs made///Complete BR
25057 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-05-08 12:56 | 2008-05-08 13:40 | 1 | 44 | 58266-1 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3103101//REPLACED CUTOUT DOOR//COD 1// VER/DBM IDCC FEC49 XXXX
25058 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-02-13 07:41 | 2022-02-13 08:25 | 1 | 44 | 4478521 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout complete
25059 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-03-28 18:46 | 2016-03-28 19:30 | 1 | 44 | 4889431 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7200 CUTOUT. VER/AWD
25060 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-07-25 12:41 | 2012-07-25 13:25 | 1 | 44 | 4825181 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BREAKER OPENED// CLOSED CB AT 1325 // MAY HAVE ADDITIONAL TROUBLE ON DISTRIBUTION LINES// PATROLLING TO RECLOSER/// CLOSED CB AT 1325 VER/TOM L3/TOM
25061 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2022-01-17 17:15 | 2022-01-17 17:37 | 2 | 22 | 4370891 | 44 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Trees rubbed neutral into on customers service drop coming off trans. pole 47-C-435, line crew and tree crew coming to help with repairs, 1 customer out. Had to open trans. to make repairs, opened up @1715, made repairs and closed back in @1737. Please send a copy to P.R., he is gonna foreward on to damage claims.// email sent
25062 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-01-12 14:40 | 2018-01-12 15:24 | 1 | 44 | 4737071 | 44 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | service neu broken at pole 189-138 repaired on 1/12/18 by TL
25063 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-02-11 09:42 | 2011-02-11 10:25 | 1 | 43 | 56140-1 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING XFMR FROM TICKET 56067. OPENED 810-42 @ 9:42. CHANGED 25KVA XFMR AND CLOSED @ 10:25. SH VER/KEP IDC XXXX
25064 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-09-12 18:11 | 2019-09-12 18:54 | 1 | 43 | 4011231 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4-3 drop burned down, replacing with 2-3 triplex.replaced drop, back on at 18.54
25065 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2013-08-19 16:01 | 2013-08-19 16:44 | 1 | 43 | 4680281 | 43 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IN 3 PHASE TRANSFORMER BANK VER/SEF
25066 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-04-15 14:32 | 2009-04-15 15:15 | 1 | 43 | 54562-1 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3004301//FOUND 2 25T LINE FUSE BLOWN ON POLE 878-82, CAUSE FOUND TWO BLOWN LIGHTNING ARRESTOR ON POLE 878-83, SEND TO MR. RAYBURN TO HAVE CREW TO COME AND REPLACE THIS LIGHTNING ARRESTOR, ASAP, THIS IS FOR MARKWEST IDC XXXX
25067 | Hazard | 3303901 | LESLIE | HYDEN | 2012-11-21 14:42 | 2012-11-21 15:25 | 1 | 43 | 4413751 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS JUST BROKEN DIDNT LOOK LIKE A FAULT//COD 1// VER/DBM IDC XXXX
25068 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-09-08 18:27 | 2008-09-08 19:10 | 1 | 43 | 60423-1 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802// BAD CUTOUT. I WILL BE CHANGING OUT. OPENED UP18:27. 6T FUSE HAD BURNT OUT. CUTOUT DOOR WAS SMOKING. AND TRACKING. I LIFTED HOT LINE CLAMP TO CUTOUT. CUST SAID POWER WOULD GO OFF AND BACK ON. I GOT CUST BACK ON AT 19:10//COD 1// VER/DBM IDC XXXX
25069 | Hazard | 3309302 | VICCO | JEFF | 2010-06-08 16:26 | 2010-06-08 17:09 | 1 | 43 | H58907-1 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER MAPPED TO WRONG POLE // SHOULD BE 323-83 // OPENED TR ON POLE 323-83 @ 1702 TO MAKE REPAIRS TO RISER THAT IS BURNT OFF.CONNECTOR ON SECONDARY RISER AT XFMR 37830323D00083 FAILED OPENED XFMR AT 17:02 AND CLOSED BACK AT 17:09 ENTERED MD...HFP COD-9 ISO TF 37830323D00083 VER/HFP L3/HFP IDCC DUP FOR ORIGINAL OUTAGE XXXX
25070 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-12-15 16:00 | 2015-12-15 16:43 | 1 | 43 | 4535231 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE DROP INSULATION WAS DETERRIATED///REPLACED SERVICE DROP/// OPENED XFM@ 16:00 AND CLOSE BACK IN @ 16:43 VER/CRB
25071 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-12-05 14:47 | 2016-12-05 15:30 | 1 | 43 | 4166861 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA CAN USE TRUCK, NOONE LIVING IN TRAILER, JUST FEEDS D TO D LIGHT, HAVE FUSE OPEN AND TRANSFORMER CLEARED UP, TALKED TO CUST CAN WAIT TILL TOMMORROW//SENT TO LINE DEPT VER/CRB L3/HFP XXXHFP
25072 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-11-17 13:27 | 2008-11-17 14:10 | 1 | 43 | 65992-1 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BROKE CUTOUT I WILL REPLACE,,,BACK ON IDC XXXX
25073 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-06-05 22:02 | 2013-06-05 22:45 | 1 | 43 | 4225301 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BURNT UP CUTOUT DOOR.//COD 1// VER/DBM
25074 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-03-03 09:52 | 2009-03-03 10:35 | 1 | 43 | 54491-1 | 43 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV SPLICE FROZE OUT == ON CUST POLE == REPAIRED ==//VER/CRB IDC XXXX
25075 | Hazard | 3310502 | HADDIX | CANOE | 2011-09-19 18:00 | 2011-09-19 18:43 | 1 | 43 | 4885421 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NETURAL BEHINE CONNECTOR AT WEATHERHEAD AND WHEN WE MADE LINE HOT BURNED NETURAL IN TWO VER/HFP L3/HFP IDC XXXX
25076 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-03-17 13:40 | 2017-03-17 14:23 | 1 | 43 | 4564951 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT IS BROKE/ CUSTOMER WANTS US TO HOLD OFF ON THIS UNTIL DRYER WEATHER SO WE CAN CAN GET A TRUCK INTO THE YARD AND REPLACE/ SERVICER HAS SPOKE TO CUSTOMER AND CUSTOMER IS OK AWITH LEAVING IT FOR NOW AND SERVICER WILL REPLACE LATER/ ISO 38830292C00007/ COD 1/ OPS 035526396/ VER/BOW
25077 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-05-28 13:52 | 2013-05-28 14:35 | 1 | 43 | 4191141 | 43 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CLOSED LINE FUSE IN AT 14;35 COD-1 ISO LF 38831126A00190 VER/HFP L3/HFP IDC XXXX
25078 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-11-27 12:08 | 2008-11-27 12:50 | 1 | 42 | 52658-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR# 27461889 // BAD S/C CUTOUT DOOR IDCC CDC92 XXXX
25079 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2015-04-14 21:48 | 2015-04-14 22:30 | 1 | 42 | 4319731 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NUETRAL CONNECTION PULLED APART IN SERVICE DROP/// OPENED XFM @ 21:48 TO MAKE REPAIRS//// REPAIRS MADE AND CLOSED XFM IN @ 22:30 AND RESTORED SERVICE//// SEND COPY TO PEGGY WYSONG/ ISO 37820149A10233/ COD 1/ VER/BOW
25080 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-02-16 14:43 | 2011-02-16 15:25 | 1 | 42 | 58247-1 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION ON TRANSFORMER POLE--- POWER RESTORED. VER/HFP L3/HFP IDC XXXX
25081 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-01-01 09:33 | 2015-01-01 10:15 | 1 | 42 | 4896351 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE. 38830826000052 VER/CRB VER/DKG L3/DKGXXXX
25082 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-10-02 20:25 | 2010-10-02 21:07 | 1 | 42 | 56337-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRMR FUSE OUT.....NEW POLE & XFRMR HERE....WILL INSPECT & RE-FUSE....POLE 38821087A00515.....//....FUSE LINK HAD BROKEN....NO FAULT...REPLACED & CLOSED CUTOUT....POWER ON.....ONLY ONE CUSTOMER.....JRV...10/02/10 //VER/GAH IDCC PN14 XXXX
25083 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2021-12-27 10:37 | 2021-12-27 11:19 | 1 | 42 | 4229461 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | transformer hot tap smoking and arcing.//// tight hot tap up on middle transformer lead.
25084 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-02-19 18:53 | 2011-02-19 19:35 | 1 | 42 | 59390-1 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE SECONDARY POLE//VER/CRB IDC XXXX
25085 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2018-11-28 12:03 | 2018-11-28 12:45 | 1 | 42 | 4486391 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 connections burndt into @ weatherhead, had to go to office to get wire for repairs, will keep track of times when I open up secondary. Opened up secondary @1203, replaced all connections and restored @1245.
25086 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-02-01 09:09 | 2017-02-01 09:30 | 2 | 21 | 4351011 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE ON A SERVICE OFF POLE 1077-81, WILL HAVE TO OPEN TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. TOOK TRANS. OFF @0909 PUT BACK IN @0930, ALL REPAIRS MADE. 38831077A00081 VER/AWD L3/HFP XXXHFP
25087 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-10-15 16:27 | 2014-10-15 17:09 | 1 | 42 | 4634621 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK// COD 1// VER/ ADH
25088 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-06-22 20:07 | 2022-06-22 20:49 | 1 | 42 | 4279911 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout, apr at 2049 close ticket
25089 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-12-06 11:04 | 2018-12-06 11:18 | 3 | 14 | 4511991 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connectionat xfmr , opened xfmr at 11:04 made repairs restored at 11:18. L3/HFP
25090 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-05-01 15:05 | 2009-05-01 15:47 | 1 | 42 | 62460-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CHANGE CUTOUT COD-1 L3/HFP IDC XXXX
25091 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-12-07 14:42 | 2010-12-07 15:24 | 1 | 42 | 64114-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THERE IS A JOB TO REPLACE THIS TRANSFORMER AND CREW IS GONG TO DO IT FIRST THING IN THE MORNING 12/08 - PER DEWAYNE & CUST HAS AGREEED TO WAIT ANOTHER DAY. VER/HFP L3/HFP IDC XXXX
25092 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2014-03-04 09:41 | 2014-03-04 10:02 | 2 | 21 | 4450221 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE , REPLACED CUTOUT GATE REATORED POWER AT 10:02 VER/CRB
25093 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-07-10 11:30 | 2008-07-10 12:12 | 1 | 42 | 50655-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL REPLACE 4/3 SERV WITH 2/3,ALSO FOUND 1 POOR CONNECTION ON SEC POLE.CUST SAID ALL WAS OK AFTERWARDS VER/HFP IDCC TOF1043 XXXX
25094 | South Williamson | 3411401 | DEWEY | INEZ | 2012-10-02 10:47 | 2012-10-02 11:01 | 3 | 14 | H4105751 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE CHECKED AFTER REGULAR WORKTIME AS PER SET GUIDELINES //XFMR CUTOUT BROKE ON 744-39//GOING TO OPEN SIDE TAP ON THIS POLE WHILE I CHANGE OUT CUTOUT//HAD TAP OFF FROM 10:47 TO 11:01 COD +3//HAVE CUTOUT REPLACED//RESTORED AT 11:01//COMPLETE//EM //COD 4 + 3 IDCC DUP TO OPEN TAP XXXX
25095 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-10-12 14:15 | 2019-10-12 14:36 | 2 | 21 | 4134841 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT IN BANK,WE WILL CHANGE BOTH OUT. OFFTIME 1415 ON TIME 1436
25096 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-09-04 13:08 | 2011-09-04 13:50 | 1 | 42 | 4805551 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED VINES OFF XMF, AND CUT A BLOWN 19.9 ARESSTER IN THE CLEAR, REFUSED XMF APR AT 1350 CLOSE TICKET IDC XXXX
25097 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-07-04 19:28 | 2008-07-04 20:10 | 1 | 42 | 62375-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T CHANCE FUSE BROKE COD - 1 VER/HFP IDC XXXX
25098 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-03 13:23 | 2013-01-03 14:05 | 1 | 42 | 4566701 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER BAD SPLICE IN SERVICE DROP MADE REPAIRS RESTORED POWER AT 14:05//COD 1// VER/DBM IDC XXXX
25099 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-06-12 10:30 | 2017-06-12 11:12 | 1 | 42 | 4952451 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED AT POLE37830065A00384 @ 10:30, REPLACED XFMR CUTOUT, ALL WORK COMPLETE / GXJ VER/CRB
25100 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-12-16 16:03 | 2011-12-16 16:45 | 1 | 42 | 4183741 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ,CHANGED AND REFUSED COD-1 ISO PO @ 37830497000019 VER/HFP L3/HFP IDC NOT SURE WHEN POWER ACTUALLY WENT OUT XXXX
25101 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2018-08-30 12:03 | 2018-08-30 12:17 | 3 | 14 | 4015201 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER FOUND BROKEN CUTOUT REPLACING // COD-3 ISO TF 37820172000027 OFF 1203 ON 1217
25102 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-05-27 08:00 | 2008-05-27 08:21 | 2 | 21 | 51595-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802//REPLACED CUTOUT THAT MAY HAVE BEEN BREAKING DOWN,WAS CREATING A LOT OF BUZZING.ONCE NEW ONE WAS INSTALLED BUZZING STOPPED//COD 2// VER/DBM IDC XXXX
25103 | South Williamson | 3411401 | DEWEY | INEZ | 2022-11-16 13:00 | 2022-11-16 13:42 | 1 | 42 | 4149401 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on on 767-148//replaced cutout//restored at 13:42//complete//em
25104 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-02-06 11:28 | 2008-02-06 12:10 | 1 | 42 | 51268-1 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RESQUEZED BAD CONNECTION AT HOUSE//3002105//VER/CRB IDC XXXX
25105 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-02-03 15:00 | 2010-02-03 15:42 | 1 | 42 | 62658-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED PRIMARY NEUTRAL AND REPLACED 120 4/3 SD WITH 120 2/3 SD ... ALL WORK COMPLETE / GXJ VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 1245 XXXX
25106 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-03-07 14:30 | 2021-03-07 15:12 | 1 | 42 | 4311711 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have abroke Neutral on service drop,Pulled Meter so i can make repairs will keep up with Time..Neutral was broke at pole 99-49,Pulled Meter at 14:30 and replaced back at 15:12.
25107 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-04-26 13:36 | 2017-04-26 14:18 | 1 | 42 | 4684611 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TO REPLACE XFMR CUTOUT AND RECLOSER BYPASS SWITCHES OFF AT 13:36 REPAIRS MADE ON AT 14:18 D SAMMONS 38831053B10277 VER/AWD L3/HFP XXXHFP
25108 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2020-01-30 13:30 | 2020-01-30 13:37 | 6 | 7 | 4349421 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Changing a broken cutout on pole 151-75. Transformer open from 13:30 to 13:37 L3/HFP
25109 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-02-08 09:48 | 2011-02-08 10:30 | 1 | 42 | 55227-1 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SERVE ENDS ON SERVICE DROP, THEY HAD PULLED APART, CAUSING THIS PART POWER, HAVE REPAIRS MADE AND EVERYTHING IS OK AT THIS LOC VER/KEP IDC XXXX
25110 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-05-26 14:27 | 2021-05-26 15:09 | 1 | 42 | 4626331 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke c/o--allgood-ds052621
25111 | Hazard | 3302703 | HAZARD | HAZARD | 2011-02-25 12:30 | 2011-02-25 12:44 | 3 | 14 | 61468-1 | 42 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IS BROKEN IN 2/3 SECONDARY BETWEEN POLES 296-177 AND 296-373, 177 IS TRUCK ACCESSIBLE RELEASED BY CREW 077E02. NEED SERVICER//COMPLETE PER HAZARD OFFICE// VER/DBM IDCC TOF0911 ALLOWED 15 MIN TO REPAIR XXXX
25112 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-02-26 11:09 | 2010-02-26 11:30 | 2 | 21 | 61299-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED ROTTED FUSE COD-2 VER/HFP L3/HFP IDC XXXX
25113 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-06-08 22:18 | 2008-06-08 23:00 | 1 | 42 | 60302-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25T ME FUSE LINK BROKE VER/ARN IDC XXXX
25114 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-11-19 16:30 | 2017-11-19 17:12 | 1 | 42 | 90003731 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broken on pole 237-245/////will make repairs.l/f off 1630-1712 37830237C00014
25115 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2018-01-25 18:18 | 2018-01-25 19:00 | 1 | 42 | 4773841 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection into xfr ,,,,,repaired complete
25116 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2012-10-25 17:17 | 2012-10-25 17:38 | 2 | 21 | H4172311 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKING. TENSION SLEEVE PULLED LOOSE FROM CUST. PIPE MAST, WILL HAVE TO OPEN TRANS. AT POLE 496-217 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES.OPENED AT 17:17, CLOSED BACK IN AT 17:38 VER/KEP IDCC DUP TO OPEN FUSE XXXX
25117 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-12-28 21:34 | 2008-12-28 21:55 | 2 | 21 | H64779-1 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | GOT BAD CONNECTION ON SERVICE REPAIR CONNECTION OPEN TRANSF FUSE AT 2134, RESTORED ALL CUSTOMERS AT 2155 //VER/GAH L3/KEP IDC XXXX
25118 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2014-07-08 16:33 | 2014-07-08 17:15 | 1 | 42 | 4209761 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 21-6673 6T ME FUSE BROKE AGAIN VER/CRB
25119 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2012-01-14 23:12 | 2012-01-14 23:33 | 2 | 21 | 4261691 | 42 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830212C00068, CUTOUT BREAKING DOWN, WILL HAVE TO OPEN AND REPLACE CUTOUT . OPENED AT POLE68 AT 23:12 AND CLOSED AT 23:33. REPLACED CUTOUT, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 2 CUSTOMERS ON POLE 212-68 ONLY VER/ARN IDC XXXX
25120 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-01-30 13:15 | 2012-01-30 13:56 | 1 | 41 | 4305931 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITTING FUSE, OPENED BANK AT 1342 REPLACED CURRENT LIMITTING FUSE. APR AT 1356 VER/KEP IDC XXXX
25121 | Hazard | 3309302 | VICCO | JEFF | 2022-09-20 16:18 | 2022-09-20 16:59 | 1 | 41 | 4902341 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on transformer pole 323-65 ///Open transformer @ 16:30 //// Repaired connections //// Transformer closed @ 16:40//cod 1
25122 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-04-16 18:52 | 2013-04-16 19:33 | 1 | 41 | 4014841 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BURNT UP CUTOUT DOOR ///VER/CRB L/3 CRB IDC XXXX
25123 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-04-27 14:35 | 2011-04-27 15:16 | 1 | 41 | 66338-1 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONE PHASE HAD PULLED LOOSE AT WEATHER HEAD MADE REPAIRES APR CLOSE TICKET//VER/CRB IDC XXXX
25124 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-03-31 17:04 | 2009-03-31 17:45 | 1 | 41 | 63561-1 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTION PULLED APART. REPAIRED. SH - VER/TOM IDC XXXX
25125 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2020-02-11 20:04 | 2020-02-11 20:45 | 1 | 41 | 4394561 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired hot leg connection and refuse 45-1571
25126 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-12-11 16:23 | 2010-12-11 17:04 | 1 | 41 | 65357-1 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REDONE CONN ECTIONS ON TRANS POLE ALL CONNECTIONS GOOD . OLLEY A HAS A TICKET TO INSTALL A RECORDING VOLT METER ON THIS METER PLEASE SEND HIM ANOTHER COPY // SENT EMAIL AS REQUESTED..HFP ADJUSTED TIMES TO ALLOW TIME TO REPLACE CONNECTIONS VER/HFP L3/HFP IDC XXXX
25127 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-03-31 11:44 | 2015-03-31 12:25 | 1 | 41 | 4246821 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKE @ CUTOUT/ ISO 38830137000024/ COD 1/ VER/BOW
25128 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2020-01-16 12:28 | 2020-01-16 13:09 | 1 | 41 | 4312341 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections
25129 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-07-19 12:19 | 2013-07-19 13:00 | 1 | 41 | 4554161 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T XFORMER FUSE BROKE. VER/CRB L/3 CRB IDC XXXX
25130 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-07-03 14:19 | 2014-07-03 15:00 | 1 | 41 | 4188841 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PER GREG RATLIFF: THIS IS A KNOWN CONDITION//CUSTOMER HAS NOT CALLED THIS IN//WAS REPORTED BY METER DEPT//TIM HALL IS AWARE OF THIS BAD UG AND A JOB TO REPAIR IS IN THE OWRKS//CUST STILL HAS PARTIAL POWER AND THIER EQUIPMENT MUST STILL BE RUNNING AS THEY HAVE NEVER REPORTED THIS CONDITION THEMSELVES//EMAILED TO TIM HALL// VER/DBM
25131 | Whitesburg | 3401301 | FLEMING | NEON | 2013-11-12 08:16 | 2013-11-12 08:57 | 1 | 41 | 4030601 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | I CHECKED AND REFUSED XFMR FUSE BROKE FOR NO REASON VER/SEF
25132 | Pikeville | 3421001 | BREAKS | CITY | 2019-03-17 09:44 | 2019-03-17 10:25 | 1 | 41 | 4994691 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open in secondary will make repairs///Replaced bad connections and restored service
25133 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-12-28 22:19 | 2011-12-28 23:00 | 1 | 41 | 4212191 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD 1.6 FUSE LINK.//COD 1// VER/DBM IDC XXXX
25134 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-04-06 14:59 | 2011-04-06 15:40 | 1 | 41 | 50774-1 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#39465838 POLE 1123-5506 BAD CUTOUT REPLACED SERVICE ON VER/HFP L3/HFP
25135 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-10-13 02:45 | 2008-10-13 03:26 | 1 | 41 | 55301-1 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003///FUSE BROKE, CUTOUT DOOR DID NOT DROP, DOOR TRACKED OVER UNTIL BURNT, CHANGED CUTOUT AND DOOR VER/JHM IDCC CCU CHANGED TIME OFF FROM 0211 ESTIMATED XXXX
25136 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-06-14 13:19 | 2016-06-14 14:00 | 1 | 41 | 4346621 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT ALL CUST RESTORED @ 1400 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830184B00172/ COD 1
25137 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2018-12-31 15:31 | 2018-12-31 16:12 | 1 | 41 | 4616321 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power bad connection at trl pole.restored power at 16:12..only one customer affected..
25138 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-03-08 19:40 | 2020-03-08 20:21 | 1 | 41 | 4461441 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kva xfmr, no truck access. cust is ok to wait until tomorrow.//ops order # 035028495 //
25139 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2020-08-05 20:34 | 2020-08-05 21:15 | 1 | 41 | 4291141 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke, line fuse back in 38830093A00306 (1 CC) @ 21:15
25140 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-11-08 16:29 | 2014-11-08 17:10 | 1 | 41 | 4714081 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/ CHANGED/ POWER RESTORED 17:10/ ISO 38830139D00272/ COD 1/ VER/BOW
25141 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-04-25 18:43 | 2011-04-25 19:24 | 1 | 41 | 64789-1 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////////BAD SERVE-IN CONNECTION AT XFR,REPLACED,ALL OK AFTERWARDS COD-1 ISO SO 37820034C00008 VER/HFP L3/HFP IDC XXXX
25142 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-12-30 14:41 | 2019-12-30 15:22 | 1 | 41 | 4196591 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced connection
25143 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2014-04-13 22:15 | 2014-04-13 22:56 | 1 | 41 | 4601041 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OVER HEAD CONNECTION AT WEATHER HEAD WAS BAD. MADE REPAIRS EVERYTHING OK VER/ARN IDCC TOF2102, CNT6, ESTIMATED TIME OFF, FEC44 XXXX
25144 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-06-11 10:52 | 2008-06-11 11:33 | 1 | 41 | 62572-1 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3408402//XFR FUSE IS OUT,WILL DETERMINE CAUSEFUSE DIDNT APPEAR TO HAVE BLOWN,THINK IT JUST PULLED INTO//COD 1// VER/DBM IDC XXXX
25145 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-04-06 14:10 | 2022-04-06 14:51 | 1 | 41 | 4730301 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a Broke Neutral at weatherhead,Going to pull Meter and Make repairs,Will keep up with Time..Pulled Meter at 14:10 made repairs restored at 14:51.
25146 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-10-05 11:39 | 2014-10-05 12:20 | 1 | 41 | 4555231 | 41 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE VER/CRB
25147 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-03-27 18:54 | 2016-03-27 19:35 | 1 | 41 | 4885481 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN, REPLACED POWER IS RESTORED AT THIS LOC AT 1935/ ISO 39831145D00132/ COD 1/ VER/BOW
25148 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-07-22 14:09 | 2012-07-22 14:50 | 1 | 41 | 4794831 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WAS GOOD DOOR WAS BURNT UP, REPLACED DOOR AND REFUSED XMF. APR AT 1450 CLOSE TICKET. DWEST COD-1 ISO TF 38830477000213 VER/HFP L3/HFP
25149 | Hazard | 3310502 | HADDIX | CANOE | 2011-03-01 08:59 | 2011-03-01 09:40 | 1 | 41 | 65327-1 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OFF 9:22--ON 9:40 COD-1 ISO LF 37830169C00072 DUP IN HOIS SEE H65327-1 FOR FUSE OUTAGE TO MAKE REPAIRS VER/HFP L3/HFP IDC XXXX
25150 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2016-11-03 10:57 | 2016-11-03 11:38 | 1 | 41 | 4072101 | 41 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 92-936 15T LINE FUSE OUT NEEDS BIG BUCKET 2-1350 INS. NEEDS CHGED AND LA LINE OUT EVER TIME IN RAINS RELEASED BY CREW 078S08 VER/CRB
25151 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-11-08 10:15 | 2017-11-08 10:55 | 1 | 40 | 4541581 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutpout on recloser pole going bad it is the bypass cutout thats bad === changed 3 cutout === open nline at 10:15 to 10:55 power ok/ ISO 37830247C00531/ COD 1***SERVICER STATES SERVES 1 CUSTOMER MAP SHOWS 0
25152 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-11-12 09:00 | 2020-11-12 09:40 | 1 | 40 | 4668711 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no outage. due to bad cutout i opened transformer up @ 09:00 to replace cutout closed transformer back in @ 09:40 also made new connections on neutrals
25153 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-09-14 21:00 | 2008-09-14 21:20 | 2 | 20 | 62968-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREES IN LINE TOOK LINE OUT BUT CUSTOMER SAID THAT LIGHTS SLOWLY CAME BACK ON,LOOKS LIKE BOTTOM OF FUSE IS OUT BUT LINE IS STILL HOT RELEASED BY CREW 078E09//FOUND BAD CUTOUT DOOR WILL REPLACE CUT OUT P R TOLLIVER //POWER RESTORED AT 21:20 PR TOLLIVER VER/KEP IDC CHANGED TOF FROM 1659 ALLOWED 20 MIN FOR REPAIR XXXX
25154 | Pikeville | 3421001 | BREAKS | CITY | 2018-08-09 14:30 | 2018-08-09 14:50 | 2 | 20 | 4933211 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1430-1450Connections burning @ xfm ///Opened xfm bank @ 14:30 /// made repairs and closed xfm bank back in @ 14:50 /// everything ok now
25155 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2016-04-06 19:15 | 2016-04-06 19:25 | 4 | 10 | 4060311 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STINGER HAD BROKE ARCKING OVER TO HOTTAP, ISOLATED XMF BANK AND MADE REPAIRES/// OPENED AT 1915 APR AT 1925 CLOSE TICKET. ALSO PLEASE SEND COPY TO TECH ARMS ARE ROTTEN AND CUTOUTS ALSO NEED REPLACED/ ISO 38830454D16127/ COD 4/ VER/BOW
25156 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2010-03-08 15:10 | 2010-03-08 15:30 | 2 | 20 | 63909-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TAP AND TRANSFORMER POLE 142 AT 15:10 AND CLOSED AT 15:30, ARRESTER GROUND WRAPPED AROUND FIBERGLASS BRACKET ... CORRECTED , ALL WORK COMPLETE / GXJ//VER/CRB IDC XXXX
25157 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-03-20 10:40 | 2017-03-20 11:20 | 1 | 40 | H4571471 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 SERVICE GOING TO 139 BURNDT INTO, HAD TO OPEN THE TRANS. ON 24-B4-230 TO MAKE REPAIRS, OPENED @1040, BUT BACK ON @1120. VER/HFP L3/HFP
25158 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-10-28 10:40 | 2020-10-28 11:00 | 2 | 20 | 4591411 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | opened up xfr bank 351-230 @ 10:40 closed @ 11:00 replaced connections
25159 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-01-16 17:08 | 2014-01-16 17:48 | 1 | 40 | 4287721 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED BAD CONNECTION VER/CRB L3/HFP
25160 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-12-13 11:45 | 2013-12-13 12:25 | 1 | 40 | 4158881 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BURNT INTO NEUTRAL ON SERVICE DROP. CUST HAS DONE UPGRADE SOMETIME IN THE PAST AND CHANGED TO A 200AMP AT THE WEATHER HEAD THEY HAD PUT WIRE TOGEATHER WITH U BOLTS THIS IS A 4-3 DROP U BOLTS CAUSED WIRE TO HEAT UP AND BURN NEUTRAL AND MELT HOT CONDUCTORS. SEND COPY TO DAMAGE CLAIMS CUST COULD HAVE DAMAGE MAY OR MAY NOT CALL IN. BUT THIS IS A RESULT OF EVERY WHO DONE ELECTRICAL WORK. I CHANGED OUT DROP TO A 2/3 DROP AND MADE NEW CONNECTIONS. VER/CRB L3/HFP
25161 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-11-09 12:30 | 2012-11-09 13:10 | 1 | 40 | 4376801 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD SERVE END MELTED AND BURNT DOWN SERVICE NEUTRAL. SPLICED SERVICE DROP. ///VER/CRB L/3 CRB IDCC TOF1110 ESTIMATED TIME OFF FOR REPAIR, PN14 XXXX
25162 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-09-28 11:50 | 2013-09-28 12:30 | 1 | 40 | 4894371 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERV WIRE BROKE SERV TO REPAIR,XFMR FUSE IN @ 1230 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT//COD 1// VER/DBM L3/HFP IDC APPEARS TOOK OUT FOR REPAIR, CHANGED TIME OFF FROM 1014 XXXX
25163 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-12-05 09:25 | 2010-12-05 09:35 | 4 | 10 | 63248-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNED INTO REPLACED FUSE POWER RESTORED 935 CLOSE TICKET//COD 4// VER/DBM IDC XXXX
25164 | Hazard | 3420001 | SOFT SHELL | VEST | 2014-02-25 17:55 | 2014-02-25 18:15 | 2 | 20 | 4434191 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR GOING BAD. CHANGED INSULATOR OPENED PADMOUNT XFMR @ 17:55 CLOSED BACK @ 18:15 VER/CRB
25165 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-06-26 10:28 | 2015-06-26 11:08 | 1 | 40 | 4662021 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO 37830402B00053/ COD 1. I REPLACED BAD CUTOUT/ VER/BOW
25166 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2022-12-24 14:10 | 2022-12-24 14:20 | 4 | 10 | 4345471 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Transformer off from 14:10 to 14:20 to repair bad insulink
25167 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-11-25 09:45 | 2015-11-25 10:05 | 2 | 20 | 4484681 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONNECTIONS AND VOLTAGE CHECKED GOOD.FOUND CUTOUT BREAKING DOWN.WILL REPLACE.OPENED XFM @ 9:45 CLOSED BACK IN @ 10:05 ON POLE 215-383./ ISO 37830215B00383/ COD 2/ VER/BOW
25168 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-08-15 13:00 | 2008-08-15 13:20 | 2 | 20 | 52264-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | 3401302// REPLACED CONNECTIONS ON TRANSFORMER POLE // VER/TOM IDC CHANED START TIME FROM 1041 XXXX
25169 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-12-05 16:10 | 2014-12-05 16:50 | 1 | 40 | 4837151 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OFF @ 1610CREW ON SITE,,REPAIRS MADE, ALL POWER RESTORED // COD-1 ISO TF 38830185000018 VER/HFP L3/HFP
25170 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-11-19 12:38 | 2018-11-19 13:18 | 1 | 40 | 4459591 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Working with TV crew, outage needed so TV crew could perform there work. only one customer out bad connection at secondary pole , made repairs restored power at 13:18.only served tv booster.. L3/HFP
25171 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-11-13 11:15 | 2015-11-13 11:35 | 2 | 20 | 4442621 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED 1115 CLOSED 1135// VER/ ADH
25172 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2020-02-03 14:50 | 2020-02-03 15:30 | 1 | 40 | 4357761 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | service neutral broke at splice. opened xfm @14:50 and closed @ 15:30
25173 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-10-12 14:25 | 2011-10-12 14:45 | 2 | 20 | H4969191 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CONNECTED LOAD TO TRANSFORMER AT POLE 37830212A00100 TEMPORARILY, ON AT 11:55 . OPENED AT 14:25 AND RESTORED AT 14:45 , REPLACED 25KVA TRANSFORMER WITH SAME AND REPLACED 4/3 SD WITH 2/3 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 ///VER/CRB IDC DUP TO OPEN AND FINISH REPAIR XXXX
25174 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2018-04-02 08:46 | 2018-04-02 09:06 | 2 | 20 | 4163731 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6t fxr fuse broke complete
25175 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-07-26 19:35 | 2008-07-26 19:45 | 4 | 10 | 60607-1 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3410602//HOT LEAD BURNT OFF ON XFMR FEWORKED XFMR LEADS POWER BACK ON//COD 4// VER/DBM IDCC CNT1 XXXX
25176 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-12-17 15:20 | 2017-12-17 16:00 | 1 | 40 | 4654731 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limit fuse failed on xfm. on pole 287-154.removed needs replaced..please put in abnormal../ ISO 37830287000154/ COD 1
25177 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-11-07 15:40 | 2014-11-07 16:20 | 1 | 40 | 4711571 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 68-1373 6T FUSE BROKE REPLACED 8T// ISO 38830068A11373/ COD 1// VER/BOW
25178 | Hazard | 3303902 | LESLIE | WOOTON | 2015-04-17 12:15 | 2015-04-17 12:35 | 2 | 20 | 4329381 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING TRANSFORMER TO CHANGE BAD CUTOUT/COD 2/OPENED 1215 CLOSED 1235// VER/ ADH
25179 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-05-19 13:35 | 2020-05-19 13:45 | 4 | 10 | 4856981 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing broken cutout,,time off 13:25,,time on (trouble work order)replacing broken cutout,,time off 13:35,,time on 13:45 (trouble work order)
25180 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-10-21 13:45 | 2022-10-21 13:55 | 4 | 10 | 4052041 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN XFMR TO REPAIR BAD CONNECTION ON XFMR // COD 4 // OFF13:45 On@13:55. sh
25181 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-03-05 11:40 | 2016-03-05 12:00 | 2 | 20 | H4818391 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFMER. MUST BLOCK 1 LANE US 23 FLAGGERS REQD. NOTIFY CSX @ TRACKS. ACROSS FROM TRI-STATE PAWN @ 43 ST. RELEASED BY CREW 078S07/ RAILROAD HAS BEEN NOTIFIED RR REP SHAWN/ HAD TO OPEN LINE FUSE ON POLE 38830070A45181 TO REPAIR TRANSFORMER 38830070A41553/ ISO 38830070A45181/ COD 2/ MD DONE/ OPENED LINE FUSE 38830070A45181 @ 1140/ CLOSED LINE FUSE 38830070A45181 @ 1200// VER/ ADH
25182 | South Williamson | 3200302 | BELFRY | TOLER | 2019-11-22 09:40 | 2019-11-22 10:20 | 1 | 40 | 4055851 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr/// changed out power restored 10:20//COD 1 PER CREW
25183 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2018-01-03 06:17 | 2018-01-03 06:57 | 1 | 40 | 4701281 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Called customercould not reset breaker(elderly)Called customercould not reset breaker(elderly xfr fuse broke complete 38830207A00123
25184 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-27 04:00 | 2011-01-27 04:20 | 2 | 20 | 66090-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE ON TOP OF TRANS. HAS BROKEN DOWN AND IS ON FIRE. I AM GOING TO OPEN TRANS. I MAY NEED BIG BUCKET. I REMOVED BAD LIMITING FUSE. IDCC MCCNI, ESTIMATED TIME OFF CHANGED FROM 0304 XXXX
25185 | Hazard | 3303902 | LESLIE | WOOTON | 2017-04-21 08:20 | 2017-04-21 09:00 | 1 | 40 | 4663771 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT GATE TO GAS WELL 37830488000037 0900 VER/AWD L3/HFP XXXHFP
25186 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2022-11-11 13:25 | 2022-11-11 13:45 | 2 | 20 | 4126261 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout on pole 48-1772 that feeds padmount 1773 is broken will open line fuses on pole 48-684 and make repairs..will keep up with times..//OFF @ 1325 ON @ 1345
25187 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2012-12-18 09:35 | 2012-12-18 10:15 | 1 | 40 | 4479011 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOWERED POLE ///VER/CRB L/3 CRB
25188 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-01-16 11:02 | 2017-01-16 11:42 | 1 | 40 | 4301961 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED SERVE-IN PULLED APART, I REPLACED IT VER/CRB L3/HFP XXXHFP
25189 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-08-17 13:30 | 2011-08-17 14:10 | 1 | 40 | 4720551 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED CONNECTIONS//COD 1// VER/DBM IDCC TOF1243, ESTIMATED TIME OFF XXXX
25190 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-07-12 13:17 | 2019-07-12 13:37 | 2 | 20 | 4701711 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | open trans at 1317 sec. lead burnt off on at 1337
25191 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-04-05 10:00 | 2019-04-05 10:40 | 1 | 40 | 4059171 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hotleg got hot and burnt nuetral at the weather head causing voltage to fluctuate.. opened transformer @ 10:00 closed @ 10:40.. repairs made power restored L3/HFP
25192 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2019-11-15 09:00 | 2019-11-15 09:40 | 1 | 40 | 4036811 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer replacing cutout//opened @ 09:00____ // Closed @ _0940___ //cod 1
25193 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-12-11 13:05 | 2015-12-11 13:45 | 1 | 40 | 4526201 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CT CABINET FLASH OVER REPAIRED VER/HFP L3/HFP
25194 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-07-13 16:00 | 2011-07-13 16:20 | 2 | 20 | 4540741 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER VOLTAGE 278 -139. TRUCK ACESSIBLE. LINE CREW REQUIRED. SEND TICKET PHILLIP TOLLIVER RELEASED BY CREW 078S02//PRT ON SITE//COMPLETE AT 16:20 REPLACED TRANSFORMER 123/247 VOLTAGE POSSIBLE DAMAGE CLAIM// PRTOLLIVER COD-2 ISO TF 38830254B00242 VER/HFP L3/HFP IDC XXXX
25195 | Pikeville | 3413401 | GARRETT | GARRETT | 2015-01-11 19:15 | 2015-01-11 19:55 | 1 | 40 | 4928671 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OFF AT 19:15 . REPLCED CUTOUT AND ARRESTER , ALL WORK COMPLETE / GXJ/ ISO 37830017000064/ COD 1/ VER/BOW L3/DKGXXXX
25196 | South Williamson | 3411401 | DEWEY | INEZ | 2022-12-07 12:55 | 2022-12-07 13:35 | 1 | 40 | 4238681 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke @ 746-425 replacing now..repairs made//restored at 13:35//complete//em
25197 | Hazard | 3301401 | COMBS | COMBS | 2013-08-12 21:55 | 2013-08-12 22:15 | 2 | 20 | 4657721 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | GREG OPENING XMER TO RELOCATE C/O TO INSTALL LINE FUSE VER/SEF
25198 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-03-11 09:45 | 2015-03-11 10:05 | 2 | 20 | 4180961 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM//CUTOUT BREAKING DOWN//OPENED XFMR @ 0945 AND CLOSED BACK @ 1005//REPAIRS COMPLETE//COD 2 L3/DKGXXXX
25199 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2012-10-05 13:00 | 2012-10-05 13:20 | 2 | 20 | 4117591 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER OPENED TRANSFORMER TO REPAIR CONNECTIONS//COD 2// VER/DBM IDC XXXX
25200 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-08-28 07:45 | 2011-08-28 08:25 | 1 | 40 | 4767681 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST DID HAVE HIGH VOLTAGE 138VOLT PH TO GRD, AND139 PH, TO GRD ON THE OTHER LEG 277 PH TO PH,PULLED METER I CHECK 3 DIFFERENT TRANSFORMER IN SAME AREA ALL CHECK GOOD NEED CREW, AND 25 KVA TRANSFORMER RELEASED BY CREW 078S09 //VER/GAH IDCC TOF2234, ESTIMATED TIME OFF XXXX
25201 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2017-02-15 18:14 | 2017-02-15 18:22 | 5 | 8 | 4400801 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT ON 1089B32 CRACKED I LIFTED HOT LINE CLAMP AT 18:14 SO I COULD REPLACE CUTOUT REPLACED CUTOUT AND RESTORED POWER AT 18:22/ ISO 38821089B00032/ COD 5/ VER/BOW
25202 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-12-21 18:55 | 2008-12-21 19:35 | 1 | 40 | 61642-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3413401 -I WILL BE REPLACING BAD CUTOUT ON POLE. SHOULD HAVE REPLACED BY 19;30. REPLACED BAD CUTOUT EVERYTHING OK L3/HFP IDC XXXX
25203 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-03-13 16:52 | 2015-03-13 17:12 | 2 | 20 | 4190541 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ACTUALL FAULT POLE IS 38830115C00012/ ISO 38830115C00012/ COD REPLACE BAD CUTOUT- OPEN XFOMER@1652//COD 2//ISO//MD FILED // VER/DBM L3/DKGXXXX
25204 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-12-04 13:00 | 2014-12-04 13:20 | 2 | 20 | 4832991 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 SEC BROKE,OPEN XFMR @ 1300,XFMR FUSE IN @ 1320 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ ISO 38830184C00053/ COD 2/ VER/BOW
25205 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-11 16:05 | 2021-06-11 16:15 | 4 | 10 | 4715491 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout is cracked and arcing will be de-energizing xfmr to replace// Opened @16:05 replaced cutout and restored @16:15
25206 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-12-05 03:20 | 2008-12-05 04:00 | 1 | 40 | 54603-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308603// SERVICE CONNECTOR IS BURNED OFF AT TRANSFORMER VER/JHM L3/KEP IDC XXXX
25207 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-05-08 13:05 | 2012-05-08 13:15 | 4 | 10 | 4759601 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN @ 8032 HALL RDG PER LLOYD MCCARTY// POWER RESTORED OFF AT 13:05 ON AT 13:15 XFORM RISER LOOP BURN INTO ON PRI. NEU. LOOP//COD 4// VER/DBM IDC XXXX
25208 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-06-26 13:55 | 2020-06-26 14:15 | 2 | 20 | 4077071 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout open transformr at 1355 and closed at 1415
25209 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-11-07 13:25 | 2022-11-07 14:05 | 1 | 40 | 4110871 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | grounding lug on XFM was broke, opned XFM 1144-D4-96 @ 13:25 to make repairs, closed @ 14:05
25210 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-02-12 11:10 | 2011-02-12 11:30 | 2 | 20 | 56337-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BURNT UP CURRENT LIMITING FUSE ON TOP OF XFMR.....WILL REMOVE FUSE.....//...OPENED XFMR FUSE @ 11:10....REMOVED REMAINS OF CURRENT LIMITING FUSE....CLOSED XFMR @ 11:30....POWER ON NOW......JRV....02/12/11 VER/KEP IDC XXXX
25211 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2011-09-24 12:27 | 2011-09-24 13:07 | 1 | 40 | H4911441 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD LEG ON U.G.. NEED POWER TEMP. CUT BAD LEG AT XFORMER, OUTHER LEG STILL HOT. RELEASED BY CREW 078S01/CREW TO REPAIR U/G SERV/OPEN XFMR AT 1227/FETR 1430/VEM/REPAIRS MADE AND XFMR RESTORED 1307/PLEASE CLOSE TICKET/THANKS/VEM IDCC DUP TO OPEN TRANSF XXXX
25212 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-06-11 14:15 | 2017-06-11 14:55 | 1 | 40 | H4930491 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ***SEE 4930491*** CREW REQD. BAD LEG UG, RIGHT HAND LEG. NEED POWER TEMP INSTALLED OR REPAIRED. RELEASED BY CREW 078S07 RELEASED BY CREW 078H03,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ 1 CUSTOMER OUT OIGINAL SERVICE OUTAGE/ OPENED TRANSFORMER 1 ADD CUST/ OPENED @ 1415 CLOSED @ 1455/ ISO 38830116A00469/ COD 2/ VER/BOW
25213 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-03-12 22:15 | 2011-03-12 22:35 | 2 | 20 | 53921-1 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR POSSIBLE PROBLEM // OPENED TR POLE 1064-28 TO REWORK CONNECTIONS ON SECONDARY @ 2215 INTERRUPTING 2 CUST // RESTORED AT 2235 WILL CHECK FOR POSSIBLE PROBLEM//////BAD CONNECTION ON XFR POLE.SAID THIS WAS 3RD OR 4TH TIME SOMEONE HAD COME OUT,DIDNT WANT TO CLIMB POLE //VER/GAH IDC XXXX
25214 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2013-05-02 17:40 | 2013-05-02 17:50 | 4 | 10 | 4066321 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN SERVICE NETURAL WILL NEED TO OPEN TRANSFORMER ON POLE 449-55 MADE REPAIRS OPEN TRANS @17:40 ON 17:50 COD-4 ISO TF 37830449A40055 VER/HFP L3/HFP IDC XXXX
25215 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-03-04 12:44 | 2014-03-04 13:04 | 2 | 20 | 4450581 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 478 1053 BROKE IN HALF NEED TO OPEN RECLOSURE 454B43516 TO SAFELY ISOLATE CUTOUT//SEPARATE TIX ON RECLOSER OUTAGE VER/CRB IDC XXXX
25216 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-06-02 14:05 | 2013-06-02 14:45 | 1 | 40 | 4209881 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE . COD 1 ISO TF 260-99 VER/SEF IDCC FP99 XXXX
25217 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2017-10-17 15:43 | 2017-10-17 16:23 | 1 | 40 | 4466431 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED CUTOUT 37820171B30382 VER/AWD L3/HFP XXXHFP
25218 | Pikeville | 3421001 | BREAKS | CITY | 2020-07-07 22:00 | 2020-07-07 22:20 | 2 | 20 | 4126571 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on 220-265 will make repairs///Opened cutout @ 22:00 and Replaced broken cutout and restored service @ 22:20
25219 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-04-02 11:35 | 2022-04-02 12:15 | 1 | 40 | 4715431 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | splice gone bad causing customer to have prt power. replacing service due to all the splices in service. open transformer @ 11:35 closed 12:15
25220 | Whitesburg | 3312901 | JENKINS | KONA | 2014-04-07 11:50 | 2014-04-07 12:30 | 1 | 40 | 4581541 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4581191 - CREW LIFTED HOT TAP AT POLE 37830403A00027 TO ALLOW THEM TO SAFELY REPLACE DEFECTIVE CUTOUT COD-1 ISO PO @ 37830403A00027 VER/HFP L3/HFP
25221 | Hazard | 3309302 | VICCO | JEFF | 2011-02-18 20:45 | 2011-02-18 21:25 | 1 | 40 | 59062-1 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REMADE NEUTRAL CONNECTIONS AT TRANSFORMER.//VER/CRB IDC XXXX
25222 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-07-20 13:05 | 2022-07-20 13:45 | 1 | 40 | 4529731 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN XFMR TO REPLACE BROKE CUTOUT // COD 1 / OFF@13:05 ON@13:45
25223 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-03-18 11:55 | 2020-03-18 12:35 | 1 | 40 | 4488271 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701/gaj/outage to replace cutouts at 38830815B20193 Outage should last 30 mins from start Off at ____ On at ____/// off @ 11:55 IN @ 12:35 PLEASE CLOSE TICKET lrm
25224 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2021-12-11 15:30 | 2021-12-11 15:50 | 2 | 20 | 4180701 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Line fuse 39831098B43528 opened when tried TR fuse on 39831098B43526
25225 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-12-23 14:41 | 2019-12-23 15:21 | 1 | 40 | 4178451 | 40 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections ,,,complete
25226 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-06-01 14:15 | 2022-06-01 14:55 | 1 | 40 | 4993591 | 40 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva xfmr. complete time on 14:55
25227 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-10-31 07:51 | 2008-10-31 08:30 | 1 | 39 | 61035-1 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED XFMR. SH//3409301//VER/CRB IDC XXXX
25228 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-02-06 10:12 | 2018-02-06 10:51 | 1 | 39 | 4808741 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ETA: 1050 Sevice drop burnt down repairing now..need to send to a tec need secondery pole set to raise service acroos the road and get it above telephone .
25229 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2020-07-09 15:19 | 2020-07-09 15:58 | 1 | 39 | 4136271 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | A phase primary metering out @1151-D3-966, checking. Looks like fuse had melted out, refused A phase @1558.
25230 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2017-10-15 15:36 | 2017-10-15 16:15 | 1 | 39 | 4458471 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER, BAD 12KV DOOR. REPLACED DOOR, POWER RESTORED VER/AWD L3/HFP HFPC CDC97
25231 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-10-15 11:51 | 2012-10-15 12:30 | 1 | 39 | 4142711 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKEN..RE FUSED TRANSFORMER. ////VER/CRB L/3 CRB IDC XXXX
25232 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-01-04 14:29 | 2010-01-04 15:08 | 1 | 39 | 60244-1 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT WILL REFUSE AND SEE WHAT HAPPENS./// FUSE TAIL BROKE REFUSED POWER IS BACK ON. TIM MCCOY //VER/GAH IDC XXXX
25233 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2013-06-14 19:18 | 2013-06-14 19:31 | 3 | 13 | 4337291 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING XFMR TO MAKE REPAIRS _ CHANGE CUTOUT.CUSTOMER SEEN FIRE COMING FROM CUT-OUT. CUT-OUT ON POLE 353-37 WAS CRACKED . CHANGED CUT-OUT. TOOK POWER OFF AT 19:18 AND RESTORED POWER AT 19:31. ALSO, CUSTOMERS APPROXIMATELY 3 MIKES DOWN THE ROAD SAID THEIR POWER FLICKERED AT THE SAME TIME AS THESE CUSTOMERS. MAY BE PROBLEM ON THE REEDY/DEAN. 6/14/2013. COD 3 ISO TF 353A-37 VER/SEF IDCC TOF1726 XXXX
25234 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2015-07-30 15:06 | 2015-07-30 15:45 | 1 | 39 | 4960871 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE HOT LEG CONNECTION AND PULLED LOOSE AT WEATHERHEAD// REPAIRS MADE//RESTORED AT 15:45//COMPLETE/EM VER/CRB
25235 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-11-15 21:30 | 2019-11-15 22:09 | 1 | 39 | 4038921 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop hot legs burnt up. replaced all squeezes. pls close. tre/ 2130 opened/ ISO / 38830044D47627/ COD 22
25236 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-02-21 14:51 | 2013-02-21 15:30 | 1 | 39 | 4838071 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | PART POWER DUE TO BAD CURENT LIMIT FUSE. MADE REPAIR EVERYTHING OK COD-1 VER/HFP L3/HFP IDC XXXX
25237 | South Williamson | 3202201 | LOVELY | LOVELY | 2021-09-02 08:21 | 2021-09-02 09:00 | 1 | 39 | 4201071 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing broke cutout on 746-c-314//repairs made//restored at 9:00//complete//em
25238 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-12-18 15:06 | 2017-12-18 15:45 | 1 | 39 | 4656811 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t
25239 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2012-11-01 09:21 | 2012-11-01 10:00 | 1 | 39 | 4313241 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT ARRESTOR IN CLEAR AND RESTORED RECLOSER IDC ASSUMING ONLY 1 CUSTOMER CHANGED COUNT FROM 9 XXXX
25240 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-12-22 09:39 | 2021-12-22 10:18 | 1 | 39 | 4219501 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 129-A2-1005, power restored at 10:18.
25241 | Hazard | 3311102 | STINNETT | BEECH FORK | 2018-07-26 15:09 | 2018-07-26 15:48 | 1 | 39 | 4860181 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Stinnett/Beech Frk, pole 507-125, braces broken, arms cocked up, have outage schedualed with mines to open GOAB on 507-123 @ 15:00 hrs for repairs.OPENED GOAB @ 15:09 hrs to make repairs for aprox 30 min outage // COD-1 ISO PO @ 37830507000123 OFF @ 1509 ON @ 1548
25242 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-05-26 17:52 | 2013-05-26 18:05 | 3 | 13 | H4186551A | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN, 1 CUST HAD PART POWER. TR OUTAGED AT THE FOLLOWING TIMES... 1752-1805 1958-2007 2207-2245. CC 4. ORIGINAL OUTAGE 4186551. DUPLICATE OUTAGES H1181075-1, H1181076-1 & H1181077-1. VER/SDB IDCC CNT1 XXXX
25243 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2020-05-25 23:55 | 2020-05-26 00:34 | 1 | 39 | 4906201 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | called customer, lights going bright and ddim // Insulink in hotleg had melted exposing wire and burnt neutral in2 on service drop. I disconnect service @ 23:55 made repairs and restored @ 00:34//
25244 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-03-31 12:29 | 2017-03-31 13:08 | 1 | 39 | 4602531 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENED TRANSFORMER FUSE TO REPLACE ARRESTER. 4600611 1229-1308 37830095000202 VER/AWD AJB
25245 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-01-17 17:30 | 2011-01-17 17:43 | 3 | 13 | 61984-1 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BAD CHANGED FUSE POWER RESTORED AT 1743 CLOSE TICKET//VER/CRB IDC CHANGED TIME OFF FROM 1645 XXXX
25246 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-10-18 15:06 | 2015-10-18 15:45 | 1 | 39 | 4358951 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 LEG OF SERVICE BURNT INTO . REPAIRED SERVICE . ONLY 1 CUST. AFFECTED . VER/CRB
25247 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2016-12-14 10:16 | 2016-12-14 10:55 | 1 | 39 | 4193281 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | POLE 68-969 10T TRANS. FUSE AND DOOR BURNT UP REPLACED DOOR AND FUSE VER/CRB L3/HFP XXXHFP
25248 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-12-17 15:36 | 2017-12-17 16:15 | 1 | 39 | 90004977 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Opened trans. @1536, put back on @1615 1 additional customer
25249 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-01-17 22:02 | 2009-01-17 22:15 | 3 | 13 | H57850-1 | 39 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR IS BURNED OFF AT TRANSFORMER. I WILL HAVE TO OPEN IT UP LONG ENOUGH TO MAKE REPAIRS. OPENED TRANSFORMER AT 2202 AND CLOSED BACK AT 2215 VER/LDA L3/KEP AJB
25250 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-12-22 11:56 | 2012-12-22 12:35 | 1 | 39 | 4507791 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-415 BAD CUT OUT DOOR LIGHTS ////VER/CRB L/3 CRB
25251 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-04-18 09:31 | 2015-04-18 10:10 | 1 | 39 | 4331481 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE RESTORED/COD 1// VER/ ADH
25252 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-01-19 19:21 | 2009-01-19 20:00 | 1 | 39 | 58423-1 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | METER BURNT UP//3117601//VER/CRB DALE CHANGED THIS FROM NI/CE/NI L3/KEP
25253 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-06-05 20:45 | 2021-06-05 21:24 | 1 | 39 | 4673111 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken Cutout at 37820193D00180 Off at 2045 On at 2124
25254 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-06-05 20:45 | 2021-06-05 21:24 | 1 | 39 | 4672981 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ Pole 37820193D00180 we have a bad Trans Cutout,Opened at 20:45 and restored at 21:24..
25255 | Hazard | 3303901 | LESLIE | HYDEN | 2018-10-30 15:11 | 2018-10-30 15:50 | 1 | 39 | 4343781 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | per james gilley, cutout broken//crew req'd to replace//cod 1//feeds billboard// per james gilley, cutout broken//crew reqd to replace//cod 1//feeds billboard// REPLACED CUTOUT L3/HFP
25256 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-01-29 16:51 | 2012-01-29 17:30 | 1 | 39 | 4302981 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND CUTOUT DOOR BURNTED INTO, REPLACED AND POWER IS RESTORED AT THIS LOC//COD 1// VER/DBM IDCC FEC49 XXXX
25257 | Pikeville | 3410602 | E.PRESTON | LANCER | 2009-03-01 16:23 | 2009-03-01 17:02 | 1 | 39 | 52828-1 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STEVE HARRIS 606-886-3738 PHASE B PRIMARY METERING FUSE BLOWN. LIGHTNING ARRESTER ON POLE 113 BLOWN. ARRESTER IN CLEAR - RE-FUSED. SH VER/KEP L3/KEP IDC XXXX
25258 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2021-07-30 16:56 | 2021-07-30 17:35 | 1 | 39 | 4984781 | 39 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse door burned up, replaced and restored @ 17:35
25259 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-17 08:42 | 2016-02-17 09:20 | 1 | 38 | 4726061 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPLACED BAD SPLICE ON UG. OVER HEAD AT XFORMER./ ISO 38830164C00018/ COD 1/ VER/BOW
25260 | South Williamson | 3411401 | DEWEY | INEZ | 2014-02-22 11:00 | 2014-02-22 11:38 | 1 | 38 | 4425801 | 38 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN NEUTRAL AT HOUSE OPENED TRANSFORMER AT 1100 TO MAKE REPAIRS CLOSED BACK IN AT 1138//COD 1// VER/DBM
25261 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-12-28 10:15 | 2008-12-28 10:53 | 1 | 38 | 64613-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT//3001002//VER/CRB L3/KEP IDC XXXX
25262 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2014-09-22 09:32 | 2014-09-22 10:10 | 1 | 38 | 4518261 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SCHEDULED BAD LIGHTNING ARRESTERS REPLACING FOR POWER QUALITY CONCERNS---REPLACED 3 L/AS ON XFMR BANK AND INSTALLED ANIMAL GUARDS ON XTMR PRIM. BUSHINGS---ALL REPAIRS MADE--TBL TKT COMP/// ISO 38830021B43567//// COD 1// VER/BOW
25263 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-28 15:41 | 2011-06-28 16:00 | 2 | 19 | 4427421 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN TRANSFORMER AT 1541 AND CLOSED AT 1600 HAD CRACKED CUTOUT//COD 2// VER/DBM IDCC PN41 XXXX
25264 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-02-10 09:37 | 2022-02-10 10:15 | 1 | 38 | 4464151 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse door burnt into/// power restored 10:15
25265 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-04-15 14:24 | 2014-04-15 14:43 | 2 | 19 | 4607581 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOOK XMF OFFLINE AT 1424 PUT FIRE OUT AND REPLACED CUTOUT & ARRESTER APR AT 1443 CLOSE TICKET, POLE IS SAFE BUT NEEDS TO BE LOWERED AT LATER DATE PLEASE SEND COPY OF THIS TICKET TO LOYD R VER/CRB
25266 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2010-06-14 10:20 | 2010-06-14 10:39 | 2 | 19 | 63376-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , OPENED FUSE AT 10:20 & RESTORED POWER AT 10:10:39//VER/CRB
25267 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-06-19 08:32 | 2015-06-19 09:10 | 1 | 38 | 4608791 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT, FUSE MELTS OUT ALL THE TIME, PLEASE SEND TO D. CHRISTIAN, MAY NEED BIGGER XFMR/EMAILED CHRISTIAN/ADH// VER/ ADH
25268 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-01-10 22:12 | 2008-01-10 22:50 | 1 | 38 | 55669-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT COD-1 VER/KEP IDC XXXX
25269 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-01-02 15:17 | 2009-01-02 15:55 | 1 | 38 | 50891-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000701// FOUND THIS HOUSE TO BE VACANTED, HAS BEEN FOR ABOUT 5 YEARS,ALSO FOUND BAD CUTOUT ON POLE BEHIND HOUSE, PLEASE SEND CREW TO CHANGE CUTOUT ON MONDAY, CAN USE BUCKET ON THIS, SEND TO MR. RAYBURN TO BE TAKEN CARE OF MONDAY MORNING// VER/TOM L3/TOM IDC XXXX
25270 | Hazard | 3310502 | HADDIX | CANOE | 2013-11-13 21:05 | 2013-11-13 21:24 | 2 | 19 | 4037251 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP LOOSE ON LINE & ARCING , INSTALLED NEW HOT LINE CLAMP. ALSO FOUND MAIN LINE NEUTRAL DOWN ON THIS POLE 74-70 { 6A COPPER } WILL NEED SOME WIRE SPAN IS 230. SEND TO GLEN TO GET NEUTRAL PUT BACK UP. //MADE AED VER/CRB L3/HFP
25271 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2022-11-04 12:14 | 2022-11-04 12:52 | 1 | 38 | 4097681 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate melted down. Made repairs. Power restored at 12:52.
25272 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-05-09 22:50 | 2008-05-09 23:09 | 2 | 19 | 59312-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202/// CUTOUT DOOR BURNING.//VER/CRB IDCC TOF2058 XXXX
25273 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-09-29 16:30 | 2012-09-29 17:08 | 1 | 38 | 4098881 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4 -3 TRIPLEX HEATED UP BURNING NEUTRAL INTO..REPLACED 4-3 WITH 2-3 S/D. ///VER/CRB L/3 CRB IDCC TOF1435 ESTIMATED TIME OFF TO REPAIR XXXX
25274 | Hazard | 3303902 | LESLIE | WOOTON | 2021-01-15 11:29 | 2021-01-15 11:48 | 2 | 19 | 4870771 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | No outage ti TR fuse was opened at 1129 to change cutout that was failing--restored at 1148
25275 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-04-28 14:05 | 2009-04-28 14:43 | 1 | 38 | 54601-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER THAT IS LEAKING IS ON POLE 67A16. CALLED TIM HALL CREW IS ON THE WAY WITH NEW TRANSFORMER. I WILL KEEP UP WITH OFF AND ON TIME.TRANSFORMER OFF AT 14:05 BACK ON AT 14 ;40 COD-1 ISO POLE 37830067A00016 IDC XXXX
25276 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-08-24 17:24 | 2009-08-24 18:02 | 1 | 38 | 64232-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP BROKEN FUSE LINK /// COD-1 ISO TF 38830069D28138 L3/HFP IDC XXXX
25277 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-03-28 16:22 | 2008-03-28 17:00 | 1 | 38 | 61664-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000202// BAD CUTOUT DOOR//COD 1// VER/DBM IDC XXXX
25278 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2011-09-10 13:49 | 2011-09-10 14:27 | 1 | 38 | 4855011 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND SMALL PIECE OF OLD FUSETAIL LAYING ON PRIMARY BUSHING OF XMF, IT HAD BEEN FLASHING OVER, CLEARED FUSETAIL AND REFUSED XMF APR AT 1427 CLOSE TICKET COD-1 ISO TF 38830454D40163 VER/HFP L3/HFP IDC XXXX
25279 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-03-23 06:51 | 2008-03-23 07:10 | 2 | 19 | 60045-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301402 CUTOUT GATE BURNED INTO REPLACED GATE AND RESTORED POWER ---------------- JEFF COMBS VER/PDP IDC XXXX
25280 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-03-15 17:45 | 2015-03-15 18:23 | 1 | 38 | 4197341 | 38 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON POLE REPAIRED/ ISO 38830070B12020/ COD 1/ VER/BOW
25281 | Hazard | 3309302 | VICCO | JEFF | 2009-08-15 16:57 | 2009-08-15 17:35 | 1 | 38 | 59042-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP NEUTRAL BROKE IN SERVICE//// SPLICED SERVICE DROP. NEUTRAL SPLICE RUBBED INTO HOT LEG BURNING CONNECTIONS. POWER RESTORED. MICRO-WAVE BURNED UP. EVERYTHING ELSE OK. L3/HFP IDC XXXX
25282 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-07-02 09:42 | 2013-07-02 10:20 | 1 | 38 | 4444691 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1148-5530 BAD CUTOUT DOOR 6T REPLACED VER/CRB L/3 CRB
25283 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-19 02:00 | 2008-08-19 02:38 | 1 | 38 | 53042-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS ARCING. I BELEIVE GATE IS BURNING UP. I AM GOING TO TRY REPLACING GATE FOR NOW ** SERVICER CALLED OUT HELP WILL BE REPLACING ALL THREE CUT OUT`S . CUTOUT IS STILL ARCING, I HAVE CONTACTED CECIL SEXTON TO BRING 3 CUTOUTS AND BIG BUCKET.. **SERVICER OPEN TR CUTOUT AT 0200- CLOSED AT 0238. VER/PDP IDC XXXX
25284 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-03-07 13:33 | 2019-03-07 14:11 | 1 | 38 | 4959731 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout on pole 288-198 and 288-59 , opened line fuse on pole 59 at 13:33 closed at 14:11
25285 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2018-06-18 17:36 | 2018-06-18 18:14 | 1 | 38 | 4617801 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout complete
25286 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2020-01-03 16:52 | 2020-01-03 17:30 | 1 | 38 | 4208851 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout complete
25287 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-10-08 14:22 | 2009-10-08 15:00 | 1 | 38 | 64693-1 | 38 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR LEAKING OIL, CHANGED 15KV OUT TO A 25KV//VER/CRB IDC XXXX
25288 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2010-06-11 08:23 | 2010-06-11 09:00 | 1 | 37 | 59970-1 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | POLE 45-5034 BAD CUTOUT DOOR//COD 1// VER/DBM
25289 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-07-22 14:40 | 2014-07-22 15:17 | 1 | 37 | 4273081 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRING A FEW SPOTS ON THE SERVICE DROPBAD CONNECTIONS AT WEATHER HEAD, PULLED MTR AT 14:40, RESTORED AT 15:05 822 HIGHLAND// ISO POLE 39831123D37026
25290 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-11-14 13:28 | 2019-11-14 14:05 | 1 | 37 | 4034451 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad insulink, repaired
25291 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-08-23 13:35 | 2022-08-23 14:12 | 1 | 37 | 4785091 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9 25 kva txmf on pole 38830620000126, No one lives here can hold till tommorrowif need be. crew required. Please send Vernon an email on this.
25292 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-06-26 14:10 | 2019-06-26 14:47 | 1 | 37 | 4600971 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED L/F AND TRANSFORMER TO REPLACE BAD 15 KVA 38830068C00695//COD 6//OFF @ ON @ xfmr off @ 14:10 in @ 14:47 please close ticket LRM Released by crew 078H06
25293 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-02-06 10:35 | 2017-02-06 11:12 | 1 | 37 | H4360751 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND XFM. CUTOUT BROKEN ON POLE 286-79 WHILE RAPAIRING DD LIGHT.WILL MAKE REPAIRS.OPENED XFM.@ 10:35 AND LIFTED SIDE TAP ON POLE 286-79..MADE REPAIRS AND CLOSED BACK @ 11:12. VER/CRB L3/HFP HFPC DUP
25294 | Hazard | 3310502 | HADDIX | CANOE | 2013-04-09 17:13 | 2013-04-09 17:50 | 1 | 37 | 4991451 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CRACK CUTOUT, GOT VIRGIL HURT COMMING TO HELP CHANGE OUT. WILL OPEN TRANFORMER WHEN HE GET HERE OPEN TRANSFORMER AT 1713 AND CLOSED AT 1750//COD 1// VER/DBM IDC XXXX
25295 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-02-24 15:25 | 2014-02-24 16:02 | 1 | 37 | 4431441 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3007903 ****** // BAD CURRENT LIMMITTING FUSE WILL NEED TO DEENERGIZE XMF BANK TO SAFELY REPLACE RELEASED BY CREW 078S11 CHANGED BAD CUTOUT AND CURRENT LIMITING FUSE DWW CLOSE TICKET THANKS COD-1 ISO TF 38830454A27702 VER/HFP L3/HFP
25296 | South Williamson | 3411401 | DEWEY | INEZ | 2016-11-22 09:58 | 2016-11-22 10:35 | 1 | 37 | 4123961 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 744-456//FEEDS LIGHTS BEHIND HIGH SCHOOL//CUTOUT REPLACED///COMPLETE/// VER/DKM
25297 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-01-28 11:26 | 2014-01-28 12:03 | 1 | 37 | 4319581 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT FOUND///REPLACING///1 CUST////OFF 11:35 ON 12:03///PWR CK GOOD//COD 1
25298 | Pikeville | 3421001 | BREAKS | CITY | 2012-03-09 10:23 | 2012-03-09 11:00 | 1 | 37 | 4566471 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING FAILED CUTOUT//COD 1// VER/DBM IDC XXXX
25299 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-01-17 16:40 | 2011-01-17 17:17 | 1 | 37 | 61970-1 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKED ALL CONNECTIONS AND REMOVED CURRENT LIMITING FUSE, FOUND NOTHING WRONG // ADJUSTED TIME OFF TO ALLOW FOR TIME TO CHECK EQUIPMENT & REMOVE CURRENT LIMITING FUSE COD-1 ISO TF 37830177C00317 VER/HFP L3/HFP IDC XXXX
25300 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-11-13 18:18 | 2015-11-13 18:55 | 1 | 37 | 4445991 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED REPAIRED FUSE// VER/ ADH
25301 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2009-04-27 09:48 | 2009-04-27 10:25 | 1 | 37 | 64522-1 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | VER/HFP 1 FUSE OUT IN DELTA BANK// BROKEN FUSE LINK L3/HFP IDC XXXX
25302 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-07-12 14:00 | 2022-07-12 14:37 | 1 | 37 | 4465991 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Replacing damaged primary metering.. opened fuses @ 14:00 restore power @ 14:37, primary metering has been repaired ..
25303 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-05-11 09:53 | 2011-05-11 10:30 | 1 | 37 | 4055791 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BURNT CUTOUT GATE VER/HFP L3/HFP
25304 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-05-17 10:30 | 2021-05-17 11:07 | 1 | 37 | 4591371 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout is starting to burn a crossarm. need a 7200 cutout, by truck. across rd from baseball field. i isolated the cutout Released by crew 078H03/ off 1030 on 1107
25305 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-02-06 10:35 | 2017-02-06 11:12 | 1 | 37 | 4360751 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND XFM. CUTOUT BROKEN ON POLE 286-79 WHILE RAPAIRING DD LIGHT.WILL MAKE REPAIRS.OPENED XFM.@ 10:35 AND LIFTED SIDE TAP ON POLE 286-79..MADE REPAIRS AND CLOSED BACK @ 11:12. VER/CRB L3/HFP HFPC DUP
25306 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-01-13 13:00 | 2018-01-13 13:37 | 1 | 37 | 4744091 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Customer was only getting 60v on one phase, replaced bad conn all repaires made close ticket
25307 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-04-10 18:13 | 2013-04-10 18:50 | 1 | 37 | 4995901 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL BROKE IN SERVICE DROP.HOT LEAD PARTIALLY INTO ALSO.REPAIRS MADE, EVERYTHING GOOD..CUSTOMER STATED THAT HE HAD A WATER PUMP BURNT UP, AND IF SO THIS WOULD DEFINITELY CAUSE THAT.D LEWIS 4-10-13 VER/HFP L3/HFP IDCC TOF1540 ESTIMATED TIME OFF FOR REPAIRS XXXX
25308 | Cannonsburg | 3010603 | RUSSELL | ASHLANDOI | 2011-10-12 17:30 | 2011-10-12 18:07 | 1 | 37 | 4971681 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE/SETTING UP/WILL OPEN CUTOUTS ON 1148-553 AT 1715/FETR 1745/VEM/FOUND ALL 3 CUTOUTS TO BE BAD/NEW FETR1845/VEM/OPENED CUTOUTS 1730/CHG 3 CUTOUTS/POWER RESTORED 1807/CUTOUTS DONE ON LEAD REPAIR WO/CREATED GREEN SHEETS/PLEASE CLOSE TICKET/THANKS/VEMN COD-1 ISO LF 39831148B30553 VER/HFP L3/HFP IDCC TOF1715 XXXX
25309 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2010-11-25 08:45 | 2010-11-25 09:22 | 1 | 37 | 59468-1 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD-CUT-OUT ON POLE924-7 CHG-OUT ,POWER RESTORED. GIVE TO TECH TO HAVE POLE CHG OUT AT LATER DATE COD-1 ISO TF 39830924000007 VER/HFP L3/HFP IDCC TOF0737 XXXX
25310 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-02-01 08:38 | 2019-02-01 09:15 | 1 | 37 | 4745951 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced fuse door
25311 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-07-17 14:03 | 2008-07-17 14:40 | 1 | 37 | 53666-1 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN TRANSFORMER BANK/ BROKEN FUSE LINK//3008002//VER/CRB IDC XXXX
25312 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-11-08 13:20 | 2018-11-08 13:57 | 1 | 37 | 4380141 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 419-249 , replaced cutout restored power at 13:58..only one customer affected L3/HFP
25313 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-04-19 14:19 | 2010-04-19 14:56 | 1 | 37 | 65130-1 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE HANGING DOWN, FUSE BROKE INTO, POWER RESTORED COD-1 VER/HFP L3/HFP IDC XXXX
25314 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-10-17 10:38 | 2019-10-17 11:15 | 1 | 37 | 4159821 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke xfr cutout complete,,opened @10:51,,,closed @ 11:15
25315 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-10-21 15:48 | 2009-10-21 16:25 | 1 | 37 | 63500-1 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPAIRING BROKE CUTOUT //FETR REQUESTED //COD 1// VER/DBM IDC XXXX
25316 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-11-03 22:28 | 2021-11-03 23:05 | 1 | 37 | 4055151 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | power restored at 23;05
25317 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-05-15 13:41 | 2018-05-15 14:18 | 1 | 37 | 4352161 | 37 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,HAD TO REPLACE IT SO CUST COULD HAVE POWER FOR A NEW SERVICE AT SITE
25318 | South Williamson | 3200301 | BELFRY | BELFRY | 2015-02-11 12:13 | 2015-02-11 12:50 | 1 | 37 | 4008081 | 37 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE CUSTOMER SERVICE POLE. I REPLACED THE BAD CONNECTION AND POWER IS BACK ON. ONLY ONE CUSTOMER HAD PART POWER. VER/CRB L3/HFP
25319 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-09-16 14:06 | 2016-09-16 14:42 | 1 | 36 | 4899141 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830449C20078 , XFMR ONLY SERVES STREET LIGHT.RESTORED POWER AT 14:42.. VER/CRB
25320 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-08-30 00:31 | 2014-08-30 00:40 | 4 | 9 | 4437801 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 472-219, OPENED XFMR AT 00:31 REPLACED CUTOUT RESTORED POWER AT 00:40. VER/KEP
25321 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-01-19 22:24 | 2015-01-19 23:00 | 1 | 36 | 4945601 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE/ ISO 38830187000071/ COD 1/ VER/BOW
25322 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-09-24 18:03 | 2008-09-24 18:15 | 3 | 12 | 50300-1 | 36 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3201001//, ON SITE, CHECKING TROUBLE, PULLED XFORMER OFF AT 1803, BACK ON AT 1815, BAD CONNECTOR AT WEATHERHEAD//COD 3// VER/DBM IDC XXXX
25323 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-08-18 12:36 | 2018-08-18 12:48 | 3 | 12 | 4968311 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad place in service drop repaired opened xfmr at 12:36 to 12:48 L3/HFP
25324 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-03-23 10:10 | 2021-03-23 10:22 | 3 | 12 | 4364961 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | OPENING XFMR TO SAFLEY REPAIR FLOATING CONDUCTOR // COD 3 // OFF@1010 ON@,1022,all repairs made took xfmr off at 10:10,,,put back on at 10:22
25325 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-03-30 14:53 | 2022-03-30 15:29 | 1 | 36 | 4692211 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 223-C-292, power restored at 15:29.
25326 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2019-12-23 14:59 | 2019-12-23 15:35 | 1 | 36 | 4178511 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed in service. Replaced connections and restored @ 15:35. sh
25327 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-12-13 13:12 | 2013-12-13 13:48 | 1 | 36 | 4159721 | 36 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON HOUSE REPAIRED VER/CRB L3/HFP
25328 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-08-27 18:15 | 2022-08-27 18:51 | 1 | 36 | 4803461 | 36 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire burnt up/repairs made. tre
25329 | Pikeville | 3413401 | GARRETT | GARRETT | 2015-11-03 09:40 | 2015-11-03 10:16 | 1 | 36 | 4405381 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 37830065D00427 . FUSE BROKEN//CUST HAS 2 ACCTS WAS PUT IN ON WRONG ONE// VER/CRB
25330 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-04-25 15:57 | 2008-04-25 16:15 | 2 | 18 | 54166-1 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000903// TRANSFORMER FUSE ROTTED AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOCATION//COD 2// VER/DBM IDC XXXX
25331 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-05-31 10:40 | 2017-05-31 11:16 | 1 | 36 | 4885541 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT, APR AT 1116 CLOSE TICKET COD-1 ISO TF 38830669000008
25332 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-03-15 17:00 | 2011-03-15 17:12 | 3 | 12 | H54554-1 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN//ONLY PHASE C OPEN //OPENED OTHER 2 PHASES @ 1700 OPEN OTHER DISC AT COD-9 --- 2 ON A 1 B & 6 3 PHASE ISO LF 37830024B10001 THIS IS FOR THE A & B PHASE OUTAGE FROM 54554-1 FOR 3 CUSTOMERS VER/HFP L3/HFP IDC XXXX
25333 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2012-03-15 18:21 | 2012-03-15 18:33 | 3 | 12 | 4585871 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | E MAL TO RAYBURN--BAD ARRESTOR NEEDS REPLACED--TRUCK OK BAD TRAFFIC LOCATION MADE ABNORMAL VER/KEP IDC XXXX
25334 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-03-03 18:15 | 2017-03-03 18:21 | 6 | 6 | 4514721 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COPPER LEAD IN TOP OF CUTOUT BROKEOFF, LAYING ON TOP OF C/O, LESS THAN 10 FROM HENDRIX RELEASED BY CREW 078S07/CREW ON SITE/WILL NEED TO OUTAGE XFMR FOR REPAIRS/APROX 30 MINUTE OUTAGE/VEM/OPEN XFMR AT 1815 REPAIRS MADE AND ALL CUST RESTORED 1821/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
25335 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-11-14 12:59 | 2022-11-14 13:35 | 1 | 36 | 4141551 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE INSIDE CUTOUT DOOR. INSTALLED NEW FUSE AND RESTORED @13:35
25336 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2014-01-24 08:45 | 2014-01-24 09:03 | 2 | 18 | 4307061 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED FUSE TO SAFELY WORK ON 4306431 COD-2 VER/HFP L3/HFP
25337 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-07-03 08:01 | 2017-07-03 08:37 | 1 | 36 | 4068441 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFR CUTOUT 207-2117,,COMPLETE VER/CRB
25338 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-01-29 09:16 | 2018-01-29 09:28 | 3 | 12 | 4780881 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED AT 09:16 CLOSED AT 09:28//REPLACED INSULATER ON POLE 37830184B00249 //OPENED L/F ON POLE 37830184B00212
25339 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-05-03 07:56 | 2013-05-03 08:32 | 1 | 36 | 4067011 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD COME INTO WERE WELDED ON TOP OF LINK VER/KEP IDC XXXX
25340 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-11-17 12:30 | 2013-11-17 12:42 | 3 | 12 | H4045701 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEU WIRE BROKE AT POLE WILL NEED TO OUTAGE TRANFORMER TO MAKE REPAIRSOFF AT 12;30 BACK ON AT 12;42 ALL POWER RESTORED KWB DUP OF 4045701 FOR 3 CUST WHEN TR OPENED VER/HFP L3/HFP
25341 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-03-25 13:35 | 2019-03-25 13:53 | 2 | 18 | 4022711 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout cracked on 806-80 - no outage until line crew arrives to help replace. Opened xfmr @ 13:35, replaced cutout, bracket and arrester and closed @ 13:53. sh COD 2
25342 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-06-26 15:09 | 2018-06-26 15:45 | 1 | 36 | 4672301 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-1 ISO TF 38830875B00064..bad cutout .chgd cutout
25343 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-12-16 17:22 | 2016-12-16 17:40 | 2 | 18 | H4200141 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ***SEE 4200141*** ONE BAD SECONDARY UNDERGROUND LEG, SIZE OF COND IS 350. CREW REQUIRED/ ONLY 3 CUSTOMERS AFFECTED WITH PART POWER 38830478C20582 ORIGINALLY/ OPENED 38830478C20577 (2 CUST ADD.) @ 1441 TO MOVE CONDUCTOR CLOSED @ 1503 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD) @ 1531 TO DO SOME CONNECTIONS CLOSED @ 1543 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD.) @ 1722 TO FINISH WORK CLOSED @ 1740 (REST. ALL 5 CUST)/ VER/BOW
25344 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-02-01 18:00 | 2012-02-01 18:36 | 1 | 36 | 4313451 | 36 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS/////////SERVE-INS HAD HEATED UP AND CAUSED SOME VERY POOR ONNECTIONS. REPLACED ALL,CUST SAID ALL WAS OK ///VER/CRB IDCC TOF1549, ESTIMATED TIME OFF FOR REPAIRS XXXX
25345 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2016-07-13 12:24 | 2016-07-13 13:00 | 1 | 36 | 4623551 | 36 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | REPLACED BAD SPLICE AT METER POLE/ ISO 37830449A10478/ COD 1/ VER/BOW
25346 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-08-25 10:30 | 2017-08-25 10:48 | 2 | 18 | 4300151 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE CUTOUT ALTHO IT LOOKS OK AND ISNT MAKING ANY NOISE AT THIS TIME////////OFF@10:30,ON@10:48AFTER REPLACING CUTOUT/ ISO 38831104000099/ COD 2/ VER/BOW
25347 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-09-30 18:09 | 2008-09-30 18:45 | 1 | 36 | 52389-1 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003703// SERVICER SPOKE W/CUSTOMER THIS ONLY SERVES BARN OK TO WAIT UNTIL 10/1 - SERVICER TO CREATE ORDER//RELEASED BY CREW 078S01 IDC XXXX
25348 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-01-04 10:12 | 2010-01-04 10:48 | 1 | 36 | 59724-1 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CUST HAS 1 LEG OF SERVICE OUT, FOUND BAD SPLICE IN SECONDARY, REPAIRED RESTORED AT 1048 VER/KEP L3/KEP IDC XXXX
25349 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2018-12-31 11:45 | 2018-12-31 12:21 | 1 | 36 | 4615441 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew on site to change cutout on p# 1124-609 police on site due to traffic light out. FETR 12:45 LRM all repairs complete pwr restored @ 12:21 please close ticket LRM
25350 | Pikeville | 3407103 | TOPMOST | KITE | 2011-07-04 16:00 | 2011-07-04 16:18 | 2 | 18 | 4455421 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TRANSFORMER ON POLE 170 AT 16:00 . REPLACED CUTOUT AND CLOSED AT 16:18 , ALL WORK COMPLETE / GXJ COD-3 ISO TF 37830185000035 VER/HFP L3/HFP IDCC PN35, CNT3, TOF1426 XXXX
25351 | Whitesburg | 3312901 | JENKINS | KONA | 2009-03-14 20:00 | 2009-03-14 20:18 | 2 | 18 | 58601-1 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312901// BAD CUTOUT GOING TO REPLACE IT OPENED TRANSFORMER AT 2000 CLOSED IT AT 2018 // COD 2 // VER/TOM L3/TOM IDCC PN47 XXXX
25352 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-07-19 14:54 | 2018-07-19 15:12 | 2 | 18 | 4798391 | 36 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | broken neutral in service drop at point of attachment weatherhead opened xfmr at 14:54 closed 15:12 L3/HFP
25353 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-24 14:25 | 2018-02-24 15:00 | 1 | 35 | 4878541 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout .. replaced 27 kv cutout and 20 ft # 4 cu pole ground , xfmr off @ 14:25 and on @ 15:00 / ALL WORK COMPLETE / GXJ//NO OUTAGE TILL TRANSFORMER OPENED
25354 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-11-26 20:45 | 2014-11-26 21:20 | 1 | 35 | 4806671 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I REPLACED SERVICE DROP LOOP THAT WAS BURNED UP ON SECONDARY POLE 38820747B20417. ONLY ONE CUSTOMER OUT. I PULLED THE METER TO THE TRINITY FREEWILL BAPTIST CHURCH AT 20:45 TO REPAIR THE LOOP. VER/CRB
25355 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-03-07 17:40 | 2016-03-07 18:15 | 1 | 35 | 4825171 | 35 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | METER BAD REPLACED VER/KEP
25356 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2020-12-21 16:25 | 2020-12-21 17:00 | 1 | 35 | 4790981 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad xfer causing high voltage // opened xfer to change out @ 1625 closed @ 1700
25357 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-10-14 08:40 | 2008-10-14 09:15 | 1 | 35 | 55596-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3001002// BLOWN ARRESRER AND TRANSFORMER FUSE ON BANK POLE 38830327B00249//COD 1//ISO// VER/DBM IDC XXXX
25358 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2016-06-09 23:20 | 2016-06-09 23:55 | 1 | 35 | 4330671 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 44-446 POLE GROUND FELL ON TRANS RISER VER/KEP
25359 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-09-17 17:45 | 2014-09-17 18:20 | 1 | 35 | 4506851 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | GREG RATLIFF CALLED ABOUT THIS - SERVICE NEUTRAL BROKEN & HE IS GOING TO HELP AARON REPLACE SERVICE DROP/// REPLACED SERVICE DROP/// HAD CUSTOMER OUT FROM 17:45 TO 18:20/// ONLY 1 CUSTOMER AFFECTED VER/HFP L3/HFP
25360 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-01-11 13:55 | 2021-01-11 14:30 | 1 | 35 | 4861241 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | On pole 216-118 we have a 15 KVA Trans hanging from Cutout,Rick Ray is on way with New Trans to change out,Will keep up with Time that Trans is out..Opened Trans at 13:55 Restored at 14:30.
25361 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-12-07 13:00 | 2020-12-07 13:35 | 1 | 35 | 4750391 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required withsmall material handler/15kva/bad 10 kva Released by crew 078S03 / OFF@1300 ON@1335
25362 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2011-12-02 00:40 | 2011-12-02 01:15 | 1 | 35 | H1162360-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XGMER BAD NEED CREW.LIFTED HOT TAP @ POLE 809-262@ 12:40 RESTORED @ 01:15 //VER/GAH IDCC PN282, CDC92 XXXX
25363 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-09-21 11:55 | 2020-09-21 12:30 | 1 | 35 | 4482201 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | guy wire was patially broken. replaced guy wire. open transformer @ 11:55 closed @ 12:30
25364 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-09-07 11:47 | 2020-09-07 12:22 | 1 | 35 | 4439021 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10 lf restored @ 141-232
25365 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-04-24 13:15 | 2021-04-24 13:50 | 1 | 35 | 4476011 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | No outage till transformer was opened at 1315///cutout going bad and tracking across T bracket opened transformer and changed cutout and bracket///restored at 1350
25366 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-07-07 14:25 | 2016-07-07 15:00 | 1 | 35 | 4557121 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT ON FIRE AT 183-209, GOING TO OPEN TRANSFORMER TO CHANGE/OPENED 1445 CLOSED 1500//ALL POWER RESTORED VER/AWD
25367 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-09-22 15:41 | 2008-09-22 16:16 | 1 | 35 | 66284-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CHANGED OUT BROKEN CUTOUT ON XFORM. POLE 1123-1578 IDC XXXX
25368 | Pikeville | 3407103 | TOPMOST | KITE | 2021-11-23 10:55 | 2021-11-23 11:30 | 1 | 35 | 4118221 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Nuetral broke at splice.//Opened xfm to make repairs//No other customer affected.// Opened 10:55.// Closed 11:30
25369 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-01-12 17:55 | 2015-01-12 18:30 | 1 | 35 | 4931281 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE MELTED OUT ON POLE 165-139 15 T 18:30 COD 1// VER/ ADH
25370 | Hazard | 3303902 | LESLIE | WOOTON | 2020-05-21 13:15 | 2020-05-21 13:50 | 1 | 35 | 4879841 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | opened transformer to replace anchor and guy opened at 13:15 closed backat13:50
25371 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-10-14 16:10 | 2010-10-14 16:45 | 1 | 35 | 59796-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE TO ISOLATE CUTOUT THAT FAILED CAUSING POLE FIRE.. SEE 59785-1 FOR ORIGINAL CALL REPORTING POLE FIRE COD-1// I OPENED TRANSFORMER ON POLE 42B452 AT 16:10 DUE TO BAD CUTOUT. WILL BE CHANGING OUT // SEE 59796-1 FOR OUTAGE I OPENED TRANSFORMER ON POLE 42B452 AT 16:10 DUE TO BAD CUTOUT. WILL BE CHANGING OUT. CUTOUT CHANGED TRANSFORMER BACK ON AT 16:45. EVERYTHING OK. SEND COPY TO ENG PIKEVILLE BURNT A PLACE ABOUT 3 INCHES DEEP IN BACK SIDE OF POLE. VER/HFP L3/HFP IDC XXXX
25372 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2020-08-23 21:30 | 2020-08-23 22:05 | 1 | 35 | 4362011 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found bad cutout while i was re sagging drop.lifted hot tap replaced cutout. opened cutout out at 21:30. back on at 22.05
25373 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-03-17 14:25 | 2015-03-17 15:00 | 1 | 35 | 4204381 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN ON POLE # 155-82, CUTOUT GATE BURNT UP. REPLACED GATE, RESTORED POWER COD-1 ISO TF 37830155C10203 VER/HFP L3/HFP
25374 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-11-18 15:55 | 2020-11-18 16:30 | 1 | 35 | 4706321 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connections @ weatherhead is burnt up ///Opened xfm @ 15:55 to make repairs/// Repairs made closed xfm back in @ 16:30 and restored service
25375 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-05-07 13:05 | 2010-05-07 13:40 | 1 | 35 | 56914-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1 FUSE IS OUT ON BANK OF XFMRS, FUSE BROKE VER/KEP L3/KEP IDC XXXX
25376 | Pikeville | 3407101 | TOPMOST | DEMA | 2014-07-18 13:20 | 2014-07-18 13:55 | 1 | 35 | 4259501 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED XFMR POE 178 AT 13:20, REPLACED CUTOUT AND CLOSED AT 13:55 // ALL WORK COMPLETE / GXJ//COD 1// VER/DBM
25377 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-06-25 18:30 | 2018-06-25 19:05 | 1 | 35 | 4663461 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened transformer up at 18:30 due to bad cutout changed cutout closed transformer back in at 19:05
25378 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-01-18 16:05 | 2011-01-18 16:40 | 1 | 35 | 62290-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTS VOLTAGE READING GOOD...CHECKED MTR BASE, ENTRANCE, SERVICE, & XFMR ALL CONNECTIONS GOOD BUT DID REPLACE A FEW NEUTRAL CONNECTIONS ON SERVICE & XFMR THAT LOOKED SUSPECT....TALKED TO NEIGHBOR ON SAME XFMR....THEY ARENT HAVING ANY PROBLMS....TOLD CUST TO CHECK THEIR INSIDE BREAKER BOX...MORE THAN LIKELY, ITS CUST TROUBLE.....JRV.....01/18/11 // ADJUSTED TIME OFF TO ALLOW TIME TO CHECK & REPAIR.. COD-1 VER/HFP L3/HFP IDC XXXX
25379 | Hazard | 3302704 | HAZARD | KENMONT | 2013-08-14 21:25 | 2013-08-14 22:00 | 1 | 35 | 4666481 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BROKE IN 2 DEFFERENT PLACES. NEEDS POLE SET IN LINE 227 SPAN OF 1/0 SECONDARY. OPENED XFMR ON POLE 279-198 @ 21:25 CLOSED BACK IN @ 22:00. SEND COPY OF THIS TO DOUG . VER/SEF
25380 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-12-20 02:23 | 2020-12-20 02:58 | 1 | 35 | 4787741 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Span of secondary going to pole 1036B10348 has burned into at trans pole,Will have to splice wire and climb pole to make repairs.Going to have to open trans to make repairs will keep up with time..Opened trans at 02:23 made repairs restored at 02:58.
25381 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-12-08 17:14 | 2014-12-08 17:49 | 1 | 35 | 4848201 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE ./ ISO 37830177B30559/ COD 1/ VER/BOW
25382 | Hazard | 3309301 | VICCO | REDFOX | 2018-06-20 16:00 | 2018-06-20 16:35 | 1 | 35 | 4629621 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer leaking oil / changed transformer//OPENED 1600 CLOSED 1635
25383 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-03-26 09:50 | 2012-03-26 10:25 | 1 | 35 | 4616861 | 35 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CLIMBED XFMR POLE AND CHANGED ALL NEUTRAL CONNECTIONS, APPEARS TO HAVE CORREDCTED PROBLEM// VER/DBM IDCC TOF821 ESTIMED TIME OFF FOR REPAIR XXXX
25384 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2022-04-23 14:30 | 2022-04-23 15:05 | 1 | 35 | 4793041 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | had a bad arrester and on banke pole 785-A2-1382.///// got cleared up and restored at 15:05
25385 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-09-30 16:10 | 2016-09-30 16:45 | 1 | 35 | 4949501 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW GOING TO CHANGE XFM/ ISO 37830508000010/ COD 1 OPENED XFMR AT 1610 CHANGED XFMR ANDRESTORED POWER AT 1645 CREW 077H01/ VER/BOW L3/HFP XXXHFP
25386 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-01-01 17:45 | 2011-01-01 18:20 | 1 | 35 | H57638-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED. TOP OF POLE#-190-135 IS BURNED ALMOST INTO. CUTOUT BROKE DOWN. I OPENED TRANS. ON THIS POLE. WE HAVE 2 PEOPLE OUT NOW. WE WILL HAVE TO HAVE SINGLE TAP OPENED UP AT POLE 190-49 WHEN CREW ARRIVES. I CALLED DAVE SAMMONS AND HE SAID HE WOULD HEAD THIS WAY WHEN THEY GOT CLEARED UP ON JOB THEY WERE WORKING ON. I LIFTED HOTTAP ON POLE 190-49 AT 17:45 AND CLOSED IT IN AT 18:20. WE PUT A BRACE ON POLE. COD-5 THIS IS FOR THE 1 CUST WHEN CREW ARRIVED SEE 57638-1 VER/HFP L3/HFP IDCC PN135 XXXX
25387 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-11-14 11:00 | 2019-11-14 11:35 | 1 | 35 | 4033721 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout,transformer back in at 11:35
25388 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-12-26 22:40 | 2018-12-26 23:15 | 1 | 35 | 4600371 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 38830235000130 L3/HFP
25389 | Hazard | 3310502 | HADDIX | CANOE | 2014-10-31 15:10 | 2014-10-31 15:45 | 1 | 35 | 4677031 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 C/O///// CHANGED C/O, POWER RESTORED. OPENED 15:10 CLOSED 15:45.// COD 1//VER/ ADH
25390 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2009-01-12 14:56 | 2009-01-12 15:31 | 1 | 35 | 54503-1 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402204//REPLACED BAD CUTOUT//VER/CRB L3/KEP IDC XXXX
25391 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-01-30 14:25 | 2014-01-30 15:00 | 1 | 35 | 4330221 | 35 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CRACKED CUTOUT. // VACANT HOUSE VER/HFP L3/HFP
25392 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-06-20 19:38 | 2021-06-20 20:12 | 1 | 34 | 4775771 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | service neutral broke in customers drop, will have to open XFM on pole 1102-14 to safely make repairs// opened XFM @ 19:38 closed @ 20:12
25393 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-23 10:56 | 2018-04-23 11:30 | 1 | 34 | 4265051 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 815-193//repairs made//restored at 11:30//complete//em COD-1 ISO TF 38830815B20193
25394 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-11-22 13:06 | 2017-11-22 13:40 | 1 | 34 | 4596081 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required broken link 38830223000072//COD 1
25395 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-06-15 08:26 | 2015-06-15 09:00 | 1 | 34 | 4572211 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE REPAIRED, AND REPLACED POWER RESTORED AT THIS LOC AT 0900// VER/ ADH
25396 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-04-13 13:28 | 2018-04-13 14:02 | 1 | 34 | 4220341 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Service hot leg and neutral burndt into on service drop off pole 168-A-176, will have to open trans. to make repairs, will keep track of times. Opened trans @1328, made repairs and put back in @1402.
25397 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-03-30 14:46 | 2016-03-30 15:03 | 2 | 17 | 4006181 | 34 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR , PART POWER, MADE REPAIRS RESTORED POWER AT 15:03..ISO 37830468000057 COD 2 VER/AWD
25398 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-09-15 15:46 | 2019-09-15 16:20 | 1 | 34 | 4021131 | 34 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired secondary connection complete
25399 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2012-05-15 16:46 | 2012-05-15 17:20 | 1 | 34 | 4798371 | 34 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | THE NEUTRAL CONDUCTOR WAS BROKEN IN THE SERVICE DROP. I REPAIRED THE NEUTRAL CONDUCTOR. ONLY ONE CUSTOMER AFFECTED. ///VER/CRB L/3 CRB IDC XXXX
25400 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-12-30 21:18 | 2021-12-30 21:35 | 2 | 17 | 4240871 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 22-167// will be making repairs// XFM on 22-167 off @ 21:18 on @ 21:35
25401 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-12-13 14:00 | 2009-12-13 14:34 | 1 | 34 | 51872-1 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPAIRED POLE & REPLACED CUTOUT .THIS WAS NOT OU . I PULLED OFF @ 14:00 VER/KEP L3/KEP
25402 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2020-11-20 09:35 | 2020-11-20 10:09 | 1 | 34 | 4710771 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | no crew required 6t fuse broke
25403 | South Williamson | 3411401 | DEWEY | INEZ | 2018-01-12 13:16 | 2018-01-12 16:36 | 1 | 200 | 4736391 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL796626 // sdb // 1316 / SCADA shows feeder breaker locked out. Crews en route. 2811 cc //pole 837-8 insulator failed ,burned cross arm off//repairs made Released by crew 079S01//times are wrong, see DOL//
25404 | South Williamson | 3411401 | DEWEY | INEZ | 2015-05-28 14:11 | 2015-05-28 14:45 | 1 | 34 | 4476851 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR BAD ON POLE 744-38//FEEDS SCHOOL FLASHER AND A GARAGE THAT IS CURRENTLY DISCONNECTED AT METER//TALKED TO GARAGE AND THEY ARE OK WITH CHANGING IT IN THE MORNING//ROGER MAYNARD WILL CHANGE IN THE MORNING CREATED OPS ORDER #039486824 FOR HIM TO WORK/// VER/CRB
25405 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-07-14 13:29 | 2009-07-14 14:03 | 1 | 34 | 56469-1 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP REPLACED CUTOUT DOOR POWER BACK ON IDC XXXX
25406 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-06-25 16:41 | 2010-06-25 17:15 | 1 | 34 | 57550-1 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN ARRESTER, POWER BACK ON. IDC XXXX
25407 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-05-06 16:06 | 2009-05-06 16:40 | 1 | 34 | 60462-1 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND B PHASE LINE FUSE BLOWN, ALSO FOUND BAD ARRESTOR ON POLE 1073-2141, THIS POLE NEEDS TO BE REWORK VERY BADLY, SEND TO MR. RAYBURN, TO HAVE SOMEON TO COME DOWN TOMMORROW, AND BRING 3 CUTOUTS AND 3 ARRESTORS, HAVE TALK TO KINNERS, CAN HAVE THEM OFF ANYTIME//3110902//VER/CRB
25408 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-05-01 15:50 | 2020-05-01 16:24 | 1 | 34 | 4786061 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pl 426-171 replaced cutout power restored at 16:24 off at 15:50
25409 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2014-10-25 19:25 | 2014-10-25 19:42 | 2 | 17 | 4661371 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S01 CREW ON SITE REPLACING BROKEN CUTOUT//OPEN XFORMER AT 19:25 CLOSED AT 19:42 CUTOUT REPLACED ALL CUSTOMERS BACK ON VER/CRB
25410 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-04-08 16:06 | 2013-04-08 16:40 | 1 | 34 | 4989011 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND TRANSFORMER FUSE BLOWN, ALSO FOUND BAD LIGHTNING ARRESTOR, BLOWN ON POLE 1146-B1-271, CAN USE TRUCK IF DRY, IF NOT WILL HAVE TO CLIMB THIS POLE, CUST HAS HORSE DO NOT LET THEM OUT RESTORED POWER AT LOC AT 1640 COD-1 ISO TF 39831146B00271 VER/HFP L3/HFP IDC XXXX
25411 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-10-08 15:08 | 2020-10-08 15:42 | 1 | 34 | 4537511 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced door
25412 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-06-17 11:31 | 2011-06-17 12:05 | 1 | 34 | 4333651 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A BAD CUTOUT ON POLE 266-162 COD-1 ISO TF 37820266000162 VER/HFP L3/HFP
25413 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-10-01 17:00 | 2011-10-01 17:34 | 1 | 34 | 4937941 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN SERVICE, REPLACING CONNECTION. CONNECTIONS REPLACED RESAGGED SERVICE. VER/HFP L3/HFP IDCC TOF1357, ESTIMATED TIME OFF BAD NEUTRAL XXXX
25414 | Hazard | 3303902 | LESLIE | WOOTON | 2019-02-28 12:10 | 2019-02-28 12:44 | 1 | 34 | 4936461 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral burnt into , opened at 12:10, closed at 12:44
25415 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-03-10 11:36 | 2009-03-10 12:10 | 1 | 34 | 56901-1 | 34 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | VER/HFP CUSTOMER HAS PARTIAL POWER. I AM CHECKING NOW. METER WAS BAD. I CHANGED METER. L3/HFP IDC XXXX
25416 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-01-24 14:35 | 2018-01-24 15:09 | 1 | 34 | 4771061 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found bad xfm. cutout on pole 166-175/////opened xfm. @ 14:35 and made repairs closed back in @ 15:09
25417 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-03-15 13:47 | 2011-03-15 14:04 | 2 | 17 | 54505-1 | 34 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE // COD 2// VER/DBM IDCC CDC83 XXXX
25418 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-02-21 20:27 | 2015-02-21 21:00 | 1 | 33 | 4067581 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED FUSE TO CHANGE TRANSFORMER 37830426C00176 IN POWER ON ORDER 4066531/ 2027 TO 2100/ ISO 37830426C00176/ COD 1/ VER/BOW
25419 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2019-03-13 10:28 | 2019-03-13 10:39 | 3 | 11 | 4976741 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING CUTOUT TO MAKE REPAIRS,,,opened xfr 376-92 @ 10:28,,closed @ 10:39 and replaced cutout complete
25420 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2008-05-08 19:55 | 2008-05-08 20:06 | 3 | 11 | 58406-1 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BREAKING DOWN ON POLE #465-22 REPLACED CUTOUT OPENED LINE FUSE AT 19;55 RESTORED POWER AT 20;06//3309902//VER/CRB IDC XXXX
25421 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-08-08 16:27 | 2008-08-08 17:00 | 1 | 33 | 50350-1 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3116102// BROKEN 6T FUSE VER/TOM IDC XXXX
25422 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-01-08 23:27 | 2020-01-09 | 1 | 33 | 4226381 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke, Time on 00:00
25423 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-01-21 16:47 | 2015-01-21 17:20 | 1 | 33 | 4950191 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION/ ISO 38830292B00096/ COD 1/ VER/BOW
25424 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-07-02 15:30 | 2015-07-02 16:03 | 1 | 33 | 4709001 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CONNECTION HAS BURNED INTO ON BANK OF TRANSFORMERS. I CALLED FOR BIG BUCKETT TO HELP. WE FIXED NEUTRAL AND CHANGED 1 CUTOUT./ 1530-1600/ ISO 37830358D00338/ COD 1/ VER/BOW
25425 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-01-18 10:27 | 2012-01-18 11:00 | 1 | 33 | 4272531 | 33 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON WEATHERHEAD. <<ONLY ONE CUSTOMER AFFECTED>> REPLACED CONNECTIONS AT WEATHERHEAD AND POLE. RESTORED @ 11:00. SH VER/KEP IDC XXXX
25426 | South Williamson | 3411401 | DEWEY | INEZ | 2016-09-01 11:35 | 2016-09-01 12:08 | 1 | 33 | 4860361 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OFF AT 11:35 ON AT 12:08//REPLACING TRANS VER/CRB L3/HFP XXXHFP
25427 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-02-21 20:27 | 2015-02-21 21:00 | 1 | 33 | H4066531 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 426-176, 1 CUST. OUT, WILL BE CHANGING. LINE FUSE CUTOUT ALSO BAD ON THIS POLE, CHANGED THEM OUT. TOOK THE POWER OFF ON LINE FUSE AT 2027, CLOSED BACK IN AT 2100. BOTH CUSTOMERS RESTORED./ ISO 37830426C00176/ COD 1/ VER/BOW
25428 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2014-11-17 19:00 | 2014-11-17 19:33 | 1 | 33 | H4737281 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE /// NEED 1 MAN NO TRUCK/ OPENING HOT TAP ON POLE 149-146 WILL HAVE 149-147 AND 149-155 CUTOUT BROKE /// NEED 1 MAN NO TRUCK/ OPENING HOT TAP ON POLE 149-146 WILL HAVE 149-147 AND 149-55// TOOK HOT TAP OFF @19:00 AND PUT HOT TAP BACK ON @ 19:31 THESE ARE TIMES FOR 37820149000155/// CHANGED BAD CUTOUT AND RESTRED SERVICE @ 19:33 37820149000147// ISO 37820149000147// COD 4 TOTAL/ VER/BOW
25429 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-05-30 09:30 | 2011-05-30 09:41 | 3 | 11 | 4208271 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TRANSFORMER AT 0930 CHANGED CUTOUT CLOSED AT 0941 GOOD VOLTAGE CLOSE TICKET VER/TOM L3/TOM IDC XXXX
25430 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-08-12 09:39 | 2021-08-12 10:12 | 1 | 33 | 4043901 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required bad cutout
25431 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-11-24 19:42 | 2008-11-24 20:15 | 1 | 33 | 51750-1 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301// BROKEN CUTOUT. OPENED XFMR AT 19:42. REPLACED CUTOUT AND REPAIRED POLE GROUND. CLOSED XFMR AT 20:15. SH//COD 1//ISO// VER/DBM IDC XXXX
25432 | Pikeville | 3408401 | KIMPER | LONGFORK | 2011-10-30 12:45 | 2011-10-30 13:18 | 1 | 33 | 4037061 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERV DROP TO REPLACE//////LOOSE SERVEIN CONNECTION LET INSULATION HEAT UP EVENTUALLY SHORTING OUT,BURNED NEUT IN TWO.REPLACED SERV DROP///VER/CRB IDC XXXX
25433 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-02-24 21:20 | 2016-02-24 21:53 | 1 | 33 | H4761741 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ****SEE 4761741**** CUTOUT BROKE ON 169-91 (2 CUSTOMERS ORIGNALLY) // WILL NEED TO OPEN L/F ON 169-20 TO MAKE REPAIRS (1 MORE CUSTOMER) 21:20 //REPAIRS MADE // OPENED 21:20 // CLOSED 21:53/ALL POWER RESTORED 2153/ DUPLICATE IN HOIS/ VER/BOW
25434 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-11-16 15:00 | 2015-11-16 15:33 | 1 | 33 | 4451791 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED XFM UP @ 15:00 MADE REPAIRS ///CLOSED XFM BACK IN @ 15:33/// NEUTRAL BURNT INTO @ CLEVIS/ ISO 38821129B00149/ COD 1/ VER/BOW
25435 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-02-25 12:42 | 2009-02-25 13:15 | 1 | 33 | 51407-1 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN XFMR FUSE // VER/TOM L3/TOM IDC XXXX
25436 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-08-28 22:42 | 2022-08-28 23:15 | 1 | 33 | 4805741 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse link broke
25437 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-03-14 19:15 | 2016-03-14 19:48 | 1 | 33 | 4846971 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENING TRANSFORMER 38831074D00015 TO MAKE REPAIRS IN ORDER #4844491/ ISO 38831074D00015/ COD 1/ 1915-1948/ VER/BOW
25438 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2017-04-08 18:43 | 2017-04-08 19:16 | 1 | 33 | 4631191 | 33 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON SERVICE POLE, MADE REPAIRES//COD 1// VER/DBM L3/HFP XXXHFP
25439 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2016-10-14 10:32 | 2016-10-14 11:05 | 1 | 33 | 4016611 | 33 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 37830449A20991. BAD CUTOUT ON PADMOUNT XFMR, REPLACED CUTOUT RESTORED POWER AT 11:05. SENT INFO TO D CHRISTIAN VER/AWD // SENT INFO TO HAVE MAPS UPDATED BY TECH = L3/HFP XXXHFP
25440 | Cannonsburg | 3001401 | LOUISA | CITY | 2015-01-26 17:40 | 2015-01-26 18:13 | 1 | 33 | 4965801 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELOCATED DROP CUSTOMER IS NOW FED OFF SEC POLE 38830454A41805 PLEASE SEND COPY TO MAPPING APR AT 1805 ONE CUSTOMER OFF AT 1740 CLOSE TICKET VER/CRB
25441 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-10-14 13:55 | 2009-10-14 14:28 | 1 | 33 | 62462-1 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD SERVIN CONNECTIONS. VER/TOM IDCC TOF1239 XXXX
25442 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-08-11 14:00 | 2021-08-11 14:33 | 1 | 33 | 4034311 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Service barrel burned out. Opened transformer to make repairs. Opened 14:00 Closed 14:33.
25443 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-12-23 16:49 | 2015-12-23 17:00 | 3 | 11 | 4553201 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN SERVICE, OPENED XFMR AT 16:49, CLOSED BACK AT 17:00, ALL POWER RESTORED VER/CRB
25444 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-05-23 11:48 | 2014-05-23 12:21 | 1 | 33 | 4744741 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-1 ISO TF 38830163000037 VER/HFP L3/HFP
25445 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2015-12-15 11:45 | 2015-12-15 11:56 | 3 | 11 | 4534651 | 33 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.. OPENED XFMR AT 11:45 REPLACED CUTOUT, RESTORED POWER AT 11:56.. VER/CRB
25446 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-06-16 20:28 | 2016-06-16 21:00 | 1 | 32 | 4367361 | 32 | PARTIAL POWER | EQUIPMENT FAILURE | METERING | BAD METER @ HOUSE, COMPLETE VER/CRB
25447 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-12-10 15:45 | 2008-12-10 16:17 | 1 | 32 | 56359-1 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP CUST IS AN CITY BLOCK AWAY FROM TRANSFORMER WE HAVE OPEN WIRE SEC, GOING THRU TREES COULD ALSO BE PROBLEM.ALSO GOING TO CHANGE OUT SER DROP TODAY ,AND SEE IF THIS WILL FIX PROBLEM//3000902 L3/WHV IDCC TOF1438 ALLOWED 30 MIN FOR REPAIR XXXX
25448 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-06-23 20:18 | 2009-06-23 20:50 | 1 | 32 | 52727-1 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD XFORMER FUSE LINK//COD 1// VER/DBM IDC XXXX
25449 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2013-10-02 17:03 | 2013-10-02 17:35 | 1 | 32 | 4905411 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMR LEAKING OIL.CREW COMING FROM PIKEVILLE WITH XFMR.REPLACED 10 KVA WITH 15 KVA..OFF AT 17:03 AND BACK ON AT 17:35 VER/CRB L/3 CRB IDC XXXX
25450 | Pikeville | 3421001 | BREAKS | CITY | 2008-08-05 20:34 | 2008-08-05 21:06 | 1 | 32 | 65739-1 | 32 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3400901// BAD CONNECTION ON HOT LEG AT THE TRANSFORMER. VER/KEP IDC XXXX
25451 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-02-12 14:22 | 2020-02-12 14:30 | 4 | 8 | 4396951 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | changed connections at weatherhead & at xfmer & sec pole. cust has been having issues for a while according to them. everything on our end is good.
25452 | South Williamson | 3200302 | BELFRY | TOLER | 2018-04-09 13:00 | 2018-04-09 13:16 | 2 | 16 | 4203461 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad side tap cutout at pole 38821039C00039. I opened the side tap and transformer at 13:00, and closed back in at 13:16. Pole top is burned half through, send to Ryan Thornbury to have the pole replaced. 1300-1515
25453 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2022-06-14 17:00 | 2022-06-14 17:32 | 1 | 32 | 4110641 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | broke sec pole 902-624. 35-5. trk ok. feeds 119 3rd street Released by crew 078S07,open 1 cust @ 1700 close @ 1732 please close ticket thanks.bt
25454 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-08-17 17:30 | 2020-08-17 18:02 | 1 | 32 | 4340541 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burned up. replaced door, power restored
25455 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-02-02 19:29 | 2019-02-02 19:37 | 4 | 8 | 4749131 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 280-31 load side stinger burnt off cutout,,opened @ 19:29 closed @19:37 complete///flickering lights till TR was opened
25456 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-04-12 14:43 | 2018-04-12 15:15 | 1 | 32 | 4215321 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repair hot tap
25457 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-07-21 13:43 | 2018-07-21 14:15 | 1 | 32 | 4827621 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | gave to Ryan Schoolcraft and put in pr name blown arrester and cleared by Rayn Schoolcraft at 14:15/ ISO 37830089000191/ COD 1
25458 | South Williamson | 3200302 | BELFRY | TOLER | 2018-11-08 15:44 | 2018-11-08 16:00 | 2 | 16 | 4380651 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found and replaced a bad cutout off @ 1544 on @ 1600 l3/hfp
25459 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-02-28 11:43 | 2022-02-28 11:59 | 2 | 16 | 4552171 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO OUTAGE TILL CUTOUT OPENED ON POLE 38830478A31099//OFF @ ON @Opened txmf at 1143 to replace door and fuse apr at 1159 close ticket
25460 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-07-19 15:58 | 2011-07-19 16:30 | 1 | 32 | 4564221 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUIND BASKET BURNTED OFF, I MADE REPAIRS AND THERE IS POWER TO THE METER FOR THE TRAFFIC LIGHT, WELL NEED TO CALL STATE DEPT TO RESET LIGHT COD-1 ISO LF 39831097D00331 VER/HFP L3/HFP
25461 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-12-23 21:25 | 2017-12-23 21:41 | 2 | 16 | 4670741 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | xfr 1073-2056,,bad secondary connection and neutral bushing loose,,,,no outage until opened,,,opened @ 21:25 closed @ 21:41,,complete
25462 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-07-20 14:24 | 2021-07-20 14:56 | 1 | 32 | 4939201 | 32 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broken service neutral/ repaired
25463 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-11-17 18:39 | 2017-11-17 18:47 | 4 | 8 | 4563761 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr 37830225A00291 1839-1847
25464 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-07-17 19:03 | 2019-07-17 19:35 | 1 | 32 | 4724501 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called no answer. restored
25465 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2022-07-14 12:58 | 2022-07-14 13:30 | 1 | 32 | 4489211 | 32 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | pri. metering a phase 100t open. restored @ 13:30
25466 | Hazard | 3309302 | VICCO | JEFF | 2013-03-22 17:03 | 2013-03-22 17:35 | 1 | 32 | 4949101 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HOT LINE CLAMP BURNED OFF ON PRIMARY METERING === REPAIRED === POWER OK//COD 1// VER/DBM IDC XXXX
25467 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2019-11-18 16:40 | 2019-11-18 17:12 | 1 | 32 | 4044951 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | customer xfm. leaking in driveway.talked to PR and he is sending man with xfm..15 kv 7200.opened xfm. @ 16:40 and closed back in @ 17:12
25468 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-02-22 10:33 | 2010-02-22 11:05 | 1 | 32 | 59787-1 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ... REPLACED CUTOUT RESTORED POWER AT 11:05//VER/CRB IDC XXXX
25469 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-04-01 21:10 | 2014-04-01 21:42 | 1 | 32 | 4554041 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK DROP////SERVE-IN HEATED UP,BURNED SERV NEUTRAL INTO.MADE REPAIRS.POSSIBLE DAMAGES HERE.MAY HEAR FRM CUST VER/HFP L3/HFP IDCC TOF2004, FEC57, ESTIMATED TIME OFF FOR REPAIR XXXX
25470 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-11-12 12:10 | 2008-11-12 12:42 | 1 | 32 | 64149-1 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001101// POLE 68-860 BAD CUTOUT AND OPEN GAP LA CHGED 1-CUST TIME OFF 12-10 TIME ON 12-35 PM IDCC PN858, TOF1131 XXXX
25471 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-05-09 05:20 | 2022-05-09 05:52 | 1 | 32 | 4867101 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF cutout on the arm is broke down will require big bucket to make repairs// opened LF & XFMR on 69-215 off @ 05:20 on @ 5:52
25472 | South Williamson | 3200301 | BELFRY | BELFRY | 2018-12-14 16:43 | 2018-12-14 17:15 | 1 | 32 | 4565791 | 32 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Replaced 50 kva transformer with 100 kva.. L3/HFP
25473 | Hazard | 3302704 | HAZARD | KENMONT | 2010-01-02 19:23 | 2010-01-02 19:54 | 1 | 31 | 57833-1 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE TAIL VER/HFP L3/HFP IDCC CCO XXXX
25474 | Hazard | 3309302 | VICCO | JEFF | 2017-01-03 12:32 | 2017-01-03 13:03 | 1 | 31 | 4263761 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === NEED LINE CREW TO CHANGE CUTOUT UP ON HILL BEHIND HOUSE 19.9 === MANUAL // NO OUTAGE UNTIL XFMR OPENED @ 1232 CLOSED @ 1303BAD CUTOUT === NEED LINE CREW TO CHANGE CUTOUT UP ON HILL BEHIND HOUSE 19.9 === MANUAL // NO OUTAGE UNTIL XFMR OPENED @.1232 ON @ 1303 .CHANGED CUTOUT077H18. 37830348B00262 VER/AWD // VER TIMES PER VOICE RECORDER = L3/HFP XXXHFP
25475 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-05-01 14:50 | 2018-05-01 15:21 | 1 | 31 | 4292311 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 83-332/51 needs 15kva 7200 tran changed out leaking-may want to scoop up 2x2 area base of pole--crew req --ds043018 hold for day shift Released by crew 078S01replaced xfmr all cust restored @1521 please close ticket thanks.bt
25476 | Pikeville | 3410602 | E.PRESTON | LANCER | 2018-01-11 12:24 | 2018-01-11 12:55 | 1 | 31 | 4729921 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | removed guy wire that was laying on secondary xfmr riser.pulled off @ 12: 24 & back on @12:55/ ISO 38830955D00435/ COD 1
25477 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-01-22 14:25 | 2016-01-22 14:56 | 1 | 31 | 4641711 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNT POLE 2/3 OF THE WAY THROUGH/ POLE OK FOR NOW/ SEND TO MIKE HATFIELD TO GET THE POLE REPLACED AS SOON AS POSSIBLE/ TIME OFF 1425 TIME ON 1456/ ISO 37820098C00678/ COD 1/ VER/BOW
25478 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-10-11 10:42 | 2013-10-11 11:13 | 1 | 31 | 4930021 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHG DEFECTIVE XFMR/APPROX 1 HOUR OUTAGE/VEM/OPEN XFMR @ 1045/BACK IN @ 1113/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB
25479 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-01-03 07:58 | 2011-01-03 08:29 | 1 | 31 | 58102-1 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/KEP L3/KEP IDC XXXX
25480 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-03-21 09:10 | 2011-03-21 09:41 | 1 | 31 | 56201-1 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-6702 BAD CUTOUT DOOR 6T TRANS FUSE // COD-1 ISO TF 38830045D26702 VER/HFP L3/HFP IDC XXXX
25481 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-05-31 09:04 | 2019-05-31 09:35 | 1 | 31 | 4395611 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burnt up. Replaced and restored @ 9:35. sh
25482 | South Williamson | 3411401 | DEWEY | INEZ | 2018-11-14 22:12 | 2018-11-14 22:43 | 1 | 31 | 4399961 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Report of wire arcing between pole 861-a3-69 toward main line. More info from prison at 606-433-2552//solid blad burning top spring out of top of cutout on pole 861-A3-60//no outage until i arrived//opened recloser on 861-A3-70 to replace cutout//repairs made//opened at 22:12//closed at 22:43//complete//em L3/HFP
25483 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-08-24 20:15 | 2021-08-24 20:46 | 1 | 31 | 4146211 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | upgrading transformer (1COD) off at 2015 -- on at 2046
25484 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-05-18 16:44 | 2012-05-18 17:15 | 1 | 31 | 4807881 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD JUST PULLED LOOSE. REFUSED XMF APR CLOSE TICKET VER/KEP IDC XXXX
25485 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-08-02 17:15 | 2014-08-02 17:46 | 1 | 31 | 4319511 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VOLTAGE 266 ACROSS, 133V EACH LEG, CHECKING ANOTHER XFMR ON SAME PHASE. IF THAT CHEKS SAME WILL GO TO REG. BANK. BAD 10KV 19.9 XFMR, RONNIE AND PHILLIP BRING ME ONE. TOOK POWER OFF AT 17:15 BACK ON 17:46. VER/CRB
25486 | South Williamson | 3411401 | DEWEY | INEZ | 2020-03-18 10:39 | 2020-03-18 11:10 | 1 | 31 | 4488241 | 31 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401/gaj/outage to replace Cutout at 38830815B20193 Out at 1039 In at 1110
25487 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-04-26 08:05 | 2011-04-26 08:35 | 1 | 30 | 65252-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | FOUND FUSE OUT ON 3 PHASE BANK, DOOR WAS BAD, HAVE REPLACED AND OK AT THIS LOC//COD 1// VER/DBM IDC XXXX
25488 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-01-11 20:30 | 2011-01-11 21:00 | 1 | 30 | 60735-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38406771 //..BAD CUTOUT....CROSSARM BURNT IN TWO....WILL DE-ENERGIZE XFMR BANK ON THIS POLE...DOUBLE ARMS HERE...OTHER ARM GOOD & WILL HOLD CONDUCTORS....CAN EXTINGUISH FIRE & REPLACE CUTOUT OK....//....DE-ENERGIZED XFMRS @ 20:30.....CUT BURNING PIECES OF CROSSARM OFF.....TIGHTENED UP GOOD CROSSARM....REMOVED BAD CUTOUT....RE-ENERGIZED XFMR BANK....POWER ON....JRV....01/11/11 /// WRONG CKT SHOULD BE 3200204 COD-1 ISO TF 38821065D20151 VER/HFP L3/HFP IDC XXXX
25489 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-05-23 16:13 | 2020-05-23 16:23 | 3 | 10 | 4892691 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 490-163, power off at 16:13, restored at 16:23.//NO OUTAGE TILL 1613
25490 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-12-04 14:19 | 2018-12-04 14:34 | 2 | 15 | 4507031 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced craked cutout time off 1419 time on 1434 close ticket L3/HFP
25491 | Hazard | 3303902 | LESLIE | WOOTON | 2008-02-23 13:15 | 2008-02-23 13:45 | 1 | 30 | 66518-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902//BAD CUTOUT AND ARRESTER BURNT POLE WILL REPLACE CUTOUT.//VER/CRB IDC XFIRST CALL WAS FULL POWER ESTIMATED TIME OFF AND CHANGED FROM 1219 XXXX
25492 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-02-25 10:00 | 2013-02-25 10:10 | 3 | 10 | H4843631 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER AT 10:00, REMADE CONNECTIONS AT TRANSFORMER, RESTORED POWER AT 10:10, ONLY 1 CUSTOMER WITH PART POWER. VER/KEP IDC XXXX
25493 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-12-21 21:00 | 2008-12-21 21:30 | 1 | 30 | 61717-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP FOUND 4/3 SERVICED DROP BURNTED DOWN, HAVE REPAIRS MADED AND POWER IS RESTORED AT THIS LOCATION L3/HFP IDC TICKET SAYS POWER IS ON CHANGED TIME OFF FROM 1927 XXXX
25494 | Pikeville | 3403001 | PIKEVILLE | CITY | 2009-12-10 18:45 | 2009-12-10 19:00 | 2 | 15 | H66333-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPEN THE TRANSFORMER FOR ABOUT 15 MINUTE THE 1/0 SEC HERE NEEDS TO BE REPLACED. CONNECTIONS ARE BURNING UP WHERE THE IN INSULATION WILL NOT COME OFF. SEND TO TIM HALL .....DAH VER/KEP L3/KEP IDC DUP TO OPEN TRANSFORMER XXXX
25495 | Pikeville | 3413401 | GARRETT | GARRETT | 2021-07-04 14:00 | 2021-07-04 14:30 | 1 | 30 | 4855691 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | //Previous order: Everything checked fine on our side, customers meter base was underwater a couple times last month and really corroded, I let them know their side could be bad. off 1400-1430
25496 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-11-02 11:00 | 2012-11-02 11:15 | 2 | 15 | H4335131 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE BURNT IN TWO AT CONNECTION NEAR SEC. POLE. -- OPENED TRANSFORMER AT 11:00 = CLOSED AT 11:15. COD-3 ISO TF 37830224D00158 DUPLICATE OF 4335131 FOR 2 CUST..... VER/HFP L3/HFP IDC XXXX
25497 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-02-04 19:30 | 2013-02-04 19:40 | 3 | 10 | H4791191 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SERVICE DUP IN HOIS FOR 3 FROM 1930 TO 1940 @ TR ISO TF 39831147C14063 DUP FROM 4791191 FOR 3 CUST VER/HFP L3/HFP VER/HFP L3/HFP IDC XXXX
25498 | Hazard | 3303902 | LESLIE | WOOTON | 2017-01-16 22:45 | 2017-01-16 23:00 | 2 | 15 | 4303961 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | OPENED RECLOSER ON 37830510000086 TO SAFELY PICKUP CUSTOMERS FROM OUTAGE 4303901. 2245-2300 VER/AWD L3/HFP HFPC CCU FEC57
25499 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-08-05 14:30 | 2014-08-05 14:45 | 2 | 15 | 4333671 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, HAVE CHANGED TIMEOFF WAS 1430 TIME ONE WAS 1445/// ISO 38830018000002/// COD 2// VER/BOW
25500 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-08-15 12:15 | 2009-08-15 12:30 | 2 | 15 | 58834-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP RELEASED BY CREW 078S07 OPENED XFORMER CUTOUT ON POLE 188-232 AT 12:15 TO CHANGE OUT CUTOUT, BACK ON AT 12:30 COD-2 ISO TF 38830188A00232 L3/HFP IDC XXXX
25501 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-01-04 13:47 | 2010-01-04 14:17 | 1 | 30 | 60152-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION INTO MADE REPAIRS RESTORED POWER AT 14:17//COD 1// VER/DBM IDC XXXX
25502 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-03-26 16:55 | 2019-03-26 17:10 | 2 | 15 | 4028071 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connections on transformer opened at16:55 to repair and closed back at 17:10
25503 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-01-25 09:15 | 2010-01-25 09:30 | 2 | 15 | 59258-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONN BAD ON TRANSFORMER WILL NEED ONE MAN AND BIG BUCKETT I TALKED TO CECIL AND HE IS SENDING ME A BUCKETT NO POWER IS OFF AT THIS TIME REPAIRED CONNECTION ON POLE//VER/CRB IDCC TOF0836 ESTIMATED TIME OFF XXXX
25504 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2010-09-28 15:20 | 2010-09-28 15:35 | 2 | 15 | 54894-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | REPLACED TRANSFORMER LEADS WE NEED TO SET A POLE IN A LOW SERVICE DROP TICKET NEEDS TO GO TO A TECH OPENED TRANSFORMER AT 1520//EMAILED TO D CHRISTIAN //COD 1// VER/DBM IDCC TOF1432 XXXX
25505 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-11-12 15:40 | 2009-11-12 16:10 | 1 | 30 | 51146-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP BROKEN NEUTRAL ON SERVICE//CALLED DRT TO HELP--RELOCATED AN REPAIRED SERVICE L3/HFP IDCC TOF1405 , ESTIMATED TIME OFF XXXX
25506 | Hazard | 3303901 | LESLIE | HYDEN | 2022-12-10 10:45 | 2022-12-10 11:00 | 2 | 15 | 4247491 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cusomer ok to wait till daylight, no outage ///TRANSFORMER ARRESTER WENT BAD ON POLE 267-148 //// OPEN TRANSFORMER @ 10:45, CHANGED ARRESTER /// CLOSED TRANSFORMER @ 11:00
25507 | Hazard | 3310502 | HADDIX | CANOE | 2022-12-19 14:27 | 2022-12-19 14:42 | 2 | 15 | 4276841 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Open TR 37830074000047 to replace Cutout //// Open at //// Close at .Open TR 37830074000047 to replace Cutout. Open @ 14:27, Closed @ 14:42
25508 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-05-22 11:35 | 2020-05-22 11:45 | 3 | 10 | 4886921 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken cutout, ( trouble work order ) off @ 11:35 on @ 11:45
25509 | Pikeville | 3421001 | BREAKS | CITY | 2012-12-19 17:25 | 2012-12-19 17:55 | 1 | 30 | H4483691 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4483691 // HOT TAP LEAD HAS BURNT OFF ON C/PHASE ON POLE 244-15 NEED TO OPEN 3 SOLID BLADES ON POLE 244-15 TO MAKE REPAIRS . REPLACED BAD CUT - OUT AND HOT TAP LEAD ON POLE 244-15 OPENED 3 SOLID BLADES UP @17:25 ON POLE 244-15 AND CLOSED BACK IN @ 17:55 RESTORED SERVICE//COD 1// VER/DBM
25510 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-02-09 18:15 | 2017-02-09 18:30 | 2 | 15 | 4379771 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY HOT LUG ON TRANS. WAS LOOSE CAUSING A BRIGHT/DIM, MADE REPAIRS. 37830072A00272 1815-1830. VER/AWD L3/HFP XXXHFP
25511 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-06-15 20:18 | 2009-06-15 20:28 | 3 | 10 | 53103-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON XFMR POLE REPAIRED RELEASED BY CREW 077H14 OPENED @ 2018 CLOSED @ 2028 IDCC TOF1756, TON2020 XXXX
25512 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2010-12-28 10:00 | 2010-12-28 10:15 | 2 | 15 | 56352-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKED VOLTAGE 116 PHASE TO GROUND, 128 PHASE TO GROUND. 243 PHASE TO PHASE. LINE CREW WILL BE OUT TOMARROW. RELEASED BY CREW 078S01 /// OPENED TR @ 1000TO CHECK CONNECTIONSCHECKED VOLTAGE 116 PHASE TO GROUND, 128 PHASE TO GROUND. 243 PHASE TO PHASE. LINE CREW WILL BE OUT TOMARROW. RELEASED BY CREW 078S01 REPLACED BAD CONNECTION RESTORED AT 10:15 VER/HFP L3/HFP IDC XXXX
25513 | Hazard | 3303902 | LESLIE | WOOTON | 2018-12-08 12:15 | 2018-12-08 12:45 | 1 | 30 | 4517531 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr hanging by 1 hanger going to replace xfmr Released by crew 077H14//LIFTED HT ON POLE 37830462000068//NO OUTAGE TILL THEN//OFF @ 1215 ON @ 1245 L3/HFP
25514 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2019-05-01 11:17 | 2019-05-01 11:47 | 1 | 30 | 4192741 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replaced C/O & arrester opened @ 11:17 closed 11:47
25515 | Pikeville | 3410602 | E.PRESTON | LANCER | 2013-06-26 08:00 | 2013-06-26 08:30 | 1 | 30 | 4399621 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NETURAL CONDUCTOR WAS BROKEN @ WEATHERHEAD. REPLACED 4/3 SERVICE DROP WITH 2/3 ESTIMATED TIME OFF FOR REPAIR VER/SEF IDC XXXX
25516 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-10-27 08:40 | 2010-10-27 08:50 | 3 | 10 | H65457-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 37505345 // SER END PULLED LOOSE REPAIRED TRANS OFF 08;40 TO 08;50//COD 4// VER/DBM IDC DUP CREATED TO OPEN TRANS XXXX
25517 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2022-04-11 13:45 | 2022-04-11 14:00 | 2 | 15 | 4748431 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened line fuse 0n 738-284 at 13:45 back on at 14:00
25518 | Pikeville | 3120102 | STANVILLE | TRAM | 2021-02-05 13:30 | 2021-02-05 13:45 | 2 | 15 | 4939651 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | we have a open neutral on our end// will have to open XFM to repair connections//XFM off@ 13:30 on@ 13:45// bad connection was in meter base, reconnected customers neutal inside meter base, customer is restored
25519 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-04-05 22:00 | 2010-04-05 22:30 | 1 | 30 | 59085-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR ON SERVICE, MADE REPAIRS RESTORED POWER AT 22:30//COD 1// VER/DBM IDCC TOF1935 XXXX
25520 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-04-01 18:10 | 2009-04-01 18:25 | 2 | 15 | 63860-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP RELATED TO ORDER 63848-1 CREW HAD TO OPEN TRANSFORMER TO REPLACE CONNECTIONS L3/HFP IDC XXXX
25521 | Hazard | 3303902 | LESLIE | WOOTON | 2022-05-10 11:30 | 2022-05-10 12:00 | 1 | 30 | 4872611 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Repaired neutral. Transformer open @ 11:30 closed @ 12:00
25522 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-03-08 18:30 | 2013-03-08 19:00 | 1 | 30 | 4891671 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL BOKE IN SERVICE DROP.VERY LONG DROP . NEED SECONDARY POLE SET..SEND TO CLIFF FREEMAN FOR JOB. MADE REPAIRS. D LEWIS 3-8-13 19:00 ///VER/CRB L/3 CRB IDCC TOF1716 ESTIMATED TIME OFF FOR REPAIR XXXX
25523 | Whitesburg | 3314401 | MAYKING | ERMINE | 2019-07-25 18:00 | 2019-07-25 18:30 | 1 | 30 | 4793291 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER//COD 1//CREW ENROUTEwe changed bad xfmr. we opened the xfme at 18:00closed back at 18:30
25524 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2013-03-31 16:30 | 2013-03-31 17:00 | 1 | 30 | 4969881 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN, 1 ARM BURNED APART ( DOUBLE ARM CONSTRUCTION ) OPENED CUTOUT AT 16:30 AND CLOSED AT 17:00 , ALL WORK COMPLETE / GXJ POWERON SHOWS NO CUSTOMERS ON THIS TR... GOING WITH 1 COD-1 ISO TF 37830234000099 VER/HFP L3/HFP IDC XXXX
25525 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2014-11-17 14:00 | 2014-11-17 14:30 | 1 | 30 | 4736131 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE WILL REPLACE//// OPENED TRANSFORMER @ 14:00 CHANGED BAD CUTOUT AND CLOSED TRNASFORMER BACK IN @ 14:30 AND RESTORED SERVICE// COD 1// VER/ ADH
25526 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-06-01 23:15 | 2015-06-01 23:30 | 2 | 15 | 4497651 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT REPLACED IT OPENED CUTOUT AT 23:15 CLOSED CUTOUT IN AT 23:30 VER/CRB
25527 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-04-23 10:45 | 2015-04-23 11:15 | 1 | 30 | 4358111 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED XMF AT 1045 TO MAKE REPAIRES CLOSED AT 1115, REPLACED STOLEN POLEGROUND ,ALSO REPLACED CUTOUT & ARRESTER APR CLOSE TICKET// VER/ ADH
25528 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2016-06-06 21:09 | 2016-06-06 21:39 | 1 | 30 | 4316591 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP LEAD BURNT OPEN/ONE CUST SINGLE PHASING/CREW TO MAKE REPAIRS/VEM/REPAIRS MADE AND FULL POWER RESTORED 2139/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830045C14342/ COD 1/ VER/BOW
25529 | Hazard | 3311103 | STINNETT | WENDOVER | 2011-09-21 17:50 | 2011-09-21 18:00 | 3 | 10 | H4893491 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER CHECKING CONNECTIONS /// OPENED TR @ 1750 TO MAKE REPAIRSPART POWER CHECKING CONNECTIONS/// CHANGED CONNECTIONS, POWER RESTORED COD-4 ISO TF 37830412B00344 DUP OF 4893491 VER/HFP L3/HFP IDC XXXX
25530 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-12-02 19:45 | 2013-12-02 19:55 | 3 | 10 | 4094181 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 077S08///// BAD ARRESTOR ON POLE 37830134B00113 WAS BREAKING DOWN, CHANGED OUT, POWER OK. OPENED XFMR FOR ABOUT 10 MINUTES 19:45 TO 19:55 TO CHANGE ARRESTOR. VER/CRB L3/HFP
25531 | Hazard | 3301401 | COMBS | COMBS | 2017-02-17 20:45 | 2017-02-17 21:15 | 1 | 30 | 4405451 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD NETURAL CONNECTION ,MADE REPAIRES,,PULL METER AT 20:45 AND CLOSE AT 21:15/ ISO 37830271C00089/ COD 1/ VER/BOW L3/HFP XXXHFP
25532 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-10-16 14:18 | 2020-10-16 14:33 | 2 | 15 | 4562331 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 490-190, opened xfmr at 14:18 replaced cutout restored power at 14:33.
25533 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-04-21 14:30 | 2009-04-21 14:45 | 2 | 15 | 63981-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303//, ON SITE, BAD CUTOUT, REPLACING IT//COD 2 VER/KEP L3/KEP IDCC TOF1404 XXXX
25534 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-04-12 18:15 | 2017-04-12 18:45 | 1 | 30 | 4641541 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *** SEE 4641441*** OPENING XFMR TO REPLACE L/LF CUTOUT THAT BROKE/ ISO 37830387C00240/ COD 1 VER/AWD L3/HFP XXXHFP
25535 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-05-17 10:35 | 2017-05-17 10:41 | 5 | 6 | 4807321 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD SEC. CONNECTION ON XFM. POLE 214-126.OPENED XFM. UP TO MAKE REPAIRS.ALTHOUGH CUSTOMER BREAKER BOX DID HAVE CORROSION ON BREAKER..PLEASE SEND COPY TO DAMAGE COMPLAINTS.CUSTOMER STATED THAT APPLIANCES WAS NOT WORKING...OPENED 1035 CLOSED 1041//SENT TO CLAIMS VER/CRB
25536 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-11-08 13:05 | 2012-11-08 13:20 | 2 | 15 | 4373701 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA XFMR NEEDS CHANGED FROM LOUD BUZZING NOISE..2ND CALL IN A WEEK FROM CUST BEING WORRIED .. CREW IN ROUTE.. REPLACED 25 KVA VOLTAGE CHECKED GOOD .. COMPLETE .. XFMR OFF AT 13:05 BACK ON AT 13:20 COD-2 ISO TF 38830453000125 VER/HFP L3/HFP IDC XXXX
25537 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-03-11 11:00 | 2016-03-11 11:15 | 2 | 15 | 4836871 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHANGING CUTOUT AND ARRESTER ON POLE 39831148A00383/ OPENED AT 11:00 AM____ON 11:15AM/ ISO 39831148A00383/ COD 2/ VER/BOW
25538 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-01-03 14:10 | 2012-01-03 14:25 | 2 | 15 | H4228162 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PART OF 4228161//BAD UNDERGROUND SERVICE RELEASED BY CREW 077S04BAD UNDERGROUND SERVICE ---OPENED TRANSFORMER AT 11:12 CLOSED AT 12:00 -- OPENED AT 14:10, CLOSED AT 14:25 SPLICED WIRE, POWER RESTORED.// + 2 // VER/DBM IDC XXXX
25539 | South Williamson | 3411401 | DEWEY | INEZ | 2018-06-13 00:18 | 2018-06-13 00:28 | 3 | 10 | 4594601 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no outage when i arrived//cutout breaking down on pole 744-441//i opened xfmr to replace cutout//opened at 00:18//closed back at 00:28//complete//cod 3
25540 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-02-06 17:15 | 2010-02-06 17:45 | 1 | 30 | 50705-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BAD CONSTRUCTION , LEAD ON TRANSFORMER HAD BEEN SPLICED A COUPLE OF TIMES , POLE HAD BEEN CHANGED RECENTLY SHOULD HAVE BEEN REPLACED . REPLACED LEADS ON TRANSFORMER AND RESTORED POWER AT 1745 JKC VER/KEP L3/KEP IDCC TOF1555 FULL POWER CALL XXXX
25541 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-12-16 19:05 | 2008-12-16 19:35 | 1 | 30 | H59159-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE. REMOVED HOT LINE CLAMP ON POLE 38830811B00004 TO ISOLATE TROUBLE. OPENED TAP AT 19:05 TAKING XFMR ON POLE 811- 4 OFFLINE ALSO 2 CUSTOMERS . REPAIR IN PROGRESS. REPLACED CUTOUT AND ENERGIZED TAP AT 19:35 RESTORING BOTH CUSTOMERS. SH VER/KEP L3/KEP IDC XXXX
25542 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-04 03:05 | 2015-01-04 03:35 | 1 | 30 | 4901391 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN WILL REPLACE..OPENED XFM @ 3:05 TO REPLACE CUTOUT/////RE-ENERGIZED @ 3:35.. ****CHANGE ISO POLE**** VER/SEF L3/DKGXXXX
25543 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-08-20 09:55 | 2011-08-20 10:10 | 2 | 15 | 4733181 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED TRANSFORMER TO ALLOW THEM TO REPLACE A DEFECTIVE CUTOUT // COD-2 ISO TF 38820941D00455 OPENED TRANSFORMER @ 09:55, BACK ON @10:10. VER/HFP L3/HFP IDC XXXX
25544 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2012-12-26 09:00 | 2012-12-26 09:30 | 1 | 30 | 4519411 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT -OUT ON POLE 196-21 GOING TO REPLACE . REPLACED BAD CUT-OUT RESTORED SERVICE . OPENED LINE FUSE UP @ 09:00 CLOSED BACK IN @ 09:30. NEED TO SEND COPY OF TICKET TO CLIFF FREEMAN POLE AND ARM BURNT ///VER/CRB L/3 CRB
25545 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-10-10 10:15 | 2019-10-10 10:45 | 1 | 30 | 4127331 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | frying noise from primary, going to replace cutout and arresstor, bad cutout and found neutral to be loose in xfmr bushing//COD 2//OFF @ 1015 ON @ 1045
25546 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-08-02 08:57 | 2018-08-02 09:12 | 2 | 15 | 4894491 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced secondary connections and ct wiring,,opened @ 0912
25547 | Hazard | 3420001 | SOFT SHELL | VEST | 2016-03-06 23:30 | 2016-03-06 23:45 | 2 | 15 | 4822281 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC. CONNECTIN FAIL, REPLACE NETURAL AND HOT LEG.OPEN TANSFORMER AT 11:30 AND CLOSE AT 11:45 VER/ARN
25548 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-05-01 19:55 | 2012-05-01 20:25 | 1 | 30 | 4732681 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 XFMR OUT DUE TO LOOSE CONNECTION ON RISER, ONLY 1 CUSTOMER AFFECTED, REPAIRED CONNECTION, ALL POWER RESTORED//ISO //COD 1// VER/DBM IDCC CNT19 XXXX
25549 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-11-08 15:00 | 2017-11-08 15:30 | 1 | 30 | 4542471 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | broken neutral in sd, repairs made. open xfmer @ 15:00, closed @ 15:30/ iso 39831123D16090/ COD 1 per servicer only one customer off cfmr map shows 3
25550 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-04-18 22:50 | 2018-04-18 23:00 | 3 | 10 | 4252871 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Opened txmf at 2250 closed at 2300. repaired 1/0 hot leg and neutral. apr at 2300 close ticket
25551 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-11-29 13:00 | 2018-11-29 13:15 | 2 | 15 | 4489901 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | last time the wire was down we wrapped the cable line with our main line neu. will have to climb pole and un-wrap --- opened xfm at 13:00 back on at 13:15 L3/HFP
25552 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-10-01 11:15 | 2013-10-01 11:45 | 1 | 30 | 4900621 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED LINE CREW TO REPLACE 25 KVA & CUTOUT TRUCK OK RELEASED BY CREW 078S05,,,CREW ON SITE, OPENED AT 11:15, CLOSED AT 11:45, REPLACED XFMR, CUTOUT, AND ARESTER,,XFMR WAS SHOT // COD-1 ISO TF 38830327B00248 VER/CRB L/3 CRB IDC XXXX
25553 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-07-27 20:20 | 2015-07-27 20:30 | 3 | 10 | 4949101 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE196-205 . REPLACED ARRESTER .OPENED XFMR ON POLE 196-205 @ 20:20 CLOSED BACK @ 20:30 ./ ISO 37830196C00205/ COD 3/ VER/BOW
25554 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-08-05 06:53 | 2012-08-05 07:23 | 1 | 30 | 4898231 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN ON BANK/SERVICER TO TRY FUSE/VEM/1ROKEN FUSE LINK POWER RESTROLED AT 07;23 PLEASE CLOSE TIC. IDC XXXX
25555 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2018-02-22 14:40 | 2018-02-22 14:50 | 3 | 10 | 4873331 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout breaking down on pole 381-301. opened at 1440 and change cutout, closed at 1450/ ISO 37830381C00301/ COD 3
25556 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-07-29 | 2020-07-29 00:15 | 2 | 15 | 4248311 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Failed cutout & arrestor at 37830482A00061 (2 CC) out at 0000 On at 0015
25557 | Pikeville | 3401001 | ELWOOD | DORTON | 2014-12-06 12:29 | 2014-12-06 12:39 | 3 | 10 | H4840291 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 SECONDARY BURNED DOWN DUE TO A CONNECTION HEATING. OPENED TRANSFORMER AT 1229 CLOSED AT 1239//THIS CAUSED 3 OTHERS OUTAGE//ORGINAL WAS 1 VER/CRB
25558 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-05-18 21:30 | 2016-05-18 21:45 | 2 | 15 | H4232271 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | (2 CUST PART POWER ORGINALLY) TRANSFORMER CONNECTION FROM SECONDARY LEAD TO 1/0 LASH CABLE BURNT UP ON834-A-37 REPLACED CONNECTION OPENED TRANS (2 CUST) AT 21:30 AND RESTORED POWER AT 21:45/ ISO 38830834A00037/ COD 4/ DUPLICATE IN HOIS/ VER/BOW
25559 | Hazard | 3303902 | LESLIE | WOOTON | 2016-03-22 17:15 | 2016-03-22 17:45 | 1 | 30 | 4871721 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENING TRANSFORMER 37830462A30302 TO REPLACE ARRESTER/ ISO 37830462A30302/ COD 1//OPEN AT 17:15 AND CLOSE AT 17:45/ VER/BOW
25560 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-08-21 09:50 | 2015-08-21 10:05 | 2 | 15 | 4160521 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGED OUT..OPENED XFM BANK @ 09:50 CLOSED BACK IN @ 10:05// VER/ ADH
25561 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-08-23 10:00 | 2018-08-23 10:30 | 1 | 30 | 4991901 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | burnt connection on one hot leg and the neutral. opened transformer @ 1000 closed back @ 10:30.. power 10:30 L3/HFP
25562 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-10-03 21:35 | 2011-10-03 21:50 | 2 | 15 | 4944861 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WAS BURNNING, REPLACED CUTOUT TIME OFF 2135 TIME ON 2150 APR CLOSE TICKET//COD 2// VER/DBM IDC XXXX
25563 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-05-04 14:15 | 2010-05-04 14:45 | 1 | 30 | 55666-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL BURNT INTO , ONLY ONE CUSTOMER AFFECTED, REPAIRED NEUTRAL RESTORED POWER AT 14:45 VER/HFP L3/HFP IDCC TOF1331 FULL POWER CALL ALLOWED 30 MIN FOR REPAIR XXXX
25564 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-02-05 09:05 | 2015-02-05 09:15 | 3 | 10 | 4991831 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LEAD BURNT INTO AT CONNECTION AT XFMR, OPENED XFMR AT 09:05 MADE REPAIRS RESTORED POWER AT 09:15./ ISO 37830376B00045/ COD 3/ VER/BOW L3/HFP XXX
25565 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-08-07 10:12 | 2009-08-07 10:42 | 1 | 30 | 57384-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411901//REPLACE SERVICE FROM 1/0 TO 4/0 // VER/DBM IDCC MCCNI ALLOWED 30 MIN FOR REPAIR XXXX
25566 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-07-08 14:30 | 2009-07-08 14:45 | 2 | 15 | 61061-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL HAVE TO OPEN XFMR ON POLE 128-69, TO RESAG SECONDARY, OPENED XFMR AT 14:30 BACK ON AT 14:45. COMPLTED//COD 2// VER/DBM IDC XXXX
25567 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-01-14 19:25 | 2015-01-14 19:40 | 2 | 15 | 4936031 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SERVICER OPENING TRANSFORMER 187-D1-215 TO SAFELY MAKE REPAIIRS/COD 2/UNDERGR. SER. NEU PULLED OUT OF CONNECTOR IN SEC. BUCKET ,SEND COPY TO BOB REYNOLDS TO MAKE REPAIRS ON SEC BUCKETUNDERGR. SER. NEU PULLED OUT OF CONNECTOR IN SEC. BUCKET, REPAIRED POWER RESTORED/EMAILED BOB REYNODLS AND LLYOD/ADH/OPENED1925 CLOSED 1940// VER/ ADH
25568 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-08-19 15:30 | 2016-08-19 16:00 | 1 | 30 | 4814561 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GOING BAD NO POWER YET, BUT WILL TAKE OUTAGE TO REPLACE IT TOOK IT OFF AT1530 AND BACK PN AT 1600/ ISO 37830409000032/ COD 1/ VER/BOW
25569 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-06-01 16:10 | 2014-06-01 16:25 | 2 | 15 | 4957801 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2139 - ATTEMPTED CUSTOMER CALL BACK AT BOTH # LLISTED. N/A CSC NOTIFIED WILL BE DISPATCHED AFTER DAYLIGHT HRS ON 6/1/14 UNLESS PROBLEM ESCALATES. ARRESTOR ISSUE WILL FIX NEXT JOB--JIM RELEASED BY CREW 077S06 OPENED TRANSFORMER AT 16:10, REPLACED ARRESTOR, POWER RESTORED AT 16:25//NO OUTAGE TIL FUSE WAS OPENED VER/CRB
25570 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-06-04 10:15 | 2019-06-04 10:45 | 1 | 30 | 4425521 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no crew required bad arrestor removed didnt need
25571 | South Williamson | 3411401 | DEWEY | INEZ | 2017-08-04 12:40 | 2017-08-04 13:10 | 1 | 30 | 4224671 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER ON 38830861A30070 TO ISOLATE CUTOUT ON FIRE AT 38830861A30060. OPENED 1240. CLOSED BAD CUTOUT ON 861-60. OPENED RECLOSER 38830861A30070 @ 12:40 TO ISOLATE. REPLACED CUTOUT AND CLOSED RECLOSER @ 13:10. SH VER/AWD
25572 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-01-25 14:20 | 2013-01-25 14:30 | 3 | 10 | H4740271 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT OPENED SIDE TAP AT 1420 CLOSED AT 1430 COD-2 ISO TF 37820126000041 DUP IN HOIS FOR 3 CUST ON TAP OFF POLE 37820126000041 DUP FROM 4740271 FOR 3 CUST VER/HFP L3/HFP IDCC TOF1235, TON1432 XXXX
25573 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-04-19 13:15 | 2015-04-19 13:45 | 1 | 30 | H4333761 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR LEAD.OPENED XFMR AT 13:15 CLOSED IN AT 13:45/COD 1+1 DUPLICATE IN HOIS// VER/ ADH
25574 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-06-25 18:25 | 2012-06-25 18:40 | 2 | 15 | 4961671 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUYWIRE RUSTED OFF AT GROUND LEVEL & FELL AGAINST XFMR, OPENED XFMR AT 18:25 TO MAKE REPAIRS & RESTORED POWER AT 18:40 ///VER/CRB L/3 CRB
25575 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-07-04 01:27 | 2010-07-04 01:37 | 3 | 10 | 62037-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE HOT LINE CLAMP ON XFRMER RISER....CAN CLEAR UP AND REPLACE CLAMP....WILL HAVE TO OPEN XFRMER....//....OPENED XFRMER @ 01:27....REPLACED BURNT UP HOT LINE CLAMP....CLOSED XFRMER @ 01:37.....JRV...07/04/10 //VER/GAH IDC XXXX
25576 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-10-20 11:40 | 2008-10-20 11:55 | 2 | 15 | H57271-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/HFP WIRE BURN-INTO ON SECONDARY,OPEN TRANSFORMER AT 11:40, SEND TICKET TO RON RYE CREW TO HAVE A TECT WRITE A JOB TO UPGRADE SECONDARY TO 1/0 /// COD-3 NEED OUTAGE FOR 2 CUST CREATED IN HOIS IDC XXXX
25577 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2021-08-06 07:57 | 2021-08-06 08:27 | 1 | 30 | 4010871 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Hot leg burndt into @48-D2-103, only 1 customer affected, will be making repairs. Got connection replaced @0827.
25578 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-12-06 23:55 | 2014-12-07 00:25 | 1 | 30 | H4843801 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | GUY/ANCHOR | GUY RUSTED OFF LET POLE LAY OVER & PULL XFMR LEAD INTO TANK AND BURN OFF, ALL REPAIRS MADE AT XFMR, NEED TO SEND NOTE TO ENG. TO REPLACE GUY AT POLR 38831027B00213, OPENED XFMR UP AT 23:55 CLOSED IN AT 00:25 DUPLICATE IN HOIS FOR OTHER 1 CUSTOMER ON XMER FROM 2355 TILL 0025 VER/SEF
25579 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-08-15 10:50 | 2018-08-15 11:20 | 1 | 30 | 4955701 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ooNO OUTAGE UNTIL I OPEN FUSESoo to replace failed cutout. Open riser fuses @ 10:50. Replaced all three cutouts and restored @ 11:20. sh
25580 | South Williamson | 3200302 | BELFRY | TOLER | 2011-03-05 17:40 | 2011-03-05 17:55 | 2 | 15 | 50124-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39051699 //....BAD XFMR CUTOUT ON POLE 1014-C3-114.....XFMR STILL HOT....WILL OPEN & REPLACE CUTOUT....CROSSARM OK....//...OPENED CUTOUT @ 17:40.....REPLACED CUTOUT....CLOSED @ 17:55....POWER ON....JRV...03/05/11 VER/HFP L3/HFP IDC XXXX
25581 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-01-17 21:53 | 2011-01-17 22:03 | 3 | 10 | 62019-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGING CUTOUT LIFTED HOTTAP AT 2153 POWER RESTORED AT 2203 CLOSE TICKET//VER/CRB IDC XXXX
25582 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-01-26 15:20 | 2015-01-26 15:30 | 3 | 10 | HA4964771 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT OFF POLE @ 326-53 NO TRUCK NEED LINE CREW TO REPLACE,OPEN SWITCH @ 326-11 @ 1120 CLOSED SWITCH @ 11:56/ ISOLATED GROUNDED AND TAGGED TO DDC AT POLE 38830326000120/ RELEASED BY CREW .. CREW ON SIGHT MAKING REPAIRS FETR 15:30 078S05.. OPENED XFMR ON 326-120 AT 15:20 BACK ON AT 15:30.. SOLID BLADE ON POLE 326-120 RESTORED AT 15:30 // SEE DUP H4964771 & HA4964771FOR ADD OUTAGE - PER SERVICER ONLY 1 CUST INITALLY OFF // VER/HFP L3/HFP AJB
25583 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-10-01 18:45 | 2022-10-01 19:00 | 2 | 15 | 4962141 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad cutout. Opened txmf at 1845 apr at 1900 close ticket. dwest
25584 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-05-02 15:45 | 2009-05-02 16:00 | 2 | 15 | 63180-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29635489 //RELEASED BY CREW 077H04 BAD CUTOUT ON POLE 313;; 41 POLE 313..9 IS THE TAKE OFF POLE ;;WILL SEND JOB TO TECH. TO CHANGE OUT POLE L3/HFP IDCC PN9, TOF1426, MCCDIS XXXX
25585 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-02-02 10:50 | 2012-02-02 11:20 | 1 | 30 | 4315641 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD CONNECTION VER/KEP IDC XXXX
25586 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-12-30 21:28 | 2014-12-30 21:43 | 2 | 15 | 4893621 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON PRIMARY RISER, ON TAKE OFF FOR SINGLE PHASE TAP, ON 3 PHASE POLE, WILL HAVE TO OPEN TAP AND CLIMB TO FIX. POLE 387-279.OPEN FUSE AT 21:28 AND MADE REPAIRES, CLOSED FUSE AT 21:43HRS..ALL POWER RESTORED.P.HICKS RELEASED BY CREW 077H09/ ISO 37830387C00279/ COD 2// VER/BOW
25587 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-07-11 22:00 | 2009-07-11 22:30 | 1 | 30 | 60422-1 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT == REPLACED CUTOUT === POWER OK L3/HFP IDCC TOF2046, ESTIMATED TIME OFF XXXX
25588 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-07-06 12:30 | 2014-07-06 13:00 | 1 | 30 | 4196521 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SERVICE BURNT INTO REPAIRED/// CCC 1/// VER/HFP L3/HFP
25589 | Hazard | 3310502 | HADDIX | CANOE | 2018-08-08 19:42 | 2018-08-08 20:12 | 1 | 30 | 4930061 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | cut arrester in the clear and refused transformer
25590 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-01-01 18:30 | 2009-01-01 19:00 | 1 | 30 | 50517-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3301701// == LASHING WIRE CUT INTO ONE OF THE HOT LEGS == BURNING NEUT INTO ON 1/0 LASH == REPAIRED == CUST MAY HAVE DAMAGES ==//VER/CRB L3/JAW IDC CHANGED START TIME FROM 1143 ALLOWING 30 MIN FOR REPAIR, CHANGED CAUSE FROM OTHER XXXX
25591 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-06-18 16:00 | 2019-06-18 16:30 | 1 | 30 | 4538501 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | T LEWIS/// 1/0 secondary between 39831124B22545, and 39831124B22549 Burned up at 1124-b2-2545, one hot leg holding secondary up. Pole 1124-b2-2545 Has multiple wood pecker holes around telephone, and is hollowed out. Need Crossarm to scab pole to make safe to climb. Windstream pole, send copy to technicians to get a job written to get pole changed. Crew required. 1/0 secondary between 39831124B22545, and 39831124B22549 Burned up at 1124-b2-2545, one hot leg holding sec BLANKED OUT 105 AND 107 ME
25592 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-10-21 22:15 | 2008-10-21 22:45 | 1 | 30 | 57761-1 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION FROM SERVICE TO SEC.....DAH//3411902//VER/CRB IDC CHANGED TIME OFF FROM 2139, ESTIMATED TIME OFF XXXX
25593 | Hazard | 3303901 | LESLIE | HYDEN | 2022-04-28 19:18 | 2022-04-28 19:33 | 2 | 15 | 4812651 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | changed xfmr, customer out for 15 min while changing, secondary bushing leaking, open 19:18, closed 19:33, p.hicks
25594 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-04-21 15:05 | 2020-04-21 15:35 | 1 | 30 | 4729181 | 30 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Power restored @ 15:35
25595 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-12-31 19:07 | 2020-12-31 19:37 | 1 | 30 | 4839671 | 30 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse broke. Power restored @ 19:37
25596 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-07-10 11:00 | 2020-07-10 11:29 | 1 | 29 | 4140761 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout open transformer at1100 and closed at 1129
25597 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2022-12-21 16:06 | 2022-12-21 16:35 | 1 | 29 | 4284831 | 29 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | 3phase service 1 transformer blown back in and power restored 16:35
25598 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-03-18 13:39 | 2010-03-18 14:08 | 1 | 29 | 51375-1 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25KVA SEN TO LLOYD MC. WR#34303783 NO OUTAGE TILL CREW OPENS TO REPLACE// CUSTOMER OFF AT 13:39 BACK ON AT 14:08 REPLACED 15 KVA WITH 25 KVA PLUS RESQUEEZED NEUT ON SERVICE VER/KEP L3/KEP IDC XXXX
25599 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-02-11 17:26 | 2012-02-11 17:55 | 1 | 29 | 4336701 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE REPLACED FUSE///VER/CRB IDC XXXX
25600 | Hazard | 3303901 | LESLIE | HYDEN | 2022-03-29 14:51 | 2022-03-29 15:20 | 1 | 29 | 4688071 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | putting service back up
25601 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-08-30 09:15 | 2011-08-30 09:44 | 1 | 29 | 4774121 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED CHG CONNECTIONS// VER/DBM IDCC TOF0801 FLICKERING CALL ESTIMATED TIME OFF XXXX
25602 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-02-20 17:21 | 2018-02-20 17:50 | 1 | 29 | 4865271 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad secondary wire , insulation gone off wire in several places , replacing wire, opened service at 17:21 replaced wire restored power at 17:50.
25603 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-04-15 09:51 | 2013-04-15 10:20 | 1 | 29 | 4009951 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BROKEN FUSE LINK. COD-1 ISO TF 38830282000078 IDC XXXX
25604 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-07-20 12:14 | 2021-07-20 12:43 | 1 | 29 | 4938411 | 29 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | changed out connections at trailer pole & xfmer pole/cust experiencing part power apparantely/volt check good. pls close. tre
25605 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2013-04-05 13:41 | 2013-04-05 14:10 | 1 | 29 | 4981901 | 29 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | POLE 21-2058 6T FUSE BROKE ///VER/CRB L/3 /CRB IDC XXXX
25606 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-12-22 15:26 | 2010-12-22 15:55 | 1 | 29 | 55113-1 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BLOWN ON POLE 37830248C00060 === FUSE BROKE-- POWER RESTORED.//VER/CRB IDC XXXX
25607 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-10-25 12:01 | 2012-10-25 12:30 | 1 | 29 | 4171031 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC AT 1230 VER/KEP IDC XXXX
25608 | Hazard | 3309003 | JEFF | VIPER | 2020-03-18 15:58 | 2020-03-18 16:27 | 1 | 29 | 4489241 | 29 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad conn. on transformer pole opened at 15:58 closed at 16:27 power ok
25609 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2022-06-14 18:46 | 2022-06-14 19:15 | 1 | 29 | 4115571 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary has strands broke in it. Going to open up clamp on pole 377b-228 so i can let wire down to make repairs. Restored at 19:15
25610 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-11-06 13:05 | 2014-11-06 13:34 | 1 | 29 | 4704451 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING DAMAGED TRANSFORMER.OPENED TRANSFORMER AT 13:05. CLOSED IN AT 13:34// COD 1// VER/ ADH
25611 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2016-03-15 11:31 | 2016-03-15 12:00 | 1 | 29 | 4850781 | 29 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | RISER FALL OUT OF LUG ON TRANSFORMER I MADED REPAIRS ALL IS GOOD AT THIS LOC , TIME REPAIRED 1200// VER/ ADH
25612 | Hazard | 3302704 | HAZARD | KENMONT | 2018-04-09 10:00 | 2018-04-09 10:29 | 1 | 29 | 4203131 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | off 1000-1029 K MILLER CHANGING CUTOUTS.
25613 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-05-01 15:50 | 2018-05-01 16:19 | 1 | 29 | 4294841 | 29 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 xfm. cutout broke on pole 190C-110.will make repairs../ ISO 37830190C00110/ COD 1
25614 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-12-05 02:17 | 2020-12-05 02:24 | 4 | 7 | 4746601 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout feeding side tap on pole 900-27 is going bad and cracked. This is what customer saw arcing. I will be de-energizing to safely replace// Off@02:17 replaced cutout and restored @02:24
25615 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-06-01 18:15 | 2010-06-01 18:29 | 2 | 14 | 55020-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANSFORMER AT POLE 38830070B43501 AT 18:15 FOR APX 15 MINUTES TO MAKE REPAIRS-TRANSFORMER BACK ON AT 18;29//COD 2// VER/DBM IDC XXXX
25616 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-06-16 11:43 | 2010-06-16 12:11 | 1 | 28 | 66198-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RANDY FOUND BAD CUTOUT REPLACED // ON AT 1205
25617 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-28 10:17 | 2011-06-28 10:45 | 1 | 28 | 4426301 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR.//COD 1// VER/DBM IDC XXXX
25618 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-09-06 09:27 | 2022-09-06 09:55 | 1 | 28 | 4845341 | 28 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection at weather had went bad. Made repairs. Power restored.
25619 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-12-17 07:32 | 2014-12-17 08:00 | 1 | 28 | 4865721 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE, ON 0800// COD 1//POLE 68-786 6T TRANS, FUSE BROKE REFUSED// VER/ ADH
25620 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-03-21 14:23 | 2017-03-21 14:51 | 1 | 28 | 4575251 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRIMARY TIE WIRE BROKEN FROM PIN--CREW ON SITE TO RE-TIE --ALSO CHANGING CUTOUT AND ARRESTOR WHILE WORKING POLE--FETR 15:01--OENED XFMR AT APPX 14:23---BACK IN AT 14:51--3 CUSTOMERS OUT TOTAL-TBL TKT COMP 38830044C24564 VER/AWD
25621 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2019-02-15 09:31 | 2019-02-15 09:59 | 1 | 28 | 4796521 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE
25622 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-11-22 16:36 | 2022-11-22 16:50 | 2 | 14 | 4174201 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out burnt opened tap from 1636 everything back on at 1650
25623 | Pikeville | 3413401 | GARRETT | GARRETT | 2010-03-28 14:08 | 2010-03-28 14:22 | 2 | 14 | 55253-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 66-83 //VER/GAH IDC CHANGED COUNT FROM 1 SEE 55252-1 XXXX
25624 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-03-28 10:52 | 2011-03-28 11:06 | 2 | 14 | 59823-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL BROKEN MID-SPAN. OPENED TRANSFORMER AT 10:52 -- CLOSED AT 11:06 --POWER RESTORED. ONLY 1 CUSTOMER AFFECTED BY THIS OPEN NEUTRAL.//VER/CRB IDC CHANGED CLEARING DEVICE FROM SECONDARY XXXX
25625 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-03-05 17:45 | 2013-03-05 17:59 | 2 | 14 | 4872711 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT. COD-2 ISO TF 38821061A00002 VER/HFP L3/HFP IDCC TOF1653 ESTIMATED TIME OFF XXXX
25626 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-10-09 11:11 | 2020-10-09 11:25 | 2 | 14 | 4539351 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customers service neutral broke @service pole, will have to open trans. to make repairs, will keep track of times. Opened trans. @95-272 @1111, made repairs and closed back in @1125.
25627 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2022-06-07 11:51 | 2022-06-07 12:19 | 1 | 28 | 4030581 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Replacing secondary pole 38830094D16061 (1COD) crew on site changing out rotten windstream pole 1 customer out when moving to new pole times 11:51to 12:19 please close ticket LRM
25628 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-09-27 15:47 | 2010-09-27 16:15 | 1 | 28 | 54346-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BAD FUSE LINK.//COD 1// VER/DBM IDC XXXX
25629 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-06-26 10:47 | 2008-06-26 11:15 | 1 | 28 | 54693-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000801// CREW TO REPLACE TRANSFORMER/ REYNOLDS BACK ON @ 1115 // REPLACED TRANSFORMER READING OF 123/123/246 // OFF @ 1047 ON @ 1115 // VER/TOM IDC XXXX
25630 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-12-28 11:40 | 2021-12-28 12:08 | 1 | 28 | 4230761 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Can not see anything wrong there is a buzzing on pole 482A/62 need line crew in AM 19.9 cutout and arr. T/bracket 5 pole top insulatores line crew and flaggers maybe tie wirw cant really tell send to J.Gilley been here 2 times cuut. has called 5 times Released by crew 077S03, found arrester tracking over will need to open xfmr to repair// off@1140 on@1208
25631 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-09-06 14:00 | 2022-09-06 14:28 | 1 | 28 | 4847461 | 28 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in customers service drop at pole 1150-19, made repairs and restored at 14:28
25632 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-01-12 10:19 | 2009-01-12 10:47 | 1 | 28 | 54416-1 | 28 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3001003//WR# 28024324/ BAD SPLICE IN SERVICE DROP VER/KEP L3/KEP IDC XXXX
25633 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-06-29 12:35 | 2016-06-29 13:03 | 1 | 28 | 4501591 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CAME OUT ON STOPPED METER, AND D TO D LIGHT OUT, FOUND BAD 10 KVA, CREW REQ, CAN USE TRUCK, JUST FEEDS GARAGE AND D TO D LIGHT SEND TO MR. RAYBURN, TO HAVE CREWS COME TAKE CARE OF THIS RELEASED BY CREW 078S06 VER/CRB
25634 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-11-17 10:17 | 2008-11-17 10:45 | 1 | 28 | 65901-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP S/C CUTOUT DOOR 6T BURNT UP COD-1 IDC XXXX
25635 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-02-07 14:42 | 2019-02-07 15:10 | 1 | 28 | 4764101 | 28 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Insulink splice came loose at weather head. I made repairs customer now has full power
25636 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2019-04-02 11:30 | 2019-04-02 11:58 | 1 | 28 | 4049671 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Changed bad cutout opened 11:30 closed 11:58 L3/HFP
25637 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-03-16 12:47 | 2010-03-16 13:15 | 1 | 28 | 50726-1 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED XFMR FUSE THAT WAS BROKE//COD 4 IDCC CNT4, PN537 XXXX
25638 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-03-27 14:48 | 2020-03-27 14:55 | 4 | 7 | 4516921 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Single phase primary down repaairs made Off @ 13:15 back on @ 14:55
25639 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-06-05 10:32 | 2018-06-05 11:00 | 1 | 28 | 4557651 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | one cust out to make repairs to ug repairs made cust restored please close ticket thanks.bt
25640 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2012-08-10 17:40 | 2012-08-10 18:08 | 1 | 28 | 4925951 | 28 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | 1 FUSE OUT IN BANK--BROKEN FUSE LINK COD-1 ISO TF 38830045A31239 VER/HFP L3/HFP IDC XXXX
25641 | Hazard | 3303902 | LESLIE | WOOTON | 2021-01-04 15:51 | 2021-01-04 16:05 | 2 | 14 | 4847661 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 37830463A20137
25642 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-06-08 21:20 | 2011-06-08 21:48 | 1 | 28 | 4272481 | 28 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 40310206 POLE 68-208 BAD PLACE IN 4/3 DROP REPAIRED ADJUSTED TIME OFF (2120) UNTIL APPROXIMATE ARRIVAL TIME TO ALLOW FOR REPAIRS... NO OUTAGE UNTIL THEN.. VER/HFP L3/HFP IDC XXXX
25643 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-04-22 19:57 | 2009-04-22 20:25 | 1 | 28 | 52105-1 | 28 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP WR # 29481951 // L3/HFP IDC XXXX
25644 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-02-18 19:23 | 2022-02-18 19:50 | 1 | 27 | 4514431 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke back in at 1950
25645 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-10-22 11:30 | 2013-10-22 11:57 | 1 | 27 | 4953311 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BARE SPOT ON OLD S/D BURNED NEUT. IN TWO// REPAIRS MADE - ADJUSTED TIME OFF TO AFTER SERVICER ARRIVED -- HE PULLED METER TO REPAIR SERVICE VER/HFP L3/HFP IDCC CCO XXXX
25646 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-01-20 08:03 | 2017-01-20 08:30 | 1 | 27 | 4314391 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 69-6072 6T TRANS FUSE BROKE VER/CRB L3/HFP XXXHFP
25647 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-12-14 12:58 | 2012-12-14 13:25 | 1 | 27 | 4469851 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CRE REQUIRED BROKEN FUSE LINK COD-1 ISO TF 38830175000077 VER/HFP L3/HFP
25648 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-12-09 11:53 | 2013-12-09 12:20 | 1 | 27 | 4136821 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COMPETED 12 09 13 TOMCCOWN RESTORED VER/CRB L3/HFP
25649 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-03-04 13:35 | 2011-03-04 14:02 | 1 | 27 | 66476-1 | 27 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL WIRE PULL LOOSE ADJUSTED TIME OFF TO ALLOW FOR REPAIRS OF NEUTRAL // VER/HFP L3/HFP IDC XXXX
25650 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-05-18 20:51 | 2008-05-18 21:00 | 3 | 9 | 65631-1 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409301// SPAN OF OPEN WIRE SECONDARY DOWN IN PASTURE. REMOVED WIRE FROM POLE 836-7 TO 836-8 AND REWORKED XFMR. ALSO REMOVED SEC. GUY AND ANCHOR AT CUSTOMERS REQUEST AS IT IS NO LONGER NEEDED. OPENED XFMR AT 20:51 - CLOSED AT 21:00. SH VER/JHM IDCC MCCNI XXXX
25651 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-05-26 19:58 | 2013-05-26 20:07 | 3 | 9 | H4186551B | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN, 1 CUST HAD PART POWER. TR OUTAGED AT THE FOLLOWING TIMES... 1752-1805 1958-2007 2207-2245. CC 4. ORIGINAL OUTAGE 4186551. DUPLICATE OUTAGES H1181075-1, H1181076-1 & H1181077-1. VER/SDB IDCC CNT1 XXXX
25652 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2013-06-16 08:26 | 2013-06-16 08:53 | 1 | 27 | 4347371 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED LOOSE ON ONE PHASE//RESTORED 0853//DIFFERENT TRANSFORMERS ON THIS BANK HAVE BEEN OUT MULTIPLE TIMES OVER PAST FEW WEEKS, SEND TO ENGINEERING TO SEE ABOUT POSSIBLE UPGRADE//COD 1//EMAILED TO ENGINEERING// VER/DBM IDC XXXX
25653 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-01-25 13:44 | 2010-01-25 14:11 | 1 | 27 | 59547-1 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PART POWER, LEAD HAS COME LOOSE FROM XFMR, REPAIRED CONNECTION IDC XXXX
25654 | Hazard | 3309302 | VICCO | JEFF | 2012-12-10 10:45 | 2012-12-10 11:12 | 1 | 27 | 4455601 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSF POLE === REPLACED CUTOUT === OPEN TRANSF 10:45 BACK ON AT 11:12 === POWER OK COD-1 ISO TF 37830322C00242 VER/HFP L3/HFP
25655 | Pikeville | 3421001 | BREAKS | CITY | 2014-03-17 13:15 | 2014-03-17 13:42 | 1 | 27 | 4502491 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE POLE 220-725 EXTINGUISHED FIRE, CHANGING CUTOUT //VER/GAH
25656 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-03-07 14:21 | 2018-03-07 14:30 | 3 | 9 | 4976041 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Opened txmf at 1421 closed at 1430 apr. Tightned riser wire in top of txmf. apr close ticket
25657 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2016-01-28 15:21 | 2016-01-28 15:30 | 3 | 9 | H4656861 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON POLE 425-51, WILL HAVE TO OPEN LINE FUSE ON THAT POLE TO REPLACE IT ..OPENED LINE FUSE AT 15:21 REPLACED CUTOUT RESTORED POWER AT 15:30.. VER/KEP
25658 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-11-29 07:42 | 2010-11-29 08:09 | 1 | 27 | H60429-1 | 27 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 60429-1 // OFF 07:42 TO 08:09 TO REPAIR.CHARLIE HALL IS CUSTOMER//COD 1// VER/DBM IDC XXXX
25659 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-03-25 10:15 | 2009-03-25 10:42 | 1 | 27 | 61302-1 | 27 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 080S01 REPLACED BAD CUTOUTS ON THREE PHASE TAP. IDCC TOF0904 XXXX
25660 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2009-07-29 17:25 | 2009-07-29 17:38 | 2 | 13 | 65042-1 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING TROUBLE, XFORMER OFF AT POLE#11-B-53, OFF AT1725, BACK ON AT 1738//COD 2//ISO 37820011A00053// VER/DBM IDC XXXX
25661 | South Williamson | 3411401 | DEWEY | INEZ | 2012-08-13 11:09 | 2012-08-13 11:35 | 1 | 26 | 4931961 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 768-243//REPAIRS MADE//RESTORED AT 11:35//COMPLETE//EM //VER/GAH IDCC PN233 XXXX
25662 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-03-09 14:56 | 2010-03-09 15:22 | 1 | 26 | 64341-1 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34182783 // LIFTED HOT TAP ON POLE 430-261 , 1 CUSTOMER VER/HFP L3/HFP IDCC PN327 XXXX
25663 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2015-08-11 10:04 | 2015-08-11 10:30 | 1 | 26 | 4122221 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE D BAD CUTOUT RESTORED POWER AT 10:30 VER/CRB
25664 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-03-11 09:12 | 2008-03-11 09:38 | 1 | 26 | 56136-1 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001002//POLE FIRE ON POLE 38830349000001, FIRE IS OUT AND CUTOUT REPLACED. POLE IS BURNT ABOUT 3/4 AT CUTOUT. 45 CLASS 5 POLE, TRUCK OK// REYNOLD WILL WORK// SERVICER MARKED AS NO INTERRUPTION - NO FETR// VER/TOM IDC CHANGED TOF FROM 0840 AND TON FROM 0946 XXXX
25665 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2022-10-26 10:51 | 2022-10-26 11:17 | 1 | 26 | 4067391 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | XFMR OPEN BROKE LEAD // RESTORED @ 11:17---replaced HT lead to cutout--comp--rmv
25666 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-02-08 11:30 | 2009-02-08 11:56 | 1 | 26 | 56705-1 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE ON SERVICE, REPAIRED SPLICE// VER/TOM L3/TOM IDC CHANGED START TIME FROM 1111 XXXX
25667 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-06-29 18:55 | 2017-06-29 19:21 | 1 | 26 | 4059231 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED 6T FUSE VER/CRB
25668 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2012-10-21 15:45 | 2012-10-21 16:11 | 1 | 26 | 4161081 | 26 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE PULLED APART IN THE SERVICE NEUTRAL, SERVICE TIGHT IN TREES AND VINES ///VER/CRB L/3 CRB IDCC TOF1505 ESTIMATED TIME OFF FOR REPAIR XXXX
25669 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-12-12 08:02 | 2017-12-12 08:15 | 2 | 13 | 90004652 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burnt into.opened xfmr to make repaires at 8:02 restored power at 8:15/ 1 customer part out originally/ when opened 2 add cust/ ISO 37830205D00107/ COD 3
25670 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-08-06 17:20 | 2022-08-06 17:33 | 2 | 13 | 4695001 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LF OPEN 27-16 / INSULATOR FAILED ON POLE 327-20
25671 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-02-24 12:04 | 2022-02-24 12:30 | 1 | 26 | 4540041 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE VACCANT HOUSE // COD 1 //
25672 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-06-12 07:55 | 2013-06-12 08:21 | 1 | 26 | 4262101 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/KEP IDCC FP205 XXXX
25673 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-04-05 19:40 | 2016-04-05 20:06 | 1 | 26 | 4055781 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CUSTOMER WAS HAVING FLICKERING LIGHTS AND LOW VOLTAGE UNDER LOAD REPLACE MELTED CONNECTIONS AT SERVICE POLE AND LOOSE TRANSFORMER CONNECTIONS AND SPLICE IN SERVICE DROP OPENED TRANSFORMER ON 98-B464 AT 19:40 AND RESTORED POWER AT 20:06 PLEASE SEND COPY TO PEGGY WYNSONG/ISO 37820098B00464/ COD 1/ VER/BOW
25674 | Whitesburg | 3314401 | MAYKING | ERMINE | 2019-02-21 19:02 | 2019-02-21 19:15 | 2 | 13 | 4840591 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repair connection on xfmr/ opened @ 1900 closed @ 1915
25675 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-12-21 15:45 | 2013-12-21 16:11 | 1 | 26 | 4181941 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NO CREW REQUIRED REPAIRED RISER//COD 1// VER/DBM L3/HFP
25676 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-05-27 09:04 | 2022-05-27 09:30 | 1 | 26 | 4963001 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout
25677 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-11-24 11:05 | 2014-11-24 11:18 | 2 | 13 | H4759981 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RED TO RED IS PULLED OUT ON POLE 400-1. OPENED X-FMR ON POLE 400-1 AT 11:05 TO MAKE REPAIRS AND CLOSED XFMR BACK IN AT 11:18 RESTORING POWER. 11/24/2014 // DUP OF 4759981 FOR 2 CUST WHEN TR OPENED // VER/HFP L3/HFP
25678 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2015-11-15 13:41 | 2015-11-15 14:07 | 1 | 26 | H4449321 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE BURNT DOWN DUE TO SIZE WILL REPLACE WITH 2/3 DROP 4/3 IS WHATS HERE RELEASED BY CREW 077H14SERVICE BURNT DOWN DUE TO SIZE WILL REPLACE WITH 2/3 DROP 4/3 IS WHATS HERE OPENED XFMR AT 13:41 CLOSED BACK AT 14:07 // DUP OF 4449321 FOR 1 -- ISO TF 37830295D00149 VER/HFP L3/HFP
25679 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-06-04 23:15 | 2008-06-04 23:28 | 2 | 13 | 57706-1 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS TRANSFORMER FUSE HANGING DOWN 38831108A00004 COD-2 VER/KEP
25680 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-06-19 13:07 | 2011-06-19 13:20 | 2 | 13 | 4343951 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACE CUTOUT AND ARRESTOR, PLEASE SEND A E-MAIL TO CLIFF FREEMAN POLE 24-963 IS ROTTEN AND NEED TO BE REPLACE SOON. // CHANGED TIME OFF TO TIME SERVICER OPENED TR TO REPLACE CUTOUT COD-2 ISO 37830024C00963 VER/HFP L3/HFP
25681 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-10-22 13:19 | 2013-10-22 13:45 | 1 | 26 | 4954331 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT BAD CUTOUT ON POLE#38831083C20166. HAD ONE CUST, OPEN TRANS AT 1319 AND CLOSED AT 1345 COD-1 ISO TF 38831083C20166 VER/HFP L3/HFP IDC XXXX
25682 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-03-28 17:34 | 2013-03-28 18:00 | 1 | 26 | 4965321 | 26 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK. VER/KEP IDC XXXX
25683 | Whitesburg | 3312901 | JENKINS | KONA | 2014-11-19 18:05 | 2014-11-19 18:30 | 1 | 25 | 4747071 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKE, CUSTOMER SAYS IT HAS BEEN BROKEN FOR A COUPLE OF MONTHS. REPAIRED SERVICE AND RESTORED POWER AT 1830//OLD # 4//OPENED LOOPS ON DROP AT 1805 VER/CRB
25684 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-11-03 15:45 | 2008-11-03 16:10 | 1 | 25 | 61894-1 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP RELATED TO ORDER 61792-1 CREATED THIS ORDER FOR TRANSFORMER OUTAGE SO CREW COULD REPAIR NEUTRAL CONDUCTOR THAT WAS DOWN. COD-1 IDCC U XXXX
25685 | Pikeville | 3421001 | BREAKS | CITY | 2014-05-09 20:45 | 2014-05-09 21:10 | 1 | 25 | 4678931 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BEEN ARCING. I AM GOING TO CHANGE CUTOUT. I OPENED TRANSFORMER ON 219-10 AT 20:45 AND CHANGED CUTOUT. I CLOSED TRANS. AT 21:10.//COD 1 VER/CRB
25686 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-12-26 09:50 | 2017-12-26 10:15 | 1 | 25 | 4678761 | 25 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connections burnt open on neutral and one hot leg//// will open Xfm and make repairs///Opened XFM @ 09:50 /// Made repairs to service drop connections and restored service @ 10:15/// Send copy to Peggy Wysong in case they are any damages
25687 | Hazard | 3303902 | LESLIE | WOOTON | 2014-09-01 16:30 | 2014-09-01 16:55 | 1 | 25 | 4444091 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING TRANSFORMER 317-12// LOOSE CONNECTION ON XFMR// OPENED 16:30// CLOSED 16:55// VER/BOW
25688 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-12-07 08:35 | 2015-12-07 09:00 | 1 | 25 | 4514931 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CALLED CUSTOMER BACK AND DID NOT GET ANSWER FUSE LINK BROKEN, REPLACED POWER RESTORED AT THIS LOC AT 0900 // COD-1 ISO TF 39830999000023 VER/HFP L3/HFP
25689 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-01-10 08:24 | 2018-01-10 08:49 | 1 | 25 | 4725551 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK 1/10 CALLED CUSTOMER: DD LIGHT MAKING BUZZING SOUND. OK WITH CUSTOMER TO CHECK IN MORNING. change cutout open transformer at 0824 and closed at 0849/ ISO 38831061A00192/ COD 1
25690 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-10-02 00:50 | 2011-10-02 01:15 | 1 | 25 | 4939241 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.POLE BURNING..WILL HAVE TO LIFT HOT LINE CLAMP..EXTINGUISH FIRE.& REPLACE CUTOUT..WILL NOTE OFF & ON TIMES..//..OPENED XFMR @ 00:50..REPLACED CUTOUT.DOUSED FIRE..CLOSED XFMR @ 01:15..POLE OK...JRV..010/02/11 //VER/GAH IDC XXXX
25691 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-11-18 15:19 | 2014-11-18 15:44 | 1 | 25 | 4742811 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS BROKEN, REFUSED XMF APR AT 1544 CLOSE TICKET COD-1 ISO TF 38830478B40063 VER/HFP L3/HFP
25692 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-05-11 00:30 | 2016-05-11 00:55 | 1 | 25 | H4195421 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT POLE 92-51 DUE TO BAD CUTOUT. HAD TO OPEN HOT LINE CLAMP POLE 92-51 AT 00:30 CLOSED LOOP AT 00:55 AND TRANFORMER BACK IN ON POLE 92-51 AT 00:55/// VER/ ADH
25693 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-05-24 09:00 | 2017-05-24 09:25 | 1 | 25 | 4847041 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO INTERRUPTION UNTIL I OPENED XFMR @ 9:00. REPLACED BAD CUTOUT AND RESTORED @ 9:25. COD-1 ISO TF 38830858A00384 VER/HFP L3/HFP
25694 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-11-26 11:28 | 2019-11-26 11:53 | 1 | 25 | 4069051 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened line fuse on pole 37830208000124 to safely change cutout on pole 37830208000128 off @ 1128 On @ 1153
25695 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-01-14 08:55 | 2013-01-14 09:20 | 1 | 25 | H4601781 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, CUTOUT BROKE/OPENED FUSE ON POLE#26 TO ISOLATE AT XFMR FUSE OUT, CUTOUT BROKE. OPENED LINE FUSE ON POLE 134-26 AT 08:55, REPLACED CUTOUT, CLOSED FUSE BACK AT 09:20. ALL POWER RESTORED COD-3 ON TRANS AND 1 MORE ON FUSE VER/KEP IDC XXXX
25696 | Hazard | 3310502 | HADDIX | CANOE | 2014-03-29 23:30 | 2014-03-29 23:55 | 1 | 25 | 4537351 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD CUTOUT GOING BAD , CHANGED OUT. OPENED XFMR @ 23:30 CLOSED BACK @ 23:55 VER/PDP
25697 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-03-31 11:55 | 2014-03-31 12:20 | 1 | 25 | 4547181 | 25 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | OPEN TRANS ON P 211-90 TO MAKE REPAIRS TO SERVICE DROP OPEN @ 11:55 CLOSED @ 12:20 PLEASE CLOSE TICKET//COD 1// VER/DBM
25698 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-12-23 18:55 | 2015-12-23 19:20 | 1 | 25 | 4553311 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER HAS 130 VOLTS PHASE TO GRD AND 260 VOLTS PHASE TO PHASE NEED TRANSFORMER REPLACED/ 1855-1920//HANDED OVER TO SWITCHING DESK// CALLING STATION SERVICER TO CHEK LTC / ISO 38821036C00004/ COD 1/ VER/BOW
25699 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-05-08 14:45 | 2012-05-08 15:10 | 1 | 25 | 4760461 | 25 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN, REPAIRED NEUTRAL, POWER RESTORED. ---- OPENED TRANSFORMER ON POLE 37830130000121 AT 14:45, CLOSED AT 15:10//COD 1// VER/DBM IDC XXXX
25700 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-09-14 13:35 | 2018-09-14 14:00 | 1 | 25 | 4096791 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CREW OPENING XFMR TO REPAIR BROKEN GUY /// 38830259000125 COD-1/open@13:35 closed@14:00 please close tic RM COD-1
25701 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-12-11 10:15 | 2020-12-11 10:40 | 1 | 25 | 4760421 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | opened tranformer to make repaire to service connector @1015 closed back in @1040
25702 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-05-08 22:20 | 2020-05-08 22:45 | 1 | 25 | 4815281 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | opened transformer @38821058B00069 affecting 1 CC to make up loop feeding towards 38821058D00174 (separate outage # 4814831 for CC)
25703 | Whitesburg | 3401301 | FLEMING | NEON | 2015-05-13 10:55 | 2015-05-13 11:20 | 1 | 25 | 4424871 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | HOUSE KNOB BROKE FROM CUST. HOUSE, HAD TO OPEN TRANS. AT POLE 355-451 AT 1055 TO MAKE REPAIRS, CLOSED BACK IN AT 1120//COD 1// VER/DBM
25704 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2016-08-01 08:35 | 2016-08-01 09:00 | 1 | 25 | 4717231 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 45-1751 40T LINE FUSE OUT 40T ME FUSE BROKE SEND NOTE TO BOB R. THIS UNDERGROUND IS THE OLD CABLE NEEDS CHGED/EMAILED BOB/LLYOD/ADH// VER/ ADH
25705 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-03-12 11:30 | 2013-03-12 11:55 | 1 | 25 | 4900881 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN SECONDARY GOING TO POLE 37830230A00134 IS LAYING ON CABLE CO. CABLE. WILL OPEN XFMR ON POLE 37830230A00101 TO RESAG OPEN SECONDARY. WILL KEEP TIME. OPENED XFMR AT 11:30 CLOSED AT 11:55. COMPLTED ///VER/CRB L/3 CRB IDC XXXX
25706 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-05-05 16:50 | 2021-05-05 17:15 | 1 | 25 | 4540441 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | on arrival i opened up the transformer fuse on pole 8-D-21.when i pulled in the (K-mate) current limiting fuse was on fire..a few min after i opened the door the K-mate burned in two..i remove the k-mate and wired the riser out of the bottom of the cutout straight to the transformer and closed the cutout door.fuse was open at 16:50 and restored at 17:15
25707 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-01-29 18:45 | 2010-01-29 19:10 | 1 | 25 | 61234-1 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CURRENT LIM. FUSE BURNING ----- REPLACED RISER IN XFMR. ALSO ONL 1 CUST. WAS OUT VER/KEP L3/KEP IDCC TOF1743 ESTIMATED TIME OFF XXXX
25708 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-12-31 13:35 | 2014-12-31 14:00 | 1 | 25 | 4895051 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 38830020B20365 FUSE BROKE REPLACED FUSE AND OLD BROWN DOOR VER/CRB
25709 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-07-03 10:10 | 2013-07-03 10:35 | 1 | 25 | 4453191 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 140-2014 TRANS HAS HIGH VOLAGE 131-251 VOLTS NEED LINE CREW 25KVA TRUCK OK 19.9 TRANS. RELEASED BY CREW 078S08,,OPENED XFMR AT 10:10, CLOSED NEW XFMR AT 10:35, VOLTAGE 124-124-248, ALL POWER RESTORED VER/CRB L/3 CRB
25710 | Hazard | 3303902 | LESLIE | WOOTON | 2020-03-30 14:45 | 2020-03-30 15:10 | 1 | 25 | 4543081 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad neutral service connection. Opened transformer at 14:45 Closed at 15:10
25711 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-04-17 11:36 | 2019-04-17 12:01 | 1 | 25 | 4125671 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | opened xfr @ 11:36 closed @ 12:01 complete,,,replaced secondary connections
25712 | Hazard | 3303902 | LESLIE | WOOTON | 2020-05-28 15:00 | 2020-05-28 15:25 | 1 | 25 | 4921741 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
25713 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-12-20 08:10 | 2013-12-20 08:35 | 1 | 25 | 4178241 | 25 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | OPENED TRANSFORMER AT 08:10 DUE TO BAD CURRENT LIMIT FUSE. WILL BE MAKING REPAIRS. HAVE REPAIRS MADE CLOSED TRANSFORMER BACK IN AT 08:35 EVERYTHING OK//COD 1// VER/DBM L3/HFP
25714 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-12-08 16:42 | 2015-12-08 16:54 | 2 | 12 | H4518601 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | // REMOVED HOT TAP ON SIDE TAP AT 1642 ALL RESTORED AT 1654 RELEASED BY CREW 074S02 VER/CRB
25715 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-05-09 19:00 | 2013-05-09 19:24 | 1 | 24 | 4091251 | 24 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION IN SERVICE, ALSO PUTTING IN SLACK WHERE IT HAS PULLED MAST OVER. ///VER/CRB L/3 CRB IDCC MCCPP TOF1622, ESTIMATED TIME OFF XXXX
25716 | Hazard | 3302703 | HAZARD | HAZARD | 2022-12-21 08:40 | 2022-12-21 08:52 | 2 | 12 | 4282341 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad xfmr connections, repaired. Open @ 08:40 Closed @ 08:52
25717 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-01-21 17:06 | 2015-01-21 17:30 | 1 | 24 | 4950311 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE FUSE HAD PULLED LOOSE REFUSED XMD APR AT 1730 CLOSE TICKET/ ISO 38830453D20405/ COD 1/ VER/BOW
25718 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-11-24 11:59 | 2008-11-24 12:23 | 1 | 24 | 51604-1 | 24 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | XFMR FUSE ROTTED INTO//3308502//VER/CRB IDC XXXX
25719 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2015-04-10 17:25 | 2015-04-10 17:37 | 2 | 12 | H4303661 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED FULL ROLL FO #2 / 3 SERVICE DROP , LINE CREW AND MAN TREE CREW. TREES RUBED SERVICE DROP INTO/T.MORRIS ARRIVED ON SITE/ //IDC SETTING POLE ROCK HOLE/CREW OPENING TRANSFORMER454-B4-2586 TO MAKE REPAIRS/OPENED 1725 CLOSED 1737/ WORKING ON POLE 454-7623, SHOUDLN`T HAVE TO OUTAGE/ VER/KEP
25720 | South Williamson | 3200203 | BARRENSHE | SLATE BRANCH | 2010-08-10 10:03 | 2010-08-10 10:11 | 3 | 8 | 51928-1 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED STATION BREAKER TO ISOLATE REGULATORS ON POLE 1064-C-208 DUE TO REGULATOR STUCK IN 2 R //VER/GAH IDC XXXX
25721 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-08-19 20:36 | 2010-08-19 21:00 | 1 | 24 | H58437-1 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 449-1037 , OPENED LINE FUSE ON 449-560 AT 20:36 TO ISOLATE.. MADE REPAIRS RESTORED POWER AT 2100 VER/KEP L3/KEP IDC XXXX
25722 | Hazard | 3309302 | VICCO | JEFF | 2016-08-05 16:26 | 2016-08-05 16:50 | 1 | 24 | 4738931 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF OVERLOAD === CAUSEING LOW VOLTEAGE === NEED 1MAN & 50 KVA 19.9 TRANSF ==== OPEN TRANSF 16:26 CLOSED AT 16:50 CHANGED TRANSF POWER OK VER/CRB
25723 | Hazard | 3308001 | JACKSON | S.JACKSON | 2021-09-30 17:03 | 2021-09-30 17:15 | 2 | 12 | 4306341 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, GROUNDING | bad lug in xfmr ,opened@ 17:03 closed @ 17:15..
25724 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-12-12 15:16 | 2017-12-12 15:40 | 1 | 24 | 4642501 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse link broke. Restored @ 15:40. sh/ ISO 38830807000034/ COD 1
25725 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2013-07-18 15:35 | 2013-07-18 15:47 | 2 | 12 | 4550111 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CREW REQUIRED OFF AT 1535 BACK ON AT 1547//COD 2// VER/DBM IDC XXXX
25726 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-12-22 19:28 | 2021-12-22 19:36 | 3 | 8 | 4221121 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TransformerCutout is cracked on pole 333-57 need to open up to replace. Opened up at 19:28 closed back in at 19:36.
25727 | South Williamson | 3200302 | BELFRY | TOLER | 2015-08-04 22:04 | 2015-08-04 22:16 | 2 | 12 | 4978931 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CRACKED TRANS CUTOUT ON POLE 1039-A-8 REPLACED CUTOUT RESTORED POWER LIFTRD HOT TAP AT 22;04 CLOSED CUTOUT DOOR IN AT 22;16 VER/CRB
25728 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-12-14 11:36 | 2015-12-14 11:42 | 4 | 6 | 4530061 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | ANCHOR HAS PULLED OUT ON THE TRANSFORMER DEADEND POLE LETTING THE POLE LEAN CAUSING THE SERVICE NEUTRAL TO BREAK. I OPENED THE TRANSFORMER AT 11:36, AND CLOSED AT 11:45. SEND TO CLIFF FREEMAN TO REPLACE THE ANCHORS ASAP. THIS IS THE SECOND TIME WE HAVE HAD TROUBLE BECAUSE OF THE ANCHOR. COD-4 ISO TF 38820966A10493 VER/HFP L3/HFP
25729 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-03-18 17:36 | 2016-03-18 18:00 | 1 | 24 | 4862471 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER STATES HEARING BUZZING NOISE INTERMITTENTLY I COULDNT FIND ANYTHING WRONG BUT SINCE I WAS HERE I CHANGED CUTOUT AND BRACKET IN CASE IT WAS BAD AND I COULDNT TELL TOOK TRANS OFF @17:36 CLOSED IT IN AT 18:00 ISO 37820025D00208 COD 1 VER/AWD
25730 | Whitesburg | 3401301 | FLEMING | NEON | 2015-07-26 16:50 | 2015-07-26 17:14 | 1 | 24 | 4944081 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT SECONDARY , OPEN XFMR AT 16:50 MADE REPAIRS ,RESTORED POWER AT 17:14.. VER/CRB
25731 | Paintsville | 3401101 | FALCON | FALC-OILS | 2021-06-10 14:11 | 2021-06-10 14:35 | 1 | 24 | 4706971 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT Replaced and restored @ 14:35. sh
25732 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-11-24 18:30 | 2008-11-24 18:54 | 1 | 24 | 51710-1 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410501//REPLACED BAD XFR CUTOUT//COD 1//ISO// VER/DBM IDC XXXX
25733 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2010-12-12 11:17 | 2010-12-12 11:25 | 3 | 8 | 65537-1 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38077398 // OPENED TR @ 1117 TO MAKE REPAIRSSTS WR # 38077398 //BAD CONNECTIONS, REPLACED CONNECTIONS ON TRANSFORMER COD-3 ISO TF 37830381C00535 VER/HFP L3/HFP IDC XXXX
25734 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-04-04 14:15 | 2008-04-04 14:39 | 1 | 24 | 63936-1 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000701// BAD SERVE ENDS ON HOUSE SIDE, HAVE RESQUEEZED, AND EVERYTHING IS OK, AT THIS LOCATION VER/HFP IDCC TOF1348 ALLOWED 25 MIN FOR REPAIR XXXX
25735 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-10-17 17:53 | 2015-10-17 18:17 | 1 | 24 | 4356351 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6A NEUTRAL DOWN/NO OUTAGE/WILL NEED TO OPEN XFMR FOR REPAIRS/APROX ONE OUR OUTAGE/VEM/FOUND BAD XFMR CUTOUT AS WELL/OPEN XFMR @1753/REPAIRS MADE AND POWER RESTORED 1817/PLEASE CLOSE TICKET/THANKS/VEM 38830596000035 VER/CRB
25736 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-01-17 13:55 | 2009-01-17 14:07 | 2 | 12 | H57389-1 | 24 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP THIS IS FOR TR OUTAGE ///SERVICE NEUTRAL BROKEN IN MIDSPAN. I OPENED TRANSFORMER AT 1355 AND CLOSED BACK AT 1407 COD-3 L3/HFP AJBC CNT3 CDC91. FIRST CUST WAS OUT FROM 10:39 TO 14:07. SEE 57389-1.
25737 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-12-16 15:31 | 2016-12-16 15:43 | 2 | 12 | H4200141 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ***SEE 4200141*** ONE BAD SECONDARY UNDERGROUND LEG, SIZE OF COND IS 350. CREW REQUIRED/ ONLY 3 CUSTOMERS AFFECTED WITH PART POWER 38830478C20582 ORIGINALLY/ OPENED 38830478C20577 (2 CUST ADD.) @ 1441 TO MOVE CONDUCTOR CLOSED @ 1503 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD) @ 1531 TO DO SOME CONNECTIONS CLOSED @ 1543 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD.) @ 1722 TO FINISH WORK CLOSED @ 1740 (REST. ALL 5 CUST)/ VER/BOW
25738 | Hazard | 3309301 | VICCO | REDFOX | 2010-01-13 10:25 | 2010-01-13 10:49 | 1 | 24 | 53417-1 | 24 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GOING BAD WILL NEED BIG BUCKET TO CHANGE CUTOUT... OPENED XFMR AT 10:25 & MADE REPAIRS RESTORED POWER AT10:49 VER/KEP L3/KEP IDC XXXX
25739 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-04-25 13:05 | 2012-04-25 13:28 | 1 | 23 | 4706231 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT HAS A CRACK IN IT CAUSING IT TO BUZZ WHEN IT WAS RAINING THIS MORNING. REPLACED CUTOUT, RESTORED POWER AT 13:28 //VER/GAH IDCC TOF1034 ESTIMATED TIME OFF, PN NULL XXXX
25740 | Pikeville | 3409502 | BURDINE | LEVISA | 2018-09-18 17:01 | 2018-09-18 17:24 | 1 | 23 | 4127081 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened transformeronpole 37830358C00195 at 1701 cleared secondary up and closed at 1724. P R will send a crew to put the secondary back up tomorrow.
25741 | Hazard | 3309302 | VICCO | JEFF | 2011-03-18 14:17 | 2011-03-18 14:40 | 1 | 23 | 55359-1 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF CUTOUT IS BURNING ON POLE 37830299C00251 === NEED BIG BUCKET TO CHANGE OUT CUTOUTS == CENTER PHASE === === CALLED FOR LINE CREW === WILL WORK LATER TODAY RELEASED BY CREW 077S03TOP OF CUTOUT IS BURNING ON POLE 37830299C00251 === NEED BIG BUCKET TO CHANGE OUT CUTOUTS == CENTER PHASE === MAY NEED TO BRING ALL 3 === CALLED FOR LINE CREW === WILL WORK LATER TODAY RELEASED BY CREW 077S01 OPENED LINE AT 1417 ON AT 1440 REPLACED CUTOUT CREW 077H01//COD 1//ISO// VER/DBM IDC DCMT XXXX
25742 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-10-05 15:07 | 2018-10-05 15:30 | 1 | 23 | 4201731 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required 6t L3/HFP
25743 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2019-04-30 10:10 | 2019-04-30 10:33 | 1 | 23 | 4187781 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Insulink connection failing on transformer pole 833-27. Opening xfmr to make repairs. Had xfmr open from 10:10 to 10:33 to make repairs. sh L3/HFP
25744 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-03-02 13:04 | 2015-03-02 13:27 | 1 | 23 | 4091651 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW FOUND BAD CUTOUT ON POLE 427-D-53/BAD CUTOUT CHANGED ON PN 427-53 PLEASE CLOSE TICKET THANKS DWW CLOSED 1327// VER/ ADH L3/HFP XXX
25745 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-04-08 23:30 | 2009-04-08 23:53 | 1 | 23 | 50642-1 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/KEP L3/KEP IDCC MCCDIS CHANGED TIME OFF FROM 2149 XXXX
25746 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-10-16 11:12 | 2015-10-16 11:35 | 1 | 23 | 4353591 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT WILL REPLACE POWER RESTORED KWB VER/CRB
25747 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-05-04 11:24 | 2017-05-04 11:47 | 1 | 23 | 4744181 | 23 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT/ WILL OPEN XFMR TO REPLACE/ FEEDS DD LIGHT AND 1 CUSTOMER/ ISO 37830284000117/ COD 1...OPENED @ 11:24 AND CLOSED BACK IN @ 11:47..METER # 533744490/ MD DONE/ VER/BOW
25748 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-22 15:14 | 2022-06-22 15:37 | 1 | 23 | 4276501 | 23 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral burnt into in service drop///Repaired broken neutral///Good voltage @ meter 124/124/248////Customer has damages please send copy to Damage claims////
25749 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-01-11 19:40 | 2015-01-11 20:02 | 1 | 22 | 4928691 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RED/RED SERVE END WENT BAD & BURNED NEUTRAL INTO ON SERVICE . OPENED XFMR ON POLE 196-28 @ 19:40 CLOSED BACK @ 20:02/ ISO 37830196D00028/ COD 1/ VER/BOW LE/DKGXXXX
25750 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-01-14 20:20 | 2017-01-14 20:31 | 2 | 11 | 4298601 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BREAKING DOWN ON POLE 37830190C00111 NO OUTAGE WHEN ARRIVED/ WILL NEED TO OPEN TRANS AND HOT LINE CLAMP/ ISO 37830190C00111/ COD 2/ OPENED @ ____ CLOSED @____XFM. CUTOUT BREAKING DOWN ON POLE 190C-111.WILL HAVE TO LIFT HOT TAP FEEDING TO POLE 190C-281 FEEDING ONE OTHER CUSTOMER TO CHANGE OUT SAFELY..XFM. CUTOUT BREAKING DOWN ON POLE 190C-111.WILL HAVE TO LIFT HOT TAP FEEDING TO POLE 190C-281 FEEDING ONE OTHER CUST TO CHANGE OUT SAFELY..OPENED @ 20:20 AND CLOSED BACK @ 20:31. VER/BOW L3/HFP XXXHFP
25751 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-12-21 11:38 | 2019-12-21 12:00 | 1 | 22 | 4174661 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad insilink, repaired
25752 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-10-10 16:09 | 2009-10-10 16:20 | 2 | 11 | 54728-1 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON TR 989-196 SERVICER OPENED AT 1609 TO MAKE REPAIRS., .CUTOUT FAILED /./ VER/TOM IDC XXXX
25753 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-12-21 00:56 | 2012-12-21 01:18 | 1 | 22 | 4495831 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | SERVICER FOUND B PHASE TR OUT. NOTHING FOUND FUSE HAD PULLED LOOSE. APR AT 0118 CLOSE TICKET VER/PDP
25754 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-05-14 17:23 | 2011-05-14 17:45 | 1 | 22 | 4092741 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC
25755 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2021-05-10 09:51 | 2021-05-10 10:13 | 1 | 22 | 4569641 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | B PHase hot line clamp lead burnt in to---open xfmr bank @ 09:51 to make repairs---made repairs pwr restored to xfmr bank @ 10:13---tbl tkt comp---rmv
25756 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-10-30 11:58 | 2020-10-30 12:20 | 1 | 22 | 4606761 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on the primary metering on pole 247-B-954. I opened the primary metering at 11:58, repaired the failed connection and restored power at 12:20.
25757 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-11-15 10:14 | 2018-11-15 10:36 | 1 | 22 | 4413801 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout at pole 404-062. replaced cutout, ticket complete. L3/HFP
25758 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-02-08 09:42 | 2022-02-08 10:04 | 1 | 22 | 4457131 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | COD 1//RE-WORKING CUSTOMERS SERVICE DROP//TRANSFORMER NOT OPENED// had customer at 218 barn br off from 09:42 to 10:04 no other customers interrupted
25759 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-03-24 09:59 | 2016-03-24 10:21 | 1 | 22 | 4876541 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BAD CUTOUT - COMPLETE AT 1021// VER/ ADH
25760 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-01-12 14:55 | 2020-01-12 15:17 | 1 | 22 | 4290891 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad insulink. repairs made. pls close. tre/ ISO 39831147C35050/ COD 1
25761 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-05-31 08:56 | 2011-05-31 09:18 | 1 | 22 | 4212061 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER BANK AT 0856;; CLOSED AT 0918. BAD CONNECTION ALL POWER RESTORED CLOSE TICKET//VER/CRB IDC XXXX
25762 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2019-02-28 09:33 | 2019-02-28 09:55 | 1 | 22 | 4936511 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced service connections ,,complete
25763 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-04-17 13:00 | 2013-04-17 13:22 | 1 | 22 | H4016911 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD ON LINE FUSE POLE, THERE IS TWO CUTOUTS ON THIS POLE THAT NEEDS TO BE CHANGED , I WILL NEED HELP RELEASED BY CREW 077S12 PULLED 2ND TAP OFF AT 1300 BOTH ON AT1322 RELEASED BY CREW 075H01 VER/KEP IDC XXXX
25764 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-01-27 10:20 | 2014-01-27 10:31 | 2 | 11 | 4316701 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | COD 2//SERVICER OPENED OTHER 2 PHAES (A&C) TO MAKE REPAIRS RELATED TO 4316061// IDCC CCO, CNT4 XXXX
25765 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-11-26 12:47 | 2011-11-26 13:09 | 1 | 22 | 4115691 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BROKEN DOWN ON POLE 311-129. I AM GOING TO CHANGE CUTOUT. (OPEN XFMR). I CHANGED CUTOUT AND CLOSED TRANS. IN AT 13:09. VER/PDP IDC XXXX
25766 | Cannonsburg | 3110901 | WURTLAND | WURTLAND | 2008-09-25 15:48 | 2008-09-25 16:10 | 1 | 22 | 50549-1 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3110901// HAVE A FUSE OUT ON A 480V TRANSFORMER BANK, CAUSE WAS DOOR WAS BURNTED INTO, REPLACED DOOR, AND REFUSED IT, EVERYTHING IS OKIE DOKIE HERE NOW//COD 1// VER/DBM L3/GDK FEC 49 IDC XXXX
25767 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-01-25 19:33 | 2019-01-25 19:55 | 1 | 22 | 4723051 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on pole opened xfmr at 19:33 closed at 19:55
25768 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2012-12-03 15:10 | 2012-12-03 15:32 | 1 | 22 | 4439261 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV CUTOUT HERE PER STEVE MARTIN//---- TIME OFF 15:10----- TIME ON 15:32 //COD 1?// VER/DBM IDC XXXX
25769 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2015-01-23 04:08 | 2015-01-23 04:30 | 1 | 22 | 4952341 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED UP XFMR ON POLE 1052-416 AT 4:20 CLOSED BACK AT 4:30, HAD TO REPLACE MELTED 4/0 SEC LEAD ON XFMR VER/TOM L3/TOM
25770 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2020-04-27 13:07 | 2020-04-27 13:29 | 1 | 22 | 4757571 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1307 - 1329 OPENED XFRMR TO MAKE REPAIRS TO CONNECTIONSbad connections at weather head. opened xfmr bank on 115B372 1307 to make repairs, closed at 1329
25771 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-06-13 23:10 | 2022-06-13 23:21 | 2 | 11 | 4080391 | 22 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connections on XFMR 223-B-201, this XFMR was opened at 23:10 and closed at 23:21.
25772 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-03-28 15:05 | 2019-03-28 15:27 | 1 | 22 | 4033491 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WHILE@SITE ABT A WEEK AGO,OBSERVED THE XFR CUTOUT HAD A BIG CRACK IN IT.REPLACED BAD XFR CUTOUT
25773 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-10-27 17:44 | 2022-10-27 17:55 | 2 | 11 | 4072531 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | No outage untill arrived and opened LF on 624-161 , to replaced failed cutout. Off at 1744 apr at 1755. close ticket. dwest
25774 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-02-24 11:27 | 2016-02-24 11:49 | 1 | 22 | 4756381 | 22 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY HAS SLACK IN IT , CONTACT WITH PRI BUSHING ON XFMR, BLOWN MID PHASE XFMR FUSE. RESAG GUY AND REFUSED XFMR @ 11:49 HRS ALL POWER RESTORED. P.HICKS VER/CRB
25775 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-09 13:45 | 2018-06-09 13:52 | 3 | 7 | 4570781 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NEED CREW ,35C5 POLE ,1/0 TRIPLEX ,CLEVIS ,CAN SET IN SAME HOLE AFTR PULLING OLD POLE .POLE #1033-93 BROKE.PUT AS-BUILT DD LITE ON ORDER Released by crew 074S06/ NO OUTAGE TILLTRANSFORMER OPENED @ 1345 CLOSED 1352
25776 | Hazard | 3302703 | HAZARD | HAZARD | 2022-04-13 12:11 | 2022-04-13 12:32 | 1 | 21 | 4757331 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A bad 12KV arrestor on the C phase XFMR at pole 296-A3-158 had the XFMR fuse blown. I cut the arrestor in the clear and restored power at 12:32.
25777 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-09-14 11:19 | 2021-09-14 11:40 | 1 | 21 | 4239441 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Found xfmr cutout to be cracked while replacing light, opening to replace/// Opened @ 11:19 replaced cutout and restored @ 11:40
25778 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-09-21 22:39 | 2019-09-21 22:46 | 3 | 7 | 4045291 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on pole opened xfmr at 22:39 closed at 22:46/ ISO 37830257000007/ COD 3
25779 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-01-26 09:03 | 2012-01-26 09:24 | 1 | 21 | 4293801 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | BAD CONN, CUSTOMER STATED RISER WIRE WAS GLOWING. TIME OFF 0903 TIME ON 0924 TWO BAD CONNECTIONS, CLOSE TICKET VER/KEP IDC XXXX
25780 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2020-12-15 17:07 | 2020-12-15 17:14 | 3 | 7 | 4772311 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing broke c/o///opened @17:07 Closed@17:14///comlpete BR
25781 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-07-19 10:54 | 2019-07-19 11:15 | 1 | 21 | 4732771 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on trans. pole 45-105, no outage until I opened @1054, made repairs and closed back in @1115.
25782 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-11-14 14:34 | 2019-11-14 14:55 | 1 | 21 | 4034761 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OUTAGE NECESSARY TO REPAIR LOOP THAT IS OPEN OFF@ 1434 ON 1455
25783 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2010-02-14 15:39 | 2010-02-14 16:00 | 1 | 21 | 57611-1 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKEN. FUSED UP EVERYTHING OK. //VER/CRB IDC XXXX
25784 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-09-25 09:00 | 2014-09-25 09:21 | 1 | 21 | 4527601 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING BAD CUTOUT L3/IDC XXXX
25785 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-04-22 11:57 | 2020-04-22 12:18 | 1 | 21 | 4735391 | 21 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER FOUND BROKEN CUTOUT & IS CHANGING ¦¦ COD-1 ISO TF 38821133000063 OFF@ 1157 ON@ 1218
25786 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-11-13 03:51 | 2013-11-13 04:01 | 2 | 10 | 4034011 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPLACING BAD CROSSARM IN DIFFICULT LOCATION APPROX ONE HOUR OUTAGE/VEM/OPENED FUSES AT 0351/REPLACED ARM AND ALL CUST RESTORED@0401/PLEASE CLOSE TICKET/THANKS/VEM - 2 CUSTOMERS OUT PER VERNON/ // VER/TOM L3/TOM
25787 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-10-14 21:10 | 2016-10-14 21:30 | 1 | 20 | 4017681 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ARCING 38830138C00148. CREW REQD. NO TRK.COMP. XFMER 21:10 OFF, ON @ 21:30/ ISO 38830138C00148/ COD 1/ VER/BOW L3/HFP XXXHFP
25788 | South Williamson | 3411401 | DEWEY | INEZ | 2012-12-10 10:15 | 2012-12-10 10:35 | 1 | 20 | 4456391 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE//GOING TO REPLACE//REAIRS MADE RESTORED AT 1035//COMPLETE//EM COD-1 ISO TF 38830744A30138 VER/HFP L3/HFP
25789 | Whitesburg | 3312902 | JENKINS | JENKINS | 2022-03-11 09:15 | 2022-03-11 09:25 | 2 | 10 | 4599261 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp has burned off th line. will need to open all transformers on pole to make repairs. open @ 09:15 closed @ 09:25
25790 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-11-07 11:45 | 2011-11-07 12:05 | 1 | 20 | 4056561 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REMADE CONNECTIONS ON TRANSFORMER -- OPENED TRANSFORMER AT 1145 CLOSED AT 1205 COD-3 ISO TF 37830153B00121 VER/HFP L3/HFP IDC XXXX
25791 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-07-10 08:50 | 2008-07-10 09:10 | 1 | 20 | 50585-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CUTOUT RISER BROKE COD-1 VER/HFP IDC XXXX
25792 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-05-04 12:30 | 2009-05-04 12:50 | 1 | 20 | 50960-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3008701// HAD TO OPEN TRANSFORMER TO REMOVE INACTIVE SERVICE// POLE IS ROTTED BUT BRACED// APPROX 1 HOUR OUTAGE// OPENED @ 1230 BACK ON @ 1250 VER/TOM L3/TOM IDC XXXX
25793 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-07-13 11:00 | 2012-07-13 11:20 | 1 | 20 | 4709271 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED, CAUSING A POLE FIRE. I OPENED THE TRANSFORMER AT 1100 AND CLOSED BACK IN AT 1120 VER/KEP
25794 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-07-08 08:35 | 2008-07-08 08:45 | 2 | 10 | 64136-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001201//POLE 68-180 BAD CUTOUT AND LA//VER/CRB IDC XXXX
25795 | Paintsville | 3409302 | KENWOOD | AUXIER | 2009-02-16 21:00 | 2009-02-16 21:20 | 1 | 20 | 62756-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3409302// TREE ON OPEN WIRE SERVICE. WIRE WAS BURNT IN A FEW PLACES. REMOVED OPEN WIRE AND INSTALLED NEW #2 TWIST. OPENED TR AT POLE 881-34 2100 - 2120 20 MINUTE OUTAGE TR CC 1 VER/PDP
25796 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-08-23 14:00 | 2013-08-23 14:20 | 1 | 20 | 4699831 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL IN SERVICE DROP IS BROKEN. I AM GOING TO SPLICE DROP. RELEASED BY CREW 074S01// REPLACED SD// POWER IS RESTORED VER/SEF IDCC PN630, CNT3, TOF1013, CDC89, ESTIMATED TIME OFF FOR REPAIR XXXX
25797 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-03 13:55 | 2018-04-03 14:15 | 1 | 20 | 4168661 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no outage when i arrived///customer says power flickers all the time//voltage was good when i checked it/said they saw arcing around xfmr last night//i reworked connections at xfmr///opened xfmr at 13:55 and closed back at 14:15//complete//em
25798 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-01-22 17:35 | 2022-01-22 17:45 | 2 | 10 | 4396811 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | had bad servin froze out open transformer at 1735 and closed at 1745
25799 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-08-07 14:20 | 2011-08-07 14:30 | 2 | 10 | 4675591 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 2 INSULINK CONNECTIONS OVERHEATING & GOING BAD ON SECONDARY RISERS COMING OFF XFMR.WILL REPLACE..WILL HAVE TO DE-ENERGIZE XFMR..//.OPENED XFMR @ 14:20.REPLACED BAD CONNECTIONS.CLOSED XFMR @ 14:30..JRV..08/07/11//VER/CRB IDC XXXX
25800 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-01-11 10:20 | 2009-01-11 10:40 | 1 | 20 | 54206-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3417602//, ON SITE, CHECKING TROUBLE,CONNECTOR WHERE SERVICE MAKES UP TO SECONDARY WAS BAD VER/LDA L3/KEP IDCC TOF818 ESTIMATED TIME OFF XXXX
25801 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-11-01 13:25 | 2016-11-01 13:45 | 1 | 20 | 4068031 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED BAD SECONDARY CONNECTIONS AT THE TRANSFORMER. I OPENED THE TRANSFORMER AT 13:25, AND CLOSE AT 13:45. VER/AWD
25802 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-11-18 14:55 | 2019-11-18 15:05 | 2 | 10 | 4044991 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD 2//bad connection on xfmr pole 279-128, repaired. opened xfmr at 14:55, closed back in at 15:05
25803 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-10-01 13:10 | 2009-10-01 13:30 | 1 | 20 | 62321-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#32001720---BAD XF FEEDING AFLASHING LIGHT FOR SCHOOL ZONE---REPLACED XF, ON AT 1330--- VER/KEP L3/KEP IDC XXXX
25804 | Whitesburg | 3314401 | MAYKING | ERMINE | 2012-02-15 10:40 | 2012-02-15 11:00 | 1 | 20 | 4350011 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | REPLACING INSULATOR ///VER/CRB IDC XXXX
25805 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2022-11-11 14:40 | 2022-11-11 15:00 | 1 | 20 | 4127041 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RANDY CHAPMAN METER ELECTRCIAN REPORTS TOP OF SERVICE POLE SMOKING.cutout breaking down on pole 917B-353..replaced cut out.had it open from 14:40 to 15:00
25806 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-03-18 15:10 | 2011-03-18 15:30 | 1 | 20 | 55532-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED XFMR ON POLE 747-205 AT 15:10// CUTOUT GOING BAD//REPLACED CUTOUT //RESTORED AT 15:30//COMPLETE//EM//ISO//COD 1// VER/DBM IDC XXXX
25807 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2018-07-23 14:20 | 2018-07-23 14:40 | 1 | 20 | 4841991 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | while in area crew noticed bad cutout also on pole 68-D-161, will change while near by. Replaced the cutout on the transformer and the side tap. Opened at 14:20, and closed back in at 14:40.
25808 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-12-23 14:08 | 2009-12-23 14:28 | 1 | 20 | 60294-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | //EJC..RESTORED WITH LINE OUTAGE 60638 AT SWITCH 619-41//EJC..THIS CUSTOMER OUTAGED AT LINE SWITCH TO REPAIR DAMAGED CUTOUT 619-42//
25809 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2017-07-05 16:50 | 2017-07-05 17:00 | 2 | 10 | 4076401 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL PULLED APART IN SPLICE. OPENED XFM AT 16:50 COSED BACK IN AT 17:00. REPAIRS COMPLETE/ ISO 37830401C00335/ COD 2/ VER/BOW
25810 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-11-27 20:15 | 2008-11-27 20:35 | 1 | 20 | H52710-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP SERVICE WIRE BURNED DOWN AT CUST SERV POLE. HAD XFMR 38830783000148 OPEN FROM 20:15 TO 20:35 TO MAKE REPAIRS. REPAIRS COMPLETE. SH ON @ 2047//VER/CRB IDCC DUP FOR ORIGINAL CUSTOMER OUT XXXX
25811 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2014-02-12 11:40 | 2014-02-12 12:00 | 1 | 20 | 4375611 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STEVE OPENING RISER FUSES TO REPAIR RISER VER/SEF
25812 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-05-31 23:55 | 2018-06-01 00:05 | 2 | 10 | 4535311 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burned up, replaced and power restored. Power off at 23:55
25813 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-10-30 22:40 | 2022-10-30 23:00 | 1 | 20 | 4079451 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad xfm cutout @ 37830043000052.//Deenergized @ 22:40 to make repairs.//Restored @ 23:00
25814 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-11-04 16:55 | 2013-11-04 17:05 | 2 | 10 | H4008951 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN LINE CUTOUT ON POLE 211-33 NO TRUCKS TO POLE. NEED LINE CREW. RELEASED BY CREW 078S01,, OPENED XFMR AT 16:55, CLOSED AT 17:05,, CHANGED CUTOUT, ALL POWER RESTORED DUP IN HOIS FROM ORDER 4008951 FOR 2 ON TR @ 38830211000033 VER/HFP L3/HFP
25815 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-02-26 08:20 | 2008-02-26 08:40 | 1 | 20 | 50425-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000903/// CREW OPENING UP HOT TAP ON POLE 39831098D00694 TO ALLOW THEM TO SAFELY REPLACE DEFECTIVE CUTOUT ON POLE 39831098D00694// RELATED TO ORDER 50396-1 NO CUSTOMERS ON POLE 6011 PER POWERON VER/HFP IDC XXXX
25816 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-01-28 09:00 | 2019-01-28 09:20 | 1 | 20 | 4726951 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 service had burned down off pole 402-51, replaced service and restored power. opened xfm 402-50 at 9:00 closed at 9:20
25817 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-04-17 11:55 | 2014-04-17 12:05 | 2 | 10 | 4614201 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BLOWN OFF OF CSP XFMR , I AM GOING TO LIFT TAP AND CLEAR ARRESTOR. I OPENED XFMR AT 11:55 CLOSED AT 12:05 COD-2 ISO TF 37830356B00009 VER/HFP L3/HFP
25818 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-07-21 07:10 | 2022-07-21 07:30 | 1 | 20 | 4533611 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer had a broke neutral in service drop and had to open xformer up at pole 187-C-9 at a time of 7:10 to make repairs///// spliced neural out and got restored at a time of 7:30
25819 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-06 16:10 | 2018-04-06 16:30 | 1 | 20 | 4196871 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | customer flagged me down //xfmr cutout broke on pole 767-109//replaced cutout//restored at 16:30/ ISO 38830767B00109/ COD 1
25820 | South Williamson | 3411401 | DEWEY | INEZ | 2020-01-03 14:53 | 2020-01-03 15:03 | 2 | 10 | 4207981 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//OFF 1453 ON 1503
25821 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2021-10-08 03:07 | 2021-10-08 03:27 | 1 | 20 | 4329591 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing cutout, off from: 0307-0327
25822 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-11-02 21:35 | 2014-11-02 21:55 | 1 | 20 | 4694131 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON TOP OF XFMR CUTOUT WAS ARCING ON 809-329. OPENED XFMR @ 21:35, REPLACED CUTOUT - RISER - HOT-LINE CLAMP AND CLOSED XFMR @ 21:55. SH VER/ARN
25823 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2016-10-18 15:40 | 2016-10-18 16:00 | 1 | 20 | 4023761 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CONTACTED CUST//CAN WAIT TILL AM// POLE 237-53 IS LEANING REAL BAD & IS FLAGGED TO BE CHANGED .POLE NEEDS ATTENTION TODAY TO BE STRAIGHTEN OR REPLACED SEC POLE ,1 SER.DROP &DOWN GUY.NO OUTAGE CUST OK TR TO POLE IN FIELD OR BESIDE CARPORT RELEASED BY CREW 078S04/ 1540-1600/ ISO 38830237000014/ COD 1/ VER/BOW L3/HFP XXXHFP
25824 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2012-01-29 16:50 | 2012-01-29 17:10 | 1 | 20 | 4302631 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GOING TO OPEN LINE AT POLE 38830254B00478 AND RESAG 2 SPANS PRIMARY AND NEUTRAL THAT ARE TOO CLOSE, CREW IN ROUTE FOR ASSISTANCE. MAY NEED TO LOWER NEUTRAL ON 3 POLES FOR CLEARANCE. REPAIRS MADE, OPENED AT 16:50, CLOSED AT 17:10//COD 1//ISO// VER/DBM IDC XXXX
25825 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-07-24 00:15 | 2015-07-24 00:35 | 1 | 20 | 4936761 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ARCHING WILL CHG. CHANGED 7200 COUTOUT & ARRESTOR ON POLE # 37830067C00304 PULLED OFF @ 12:15 ON@ 12:35//COD 1// VER/DBM
25826 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-10-19 14:40 | 2015-10-19 15:00 | 1 | 20 | 4361341 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE CUTOUT PLEASE CLOSE TICKET THANKS.BT/MADE MD FOR TRANSFORMER// VER/ ADH
25827 | South Williamson | 3411401 | DEWEY | INEZ | 2021-02-01 10:55 | 2021-02-01 11:15 | 1 | 20 | 4925771 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 743-213//replaced cutout//restored at 11:15//complete//em
25828 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2012-01-25 20:35 | 2012-01-25 20:45 | 2 | 10 | 4293221 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN SERVICE FAILED AND BURNT NEUTRAL INTO.WILL HAVE TO HAVE SHORT OUTAGE ON XFMR TO REPLACE SERVICE.HAD XFMR OPEN FROM 20:35 TO 20:45.CUSTOMER WAS NOT HERE TO CHECK FOR DAMAGES BUT VOLTAGE IS GOOD AT METERBASE // COD-2 ISO TF 37820197000007 VER/HFP L3/HFP IDC XXXX
25829 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-03-09 15:25 | 2010-03-09 15:35 | 2 | 10 | 64351-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED TRANSFORMER TO ALLOW THEM TO REPLACE DEFECTIVE CUTOUT. COD-2 VER/HFP L3/HFP IDC XXXX
25830 | Pikeville | 3421001 | BREAKS | CITY | 2008-01-15 01:00 | 2008-01-15 01:20 | 1 | 20 | 56775-1 | 20 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400901SERVICE DROP NEUTRAL WAS BURNED APART. INSULATION ON #2 SERVICE WAS DETERIOATED AND THE CONDUCTOR WAS BARE IN SEVERAL PLACES. I RFEPLACED THE SERVICE DROP WITH A NEW #2 DROP. CUSTOMER IS COMPLAINING OF DAMAGED APPLIANCES.//VER/CRB IDC BRIGHT DIM CALL INITIALLY CHANGED START TIME FROM 2320 XXXX
25831 | Hazard | 3302703 | HAZARD | HAZARD | 2013-11-06 17:40 | 2013-11-06 18:00 | 1 | 20 | 4016161 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 37830296A30704 ROTTED OFF AT GROUND, CREW ENROUTE.---- 1 CUST. OUT FROM 17:40 TIL 18:00, POWER RESTORED. VER/CRB
25832 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-06-02 12:35 | 2017-06-02 12:45 | 2 | 10 | 4898061 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND A BAD CONNECTION ON POLE 449-599. OPENED X-FMR BANK UP AT 12:35 AND REPLACED BAD SQUEEZE ON. RESTORED POWER AT 12:45. 37830449C40599 VER/AWD
25833 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-05-13 13:30 | 2012-05-13 13:40 | 2 | 10 | 4785761 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER ETA 1315 // POLE 1147-556 BAD CUTOUT OPENED TRANS 13;30 ON13;40 SEND NOTE TO TEC. POLE BURNT 1/4 INTO POLE POLE NEEDS CHGED//COD 2//EMAILED TO S MARTIN// VER/DBM IDC XXXX
25834 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-03-17 16:08 | 2009-03-17 16:28 | 1 | 20 | H59475-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP BAD PLACE IN SERVICE, OPEN TRANSFORMER AT 1608 AND CLOSED AT 1628 COD-2 THIS IS FOR THE TRANSFORMER OUTAGE FOR THE 1 ADDITIONAL CUSTOMER L3/HFP IDCC CDC89 XXXX
25835 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-05-11 11:00 | 2011-05-11 11:20 | 1 | 20 | 4033861 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SERVICE NEUTRAL. DC ESTIMATED TIME OFF OF 11:00 ON 5/11 IDC XXXX
25836 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-12-15 09:35 | 2022-12-15 09:55 | 1 | 20 | 4262341 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout on pole 171-208 . opened line fuse on pole 171-207 @ 09:35 to make repairs .. restored power @ 09:55
25837 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-12-03 13:20 | 2010-12-03 13:30 | 2 | 10 | H62709-1 | 20 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PART OF 62709-1//XFMER OFF 13:20 ON 13:30 ADD A PHASE INSTALLED VOLTAGE GOOD 123/247 RESTORED @ 13:35 J. HEMLEPP/ SEND INFO ON BAD UNDG LOCATION TO L. RAYBURN.//COD 2//EMAILED TO L RAYBURN// VER/DBM IDCC TON1335 XXXX
25838 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2013-03-15 14:30 | 2013-03-15 14:50 | 1 | 20 | 4908401 | 20 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER BANK AT 1430 CLOSED AT 1450 ///VER/CRB L/3 CRB IDC XXXX
25839 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-04-21 16:45 | 2021-04-21 17:05 | 1 | 20 | 4468521 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened line fuse at 38830117B00028 to replace cutout at 38830117B00357 Off at xxxx On at xxxxcrew on site opening up lf on 117-28 to climb pole and change cutout FETR 17:30 LRMcrew on site opening up lf on 117-28 to climb pole and change cutout FETR 17:30 LRM opened line at 16:45 in at 17:05 please clsoe ticket LRM
25840 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-10-14 16:15 | 2011-10-14 16:35 | 1 | 20 | 4981201 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DEFECTIVE CUT-OUT CAUSING POLE FIRE. CREW ON SITE. OPENED X-FMR AT 16:15, CLOSED AT 16:35. ONLY ONE CUSTOMER OUTAGED.//COD 1// VER/DBM IDCC TOF1452 XXXX
25841 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-03-13 16:35 | 2008-03-13 16:55 | 1 | 20 | 56980-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT DOOR BURNT UP//3008701//VER/CRB IDC XXXX
25842 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-06-23 15:10 | 2015-06-23 15:30 | 1 | 20 | H4644931 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT 37830328D00187/ ISO 37830328D00187/ COD 2/ BAD 19.9 CUTOUT POWER RESTORED OPEN LINE FUSE AT 15:10 CLOSED AT 15:30 L3/DKG THISOUTAGE FOR OPENING LINE FUSE ..SEE 4644931 FOR ORIGINAL OUTAGE
25843 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-10-25 10:55 | 2022-10-25 11:15 | 1 | 20 | 4062951 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Have Neutral almost into on service drop going to open Trans to make repairs..Open 10:55 Closed at 11:15..
25844 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-10-07 17:40 | 2009-10-07 18:00 | 1 | 20 | 61366-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD PLACE IN SERV WIRE VER/KEP L3/KEP IDCC TOF1709 XXXX
25845 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2009-08-08 11:00 | 2009-08-08 11:10 | 2 | 10 | 62627-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400702// OPENED TRANSFORMER @11:00 TO REPAIR BAD SERVICE // COD 2 // CLOSED BACK @ 11:10 // VER/DBM IDC XXXX
25846 | Hazard | 3311103 | STINNETT | WENDOVER | 2015-10-22 08:30 | 2015-10-22 08:50 | 1 | 20 | 4368041 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEC LEAD BURNT OFF WILL NEED BIG BUCKET TO MAKE REPAIRS//NO OUTAGE @ THIS TIME TILL TRANS OPENEDSEC LEAD BURNT OFF WILL NEED BIG BUCKET TO MAKE REPAIRS OPENED @0830 AND CLOSED @0850 VER/CRB
25847 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-07-17 12:00 | 2013-07-17 12:20 | 1 | 20 | 4536571 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD BAD CONNECTION AT MAST PIPE, HAVE PROBLEM FIX AND EVERYTHING IS FINE AT THIS LOC, OPEN UP TRANSFORMER AT 1200, AND CLOSED BACK IN AT 1220, JUST HAD ONE CUST OUT VER/SEF IDC XXXX
25848 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-06-23 22:45 | 2014-06-23 23:05 | 1 | 20 | 4144721 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD 4/3 SERVICE CHGED TO 2/3// ESTIMATED TIME OFF TO MAKE REPAIRS/// VER/BOW
25849 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-03-14 11:30 | 2016-03-14 11:50 | 1 | 20 | 4842381 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | REPAIRED LOSSE LUGS POWER OFF@ 1130 ANF ON @ 1150// VER/ ADH
25850 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-09-17 16:15 | 2020-09-17 16:25 | 2 | 10 | 4472771 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Outage to install new guy wire (2 CC) Off at 1615 On at 1625
25851 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-03-27 13:01 | 2014-03-27 13:21 | 1 | 20 | 4528581 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | POLE # 37830224D21202 OPENED TRANSFORMER AT 13:01, RESAGED GUY CLOSED AT 13:21 VER/SEF
25852 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-03-23 15:13 | 2011-03-23 15:23 | 2 | 10 | 57138-1 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//ISO//COD 2//MD FILED ON MISSING FUSE// VER/DBM IDC XXXX
25853 | Hazard | 3310502 | HADDIX | CANOE | 2022-09-05 13:45 | 2022-09-05 14:05 | 1 | 20 | 4836651 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had a chipped and cracked cutout.got cutout replaced.//no outage till fuse opened at 1345 on 09-05
25854 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-04-06 14:02 | 2019-04-06 14:22 | 1 | 20 | 4063961 | 20 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failing on pole 37830029000175 Opened to repalace /// COD 1 // OFF @ 14:02 ON @14:22..broken cutout, AS BUILT COMPLETED..P.HICKS L3/HFP
25855 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-04-27 23:07 | 2008-04-27 23:26 | 1 | 19 | 54720-1 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | 3008701// 2320 TALKED WITH DUTY SUPV WHO ADVISED TO CHECK WITH CUSTOMERS TO SEE IF OKAY TO WORK IN MORNING. HE REPORTED WILL GET FIRST THING IN MORNING. ADVISED CUSTOMER TO TURN OFF ALL EQUIPMENT UNTIL REPAIRS CAN BE MADE./LDA IO ORDER #035094537 VER/LDA IDC XXXX
25856 | Pikeville | 3421001 | BREAKS | CITY | 2014-10-15 01:25 | 2014-10-15 01:44 | 1 | 19 | H4629771 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE ON POLE #243-B-131 WILL CHANGE/// LIFTED HOT TAP ON POLE 243-B-19 @ 1:25 MADE REPAIRS AND PUT HOT TAP BACK ON @ 01:44 AND RESTORED SERVICE VER/CRB L3/HFP
25857 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-07-06 11:51 | 2016-07-06 12:10 | 1 | 19 | 4546711 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BROKE CUTOUT, BACK IN SERVICE,
25858 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2009-10-19 20:02 | 2009-10-19 20:21 | 1 | 19 | 59101-1 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2150502//ASSOC. WITH 58860//OPENING RCLSR 941C277 @ 2002 TO MAKE REPAIRS TO FAILED C/O ON POLE 941C16//CC82////VER/WHV// IDC 82 CUSTOMERS ON WV SIDE SIDE XXXX
25859 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-03-06 07:29 | 2014-03-06 07:48 | 1 | 19 | 4455461 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SMALL IN-LINE ARRESTOR BURNED INTO,WILL MAKE REPAIRS/////////MADE NECESSARY REPAIRS AND RESTORED,ALL OK AFTERWARDS ACTUALLY CURRENT LIMITING FUSE IDC XXXX
25860 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-08-24 13:11 | 2022-08-24 13:30 | 1 | 19 | 4789721 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew on site to change xfmr. vacant house LRM fetr 14:00 LRM complete 13:30 bad current limiting fuse
25861 | Hazard | 3303902 | LESLIE | WOOTON | 2020-11-07 09:55 | 2020-11-07 10:14 | 1 | 19 | 4650431 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT//OFF 0955 ON @ 1014
25862 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-02-16 11:00 | 2022-02-16 11:19 | 1 | 19 | 4486491 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced cutout. Opened xfrm up at 11:00 closed back in at 11:19. Power restored.
25863 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-07-05 17:14 | 2016-07-05 17:33 | 1 | 19 | 4542001 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE ON XFMR 477-10---CHANGED---PWR RESTORED AT 17:33
25864 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2012-05-24 09:36 | 2012-05-24 09:55 | 1 | 19 | 4826701 | 19 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T FUSE BROKE. FUSED UP EVERYTHING OK. VER/KEP IDC XXXX
25865 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2021-10-08 02:41 | 2021-10-08 02:59 | 1 | 18 | 4329581 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing cutout off from: 0241-0259
25866 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-02-04 15:42 | 2008-02-04 16:00 | 1 | 18 | 66270-1 | 18 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKE OFF VER/HFP IDC XXXX
25867 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2017-01-05 21:46 | 2017-01-05 22:04 | 1 | 18 | H4272411 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | **SEE 4272411*** PART POWER,OPENED XFMR AT 21:46 (1 ADD CUST) REPAIRED SPLICE RESTORED POWER AT 22:04 (2 CUST REST)../ ISO 37830449C20150 / COD 2/ VER/BOW L3/HFP XXXHFP
25868 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-01-02 14:12 | 2019-01-02 14:21 | 2 | 9 | 4623321 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | open line at 1412 closed at 1421
25869 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-04-22 11:12 | 2017-04-22 11:21 | 2 | 9 | H4667031 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE SECTIONALIZER CUT-OUT HAS FAILED @ POLE 99-14, WILL BE PATROLLING TO MAKE SURE NO OTHER PROBLEMS. FOUND NO OTHER TROUBLE, HAD TO OPEN TRANS. ON POLE 99-14 TO CHANGE SEC., OPENED @1112, CLOSED @1121, AND PUT SEC. BACK IN @1130. OPENED TFO ON 4667611. VER/AWD L3/HFP HFPC DUP
25870 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-11-30 11:35 | 2016-11-30 11:53 | 1 | 18 | 4149031 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED TAP ON 302-48 FROM 1135-1153.REPACED TRANSFORMER 077H04/ ISO 37830302A00048/ COD 1/ VER/BOW L3/HFP HFPC TOF1026 TON1158
25871 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-02-02 18:34 | 2008-02-02 18:43 | 2 | 9 | 65570-1 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310501// NEUTRAL WIRE SPLIT - WILL OPEN TRANSFORMER TO MAKE REPAIRS// COD 2 FLT/ISO - 37830055000089// REPAIRED BAD PLACE IN NEUTRAL COND OPENED XFMR AT 1834 CLOSED AT 1843// VER/TOM IDC XXXX
25872 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-06-12 11:05 | 2019-06-12 11:23 | 1 | 18 | 4487521 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | only one cust out. hot legs were melting, insulinks going bad on each leg. cut out & replaced w regular squeezes, reworked loops off of awning also. pls close. tre
25873 | Hazard | 3303902 | LESLIE | WOOTON | 2016-04-28 19:54 | 2016-04-28 20:12 | 1 | 18 | 4139961 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4139791*** BAD TRANSFORMER CUTOUT ON POLE 37830462000109/ HAD TO OPEN LINE FUSE TO CHANGE/ ISO 37830462000109/ COD 1/ LINE FUSE AT 19:54 AND CLOSE AT 20:12/ VER/BOW
25874 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2017-08-02 12:55 | 2017-08-02 13:13 | 1 | 18 | H4216471 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE 4216471*** POLE 20 C4 5667 BAD 12KV C/O (2 CUST PRT OUT). CHANGE OTHER 2 W/ OUTAGE. 100T LF ON 20-350 WILL OUTAGE TAP. RELEASED BY CREW 078S07/CREW ON SITE/FETR 1345/VEM/OPENED FUSE 38830020C30350 AT 1255 (1 ADDITI CUST)/REPAIRS MADE AND ALL CUST RESTORED 1313/PLEASE CLOSE TICKET/THANKS/VEM/ VER/BOW
25875 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2016-04-04 10:12 | 2016-04-04 10:30 | 1 | 18 | 4048331 | 18 | PARTIAL POWER | EQUIPMENT FAILURE | NONE | HAD A PHASE FUSE OUT ON TRANFORMER BANK HAVE REFUSED AND ALL POWER IS RESTORED AT THIS LOC AT 1030 VER/AWD
25876 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2017-05-21 23:02 | 2017-05-21 23:20 | 1 | 18 | 4836341 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER ONLY HAVING PROBLEMS IN KITCHEN/ STOVE DOESNT WORK SOMETIMES/ SAID NEIGHBOR HAS TV AND OUTLETS THAT DONT WORK/ ADVISED CUSTOMER NORMALLY PART OUTS ON AEP SIDE MAJOR 220 OUTLETS DONT WORK AND NORMALLY ITS NOT JUST ONE ROOM IN HOUSE/ CUSTOMER SAID POWER CAME BACK ON WHILE ON PHONE BUT DIDNT WANT HER HOUSE TO BURN DOWN WHILE IN BED/ REPAIRED CONN. ALL PWR RESTORED @ 23:20 VER/ARN
25877 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-01-21 22:30 | 2010-01-21 22:48 | 1 | 18 | 57519-1 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL INVESTIGATE COMPLAINT///////FOUND SOME CONNECTIONS AT XFR THAT WERE HEATING UP,EVEN MELTED THE INSULATION.RE-WORKED THESE AND ALL APPEARED OK PER CUST VER/HFP L3/HFP IDCC TOF2152 ESTIMATED TIME OFF XXXX
25878 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-11-23 07:02 | 2021-11-23 07:20 | 1 | 18 | 4117761 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
25879 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-09-11 23:01 | 2008-09-11 23:19 | 1 | 18 | 61678-1 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002107//CALLING CREW-BAD CUTOUT-SEND TO V MULLINS //OPENED CUTOUT 2301/BACK IN AT2319/PLEASE CLOSE TICKET/VEM// ISO// VER/DBM IDCC TOF1938, TON XXXX
25880 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-05-19 13:18 | 2020-05-19 13:24 | 3 | 6 | 4855431 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad 19.9 cutout. time off 1318 time on 1324 apr close ticket
25881 | South Williamson | 3411401 | DEWEY | INEZ | 2015-09-12 10:45 | 2015-09-12 11:03 | 1 | 18 | 4231061 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER MAKING SIZZLING NOISE/185 KENNY HARLESS DRIVE INEZ, 38830767C00119/ TRANSFORMER MAKING SIZZLING NOISE/185 KENNY HARLESS DRIVE INEZ, 38830767C00119/ TRANSFORMER CUTOUT ARCING. OPENED AT 10:45, REPLACED CUTOUT AND CLOSED AT 11:03. SH// VER/ ADH
25882 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-10-18 20:15 | 2015-10-18 20:33 | 1 | 18 | 4359181 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | THE CURRENT LIMITING FUSE WAS DEFECTIVE AND CAUSING INTERMITTENT VOLTAGE FLUCTUATIONS. I OPENED THE TRANSFORMER AT 2015 AND CLOSED AT 2033. VER/CRB
25883 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-04-22 11:12 | 2017-04-22 11:21 | 2 | 9 | 4667611 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | OPENED 1112-1121 TO SAFELY REPLACE SECTIONALIZER ON ORDER 4667031. VER/AWD L3/HFP HFPC FP
25884 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-02-10 10:22 | 2022-02-10 10:40 | 1 | 18 | 4464431 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Made per Ken Little. Found a bad cutout replacing// changed XCO took XFM off @ 10:22 on @ 10:40
25885 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-09-26 16:34 | 2008-09-26 16:40 | 3 | 6 | 51029-1 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP SERVICER ON SITE REPLACING BAD CUTOUT THIS ORDER CONTAINS THE OUTAGE FOR ORDER 51010-1 WHEN THE TRANSFORMER BANK WAS OPENED. COD-4 3 FOR THIS ORDER 1 FOR ORDER 51010-1 IDCC CNT4 XXXX
25886 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-02-28 16:15 | 2011-02-28 16:33 | 1 | 18 | 64859-1 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN DOWN. I AM GOING TO CHANGE CUTOUT. I CHANGED 19.9 CUTOUT. VER/HFP L3/HFP IDCC TOF1541, ESTIMATED TIME OFF XXXX
25887 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-01-17 11:30 | 2015-01-17 11:48 | 1 | 18 | 4940941 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOING TO REPLACE CUTOUT//GOING TO REPLACE CUTOUT, OPENED XFMR AT 11;30, CLOSED BACK AT 11;48, CUTOUT REPLACED 37830279000158 VER/CRB L3/HFP HFPC TON1208
25888 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-04-14 12:08 | 2015-04-14 12:17 | 2 | 9 | 4316181 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 37820010D00032, I WILL TRY TO REPLACE IT. NO OUTAGE TILL I OPEN THE TRANSFORMER FUSE. I OPENED THE TRANSFORMER AT 12:08, AND CLOSED AT 12:17/COD 2// VER/ ADH
25889 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-08-01 13:35 | 2014-08-01 13:53 | 1 | 18 | 4316131 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER CONNECTION IS ARCING ON BANK OF 167 KVA XFMRS. NEED BIG BUCKET, (2) 500 MCM TWO-HOLE PADS AND A PRESS TO INSTALL PADS. MAY BE ABLE TO CLEAN UP EXISTING PADS. CALL ROY @ 454-9413 TO DROP LOAD AT PLANT. CREW ENROUTE TO MAKE REPAIRS. OPENED XFMR BANK @ 13:35. REPAIRED AND CLOSED @ 14:00. SH RELEASED BY CREW 076S02//NO OUTAGE TIL TRANS OPENED. VER/CRB
25890 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-03-01 13:12 | 2010-03-01 13:30 | 1 | 18 | 61937-1 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND ROTTEN TRANSFORMER FUSE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC// VER/DBM IDC XXXX
25891 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-12-02 14:00 | 2015-12-02 14:18 | 1 | 18 | 4504301 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE ON FIRE, WILL NEED TO OPEN XFMR TO REPAIR. OPENED XFMR AT 14:00, CLOSED BACK IN AT 14:18, REMOVED FUSE, POWER RESTORED//NO OUTAGE TILL TRANS OPENED. VER/CRB
25892 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-05-22 11:07 | 2020-05-22 11:25 | 1 | 18 | 4886401 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing broken cutout, trouble work order, time off was 11:07 , time on was 11:25,,,blr
25893 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-06-20 11:40 | 2018-06-20 11:49 | 2 | 9 | 4627021 | 18 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | neut broke in service drop. work complete pls close. tre
25894 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-08-15 04:15 | 2010-08-15 04:32 | 1 | 17 | H55473-1 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE AND LAYING ON BRACKET..NEED TO OPEN LINE FUSE ON POLE 210-44 LONG ENOUGH TO MAKE REPAIRS.. OPENED FUSE ON POLE 210-44 AT 4:15 CLOSED BACK IN AFTER RELACING CUTOUT AT 4:32.. VER/KEP L3/KEP
25895 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-01-25 15:43 | 2014-01-25 16:00 | 1 | 17 | 4312501 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT DOOR // 1543 OPENED CUTOUT TO REPLACE CUTOUT BARREL // COD-1 ISO TF 38830207A00228 VER/HFP L3/HFP
25896 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-12-19 12:18 | 2019-12-19 12:35 | 1 | 17 | 4170211 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Customers cutout is busted, still has full power, will have to open trans. to make repairs, will keep track of times. Opened trans. @26-B2-263 @1218, changed c/o and closed @1235.
25897 | South Williamson | 3202201 | LOVELY | LOVELY | 2021-11-03 11:28 | 2021-11-03 11:45 | 1 | 17 | 4053121 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MAKING REPAIRS TO CUSTOMER SERVICE NEUTRAL//repaired service neutral restored at 11:45
25898 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-07-02 12:40 | 2015-07-02 12:57 | 1 | 17 | 4708801 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE H4708801*** BAD CUTOUT ON POLE 204-157/ OPENED LINE FUSE 37830204000067 @ 1245 TO ISOLATE POLE 37830204000157/ CLOSED LINE FUSE @ 1247/ CLOSSED TRANSFORMER @ 1257/ ISO 37830204000067/ COD 4/ VER/BOW
25899 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2014-08-18 17:43 | 2014-08-18 18:00 | 1 | 17 | 4381141 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT WEATHERHEAD. VER/CRB
25900 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-02-09 15:15 | 2010-02-09 15:32 | 1 | 17 | 54399-1 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S01 BAD CONNECTIONS ON POLE//VER/CRB IDC TOF1318 FLICKERING LIGHTS CALL ALLOWED 15 MIN FOR REPAIR XXXX
25901 | South Williamson | 3411401 | DEWEY | INEZ | 2018-03-29 15:20 | 2018-03-29 15:37 | 1 | 17 | 4147731 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on 744-B-532//opened line fuse on pole 743-25//only 1 customer out//opened at 15:20///restored at 15:37//complete//em//NO OUTAGE TILL L/F OPENED
25902 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-04-01 16:15 | 2020-04-01 16:32 | 1 | 17 | 4552961 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308502/gaj/1615-1632 Outage to replace Cutout
25903 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-01-17 18:48 | 2010-01-17 19:05 | 1 | 17 | 55552-1 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT TRACKING.. CHG CUTOUT...NOONE WAS OUT UNTIL I PULLED TRANSFORMER CUTOUT...POLE# 876-126...CHG CUTOUT..BB VER/TOM IDCC TOF1548 XXXX
25904 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-04-28 09:43 | 2017-04-28 10:00 | 1 | 17 | 4690731 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY LEAD BURNT INTO ON POLE 1034-260, OPENED X-FMR AT PL#1034-259 TO MAKE REPAIRS/// OFF AT 09:43 ON AT 10:00 RICK RAY COD-1 ISO TF 38821034B20259/ VER/BOW L3/HFP HFPC FP38821034B20259
25905 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-12-01 13:30 | 2009-12-01 13:47 | 1 | 17 | 53761-1 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON CUST WEATHERHEAD, NEUTRAL CONNECTER BAD ON POLE, CALLING FOR BIG BUCKET TO REPLACE CONNECTIONS. COMPLTED IDCC TOF1258, ALLOWED 15 MIN FOR REPAIR XXXX
25906 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-04-27 12:04 | 2017-04-27 12:21 | 1 | 17 | 4686851 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT OPEN AT 1204 AND CLOSED AT 1221 37830079000004 VER/AWD L3/HFP XXXHFP
25907 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2021-10-13 09:43 | 2021-10-13 10:00 | 1 | 17 | 4345941 | 17 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse melted out @23-56, this needs to be changed on the map it shows no customers off this pole, got trans. restored @1000. 15kva map Disc needed. MDR complete
25908 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-01-30 12:45 | 2013-01-30 13:01 | 1 | 16 | 4755521 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830335D00221 BAD CUTOUT NO OUTAGE AT THIS TIME NEED CREW THE LATERAL WILL NEED TO BE DE-ENERGIZED TO WORK. CREW ENROUTE. RELEASED BY CREW 074S02 COD-1 ISO TF 37830335D00221 VER/HFP L3/HFP IDCC TOF0940, ESTIMATED TIME OFF, DONT KNOW IF TRANS OR LINE FUSE WAS OPEN LEFT AS TRANS FUSE XXXX
25909 | Hazard | 3303902 | LESLIE | WOOTON | 2020-06-04 11:48 | 2020-06-04 12:04 | 1 | 16 | 4953481 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken neutral in service drop opened xfmr at 11:48 closed at 12:04, service drop is about 8 feet above deck
25910 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-07-15 18:23 | 2009-07-15 18:39 | 1 | 16 | 62606-1 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS OPEN TRANSFORMER 1823 AND CLOSED AT 1839//COD 1// VER/DBM IDC XXXX
25911 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-11-24 14:24 | 2015-11-24 14:40 | 1 | 16 | 4483331 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEND XFM AT 14:24 CLOSED BACK IN AT 14:40..CONNECTIONS AT WEATHER HEAD WAS HEATING UP CAUSING INSULATION TO MELT.. VER/CRB
25912 | South Williamson | 3200302 | BELFRY | TOLER | 2014-09-25 09:26 | 2014-09-25 09:42 | 1 | 16 | 4527611 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THE PRMARY BUSHING LUG BROKE. REPLACED THE LUG AND POWER IS BACK ON. ONLY ONE CUSTOMER WAS OUT. RESTORED AT 09:42 CAN CLOSE TICKET//BMC VER/DKG L3/DKG
25913 | Hazard | 3309302 | VICCO | JEFF | 2018-03-23 09:14 | 2018-03-23 09:22 | 2 | 8 | 4044431 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | open transformer at 0914 and closed at 0922. complted
25914 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-07-02 13:45 | 2015-07-02 13:53 | 2 | 8 | 4709531 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFR CUTOUT. OPENED CUTOUT @13:45 CHANGED BAD CUTOUT CLOSED BACK IN @13:53 COMPLETE/ ISO 38830159000040/ COD 2/ VER/BOW
25915 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-08-24 11:30 | 2010-08-24 11:38 | 2 | 8 | 59880-1 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A FAILED CUTOUT ON THIS POLE IT WAS A CHROME TOP CUTOUT. I OPENED THE TRANSFORMER BANK AT 1130 AND CLOSED BACK AT 1138.//VER/CRB IDC XXXX
25916 | Hazard | 3301401 | COMBS | COMBS | 2018-03-02 14:04 | 2018-03-02 14:12 | 2 | 8 | 4935881 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer fuse broke COD - 2 ISO TF 37830271A00347
25917 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2009-03-14 22:25 | 2009-03-14 22:41 | 1 | 16 | 58637-1 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200204 //ON SITE, BAD CUTOUT, CHANGING IT OUT, OFF AT 2225, BACK ON AT2241 VER/LDA IDC XXXX
25918 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-09-03 12:51 | 2019-09-03 13:07 | 1 | 16 | 4974311 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | got splice pull out on service netural, got birian clemons coming to help me , got to climb pole let wire down and resag service open transformer at 1251 and closed at 1307
25919 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2018-03-16 11:47 | 2018-03-16 12:03 | 1 | 16 | 4019181 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 45-c2-4583 bad 12kv c/o. need c/o & arrestor. trk ok. 615 17th street Released by crew 078S07/crew on site/no outage at this time/will open xfmr for repairs/spoke with cust/aprox 30min outage/vem/open xfmr 1147/repairs made and all cust restored 1203/please close ticket/thanks/vem COD-1 ISO TF 38830045C24583
25920 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-11-23 10:44 | 2021-11-23 11:00 | 1 | 16 | 4118541 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout. Power restored at 11:00.
25921 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-07-10 08:47 | 2017-07-10 09:03 | 1 | 16 | 4100771 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENED XMF AT 0847 MADE REPAIRES TO BROKEN RISER, CLOSED AT 0903 APR CLOSE TICKET38830284000100 VER/AWD SJGC TOF 08:47 7-1-17
25922 | Pikeville | 3421001 | BREAKS | CITY | 2008-11-10 13:41 | 2008-11-10 13:49 | 2 | 8 | 63663-1 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400901/CREW OPENED RECLOSERS SO JOHNY SHEPHERD COULD SAFELY MAKE REPAIRS ON ORDER 63585-1 COD-2 VER/KEP IDC XXXX
25923 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-07-28 20:00 | 2016-07-28 20:16 | 1 | 16 | 4702881 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT. OPENED XFMR 761-218 @ 20:00, REPLACED CUTOUT AND RESTORED @ 20:16. SH VER/CRB
25924 | Hazard | 3309302 | VICCO | JEFF | 2015-06-25 13:50 | 2015-06-25 14:06 | 1 | 16 | H4655261 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TREE FELL HITTING LINE == NO DAMAGE === REFUSED LINE POWER ==== TOOK TRANS OFF AT 13:50 ON POLE 216 TO REPAIR SERV NEUT === ALL ON AT 14:00// AED 419-216/FIX IT IN HOIS/AED MADE/ADH// VER/ ADH
25925 | Hazard | 3310502 | HADDIX | CANOE | 2022-06-10 19:42 | 2022-06-10 19:50 | 2 | 8 | 4055661 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Repaired broke neutral in service drop. Opened transformer @ 19:42 Closed @ 19:50
25926 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2008-03-26 14:09 | 2008-03-26 14:25 | 1 | 16 | 60888-1 | 16 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE VER/HFP IDC XXXX
25927 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2009-06-17 16:04 | 2009-06-17 16:20 | 1 | 16 | 62823-1 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT ON POLE 220(LINE FUSE). OPENED LINE FUSE ON POLE 117-220 AT 16:04 TO REPLACE. REPLACED CUTOUT AND CLOSED LINE FUSE AT 16:20. SH COD-1 ISO 37830117000220 L3/HFP
25928 | Hazard | 3310502 | HADDIX | CANOE | 2016-02-29 15:06 | 2016-02-29 15:22 | 1 | 16 | 4788341 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT OPEN TRANSFORMER AT 1506 AND CLOSED AT 1522/ ISO 37830050000043/ COD 1/ VER/BOW
25929 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-07-01 22:00 | 2015-07-01 22:16 | 1 | 16 | 4707061 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUTON P0LE 38820819D10081OPENED TRANS UP AT 22:00 CLOSED IN AT 22:16// VER/ ADH
25930 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2009-10-15 17:15 | 2009-10-15 17:23 | 2 | 8 | 66602-1 | 16 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//, ON SITE, CHECKING TROUBLE, BAD CUTOUT, POWER OFF AT1715 TO CHANGE CUTOUT, BACK ON AT 1723 IDCC TOF1602 XXXX
25931 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-03-13 12:20 | 2008-03-13 12:35 | 1 | 15 | 56828-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3002001// BAD SERVE END ON MAST PIPE, RESQUEEZED EVERYTHING, ALL IS OK NOW AT THIS LOCATION// VER/DBM IDCC TOF1104 ALLOWED 15 MI FOR REPAIR XXXX
25932 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-06-24 11:45 | 2020-06-24 12:00 | 1 | 15 | 4069221 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Opened Tr to tie in floating phase at 38830655B00271 (1 CC) FETR 1200opened @11:45 closed @12:00 replased tie wire.
25933 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-02-12 11:10 | 2011-02-12 11:25 | 1 | 15 | 56372-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN//////SPLICED AND RESAGED NEUTRAL, POWER OK VER/KEP IDCC TOF1015, BRIGHT DIM CALL ESTIMATED TIME OFF FOR REPAIR XXXX
25934 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-03-09 16:35 | 2008-03-09 16:50 | 1 | 15 | 55713-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3007903//SERVICE DROP BRUNT INTO I REPLACED WHOLE SPAN,,,// VER/DBM IDC XXXX
25935 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-05-16 15:45 | 2011-05-16 16:00 | 1 | 15 | 4101671 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT //SERVICER REPLACED//OPENED TRANSFORMER @ 1545//CLOSED 1600 //COD 1// VER/DBM
25936 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-11-12 12:15 | 2012-11-12 12:30 | 1 | 15 | 4386021 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BAD CUTOUT ON POLE 620-231.. OPENED XFMR AT 12:15 BACK ON AT 12:30.. COMPLETE//COD1// VER/DBM IDC XXXX
25937 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-23 17:15 | 2012-08-23 17:30 | 1 | 15 | 4966201 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMER BANK ///VER/CRB L/3 CRB IDCC TOF1533 FULL POWER CALL ESTIMATED TIME OFF FOR REPAIR XXXX
25938 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-12-28 10:00 | 2017-12-28 10:15 | 1 | 15 | 4684831 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened @ 10:00 closed @ 10:15
25939 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-10-06 21:15 | 2015-10-06 21:30 | 1 | 15 | H4323141 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREE FELL TORE OPEN WIRE SECONDARY/ WILL HAVE TO OPEN TRANSFORMER 900-90/ CREW ENROUTE TO HELP/NOW OPENING TAP ON 900-90 BROKEN CUTOUT/OEPNED TRANSFORMER 1945 OPENED TAP 2115 RESTORED ALL 2130// VER/ ADH L3/HFP XXXHFP
25940 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2019-10-24 18:15 | 2019-10-24 18:30 | 1 | 15 | 4193711 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had FBR out this moring, did not find anything at that time, engineeering came down run daignostic on breaker said something was wrong on B phase, so i came back this evening to keep cust from losing power in the morning, found cracked c/o on 878-29, on B phase, crew on the way to change it, to keep the lights on for the customers have c/o change time off was 1815, time on was 1830
25941 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-08-26 01:30 | 2012-08-26 01:45 | 1 | 15 | 4972911 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THE SERVICE NEUTRAL WAS BURNED APART DUE TO THE INSULATION BEING RUBBED ON THE PHASE WIRE. ONLY ONE CUSTOMER AFFECTED. VER/PDP IDCC TOF2327 ALLOWED 15 MIN FOR REPAIR, CNT2 XXXX
25942 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-08-23 11:10 | 2014-08-23 11:25 | 1 | 15 | 4412311 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR WERE LEAD CONNECTS TO SERVICE, WILL OPEN BANK AND REMAKE CONNECTIONS, OPENED XFMR BANK FUSES AT 11:10 CLOSED AT 11:25. CUSTOMER HAPPY, POWER OK! VER/SEF
25943 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-06-08 14:45 | 2015-06-08 15:00 | 1 | 15 | 4526631 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD HOT LINE CLAMP ON XFM RISER OPEN AT 14:45 CLOSED AT 15:00 VER/HFP L3/HFP
25944 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-12-19 11:30 | 2022-12-19 11:45 | 1 | 15 | 4275311 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one leg was burnt in two.. cut out bad spot in service and reconnected with new wire. open transformer @ 11:30 closed @ 11:45
25945 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-03-14 10:40 | 2009-03-14 10:55 | 1 | 15 | 58406-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301402 -REPLACED BAD CUTOUT // COD 1 // VER/TOM L3/TOM IDCC MCCDIS TOF0859 XXXX
25946 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-05-13 18:15 | 2012-05-13 18:30 | 1 | 15 | 4786341 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 410-73 OPENED CUTOUT ON POLE 410-73 @ 18:15 CLOSED BACK IN @ 18:30.//COD 1// VER/DBM IDC XXXX
25947 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-06-11 15:23 | 2020-06-11 15:38 | 1 | 15 | 4004811 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | customer said they saw arcing after dark, found a burned spot on current limiting fuse and cutout was also bad, made repairs, transformer on pole 1105-C-159 was off from 15:23 to 15:38
25948 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-08-07 18:40 | 2011-08-07 18:55 | 1 | 15 | 4676131 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-184 BAD CUTOUT REPLACED TIME OFF 18;40 ON 18;55.//VER/CRB IDC XXXX
25949 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-06-02 04:45 | 2008-06-02 05:00 | 1 | 15 | 54218-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3311401 - HOT LINE CLAMP IS BURNING OFF WILL OPEN TRANSFORMER TO REPAIR CLAMP REPLACED HOT LINE CLAMP IDCC TOF2216 XXXX
25950 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2012-03-21 12:30 | 2012-03-21 12:45 | 1 | 15 | 4602711 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BROKEN NEUTRAL ON SERVICE DROP, REPAIRED AND RESAGGED WIRE, ALL POWER RESTORED VER/KEP IDCC TOF1154 ESTIMATED TIME TO RESTORE XXXX
25951 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-04-01 15:20 | 2016-04-01 15:35 | 1 | 15 | 4015841 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | POLE 771-A3-1 ARCING LOUDLY///FOUND BAD RIDE AROUND POLE MOUNT//THIS IS ONE THAT I THINK LAST WEEK THEY WERE TOLD TO REMOVE FROM SHELVES IN STOREROOM//I REMOVED BRKET AND INS. GOING TO BACK XFMR///MAY NEED CREW TO COME AND RELOCATE CUTOUT ON ARM ON BACK OF PLE NEXT WEEK///PLEASE SEND A COPY TO TIM HALL//OPENED BANK AT 15:20,,CLOSED AT 15:35//COMPLETE//EM//NO OUTAGE TILL 1520 VER/CRB
25952 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2013-10-28 11:55 | 2013-10-28 12:10 | 1 | 15 | 4969641 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | POLE IS LEANING AND PUTTING TENSION ON SECONDARY AND SERVICES. I WILL SEND A JOB TO ENGINEERING TO CORRECT. OPENED XFMR 785-489 @ 11:55, REPAIRED A BROKEN SERVICE NEUTRAL AND CLOSED @ 12:10. SH VER/CRB L/3 CRB
25953 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-01-08 16:55 | 2009-01-08 17:10 | 1 | 15 | 53463-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3007905//,,,,BROKE CONDUCTOR OUT OF TRANSFORMER LUG I MADE REPAIRS,,,BACK ON // OPENED @ 1655// VER/TOM L3/TOM IDC XXXX
25954 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-12-07 11:00 | 2010-12-07 11:15 | 1 | 15 | 63938-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUT SEVERAL LIMBS TO GET TO XFMR. FOUND LOOSE CONNECTION ON RISER WHERE IT GOES INTO XFMR LUG. PULLED ALL SEC RISERS OUT AND CLEANED. RE-INSTALLED RISERS. HAD XFMR OPE FROM 11:00 TO 11:15. SH COD-1 ISO TF 38830858A00343 VER/HFP L3/HFP IDC XXXX
25955 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2010-06-09 12:15 | 2010-06-09 12:30 | 1 | 15 | 59157-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAD TRABSFORMER OUT POLE 212C67 FROM 12:15 TO 12:30 .I CHANGED BAD CUTOUT ON POLE 212-C-67. ARM HAS A BAD BURNT PLACE IN IT I CALLED TIM HALL HE WILL GET A JOB WRITTEN UP TO CHANGE ARM. SEND COPY TO ROW PIKEVILLE TREES NEED CUT BAD IN THIS AREA. VER/KEP L3/KEP
25956 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2013-07-23 12:25 | 2013-07-23 12:40 | 1 | 15 | 4581871 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 148-205 METRE # 190229452 IS SERVED FROM THIS TRANSFORMER ON POLE 148-205. NEED TO SEND TO ENGINEERING FOR A WORK ORDER TO REPLACE THIS POLE. OPENED TRANSFORMER AT 1225, CLOSED AT 1240.//COD 1//MD FILED//EMAILED TO C FREEMAN// VER/DBM IDC XXXX
25957 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2008-05-28 12:40 | 2008-05-28 12:55 | 1 | 15 | 52139-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE IS BURNING. I HAVE REMOVED PRIMARY RISER TO TRANSFORMER AT POLE 492-21. REPLACED CUTOUT. OPENED CUTOUT AT 1240 AND CLOSED BACK AT 1255//3301701//VER/CRB IDC XXXX
25958 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2020-06-10 09:09 | 2020-06-10 09:24 | 1 | 15 | 4989521 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW REPLACING BAD LIGHTENING ARRESTOR ¦¦ COD-1 ISO TF 38821112C00051 OFF@ 0909 ON@0924
25959 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-03-27 19:55 | 2010-03-27 20:10 | 1 | 15 | H55027-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON TRANSFORMEROPENED TRANSFORMER AT 1955 CLOSED IT AT 2010 DUPLICATED IN HOIS FOR ORDER 55027-1 VER/HFP L3/HFP IDCC MCCDIS XXXX
25960 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-08-30 19:45 | 2021-08-30 20:00 | 1 | 15 | 4180561 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke @ 38831098A00790//Replaced cutout and bracket// OFF @ 19:45//Restored @ 20:00
25961 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-09-12 10:30 | 2011-09-12 10:45 | 1 | 15 | 4858091 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | TALKED TO CUSTOMER , WILL WORK MONDAY MORNING-RESEND--BAD CONNECTION AT SECONDARY BUSHING--NEED 4/0 RISER WIRE AND NEW BUSHING--50KVA CSP--CREW REQUIRED-- RELEASED BY CREW 078S07OFF @ 10:30 ON @ 10:45//VER/CRB IDC XXXX
25962 | South Williamson | 3411401 | DEWEY | INEZ | 2015-09-29 19:15 | 2015-09-29 19:30 | 1 | 15 | 4291291 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER CUTOUT ON POLE 744-335 WAS BAD///OPENED XFMER AT 19:15 TO REPLACED BAD CUTOUT////CLOSED AT 19:30///COMPLETE BR/ ISO 38830744A20335/ COD 1/ VER/BOW
25963 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2017-09-16 10:10 | 2017-09-16 10:25 | 1 | 15 | 4366311 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 38821087D00062 TWIST ON STIRRUP WAS NOT MAKING A GOOD CONNECTION AND WAS HEATING UP, SO I REPLACED IT. I OPENED THE TRANSFORMER AT 10:10. VER/AWD
25964 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-11-01 17:20 | 2011-11-01 17:35 | 1 | 15 | 4043101 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | SECONDARY TIE BROKE ON POLE 37830272B21164 ALLOWING OPEN SECONDARY TO CONTACT NEUTRAL, REPLACED TIE WIRE, POWER RESTORED. NO TRANSFORMER ON THIS POLE IN PO... 37830272B21164 VER/HFP L3/HFP IDCC FULL POWER CALL TOF1708 ESTIMATED TIME OFF FOR REPAIR XXXX
25965 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-04-29 11:15 | 2008-04-29 11:30 | 1 | 15 | 55423-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3411801//SD NEUTRAL INTO IN MID-SPAN,WILL REPAIRMADE NECESSARY REPAIRS,RESTORED,ALL OK AFTERWARDS// VER/DBM IDC CHANGED TIME OFF FROM 1041 ALLOWED 15 MIN FOR REPAIR XXXX
25966 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2011-04-22 13:45 | 2011-04-22 14:00 | 1 | 15 | H61885-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQ 39668051 // RELEASED BY CREW 078H14WORK REQ 39668051 // BROKEN CUTOUT ON POLE 329-153 NEED LINE CREW NO TRUCKS TO POLE.WORK REQ 39668051 // BROKEN CUTOUT ON POLE 329-153 NEED LINE CREW NO TRUCKS TO POLE. RELEASED BY CREW 078S01//FUSE PL #329-111 OPEN @ 13:45 CLOSED 14:00 REPAIRS COMPLETE @ 14:00 J. HEMLEPP VER/TOM L3/TOM IDC XXXX
25967 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-06-25 10:30 | 2010-06-25 10:45 | 1 | 15 | 57298-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ACTUALLY ON POLE 524-209 NO DEVICE SHOWN ON THIS POLE BROKEN CUTOUT COMP10:45 M.PHELPS OFF 10:30 RESTORED 10:45 RELEASED BY CREW 078H12 VER/KEP L3/KEP IDC XXXX
25968 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2020-05-18 10:50 | 2020-05-18 11:05 | 1 | 15 | 4848101 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection on at the weatherhead/CTs. Released by crew 077H20 opened at 10:50 closed at 11:05 power restored at 11:05
25969 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-07-16 22:00 | 2013-07-16 22:15 | 1 | 15 | H4533691 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE NETURAL. PULLED XFMR OFF ON POLE#38831101C40077 @ 10:00 BACK ON @10:15//COD 1// VER/DBM IDC XXXX
25970 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-05-10 16:10 | 2019-05-10 16:25 | 1 | 15 | 4249731 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection in splice, opened xfmr at 16:10 to 16:25
25971 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-10-19 21:55 | 2010-10-19 22:10 | 1 | 15 | 61075-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STS WR # 37394005 // SEC. POLE 1123- 4077 ROTTED OFF @ GROUND. RELEASED BY CREW 078H12 / TOOK SMALL OUTAGE TO MTR # 532 284 652 TO MAKE REPAIRS/ COMPLTED @ 22:10 J. HEMLEPP VER/HFP L3/HFP IDC XXXX
25972 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-06-06 07:18 | 2018-06-06 07:33 | 1 | 15 | 4560471 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | connection failed where service is connected to secondary riser. will repair connection,pulled off @07:18 back on @07:33
25973 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-07-08 14:00 | 2021-07-08 14:15 | 1 | 15 | 4873891 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE AT 14:00 to replace cutout power restored at 14:15
25974 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-08-09 23:55 | 2013-08-10 00:10 | 1 | 15 | 4642041 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 179-117 NO POWER OUT OPENED XFMR ON POLE 179-117 @ 23:55 CLOSED BACK IN @ 00:10. ONLY ONE CUST. ON XFMR.//COD 1//ISO// VER/DBM
25975 | Hazard | 3309302 | VICCO | JEFF | 2015-07-17 18:25 | 2015-07-17 18:40 | 1 | 15 | 4903891 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/
25976 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2009-09-28 10:40 | 2009-09-28 10:55 | 1 | 15 | 66523-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED XFMR BANK ON POLE 978-160 AT 10:40 TO REPLACE A BAD HOTLINE CLAMP. POWER WAS ON WHEN I ARRIVED BUT EQUIPMENT WAS ARCING. REPLACED AND RESTORED BANK TO SERVICE AT 10:55. SH//VER/CRB
25977 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-02-18 17:15 | 2008-02-18 17:30 | 1 | 15 | 64919-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000801//REPLACING CONNECTIONS VOLTAGE CHECKS FINE// VER/TOM IDCC TOF1525 ALLOWED 15 FOR REPAIR XXXX
25978 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-10-28 13:30 | 2015-10-28 13:45 | 1 | 15 | 4387821 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE NEUT @ XFMER, OPEN @ 13:30 ON @ 13:45. POSS. DAMAGE CLAIM// VER/ ADH
25979 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-01-13 13:30 | 2010-01-13 13:45 | 1 | 15 | 53478-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED CONNECTIONS ON POLE VER/KEP L3/KEP IDCC TOF0954 XXXX
25980 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-02-24 22:15 | 2010-02-24 22:30 | 1 | 15 | 60729-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED BAD CUTOUT VER/KEP L3/KEP IDCC TOF2124 XXXX
25981 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-02-19 15:55 | 2009-02-19 16:10 | 1 | 15 | 65568-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401702//CONTACTING SERVICER// REPLACED CUTOUT AND PUT OUT POLE FIRE OPENED AT 1555 NO OUTAGE TILL THEN VER/KEP L3/KEP IDC XXXX
25982 | South Williamson | 3200302 | BELFRY | TOLER | 2015-03-02 08:00 | 2015-03-02 08:15 | 1 | 15 | 4090201 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT, NEED TO OPEN CUTOUT TO PUT POLE FIRE OUT AND REPLACE THE CUTOUT/COD1/BAD TRANSFORMER CUTOUT, NEED TO OPEN CUTOUT TO PUT POLE FIRE OUT AND REPLACE THE CUTOUT. I OPENED TRANSFORMER AT 08:00, AND CLOSED BACK IN AT 08:15./FIX IT IN HOIS// VER/ ADH L3/HFP XXX
25983 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2011-05-14 12:07 | 2011-05-14 12:22 | 1 | 15 | 4090421 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | RISER ON ONE HOT LEG HAD BURNED INTO REPAIRED ALL POWER RESTORED AT 1222;; OPENENED TRANSF AT 1207 CLOSE TICKET IDC XXXX
25984 | South Williamson | 3411401 | DEWEY | INEZ | 2019-03-19 14:45 | 2019-03-19 15:00 | 1 | 15 | 4000621 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | school board called me no power to guard shack and sign//broke xfmr cutout on pole 744-445//i replaced cutout//restored at 15:00//complete//em
25985 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2008-03-24 12:35 | 2008-03-24 12:50 | 1 | 15 | 60262-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3404301CONNECTION BAD WHERE ENTRANCE MAKES UP TO SERVICE DROP VER/HFP IDC CHANGED TIME OFF FROM 1157 ALLOWED 15 MIN FOR REPAIR XXXX
25986 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-08-01 09:55 | 2016-08-01 10:10 | 1 | 15 | 4717021 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 144-317 BANK OF XFMS WILL MAKE REPAIRS...OPEND UP BANK @ 09:55 TO MAKE REPAIRS..CLOSED BACK IN @ 10:10.RESTORED.// VER/ ADH
25987 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-04-24 18:45 | 2010-04-24 19:00 | 1 | 15 | 50260-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34817970 //CHGING CUTOUT DOOR/NO CREW REQUIRED/OFF AT 1845 HRS BACK AT1900 HRS VER/HFP L3/HFP IDCC PN8052, CNT8 XXXX
25988 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-09-03 22:30 | 2010-09-03 22:45 | 1 | 15 | 63438-1 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RED-RED CONN. BAD AT TRANSFORMER. COD-1 VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 2006 PER CUST TICKET XXXX
25989 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-06-24 14:30 | 2020-06-24 14:45 | 1 | 15 | 4069841 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | replaced braces,,, opened @ 14:30 closed @14:45
25990 | Pikeville | 3407101 | TOPMOST | DEMA | 2021-05-31 21:00 | 2021-05-31 21:15 | 1 | 15 | 4652711 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Service drop was low going to house// outage to Resagged service/ 2100- 2115/ ISO 37830186000030/ COD 1
25991 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2010-03-04 16:15 | 2010-03-04 16:30 | 1 | 15 | 62884-1 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SERVE END.// VER/DBM IDCC TOF1551 ALOWED 15 FOR REPAIR, ORIGINALLY DIM LIGHTS ONLY XXXX
25992 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-03-26 18:40 | 2012-03-26 18:55 | 1 | 15 | 4620061 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 90-194 6T TRANS FUSE BROKE COD-1 ISO TF 38830090000194 VER/HFP L3/HFP IDC XXXX
25993 | Hazard | 3303902 | LESLIE | WOOTON | 2014-10-07 17:05 | 2014-10-07 17:20 | 1 | 15 | H4566101 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFMR , OPENED LINE FUSE ON POLE 438-3 @ 17:05 , CLOSED LINE FUSE BACK @ 17:20 , CLOSED XFMR FUSE @ 17:20 . ONLY 2 CUST. ON XFMR . DUP OF 4566101 FOR 1 CUST VER/HFP L3/HFP
25994 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-07-05 15:45 | 2011-07-05 16:00 | 1 | 15 | 4469891 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BAD CONNECTION ON 480V BANK ON GROUNDED HOT LEG.. REPAIRED .. TIME OFF 15:45 BACK ON AT 16:00 COD-1 ISO TF 39831097C00279 VER/HFP L3/HFP IDC XXXX
25995 | Hazard | 3302703 | HAZARD | HAZARD | 2010-10-22 20:35 | 2010-10-22 20:50 | 1 | 15 | 62188-1 | 15 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37448050 //THIS CUST. IS MISMAPPED ACTUALLY FED FROM POLE 272D-396 NEED CREW .STS WR # 37448050 // PLEASE SEND THIS TO JEFF COMBS. RELEASED BY CREW 077S04 BAD LEAD ON TRANSFORMER JKC ENTERED MD...HFP CCC COD-1 ISO TF 37830272D10396 VER/HFP L3/HFP IDCC MCCDL XXXX
25996 | Hazard | 3303901 | LESLIE | HYDEN | 2022-04-08 21:05 | 2022-04-08 21:20 | 1 | 15 | 4742641 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection on xfmr opened 21:05 closed at 21:20
25997 | South Williamson | 3411401 | DEWEY | INEZ | 2020-11-11 12:42 | 2020-11-11 12:57 | 1 | 15 | 4662221 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Opened TR fuse to clear failing arrestor outage should last less than 30 mins from start
25998 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-05-23 09:55 | 2022-05-23 10:10 | 1 | 15 | 4931491 | 15 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no outage when I arrived//bad arrestor on xfmr//i replaced cutout and arrestor//opened at 9:55//closed at 10:10//complete//
25999 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-20 14:11 | 2008-03-20 14:25 | 1 | 14 | 59476-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// FAULT POLE 37830202000046 OPENED AT 1411 CLOSED AT 1425 BAD CONNECTION XFMR POLE//COD 1// VER/DBM IDC XXXX
26000 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-10-26 14:48 | 2022-10-26 15:02 | 1 | 14 | 4068661 | 14 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral in customers service drop broke at the XFM, opened XFM 1027-C-181 @ 14:48 closed @ 15:02 to make repairs// send to bill johnson to send tech have job drawn up to set secondary pole for customer at 40 Hall st email sent to b johnson
26001 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-11-07 16:15 | 2017-11-07 16:22 | 2 | 7 | 4538141 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer making loiud noise when it rains/no arcing/no fluctuations opened 1615-1622 38820770C00120
26002 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-30 09:01 | 2014-01-30 09:15 | 1 | 14 | 4328481 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT FUSE BROKE INTO COD-1 ISO TF 38831062000017 VER/HFP L3/HFP IDC XXXX
26003 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-04-29 14:01 | 2010-04-29 14:15 | 1 | 14 | 52820-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FOUND BAD FUSE LINK, ROTTEN AND BROKE, HAVE REPLACED AND POWER IS RESTORED AT THIS LOC//COD 1// VER/DBM IDC XXXX
26004 | Pikeville | 3407101 | TOPMOST | DEMA | 2021-12-03 07:26 | 2021-12-03 07:40 | 1 | 14 | 4144181 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse blown @ 37830162000170.// Door failed to drop and was flaming up due to tracking//Replaced fuse and door.//Restored @ 7:40
26005 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-02-04 11:51 | 2011-02-04 12:05 | 1 | 14 | 53997-1 | 14 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | XFMR FUSE BROKE. RE-FUSED @ 12:05. XFMR BANK 38830978A30276 SERVES METHODIST CHURCH (METER 428783819). 350 MCM UNDERGROUND SERVICE. SH//MD FILED//COD 1// VER/DBM IDC XXXX
26006 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-09-10 15:10 | 2013-09-10 15:24 | 1 | 14 | 4835791 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE NEUTRAL BROKEN AT POLE 37830175000238.. OPENED TRANSFORMER ON POLE 37830175000238 AT 15:10, CLOSED AT 15:24, POWER RESTORED. ONLY 1 CUST OUT. *****CHANGE ISO POLE **** VER/SEF
26007 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-09-25 16:46 | 2015-09-25 17:00 | 1 | 14 | 4270161 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE ON POLE# 46-160 WILL CHANGE/// OPENED XFM FUSE @ 16:46 MADE REPAIRS AND CLOSED XFM IN @ 17:00 ////RESTORED SERVICE 2 CUSTOMERS// VER/ ADH
26008 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-09-30 14:00 | 2019-09-30 14:14 | 1 | 14 | 4075121 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | T-line reported single phase primary frayed, looks like single strand is all thats is holding it---looks to have one possibly two strands broke--need big bucket to work-- crew on site going to open xfmr on p# 188-149 LRM FETR 14:25 Off @ 1400 On @ 1414
26009 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2017-12-14 01:31 | 2017-12-14 01:38 | 2 | 7 | 4647711 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | open wire together,,,opened xfr @ 01:31 closed @ 01:38,,,resaged open wire ,,no outage until opened
26010 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-01-06 16:55 | 2009-01-06 17:09 | 1 | 14 | 52000-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HPF COD-1 3404302//, BAD CUTOUT, JOEY REED ON WAY WITH CUTOUT, TOOK XFORMER OFF AT 1655, BACK ON AT1709 L3/HFP IDC XXXX
26011 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-06-12 13:01 | 2011-06-12 13:15 | 1 | 14 | 4301701 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON XFMR POLE///CHANGED OUT CUTOUT AND VOLTAGE CHECKS OK//COD 1// VER/DBM IDC XXXX
26012 | South Williamson | 3411401 | DEWEY | INEZ | 2009-02-21 13:55 | 2009-02-21 14:09 | 1 | 14 | 66533-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-1 CUTOUT BAD L3/HFP IDCC TOF1241 ESTIMATED TIME OFF XXXX
26013 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2013-10-07 13:46 | 2013-10-07 14:00 | 1 | 14 | 4918841 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED CUTOUT AND EXTINGUISHED POLE FIRE. THIS POLE WILL NEED TO BE REPLACED. PLEASE SEND TO ENGINEERING FOR A WORK ORDER. //VER/GAH L3/HFP IDCC GOV1346 ESTIMATED TIME OFF XXXX
26014 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-06-19 14:59 | 2014-06-19 15:13 | 1 | 14 | 4112081 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL NEED TO OPEN FUSES ON 1147-4007/MOMENTARY OUTAGE TO CLEAR BAD CUTOUT ON POLE# 1123-6695/VEM OPENED FUSES @ 1457 BACK ON @ 1503WILL NEED TO OPEN FUSES ON 1147-4007/MOMENTARY OUTAGE TO CLEAR BAD CUTOUT ON POLE# 1123-6695/VEM/OPENED FUSES @1459/BACK IN @1503/ 25T FUSES ON POLE#1123D26695 BACK IN @1513/PLEASE NOTE 25TS TO GRAPHICS/THANKS/VEM 33 CUST OFF @ 1457 // 32 ON @ 1503 & 1 ON @ 1513
26015 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-01-14 22:50 | 2008-01-14 23:04 | 1 | 14 | 56766-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3403201 I WILL BE REPLACING CONNECTIONS AT CUST SERVICE POLE. BAD CONNECTORS AT SERVICE POLE REPLACED CONECTIONS EVERYTHANG OK.//VER/CRB IDC ASSUMING 15 MIN OUT FOR REPAIR XXXX
26016 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-05-22 21:10 | 2018-05-22 21:17 | 2 | 7 | 4397161 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 15min ETA secondary connection ad on 115-84. opened trans up at 21:10 repaired connection re energized trans at 21:17/ ISO 38831150000084/ COD 2
26017 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-03-20 18:15 | 2010-03-20 18:22 | 2 | 7 | 52039-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN ARRESTER, WILL HAVE TO OPEN XFMR TO ISOLATE ARRESTER... OPENED XFMR AT 18:15 & RESTORED POWER AT 18:22//COD 2// VER/DBM IDC XXXX
26018 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-12-09 17:18 | 2011-12-09 17:25 | 2 | 7 | H4165901A | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN TRANSFORMER AT 17:18 CLOSE AT 17:25. 1/0 SECONDARY BURNT DOWN THEIR WILL BE TWO CUSTOMER OUT OF SERVICE UNTIL I CAN MAKE REPAIRS. OFF AT 18:54 ON AT 19:30//COD 4 IDCC DUP TO OPEN TRANSFORMER XXXX
26019 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-03 00:38 | 2011-01-03 00:45 | 2 | 7 | 58059-1 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WE HAVE A CURRENT LIMITING FUSE GOING BAD. I AM CALLING FOR A BIG BUCKET TO REPLACE IT. WE WILL HAVE TO OPEN TRANS. WHEN TRUCK GETS HERE. WE FIXED TRANS. VER/ARN IDC XXXX
26020 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-04-01 01:48 | 2021-04-01 01:55 | 2 | 7 | 4409581 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout
26021 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-05-27 19:00 | 2013-05-27 19:14 | 1 | 14 | 4188691 | 14 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REPAIRED SERVICE DROP NEUTRAL. VER/HFP L3/HFP IDCC TOF1714 ESTIMATED TIME FOR REPAIR XXXX
26022 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-07-26 20:15 | 2008-07-26 20:28 | 1 | 13 | H60615-1 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001/ RISER WIRE CUTOUT LOOSE//COD 17//TRANSFORMER OFF AT 20:15//TOOK OFF TRANSFORMER ON THE SAME POLE AS THE FUSE TO WORK SAFELY//INTERRUPTED 1 EXTRA CUSTOMER// VER/DBM IDC XXXX
26023 | Hazard | 3311103 | STINNETT | WENDOVER | 2008-11-22 09:55 | 2008-11-22 10:08 | 1 | 13 | 50987-1 | 13 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3311103// SECONDARY CONNECTION FAILED ....REPAIRED CONNECTION, RESTORED POWER AT 10:08 IDCC TOF800 XXXX
26024 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-10-25 10:36 | 2008-10-25 10:49 | 1 | 13 | 58896-1 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CHANGED BAD CUTOUT, POLE FIRE IDC CHANGED TIME OFF FROM 0949 ESTIMATED XXXX
26025 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-02-26 19:00 | 2015-02-26 19:13 | 1 | 13 | H4084521 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NEUTRAL BROKEN WILL HAVE TO OPEN TRANSFORMER 358-D-128 TO SAFELY MAKE REPAIRS/SERVICE NEUTRAL BROKE OFF OF HOUSE, HAD TO OPEN TRANS. AT POLE 358-128 TO MAKE REPAIRS, OPENED AT 1900, CLOSED BACK IN AT 1913, ALL REPAIRS MADE.1 PART POWER, THEN TOOK TRANSFORMER OFF/COD 1+1// VER/ ADH
26026 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-02-25 13:42 | 2020-02-25 13:55 | 1 | 13 | 4431401 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OUTAGE TO ALLOW CREW TO REPLACE DEFECTIVE ARRESTOR ¦¦ COD -1 ISO TF 38830572000031 OFF@ 1342 ON@ 1355 Equip Disp#: 1000004900 L3/HFP
26027 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-04-30 16:48 | 2021-04-30 17:01 | 1 | 13 | 4500511 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | pole 38830269C00215 has pulled over primary guy and phone guys are broke primary nuetrul is 8ft off ground/ pole has caused service nuetrul to pull out of a press sleeve at pole this will need a crew to get a new guy installed at pole straightned in order to fix service nuetrul//meter is pulled and blanked out, meter is laying on ground beside meter base Released by crew 078H09///OPEN@ 16:48 CLOSED @ 17:01//complete BR
26028 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-12-02 17:05 | 2015-12-02 17:18 | 1 | 13 | 4505281 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 269A-77 11XFMR @ 17:05 CLOSED BACK @ 17:18 ./ ISO 37830269A00077/ COD 1/ VER/BOW
26029 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-10-06 16:35 | 2014-10-06 16:48 | 1 | 13 | 4558421 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | HOUSE NOB BROKE REPAIRED COMPLTED OPEN AT 16:35// VER/BOW VER.DJG K3.DJG AJBC CCCE CDC57 ONLY ONE CUST ON XFR.
26030 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-05-17 12:40 | 2013-05-17 12:53 | 1 | 13 | 4126591 | 13 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL PULLED OUT OF SPLICE. REPAIRS MADE- POWER RESTORED. ONLY 1 CUST. WITH DIM LTS. VER/SEF IDCC TOF1140 ESTIMATED TIME OFF FOR REPAIR XXXX
26031 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-05-02 19:00 | 2013-05-02 19:13 | 1 | 13 | 4066371 | 13 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SERVICE NEUTRAL BOKE ON POLE 42-120.REPAIRS MADE.POWER RESTORED. VER/HFP L3/HFP IDCC TOF1722 ESTIMATED TIME OFF FOR REPAIR XXXX
26032 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2019-06-19 11:35 | 2019-06-19 11:48 | 1 | 13 | 4546121 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I replaced the bad transformer cutout. Customer had power till I opened the transformer at 11:35, closed back in at 11:48. Send a copy to Ryan Thornbury to have pole 38821087A00002 replaced. ¦¦¦ SENT EMAIL AS REQUESTED ....HFP
26033 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-02-07 08:21 | 2018-02-07 08:34 | 1 | 13 | 4810641 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, opened xfmr at 08:21 replaced cutout, restored power at 08:34.//NO OUTAGE TILL TRANS OPENED
26034 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-01-06 11:20 | 2015-01-06 11:33 | 1 | 13 | 4910361 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ABOUT TO FAIL ON POLE 38830478D10320 TIME OFF 1120 TIME ON 1133 CLOSE TICKET/ VER/BOW L3/DKGXXXX
26035 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-05-27 21:50 | 2019-05-27 22:03 | 1 | 13 | 4351421 | 13 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | current limiting fuse, burning. opened can to make repairs @ 21:50 closed back in @ 22:03 pls close. tre/ riser was arcing opened transformer/ ISO 38830140A00371/ COD 1
26036 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-05-16 10:25 | 2010-05-16 10:37 | 1 | 12 | 63160-1 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BREAKING DOWN //REPLACED CUTOUT ON XFMR//COD 1// VER/DBM IDCC PN8, TOF0855 XXXX
26037 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-03-04 15:09 | 2015-03-04 15:21 | 1 | 12 | 4099961 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/APPROX 30 MINUTE OUTAGE/VEM/OPEN XFMR38830118B00240 @1509/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1521/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L3/DKGXXXX
26038 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-06-25 12:09 | 2014-06-25 12:21 | 1 | 12 | 4154181 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN GUY STUB20-A3-1011 NEED TECH AND LINE TO FIX MADE SAFE OPEN TRANS AT 12;09 BACK ON AT 12;21 VER/CRB
26039 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-01-08 11:34 | 2021-01-08 11:46 | 1 | 12 | 4856521 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Outage to replace cutout at 39830925000152 (1 CC) Off at 1134 On at 1146 FETR 1230
26040 | Pikeville | 3407103 | TOPMOST | KITE | 2012-06-01 08:00 | 2012-06-01 08:12 | 1 | 12 | 4858631 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE CUTOUT, POLE OK . TRANSFORMER OPENED FROM 08:00 TO 08:12 , ALL WORK COMPLETE / GXJ VER/KEP IDC XXXX
26041 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-08-27 13:23 | 2019-08-27 13:35 | 1 | 12 | 4952081 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING CUTOUT ON POLE 37830190B00360//COD 1//OFF @1323 ON @1335
26042 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-03-19 09:08 | 2017-03-19 09:14 | 2 | 6 | H4570021 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NETURAL BROKE IN SERVICE,MADE REPAIRES ,OPEN TRANSFORMER AT9:08 AND CLOSE AT9:14///RECORD FOR OPENING THE TRANSFORMER///VER/DKM
26043 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-01-10 14:35 | 2008-01-10 14:41 | 2 | 6 | 55532-1 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3309103// REPLACED CONNECTION ON POLE 424-312//COD 2//ISO 37830424D0312// VER/DBM IDC CHANGED THE TIME OFF FROM 1358 XXXX
26044 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-04-04 16:20 | 2021-04-04 16:32 | 1 | 12 | 4417441 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | splice is laying on dd light arm and arcing will have to open XFM on pole 93-354 to safely make repairs, will keep up with times// off @ 16:20 on @16:32
26045 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2012-02-23 10:45 | 2012-02-23 10:51 | 2 | 6 | 4485051 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT ON POLE 147-154 IS ARCING AT BOTTOM CONNECTION. I AM GOING TO OPEN CUTOUT AND CHANGE IT WHEN FLAGMEN GET ON JOB SITE. THERE IS NO OUTAGE AT THIS TIME. I OPENED LINE CUTOUT AT 10:45 CHANGED CUTOUT AND CLOSED IT BACK IN AT 10:51. VER/KEP AJB
26046 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-04-08 14:12 | 2020-04-08 14:18 | 2 | 6 | 4573121 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW FOUND BROKEN CUTOUT THAT NEEDS REPLACED ASAP... COD-2 ISO LF 38830279000105 OFF@ 1412 ON@ 1418
26047 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-07-08 22:00 | 2014-07-08 22:12 | 1 | 12 | 4215021 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POSSIBLE CRACKED CUTOUT NEED BIG BUCKET TO CHECK. RELEASED BY CREW 079H07 REPLACED BAD TRANSFORMER CUTOUT OPENED AT 2200 CLOSED TRANSFORMER AT 22:12 RELEASED BY CREW 079H03 VER/SEF
26048 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-06-03 09:51 | 2019-06-03 10:03 | 1 | 12 | 4419361 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replacing cutout/////while repairing DD light noticed xfm. cutout cracked on pole 334-5.opened xfm. @ 09:51 replaced cutout closed back in @ 10:03.
26049 | South Williamson | 3411401 | DEWEY | INEZ | 2019-05-11 14:27 | 2019-05-11 14:39 | 1 | 12 | 4252721 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout on 745-D-71 is breaking down,need big bucket to make repairs.i got trk in position and made repairs.opened trans cutout on 745D71 at 14:27 made reppairs,restored power at 14:39
26050 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-10-24 16:39 | 2008-10-24 16:45 | 2 | 6 | 58589-1 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//3402802//BAD CUTOUT/// / REPLCED CUTOUT COMPLETE. SH//VER/CRB IDC XXXX
26051 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-06-15 19:39 | 2017-06-15 19:45 | 2 | 6 | 4975201 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION TRANSFORMER,OPEN TRANSFORMER AT 19:39 AND CLOSE AT 19:45 37830279000142 VER/AWD
26052 | Hazard | 3303902 | LESLIE | WOOTON | 2019-06-30 21:00 | 2019-06-30 21:12 | 1 | 12 | 4624031 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broken neutral in service drop // opened xfer to make repairs Off @ 2100 On @ 2112
26053 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-08-22 08:07 | 2020-08-22 08:19 | 1 | 12 | 4356941 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Replacing bad current limmiting fuse off at 0807 time on 0819. No outage untill i opened. Was driving by and seen current limmiting fuse burning. apr at 0819 close ticket. dwest/ ISO 38830454A27701/ COD 1
26054 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-04-24 16:00 | 2015-04-24 16:12 | 1 | 12 | 4362871 | 12 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TRANS BANK WAS ARCING, TOOK CARE OF, HAD TO REMOVE A STICK PIN THAT WAS ARCING. MAYBE A TIE WIRE REMOVED INSULATOR. THIS IS THE TRANS. BANK AT POLE 375-2758.OPENED AT 1600, PUT BACK IN AT 1612. ONLY 1 CUST. WAS OUT./ ISO 37830375A32758/ COD 1/ VER/BOW
26055 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-01-03 17:09 | 2018-01-03 17:20 | 1 | 11 | 4703851 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout ,lightning arrestor & retied primary conductor in
26056 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-03-07 17:54 | 2011-03-07 18:05 | 1 | 11 | 51505-1 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TIME OFF 1754 TIME ON 1805 POWER RESTORED CUTOUT CHANGED CLOSE TICKET//COD 1 PER SERVICER// VER/DBM IDC XXXX
26057 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-11-03 12:24 | 2011-11-03 12:35 | 1 | 11 | 4047061 | 11 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IN SERVICE WIRE WAS BROKE. I REPAIRED SERVICE NEUTRAL VER/KEP IDCC TOF1152 ESTIMATED TIME OFF FOR REPAIR XXXX
26058 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-02-06 07:15 | 2016-02-06 07:26 | 1 | 11 | 4680351 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DOOR WAS BURNNING ON ARRIVAL, FUSE HAD BLOWN BUT DOOR DIDNT DROP, REPLACED CUTOUT AND DOOR APR AT 0726 CLOSE TICKET OFF AT 0715 VER/KEP
26059 | South Williamson | 3200302 | BELFRY | TOLER | 2009-08-28 13:59 | 2009-08-28 14:10 | 1 | 11 | 55163-1 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT.POLE 991-C-497 OFF AT 1359 ON 1410 COD-1 ISO TF 38820991A00259 L3/HFP IDC XXXX
26060 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-07-14 13:19 | 2022-07-14 13:30 | 1 | 11 | 4489361 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 37830022A20333 (COD 1)replaced cutout
26061 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-08-29 01:10 | 2019-08-29 01:21 | 1 | 11 | 4959521 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | spoke with customer, pole feeding next door neighbor is arcing, making loud noise //LOOKS LIKE LIGHTNING ARRESTOR HAS BROKEN DOWN,BELIEVE I CAN CLEAR IT UP SAFELY.WILL DO SO////////CUT IN CLEAR,OFF@01:10,ON@01:21//cod 1//AED created//
26062 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-03-18 15:13 | 2015-03-18 15:24 | 1 | 11 | 4207971 | 11 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I CUT SECONDARY OPEN AT 15:13 TO REPLACE BAD SECONDARY CONNECTIONS ON POLE 38820964B00152. POWER IS BACK ON. VER/ARN
26063 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2016-05-19 18:00 | 2016-05-19 18:10 | 1 | 10 | 4236461 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CUSTOMER STATES THEY WERE HAVING FLICKER PROBLEMS AND THEIR FRIDGE SHORTED OUT INSIDE FRIDGE THE METER DISPLAY WAS NOT WORKING THEY HAVE UNDERGROUND SERVICE THEIR VOLTAGE CHECKED GOOD AND BEAST OF BURDEN CHECKED GOOD I REPLACED METER AND DISPLAY IS WORKING ON NEW METER CUSTOMER STATES EVERYONE IN THE AREA IS HAVING SURGES THERE IS 5 CUSTOMERS FED OFF OF 50 KVA CSP TRANSFORMER NO OTHERS ARE EXPERIENCING SURGES ONLY FLICKER/ PULLED MTR 1800 RESTORED 1810/ ISO 37820052000021/ COD 1/ VER/BOW
26064 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-09-26 13:05 | 2009-09-26 13:15 | 1 | 10 | 63865-1 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT DOOR. VER/KEP L3/KEP IDCC TOF1225 EST TIME OFF XXXX
26065 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2021-05-31 21:50 | 2021-05-31 22:00 | 1 | 10 | 4652871 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | meter went bad, replaced with 657688967/ replaced meter/ outage 2150 to 2200/ ISO 39831147C14132/ COD 1
26066 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-02-19 18:25 | 2011-02-19 18:35 | 1 | 10 | 59378-1 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMITING FUSE CHANGED FUSE POWER RESTORED AT 1835 CLOSE TICKET//VER/CRB IDC FLICKERING LIGHTS CHANGED OFF TIME FROM 1755, ESTIMATED TIME OFF XXXX
26067 | Hazard | 3303902 | LESLIE | WOOTON | 2017-06-06 10:35 | 2017-06-06 10:45 | 1 | 10 | 4914561 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.REPLACED CUTOUT..P.HICKS..10 MINUTE OUTAGE TO ONE CUSTOMER..P.HICKS/ 1035-1045/ ISO 37830437C40145/ COD 1/ VER/BOW
26068 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-05-05 19:45 | 2021-05-05 19:55 | 1 | 10 | 4541811 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection on xfm bank 435-245 burnt out. made repaires. xfm bank open from 19:45 to 19:55
26069 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-08-26 12:25 | 2022-08-26 12:35 | 1 | 10 | 4796521 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke midspan in service drop.//Will need flagging crew to repair.// Customer off from 12:25 to 12:35
26070 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2012-10-31 16:05 | 2012-10-31 16:15 | 1 | 10 | 4290001 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR ON SERVICE NEUTRAL PULLED LOOSE, CAUSING CUSTOMER TO HAVE BRIGHT AND DIM LIGHTS//// SPLICED AND REPULLED SERVICE. COMPLTED. COD-1 ISO TF 37830377B00120 VER/HFP L3/HFP IDCC TOF1041 ESTIMATED TIME OFF FOR REPAIR XXXX
26071 | Hazard | 3303901 | LESLIE | HYDEN | 2020-08-17 15:25 | 2020-08-17 15:35 | 1 | 10 | 4339751 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Replacing transformer on pole 37830316A10200 (1 COD////off at XXXX - on at XXXXreplace xfrm leaking oil. open trans fuse @ 15:25, closed @ 15:35 hrs
26072 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-10-28 16:45 | 2021-10-28 16:55 | 1 | 10 | 4030941 | 10 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke in customers service drop at pole, will have to open XFM to make repairs, will keep up with times// XFM off at 1645 on at 1655
26073 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2019-04-17 11:45 | 2019-04-17 11:55 | 1 | 10 | 4125471 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | POLE TOP BURNING ON POLE 38830020C31008 COD-1 OFF 1145 ON 1155POLE TOP BURNING ON POLE 38830020C31008 all repairs made please close ticket LRM
26074 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-06-07 11:50 | 2019-06-07 12:00 | 1 | 10 | 4444401 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Bad insulink in secondary. Repaired 1150 - 1200
26075 | Hazard | 3303902 | LESLIE | WOOTON | 2020-05-16 13:35 | 2020-05-16 13:45 | 1 | 10 | 4842271 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut-out blown on pole 37830461000075. Replaced cut-out and arrester. Open transformer @ 13:35 Closed @ 13:45
26076 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-08-13 20:40 | 2013-08-13 20:50 | 1 | 10 | 4662831 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT CRACKED & BURNING UP ON 990B9..OPENED XFMR @ 20:40..REPLACED CUTOUT..CLOSED XFMR @ 20:50.ONLY ONE CUST AFFECTED..JRV.08/13/13 VER/SEF
26077 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2022-01-26 22:40 | 2022-01-26 22:50 | 1 | 10 | 4407611 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | had a broke neutral in serves drop off of xformer pole 212-A-77/ 2240-2250/ ISO 37830212A00077/ COD 1
26078 | Paintsville | 3410602 | E.PRESTON | LANCER | 2022-01-25 15:48 | 2022-01-25 15:58 | 1 | 10 | 4404361 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | bad connection at weather head, opened XFM bank to make repairs, off @ 15:48 on @ 15:58
26079 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-06-15 18:00 | 2013-06-15 18:10 | 1 | 10 | 4344071 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKE SECONDARY POLE//---- NEED 3 MEN AND FLAGGERS AND 40 FT POLE AND 100 WATT LT. RELEASED BY CREW 077S04// VER/DBM IDC XXXX
26080 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-07-24 16:20 | 2015-07-24 16:30 | 1 | 10 | 4939351 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD A SECONDARY CONNECTION ALMOST BURNDT INTO AT THIS LOCATION, HAD TO OPEN THE TRANSFORMER TO MAKE REPAIRS. OPENED AT 1620, CLOSED AT 1630. VER/CRB
26081 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-06-27 21:25 | 2021-06-27 21:35 | 1 | 10 | 4812701 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cracked 19.9 utout caught pole on fire. put fire out and replaced bad cutout on pole 38830141d00051. opened that cutout at 2125 and closed it in at 2135///cod 1//iso
26082 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-06-15 09:10 | 2020-06-15 09:20 | 1 | 10 | 4020161 | 10 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 38830020D33851, Line fuse on 38830020D38351 open @ 09:10, power restored @ 09:20.
26083 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-04-12 10:50 | 2008-04-12 11:00 | 1 | 10 | 50380-1 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL CLAMP ON XFORMER BROKEN, CUST HAD NO NEUTRAL ON THIS SERVICE. SOME DAMNAGED LIGHTS. POWER OFF AT 10:50 TO MAKE REPAIRS, BACK ON AT 11:00. VER/ARN IDC XXXX
26084 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-12-14 16:40 | 2013-12-14 16:50 | 1 | 10 | 4161521 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SQUEEZE ON BAD ON POLE 34D104 SERVICER TO MAKE REPAIRS// COMPLETE ALL PWR RESTORED @ 16:50 PLEASE CLOSE TICKET LRM VER/CRB L3/HFP
26085 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-04-25 14:30 | 2018-04-25 14:40 | 1 | 10 | 4277511 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CREW REQUIRED/ patrolling line on whetstone, found broken c/o on pole 1072-165, is hanging in mid air off t bracken, crew req, may not be able to get a truck to this cust has low serv from house to garage in way, 8 poles from rec on whetstone rd./ ISO 39831072000165/ COD 1/ 1430-1440
26086 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-05-05 16:16 | 2008-05-05 16:26 | 1 | 10 | 57273-1 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3310501// FUSE BROKE INTO 38831084D00346 VER/HFP IDC XXXX
26087 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-11-13 19:16 | 2019-11-13 19:26 | 1 | 10 | 4031951 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replacing broken cutout. Off at 1916 apr at 1926 close ticket. dwest
26088 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-08-06 11:00 | 2015-08-06 11:10 | 1 | 10 | 4103821 | 10 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | I OPENED XFMR AT 11:00 AND CLOSED BACK AT 11:10 IN ORDER TO REMOVE BROKEN GUY . PLEASE SEND SOMETHING TO DOUG CHRISTIAN TO REPLACE ANCHOR AND GUY/EMAILED HAZARD/ADH// VER/ ADH
26089 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-09-11 08:51 | 2010-09-11 09:00 | 1 | 9 | 65430-1 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON TRANSFORMER POLE, 1097-241, HAD LINE FUSE OUT ON POLE 1097-123, HAVE ALL REPAIRS MADED AND POWER IS RESTORED AT THIS LOC COD-1 (0 PER POWERON) VER/HFP L3/HFP IDC XXXX
26090 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-04-30 16:49 | 2017-04-30 16:58 | 1 | 9 | 4698171 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND AND REPLACED BROKE CUTOUT ON 38830188B02004. TIME OFF 1649 APR AT 1658 CLOSE TICKET. DWEST/ ISO V/ COD 1/ VER/BOW L3/HFP XXXHFP
26091 | Pikeville | 3407103 | TOPMOST | KITE | 2021-04-30 14:59 | 2021-04-30 15:08 | 1 | 9 | 4504741 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke on pole 37830210000051// Replaced & restored @ 15:08
26092 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-12-18 13:05 | 2008-12-18 13:14 | 1 | 9 | 59862-1 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302//, ON SITE, BAD CUTOUT, REPLACING IT, TOOK OFF AT 1305 BACK ON AT 1314//COD 1//ISO 38821061C00154// VER/DBM L3/KEP IDC XXXX
26093 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2017-12-17 21:57 | 2017-12-17 22:06 | 1 | 9 | 4655001 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer/ customer seen transformer arcing, Trans. riser had loosened up and was arcing, had to open trans. @2157, tightened up hot leg and closed back in @2206, power restored.//cod 1
26094 | Pikeville | 3311401 | REEDY STATION | DEANE | 2017-02-07 16:26 | 2017-02-07 16:35 | 1 | 9 | 4367521 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CAPACITOR | EMERGENCY OUTAGE NECESSARY TO ALLEVIATE SYSTEM CONDITION// OUTAGE SHOULD BE 30 MINUTES// THISIS FOR THE 1 PIKEVILLE AREA CUSTOMER ON THIS BREAKER - VER/TOM L3/TOM XXXHFP
26095 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-01-18 15:19 | 2017-01-18 15:28 | 1 | 9 | 4309471 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PULLED METER IN ORDER TO MAKE REPAIRES IN SERVICE DROP NEUTRAL CLOSE TICKET/ PULLED OUT SLEEVE IN SERVICE DROP/PULLED MTR FOR 9 MINUTES/ ISO 38830572B10206/ COD 1/ 1519-1528/ VER/BOW L3/HFP XXXHFP
26096 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-03-24 14:45 | 2016-03-24 14:54 | 1 | 9 | H4877281 | 9 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER HAS BURNED OUT OF THE HOT TAP ON PHASE B AT POLE 38821082000101. ALL THREE FUSES ARE IN AT POLE 38821082000098 BUT WILL HAVE TO BE OPENED WHEN REPAIRS ARE MADE. I OPENED THE LINE AT 14:45, AND CLOSED AT 14:54.// VER/ ADH
26097 | Pikeville | 3421001 | BREAKS | CITY | 2011-10-04 12:02 | 2011-10-04 12:10 | 1 | 8 | 4945271 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL CONDUCTOR BROKEN IN SERVICE DROP. ONLY ONE CUSTOMER AFFECTED. ///VER/CRB IDCC TOF0846 ESTIMATED TIME OFF, CCPP XXXX
26098 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-10-15 16:12 | 2009-10-15 16:20 | 1 | 8 | 65525-1 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND CAUGHT TOP OF POLE ON FIRE. IVE GOT FIRE OUT AND GOING TO CHANGE CUTOUT. I OPENED CUTOUT AT 16:12 AND CLOSED NEW ONE IN AT 16:20. ONLY 1 CUSTOMER WAS ACTUALLY OUT.//VER/CRB IDCC TOF1228 TON1529 XXXX
26099 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2020-08-17 12:03 | 2020-08-17 12:11 | 1 | 8 | 4338801 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | time off 1203 time on 1211
26100 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-10-17 20:06 | 2008-10-17 20:14 | 1 | 8 | 56669-1 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP RELATED TO ORDER 56670-1 1 CUSTOMER WAS ACTUALLY INTERRUPTED @ 2006 & RESTORED @ 2014. CHANGED TIME OFF & CUSTOMER COUNT IN POWERON TO REFLECT ACTUAL OUTAGE TIMES. IDCC CDC83 XXXX
26101 | Pikeville | 3407101 | TOPMOST | DEMA | 2019-05-13 15:28 | 2019-05-13 15:36 | 1 | 8 | 4264651 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT REPLACING///Arm mounted cut out had broke down and burned off of bracket hanging by hot tap lead.I took off line and replaced with new one pole mounted opened @ 15:28 closed @ 15:36.This has also burned arm badly will need to email copy to tech. to create job for arm replacment when possible.
26102 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-10-19 23:01 | 2008-10-19 23:09 | 1 | 8 | 57126-1 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, CHECKING TROUBLE, PULLED XFORMER OFF AT 2301, BACK ON AT2309, CONNECTOR FAILED WHERE XFORMER LEAD MADE UP TO AERIAL CABLE VER/ARN IDCC TOF2126 XXXX
26103 | Cannonsburg | 3010603 | RUSSELL | ASHLANDOI | 2019-06-04 14:29 | 2019-06-04 14:37 | 1 | 8 | 4426541 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bolt in sec bushing holding hot leg missing. no cust out but will need to open xfmer to make repairs. Opened @ 14:29 back in @ 14:37
26104 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2021-09-15 12:34 | 2021-09-15 12:42 | 1 | 8 | 4243811 | 8 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING TO REPLACE BAD CUTOUT // COD 1 // OFF@12:34 On@12:42
26105 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-01-20 14:53 | 2020-01-20 15:00 | 1 | 7 | 4323481 | 7 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout 38830222B00035/no crew required /replaced door/ ISO 38830222B00035/ COD 1 L3/HFP
26106 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-10-19 11:00 | 2020-10-19 11:07 | 1 | 7 | 4567241 | 7 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad insulink. part power, repairs made. pls close. tre
26107 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-03-15 12:25 | 2012-03-15 12:32 | 1 | 7 | 4580431 | 7 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 078S08 HAD TO REPLACE SERVICE// VER/DBM IDC XXXX
26108 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-03-09 15:08 | 2018-03-09 15:15 | 1 | 7 | 4982241 | 7 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replace cutout/ ISO 38830220D10118/ COD 1***per servicer
26109 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-03-18 16:27 | 2011-03-18 16:34 | 1 | 7 | 55556-1 | 7 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND CRACKED CUTOUT ON POLE 38830571000074 DRIVING BY. POLE HAD BEEN BURNNING TIME OFF 1627 ALL POWER RESTORED AT 1634 CLOSE TICKET//COD 1// VER/DBM IDC XXXX
26110 | Hazard | 3303902 | LESLIE | WOOTON | 2020-04-08 10:54 | 2020-04-08 11:00 | 1 | 6 | 4572231 | 6 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout
26111 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-08-17 11:45 | 2020-08-17 11:51 | 1 | 6 | 4338591 | 6 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING CUTOUT // COD 1 // OFF@ ON@1145 to1151
26112 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-03-10 13:14 | 2020-03-10 13:20 | 1 | 6 | 4465691 | 6 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | OPENING TRANSFORMER TO REPAIR SERVICE // COD 1 // OFF@ ON@ off @ 13:20 LRM pwr restored @ 14:10 please close ticket LRM ticket same as out#4451921 on 3/4/2020 LRM please remove power temp out of abnormal
26113 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-04-16 20:14 | 2008-04-16 20:20 | 1 | 6 | 51673-1 | 6 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3314401// NUETRAL WAS BROKE IN SERVICE DROP WE RESAGED SERVICEHEAVY EQUIP BROKE SERVICE// OPENED SERVICE TO REPAIR// SINGLE CUSTOMER OUT WHILE REPAIRS MADE - OPENED AT 2014// VER/TOM IDC XXXX
26114 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-11-11 11:44 | 2020-11-11 11:50 | 1 | 6 | 4661711 | 6 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | repaired neutral connection and resagged service
26115 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-04-30 09:44 | 2014-04-30 09:50 | 1 | 6 | 4650451 | 6 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT WAS FOUND WHILE REPAIREING LIGHT IN THE PROCESS OF CHANGING, OFF TIME 0944 APR AT 0950 CLOSE TICKET//COD 1// VER/DBM
26116 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-09-18 10:15 | 2019-09-18 10:21 | 1 | 6 | 4032581 | 6 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING CUTOUT ON POLE 38830139C46053//COD 1//OFF @ 1015 ON @ 1021

## 2008-2022 CMI per Equip
CMI
CMI | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | TOTAL
ARRESTER | 857810 | 1588182 | 433833 | 712844 | 732304 | 1883255 | 315606 | 572151 | 776812 | 1018544 | 792497 | 344676 | 2125857 | 832512 | 38575 | 13025458 | 5
BREAKER |  |  | 1222353 |  | 14568 | 59768 |  |  |  | 166178 |  | 378306 | 5760 |  | 1071661 | 2918594
CABLE TERMINATOR | 2112 | 4909 | 4181 | 63379 | 35935 | 8103 | 585 |  | 1050 |  | 315 | 1122 |  | 456 | 15478 | 137625
CAPACITOR |  | 840 |  | 186024 | 129831 |  |  | 411202 |  | 28697 | 48664 |  |  | 13884 |  | 819142
CIRCUIT SWITCHER | [12 empty] | 140766 | 57 |  | 140823
CONDUCTOR OVERHEAD | 853225 | 1040937 | 934922 | 1225618 | 1015332 | 909430 | 599127 | 1660257 | 442498 | 309362 | 1138343 | 893169 | 2611522 | 622877 | 1565594 | 15822213 | 4
CONDUCTOR UG | 108252 | 417813 | 179386 | 1072445 | 168941 | 200016 | 55241 | 912730 | 78019 | 42018 | 43755 | 39974 | 44643 | 119099 | 357051 | 3839383
CONN/CLAMP | 891676 | 1084581 | 714273 | 904573 | 664360 | 675625 | 1189562 | 835790 | 916676 | 804405 | 839571 | 514040 | 651464 | 925459 | 1111618 | 12723673 | 7
CROSSARM | 1151815 | 1116037 | 1374739 | 467073 | 435767 | 207837 | 779659 | 915137 | 151315 | 1118001 | 1224875 | 904547 | 864042 | 763591 | 1292497 | 12766932 | 6
CUTOUT | 6513586 | 5382767 | 3970414 | 4156824 | 3367546 | 3376057 | 5004143 | 4461908 | 3884287 | 2704737 | 3203200 | 2711115 | 1769482 | 2290386 | 1849019 | 54645471 | 1
FUSE | 55742 | 66933 | 39440 | 254675 | 78277 | 84712 | 90878 | 301297 | 74118 | 54888 | 68304 | 85214 | 158952 | 97791 | 149699 | 1660920
GUY/ANCHOR | 8682 | 29769 | 22223 | 92422 | 51614 | 42369 | 232384 | 7390 | 340450 | 5083 | 2952 | 30707 | 9174 | 1564 | 1060 | 877843
INSULATOR | 1953290 | 2428236 | 2296932 | 2635958 | 2180288 | 3235870 | 3609586 | 2754053 | 1201696 | 2076228 | 2769667 | 2986822 | 2008072 | 1430600 | 4600384 | 38167682 | 2
JUMPER/RISER | 302437 | 179404 | 1027484 | 149257 | 101121 | 87288 | 60799 | 154351 | 374536 | 104498 | 379738 | 335156 | 299840 | 69713 | 818751 | 4444373
METERING | 177 | 2090 | 716871 | 19519 | 2811 | 327 | 494 | 425 | 1271 | 4920 | 5260 | 927 | 11591 | 555 | 5556 | 772794
MOAB |  |  |  |  | 229065 |  |  |  | 1470 |  |  |  | 1469 |  |  | 232004
NONE | 6130 | 38105 | 421392 | 206308 | 161862 |  | 130331 | 661275 | 58730 | 2288 | [5 empty] | 1686421
OTHER EQUIPMENT | 1409824 | 297766 | 378085 | 814088 | 23159 | 156412 | 203171 | 68090 | 337084 | 120548 | 198731 | 1450375 | 40642 | 19769 | 180809 | 5698553
PEDESTAL | 1164 | 1586 |  | 1120 |  | 1170 | 1337 | 381 |  |  | 294 | 994 |  |  | 99 | 8145
POLE | 2025694 | 272050 | 117555 | 1324018 | 686427 | 188521 | 1492310 | 1067029 | 1680795 | 413398 | 1384846 | 746165 | 1025075 | 1442643 | 2014537 | 15881063 | 3
POLE HARDWARE | 184642 |  | 24476 | 25953 | 528430 | 13258 | 322 | 16643 | 30995 | 168 | 100741 | 10829 | 295652 | 54826 | 42749 | 1329684
RECLOSER, LINE/OCR/BR | 19297 | 245794 | 152054 | 139378 | 593689 | 252173 | 107757 | 22788 | 323651 | 212021 | 136879 | 138110 | 340570 | 135007 | 725198 | 3544366
REGULATOR | 220606 | 332930 | 524487 | 619995 | 106352 | 3881 | 65817 | 75000 | 11762 | 505912 | 501280 | 55851 | 218479 | 66160 | 225246 | 3533758
RELAY |  | 86266 |  | 453084 | [8 empty] | 644255 |  |  | 1183605
SECTIONALIZER | 85851 |  | 6264 | 1198 |  |  |  |  | 2176 | 117644 |  |  |  |  | 82701 | 295834
SPLICE, OH | 380474 | 297386 | 2012009 | 65563 | 189748 | 147011 | 436322 | 309443 | 88095 | 48847 | 196824 | 59704 | 96348 | 64108 | 1091774 | 5483656
SPLICE, UG |  | 1382 | 55 | 282 | 591 | 240 |  | 2754 | 3851 | 930 |  |  | 6349 |  |  | 16434
STATIC WIRE |  | 50592 | [10 empty] | 33128 |  | 3849 | 87569
SWITCH, OH | 523186 | 784613 | 476985 | 67626 | 784702 | 59143 | 342564 | 477272 | 1047853 | 395928 | 450592 | 230694 | 185286 | 373149 | 31367 | 6230960
TRANSFORMER, GROUNDING |  |  |  | 778 | 756 | [8 empty] | 462 |  | 1996
TRANSFORMER, OH | 553680 | 507207 | 788388 | 433420 | 534589 | 202967 | 346075 | 516941 | 210492 | 274283 | 389347 | 287515 | 404189 | 295327 | 365717 | 6110137
TRANSFORMER, POWER - LTC | 944081 |  |  |  | 137592 | 200964 | 107646 | 1610228 |  | 392177 |  | 23796 |  | 641170 | 484 | 4058138
TRANSFORMER, POWER - NON LTC |  |  |  | 10577 | [5 empty] | 7447 |  | 6708 |  |  |  | 24732
TRANSFORMER, STATION SERVICE | 70919 |  | 713383 |  |  |  | 4739 | [5 empty] | 362814 | 1502922 |  | 2654777
TRANSFORMER, UG | 9944 | 41250 | 18847 | 64529 | 656 | 13166 | 13176 | 33285 | 20439 | 7671 | 17987 | 33144 | 20154 | 38796 | 3364 | 336408
Total | 19134296 | 16299425 | 18571031 | 16168528 | 12956313 | 12009563 | 15189631 | 17847820 | 12060121 | 10936821 | 13894662 | 12269660 | 14375575 | 11802883 | 17644837 | 221161166

## Insulator Data
CMI | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | TOTAL
INSULATOR | 1953290 | 2428236 | 2296932 | 2635958 | 2180288 | 3235870 | 3609586 | 2754053 | 1201696 | 2076228 | 2769667 | 2986822 | 2008072 | 1430600 | 4600384 | 1317580 | 1998643 | 1383378 | 42867283
[13 empty] | Average from 2008 to 2024 | 2440230
[13 empty] | 2024 CMI | 1998643
0.81904
441587

## MR-4 Cutout Data
CMI | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | TOTAL
CUTOUT | 6513586 | 5382767 | 3970414 | 4156824 | 3367546 | 3376057 | 5004143 | 4461908 | 3884287 | 2704737 | 3203200 | 2711115 | 1769482 | 2290386 | 1849019 | 1688497 | 2139446 | 441880 | 58915294
67% better than 2008
46% better than 2010

## MR-3 Total Equipment Failures
CMI | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | TOTAL
All Equipment | 19134296 | 16299425 | 18571031 | 16168528 | 12956313 | 12009563 | 15189631 | 17847820 | 12060121 | 10936821 | 13894662 | 12269660 | 14375575 | 11802883 | 17644837 | 7695056 | 10044529 | 6029655 | 244930406
Note on S1: s282992: I will not use 2025 data for the equipment failures conversation

## TOTAL CMI DATA SINCE 2008
CMI
CMI | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | TOTAL |  | Insulator Average
ARRESTER | 857810 | 1588182 | 433833 | 712844 | 732304 | 1883255 | 315606 | 572151 | 776812 | 1018544 | 792497 | 344676 | 2125857 | 832512 | 38575 | 743748 | 678908 | 174089 | 14622203 | ARRESTER | 41483905 | CMI from 08 thru 24
BREAKER |  |  | 1222353 |  | 14568 | 59768 |  |  |  | 166178 |  | 378306 | 5760 |  | 1071661 |  | 87561 |  | 3006155 | BREAKER | 17 | years
CABLE TERMINATOR | 2112 | 4909 | 4181 | 63379 | 35935 | 8103 | 585 |  | 1050 |  | 315 | 1122 |  | 456 | 15478 | 282 | 94 |  | 138001 | CABLE TERMINATOR | 2440229.7059 | CMI per year
CAPACITOR |  | 840 |  | 186024 | 129831 |  |  | 411202 |  | 28697 | 48664 |  |  | 13884 |  |  |  |  | 819142 | CAPACITOR | 1998643 | 2024 CMI
CIRCUIT SWITCHER | [12 empty] | 140766 | 57 |  |  |  |  | 140823 | CIRCUIT SWITCHER | 81.9%
CONDUCTOR OVERHEAD | 853225 | 1040937 | 934922 | 1225618 | 1015332 | 909430 | 599127 | 1660257 | 442498 | 309362 | 1138343 | 893169 | 2611522 | 622877 | 1565594 | 526269 | 815014 | 1594727 | 18758223 | CONDUCTOR OVERHEAD
CONDUCTOR UG | 108252 | 417813 | 179386 | 1072445 | 168941 | 200016 | 55241 | 912730 | 78019 | 42018 | 43755 | 39974 | 44643 | 119099 | 357051 | 61743 | 74348 | 64331 | 4039805 | CONDUCTOR UG
CONN/CLAMP | 891676 | 1084581 | 714273 | 904573 | 664360 | 675625 | 1189562 | 835790 | 916676 | 804405 | 839571 | 514040 | 651464 | 925459 | 1111618 | 434377 | 1094207 | 384191 | 14636448 | CONN/CLAMP
CROSSARM | 1151815 | 1116037 | 1374739 | 467073 | 435767 | 207837 | 779659 | 915137 | 151315 | 1118001 | 1224875 | 904547 | 864042 | 763591 | 1292497 | 951503 | 522427 | 354064 | 14594926 | CROSSARM
CUTOUT | 6513586 | 5382767 | 3970414 | 4156824 | 3367546 | 3376057 | 5004143 | 4461908 | 3884287 | 2704737 | 3203200 | 2711115 | 1769482 | 2290386 | 1849019 | 1688497 | 2139446 | 441880 | 58915294 | CUTOUT
FUSE | 55742 | 66933 | 39440 | 254675 | 78277 | 84712 | 90878 | 301297 | 74118 | 54888 | 68304 | 85214 | 158952 | 97791 | 149699 | 97065 | 155026 | 82075 | 1995086 | FUSE
GUY/ANCHOR | 8682 | 29769 | 22223 | 92422 | 51614 | 42369 | 232384 | 7390 | 340450 | 5083 | 2952 | 30707 | 9174 | 1564 | 1060 | 3295 | 137988 | 6413 | 1025539 | GUY/ANCHOR
INSULATOR | 1953290 | 2428236 | 2296932 | 2635958 | 2180288 | 3235870 | 3609586 | 2754053 | 1201696 | 2076228 | 2769667 | 2986822 | 2008072 | 1430600 | 4600384 | 1317580 | 1998643 | 1383378 | 42867283 | INSULATOR
JUMPER/RISER | 302437 | 179404 | 1027484 | 149257 | 101121 | 87288 | 60799 | 154351 | 374536 | 104498 | 379738 | 335156 | 299840 | 69713 | 818751 | 136681 | 131500 | 13100 | 4725654 | JUMPER/RISER
METERING | 177 | 2090 | 716871 | 19519 | 2811 | 327 | 494 | 425 | 1271 | 4920 | 5260 | 927 | 11591 | 555 | 5556 | 1049 | 52152 | 312 | 826307 | METERING
MOAB |  |  |  |  | 229065 |  |  |  | 1470 |  |  |  | 1469 | [5 empty] | 232004 | MOAB
NONE | 6130 | 38105 | 421392 | 206308 | 161862 |  | 130331 | 661275 | 58730 | 2288 | [8 empty] | 1686421 | NONE
OTHER EQUIPMENT | 1409824 | 297766 | 378085 | 814088 | 23159 | 156412 | 203171 | 68090 | 337084 | 120548 | 198731 | 1450375 | 40642 | 19769 | 180809 | 33324 | 421951 | 705746 | 6859574 | OTHER EQUIPMENT
PEDESTAL | 1164 | 1586 |  | 1120 |  | 1170 | 1337 | 381 |  |  | 294 | 994 |  |  | 99 | 216 |  |  | 8361 | PEDESTAL
POLE | 2025694 | 272050 | 117555 | 1324018 | 686427 | 188521 | 1492310 | 1067029 | 1680795 | 413398 | 1384846 | 746165 | 1025075 | 1442643 | 2014537 | 508770 | 329096 | 287960 | 17006889 | POLE
POLE HARDWARE | 184642 |  | 24476 | 25953 | 528430 | 13258 | 322 | 16643 | 30995 | 168 | 100741 | 10829 | 295652 | 54826 | 42749 | 630 | 66978 | 52664 | 1449956 | POLE HARDWARE
RECLOSER, LINE/OCR/BR | 19297 | 245794 | 152054 | 139378 | 593689 | 252173 | 107757 | 22788 | 323651 | 212021 | 136879 | 138110 | 340570 | 135007 | 725198 |  | 650816 | 95529 | 4290711 | RECLOSER, LINE/OCR/BR
REGULATOR | 220606 | 332930 | 524487 | 619995 | 106352 | 3881 | 65817 | 75000 | 11762 | 505912 | 501280 | 55851 | 218479 | 66160 | 225246 | 478992 | 102642 | 429 | 4115821 | REGULATOR
RELAY |  | 86266 |  | 453084 | [8 empty] | 644255 | [5 empty] | 1183605 | RELAY
SECTIONALIZER | 85851 |  | 6264 | 1198 |  |  |  |  | 2176 | 117644 |  |  |  |  | 82701 |  |  |  | 295834 | SECTIONALIZER
SPLICE, OH | 380474 | 297386 | 2012009 | 65563 | 189748 | 147011 | 436322 | 309443 | 88095 | 48847 | 196824 | 59704 | 96348 | 64108 | 1091774 | 45602 | 107289 | 45673 | 5682220 | SPLICE, OH
SPLICE, UG |  | 1382 | 55 | 282 | 591 | 240 |  | 2754 | 3851 | 930 |  |  | 6349 |  |  | 1328 | 523 | 429 | 18714 | SPLICE, UG
STATIC WIRE |  | 50592 | [10 empty] | 33128 |  | 3849 |  |  | 50180 | 137749 | STATIC WIRE
SWITCH, OH | 523186 | 784613 | 476985 | 67626 | 784702 | 59143 | 342564 | 477272 | 1047853 | 395928 | 450592 | 230694 | 185286 | 373149 | 31367 | 191586 | 83262 | 59904 | 6565712 | SWITCH, OH
TRANSFORMER, GROUNDING |  |  |  | 778 | 756 | [8 empty] | 462 |  | 1068 | 1773 |  | 4837 | TRANSFORMER, GROUNDING
TRANSFORMER, OH | 553680 | 507207 | 788388 | 433420 | 534589 | 202967 | 346075 | 516941 | 210492 | 274283 | 389347 | 287515 | 404189 | 295327 | 365717 | 241078 | 386911 | 221626 | 6959752 | TRANSFORMER, OH
TRANSFORMER, POWER - LTC | 944081 |  |  |  | 137592 | 200964 | 107646 | 1610228 |  | 392177 |  | 23796 |  | 641170 | 484 |  | 1230 | 4674 | 4064042 | TRANSFORMER, POWER - LTC
TRANSFORMER, POWER - NON LTC |  |  |  | 10577 | [5 empty] | 7447 |  | 6708 | [6 empty] | 24732 | TRANSFORMER, POWER - NON LTC
TRANSFORMER, STATION SERVICE | 70919 |  | 713383 |  |  |  | 4739 | [5 empty] | 362814 | 1502922 |  | 226569 |  |  | 2881346 | TRANSFORMER, STATION SERVICE
TRANSFORMER, UG | 9944 | 41250 | 18847 | 64529 | 656 | 13166 | 13176 | 33285 | 20439 | 7671 | 17987 | 33144 | 20154 | 38796 | 3364 | 3804 | 4744 | 6281 | 351237 | TRANSFORMER, UG
Total | 19134296 | 16299425 | 18571031 | 16168528 | 12956313 | 12009563 | 15189631 | 17847820 | 12060121 | 10936821 | 13894662 | 12269660 | 14375575 | 11802883 | 17644837 | 7695056 | 10044529 | 6029655 | 244930406
Note on S2: s282992: I will not use 2025 data for the equipment failures conversation