756 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-03-11 12:00 | 2016-03-11 15:55 | 407 | 235 | 4837051 | 67845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN RECLOSERS @ POLE 206A3-1122 @ 1200,OPEN SWITCHS @ POLE 206C-2031 & TAG TO BRENT TACKETT,POLE BURNT OFF 2 206D-2050,RECLOSERS IN @ 1235, RELEASED BY CREW 078S05,,,CREW ON SITE,,PLEASE MAKE MAP DISCR.. MOVED XFMR TO C PHASE,,,,,LOWERED FACILITIES,,,ALL POWER RESTORED,,CLOSED NO SWITCHES @1555 RELEASED BY CREW 078H03/ ISO 38830206A31122/ COD 407/ VER/BOW AJBC TOF11:35
757 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-09-10 09:03 | 2022-09-10 14:08 | 561 | 297 | 4861751 | 67813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REC 1127-B1-954 open, A B and ground fault// checking// bad pole top insulator on pole 1127-A-264, need manual ROW crew, paul layne is coming to assist with repairs Released by crew 074S09
758 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-01-25 10:13 | 2019-01-26 13:52 | 592 | 1659 | 4721401 | 67800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | A PHASE OUT INITIALLY (149 CUST)¦¦ OPENED B&C @ 1220 (148 CUST)¦¦ have two broke poles, 1048-15, 114, and 133, looks like just pulled over needs straighten and needs crossarms, tech is on site, loop ccut on 104-237, grd and tg at this loc to ron virgin closed in rec on 1024-2054, at 1430, restoring power to all cust, but one wlgc radio tower on hill---crew on site today--call in Dozer and DHE Track digger---crews on site working 1/26---repairs made-- Released by crew 078H16 L3/HFP
759 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-06-06 15:54 | 2018-06-06 17:30 | 706 | 96 | 4562891 | 67776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened @ 1554 closed @1730 // cod 706 iso 37830459B00166
760 | South Williamson | 3411401 | DEWEY | INEZ | 2021-02-23 13:29 | 2021-02-23 18:35 | 248 | 306 | 4232081 | 67626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | recloser open at 767-110//conductors very low at pole 767-28 touching trees///opened switches on 767-674//crew enroute to resag wire//also found phase off insulator on pole 742-84 touching ridge pin//repairs made//restored all customers at 18:35//complete//em Released by crew 079S01
761 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2015-03-04 00:43 | 2015-03-04 06:05 | 210 | 322 | 4095871 | 67620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER PATROLLING LINES/PATROLED PAST STEPDOWNS AND RECLOSER//FOUND NOTHING//PATROLED PAST STEPDOWNS AND RECLOSER//FOUND NOTHING//FOUND FAILED INSULATOR ON POLE 795-85 //INSILATOR REPLACED//RESTORED AT 06:05//COMPLETE//EM VER/HFP L3/HFP AJB
762 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-08-25 01:25 | 2014-08-25 03:55 | 450 | 150 | 4419961 | 67500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | POLE 70-3612 SPLICE PULLED APART CALLED CREW RELEASED BY CREW 078S08 VER/DKG L3/DKG THIS IS THE ORIGINAL OUTAGE WHERE CUSTOMERS WERE INTERRUPTED BY SPLICE PULLING LOOSE ON HENDRIX CABLE AJBC LCD 3008003 PH B INLT OUT. SEE 4420091 FOR CB OUTAGE.
763 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-03-29 11:41 | 2012-03-29 12:36 | 1226 | 55 | 4631331 | 67430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | OPENED REC TO ISOLATE CROSSARM FIRE CREW ENROUTE TO CHANGE CROSSARMARM BURNT INTO POWER RESTORED VER/KEP IDCC TOF1100 XXXX
764 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-04-18 01:45 | 2022-04-18 08:32 | 556 | 407 | 4772001 | 67364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 1198929/SCADA INDICATED CB L/O AT 0145//Crews found phase off insulator on hill side. Making repairs//DOL 1198929/SCADA INDICATED CB L/O AT 0145//SERVICER EN ROUTE TO ASSESS Phase off of the arm at pole 224-D-253. Released by crew 077S04. all power restored @08:32 hrs p.hicks
765 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-02-24 10:30 | 2011-02-24 11:40 | 962 | 70 | 60679-1 | 67340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM ON POLE 179-38 WAS ROTTON AND BROKE, LINE ACROSS CREEK IN VERY DIFFICULT LOCATION, OPENED GOAB ON POLE 179-185 AT 10:30 HRS , CLOSED BACK IN AT 11:40//VER/CRB IDC XXXX
766 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-07-05 09:15 | 2016-07-05 11:39 | 720 | 144 | 4536271 | 67317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | .CUTOUT BROKE DOWN ON POLE 166-125 AND TOOK OUT RECLOSER ON POLE 190-406. I OPENED LINE FUSE ON POLE 166-101 TO ISOLATE FAULT AND CLOSED RECLOSER IN AT 10:48. WE ARE GOING TO CHANGE CUTOUT. WE CHANGED CUTOUT AND CLOSED LINE FUSE IN AT 11:39. THIS SHOULD HAVE PICKED UP EVERYONE. RELEASED BY CREW 074H21 AJB
767 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-01-23 02:53 | 2013-01-23 04:30 | 870 | 97 | H4731171 | 67275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED PRC CREW /WIRE BURNED DOWN AT 94-258 "B" PHASE ONLY COD-407.OPENED SWITCHES ON 70-3503 @ 02:50 TO SAFELY MAKE REPAIRS..BLR.ALSO OPENED REC ON 94-6574 (FOR COLD LOAD PICK UP AFTER REPAIRS) CLOSED SWITCHES @ 03:55,RECLOSURES @ 04:30 VER/KEP IDC XXXX
768 | Hazard | 3309302 | VICCO | JEFF | 2018-09-27 15:37 | 2018-09-27 21:10 | 202 | 333 | 4168571 | 67266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | looks like bad insulator on middle phase deadend insulator 19.9 manuel pole Released by crew 077H14
769 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-02-21 08:11 | 2015-02-21 21:15 | 152 | 784 | 4060911 | 67153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WIRE DOWN ON POLE 450C-124/ ARMS BROKEN ON PL 450C37/ WILL OPEN LOOPS ON POLE 450C-162 WILL RESTORE POWER TO WHEN WIRE UP ON 450C124 RECLOSERS OPEN PL 426D-43 POWER RESTORED TO PL 450C-162 AT 12:50 RELEASED BY CREW 075H03/ ISO 38821107000030/ COD 152 TOTAL VER/HFP L3/HFP AJB
770 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2015-07-16 16:37 | 2015-07-17 19:15 | 42 | 1598 | 4903021 | 67116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO ORDER 4893461 - CREW NEEDED TO OPEN RECL ON POLE 242-38 TO ALLOW THEM TO MAKE REPAIRS TO RECLOSER ON POLE 37820242000049 - NO TRUCK ACCESS MUST CLIMB OPENED AT 17:42 ON AT 19:15 D SAMMONS AJB
771 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2012-06-19 17:08 | 2012-06-19 20:37 | 321 | 209 | 4932771 | 67089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE 327 CUST // RISER BURNT OFF OF TWO HOLE PAD CONNECTOR ON GOAB SWITCH ON 7-C-5..NEED CREW.WILL HAVE TO DROP STATION BREAKER TO REPAIR...//..JUSTICE, HOMER & MATNEY, EDWARD OPENED CB @ 2001 INTERUPTING AN ADDITIONAL 260 CUSTOMERS. // CLOSED CB @ 2037 RESTORING ALL CUSTOMERS. VER/HFP L3/HFP IDC XXXX
772 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-02-20 03:48 | 2015-02-20 13:15 | 125 | 567 | 4047231 | 67079 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER FOUND STEPDOWN OUT/ MAKING CHECKS ON STEPDOWN//STEPDOWN HIGH SIDE FUSE IS BLOWN ON POLE 144-191. I AM GOING TO OPEN RECLOSER ON SAME POLE TO DROP LOAD AND PUT A SMALL FUSE IN AND TRY TRANS.STEPDOWN HIGH SIDE FUSE IS BLOWN ON POLE 144-191. I AM GOING TO OPEN RECLOSER ON SAME POLE TO DROP LOAD AND PUT A SMALL FUSE IN AND TRY TRANS. I PUT A 6T FUSE IN HIGH SIDE OF STEPDOWN TRANS. AND IT BLEW BACK OUT HARD. WE HAVE A BAD 500 STEPDOWN TRANS. TRUCK ACCESSIBLE.CREW REQUIRED. VER/HFP L3/HFP AJB
773 | Hazard | 3309302 | VICCO | JEFF | 2018-04-25 20:46 | 2018-04-26 02:20 | 200 | 334 | 4279611 | 66800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Wire down and crossarm broken at 37830323D00596.Crossarm broke on 323D/596 // xarm rotted in two//cod 343
774 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-05-11 07:27 | 2019-05-11 10:58 | 421 | 211 | 4251371 | 66799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 161 CUSTS ON APCO SIDE//THEY ARE PATROLLING//RECL CLOSED AT 0937 TO SECT/ Closed sec on 552-581 @ 1058 apr close ticket. Released by crew 078S11 L3/HFP
775 | Hazard | 3303902 | LESLIE | WOOTON | 2009-02-18 06:28 | 2009-02-18 09:00 | 439 | 152 | 63723-1 | 66728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3303902//FOUND BAD L/A ON POLE 437-40//COD 439// VER/DBM IDC XXXX
776 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-12-18 05:19 | 2016-12-18 15:20 | 111 | 601 | 4208951 | 66711 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURNED INTO ON POLE 37830538000017 NEED LINE CREW ==== POLE UP ON HILL === ALSO HAVE WIRE DOWN ON POLE 37830538000160 GET TO THIS WITH TRUCK === POWER ON MAIN LINE AT THIS TIME AT === 37830538000021 WIRE DOWN REPAIERED LINE ON AT 13:25 ==== POLE 37830538000046 WIRE DOWN REPAIRED LINE POWER ON AT 15:20 === ALL POWER ON RELEASED BY CREW 077S03 AJB
777 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-12-03 02:52 | 2012-12-03 08:25 | 573 | 333 | 4437421 | 66694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED PRC CREW--NEED FLAGERS--OPEN AND TAGED SWITCHES ON POLE 39831123D37003 AT 04:10/// CLOSED B AN C PHASE RECLOSERS IN ON POLE 39831123D26526 AT 04:24--NEED HD ARM 3 PINS AND INSULATORS--CUTOUT ARRESTOR--TOP OF POLE BURNT OFF--CAN LOWER EVERYTHING? RELEASED BY CREW 078S07//COD 575 + 22 // IDCC CNT764 XXXX
778 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-01-30 01:36 | 2010-01-30 11:13 | 120 | 577 | 61301-1 | 66664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | COD-120 / 31 MINUTES AND HAD TO MANUALLY ROLL TICKET UP TO RECLOSER 459-C-235 / HAZARD BRINGING CREWS OUT AT DAYLIGHT TO WORK TROUBLE. WILL HOLD TICKET UNTIL THEN DUE TO BAD ROAD CONDITIONS. REPAIRED PRIMARY WIRE DOWN DUE TO BAD PLACE IN WIRE // SEE RECORD 61406-1 FOR 28 CUSTOMERS THAT WENT BACK OUT AFTER RECLOSER WAS RESTORED, 28 CUSTOMERS. VER/HFP L3/HFP IDC CREATED A STEP FOR 28 CUSTOMERS XXXX
779 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-10-21 14:11 | 2011-10-21 18:32 | 334 | 261 | 4008151 | 66602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ON POLE 1040-3 GOT CROSS ARM ROTTED OFF GOING TO OPEN GOAB SWITCH ON POLE 1039-133 CLOSED RECLOSER AT 1613 TO OPEN GOAB ON POLE 1039-133 CLOSED GOAB AT 1832 RELEASED BY CREW 077S05 ///VER/CRB IDC XXXX
780 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-02-09 15:32 | 2009-02-09 17:18 | 628 | 106 | 57085-1 | 66568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3307301//CREWS OPENED GOAB IN ORDER TO MAKE SAFE REPAIRS TOA CONDUCTOR THAT ONLY HAS 1 OR 2 STRANDS HOLDING IT UP//COD 628// VER/DBM L3/DKG MLR OK
781 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-10-08 14:00 | 2008-10-08 14:52 | 1277 | 52 | 54346-1 | 66404 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP MIKE LASSL0 REPORTED TROUBLE AT TDC STRUCTURE # 333-2 (STRUCTURE DOWN) DISTRIBUTION POLE 37830296C20233 WHICH IS IN THE HAZARD/BLACKGOLD CKT. THIS IS UNDERBUILD. PER MIKE WILLIAMS & P PARSONS - TRANSMISSION CROSS ARM BROKE WILL NEED TO VERFIY IDC XXXX
782 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-07-13 14:10 | 2012-07-13 21:11 | 170 | 421 | 4714321 | 66393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OP[ENED REC TO ISOLATE DAMAGED POLE ... OUTAGE FOR ORDER 4712771 NOTES FROM THAT ORDER... POLE 37830249B00089 ALMOST BURNT OFF AT TOP, DUTY SUPERVISOR NOTIFIED.-- OPENED RECLOSERS ON POLE # 37830249B10346 AT 14:10 EVERYBODY HAPPY AT 2111 // COD-170 ISO 37830249B10346 IDC XXXX
783 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-10-09 05:01 | 2014-10-09 05:47 | 1663 | 46 | 4577351 | 66369 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP L3/HFP AJB CCTIN FEC57 PER TRANS LOG AND DISP LOG. OPCO CROSSER AND STATE CROSSER. SEE SAME ORDER NUMBER.
784 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-11-10 07:36 | 2010-11-10 10:32 | 377 | 176 | 54496-1 | 66352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | "A" PHASE ONLY DOWN/OPENED AND ISOLATED BREAKER TO SAFELY ISOLATE DOWNED LINE/CREW ENROUTE SQUIRREL BURNED PRIMARY HENDRIX DOWN. CREW ON SITE - REPAIRS UNDERWAY. REPAIRS COMPLETE. RELEASED BY CREW 076S02 VER/KEP L3/KEP IDC XXXX
785 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2016-02-03 00:19 | 2016-02-03 10:22 | 110 | 603 | 4668981 | 66330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE LOOP BURNT OPEN AT 401-D-20 COD-110/ WILL NEED TO ISOLATE TO REPAIR AFTER WORKING 4669041//CLOSED SWITCHES @ 1022//SEE OUTAGE 4668981 VER/CRB AJB
786 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-05-12 21:59 | 2016-05-12 23:18 | 838 | 79 | 4210081 | 66202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WILL HAVE TO OPEN STATION CB TO ALLOW CREWS TO SAFELY MAKE REPAIRS// WILL PROVIDE FETR ONCE CREW ON SITE AND ABLE TO PROVIDE//TOM ASSOCIATED WITH PO 4209431//TOM - OPENED @ 2159- FETR 2330 UNLESS OTHER PROBLEMS ARE FOUND//TOM VER/TOM L3/TOM AJB
787 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-10-26 18:33 | 2021-10-26 22:03 | 600 | 210 | 4021281 | 66160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | Had regulator go bad on Pole 446-299. Got it bypassed. opened Recl on pole 446-c4-300 @ 1922 to isolate bad regulator // Recl on 446-c4-300 was defective and only opened A and B phase // C Phase was energized until Recloser on pole 423-C-278 was opened to isolate the line @ 2123 // Reg and Recl isolated and all customers restored @ 2203
788 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2018-02-14 12:22 | 2018-02-14 15:34 | 344 | 192 | 4840081 | 66048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | xarm on pole #38831053B00004 is broke. we are in the process of cutting deadends on pole# . 1053B00105 &1053B00007. then will install loops on38831053B00008 closed @ 1534
789 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-02-24 18:12 | 2011-02-24 20:05 | 583 | 113 | 60887-1 | 65879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 60827-1 CREW HAD TO TAKE EMERGENCY OUTAGE TO REPLACE DEFECTIVE CUTOUTS NOTES FROM 60827-1 " BAD CUTOUT ON POLE 37830249C00018 CREW AND FLAGGERS REQUIRED, DUTY SUPERVISOR NOTIFIED. // SEE 60887-1 FOR RECLOSER OUTAGE TO MAKE REPAIRS ///OPENED RECLOSERS ON POLE 37830248A41086 AT 18:12, CLOSED AT 20:05 POWER RESTORED. COD-583 ISO OCR 37830248A41086 VER/HFP L3/HFP IDC XXXX
790 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-07-28 15:15 | 2016-07-28 19:15 | 274 | 240 | 4699501 | 65760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 W/ETA: 1420.BAD CUTOUT NO OUTAGE POLE IS ON FIRE WILL NEED TO OPEN LINE TO MAKE REPAIRS//OPEN SW 408-216 DUE TO POLE FIRE//BAD CUTOUT NO OUTAGE POLE IS ON FIRE WILL NEED TO OPEN LINE @ 1515 TO MAKE REPAIRS ON POLE 408-216 BAD CUTOUT NO OUTAGE POLE IS ON FIRE WILL NEED TO OPEN LINE @ 1515 TO MAKE REPAIRS ON POLE 408-216 RELEASED BY CREW 077S01 VER/CRB AJB
791 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-10-19 21:06 | 2011-10-20 04:04 | 762 | 418 | 4001381 | 65751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OCRS AT POLE 1123-D2-6526 OPENED DUE TO POLE FIRE AT POLE 1123-5512 // WILL OPEN SWS AT POLE 1123-7003 AND TAG// THEN CLOSE RECLOSERS AND THIS WILL RESTORE 685 CUSTOMERS// REMAINING 77 WILL BE OUT UNTIL REPAIRS COMPLTED// NO TRANSFER CAPABILITY//PRT ON SITE REPLACING 50FT JUNCTION POLE FETR 07:00//POWER RESTORED AT 04:04// RELEASED BY CREW 078H03 // VER/TOM L3/TOM IDC CHANGED START TIME FROM 2042, FIRST CALL POLE FIRE ONLY XXXX
792 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-02-09 17:27 | 2010-02-10 02:30 | 121 | 543 | 54569-1 | 65703 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C PHASE ONLY OUT WHEN ARRIVED, CROSSARM BROKE AT POLE 38830278000015 AND 38830278000016, 1 PHASE OFF OF INSULATOR AT POLE 38830278000017, NO TRUCK TO ANY., WIRE ON GROUND HOT, NEED TO OPEN OTHER 2 PHASES. OPENED AND TAGGED AT 19:12// VER/TOM L3/TOM IDC XXXX
793 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-07-11 15:54 | 2020-07-11 20:05 | 617 | 251 | 4152991 | 65662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1035489 // SCADA indicated the DA INTELLIRUPTER 1098-B1-6133 locked out interrupting 617 customers //bad insulator on switch cap bank pole on c phase, crew req, luke mccoy on site open 600 amp solid blades on 1122-48 also insulator is on pole1146-1119 fetr 20:30 for lf on pole 1146-7 Released by crew 078H06
794 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-12-13 08:45 | 2009-12-13 16:29 | 219 | 464 | 50120-1 | 65625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONFIRMED ALL THREE RECLOSERS OUT PATROLLING HAZARDS//7200 CUTOUT FAILED POLE 37830201B00078 BURNED INTO CALLING FOR ASSISTANCE//PARTIAL RESTORE BACK TO OPEN SWITCHES 201-33 COMPLTED AT 11:50 RELEASED BY CREW 077S04CONFIRMED ALL THREE RECLOSERS OUT PATROLLING HAZARDS//7200 CUTOUT FAILED POLE 37830201B00078 BURNED INTO CALLING FOR ASSISTANCE//PARTIAL RESTORE BACK TO OPEN SWITCHES 201-33 COMPLTED AT 11:50 //RESTORED COMPLETE AT 16:29 MLR
795 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-12-01 08:52 | 2018-12-01 10:38 | 619 | 106 | 4496161 | 65614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | rec. open on pole 122-343.rec. possibly bad..not operating.opened source side and load side switches and tagged to DDC and closed bypass switches in @ 10:38..please send copy to Dwayne Thacker.
796 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-08-31 19:10 | 2012-09-01 03:20 | 133 | 490 | 4990111 | 65170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC OPEN POLE 879-B-388, FAULT POLE 879-B-237 RESTORED @ 3:20 MP. CC 133. VER/SDB IDC XXXX
797 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-04-15 20:11 | 2018-04-15 22:20 | 505 | 129 | 4234001 | 65145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | switch pole 441-263 is old and was not completely closed on b&c phase/emergency opened switch 941-D-440 at 21222 due to the arcing switch, closed 941-D-440 back in at 2206. This switch is inoperable and should not be operated again until replaced/
798 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-04-21 18:32 | 2020-04-21 19:56 | 773 | 84 | 4731871 | 64932 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 1011786/SCADA INDICATED CB L/O AT 1832/CREWS EN ROUTE/ phases are out of sag on pole 37830230C00005. Released by crew 077S02 back on at 1956
799 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-06-06 21:12 | 2013-06-07 10:13 | 83 | 781 | 4232971 | 64823 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINECREW REQUIRED, 19.9 UNDERGROUND CABLE, NEED STANDOFFS FAULT WIZZARD AND HIPOD STICKS. OLDER 19.9 CABLE RELEASED BY CREW 078S11----- CABLE TEST BAD FROM POLE 478-415 TO PAD 478-417 RELEASED BY CREW 078H01 VER/KEP IDCC CDC83 XXXX
800 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2021-05-21 19:23 | 2021-05-21 21:48 | 447 | 145 | 4608711 | 64815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | bad switch c ph. pole 45-2542 Released by crew 078S07
801 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-06-16 10:48 | 2008-06-16 13:10 | 1468 | 142 | 65489-1 | 64788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND A BAD CUTOUT ON POLE 115-628 ISOLATED POLE AND RESTORED CB A AT 1132// STS WR # 24799401 FAULT POLE 38830115C00628FOUND A BAD CUTOUT ON POLE 115-628 ISOLATED POLE AND RESTORED CB A AT 1132// STS WR # 24799401, CHANGED CUTOUT AND BRACKET,LIGHTING ARRESTER RESAGED LOW SERVICE, NO TRUCKS TO POLE VER/HFP IDC XXXX
802 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-11-10 15:38 | 2020-11-10 17:16 | 661 | 98 | 4658001 | 64778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CB tripped while on HLT/ DOL 1068385 Released by crew 078H16///cutout at pole 45-C4-5732 failed and burned crossarm in two///Outage for portion of 47th St-39th St ckt that is currently abnormally fed from Ashland-29th St ckt
803 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-06-01 00:09 | 2021-06-01 02:39 | 430 | 150 | 4652791 | 64500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crew required need 2 sets of double duty arms and braces probably 2 buckets/ fault pole 38830376000017 Opened Reclosers on 351-C2-290 at 00:09. Isolated and tagged to K.Griffith. Closed rec 351-c2-290 at 02:39. Ticket complete.
804 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-12-03 12:05 | 2010-12-03 13:25 | 805 | 80 | 62746-1 | 64400 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | FOUND BLOWN SURGE ARRESTOR ON THE STATION REGULATOR MOAB X1 OPEN, CREW CUT IN CLEAR AND RESTORED POWER AT 1325 VER/KEP L3/KEP IDC XXXX
805 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-12-15 05:36 | 2010-12-15 13:00 | 145 | 444 | 50404-1 | 64380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE OUT ON STEPDOWN TRANS--FLAGERS AND HELP ON WAY //C PHASE STEP DOWN OUT 143 CUSTOMERS - CREW INSTALLING NEW STEPDOWN TR // ISO LF 37830149B00116 // OPENED OTHER STEPDOWN @ A PHASE 1049 & C AT 1158 ALL RESTORED @ 1300 SEE H1145828-1 & H1145829-1 FOR A & C PHASE OUTAGES VER/HFP L3/HFP IDC XXXX
806 | Hazard | 3310502 | HADDIX | CANOE | 2020-04-04 15:03 | 2020-04-04 17:18 | 550 | 118 | 4560661 | 64350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DOL 1006633 // DA Scheme auto-load xfer on tail end of outage // RECL 51-58 open // 3rd time this RECL has been out in past week //possible equipment misoperation // patrolled line and found nothing // will bypass bad equipment to keep from happening again // cod 796 //
807 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-05-22 11:36 | 2014-05-22 14:25 | 1244 | 169 | 4739761 | 64270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 851 108 BAD CUTOUT BURNED TOP OF POLE..108 OFF.ISOLATED ON P-851-31..ONLY 1 XFMR OFF..851-108.LAST XFMR BACK ON AT 14.25.//COD 1244 VER/KEP AJB CDC86 PER SCADA.
808 | Pikeville | 3421001 | BREAKS | CITY | 2022-03-31 15:49 | 2022-03-31 18:56 | 373 | 187 | 4706871 | 64264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 556 has come off of insulator on pole 220-316 and has locked C phase recloser out on pole 220-171///will open A & B phase up to keep 3 phase customers from single phasing///Opened other 2 phases @ 16:20///will need line crew and flaggers///Repairs made closed reclosers in @ 18:56 and restored all customers
809 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-02-03 11:12 | 2010-02-03 14:58 | 1561 | 226 | 62593-1 | 64186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33719936 //1112 SCADA INDICATED CB LOCKED OUT SERVICE ENROUTE//ISOLATED BAD 10 KVA XFMR ON POLE 37830247A00382 TRYING FOR PARTIAL RESTORE//PARTIAL COMPLETE NEED 25 KVA 19.9 XFMR TRUCK ACCESS AND FLAGGERS REQUIRED RELEASED BY CREW 077S04 REPLACED XFMR AND RESTORED POWER AT1458 CREW 077H01//VER/CRB IDCC TOF1114 CHECK FUSING AND BREAKER SETTINGS XXXX
810 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-11-01 04:15 | 2013-11-01 11:28 | 148 | 433 | 4990031 | 64084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVE 2 PHASES OF #2 HENDRIX BROKE . CB NEVER OUT.. 2 PHASE OUT HAVE A LINE CREW FROM PIKEVILLE IN ROUTE TO REPAIR ** OPNED PHASE OTHER PHASE AT 0900 CLOSED ALL AT 1128 ** AT 1101 STEVE RAY HAS PERM TO CLOSE GOAB AT 954-100 // BASED ON CALLS & B.O. 148 CUST INITALLY OUT ON A & C PHASES & 103 OUTAGE WHEN SW OPENED DUPLICATING FOR SW OUTAGE VER/HFP L3/HFP IDC XXXX
811 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-08-17 23:20 | 2021-08-18 06:51 | 166 | 451 | 4094461 | 63988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1140699 ///big bucket required//CLOSED RECLOSER IN AT 0157 UP TO SWITCH 38830198C30165big bucket required///tagged to ddc Released by crew 078S03
812 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-08-19 00:55 | 2018-08-19 12:23 | 198 | 675 | 4971971 | 63855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Grounded&tagged to DDC at 620A1-342/// #4alum dn @619-8to619-10//// Manual treecrew&linecrew required Released by crew 078S11//CLOSED OCR @ 1015//OPENED BACK UP @ 1028 CLOSED BACK IN @ 1129//UP TO SWITCH 38830619000041//FOUND WIRE DOWN @ POLE 38830619000042//Grounded &tagged to DDC at 620A1-342/// #4alum dn @619-8to619-10//// Manual treecrew&linecrew required Released by crew 078S11.reclosure on at 11;29..blr..solid blade switch on pole 41 in @ 12:23 Released by crew 078H07 // L3/HFP
813 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-07-28 05:43 | 2012-07-28 13:15 | 141 | 452 | 4855161 | 63732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE STEPDOWN FUSE BLOWN ON POLE 37820098D20148A  333KVA STEPDOWN BAD ON PLATFORM  WILL NEED LINE CREW AND CREW TO CLEAN OIL SPILL  RECLOSER SHOWS IN ON POLE 37820098D00149 RELEASED BY CREW 074H18 VER/KEP IDC XXXX
814 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-06-18 03:27 | 2018-06-18 06:24 | 360 | 177 | 4614391 | 63720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | related to 4611141 // crews patrolling //Phase A is out, loop burnt open on A phase at pole 38830503D10052//will require outaging addtl cust to make repairs//cod 360 //
815 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-08-20 14:08 | 2017-08-20 18:32 | 241 | 264 | 4280451 | 63624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED SWS AT 1065-D2-287 AT 1457PHASE A LAYING ON THE GROUND BURNING, I OPENED SWITCHES ON POLE 38821065D20287 AT 14:57. NEED COIL OF 1/0 PRIMARY. VER/AWD SJGC CDC88, PN 38821065D20287, CNT46 (B&C-PH CALL)
816 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-12-09 00:28 | 2010-12-09 04:15 | 357 | 227 | 64571-1 | 63559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN AT POLE 1065-B-85.....STA BREAKER OPEN.// OPENED SWS AT 1065-D2-287 //CLOSED STA CB AT 117 // REPAIRS COMPLETED AT 1065-B-85 AND CLOSED SWS AT 1065-D2-287 AT 0215 PICKING UP TO 1065-B-275 // CLOSED RECLS AT 1065-B-275 AT 0300 RESTORING TO POLE 1041-A-69 & 1041-B-10 // CLOSED RECLS AT 1041-A-69 AT 0337 // CLOSED SWS AT POLE 1041-B-10 AT 0415 //VER/GAH IDC XXXX
817 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-11-26 14:54 | 2013-11-26 21:12 | 182 | 378 | 4076291 | 63546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | *** HOLD ORDER REQUIRED ***RECLOSER ON POLE 37830175000166 OPEN, PATROLLING LINE, JEFF COMBS AND CREW ENROUTE TO HELP. BAD INSULATOR ON POLE 37830175000183, ARMS ALMOST BURNT IN TWO. *** HOLD ORDER REQUIRED LOAD TRANSFER *** VER/HFP L3/HFP IDC XXXX
818 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2021-07-16 16:10 | 2021-07-16 17:41 | 698 | 91 | 4921681 | 63518 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1132376/ restored 1741/ Transmission found dead end bell failed
819 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-01-08 21:18 | 2018-01-09 12:38 | 73 | 920 | 4722821 | 63436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | B phase recloser out (73 CUST) , patrolling line. crossarm braces broke letting arms get into top of cutout, pole # 154-6 T. Smith to look at first thing in morning // O937 OPENED A & C PHASE RECLS (73 CUST) CLOSED A & C @ 1035 73 CUST// HAVING PROBLEMS PICKING UP ALL CUST DUE TO COLD LOAD PICKUP//1218 ALL CUST REST FROM RECL 129-42 // NOTE THIS IS FOR THE ORIGINAL B PHASE OUTAGE - EXTENDED DUE TO COLD LOAD PICKUP
820 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-03-30 14:45 | 2011-03-30 16:59 | 1016 | 134 | 60512-1 | 63379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | PLEASE CLOSE THIS ORDER.....HFP//IT FORCE CLOSED IDC XXXX
821 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-02-08 16:16 | 2018-02-08 19:46 | 360 | 210 | 4818151 | 63369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad stepdown xfm. on pole 73-643..will need 333 stepdown..line crew..and flagging crew to make repairs.. Released by crew 074S01
822 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-06-18 18:41 | 2015-06-18 23:33 | 308 | 292 | 4604961 | 63336 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION XFMR LTC FAILED//OPENED FEEDER BREAKER AT 1842//OPENED RECLOSER 1151-D-444 AND BACKFED FROM PIKEVILLE-CEDAR AT N.O. RECLOSER 24-A2-35 @ 2006//RESTORED 261 CUST//REPAIRS MADE ON LTC AND FEEDER RESTORED AS OF 2334//NORMAL FEED RESTORED @ 0108// SEE DUP H4604961 FOR INITAL C PHASE OUTAGE VER/HFP L3/HFP AJB
823 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-05-13 13:54 | 2009-05-13 16:30 | 405 | 156 | 52527-1 | 63180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RECLOSER OUT, CURRENT FUSE BAD, ALSO REPLACE CONTROL PANEL ON RECLOSER VER/KEP L3/KEP IDC XXXX
824 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-11-18 23:51 | 2015-11-19 14:30 | 192 | 879 | 4468071 | 62924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONFIRMED A PHASE OCR OUT - COD 30//TOM - 0318 - SERVICER REPORTED FINDING BURNT OFF POLE @ 522-205, WILL REQUIRE TRACK MACHINE - UNABLE TO LOWER //TOM/INSTALL 10T LINE FUSE ON 522-117/TAGGED TO DDC/RECLOSER AT 523-D3-183 BACK IN @0507/VEM - RESTORED ALL BUT 4 CC - 0651 - ERIC BAIER PERMISSION TO REMOVE KY DDC HOLD TAGS AT 522-117 AND REPLACE WITH OWN AND ASSUME DISPATCH AUTHOPRITY//TOM// VER/ ADH AJB
825 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2017-09-01 15:49 | 2017-09-01 18:45 | 356 | 176 | 4317471 | 62656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER ON 761-244 AT 15:49 TO ISOLATE. POLE 762-4 ON FIRE DUE TO PHASE ON ARM. POLE 762-60 CROSSARM ON FIRE DUE TO 3 BAD SOLID BLADES// REPAIRING NOW// REPAIRS COMPLETE// CLOSED RECLOSER ON POLLE 761-244 AT 18:45 RESTORING ALL CUSTOMERS VER/KEP SJG
826 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-02-21 23:46 | 2013-02-22 01:52 | 497 | 126 | 4838861 | 62622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BURNT DOWN AT REC. POLE 37830272B40477 (PH A) 497 CC. OPENED RECLOSERS AT POLE 477 AT 0015. OUTAGING AN ADDTL 601 CC, POWER RESTORED AT 01:52. VER/SDB IDC XXXX
827 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-12-10 22:06 | 2019-12-11 03:20 | 278 | 314 | 4143451 | 62392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B ph only//cod 80//closed B ph recloser in @ 2254 and it stayed in//later found out that wire had burned down at pole 37830472000048 and the recloser only picked up 2 customers//opened B ph back up to isolate wire down @ 2307 // interrupts 2 cc again//calling for crew//will need to open other 2 phases to make repairs// open recloser 02:15 (+198) closed 03:20//no cause found for down wire, it appeared to have burnt in two/// trouble tickets showing B and C phase from start
828 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-08-08 17:03 | 2014-08-08 18:39 | 648 | 96 | 4343591 | 62208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RECLOSER OPEN ON POLE #69-278 WILL PATROL/// CLOSED RECLOSER IN @ 18:39 AND IT STAYED// THIS IS SECOND TIME// CONTROL CABLE NEEDS REPLACED// AED ENTERED AND NOTE PLACE ON POWERON MAP VER/DKG L3/DKG AJB
829 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-07-14 08:07 | 2010-07-14 19:45 | 89 | 698 | 66666-1 | 62122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONFIRMED C PHASE RECLOSER OPEN PATROLLING LINE//ATTEMPTING RESTORE//LINE WONT STAY PATROLLING MORE//15:15 RESTORED TO OPEN SWITH AT POLE 200-368//C PHASE IS DOWN AT POLE 37830223C00152 OPENING ALL PHASE TO MAKE REPAIRS ALSO POLE 37830223C00466 IS BURNED OFF WILL HAVE TO LOWER XFMR AND PRIMARY IDCC CNT152 XXXX
830 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-03-02 09:09 | 2010-03-02 11:40 | 411 | 151 | 62126-1 | 62061 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | BREAKER OPENED BACK UP SEE ORDER 62082/ FAILED LINE REGULATOR AND FAILED LINE SIDE DISCONNECT VER/KEP L3/KEP IDC XXXX
831 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2016-07-08 18:43 | 2016-07-08 22:36 | 266 | 233 | 4584031 | 61978 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | WEST PAINTSVILLE STATION DE-ENERGIZED DUE TO THELMA-THEMLA 69KV LINE OUTAGE//TOM - 1925 - SERVICER IN STATION MAKING CHECKS//TOM -- SDB / 2035 / DAMAGED 69KV TRANSFORMER ARRESTER, CREWS MAKING REPAIRS. VER/TOM L3/TOM/// VER/DKM AJB
832 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-10-19 06:24 | 2008-10-19 08:13 | 567 | 109 | 56968-1 | 61803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310501 0651 NOTIFIED DOUG CHRISTIAN (HAZARD D/S CREW WOULD NEED TO BE CALLED OUT TO HELP SERVICER PATROL CKT. PATROLL TO NEXT RECLOSER AND FOUND NOTHING, GOING TO TRY RECLOSER ** PATROLLED CKT AND FOUND NO PROBLEMS , CLOSED RECL AT 0813. IDC FOUND ROTTEN POLE ON 11/4 SEE OUTAGE NUMBER 61591-1 ALLOWING PRIMARY TO SAG DURING COLD CONDITIONS CHANGED FROM UNKNOWN XXXX
833 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-04-17 16:59 | 2009-04-17 18:22 | 744 | 83 | 57340-1 | 61752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3301701//DUPED IN HOIS//SCADA INDICATES FEEDER LOCKOUT @ 1659//COD 1263// == ARRESTERS WENT BAD ON PHASES A,B, CUT IN CLEAR AND CHANGED CUTOUT ON TAP LINE ==// VER/DBM IDCC CCA XXXX
834 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2022-04-07 15:20 | 2022-04-07 23:34 | 129 | 494 | 4737841 | 61556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | rec open on pole 963C-213.broke 752 pole at 963C-7.//opened c phase @ 1551//COD 59 FROM BEGINNING OF OUTAGE //OPENED C PHASE @ 1551 THIS OUTED 70 MORE CUSTS//TOTAL COD 129//rec open on pole 963C-213.broke 752 pole at 963C-7.. dig#2204071672..a&b phase rec open on pole 963C-213. i opened c-phase at 15:51..broke 75 class2 pole at 963C-7.. dig#2204071672.. Released by crew 079S03/// REPLACE POLE AND RESTORED @23:34
835 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-04-02 22:39 | 2010-04-02 23:33 | 1139 | 54 | 57771-1 | 61506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED FEEDER BREAKER AT STATION AT 2239 DUE TO POLE FIRE AT POLE 67-A-83. RESTORED FEEDER BREAKER AT 2333 //VER/GAH AJBC CCSCO IDCC XXXX
836 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2022-12-16 08:15 | 2022-12-16 10:59 | 375 | 164 | 4268741 | 61500 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | Transmission Line Outage LR- DOL 1259093
837 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-09-23 01:51 | 2011-09-23 14:59 | 78 | 788 | 4907411 | 61464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 171-9 BURNT AT ARMS, ONLY 1 OF POLE TOP LOST, 2 PHASE DOUBLE DEAD END ON AN ANGLE WITH CUTOUT AND ARRESTER ON ARM, TRANSFORMER, SERVICE DROP AND GUY WIRE. NO TRUCK, SHOULD BE ABLE TO LOWER, NEED 2 8 ARMS AND BRACES, CUTOUT, ARRESTER. STATION BUCKET MAY REACH, ONLY C PHASE OPEN//@ 0645 OPENED OTHER PHASE//SEND TO V MULLINS //CREW ON SITE/SETTING NEW POLE/DIFF LOCATION/TRACK EQUIP TO SITE/FETR1600/VEM/REPAIRS MADE ABD POWER RESTORED TO ALL CUST 1459/PLEASE CLOSE/VEM//COD 164// VER/DBM IDCC CNT164 XXXX
838 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-04-29 07:03 | 2009-04-29 09:50 | 368 | 167 | 56864-1 | 61456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3312202//ACTUAL PREDICTED ISOLATING POLE IS 37830174A00220//COD 368//SERVICER FOUND BAD INSULATOR, CREW REQUIRED...//VER/CRB IDC XXXX
839 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-11-22 06:19 | 2009-11-22 15:35 | 116 | 556 | 61195-1 | 61346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3301701//SLEEVE FAILED//WIRE DOWN BETWEEN POLE 419-D-134 AND 419-135//LIFTED HOTTAP ON 134 AND MADE REPAIRS//OPENED RECLOSER ON POLE 20 TO REDUCE LOAD AND REPLACED HOTTAP @ 1305 RESTORING 13 CUSTOMERS... REMAINING 95 RESTORED WHEN CLOSE RECLOSER @ 1325//ISO//TOTAL CUST OUTAGED 108// VER/DBM IDC XXXX
840 | South Williamson | 3411401 | DEWEY | INEZ | 2021-05-25 13:30 | 2021-05-25 18:18 | 213 | 288 | 4620651 | 61344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | middle phase out//only feeds this 3 phase customer and a garage for the house next door//patroling to find where it is open//this is mountain crossing//OPENED SB ON POLE 38830767A40674 COD 213//OFF @ 1745 ON @ 1818 LOOP BURNT//no outage til sb opened
841 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-12-15 12:46 | 2010-12-15 20:50 | 140 | 484 | 50657-1 | 61344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 38120803 RELEASED BY CREW 074H14. 500KVA STEP DOWN TRASFORMER BLOWED OFF TOP. CALLED TIM HALL HE IS GETTING CREW TOGEATHER. GREG OPENED 600AMP SOLID BLADE ON POLE 22-B-16. RELEASED BY CREW 074S11 CLOSED STEPDOWN IN AT 19;28 LET SIT FOR A FEW MIN. TRY REST.CLOSED IN AT 22-B-16 AT 20:23 TO POLE 46-2 CLOSAD IN AT 20:50 SHOULD HAVE ALL CUST.//COD 140// VER/DBM IDCC CDC92 XXXX
842 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-07-02 20:22 | 2019-07-03 11:26 | 72 | 904 | 4642521 | 61299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | G HICKS//patrolling, Closed reclosure on 1047-c3-100, Did not hold. Opened normally closed switch on pole 1047-27 tagged to myself, Tried in reclosure on pole 1047-c3-100. Came back out. Fault between there and reclosure. Can not find fault, hold till daylight. Removed tag and closed switch on 1047-27 Released by crew 078H04 bad cutout on P# 1047-132 all pwr restored @ 11:26 Released by crew 078H06
843 | South Williamson | 3200301 | BELFRY | BELFRY | 2012-01-09 21:00 | 2012-01-10 04:44 | 138 | 464 | H4243801 | 61281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIREPHASE B RECLOSER LOCKED OUT ON 989DS18.. .POLE 990A44 BURNT OFF.JUST ABOVE XFMR..BAD CUTOUT.WILL HAVE TO REPLACE POLE..SEND TO J REED RELEASED BY CREW 080S01 // UPDATED FETR DUE TO FIELD CONDITIONS - UPDATED TO 0500 // CLOSED OCR AT 0423 - XFMR ON POLE 990-A-44 CLOSED AT 0444 // IDC ASSUMING OTHER PHASES OPEN TO MAKE REPAIR XXXX
844 | Hazard | 3303901 | LESLIE | HYDEN | 2016-12-12 01:34 | 2016-12-12 15:40 | 108 | 846 | 4185691 | 60918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD CUSTOMER REPORT FLASH WILL CHECK AT DAYLIGHT--TROUBLE ON 412-68-OPEN CLAMP AT 412-274-TAG FOR DDC---NEED RW/CUTOUT/ARR 19.9TOP OF HILL SHANNON CRISP----RECLOSER IN 1050 ONLY TAP OFF -- TAGS REMOVED 1350 // 412-68-OPEN CLAMP A VER/AWD L3/HFP XXXHFP AJB
845 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-09-18 02:36 | 2012-09-18 11:58 | 108 | 562 | 4056851 | 60696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" PHASE ONLY COD-108 PATROLLED LINE COULDN`T FIND ANYTHING AND SHOT IT CAME BACK OUT/ WILL WAIT TILL DAYLIGHT TO SEE THE LINES AND GET SOME HELPA PHASE ONLY COD-108 PATROLLED LINE COULDNT FIND ANYTHING AND SHOT IT CAME BACK OUT/ WILL WAIT TILL DAYLIGHT TO SEE THE LINES AND GET SOME HELP/// PATROLING// BROKEN CUTOUT ON 151-32// REPLACED CUTOUT//POWER IS RESTORED COD-108 ISO OCR 37820126000007 VER/HFP L3/HFP IDC XXXX
846 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-04-23 01:30 | 2016-04-23 04:40 | 645 | 190 | 4118681 | 60620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STEPDOWN POLE 69-280 ON FIRE//OPENED RECLOSER AT 0130 TO GET PUT OUT SAFELY//COD 645/. I HAVE STEPDOWN TRANSFORMER ISO AT POLE 69-280 69-281. CUTOUT BROKE DOWN LEFT HAND PHASE WITH BACK TO STATION. CLOSED RECLOSER IN ON POLE 69-282 AT 04:50 . SEND COPY OF THIS TO ENG ALSO POLE 69-280 DOES HAVE A SMALL HOLE BURNT BACK IN IT RELEASED BY CREW 074S11//AED//COD 645// VER/DBM L3/HFP XXXHFP AJB
847 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2019-10-06 15:42 | 2019-10-06 23:35 | 128 | 473 | 4102781 | 60544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 960260/// pole 39831098C04002 45-4 3arms 3cutouts. line crew required. Released by crew 078H09///crew on site making repairs///all repairs made///Tech wrote job for this pole///complete BR Released by crew 078H22/ ISO 39831098D00088/ COD 128 L3/HFP
848 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-07-09 02:30 | 2011-07-09 03:25 | 1098 | 55 | 4494901 | 60390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 0230 / CB OPENED DUE TO POLE FIRE AT POLE 1127-B-48. --- SDB / ISOLATED 3 PHASE BANK AT POLE 1127-B-48, CUT OUTS OPEN/TAPS LIFTED (SEE ORDER 4494971) --- SDB / 0325 / CB CLOSED. VER/SDB IDC XXXX
849 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-02-06 17:09 | 2008-02-06 17:45 | 1670 | 36 | 51588-1A | 60120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BURNT JUMPER ON POL.E 501-295 ABOUT FOUR SPANS OUTSIDE THE BUSSYVILLE SUB.,,, CONTRACTOR ON SITE,,, JUMPER HAS BEEN REPAIRED AND BACK ON AT 17:45 VER/KEP DEBBIE/CHECKED LOCAL OFFICE/B PHASE BURNT OPEN AT 388305010310....SEE OUTAGE 51588-1FOR ORIGINAL OUTAGE/THIS IS FOR OPENING BRK INTERRUPTING A AND C PHASES OPENED BY SCADA SUBTRACTED 89 WV CUSTOMERS FROM THIS OUTAGE IDC XXXX
850 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-03-31 13:56 | 2017-04-01 00:35 | 94 | 639 | 4602821 | 60066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BROKE DOWN AND BURNT POLE OVER HALF INTO,NEED 4 MAN LINE CREW, MANUAL POLE. OPENEING RECLOSERS ON 294-275 TO ISOLATE. RELEASED BY CREW 077H07///DKM/0046/ZIGGY REPORTS RESTORED RECL AT 0035/// VER/DKM /// PER VOICE RECORDER LINE FUSE OPENED ON POLE 37830294000110 & XFMR OPENED OR OPEN ALREADY NEED TO CHECK FOR TIMES & MORE INFO? = HFP AJB
851 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-11-12 08:15 | 2013-11-12 14:17 | 422 | 362 | 4030301 | 60058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE @ 182-63 RECLOSERS OPEN @ 0815 ON 182-B4-3567 RELEASED BY CREW 078S05/SWITCHING TO GET MAJORITY OF CUST BACK IN SERVICE/VEM. 0929 - CLOSED A & C RECL 3567 RESTORING 181 CUSTS// 0943 CLOSED BYPASS DISC TO B PHASE RESTORING 9 CUSTS/CREW WORKING ON POLE CHANGE/FETR ON REMAINING CUST 1430/VEM/APPROX 30 MINUTE OUTAGE TO REPAIR LOOPS/FETR ON ALL CUST 1430/VEM/ALL CUST RESTORED 1417/VEM RELEASED BY CREW 078H14 //VER/GAH L3/HFP IDC CHANGED TIME OFF FROM 0711 XXXX
852 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-01-25 07:20 | 2008-01-25 09:45 | 414 | 145 | 59667-1 | 60030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3103101//LOOP ON 600 AMP DISCONNECTS BURNT OPEN ATTEMPTING TO MAKE REPAIRS A PHASE//COD 414// VER/DBM PLC
853 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-07-31 22:55 | 2010-08-01 16:25 | 738 | 1050 | 59994-1 | 60010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 171-287 FELL DUE TO POLE FIRE WHICH WAS BEING WORKED ON ORDER 5998-1 INTERRUPTING CHAVIES/CHAVIES CKT. HOT LINE CLAMPS LIFTED AT POLE 171-4 AND ALL BUT 1 CUSTOMER RESTORED @ 0015 ON 8-1-10. CREW WILL MAKE REPAIRS STARTING AT 0800. RESTORED POWER AT 16:25//VER/CRB IDC XXXX
854 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-04-27 12:14 | 2010-04-27 18:48 | 400 | 394 | 52001-1 | 59888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW REQUIRED. OLD DEAD END INSULATOR HAS MELTED DOWN. I OPENED CUTOUT AND REMOVED HOT TAP ON POLE 336-7 AND ISOLATED TROUBLE. I AM GOING TO RECLOSER AT 335-305 WHICH IS OPENED AND CLOSE IT IN. I CLOSED RECLOSER IN AT 14:40 AND IT STAYED IN. THIS LEAVES ONLY 2 CUSTOMERS OUT OFF OF POLE 336-7. WE CUT TREES AND CLOSED LINE FUSE IN ON POLE 336-7 AT 18:48. RELEASED BY CREW 074S01//VER/CRB IDC XXXX
855 | Hazard | 3302703 | HAZARD | HAZARD | 2021-04-06 02:37 | 2021-04-06 06:45 | 241 | 248 | 4421701 | 59768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Seems a phase is out for most of the ckt// calls start past sw pole296-A4-595 // A phase on some spacer cable has burnt apart mid span at a spacer on pole 296-A3-715. Need a line crew, truck access. This is in the alley on main street next to the old Lees restaurant.//ISO 37830296A30715//Ph A only//cod 122//Seems a phase is out for most of the ckt// calls start past sw pole296-A4-595 // A phase on some spacer cable has burnt apart mid span at a spacer on pole 296-A3-715. Need a line crew, tr
856 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-03-29 18:30 | 2014-03-30 00:30 | 208 | 360 | H4535031 | 59699 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE IS OPEN//WILL HAVE TO OPEN OTHER 2 PHASES// B & C PHASES OPENED @ 1830 *** @ 1908 -HLC`S REM. AT POLLE 857-20 *RECL ON AT 1907 - NTA- GO TRACK NEEDED. BAD CUTOUT BURNED TOP OF POLE OFF... RELEASED BY CREW 076S01 REPAIRS COMPLETE. RESTORED @ 00:30. SH RELEASED BY CREW 07 VER/PDP IDC DUP TO OPEN RECLOSERS XXXX
857 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-04-21 19:22 | 2020-04-21 19:55 | 1805 | 33 | 4732261 | 59565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308401/gaj/1922/opened CB for crews to resag primary at 37830230C00005 on Carr Creek Ckt (double Ckt pole) FETR 2015 --- CB closed at 1955 restoring all customers
858 | Hazard | 3303902 | LESLIE | WOOTON | 2012-02-22 14:33 | 2012-02-23 16:00 | 39 | 1527 | 4480891 | 59553 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 333 STEPDOWN.CHANGED BAD STEPDOWN AND REPAIRED DOWN COND..ALL POWER RESTORED @ 16;00..P.HICKS CAN CLOSE MWL COD-39 ISO LF 37830341000093 VER/HFP L3/HFP AJB
859 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-09-28 21:04 | 2020-09-29 06:32 | 210 | 567 | 4504791 | 59535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C phase open at 37830179B00194 affecting 105 CC has locked out, patrolling lineC phase has locked out on pole 194, patrolling line. tried recloser, came back out, crew to come this way when they finish in Leslie Co found wire down at 37830178B00026 due to broken cross-arm FETR 0730 back on at 0632
860 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-08-17 21:07 | 2021-08-18 11:30 | 71 | 863 | 4092461 | 59533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | middle recloser (B phase) out on p-777-20..patrolled found nothing, rain and fog very bad conditions, closed center rec in at 2355, came back out, bad cutout on 801-6, isolating cutout..rec on 777-20 back on at 11.00.cutout on 801-6 back on at 1130.. Released by crew 076S01
861 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-19 14:06 | 2008-12-19 17:02 | 338 | 176 | 60467-1 | 59488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308401// B PHASE OUT ON POLE # 204-264, PATROLLING LINE // FOUND 2 PHASES CAME OFF INSULATORS // COD 612 - GOING TO HAVE TO OPEN OTHER PHASE WILL OUTAGE 560 ADDITIONAL CUSTOMERS// OPENED OTHER PHASE @ 1615 -- 3308401// B PHASE OUT ON POLE # 204-264, PATROLLING LINE, FOUND PHASE OFF INSULATOR ON POLE 204-232. TOOK ALL POWER OFF AT 16:15, RESTORED ALL AT 17:02 PLEASE CLOSE ORDER...THANKS HFP VER/KEP MADE DUP L3/KEP IDCC CNT612 ALSO PH A NOT B XXXX
862 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-04-01 11:48 | 2011-04-01 14:55 | 475 | 187 | 61090-1 | 59437 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 3-PHASE RECLOSER ON POLE 194-115 IS OPENED. WE ARE PATROLLING LINE NOW. GUY WIRE HAS BROKEN AND LET PHASE WIRE AND NEUTRAL SAG TOGETHER . WE ARE GOING TO TAKE HOT TAP OFF AT POLE 169-12 AND ISOLATE FAULT. WE WILL THEN CLOSE RECLOSER AT 194-115. THIS WILL LEAVE 1 CUSTOMER OUT.// IS OPENED. WE ARE PATROLLING LINE NOW. GUY WIRE HAS BROKEN AND LET PHASE WIRE AND NEUTRAL SAG TOGETHER . WE ARE GOING TO TAKE HOT TAP OFF AT POLE 169-12 AND ISOLATE FAULT. WE WILL THEN CLO//VER/CRB IDC DCMT XXXX
863 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-05-03 15:54 | 2009-05-03 20:45 | 243 | 291 | 64345-1 | 59273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29637783 /// POLE 38831098B00692 OPENED SWITCHES AT 16:55, A & C PHASE OF RECLOSER OUT 267 CUST// WR # 29637783 /// POLE 38831098B00692 OPENED SWITCHES AT 16:55,CLOSED AT POLE 606 AT 17:05 ... ALL WORK COMPLETE / GXJ REST BACK ON @ 2045 L3/HFP IDC XXXX
864 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-15 11:30 | 2018-02-15 15:42 | 577 | 252 | 4843231 | 59224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ETA: 1130//insulator failed on pole 649-196 and phase burned down//also off insulator on 649-30///right hand recloser locked out on 649-202///crew enroute//will have to open other two reclosers when crew arrives to make repairs//ETA: 1130//insulator failed on pole 649-196 and phase burned down//also off insulator on 649-30///left hand recloser locked out on 649-202///crew enroute//will have to open other two reclosers when crew arrives to make repairs//opened other two at 14:05ETA: 1130//insula
865 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-06-27 18:46 | 2016-06-27 23:07 | 533 | 261 | 4488851 | 59178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD INSULATOR RELEASED BY CREW 077S01 VER/KEP
866 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-07-30 17:19 | 2009-07-30 20:45 | 335 | 206 | 56943-1 | 59170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO 1125-199LOOKS LIKE LOOP BURNT INTO AND LAYING DOWN ON EQUIPMENT. I HAVE RECLOSER OF LINE AND GROUNDED.//COD 335// VER/DBM IDC XXXX
867 | Hazard | 3303902 | LESLIE | WOOTON | 2012-07-22 13:29 | 2012-07-22 15:30 | 489 | 121 | 4794561 | 59169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT COD-489 ISO OCR 37830414000064 VER/HFP L3/HFP IDC XXXX
868 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-07-31 01:30 | 2017-07-31 04:45 | 303 | 195 | 4208481 | 59085 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | OUTAGE FOR T-LINE TO REPLACE BROKE CROSSARMS OFF @ 0130 ON @ 0445 VER/ARN SJGC MCCDIS, CNT110
869 | South Williamson | 3200301 | BELFRY | BELFRY | 2010-01-21 22:09 | 2010-01-22 12:42 | 567 | 873 | 57520-1 | 59038 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DUE TO LOCATION OF CONDUCTOR THAT IS DOWN WILL WORK FIRST THING IN THE MORNING OF 1/22RELEASED BY CREW 080S01. TRANSMISSION LINE GOT ACROSS DIST CKT & BURNT CONDUCTOR DOWN//STS WR# 33549547 //ISSUED HOLD ORDER TO J REED/ //VER/GAH IDC XXXX
870 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-02-18 07:00 | 2009-02-18 07:46 | 1283 | 46 | 63769-1 | 59018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001202 // DUE TO A BAD CROSSARM THE HOWARD COLLINS / 29TH ST 12KV CB E HAD TO BE OPEN TO MAKE REPAIRS. IDC NO ONE OUT TILL OPEN OF BREAKER IDC BAD CUTOUT CAUSED XARM FIRE XXXX
871 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-03-29 19:04 | 2018-03-30 11:09 | 282 | 965 | 4151851 | 58958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED RECLOSER ON POLE 37830344000144 @ 2211//COD NOW 8//CALLED DUTY SUPERVISER(JEFF COMBS) WILL HOLD TILL AM//ARCOS 1 NE AND 2 MEN OUT @ 0800 //NEEDS 2-19.9 CUTOUTS 2 FIBERGLASS T BRACKETS AND 1 19.9 ARRESTER//BAD CUTOUTS ON TRANS AND L/F ON POLE 37830344000017 repairs made and power restored at 1109
872 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-07-08 15:00 | 2016-07-08 19:25 | 428 | 265 | 4564381 | 58898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT @ POLE38821138C00121CLEARED,ADDRESS=52636 RT 194,CUST. STILL OUT.CLOSED RECLOSER @ 19:25 VER/CRB/// VER/DKM AJB
873 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-08-28 15:56 | 2013-08-28 18:20 | 699 | 144 | 4715831 | 58836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC OPEN ON 478-90 PAT. LINE LRM REC IN @ 17:20 STILL HAVE TAP @ 503-237 OUT LI FUSE CLOSED @ 18:20 RELEASED BY CREW 078H06//COD 856 VER/HFP L3/HFP IDCC CDC83 XXXX
874 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-10-10 13:57 | 2019-10-10 15:25 | 749 | 88 | 4128671 | 58814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrestor pole 39831123D16137/ DA load xfer/DOL961566 Released by crew 078H04
875 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-02-05 04:29 | 2022-02-05 11:25 | 141 | 416 | 4444981 | 58656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | looks like cutout gate burnt into on B phase, had to open A&C phase to replace cutouts, opened at 10:29 to 11:25 restored
876 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-08-22 19:11 | 2014-08-22 23:02 | 253 | 231 | 4406941 | 58443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 45-2 XFMR BANK POLE BROKE AT GROUND LINE DURING STORM. TAG PLACED TO DDC ON 809-429 ISOLATED HOT LINE CLAMPS AND PLACED TEMP GROUNDS. CREW ENROUTE.// B PHASE ONLY ON RECLOSER 785-12145-2 XFMR BANK POLE BROKE AT GROUND LINE DURING STORM. TAG PLACED TO DDC ON 809-429 ISOLATED HOT LINE CLAMPS AND PLACED TEMP GROUNDS. CREW ENROUTE. FOUND WIRE DOWN ON 809-418. OPENED GOAB ON 809-819 TO ISOLATE.45-2 XFMR BANK POLE BROKE AT GROUND LINE DURING STORM. TAG PLACED TO DDC ON 809-429 ISO HO VER/ARN AJB CNT
877 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-01-02 19:44 | 2014-01-03 09:47 | 422 | 843 | 4220191 | 58425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 988-A-171 AT STEPP BR HAS THE PRIMARY OFF OF THE INSULATOR AND TRANSFORMER CUTOUT RISER IS BURNED OFF. TROUBLE IS ISOLATED AT POLE 988-A-24. CAN USE BUCKET. WILL HAVE TO FLAG ROAD TO INSTALL CUTOUT AT POLE 988-A-24 TO PROTECT THIS TAP. THIS IS ACROSS THE ROAD FROM BIG CREEK FREEWILL BAPTIST CHURCH. KYDDC TAG BE REPLACED BY CREW TAG AS NEEDED.REPLACED CUT OUT AND TIED IN CONDUCTOR VER/CRB L3/HFP IDC XXXX
878 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-02-05 20:41 | 2016-02-05 21:38 | 1023 | 57 | 4680081 | 58311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW MAKING REPAIRS NOW OFF 2041 1023CC ON @ 2138 1293 CC // VER TIMES PER DOL & SCADA = VER/HFP L3/HFP AJB
879 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-02-22 00:15 | 2013-02-22 01:52 | 601 | 97 | H4838861 | 58297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BURNT DOWN AT REC. POLE 37830272B40477 (PH A) 497 CC. OPENED RECLOSERS AT POLE 477 AT 0015. OUTAGING AN ADDTL 601 CCWIRE BURNT DOWN AT REC. POLE 37830272B40477 , POWER RESTORED AT 01:52 VER/SDB IDC XXXX
880 | Hazard | 3310502 | HADDIX | CANOE | 2022-11-30 08:57 | 2022-11-30 14:07 | 188 | 310 | 4205901 | 58280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | reclosure is open on pole 51-109, no grounds or tags placed . insulator has came off the pole top pen on pole 75-107 pole is manual. need 19.9 insulator and line crew. Released by crew 077H24..repairs comp
881 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-04-07 11:53 | 2018-04-07 17:12 | 245 | 319 | 4199081 | 58157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER 37830402C00418 @ 1153//COD 245// NO OUTAGE TILL THEN//CLOSED RECLOSER @ 1209//UPTO SWITCH ON POLE 37830378D00003//POLE FIRE @ POLE.. 37830378D00008//OPENED RECLOSER 37830402C00418 @ 1153//COD 245// NO OUTAGE TILL THEN Released by crew 077S12..repares made and all power restored @17:12 Released by crew 077H09//CLOSED SWITCH 37830378D00003 @ 1712 L3/HFP
882 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-07-25 08:19 | 2022-07-25 10:41 | 409 | 142 | 4571831 | 58078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Reclosers at 794-D-352 open affecting 409 CC, report of TR fire, line servicer enroute /1028/gaj/ no problem found, possible Recloser problem servicer on site attempting to bypass OCRs and restore all customersbeen out multiple times in last few weeks//not finding anything//bypasse per Tom Mamming//please sent to Bobby Tackett, Steve Ray and Tom Mamming to have this checked//restored at 10:41//complete//em
883 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-01-30 12:52 | 2013-01-30 15:50 | 326 | 178 | 4758641 | 58028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CENTER PHASE OUT 102 CUSTWIRE CAME OFF POLE LOCKED OUT REC AT 53-143 NEED 2 MEN NO TRUCK COD-102 ISO OCR 37820053000143 VER/HFP L3/HFP IDC THIS IS A 3 PH RECLOSER AND CUSTOMERS OUT ON ALL PHASES CHANGED COUNT FROM 102 XXXX
884 | South Williamson | 3411401 | DEWEY | INEZ | 2009-05-26 19:46 | 2009-05-26 23:55 | 233 | 249 | 53669-1 | 58017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP PATROLLING LINE/"A" PHASE ONLY COD-233 PATROLLING LINE, BAD ARRESTER, POLE#697-A-3 L3/HFP IDC XXXX
885 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-08-04 00:28 | 2015-08-04 06:12 | 178 | 344 | 4972901 | 58008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE C RECLOSER ONLY OPEN ON 810-782.//COD 178 @ THIIS TIME//PHASE C RECLOSER ONLY OPEN ON 810-782. XFMR CUTOUT BROKE DOWN AND BURNED CROSSARM OFF. CREW ENROUTE TO ASSIST.//COD 178// OPENED UP SWITCHES AT POLE 834-A-15 INTERRUPTING 117 MORE CUSTOMERS AT 0433.// SEE DUP H4972901 FOR 117 CUST - VER TIMES PER VOICE REC VER/HFP L3/HFP AJB
886 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-09-02 17:33 | 2022-09-02 18:56 | 698 | 83 | 4831781 | 57934 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 1235213//T-LINE OUTAGE// 1733-1856
887 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2018-07-08 00:36 | 2018-07-08 05:44 | 443 | 298 | 4750181 | 57931 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B & C ph HENDRIX DOWN @ POLE 978-119.have isolated & grounded @978C10127 & 978C10117 .waiting on crew Released by crew 074S04
888 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-01-05 03:33 | 2019-01-05 11:09 | 127 | 456 | 4630651 | 57912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole1109/151 recloser pole burnt off at bypass /truck /no flag just past smith br/1400 fetr/jim/send to jeff combs Released by crew 077S06replaced pole and restored power at 1109
889 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-09-25 10:10 | 2020-09-25 14:18 | 234 | 248 | 4494801 | 57825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Bad ocr on 223B/1186 closed on 223B/9 at 14:15 closed ocr on 223B/2 at 14: 18 on 223B/1186 by passed ocr and isolated ocr and tagged to KY. DDC Released by crew 077S03
890 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-09 10:25 | 2010-12-09 19:21 | 118 | 536 | 64774-1 | 57770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 500 KVA STEPDOWN TRANSFORMER. A PHASE// COD 118 // === OPENED B PHASE AT 13:45 //COD 118 + 77 //== POWER RESTORED UP TO POLE 246-439 AT 16:35.//VER/CRB IDCC DCMT, CDC92 XXXX
891 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2019-05-29 16:00 | 2019-05-29 19:32 | 272 | 212 | 4367441 | 57664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire burnt down crews on site..///restored at 1932wire burnt down crews on site.. repairs made back to normal L3/HFP
892 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-03-06 06:29 | 2012-03-06 07:08 | 1478 | 39 | 4555271 | 57642 | TRANSMISSION STATION | EQUIPMENT FAILURE | CAPACITOR | DE-ENERGIZED STATION DUE TO FIRE IN STATION // 46KV CAP BANK FAILED AT FORDS BRANCH STATION // IDC XXXX
893 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2010-04-26 19:25 | 2010-04-26 23:46 | 599 | 261 | 51659-1 | 57585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BAD BURNED TOP OF BUCK POLE OUT/ CUT LOOPS ON POLE 401-189 TO ISOLATE/ FEEDER CB CLOSED AT 2008 RESTORING 453 CUSTOMERS //2328 OPENED FEEDER TO CLOSE LOOPS /. AT 23:46 CLOSED STATION CB / SEE ALSO H51659-1 VER/LDA IDC XXXX
894 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-01-25 17:06 | 2014-01-26 00:01 | 219 | 415 | 4312681 | 57529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***HOLD TAG PLACED ON SWS @ 1011-B4-528 FOR S RAY /// STEVE RAY & R WORRIX & J GARRETT & D LEWIS///OPENED RECL @ 1706// OPENED SWS @ 1011-528// CLOSED RECL @ 1727 // CLOSED SWS AT POLE 1011-528 @ 2151 // TR AT POLE 1011-523 REMAINS ISOLATED (1 CUST)// RESTORED TR POLE 1011-523 @ 0001 RELEASED BY CREW 074S06 //VER/GAH L3/HFP IDC XXXX
895 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-07-23 18:15 | 2010-07-23 19:27 | 799 | 72 | 56108-1 | 57528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD-402 SINGLE PHASE CONDITION ON THE US 60 WEST 12KV CKT. 402 CC . CREWS PATROLLING CKT. CREWS FOUND CENTER PHASE OPEN AT SET OF JUMPERS AT POLE 162-6084, TROUBLE IS IN THE CLEAR AT THIS TIME AND PHASE A-C CAN REMAIN ENERGIZED UNTIL CREW IS PREPARED TO MAKE REPAIRS , WHEN REPAIRS BEGIN PHASE A-C WILL BE OPENED UNTIL REPAIRS R MADE. ** ALL WORK NTA .. HOOKS AND HANDS. VER/KEP L3/KEP IDC THIS IS ACTUALLY THE SECOND OUTAGE XXXX
896 | Whitesburg | 3409503 | BURDINE | JENKINS | 2022-02-25 04:50 | 2022-02-25 17:47 | 74 | 777 | 4542971 | 57498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | related to 4542511 // B phase hot clamp broke on pole 37830358D00319///to be worked with order 4542511//74
897 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-08-18 03:39 | 2013-08-18 05:45 | 455 | 126 | 4675471 | 57330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | REC. ON 38831126B10518 POEN // WILL PATROL/CONTROL IS BAD/// BY-PASSED REC//TAGGD TO DDC// POWER IS RESTORED. CC = 455 VER/HFP L3/HFP IDC XXXX
898 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-02-24 18:37 | 2020-02-25 01:03 | 148 | 386 | 4429041 | 57128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED @ 1837//opened l/f on pole 38830278000010//cod 148//no outage till then//,,,3 phase pole38830278000021burnt off ,,spoke with luke mcoy ,,gonna try to lower everything and get power restored,,,CREW REQUIRED ,,,,NO TRUCKS Released by crew 078S05 crew on site FETR 00:30 CHANGED pole out LRM. L3/HFP
899 | Hazard | 3303903 | LESLIE | HALSFORK | 2021-03-18 17:10 | 2021-03-18 20:00 | 334 | 170 | 4349191 | 56780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout// restored @2000
900 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-02-05 08:30 | 2019-02-05 11:46 | 288 | 196 | 4755121 | 56448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | THIS REPLACES ORDER 4754711 ¦¦ NO OUTAGE UNTIL SW OPENED ON POLE 37830236000002 ¦¦ cross arm insulator on pole 261-82 failed and burnt arm into and top of pole maybe be able to frame down..opened new switches installed on pole 236-02 @ 8:30..will need 10ft crossarm and cross arm insulator and line crew with big bucket to make repairs..ALL ON @ 1146
901 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-12-23 00:50 | 2017-12-23 03:35 | 638 | 165 | 4665181 | 56298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT 1130-195 TOOK RECLR OUT.ISOLATED FAULT,CLOSED RECLR Released by crew 074S06
902 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-08-18 02:52 | 2012-08-18 14:23 | 333 | 691 | 4948801 | 56295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 141-190 POLE BROKE OFF CUT LOOPS ON POLE 141-93 RELEASED BY CREW 078S08 HOLD ORDER REQUIRED TO MAKE REPAIRS - NICK MCCANN, VERNON MULLINS, MIKE PHELPS & RICK MORGAN TO ASSIST FETR// 13:00 JEH JEH/REPAIRS COMP. ALL POWER RESTORED @ 14:30 JEH IDC DA SCHEME SAVED 615 CUSTOMERS XXXX
903 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-11-10 15:38 | 2020-11-10 17:16 | 574 | 98 | 4658001 | 56252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CB tripped while on HLT/ DOL 1068385 Released by crew 078H16///cutout at pole 45-C4-5732 failed and burned crossarm in two///This is the order for the CB that locked out///portion of 47th St-39th St ckt currently abnormally fed from Ashland-29th St ckt
904 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-06-17 21:09 | 2009-06-18 00:19 | 296 | 190 | 50687-1 | 56240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | LOOP BURNT OPEN ON ONE PHASE ONLY, LOOP BURNT OPEN WHEN SWITCH FAILED WHILE FIELD SWITCHING VER/ARN
905 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-01-20 07:48 | 2008-01-20 15:40 | 208 | 472 | 57891-1 | 56231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NO. 4 COPPER WIRE DOWN ONE SPAN 1 PHASE /C PHASE COD-114/0845 RESTORED 20 CUST UP TO POLE 49 OPENED SWITCH AT 49, 366 CUST ALL 3 PHASES TO MAKE REPAIRS ON PLE 71-197/MADE REPAIRS TRIED SWITCH AT 1115 CUTOUT BURNT UP ON C PHASE AND OPENED RECLOSER POLE 72-383 ON B&C PH COD-311 REPAIRED CUTOUT TRIED RECLOSER AT 1210 IT CAME OUT OPENED RCLOSER POLE 70-151 AND 47-6 TO SECTIONALIZE,B PH RECLOSER POLE 383 WILL NOT STAY IN BYPASSED RECL RESTORED AT 1 IDC PHASEING IS CAB PH B OUT INITIALLY XXXX
906 | South Williamson | 3411401 | DEWEY | INEZ | 2010-05-02 04:17 | 2010-05-02 10:50 | 143 | 393 | 53640-1 | 56199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOING TO LIFT HOT TAP ON POLE696-99 ISOLATING RECLOSERS. POLE BURNT OFF GOING TO CALL ACREW.CREW ON THEIR WAY IDC XXXX
907 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2017-09-18 11:12 | 2017-09-18 15:50 | 603 | 278 | 4370561 | 56178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | DOL 772292 // SCADA INDICATES FEEDER L/O @ 1112 // SWITCHES BURNT UP ON POLE 38830046B11075 //600A DISC. SWITCHES BAD @ 46-B1-1075 RELEASED BY CREW 078S07//COD 1939 // CLOSED ASHL-29TH CB AND RESTORED 516 CC @ 1214 // CLOSED 47TH-49TH CB @ 1229 AND RESTORED 1336 // VER/DBM L3/HFP XXXHFP SJG
908 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2010-09-11 10:12 | 2010-09-11 15:09 | 307 | 297 | 65453-1 | 56166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3-PHASE RECLOSER ON 167-428 IS OPEN. PATROLLING LINE NOW. CROSSARM IS BROKEN ON 165-4 AND PHASE WIRE HAS FALLEN ONTO ANOTHER WIRE. I OPENED GOAB ON 166-227 AND CLOSED RECLOSER AT 167-428 BACK IN AT 11:37. FAULT IS ISOLATED. DALE HAMILTON IS ON THE WAY TO HELP. AT 14:02 WE CLOSED GOAB AT 166-227 IN. LEAVES 3 CUSTOMERS OFF UP IN COON HILL. WE HAVE A HOT TAP LIFTED AT 165-4. WIRE IS DOWN UP IN HOLLOW. WE ARE GOING TO CUT IT IN THE CLEAR. VER/HFP L3/HFP IDCC CNT104, STP MISSING XXXX
909 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-04-08 20:11 | 2022-04-09 02:15 | 228 | 364 | 4742651 | 56098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 2 FROM BEGINNING OF OUTAGE//OPENED RECLOSER 38830876B00368 TO ISOLATE BROKEN POLE 38830876D00395// OPENED OCR @ 2210/pole burnt off
910 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-09-30 01:07 | 2011-09-30 20:20 | 71 | 1153 | 4933241 | 55995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | TREES LAYING ON LINE WHEN WIND BLOWPOWER ON UP TO POLE 24-658T, U.G PRIMARY OUT RELEASED BY CREW 074S05 PADMNT X-FMR BAD AT 1089 CABLE BAD FROM 1089 TO 1091 WILL LOCAT. AND SPLICE TIME ON 20;20 R RAY //VER/CRB IDC XXXX
911 | Pikeville | 3421001 | BREAKS | CITY | 2010-01-05 09:47 | 2010-01-05 10:48 | 917 | 61 | 61058-1 | 55937 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRANSMISSION OUTAGE// VER/DBM IDC XXXX
912 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-08-05 18:31 | 2016-08-06 11:50 | 911 | 1039 | 4740151 | 55848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SCADA INDICATED THE HAZARD 34KV CB R AT BONNYMAN LOCKED OUT// SERVICER ENROUTE// REPORT OF WIRE DOWN AND TRANSFORMER FIRE//TOM POLE 223-C-5 TOP BROKE OUT// WORKING TO ISOLATE FAULT AND RESTORE ADDITINAL CUSTOMERS FROM ALTERNATE SOURCE/TOM ARCOS JEFF COMBS, 3 MAN CREW (NO SPECIFIC CLASS), FLAGGERS @ 0730. //ALL CUSTOMERS RESTORED 8/6/16 @ 1250//LOOPS STILL OPEN/TAGGED @ 223-C-354//TO RETURN NORMAL 8/8/16//SEE DOL 677456// AJB
913 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-02-21 09:55 | 2016-02-21 13:10 | 353 | 195 | 4742751 | 55811 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. ON POLE 143C-411 IS OPEN.WILL PATROL////FOUND BAD CUTOUT ON POLE 142-135//ISO @ POLE 142-113 //CLOSED REC @ 1233// REC. ON POLE 143C-411 IS OPEN.WILL PATROL////FOUND BAD CUTOUT ON POLE 142-135 WILL LIFT HOT TAP ON POLE 142-113 TO MAKE REPAIRS.//..REPAIRS MADE CLOSED BACK IN @ 13:10.. VER/CRB L3/HFP XXXHFP AJB
914 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-07-02 09:06 | 2014-07-02 11:18 | 421 | 132 | 4182381 | 55572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 0906 / FEEDER BREAKER OPENED TO ISOLATE POLE FIRE AT 988-B-6. GOING TO SCAB POLE FOR NOW. JOB IS GOING TO BE WROTE TO REPLACE THE POLE LATER. RELEASED BY CREW 079S02 VER/SEF L3/DKG AJB
915 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-01-05 06:06 | 2016-01-05 08:30 | 384 | 144 | H4585671 | 55296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE DOWN BETWEEN POLE#448-122 AND 448-299 COD-189 /OPENED ALL 3 RECLOSERS 448-365 AT 0606 TO ISOLATE FAULT AND MAKE SAFE OUTAGED ADDITIONAL 384 CUSTOMERS/CREW ENROUTE/ POWER RESTORED AT 08:30 RELEASED BY CREW 075H03 VER/CRB AJB
916 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-11-11 13:06 | 2009-11-11 22:30 | 98 | 564 | 60380-1 | 55272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQ # 32635074 // PLEASE UPDATE THE FETR...THANKS // 19.9 CUTOUT FAILED AND BURNED POLE 37830318A00124 INTO CALLING FOR CREWS TO REPLACE MANUEL POLE RELEASED BY CREW 077S04 CREW AT JOB EST TIME 22:00 WILL UP DATE IF NEEDED W.MELTON COMP. 11/11/09 W.MELTON//COD 98 IDCC TOF1231 XXXX
917 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2018-04-15 18:41 | 2018-04-16 00:03 | 323 | 322 | 4231241 | 55217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Pin insulator bent over on pole 39831124A41504 causing arcing. Opened switches on 39831124A41523 to isolate. Closed recloser on 39831124B38178 at 2215-crew req-ds041518 Released by crew 078S01 Released by crew 078H20
918 | Hazard | 3309302 | VICCO | JEFF | 2018-12-28 07:55 | 2018-12-28 12:41 | 224 | 286 | 4607101 | 55034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON HIGH SIDE OF STEPDOWN & ONE ON RECLOSER - ONLY CENTER PHASE OUT INITALLY B PHASE (119 CUST) // OPENED A&C PHASES (105 CUST) TO REPLACE ALL CUTOUTS OFF @ 0921 ON @ 1241 L3/HFP
919 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-05-21 15:47 | 2014-05-21 18:42 | 376 | 175 | 4730371 | 54964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PATROLING LINE/ STRINGING BLOCK FAILED WHILE PULLING WIRE AT POLE 250-26 /GOT RECLOSER POLE 226-15 ISOLATED SO WE CAN CUT ATREE OFF AT 1659 HRS TAGGED TO LINKOUS/ RESTORED CB AT 1800 UP TO REC 226-15 258 CUST/PATROLING LINE/ STRINGING BLOCK FAILED WHILE PULLING WIRE AT POLE 250-26 /GOT RECLOSER POLE 226-15 ISOLATED SO WE CAN CUT ATREE OFF AT 1659 HRS TAGGED TO LINKOUS/RECLOSER BACK ON AT 1842 HRS POLE 226-15PATROLING LINE/ STRINGING BLOCK FAILED WHILE PULLING WIRE AT POLE 250-26 /GOT RECLOSER VER/KEP AJB
920 | South Williamson | 3411401 | DEWEY | INEZ | 2011-04-13 04:31 | 2011-04-13 09:00 | 352 | 269 | 56141-1 | 54845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE PULLED OUT OF SLEEVE AT POLE 770-24//NEUTRAL DOWN AT POLE 770-154// CAN OPEN GOAB AT POLE 769-94 AND RESTORE SOME CUSTOMERS/ --- SDB / 0609 / RECLOSER AT POLE 744D2-527 CLOSED, 233 CUST RESTOREDPHASE PULLED OUT OF SLEEVE AT POLE 770-24//NEUTRAL DOWN AT POLE 770-154// CAN OPEN GOAB AT POLE 769-94 AND RESTORE SOME CUSTOMERS/ --- SDB / 0609 / 233 CUST RESTORED//RESTORED REMAINING CUSTOMERS AT 9:00//HAVE EVERYTHING WITCHED TO NORMAL//COMPLETE//EM RELEASED BY CREW 079S01 IDC XXXX
921 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-09-04 13:43 | 2019-09-04 19:20 | 191 | 337 | 4979651 | 54843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER PHASE OUT (B PHASE - 27 CUST)solid cutout bad burned crossarm into. p-38830875A00245solid cutout bad burned crossarm into. p-875-245.open 2other rec at 14..20..isolated and tagged for myself//closed rec @ 1853 upto SW 38830875A00245//COD NOW 65//cut arrester in clear on p-875-268.switches back in on 245 at 19. 20 Released by crew 076S01//MADE AED FOR ARRESTER L3/HFP
922 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-09-06 08:03 | 2011-09-06 13:52 | 157 | 349 | 4830081 | 54793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PH RECLOSER OUT 224 COD// WILL OPEN OTHER 2 WHEN READY// #4 COPPER DOWN ON CENTER PHASE . HAVE CREW IN ROUTE PULLED OTHER 2 PHASES OFF @12:55 BACK ON @13:52 SEE DUP H4830081 VER/HFP L3/HFP IDC HAD SAFETY MEETING AND SEVERAL ON REST PERIOD, CHANGED COUNT DUE TO MANY MISSMAPPED CUSTOMERS IDC XXXX
923 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-09-25 09:31 | 2009-09-25 22:10 | 72 | 759 | 62202-1 | 54648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE C FUSE BLOWN ONLY // COD 72//WR#31898687 // POLE-TOP BURNT OFF AT POLE#117-76 // 117-76 BURNT OFF// RELEASED BY CREW 078H07// VER/CRB IDCC CNT150 XXXX
924 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-11-29 04:07 | 2015-11-29 09:50 | 184 | 343 | 4490681 | 54502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BURNT OFF 3 PHASE POLE 976-4 NEED 8 FT ARM AND BRACES CUTOUT AND BRACKET /CUTTING LOOPS ON 976-3 /TAGGED TO YOUNGMAN NO GROUNDS INSTALLED/POLE 1000A46 BACK IN AT 0625 HRS TO 976-3 RELEASED BY CREW 078S03.. CREW ON SITE TO MAKE REPAIRS ETR 11:00.. INSTALLED 3 300 AMP SOLID BLADES ON POLE 976-3.. SOLID BLADES CLOSED IN AT 09:50 RESTORING ALL CUSTOMERS.. RELEASED BY CREW 078H22//MADE MDC TO SHOW SOLID BLADES// VER/CRB
925 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-01-02 18:03 | 2020-01-02 22:27 | 818 | 264 | 4205131 | 54432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c phase fuse out on pole 37830174A00220. patrolling line // failed cutout on 37830174A00220, will need to take outage to replace cutout, made up solid on pole //at 2203 opened sectionalizer on 37830174C14426 to make safe to replace cutout //cod 145 (+673) //closed @ 2227 // L3/HFP
926 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2015-07-05 20:03 | 2015-07-06 05:53 | 96 | 590 | 4725851 | 54324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DELINDA BORDEN ALL OUT LINE FUSE OUT ON POLE 478-501 NEED LINE CREW. CREW WORKING TO SECTIONALIZE AND TRACK DOWN THE PROBLEMDELINDA BORDEN ALL OUT LINE FUSE OUT ON POLE 478-501 NEED LINE CREW. RELEASED BY CREW 078S01 RELEASED BY CREW 078H19 VER/KEP AJB
927 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-12-11 21:43 | 2008-12-12 14:10 | 55 | 987 | 57033-1 | 54285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER ON SITE CONFIRMING WIRE DOWN ON HILL.. OPENING RECL. AT 1040-22GOT WIRE DOWN UP ON SIDE OF HILL, NEED FOUR MEN AND 6A WIRE AND SLEVES. THE POLE NUMBER IS 1040-39. WERE THE WIRE IS DOWN THERE IS OLD BACKHOLE LAYING ON ITS SIDE RELEASED BY CREW 077S05 JAMES SUMMER RADIO # IS 3665//3310501//COD 55// VER/DBM IDC XXXX
928 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-10-31 23:06 | 2009-11-01 02:00 | 521 | 174 | 54133-1 | 54266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411801// 3P RECL 1058-347 OPEN,OPEND 3 SWITCHES ON 1011-528,CLOSED IN TO THAT POINT.WILL CHECK OUT POLE FIRE CALL ON WOLF BR/MADE REPAIRS,LAST CUST ON AT 02:00 IDCC CNT718, TON0138, STP MISSING TON0200 XXXX
929 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-09-19 11:52 | 2019-09-19 12:36 | 1229 | 44 | 4035681 | 54076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ound A phase off angle pin on crossarm at 2029 E Main st, need crew to make repairs, is in station zone, traffic control as well Released by crew 078S06/broke b phase insulator opened 1073-3554@11:52 on time 12:36 all insulation replaced on pole Released by crew 078Q09 L3/HFP
930 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-08-01 01:34 | 2014-08-01 07:14 | 159 | 340 | 4315691 | 54012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "B" PHASE ONLY COD-159/ISOLATING TO SECTIONALIZE/CALLED FOR CREW TO HELP/B PHASE ONLY COD-159/ISOLATING TO SECTIONALIZE/CALLED FOR CREW TO HELP/////BAD CUTOUT POLE 1007-8,T MCCOY REPLACED IT.HE ALSO IS CLOSING RECLR 1007-167 AND SWITCH ON 1007-13 RELEASED BY CREW 074S06 VER/SEF VER/DKG L3/DKG AJB PH B.
931 | Hazard | 3310502 | HADDIX | CANOE | 2013-04-12 08:43 | 2013-04-12 16:17 | 244 | 454 | 4002901 | 54004 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | AT 10:45 RESTORED POWER TO POLE # 169-315 RELEASED BY CREW 077S10//COD 244// VER/DBM IDC XXXX
932 | Pikeville | 3407101 | TOPMOST | DEMA | 2021-07-24 08:29 | 2021-07-24 13:40 | 766 | 288 | 4951001 | 53954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 1134232///Pole 37830138000028 fell/Need 45 foot pole two 8ft arms and 6 angle pins and insulators.// Opened swithches @ 37830161C00004 and tagged to DDC//Opened viper @ 138-99 and tagged to DDC.//Closed switches on 89-58 @ 10:03//Repairs made and closed switches @ 161-4 @ 13:04.// Closed viper on pole 138-199 @ 13:40 Released by crew 074S11
933 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2019-10-24 08:43 | 2019-10-24 10:47 | 435 | 124 | 4191231 | 53940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew on site LRM all pwr restored 10:47 please send to justin LRM/ B Phase Cutout cracked on transformer bank at pole 39830878000029 L3/HFP
934 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2016-06-27 16:55 | 2016-06-27 22:07 | 342 | 312 | 4487381 | 53904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 125-18 FAULT POLE/OPENED 125-24/ CLOSED CB AT 1807 RESTORED 220CC/125-24 TAGGED TO J REED/ RELEASED BY CREW 074S02.MADE REPAIRS..RESTORED AT 22:07 RELEASED BY CREW 079H07 VER/KEP
935 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2017-06-12 18:15 | 2017-06-12 18:56 | 1314 | 41 | 4954681 | 53874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 749066//SCADA INDICATES FEEDER L/O AT 1815//POLE 1099-161 BAD HOT TAPS//CLOSED CB @ 1856//COD 1314// VER/DBM SJGC TON19:00 PER DOL
936 | South Williamson | 3411401 | DEWEY | INEZ | 2016-12-01 19:34 | 2016-12-02 12:45 | 317 | 1031 | 4159731 | 53701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SCADA - RECL 527-D2-527 LO @ 1930//COD 317//OPENED SWS 769-C-94 TO ISO POSS FAULT//CLSOED RECL "-527 @ 2121//TOP OF POLE 770-A-25 BROKE OFF LAYING ON GROUND///NO TRUCK//CAN GET TRACK MACHINE TO POLE,ROAD RECENTLY MADE DOWN IN HERE WHEN ELLIOT CREWS REPLACED A POLE//NEED 2 8FT ARMS,6ANGLE PINS,6 PIN INSULATORS,CENT PHASE DOUBLE DEADENDED//HOLD ORDER REQD BUT NOT ISSUED YET.SCADA INDICATES RECLOSER 527-D2-527 LOCKOUT @ 1930//COD 317//OPENED SWS 769-C-94 TO ISOLATE VER/KEP L3/HFP XXXHFP AJB
937 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-11-11 15:00 | 2009-11-11 18:40 | 244 | 220 | 61844-1 | 53680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP WR # 32638872 //THE RIGHT SIDE PHASE OUT ON POLE 37830071000049 40T FUSE.....DAH ENTERED MD B PHASE OUTAGE RELATED TO ORDER 61705-1 WHICH OCCURED AT 1500. 135 CUSTOMERS - ALL RESTORED @ 1715 L3/HFP IDC CHANGED FROM ERROR FIELD, LOOKS LIKE ONE PHASE RECLOSER AND FUSE UPSTREAM HERE AT 71-49 OPENED XXXXX
938 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-05-23 09:05 | 2011-05-23 19:08 | 89 | 603 | 4139961 | 53667 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASE RECLOSERS OPEN ON 963-C-213....BAD CUTOUT ON PHASE A ON POLE 963-C2-29....ALSO TREE LIMBS ON LINE BETWEEN 963C18 & 963C20...WILL NEED CUT...NEED TREE CREW & LINE CREW....WILL HAVE TO OPEN 3RD RECLOSER TO CUT ROW....// RELEASED BY CREW 080S01.OPENED OTHER RECLOSER AT 14:55 IDC A AND C NOT B CHANGED COUNT FROM 70 XXXX
939 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2016-08-08 16:35 | 2016-08-08 23:00 | 305 | 385 | 4751251 | 53492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT BROKEN ON 53-29 WILL TRY TO REMOVE HOT TAP WITH LONG STICK NEED MANUAL ROW CREWAND LINE CREW / 37820053000143 @ 1929 (303 CUST)/ 37820053000029 @ 2300 (2 CUST)TRANS CUTOUT BROKEN ON 53-29 WILL TRY TO REMOVE HOT TAP WITH LONG STICK NEED MANUAL ROW CREWAND LINE CREW RELEASED BY CREW 079H03/ VER/BOW L3/HFP XXXHFP AJB
940 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-07-14 15:03 | 2011-07-14 20:48 | 155 | 345 | 4547391 | 53475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CENTER PHASE RECLOSER OUT ON POLE 817-17//TOP OF POLE841-39 SPLIT//CENTER PHASE INSULATOR AND CONDUCTOR LAYING AGAINST POLE// BACK ON MOUNTAIN//NO TRUCK//JOEY REED BRINGING CREW/ RELEASED BY CREW 079S01.//.SWAPPED MIDDLE PHASE @ 841-A3-45 TO PHASE C AND CUT DEADEND LOOP ON CENTER PHASE ON POLE 841-63//ALL OK PER MIKE LEWIS (HAZARD ENGINEERING)//COD 155//JOEY REED TO SHOW CHANGES IN PHASING TO ENGINEERING TO GET MAPS CHANGED IDC XXXX
941 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-01-01 21:13 | 2022-01-02 11:49 | 61 | 876 | 4254061 | 53436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Wire broke in the clear between poles 49-77 and 49-341 // opening recloser 37820049000075 opened@1024 closed @1149 LR- The 1st all out call came in at 21:13 on 1-1-22
942 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-05-05 08:19 | 2018-05-05 19:00 | 83 | 641 | 4309341 | 53203 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole fire/FD en route./Tech called/Pole 38830044B00226 burned off, windstream pole. In line, with tap, transformer, and underground. Reclosure on 38830044A00158 opened and isolated, and grounded between 38830044B00266, and 38830044B00223. tagged to bob reynoldsPole 38830044B00226 burned off, windstream pole. In line, with tap, transformer, and underground. Reclosure on 38830044A00158 opened and isolated, and grounded between 38830044B00266, and 38830044B00223. tagged to bobby reynolds. Need 405 L3/HFP
943 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-11-20 12:25 | 2018-11-20 16:20 | 350 | 235 | 4463891 | 53113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOLD ORDER DOL 876808/ 4/0 Hendrix conductor burnt in two. Released by crew 076S02
944 | Whitesburg | 3409503 | BURDINE | JENKINS | 2012-04-25 22:59 | 2012-04-26 01:22 | 371 | 143 | 4708251 | 53053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DURING LIGHTNING ////VER/CRB L/3 IDC XXXX
945 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-11-07 22:27 | 2014-11-08 02:56 | 343 | 269 | 4712481 | 53047 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON 49-331 / WILL PATROL //D SAMMONS & R RAY & J HAWKINS & J SMITH// OPENED SWITCHS ON 49-70 // CLOSED N.O. SWITCH ON 26-232 @ 23:51// HOLD ORDER REQ. // TOP OF POLE BURNED OFF ON 49-16// POWER RESTORED RELEASED BY CREW 074S05 VER/TOM L3/TOM HFP XXX AJB
946 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-04-19 14:35 | 2019-04-19 18:15 | 291 | 220 | 4135051 | 53022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | rec. open on pole 167-428.will patrol..pole 37830166000229 has dead-end insulators bad will need one A lineman with big bucket and 6 19.9 insulator to make repairs..opened GOAB on pole 166-A4-227 and restored to that point..closed rec. back in @ 16:18.//rec. open on pole 167-428.will patrol..pole 166-229 has dead-end insulators bad will need one A lineman with big bucket and 6 19.9 insulator to make repairs..opened GOAB on pole 166-A4-227 and restored to that point..closed rec. back in @ 16:18. L3/HFP
947 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-05-31 09:55 | 2011-05-31 12:19 | 368 | 144 | 4212971 | 52992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | NO LOAD ON C PHASE OUT OF THE STATION//LOOP BURNT OPEN ON REGULATOR IN STATION WAITING ON STATION MECH. TO CHECK REGULATOR PR TOLLIVER//BYPASSED REGULATOR POWER RESTORED AT 12:17 PR TOLLIVER RELEASED BY CREW 078H03//VER/CRB IDCC CNT1341 PHASE C ONLY TOF1210 XXXX
948 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-03-28 19:27 | 2008-03-28 20:14 | 1126 | 47 | 61746-1 | 52922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3300601//2 BAD CUTOUTS ON FAULT POLE//CREW ONSITE//WORKING TO REPAIR//COD 1126// VER/DBM IDC XXXX
949 | Whitesburg | 3312902 | JENKINS | JENKINS | 2021-08-03 23:10 | 2021-08-04 10:10 | 616 | 660 | 4001011 | 52896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | DOL 1136859 // feeder L/O @ 2310 per SCADA //cod 614 // failed arrester on pole 37830405C00311 had previously blown in the clear but laid on metal bracket which fired up when it got wet//lifted clamp for xfmr 405-C-311 and crew will repair in the daylight// restored 612 cc @ 0034 via SCADA // 2 cc remain //restored at 1010
950 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-10-16 19:20 | 2014-10-16 23:26 | 215 | 246 | 4638551 | 52890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DANNY TRAUGOTT OPENING RECLOSERS TO ISOLATE FAULT POLE 139-4004 RELATED TO PO# 4638361. OPENED AT 1920 CLOSED AT 2326. VER/SEF AJB
951 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-03-17 18:50 | 2018-03-18 05:11 | 85 | 621 | 4023021 | 52785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | recloser open 270-53 patrol close recloser came back out will need crew send to v. mullins Released by crew 078S04/crew on site/patrolling line/vem/bad cutout pole#294-80/FETR0530/vem/repairs made and all cust restored 0511/please close ticket/thanks/vem
952 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-02-07 20:24 | 2017-02-07 22:34 | 406 | 130 | 4369731 | 52780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DKM/OPENED BREAKER AT 2024 DUE TO FAILED LOOP AT POLE 284-128 AND CLOSED BREAKER BACK AT 2234/// VER/DKM L3/HFP HFPC TOF2026 AJB
953 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-10-06 22:54 | 2019-10-07 08:48 | 95 | 594 | 4104091 | 52650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NC CREW & Manual ROW REQ/ rec on 620-342 in/ patrolling line/ #4 & #2 acsr primary & neutral down 619-3 to 619-4/ primary on pole 3 broke in clear @ shoe/ recloser on 620-342 hot to pole 619-3/ NO TAG or GROUND placed/ manual tree crew & Line crew required/ no trucks Released by crew 078H08 // Restored @ 0848
954 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-06-11 07:11 | 2009-06-11 08:07 | 940 | 56 | 56763-1 | 52640 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | @ 0712 SCADA INDICATED THE BEAVER CREEK - MCKINNEY 46KV CIRCUIT LOCKED OUT INTERRUPTING GARRETT STATION VER/ARN IDC XXXX
955 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-11-24 11:11 | 2014-11-24 15:30 | 203 | 259 | 4765411 | 52577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | BURNT UP SOLID BLADE /// PER SCADA LOOKS LIKE ONLY C PHASE OUT = 203 CUST TOTAL /// VER/HFP L3/HFP AJB
956 | Hazard | 3309301 | VICCO | REDFOX | 2020-03-16 10:47 | 2020-03-16 12:28 | 520 | 101 | 4481991 | 52520 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1001076//1047 SCADA INDICATED CB LO ¦¦ COD-520 Released by crew 077S02//// Tree on T-line between Beckham and Vicco combined with MOLDLR Y Failure at Hazard preventing radial feed of Vicco from Hazard //cod 520
957 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-11-17 08:47 | 2014-11-17 13:12 | 198 | 265 | 4734181 | 52470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TARGETS ON A AND C PHARECLOSER 5-24 BACK OUT, CUSTOMER SAW FIRE FROM TRANSFORMER 5-229/ HAVE BAD CUTOUTS ON POLE 5-229 WILL REPAIR// COD 198// ON 13:12/RELATED OR ORDER 4735761//VER/ ADH L3/HFP AJB
958 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-10-02 09:03 | 2015-10-02 11:45 | 723 | 162 | 4301701 | 52326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | I HAVE HOT LINE CLAMP LIFTED ON POLE 190-109 GOING OUT TO POLE 190-60 IM IN THE CLEAR DONNIE GOING TO RECLOSER. CLOSED RECLOSER BACK IN AT 10:15 . PUT HOT LINE CLAMP BACK ON AT POLE 190-109 AT 11:45 RELEASED BY CREW 074S11// VER/ ADH L3/HFP XXXHFP AJB
959 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2018-06-13 21:15 | 2018-06-14 14:18 | 469 | 1023 | 4599401 | 52295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | loop burned off at pole 37830380C00043/// loop (C phase 83cc) burned into on pole 380-43/ moved recloser 37830380C00053 to A Phase @ 2330 (Resotring 74cc)/ 9 customers remaining out on on c phase @ 37830380C00043/ open ocrs 37830356B00008 @ 10:35 closed @ 11:30 down to A (92cc) Phase 37830380C00043/ recl 37830356B00008 open @ 1401 closed @ 1418/ moved recloser 37830380C00053 back to C Phase/ loops c (83) & A (18) phase 37830380C00043 on @ 1418 L3/HFP
960 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-09-25 19:20 | 2012-09-26 02:50 | 116 | 450 | H4087431 | 52200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED B PHASE @ 1909//COD 30//OPENED OTHER 2 PHASES @ APPROX 1920//COD +116// POLE BURNT OFF 66-155 SEND TO BOB //COD 146 TOTAL//OPENED B PHASE @ 1909//COD 30//OPENED OTHER 2 PHASES @ APPROX 1920//COD +116// POLE BURNT OFF 66-155 SEND TO BOB RELEASED BY CREW 078S08 VER/ARN IDCC CNT16 XXXX
961 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-12-17 09:25 | 2019-12-17 13:05 | 237 | 220 | 4162131 | 52140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENED RECLS ON POLE 37830215D40494 DUE TO SW ARCHING ON SAME POLEsource side switch feeding rec. on pole 215-434 arcing opened rec. @ 09:25.source side switch feeding rec. on pole 215-434 arcing opened rec. @ 09:25.center phase source side switch feeding rec. is bad and wont stay closed..will need crew to make repairs.
962 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-10-09 12:20 | 2016-10-09 17:30 | 221 | 310 | 4978681 | 52032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECL OPEN,WILL PTRL,1062-462////POLE 1062-147 BURNED OFF,NEED FOREMAN,1MAN,BUCKET,POLE TOP PIN&INSULATOR//SENT TO RON LEWIS BECAUSE OF NON-NETWORK OUTAGES//C PHASE RECL OPEN,WILL PTRL,1062-462////POLE 1062-147 BURNED OFF,NEED FOREMAN,1MAN,BUCKET,POLE TOP PIN&INSULATOR///////REPAIRS COMPLETED,RESTORED@17:30 VER/CRB // VER TIMES PER VOICE RECORDER = L3/HFP AJB
963 | South Williamson | 3411401 | DEWEY | INEZ | 2018-01-23 09:25 | 2018-01-23 14:00 | 189 | 275 | 4765281 | 51975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire at pole 792-c-6///pole almost burned into//i opened recloser on pole 768-225 at 9:25//to isolate//need line crew and big bucket//repairs made//restored at 14:00//complete//em/ ISO 38830768D00225/ COD 189 // L3/HFP
964 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-12-30 03:48 | 2021-12-30 15:11 | 76 | 683 | 4238041 | 51908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | top of pole 37830466000045 broke off // currently on phase A is open // appears pole has rotted off //cod 8//crew required // Released by crew 077S07
965 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-02-22 21:14 | 2011-02-22 22:10 | 924 | 56 | 60306-1 | 51744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | EMERGENCY OUTAGE NECESSARY TO REPLACE FAILED TRANSFORMER AND MAKE REPAIRS TO POLE & EQUIPMENT /// RELATED TO ORDER 60287-1 // RESTORED 2210 // COD-924 VER/HFP L3/HFP IDC XXXX
966 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-06-06 21:07 | 2022-06-07 17:08 | 43 | 1201 | 4028251 | 51643 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Windstream pole 67-164 broke, 355 on maps. 25kva 120/240 7200v hanging. Primary still energized. Safe for now. No good way to access pole. No trucks. Released by crew 078S02
967 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-02-06 10:43 | 2008-02-06 11:45 | 832 | 62 | 51189-1 | 51584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A//3311101// //VER/CRB AJB
968 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-01-16 22:39 | 2022-01-17 13:45 | 625 | 906 | 4355861 | 51450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | inteleruptor open @ 1098-6133, pole 1146-161 broke. cut loop @ 1146-150 iso. broke pole. yard dog,25kva xfmer. Released by crew 078S07
969 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-07-31 21:50 | 2022-08-04 11:28 | 10 | 5138 | 4646631 | 51380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | from pole 37830156000004-37830156B20301 primary & neutral are down. large tree has fallen just past pole 37830156000004 but only affects the service drop coming from pole 37830156000259. small tree at the base of pole 37830156B20301. shouldnt need a tree crew to hang the primary . Released by crew 034M29
970 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-01-01 12:54 | 2012-01-01 18:40 | 155 | 346 | 4219821 | 51326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 078S03/ CREW REQUIRED 6A COPPER PRIMARY ONLY TRUCK OK TO POLE 4 MAN CREW TRYING TO ISOLATE TO PICK CUSTOMERS UP/204-75 I ELEASED BY CREW 078S03/////VER/CRB IDC XXXX
971 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-12-13 09:13 | 2009-12-13 15:17 | 314 | 364 | 50096-1 | 51321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENED RECLOSER 182-257 AT 1042 ISOLATED LINE ON POLE 158-151 RESTORED POWER TO POLE 158-151 RESTORED ALL CUST AT 15:17 NOT SURE WHAT ORIGINAL CUSTOMERS WERE OUT BEFORE RECLOSER WAS OPENED VER/KEP L3/KEP MLR
972 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-09-26 10:03 | 2016-09-26 11:08 | 789 | 65 | 4926211 | 51285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DKM/1115/RECLOSER AT 954-A4-116 WAS ON HOT LINE TAG AND OPENED WHEN POLE BROKE AT 930-D-130/// VER/DKM L3/HFP XXXHFP AJB
973 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2017-11-06 10:23 | 2017-11-06 16:21 | 510 | 358 | 4534611 | 51267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire outside of kentucky electric steel at 162-251// emergency opened breakerat 1023,repairs made all cust restored @1621 please close ticket thanks.bt Released by crew 078H02
974 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-02-27 13:32 | 2009-02-27 15:04 | 559 | 92 | 52238-1 | 51176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW REPLACING CROSSARM IN DIFFICULT LOCATION IDC XXXX
975 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-10-01 06:17 | 2011-10-01 09:55 | 241 | 218 | 4936591 | 51154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER RECLOSER ON POLE 17 IS OFFLINE AND SUPPOSED TO BE IN ABNORMAL//WILL HAVE TO PATROL BACK DOWN TO NEXT RECLOSER TOWARD STATION SHOT RECLOSER.APPEARS CENTER PHASE IS ALL THAT IS OUT ///CENTER RECLOSER OPEN ON POLE794-352//PATROLED ALL WIRE IS UP//TRIED RECLOSER AND CAME BACK OUT/BAD CUTOUT AT POLE 818-49 COD-225 B PHASE ISO OCR 38820794D00352 VER/HFP L3/HFP IDC APPEARS PHASE A NOT B CHANGED COUNT FROM 225 XXXX
976 | Hazard | 3309302 | VICCO | JEFF | 2017-06-22 20:27 | 2017-06-23 00:45 | 222 | 258 | 4016431 | 51138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR HAS FAILED ON ARM PIN BURNING OFF CROSSARM AND CONDUCTOR IS ON THE GROUND, FAULT POLE IS 323-852, GOING TO OPEN SOLID BLADES ON 323-609 TO ISOLATE TROUBLE. C PHASE IS ONLY RECLOSER OPEN//COD 33 (+135) SJG
977 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-08-31 14:54 | 2019-08-31 20:25 | 274 | 331 | 4968841 | 51006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | cod 110/likely b phase/broken crossarm at pole 37830269D00038/A phase open on pole 270-1446. End of crossarm broke off at pole 269-38. will need to open B and C phase when help gets here.A phase open on pole 270-1446. End of crossarm broke off at pole 269-38. will need to open B and C phase when help gets here. opened B and C phase at 18:56.. restored all power at 20:25 Released by crew 077H11 L3/HFP/// trouble calls have b phase open from start
978 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-05 02:57 | 2011-06-05 04:59 | 418 | 122 | 4234291 | 50996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | "A" PHASE SWS FAILED AT POLE 767-C-150 //VER/GAH IDC XXXX ..
979 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-10-21 04:33 | 2016-10-21 05:16 | 1185 | 43 | 4035511 | 50955 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | FAILED STATION SERVICE CUTOUT OUTGAE FOR CREW TO SAFELY REPLACE VER/KEP // VER TIMES PER SCADA & DOL L3/HFP XXXHFP AJB
980 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-11-30 21:25 | 2016-12-01 01:36 | 203 | 251 | 4154821 | 50953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 37820032C00002 CAN REPLACE CUTOUT REPLACED CUTOUT RESTORED POWER AT 01:36 VER/HFP L3/HFP AJB
981 | Hazard | 3311103 | STINNETT | WENDOVER | 2019-05-18 11:31 | 2019-05-18 14:09 | 345 | 158 | 4293161 | 50923 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 922881/ Transmission Line Operated and momentarly dropped Stinnett station the the DA KP LESSTI attempted to transfer load. It looks like DA SWS 435-23 and 411-46 opened. N.O. DA SWS 388-B1-516 never closed to restore customers. During this time DA SWS 411-46 and N.O. DA SWS 388-B1-516 were showing Comms loss. Maybe this had something to do with N.O. DA SWS 388-B1-516 not closing to restore customers. I'm also not sure why DA SWS 411-46 opened when they could've stayed close and restored up to DA SWS 435-23 from the N.O. DA SWS 388-B1-516. After everything was returned to normal the Stinnett - Wendover CB C, DA SWS 435-23, DA SWS 411-46, N.O. DA SWS 388-B1-516 all show Not All Teams Ready still. The Stinnett - Wendover CB C shows Loss Of Voltage Disabled and will not go to Enabled./
982 | Pikeville | 3421001 | BREAKS | CITY | 2022-05-03 20:50 | 2022-05-04 04:05 | 1007 | 435 | 4832651 | 50887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Aaron Sanders reports pole 37820220C20510 rotted and fell over. Will be able to lift hot taps with hot stick to isolate at pole 37820220C20085. LR- DOL 4832651
983 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-08 10:52 | 2012-08-08 14:01 | 521 | 189 | 4910791 | 50850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSER OPEN ON POLE 398-2384, 2 SPANS WIRE DOWN AT POLE 421-149 ISOLATED TAP ON 421-149. CLOSED RECLOSER IN AT POLE 398-2384 AT 12:22. MADE REPAIRS RESTORED POWER AT 14:01//COD 521// VER/DBM IDC XXXX
984 | South Williamson | 3200302 | BELFRY | TOLER | 2018-01-20 18:02 | 2018-01-20 21:45 | 228 | 223 | 4759921 | 50844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Recloser is open at pole 38821015A00052. B phase has burned down at a hot tap that goes to a primary side tap. This is a road crossing and will need 6A copper, a three man line crew and a flagging crew. Primary is also down on side tap between pole 38821015B30276, and 38821015B30277. All power is restored. // SEE 47603231 ALSO - EXTENDING THAT OUTAGE TO TIME OFF FOR THIS ORDER
985 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-08-26 10:31 | 2009-08-26 11:53 | 620 | 82 | 50411-1 | 50840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LOOKING OVER LINE//REC TREID AT 1125 AND CAME BACK OUT//LOOKING OVER LINE,,,,FOUND BROKE ARRESTER ON POLE 502-69,,, I CLEARED IT UPLOOKING OVER LINE,,,,FOUND BROKE ARRESTER ON POLE 502-69,,, I CLEARED IT UP,,,,POWER RESTORED//VER/CRB IDC CROSSOVER CHANGED COUNT FROM 751 XXXX
986 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-11-15 04:38 | 2021-11-15 17:21 | 139 | 763 | 4093171 | 50839 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DDC HOLD ORDER REQ'D// DOL 1163112 // burnt off pole at 3782-0026-D4-0005 // cod 139 //RECLR IS OPEN,FAULT ON A PHASE INDICATED///////ABT 8FT OF POLE 26-5 BURNED OFF&LAYING SIDEWAYS.55CLASS2 POLE,3PHASE WITH SIDETAP&XFR ON IT/////2XARMS,BRACES,INSUATORS,XFR APPEARS OK////////NO WIRE BROKEN@THIS TIMERECLR IS OPEN,FAULT ON A PHASE INDICATED///////ABT 8FT OF POLE 26-5 BURNED OFF&LAYING SIDEWAYS.55CLASS2 POLE,3PHASE WITH SIDETAP&XFR ON IT/////2XARMS,BRACES,INSUATORS,XFR APPEARS OK////////NO WIRE
987 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-10-16 23:20 | 2008-10-17 09:40 | 258 | 620 | 56386-1 | 50752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE TOP BURNED OFF ON POLE 793-C-91 AND #4 COPPER PRI BURNED DOWN ON POLE 818-56 OPENED LINE ON POLE 793-45 AND 818-56 CLOSED RECLOSER ON POLE 794-D-352 AT 1:28 RELEASED BY CREW 079S01//3202202//VER/CRB IDC XXXX
988 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-02-02 19:23 | 2014-02-02 20:05 | 1207 | 42 | 4337921 | 50694 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION OUTAGE TO SAFELY INSTALL MOBILE TR FW-25-1/SOS 2783 REV 571 OPENED 19 2315 MIN OUTAGE OR LESS STATION PROBLEM RAN OUTAGE TIME OVER AND ADD. OUTAGE WILL BE NEEDED LATER TONIGHT. OUTAGE NECESSARY TO ALLOW CREWS TO REMAIN SAFE. IDC XXXX
989 | Hazard | 3310502 | HADDIX | CANOE | 2019-09-04 05:51 | 2019-09-04 11:32 | 216 | 341 | 4977651 | 50665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE INITALLY OUT 133 CUST ¦¦ OPENED B & C PHASE RECLS TO REPLACE CUTOUTS ON STEP DOWN (83 CUST) OPENED @ CLOSED @got broke cutout on a phase, call hazard and they sending crew with three new cutouts to change all of them got broke cutout on a phase, call hazard and they sending crew with three new cutouts to change all of them open recloser at 1028 and closed at 1132 L3/HFP
990 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-11-18 05:36 | 2011-11-18 10:28 | 211 | 292 | 4089101 | 50651 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ONE OF 2 RECLOSERS OUT ON 746B243..(PHASE B).PATROLLING.WIRE DOWN ON 697C28..CAN ISOLATE & DO PARTIAL RESTORE.CAN OPEN ON 697C24, & THEN CLOSE RECLOSER..CORRECTION.ISOLATED LINE BY OPENING CUTOUT ON 697C105.CLOSED RECLOSER @ 08:35.SEND TO J REED RELEASED BY CREW 080S01//COD ON B 211// ///VER/CRB IDCC CNT181 XXXX
991 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-08-04 17:01 | 2020-08-05 13:58 | 342 | 1257 | 4286841 | 50618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DDC TAGS/ HOLD ORDER REQ/ DOL 1042411/ top set of cross-arms broke on buck pole 446-78.. arm and wire hanging from pole Released by crew 077S11
992 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-04-29 22:23 | 2021-04-30 01:16 | 292 | 173 | 4499221 | 50516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser open @ 190-C-3459,(ASSESSING CONDITION)..Found a bad cutout @ 190-B-125 got it changed out.Restored recloser @ 01:16.
993 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-08-07 13:52 | 2022-08-07 22:55 | 93 | 543 | 4699151 | 50499 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Released by crew 076S02// restored @ 22:55// Complete
994 | Pikeville | 3421001 | BREAKS | CITY | 2015-04-10 15:03 | 2015-04-10 19:26 | 192 | 263 | 4306521 | 50496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4305211/CUTOUT BROKE ON TRANSFORMER 243-203, WILL HAVE TO OPEN RECLOSE 244-46 TO MAKE REPAIRS/TIM MCCOY SET UP AT CUTOUT, FRANK BLANKENSHIP STANDING BY AT RECLOSER/COD 192// VER/ ADH AJB
995 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-10-28 04:19 | 2015-10-28 18:11 | 83 | 832 | 4384751 | 50492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT LOOPS ON POLE 305-125 GROUNDED AND TAGGED TO BOBBY TACKET,,,CLOSED RECLOSER BACK IN @ 18:17 RELEASED BY CREW 078S05 OPEN 300 AMP SWITCHS ON POLE 305-64 2 MAKEUP LOOPS @ POLE 305-125 @ 1802// VER/ ADH // SEE ALSO H4384751 & 4389901 L3/HFP HFPC STP DUP FP38830305000125 AJB
996 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-05-07 23:28 | 2008-05-08 02:59 | 239 | 211 | 57980-1H | 50429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3201001//,ON SITE, PATROLLING LINE, CALLED R MARCUM FOR HELP//FOUND BURNT RISER AND BUSTED CUTOUT ON POLE 1062-30//OPENING NC SWITCH @ 1062-40 TO MAKE REPAIRS AT FAULT POLE//3201001// RELEASED BY CREW 080S01//LEFT HAND PHASE WAS THE ONLY OUTAGE UNTIL SWITH WAS OPENED IDC XXXX
997 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-04-25 19:28 | 2015-04-26 02:35 | 118 | 427 | 4365511 | 50386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO RECLOSERS PLACE GROUNDS & TAG TO DDC @ 351-148 POLE 327D-111 BURNT OFF NEED LINE CREW TO REPLACE TRUCK OK/ TECHNICIAN AND FLAGGING CREW ALSO CALLED OUT/ ISO 38830351000148/ COD 118,,CREW ON SITE,,REPAIRS MADE, ALL POWER RESTORED, WORK ORDER HAS BEEN WRITTEN VER/SEF L3/HFP XXX AJB
998 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-04-22 05:50 | 2012-04-22 10:30 | 490 | 280 | 4693561 | 50336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / RECLOSERS AT POLE 190-313 NOT OUT. SECTIONALIZER AT POLE 213-66 OPEN,OUTAGING 490 CC. CREW PATROLLING. --- SDB / 0728 / FAILED CUT OUT AT POLE 237-260, CREW LIFTED TAP AT POLE 237-184 TO ISOLATE. --- SDB / 0732 / SECTIONALIZER AT 213-66 CLOSED, 488 CC REST --- SDB / GARAGE ONLY CUSTOMER OUT NOW, WILL NEED A CREW TO REPAIR ON 4-23-12//OPS ORDER 030264625 CREATED BY D MASSEY TO HAVE REPAIRS MADE MONDAY// SERVIECR SPOKE WITH CUST AND THEY ARE OK W/SERVICE BEING OUT UNTI// VER/DBM IDC XXXX
999 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-04-08 16:24 | 2010-04-08 17:58 | 1114 | 94 | 61110-1 | 50326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 34589791 // FOUND BAD CUTOUT ON POLE 1137-84, SERVICER GOING TO CLIMB POLE AND CLEAR IT UP//COD 1114//, LAST CUSTS ON AT 1758 RELEASED BY CREW 080S01// VER/DBM IDC XXXX
1000 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2022-02-14 10:41 | 2022-02-14 14:30 | 533 | 229 | 4480631 | 50317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 1183144/SCADA INDICATED CB LOCKED OUT/CREWS EN ROUTE TO ASSESS//Wire down at 401-A-87/opened sws at 401-A2-354 to isolate/closed brk at 1140//wire down @ 401-A-86 to pole 401-A-87 # 4 solid copper. wire also down @ pole 377-B-134 with line fuse being open @ 377-B-95.. looks like the wire down on pole 377-B-134 has been cause of breaker outage where it has burnt other wire down wire down @ 401-A-86 to pole 401-A-87 # 4 solid copper.///DKMay - 02/15/2022- according to email received from Rich Chriscinske there was no evidence of tree caused outage so was changed to equipment failure cause due to information provided
1001 | Hazard | 3303901 | LESLIE | HYDEN | 2014-01-03 11:20 | 2014-01-03 18:45 | 113 | 445 | 4224191 | 50285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PATROLLING LINE,RECLOSER OUT @ POLE 267-177(STEPDOWN POLE),FOUND 1 SPAN #4 ACSR DOWN @ 728 WILDER BR. RD.,WILL NEED 3 MAN CREW,HANDCOIL #4 OR #2 ACSR & SLEEVES,MANUAL. RELEASED BY CREW 077E09//COD 113// VER/DBM L3/HFP HFPC FP37830257000031 IDC XXXX
1002 | Hazard | 3303902 | LESLIE | WOOTON | 2014-08-20 18:20 | 2014-08-20 20:02 | 991 | 102 | 4391581 | 50252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN GOAB ON #413-46 & CLOSED RECLOSER ON #389-328 @18:54 HRS PART RESTORE..FOUND BBROKEN 19.9 KV CUTOUT ON POLE 413-24..ISOLATED BAD C/O AND CLOSED GOAB #413-46 @19:28 HRS.CHANGED C/O.ALL POWER RESTORED @20:02 HRS RELEASED BY CREW 077H09//COD 991// VER/DBM AJB
1003 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-10-12 16:20 | 2016-10-12 19:00 | 314 | 160 | 4988921 | 50240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON POLE 190-459...WILL PATROL...CLOSED REC. BACK IN @ 19:00 AND STAYED...FOUND CUTOUT BROKE ON POLE 189-243 THAT FED ABANDONED HOME LIFTED HOT TAP../ ISO 37830190C30459/ COD 314/ VER/BOW L3/HFP XXXHFP AJB
1004 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-06-13 09:19 | 2022-06-13 15:08 | 168 | 349 | 4063871 | 50235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary broke in the clear at pole 746B-139.wire down from 139 to 314.i have a line crew on the way Released by crew 079S03 // opened switch 746-a-65 @1430 // restored@1508
1005 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-07-02 16:12 | 2019-07-02 19:46 | 234 | 214 | 4637961 | 50076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Switch on 38830478A40380 is open. B phase cond burnt dn @ 478A31092 to 478-1043. Crew in route Restored 1946Switch on 38830478A40380 is open. B phase cond burnt dn @ 478A31092 to 478-1043. Crew in route Released by crew 078S11 L3/HFP
1006 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-08-19 09:48 | 2009-08-19 15:12 | 170 | 324 | 66632-1 | 50058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP W R # 31305280 // HAVE CALLED FOR RITEAWAY CREWS SUSPECT RITEAWAY PROBLEM OPEN DISC ON POLE 447-229 CLOSED REC ON POLE 446-180 AT 1410 POWER ON TO POLE 229 CLOSED ON 447-229 AT 15:12 BAD CUTOUT ON 447-43 L3/HFP IDCC TON XXXX
1007 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-06-04 05:25 | 2011-06-04 07:50 | 345 | 145 | 4230141 | 50025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 345 CUSTOMERS OUT // A PHASE LOOPS BURNT OPEN AT POLE 833-474 CREW ON SITE. WILL HAVE TO OPEN KENWOOD-HAGER HILL BREAKER TO MAKE REPAIRS (EST. 30 MINUTES). OPEN STA BREAKER @ 0724 INTERRUPTING ADDITIONAL 644 CUSTOMERS // CLOSED STA BREAKER AT 0750 //VER/GAH IDC XXXX
1008 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-03-10 17:09 | 2015-03-11 13:11 | 57 | 1202 | 4179271 | 50010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KY DDC HOLD TAGS PLACED// TOM FAULT POLE IS 473-25, ISOLATED G&T TO DDC AT POLE 497-92. RECLOSER CLOSED AT 2003 HOT UP TO 497-92. CREW REQUIRED WILL WORK 3/11 DUE TO HIGHWATER RELEASED BY CREW 078S11//DDC GAVE ERIC BAIER PERMISSION TO REMOVE DDC`S HOLDF TAG AND REPLACE WITH HIS OWN @ 0918 3-11-15/ CREW REQUIRED WILL WORK 3/11 DUE TO HIGHWATER RELEASED BY CREW 078S11 VER/KEP IDCC FP125 XXXX
1009 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2020-07-02 20:04 | 2020-07-02 22:35 | 330 | 151 | 4105701 | 49830 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE HARDWARE | DOL 1032777///Beaver Creek-Elwood 46kV Ckt locked out interrupting Burton Station.//CB closed at 2235
1010 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-03-13 11:45 | 2014-03-13 18:38 | 300 | 413 | 4488881 | 49750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1409 -KEITH CAMPBELL (DHE) ISSUED HOLD ORDER. ATT POLE 40/2 // COMING TO LOWER EQUIPMENT DOWN ON POLE 1064-C-4 // VER/ARN IDC XXXX
1011 | Hazard | 3303901 | LESLIE | HYDEN | 2010-05-14 03:44 | 2010-05-14 04:54 | 707 | 70 | H61789-1 | 49490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW MAKING REPAIRS NOW, PHASE B CAME OFF INSULATOR ON ANGLE POLEB PHASE INSULATOR JUMPED OFF OF POLE TOP PIN...OPEN GOAB ON POLE 388A-307 @ 03:44 HRS, MADE REPAIRS AND CLOSED GOAB @ 04:54 HRS....ALL POWER RESTORED P.HICKS IDCC DUP TO OPEN GOAB, LOOKS LIKE POLE 37830388A00028 WAS OUT INITIALLY, CNT724 XXXX
1012 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-06-18 17:29 | 2014-06-18 19:03 | 526 | 94 | 4107911 | 49444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EMERGENCY OUTAGE TO REPLACE BROKEN CROSSARMSOPENED ON POLE#38830955D00571 @17:29.CREW IS ON THE WAY.//COD 526// VER/DBM AJB
1013 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-05-27 02:30 | 2009-05-27 04:30 | 412 | 120 | 55003-1 | 49440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LOST BREAKER AGAIN WORKING ON ORDER 54784-1 VER/KEP L3/KEP IDCC TOF0245 XXXX
1014 | Pikeville | 3421001 | BREAKS | CITY | 2022-08-12 00:50 | 2022-08-12 08:15 | 111 | 445 | 4731131 | 49395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B phase only is open // cod 60 //B Phase Recloser open 196-B4-898,Have Span Primary down 196-240 to 196-96,Line crew Required(NO TRUCK)Manual ROC to cut Path to pole..Open A and C Recloser at 06:18,Closed 08:15.. LR- Left the customer count alone though the comments says that A & C were opened at 06:18 but the calls show that All Out calls came from all the Phases from the beginning
1015 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-06-07 17:37 | 2022-06-07 20:05 | 339 | 148 | 4034381 | 49332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | power restored/ During Outage 4034381 a transformer fuse blew on 37830423A00129 due to unknown reasons. The blown transformer fuse tripped both reclosers on poles 37830446C40300 & 37830446A20323 since they could not reclose due to being backfed. LR- PowerOn shows that there are only 28 customers on device 37830446A20323
1016 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-12-08 18:44 | 2010-12-09 00:15 | 149 | 331 | 64509-1 | 49319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PHASE C IS DOWN AT POLE 1041-B-201.....ON HILLSIDE....CALLED J REED...NEED 3 MAN CREW....WILL OPEN & ISOLATE RECLOSER ON 1065-B-275....WHEN THEY ARE CLOSE....//...OPENED RECLOSER @ 22:35....MADE LINE REPAIRS.....CLOSED RECLOSER @ 00:15....POWER RESTORED.....JRV....12/09/10 // CUSTOMERS ONLY INTERRUPTED ON C PHASE FROM POLE 1041-B-201. (75 CUSTOMERS) //VER/GAH IDC LOOKS LIKE PH B NOT C CHANGED COUNT FROM 75 XXXX
1017 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-08-12 04:55 | 2009-08-12 07:12 | 359 | 137 | 60580-1 | 49183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, PATROLLING LINE, SEND COPY TO R RYE, THIS MAKES TWO OF BYPASS CUTOUTS BAD ON THIS POLE, ALSO ONE XARM BURNT INTO//COD 359// VER/DBM IDC XXXX
1018 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-11-10 08:21 | 2010-11-10 10:32 | 375 | 131 | 54517-1 | 49125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | AT 0821 OPENED AND ISOLATED BREAKER TO SAFELY ISOLATE DOWNED LINE ON 54496-1/CREW ENROUTE VER/KEP L3/KEP IDC XXXX
1019 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-10-26 12:35 | 2010-10-26 21:20 | 95 | 525 | 63976-1 | 49095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STS WR # 37489285 // OPENED SWITCHES AT 1007-118/ WIRE DOWN AT 1007-120/ ONLY C PHASE OUT 95 CUSTOMERS 1 POLE BROKE(1008-81),POLE 1007-119,XARMS BROKEN,HAVE CONTACTED T HALL IN PVILLE,CREW ENROUTE SHORTLY,THEY WILL BE CALLING FOR TICKET. RELEASED BY CREW 074S06 //VER/GAH IDCC CNT242 XXXX
1020 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2018-12-27 17:25 | 2018-12-27 21:27 | 230 | 242 | 4602611 | 48940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase rec. open @48-A4-1679 and B and C line fuse open @48-D3-147, checking. B phase cutout busted on pole 48-D3-147, only trouble found, will have to open A and C phase rec. on 48-A4-1679 to change, will keep track of times. Opened A and C @1945. Found another bad cutout @25-B-349, isolated and it will take a crew with big bucket // ok till tommorow// repaired c/o on 147, closed all 3 rec. back in @2127. Released by crew 074S05 L3/HFP
1021 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-02-18 02:54 | 2015-02-18 11:40 | 93 | 526 | 4037801 | 48918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ON POLE 38831064000009 GOT PRIMARY WIRE DOWN CROSS THE RIVER NEED BOAT 4 MEN , 3 MAN TREE CREW, #2 WIRE AND SLEEVES.//TAGGED TO L LAWSON AND GROUNDED AT POLE 1040-94//COD 93// VER/DBM L3/HFP XXX AJB
1022 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-07-18 15:34 | 2019-07-18 18:20 | 497 | 166 | 4729831 | 48842 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rec. open on pole 213-66////will patrol./// BROKE CUTOUT 37830237B00037 rec. open on pole 213-66////will patrol.found bad19.9 xfm. cutout on pole 237-37.was able to isolate cutout and closed rec. back in @ 17:12..will need big bucket to make repairs.rec. open on pole 213-66////will patrol.found bad19.9 xfm. cutout on pole 237-37.was able to isolate cutout and closed rec. back in @ 17:12..will need big bucket to make repairs. Released by crew 074S01
1023 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-04-04 19:30 | 2008-04-04 20:49 | 617 | 79 | 64085-1 | 48743 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401801//@ 1940 SERVICER PATROLLING CKT * @ 2000 UPDATE ** POLE FIRE AT POLE 678-54 CREWS IN PROCESS OF SECTIONALIZING TO RESTORE CUST.3401801//@ 1940 SERVICER PATROLLING CKT...CHG CUTOUT.... VER/HFP IDC XXXX
1024 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-10-31 13:07 | 2019-11-01 13:42 | 33 | 1475 | 4228421 | 48675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | arrived and patroling apprears to be a bigger problem, found fuse out on B phase on pole 794-246 patroled to where B ends at pole 794A-126 did not see anything else Released by crew 079F03//crossarm broke on pole 794-a-95//no truck/need 5 man crew and manual tree crew//will need to open other 2 phases before making repairs//
1025 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2018-01-02 10:30 | 2018-01-02 13:04 | 316 | 154 | 4697491 | 48664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CAPACITOR | Tried the recloser and it operated and opened back up. Bad capacitor bank on pole 38820917D00028, not shown on field view. A & B phase was blown but the door did not drop down, I opened the C phase./ ISO 38820893A00304/ COD 316
1026 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2012-08-10 20:57 | 2012-08-10 23:07 | 374 | 130 | 4926571 | 48620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 2206403--**KY SIDE CUSTS - 374 CUSTS TOTAL**--SCADA INDICATED THE SOUTH NEAL/WHITE CREEK 12KV CKT LOCKED OUT--CC779--FOUND BROKEN CROSSARM AT POLE 190-D-12--ISOLATED AT POLE 190-C-93--CLOSED CB AT 2306 REST 410 CUSTS--369 REM OUT--HOLD ORDER ISSUED TO DUANE SOWARDS 2210--RESTORED REM 369 CUSTS AT 0231 //VER ANM IDC XXXX
1027 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-09-04 17:07 | 2011-09-04 18:58 | 438 | 111 | 4808361 | 48618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN ON POLE 785-45 ONE PHASE WE ARE POPENING RECLOSURES ON POLE 785-121 SO WE CAN PUT WIRE BACK UP//COD 438// OPENED UP AT 1815 AND CLOSED THE RECLOSURES BACK IN RESTORING ALL CUSTOMERS AT 1858/ // VER/DBM IDC XXXX
1028 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-04-04 15:55 | 2014-04-04 22:55 | 276 | 420 | 4574831 | 48610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHECKED LINE BACK UP TO REC. ON 204-264, WE HAVE ONE REC. LOCKED OUT BELIEVE ITS B PHASE//COD 276// PRIMARY IS OFF INSULATOR, UP IN TREES WILL OPEN GOAB ON 178-297 WILL GO BACK TO REC 179-194 ONE REC IS OPEN AND WILL CLOSE CLOSE IT THEN GO TO REC. 204-264 AND ENERGIZE DOWN TO GOAB OPEN POINT. OPENED GOAB AT 17:48. CLOSED REC ON 37830204000264 // THIS IS B PHASE OUTAGE WILL DUP TO CORRECT IN HOIS FOR A & C PHASE OUTAGES. VER/HFP L3/HFP
1029 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-05-04 07:30 | 2016-05-04 09:15 | 709 | 105 | 4172171 | 48573 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B TACKETT REPORTED POLE FIRE ON 215-261 (3-PHASE). HAVE BAD INSUL. CREW ON WAY. OPENED 3-600 AMP SWITCHES ON 215-224. TAGGED TO S RAY. CLOSED RECLOSER ON 193-390 AT 0826. HOT UP TO 215-224.B TACKETT REPORTED POLE FIRE ON 215-261 (3-PHASE). HAVE BAD INSUL. CREW ON WAY CLOSED IN AT POLE 215-224 AT 0915 RELEASED BY CREW 074H04 AJB
1030 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-10-08 10:40 | 2017-10-08 11:22 | 1156 | 42 | 4421011 | 48552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 1156 CUSTOMERS, CREW ON SITE MAKING REPAIRS OPEN @ 1040 CLOSED @ 1122 SEE TICKET 4419671 VER/ARN /// CHECKED TIMES PER SCADA ACB
1031 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2019-03-30 23:18 | 2019-03-31 04:31 | 155 | 313 | 4041541 | 48515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C phase out on 38830020C45614/cod 78/ 56 3-ph/. crew reqd. truck ok. c phase cutout broke. Released by crew 078H17,replaced cutout all cust restored @ 0431 please close ticket thanks.bt created related outage 90052353//// trouble tickets show A phase
1032 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2015-02-17 02:49 | 2015-02-17 15:04 | 66 | 735 | 4035331 | 48510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER TIM HALL ARCOSED JOEY REED. THREE PHASE POLE BURNED OFF. 1111-88 MUST BE REPLACED.TRUCK APPROACH. CAN PICK UP SOME CUSTOMERS FROM BARRENSHE/ SLATE BRANCH CIRCUIT. I WILL TAKE HOLD ORDER (66 PIKEVILLE-COAL RUN CUST) VER/HFP L3/HFP AJB
1033 | Pikeville | 3421002 | BREAKS | GRASSY | 2010-07-18 17:40 | 2010-07-19 13:24 | 57 | 1184 | 52703-1 | 48504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3400902// STATION BREAKER LOCKED OUT/// SERVICER PATROLING THE LINE, // RELEASED BY CREW 074S02 - CLOSED SW AT 1324 ENERGIZED TO OPEN OCR ON VA SIDE 221D-190 // NOTIFIED ROANOKE DDC // IDC XXXX
1034 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-12-09 23:58 | 2019-12-10 04:00 | 271 | 242 | 4140141 | 48380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Ph A only//cod 93//wire down at 38820989A00274//opened SW 38820989A00115 to isolate (all 3 phases)// cod +48//unable to find what took wire down //closed RECL @ 0226 restoring 53 cust//made repairs and closed SW 989-A-115 @ 0400, restoring 88 cust////Trouble tickets show all phases out
1035 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2009-12-31 00:58 | 2009-12-31 10:14 | 87 | 556 | 51256-1 | 48372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, PATROPLLING LINE RELEASED BY CREW 080S01 FOUND CONDUCTOR DOWN//COD 87 IDC XXXX
1036 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-05-05 17:52 | 2011-05-05 19:25 | 518 | 93 | 4012711 | 48174 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | SCADA INDICATES STATION OUTAGE ON SOFTSHELL TANSFORMER #1 @ 1752 // SERVICER AND STATION PERSONEL ENROUTE // RESTORED AT 1925 VER/TOM L3/TOM IDCC TOF1755 TOF1937 XXXX
1037 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-08-12 05:18 | 2014-08-12 06:36 | 617 | 78 | 4358131 | 48126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FAILED INSULATOR PO#4357391/RECLOSER LOCKED OUT WHEN LINE WAS SHOT VER/KEP AJBC CNT547 INLT 31 C PH ON LF 37830045000249 WERE OUT.
1038 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-08-07 07:11 | 2017-08-07 14:21 | 269 | 430 | 4232601 | 48119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | @ 0838 PATROLLING CKT//RECLR 38821081000300 OUT (269 CUST)//////C PHSE TO GRND FAULT///WILL PTRL//TRIED RECLR,CAME OUT//////BAD INSULTOR POLE1081-28,ISOLATED@1081-175,CLOSED RECLR@10:08 (267 CUST),CREW ENROUTERE TO MAKE REPAIRS///////NOTE NEW FET/ CLOSED HOT TAP 38821081D00175 @ 1421 (2 CUST)/VER/BOW L3/WDH SJG
1039 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2009-05-17 04:17 | 2009-05-17 08:05 | 211 | 228 | 60301-1 | 48108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND RISER BURNT OUT OF CUTOUT ON A PHASE ON POLE 893-D-158, ON KY SIDE....(RIVER CROSSING POLE)....CAN REPAIR, BUT WILL HAVE TO DE-ENERGIZE BY LOAD BUSTING UNDERARM BLADES ON WV SIDE ON POLE 893-D-157....CALLED JOEY REED HE WILL DE-ENEGIZE LINE SO I CAN REPAIR CUTOUT RISER.....//J REED OPENED BLADES.....LOOP NREPAIRED....CLOSED BLADES ON POLE 893-D-157 @ 08:05......JRV...05/17/09 NOT SURE ON CUSTOMER COUNT VER/KEP
1040 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2021-10-07 11:42 | 2021-10-07 12:32 | 962 | 50 | 4327181 | 48100 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 69/12kV TR 1 tripped from service due to failed bushing at station At 1232 Closed DA SWS at 1098-366 restoring via transfer to Highland/Wurtland restoring 962 CC
1041 | Williamson | 3200204 | BARRENSHE | POUNDING | 2020-01-23 14:47 | 2020-01-23 17:54 | 257 | 187 | 4332681 | 48059 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSER 38821065B00275 WAS ON HLT PER TOMMY MORRIS(DHE) CONDUCTOR BROKE AND TOOK OUT //COD 257// 1754/ ISO 38821065B00275/ 257cc transformer was already open on load side that had 4 customers
1042 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2018-03-20 08:34 | 2018-03-20 14:57 | 271 | 383 | 4029541 | 48031 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD ORDER // DOL 811555 // SCADA indicates feeder breaker lockout @ 0832 // pole 20-5010 top burnt off// cod 264 //,repairs made all cust restored please close ticket thanks.bt Released by crew 078H02//
1043 | Whitesburg | 3409503 | BURDINE | JENKINS | 2012-03-16 00:18 | 2012-03-16 02:25 | 378 | 127 | 4586821 | 48006 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | OUTAGE TO INSTALL MOBILE TRANSFORMER VER/ARN IDC XXXX
1044 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-02 13:26 | 2010-05-02 15:48 | 338 | 142 | 53903-1 | 47996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECL 141-C-45 LOCKED OUT ON THE CANNONSBURG/PRINCESS D/A SYSTEM. BAD 19.9 CUTOUT 141-54 SEND TO LLOYD MC. RELEASED BY CREW 078S08 DC CLOSING ORDER WILL CHECK MONDAY ON CUSTOMER COUNT IDC XXXX
1045 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-11-08 00:15 | 2019-11-08 16:37 | 96 | 982 | 4009541 | 47940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | s.//pole top burned off at 38830787000005//COD-15 from beginning of outage/Opened switches on pole 38830811000267 @ 0947 interrupted 81 customers/ pole on side of hill all manual work/ALL RESTORED @ 1637 L3/HFP
1046 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-11-01 02:14 | 2013-11-01 19:37 | 48 | 1043 | 4992291 | 47844 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | 2206403; ****HOIS CREATED DUPLICATE. ORDER HAS ALREADY BEEN VERIFIED****JEFF FERRY TO ASSESS 2257 304 633-3648 FOUND A PHASE OUT ON MAIN LINE -- PAD POLE IN STATION BREAKER. -- NOTIFIED DDC RELEASED BY CREW 068E04 //DC 12 WV PH A CUSTOMERS AND 117 KY PH A CUSTOMERS. WILL BE OPENING OTHER TWO PHASES AT 1700/ DEENERGIZED 2 PHASES AT 1759/ RESTORED FROM TRANSMISSION AT 1823// VER/RSL IDC XXXX
1047 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-03-02 05:08 | 2013-03-02 14:00 | 106 | 532 | 4866171 | 47812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASE REC POLE 224-7 OPEN - 105 CUST //, PATROLLING LINE. //OPENED PH 3 RECL AT 0702 - 105 CUST, THEN OPENED SWS AT POLE 225-28// CLOSED A & B RECLS AT 0725 RESTORING 40 CUSTS // PHASE 3 RECL WOULD NOT CLOSE // WILL CLOSE PH 3 BYPASS WHEN GETS BIG BUCKET //HICKMAN, CLEMONS, AKEMON & EMBERTON TO ASSIST //COLLETT FOR STORES //@ 1020, CLOSED C PHASE BYPASS ON RECLOSER 224-7, RESTORING 19 CUST//AED CREATED FOR BAD RECLSOER// POWER RESTORED AT 1400 RELEASED BY CREW 077S04 IDCC CNT210 XXXX
1048 | Whitesburg | 3309302 | VICCO | JEFF | 2018-04-25 20:46 | 2018-04-26 02:20 | 143 | 334 | 4279611 | 47762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Wire down and crossarm broken at 37830323D00596. Crossarm broke on 323D/596 // xarm rotted in two//cod 343// trouble tkts show b phase only
1049 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-12-20 07:09 | 2012-12-20 09:06 | 408 | 117 | 4484231 | 47736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER ON POLE 103-B-210 IS OPEN WILL BE PATROLLING CLOSED RECLOSER AND IT STAYED THIS OPENED THREE TIMES THIS DAY ALL LATER FOUND RECLOSER WAS OPENING AND NOT OPERATING CHANGED CODES TO EQUIP FAIL ON ALL OF THEM AND ENTERED AED VER/KEP IDC XXXX
1050 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-01-16 06:00 | 2013-01-16 13:12 | 159 | 432 | 4609751 | 47727 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 204-30 45/4 INLINE SINGLE PHASE NO TRUCKS BEHIND TRAILOR WITH TRANSFORMER 10 KVA CREW REQUIRED NEED TECH ALSO/ISOLATED ON 204-139/6A WIRE DOWN ON 204-15 HOT TO THAT POINT TRUCK OK /RECLOSER BACK IN AT 0742 HRS TO 204-15 RELEASED BY CREW 078S03////CLOSED SOLID BLADE AT 13:12 RELEASED BY CREW 078H16. ///VER/CRB /L/3 CRB IDC XXXX
1051 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2018-12-27 23:41 | 2018-12-28 13:50 | 200 | 451 | 4603641 | 47665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Three bad, double bushing, 5kva transformers on crossarm at pole 39831124A41610, 240 power bank, trucks to pole. Feeding first and peoples bank. Released by crew 078H04 crew on site FETR 12:00 LRM All pwr restored @13:50 please close ticket LRM Released by crew 078H06
1052 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-01-12 19:44 | 2015-01-12 23:15 | 1383 | 211 | 4931451 | 47625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT THE REQUEST OF SERVICER, OPENED FEEDER VIA SCADA DUE TO POLE FIRE WITHIN THE BREAKER ZONE (SEE ORDER 4931391) //COD 1368 // SERVICER ISOLATED FAULT POLE AND FEEDER WAS RE-ENERGIZED VIA SCADA @ 2006//RESTORED 1292 CUSTOMERS//NEED 4 8FT. CROSS ARMS 1-CUTOUT/45/2 FORIEGN POLE//,,CREW ON SITE,,REPAIRS MADE, ALL POWER RESTORED AT 23:15 RELEASED BY CREW 078H03// VER/DBM L3/HFP XXX AJB
1053 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-06-16 14:54 | 2009-06-16 22:29 | 109 | 455 | 60006-1 | 47615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE REC. OPEN CHECKING LINE/// HOT LINE CLAMP BURNT OFF ON POLE 37830278B00176. NEED CREW// CALLED GREG TO GET HELP AND CALLED FOR R/W CREW.//// REPLACED C/O RISER POWER RESTORED. OPEN REC. ON POLE 279-261, CLOSING RECS. ON POLE 278-335 AT 21:45. CLOSED REC ON POLE 279-261 AT 22:29 POWER RESTORED//VER/CRB IDC XXXX
1054 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-03-26 16:01 | 2009-03-26 20:00 | 199 | 239 | 61914-1 | 47561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301// VER/CRB IDCC CNT323 PH A AND B XXXX
1055 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-11-09 02:00 | 2010-11-09 04:00 | 396 | 120 | H54155-1 | 47520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | "C" PHASE RECLOSER OUT POLE 876-B-28 // COD - 287 //..PATROLLING...1 SPAN PRIMARY DOWN 900-1..C PHASE RECLOSER OUT..PATROLLING...1 SPAN PRIMARY DOWN 900-1..TOOK ALL 3 REC.876-28 AT 2AM..C PHASE RECLOSER OUT..PATROLLING...1 SPAN PRIMARY DOWN 900-1..TOOK ALL 3 REC.876-28 AT 2AM..REPLACED WIRE..BACK ON AT 4 AM...BB //VER/GAH IDC DCMT XXXX
1056 | South Williamson | 3411401 | DEWEY | INEZ | 2021-03-25 13:23 | 2021-03-25 15:41 | 592 | 138 | 4373621 | 47440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Switching DOL 1101766 / REC. open will patrol/// B phase deadend insulator is bad on pole 767-C3-658. Opened switches on 767-C3-657 & 767-C3-265 to isolate and restore customers while making repairs///
1057 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-03-20 18:07 | 2020-03-20 20:18 | 598 | 131 | 4497521 | 47422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | bad recloser on pole 446-300, opened recloser on 423-278 at 20:05 to isolate & bypass recloser, closed 423-278 at 20:18 restoring power. Released by crew 077S11
1058 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-08-15 14:30 | 2019-08-15 16:33 | 385 | 123 | 4891991 | 47355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | END OFF CROSSARM BROKE OFF, WILL HAVE TO OPEN 3-PH LINE AT REC PL# 1032-132. BROKE ARM IS ON PL#38831031000006. I EST. ABOUT AN HOUR TO REPAIR/// OFF AT 14:30 on @ 1633
1059 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-09-09 03:14 | 2012-09-09 11:50 | 113 | 516 | 4032991 | 47308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BURNT OFF POLE TOP ON 1104-58 ON HILLSIDE.SINGLE PHASE..DUE TO BAD INSULATOR.CAN ISOLATE ON NEXT POLE BACK 1104-50, AND GET RECLOSER BACK ON.NEED CREW. // D. HAMILTON, P.LAYNE & J. HAWKINS TO ASSIST //LIFTED HOT LINE CLAMP ON 1104-50.CLOSED RECLOSER ON 1056D299 @ 08:10..// ///VER/CRB L/3 CRB IDCC CNT217 PH B ONLY XXXX
1060 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-02-24 10:36 | 2014-02-24 13:49 | 245 | 193 | 4430191 | 47285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN ON RIGHT PHASE ON POLE 746-14///NEED BIG BUCKET//CREW ON SITE///REPAIRS MADE// RELEASED BY CREW 079S01 // B PHASE INITALLY OUT 245 CUST // @ 1316 OPENED A & C PHASE SWS DROPPING 87 CUST // ALL REST @ 1349 /// VER/HFP L3/HFP IDC XXXX
1061 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-10-30 16:51 | 2014-10-31 01:19 | 93 | 508 | 4675281 | 47244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | AJB
1062 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-07-24 00:52 | 2014-07-24 15:37 | 58 | 885 | 4279531 | 47238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC HOLD CARD PLACED AT POLE#196-192/POLE 37830196B00134 BURNT OFF AT CUTOUT BRACKET.MANUAL..MIGHT BE ABLE TO LOWER XFMR AND NEUTRAL AND USE THE OLD POLE..POSSIBLE YARD DOG ACCESS../ RELEASED BY CREW 077H18// GAVE PHIL HICKS PERMISSION TO REMOVE DDC HOLD TAG // REPAIRS COMPLETE//COD 58// DKG--RESTORED 6 CUST AT 0415 BY OPENING SWITCH AND CLOSING RECLOSER VER/DKG L3/DKG AJB
1063 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2017-02-09 09:55 | 2017-02-09 16:15 | 124 | 380 | 4376341 | 47120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 37830424000174 ARMS BURNT INTO OCRS OPEN ON POLE 37830448C10498 POWER RESTORED AT 16:15 COD 124 VER/AWD L3/HFP XXXHFP AJB
1064 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-01-24 22:57 | 2015-01-25 02:43 | 208 | 226 | 4961601 | 47008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY LOOP HAS BURNED INTO ON POLE 37820008D00024. NEED FOREMAN AND ONE MAN, NO TRUCK ACCESS. I OPENED RECLOSER ON POLE 8-D-93 AT 01:42. POWER IS BACK ON.//ISO 37820008D00024//COD 208 (+2, SEE H4961601)// VER/DBM L3/HFP XXX AJB
1065 | Hazard | 3309301 | VICCO | REDFOX | 2008-07-08 15:03 | 2008-07-08 19:53 | 162 | 290 | 64554-1 | 46980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 1 PHASE OUT 0N POLE 323-430, CORRECTION, WIRE IS BURNT OFF IN STATION... 79 CUST OUT ORIGINALLY / OPENED BRK AT 1803 158 CUST OUT / TOTAL 269 CUST RISER ON LINE SIDE DISCONNECT BURNT INTO/ REPAIRED AT 1953 VER/KEP IDC XXXX
1066 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-08-21 00:57 | 2018-08-21 09:22 | 93 | 505 | 4979011 | 46965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | TAGGED TO KYDDC @ 37830238000182 DOL 853155// : Dispatched in accordance with KYPCo Late Night Callout Guidelines.////rec. open on pole 214-44////will patrol: Dispatched in accordance with KYPCo Late Night Callout Guidelines.////rec. open on pole 214-44////will patrol////rec. bad on pole 238-182.lifted source side and load side risers and tagged to DDC.: Dispatched in accordance with KYPCo Late Nigh Released by crew 074H02 L3/HFP
1067 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-02-10 00:27 | 2010-02-10 01:58 | 515 | 91 | 54739-1 | 46865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | 3420001 // SERVICER FOUND THE METERING POLE WENT TO GROUND FOR CONSOLATED COAL CO. SCADA INDICATES FEEDER LOCKOUT @ 0027// CALLING FOR SERVICER // PATROLLING NOW // VER/TOM L3/TOM IDCC TON150, CHANGED FROM CUSTOMER EQUIPMENT XXXX
1068 | Whitesburg | 3312901 | JENKINS | KONA | 2016-04-02 20:35 | 2016-04-03 02:22 | 135 | 347 | 4026721 | 46845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B-PHASE LOOP BURNT IN-TO ON POLE 405B-49 WHERE LOOP WAS MADE UP WITH SPLIT BOLT//B PHASE 211//. OPENED SWITCHES ON POLE 405-474 AT 1:36 AND CLOSED BACK IN AT 2:20//ORIGINALLY 135 B PHASE OUT/OPENED SWITCH OUTAGINING 354 CUSTOMERS// VER/ ADH AJB
1069 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2016-01-06 07:58 | 2016-01-06 13:10 | 458 | 312 | 4588911 | 46818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POWERON INDICATED THE SILOAM/DISTRIBUTION 12KV CB A // SERVICER AT STATION- CB LOCKED OUT// CHECKING REPORT OF TRANSFORMER FIRE//TOM - 0845 // 39830879B00197 FUSE OPEN - ISOLATING ONLY KNOWN FAULT//TOM - 0905 - SERVICER IN STATION READY TO CLOSE DISTRIBUTION 12KV CB A AND PERFORM PARTIAL RESTORE - UP TO OPEN FUSE ON 879-197 (56 CC TO REMAIN OUT UNTIL REPAIRS ARE COMPLTED)//TOM CREW REQ, BAD 25 KVA, AND CUTOUT, ALSO NEED TO BRING OIL CLEAN UP KIT, ACTUAL POLE IS 902-562 AJB TON FIRST REST STEP. REM STP.
1070 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2018-07-19 15:44 | 2018-07-19 23:18 | 287 | 454 | 4799501 | 46781 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | DOL 844478 // SCADA indicates high side moab on mobile tr kp-7 open @ 1543 // station personnel report bad mobile tr cable, requires repairs, unable to replace//cod 1593 //
1071 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-03-29 16:53 | 2014-03-30 00:30 | 108 | 457 | 4535031 | 46772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE IS OPEN//WILL HAVE TO OPEN OTHER 2 PHASES// B & C PHASES OPENED @ 1830 *** @ 1908 -HLC`S REM. AT POLLE 857-20 *RECL ON AT 1907 - NTA- GO TRACK NEEDED. BAD CUTOUT BURNED TOP OF POLE OFF... RELEASED BY CREW 076S01 REPAIRS COMPLETE. RESTORED @ 00:30. SH RELEASED BY CREW 07 VER/PDP IDCC CNT316 XXXX
1072 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-06-28 19:42 | 2008-06-29 03:15 | 103 | 453 | 58090-1 | 46659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4 SOLID COPPER ONE SPAN/ GOING TO PUT SPAN UP/WIRE UP PATROLING REST OF LINE WIRE DOWN 20-2059 CREW REQUIRED NO. 4 SOLID COPPER RELEASED BY CREW 078S03 AJB IDC XXXX
1073 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-03-29 18:55 | 2018-03-29 21:26 | 309 | 151 | 4151601 | 46659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 38831149000078 restored at 2126.
1074 | Hazard | 3303901 | LESLIE | HYDEN | 2008-12-14 05:38 | 2008-12-14 09:14 | 216 | 216 | 58129-1 | 46656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WR 27671521 RECLOSER OPEN ON POLE 316-99 , WIRE OFF POLE TOP PIN ON POLE267-123 ,MADE REPAIRS RESTORED POWER AT 09;14 VER/LDA IDC XXXX
1075 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-03-11 20:03 | 2014-03-11 23:38 | 217 | 215 | H4469301 | 46655 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | STATION REQUIRED AIR BREAK SWITCH 33 OPEN AT 2005 HRS STATION IN ROUTE RELEASED BY CREW 078S03 //PH 3 S.A. FAILED ON 12KV SIDE OF 69-12KV TR AT GRAHN // 1918 - PH 3 69KV FUSE BLOWN (128 CUSTS). 2003 OPENED LEON-MOREHEAD CKT INTERRUPTING 256 CUSTS //PER B.O. ONLY C PHASE CUST INITALLY INTERRUPTED 159 CUST- THIS OUTAGED 217 CUST //VER/GAH L3/HFP HFPC CDC92 CNT256 IDCC XXXX
1076 | Whitesburg | 3309302 | VICCO | JEFF | 2020-11-15 08:40 | 2020-11-15 14:15 | 139 | 335 | 4677591 | 46565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | recloser open @ 372-C4-194. one span of primary and neutral down from pole 373-131 to pole 373-130.. #4 cu primary #2 neutral. will need line crew Released by crew 077S11 power restored at 14:15
1077 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-09-15 19:30 | 2008-09-16 00:40 | 150 | 310 | 64455-1 | 46500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3312202// STS WR # 26280696 WIRE DOWN 37830126000006 @ 2309 CREW REQUESTED FETR UPDATED TO MIDNIGHT. WIRE DOWN RELEASED BY CREW 077S10/// REPAIR SLEEVE PULLED LOOSE FROM OUR CONDUCTOR VER/JHM MLRC OK IDCC PN216 XXXX
1078 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-06-01 14:58 | 2008-06-01 22:07 | 292 | 429 | 53767-1 | 46428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308401// ARMS BROKE ON POLE 159..5 OPENED CLAMPS ON POLE 159..4 GOT POWER UP TO POLE 159..4 AT 17..15 RESTORED LAST 22 CUSTOMERS AT 22..07 VER/KEP IDC XXXX
1079 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-11-14 18:44 | 2020-11-14 23:22 | 167 | 278 | 4676201 | 46426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 33-D-17 is arcing, will have to open main 3 phase line up to make repairs, will need help to cut outage time down// will have to open up 3 phase at sec. pole 9-D-232 to make repairs// will keep track of time and call before re energizing// opened sec on 9-D-232 at 22:59 closed back in at 23:22//cod 167
1080 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-07-28 16:47 | 2020-07-28 18:19 | 504 | 92 | 4246511 | 46368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout on 236-167,It is feed on a 1 span tap that doesnt have a fuse,Will be making repairs,Recloser restored at 18:19.
1081 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-04-11 14:34 | 2009-04-11 16:36 | 380 | 122 | 51512-1 | 46360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802//A PHASE OUT//COD 380//BAD CUTOUT ON POLE 1105-385,CLEARED IT OFF-LINE,ALSO CLEARED BAD ARRESTOR AT 2-113.CLOSED IN AND RESTORED//VER/CRB IDC XXXX
1082 | Pikeville | 3402002 | KEYSER | STONECOAL | 2013-04-10 15:03 | 2013-04-10 17:22 | 447 | 139 | 4995641 | 46334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TOP OF POLE 1129-306 BURNED OFF // OPENED REC. ON 1152-271// OPENED SWITCHS ON 1129-311// CLOSED SWITCHS ON 1129-167 AT 16:45// CLOSED SWITCHS ON 1129-311 AT 17:22 RESTORING ALL CUST. EXCEPT 2 SCHOOL FLASHING LIGHTS/ SDB / 1612 / 2 CC REST. ALSO SEE PO ORDER 4010781. VER/SDB IDC LAST 2 CUSTOMERS OK WITH DELAY CHANGED ENDTIME FROM 1612 4/15 XXXX
1083 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-01-21 21:45 | 2014-01-22 13:20 | 54 | 935 | 4299991 | 46314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF, NEED 4 MEN, 40 CL. 4 POLE, POLE TOP PIN AND INS. CUTOUT AND ARRESTOR. MANUAL POLE. ** DUE TO POOR ROAD CONDITIONS CREW WILL BE CALLED OUT TO MAKE REPAIRS ASAP WHEN SAFE TO DO SO.TOP OF POLE BURNT OFF, NEED 4 MEN, 40 CL. 4 POLE, POLE TOP PIN AND INS. CUTOUT AND ARRESTOR. MANUAL POLE. DUE TO POOR ROAD CONDITIONS CREW WILL BE CALLED OUT TO MAKE REPAIRS ASAP WHEN SAFE TO DO SO. COD-54 ISO OCR 37830319000034 VER/HFP L3/HFP IDC XXXX
1084 | Whitesburg | 3309302 | VICCO | JEFF | 2018-09-27 15:37 | 2018-09-27 21:10 | 139 | 333 | 4168571 | 46287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | looks like bad insulator on middle phase deadend insulator 19.9 manuel pole Released by crew 077H14
1085 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-02-27 06:24 | 2021-02-27 09:25 | 327 | 181 | 4260031 | 46187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rec. open on pole 49-331.will patrol..xfm. cutout broke o pole 260-55..will lift hottap to isolate.repaired.restored..
1086 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-02-23 05:57 | 2019-02-23 08:55 | 298 | 178 | 4846991 | 45994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rec. open on pole 190-C3-459.c phase fault.will patrol..cutout failed on pole 190-354 and fed back through 40t on pole 190-21.will make repairs..repairs made // recl in @ 0830 // Fuse in @ 0855
1087 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-06-18 01:32 | 2013-06-18 17:30 | 48 | 958 | 4361121 | 45984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 466-38 IS BROKEN, NOT TRUCK ACCESSIBLE, NEED 1-40 4 POLE 1-PRIM DE #2 AL, 1-PRIM DE 6A CW, RC UNIT #2 AL, 2 CLEVIS, 2NEU GRIPS #2, 1-10 KVA XFMR 7.2 KV, 1 T BKT, 1-CUTOUT, 1GROUND, GUY WIRE & 24 INS, 6A & #2 FOR SPLICING & SPLICES, LINE CREW & R/W CREW RELEASED BY CREW 077E02 - CAN CLOSE POWER RESTORED AT 1730 MWL COD-48 ISO LF 37830466000032 VER/HFP L3/HFP IDC CHANGED FROM UNKNOWN XXXX
1088 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-04-18 04:33 | 2020-04-18 10:45 | 136 | 372 | 4715311 | 45768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | At 0433 Poweron predicted that a section of the Johns Creek 34kV DA scheme is out. No hazard reported Recloser 26-237 is open target Cphase&ground fault, patrolling/// Bad 19.9 cutout on 74-81, crew in route//// Rec @ 26-237 in@1009///One txmf isolated @ 74-81 Released by crew 078S11,repairs made all cust restored @ 1045 please close ticket thanks.bt
1089 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-11-15 10:19 | 2008-11-15 17:15 | 151 | 416 | 65148-1 | 45681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007903//,,,POLE 453-79 IS BURNING MAKING ARRANGMENTS TO OPEN SUBSTATION SO LINE CAN BE ISOLATED AT POLE 453-72 BY CUTTING JUMPER,,,CUT JUMPER AT 10:20 ALL BACK ON EXCEPT CUSTOMER BETWEEN POLES 453-72 TO 453-79,, RELEASED BY CREW 078S02 RELEASED BY CREW 078H07 VER/KEP MAF REMOVED MOMENTARY OUTAGE STEP SEE TT H65148-1 IDC XXXX
1090 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-08-13 07:27 | 2014-08-13 10:33 | 245 | 186 | 4364531 | 45570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE HAS FELL NO BREAKER IS OPEN AT THIS TIME/"A" PHASE ONLY AT START COD-245/= OPENED @ 0959 AND CLOSED @ 1033 ON GOAB 483A-196 RELEASED BY CREW 077S01 VER/DKG A PHASESLEEVE PULLED OUT AT REC 459-166 A PHASE CUST OUT ENTIRE TIME VER/DKG L3/DKG AJB
1091 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-07-05 13:19 | 2016-07-05 14:44 | 536 | 85 | 4534701 | 45560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | NO POWER OFF UNTIL RECL OPENED @ 1319 572 CUST // CLOSED RECL @ 1322 /// CLOSED SW @ X-ARM SPLIT AT POLE 254B-6 AND PHASE LAYING HOT ON ARM.,NEED 9 X-ARM,,2 ARM PINS,,PTP,,3 PIN INS.(19.9 KV).XCO,,ARR. & BRKT. BUCKET ACCESS..WILL REQUIRE OUTAGE ON MAIN LINE..RGP. // CLOSE THIS ORDER PLEASE AJB TOF0805 REMOVED MISSTEP. AJB
1092 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-12-31 18:55 | 2010-12-31 19:50 | 827 | 55 | 57428-1 | 45485 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | EMERGENCY OUTAGE TO REPAIR LTC IN INDEX STATION // 827 CUST VER/ARN IDC XXXX
1093 | Pikeville | 3311401 | REEDY STATION | DEANE | 2019-01-22 05:26 | 2019-01-22 10:24 | 341 | 298 | 4702321 | 45484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3311401 // loop burnt into on pole 37830306000171 C PHASE (120 CUST) OPENING GOAB @ 37830306000007 TO SAFELY MAKE REPAIRS/loop burnt into on pole 37830306000171 C PHASE (109 CUST).. opened GOAB 306-7loop burnt into on pole 37830306000171 C PHASE (109 CUST).. opened GOAB 306-7 at 09:40 made repairs restored power at 09:24 -- THIS DUPLICATED
1094 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2008-06-01 17:13 | 2008-06-01 19:25 | 344 | 132 | 53940-1 | 45408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400602//WHEN TRYING TO RESTORE 53751-1, LOOP BURNT OPEN ON POLE 164-47//WILL OPEN ON POLE 187-15 TO MAKE REPAIRS ON POLE 164-47.//COD 205// VER/DBM
1095 | Hazard | 3309302 | VICCO | JEFF | 2008-05-05 08:35 | 2008-05-05 09:11 | 1259 | 36 | 57051-1 | 45324 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | 3309302//STATION SERVICER ISOLATING EQUIPMENT THAT FAILED NOW, POTENTIAL TRANSFORMER FAILED. VER/HFP IDC XXXX
1096 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-02-10 20:43 | 2009-02-11 05:30 | 86 | 527 | 57541-1 | 45322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WR # 28455909 // PATROLING LINEPOLE ON FIRE-CALLING B REYNOLDS ONLY A PHASE OUT 86 CUST AT STEPDOWN/ CREW TO OPEN/OPENED "B" & "C" (COD-66) PHASE AT MIDNIGHT CLOSED IN ALL PHASES AT 0530 DUP FOR OUTAGE AT MIDNIGHT H57541 VER/KEP L3/KEP MLR OK
1097 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-12-26 10:00 | 2015-12-26 13:22 | 317 | 202 | 4561311 | 45134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 535-17 POWER STILL ON AS OF RIGHT NOW OPENED GOAB ON POLE 536-96 AT 10:00//OPENED REC 512-56 AND CLOSED SWS 487-169 @ 1052 RESTORING 126 CUST//SEE DOL CASE #: 628380 FOR DETAILS// RESTORED ALL CUST AT 13:22 RELEASED BY CREW 077H14//SEE ALSO 4562151// VER/DBM AJB
1098 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-09-04 21:15 | 2011-09-05 01:00 | 361 | 225 | H1158470-1 | 45125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | PHASE LAYING ON CROSSARM//POLE ON FIRE//CREW ENROUTE//ONLY B & C PHASE OPEN//COD 195//OPENED PHASE "A" @ 2115 (COD +361)//TOTAL COD 556//ARM BURNT OFF NO TRUCKSARM BURNT OFF NO TRUCKS RELEASED BY CREW 078S08 //VER/GAH IDC XXXX
1099 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-07-11 07:15 | 2010-07-11 08:44 | 612 | 89 | H64966-1 | 45084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3309103// SERVICER OPENED A SET OF RECL`S TO ISOLATE A ENERGIZED CONDUCTOR.CONDUCTOR BURNED DOWN AT RECLOSER ON POLE 520-9, OPENED RECLOSER ON 448-365 AT 07:15 TO ISOLATE, OPENED SWITCHES ON 472-200 TO ISOLATE TROUBLE CLOSED RECLOSER AT 448-365 AT 07:36 ENERGIZING UP TO POLE 472-200. MAD IDC XXXX
1100 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-07-11 12:35 | 2008-07-11 13:26 | 884 | 51 | 51208-1 | 45084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3202202// TOP OF 75FT POLE BROKE OFF NEAR EMILY FORK//SERVICER OBTAINING FAULT POLE #//PHASES WRAPPED//CREW LEAD R MARCUM WAS IN AREA AND FOUND THIS SHORTLY AFTER IT HAPPENED///IS ATTEMPTING TO UNWRAP PHASES//JRV ON SITE @ 13:05R MARCUM AND CREW ALREADY HERE.....BROKEN POLE TOP 794-64....OLD POLE TOP...TOO WEAK FOR HEAVY 556 WIRE.....CREW TEMPORARILY PULLING POLE TOP BACK STRAIGHT WITH OLD DE-ENERGIZED LATERAL CONDUCTOR.....CROSS ARMS OK....HINGING AT POINT OF BRACE ATTATCHMENT....SHOULD BE A MLR OK
1101 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2008-07-05 07:57 | 2008-07-05 13:38 | 465 | 341 | 62675-1 | 45027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FEEDER LOCKED OUT . SERVICER WORKING ON SECTIONALIZING AND RESTORING CKT AT 0840 CB CLOSED REST 381 CC SECTIONALIZER OPEN AND TAGGED AT POLE 147D248 ** 84 CCFEEDER LOCKED OUT . SERVICER WORKING ON SECTIONALIZING AND RESTORING CKT . TIME NEEDS TO BE CHARGED TO WO# DKY0047336 WR# 24367926 VER/HFP IDC XXXX
1102 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-04-25 00:48 | 2012-04-25 02:20 | 489 | 92 | 4705281 | 44988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, FOUND BAD CUTOUT ON POLE 231-45, REPLACED AND RESTORED POWER. CC = 544. VER/SDB IDC XXXX
1103 | Pikeville | 3407103 | TOPMOST | KITE | 2021-10-16 08:07 | 2021-10-16 10:24 | 328 | 137 | 4354951 | 44936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed C/O on pole 37830209000195// power restored @ 10:24 /// Off @ 0807 On @ 1024
1104 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-08-14 21:40 | 2022-08-15 11:15 | 55 | 815 | 4739761 | 44825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Recloser open on 421-130, customer saw flash on pole 397-59, deadend bells look bad will need squirt boom to make repairs bridge want not safe for big truck Released by crew 077H03///restored at 1115
1105 | South Williamson | 3411401 | DEWEY | INEZ | 2009-03-03 07:45 | 2009-03-03 09:17 | 487 | 92 | 54432-1 | 44804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3411401//SWITCH 746-218 WAS CLOSED AT 0746//DC ONLY 487 CUSTOMERS OUT AFTER AUTO RESTORATION//RELAY MISOPERATION3411401//SWITCH 746-218 WAS CLOSED AT 0746// RELEASED BY CREW 079S01 VER/DKG ALSO SEE OUTAGES H54432-1B AND H54432-1A IDC CHANGED FROM DSTATION AND RELAY MISSOPERATION 5/19/2009 XXXX
1106 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-05-03 16:25 | 2021-05-03 23:10 | 200 | 405 | 4517621 | 44782 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser is open on 453-496/ patrolling line/ Removed vine off of 453-81. Also isolated bad cutout on 453-270.Linecrew required. Recloser 453-496 in at 2008. one customer off. Released by crew 078S11///Complete BR
1107 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-05-11 20:46 | 2011-05-12 09:23 | 59 | 757 | 4068711 | 44663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE ONLY COD 59 VER/KEP
1108 | Pikeville | 3421001 | BREAKS | CITY | 2017-07-03 22:41 | 2017-07-04 02:41 | 186 | 240 | 4070931 | 44640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AT 2239 SCADA INDICATED LOVELY-MOUNT STERLING 34KV CKT LOCKED OUT/DOL CASE 754173/38820795C00056 MLR
1109 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-03-27 20:56 | 2009-03-28 01:35 | 160 | 279 | 62227-1 | 44640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE PULLED OUT OF SLEEVE AT 38830351000034, HOT ON GROUND, OPENED C PHASE SWITCH ON POLE 38830351000032, C PHASE ONLY OUT,//CALLED BILL LYNCH AT 2156//COD 156 RELEASED BY CREW 078S05--- @ 2345 - WILL HAVE TO OPEN SWITCHES ON POLE 32 FOR APROX 90 MINUTES TOPUT UP WIRE DUP IN HOIS. ALL CUST RESTORED AT 0135 **** RECL *** PHASE ISSUES. PLEASE FIX , STRANDED CUSTOMERS ..PAUL PARSONS. IDCC CNT657, PN290 XXXX
1110 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-04-23 14:44 | 2020-04-23 18:57 | 176 | 253 | 4740741 | 44528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Top found blown off C phase stepdown TR at pole 37830271A11065Released by crew 077H20
1111 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2015-04-14 16:40 | 2015-04-14 17:51 | 627 | 71 | 4318331 | 44517 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POWER RESTORED AT 1751 BONNYMAN-HAZARD #2 69 LINE BURNT DOWN ACROSS OUR DISTRIBUTION CAUSING THIS OUTAGE VER/SEF L3/HFPXXX AJB
1112 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-11-09 00:26 | 2010-11-09 04:00 | 208 | 214 | 54155-1 | 44512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | "C" PHASE RECLOSER OUT POLE 876-B-28 // COD - 287 //..PATROLLING...1 SPAN PRIMARY DOWN 900-1..C PHASE RECLOSER OUT..TOOK ALL 3 REC.876-28 AT 2AM..REPLACED WIRE..BACK ON AT 4 AM...BB //VER/GAH L3/ JKW IDC PHASE A NOT C CHANGED COUNT FROM 287 XXXX
1113 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2018-10-13 08:51 | 2018-10-13 14:45 | 148 | 354 | 4246191 | 44496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | no outage till Recl open/opened 67D1-505 @ 08:51opened 67D1-505 @ 08:51, opened 67D-203 @ 09:02//closed ocr @ 09:16 . 811 # 1810130034, CREW ENROUTE to replace pole L3/HFP
1114 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-03-05 05:34 | 2012-03-05 15:10 | 77 | 576 | 4550821 | 44352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VERIFIED RECLOSER OPEN ON POLE 574-C2-201 AND TAGGED FOR B. REYNOLDS // B. REYNOLD REPLACING TRANSFORMERS AND NEUTRALS BEYOND THIS POINT // COD 77//..POWER BACK ON @ 15:10 RELEASED BY CREW 078H07// VER/DBM IDC XXXX
1115 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-05-31 01:03 | 2018-05-31 03:10 | 349 | 127 | 4525581 | 44323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rec. open on pole 262-177////will patrol///line fuse cutout broken on pole 286-10..will make repairs..fed back through single rec. on pole 262-259 and took rec. out on 262-177.please send copy to Tom Mamming
1116 | South Williamson | 3411401 | DEWEY | INEZ | 2021-08-17 20:00 | 2021-08-17 22:29 | 297 | 149 | 4091041 | 44253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1140574 // DA RECL 744-D2-527 locked out @ 1956 per SCADA //found broke cutout on pole 769-a-89//replaced cutout// cod 297
1117 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-02-17 23:46 | 2022-02-18 13:12 | 57 | 806 | 4500691 | 44134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL# 1184392//Recloser is open on 596-27, patrolling////Isolated trouble @ 621-42 Recloser 596-27 in@ 0540 Hot to S.B.on 621-42 tagged to DDCRecloser is open on 596-27, patrolling////Isolated trouble @ 621-42 Recloser 596-27 in@ 0540 Hot to S.B.on 621-42 tagged to DDC//// Srand broken hanging dn into neutral couple hundred feet past pole 31. Hillside will need foot patrolled in daylight.Manual tc&lc required. crew on site FETR 14:30 3 spansofwire down no truck Released by crew 078H06
1118 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-07-20 19:43 | 2008-07-21 10:25 | 50 | 882 | 54527-1 | 44100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THIS TROUBLE ORDER HAS APPOX. 50 CUSTOMERS HIGH WIND AND TREE NEED SERVICER TO REFUSE ON POLE 38830069C14001 TRUCK TO POLE RELEASED BY CREW 078E04RISER WIRE FROM HLC TO ARRESTOR HAS BROKEN LOOSE..CUTOUT IS STILL IN...HAVE PATROLLED LINE AND FOUND A FEW AREAS MLR OK
1119 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-06-24 08:10 | 2021-06-24 10:20 | 339 | 130 | 4801671 | 44070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hendrix wire has burnt down 2 phases @ pole 785-D2-272. Opened switches on pole785-D2-331 to isolate . Crew is onsite to make repairs/// all repaires made and restored @1020
1120 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2019-09-06 03:46 | 2019-09-06 06:48 | 242 | 182 | 4986721 | 44044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830269A00331 this is a primary metering pole witch has 2 bad cutouts on the load side of the metering, i put the 3solid blade bipasses in06:48(power restored) and took the primary metering offline, crew required to replace cutouts Released by crew 078H09///replaced broken cutouts///complete BR L3/HFP
1121 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-01-18 06:14 | 2008-01-18 08:16 | 361 | 122 | 57510-1 | 44042 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | 3403201//SECTIONALIZER OUT ON POLE 141A116. LOOKED OVER LINE EVERYTHANG LOOKED OK. REDONE CAUSE CODES AFTER LATER OUTAGE BAD SECTIONALIZER WAS PROBLEM VER/KEP IDC XXXX
1122 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2016-01-14 12:46 | 2016-01-14 19:10 | 115 | 384 | 4620001 | 44020 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | ARRESTER ON DIST SIDE OF STATION TRANSFORMER FAILED. STATION CREW ENROUTE.//SEE DOL CASE 632008 FOR SWITCHING//ARRESTER ON DIST SIDE OF STATION TRANSFORMER FAILED. STATION CREW ENROUTE. REPAIRS COMPLETE.ARRESTER ON DIST SIDE OF STATION TRANSFORMER FAILED. STATION CREW ENROUTE. REPAIRS COMPLETE. RELEASED BY CREW 076S02 VER/KEP AJB
1123 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2022-08-06 14:02 | 2022-08-06 20:48 | 108 | 406 | 4695231 | 43848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830284000036 40/5 nbt needs a pole top (big one has a lat ) critter still on line (taking off will kick main line and crew will have off making repairs remove at that time )--call duane for info--crew req-ds080622 Released by crew 078S01. crew on site. repairs made recloser in @ 20:48 complete
1124 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-12-21 15:11 | 2013-12-21 16:46 | 461 | 95 | H4180921 | 43795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ONLY PHASE A IS OPEN// MIDDLE PHASE (A) JUMMPED OFF OF INSULATOR ON POLE 179-B-148//SUSPECT DUE TO WIND//LINE CREW REQUIRED//COD 297//REC. POLE 202-208 ARE ALL CLOSED./// POLE 37830179B00148 MIDDLE HAS JUMPED OFF INSULATOR AND LAYING ON THE ARM. CREW REQUIRED. MANUAL POLE. THIS IS ACROSS ROAD FROM EMALENA GRADE SCHOOL. MIDDLE PHASE REC. IS OPEN ON POLE 179-194. WILL LEAVE OTHER 2-PHASES IN.REC. POLE 202-208 ARE ALL CLOSED.///OPENED OTHER 2 PHASES @ 1511 (COD +461)// VER/HFP L3/HFP IDC XXXX
1125 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2017-05-06 05:06 | 2017-05-06 10:40 | 131 | 334 | 4759311 | 43754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GROUND AND TAGS AT RECLOSER 188-A-416, POLE 188-29 GROUNDS ALSO PLACED// VER/CRB AJB
1126 | Hazard | 3302703 | HAZARD | HAZARD | 2017-07-24 07:46 | 2017-07-24 08:51 | 673 | 65 | 4170481 | 43745 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | DOL 759463//PER SCADA, 138/34 MOBILE TR AP-1 TRIPPED OUT AT 0746//COD 673//CLOSED 37830296A30445 @ 0851//RESTORED ALL CUST// VER/DBM L3/HFP XXXHFP SJG
1127 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2015-09-28 05:39 | 2015-09-28 19:40 | 52 | 841 | 4280801 | 43732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF MAIN LINE POLE BURNT OFF, POLE 184-200, CAN OPEN SWITCHES ON POLE 207-177, MADE RECLOSER BACK HOT AT 07:40, CUT LOOPS ON 207-239 AND MADE HOT AT 08:33/ UPDATE ALL CUSTOMERS RESTORED THAT CAN BE, REMAINDER OUTAGED UNTIL REPAIRS COMPLETE/ TO MAKE HOT TAP UP @ 1935 ON 207-239 OPENED SWITCH 207-54 @1928 CLOSED @1940/ VER/HFP L3/HFP AJB
1128 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2010-06-25 20:46 | 2010-06-25 22:42 | 377 | 116 | 57611-1 | 43732 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | SCHEDULED 2 HR OUTAGE FOR EMERGENCY WORK IN STATION / @2232 SWITCHING STARTED TO RETURN NORMAL / IDCC MCCST, CCSCO XXXX
1129 | Hazard | 3310502 | HADDIX | CANOE | 2016-02-26 06:11 | 2016-02-26 15:05 | 122 | 534 | 4778751 | 43676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE AND SECTIONALIZINGCUT OUT AND ARRESTOR ON POLE 25-55 WAS BAD PUT FUSE IN AT POLE ON POLE 25-48 AND PUT 20 T FUSE AND CHANGE FUSE ON POLE37830026000021 TO A 12 T//MD MADE/ADH// VER/ ADH AJB
1130 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-07-18 15:55 | 2022-07-18 19:25 | 296 | 210 | 4515521 | 43560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | A phase rec open on pole 29-A1-197. end of crossarm broke off at 290-190. need 8 foot arm and two 7200 arm pins and insulators. will have to step back and open other two phases when help gets here to make repaires. opened B and C phases at 17:55. restored all power at 19:25 Released by crew 077S10
1131 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-11-30 16:39 | 2010-11-30 19:32 | 417 | 173 | 61210-1 | 43518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 37931041 // BAD INSULATORS ON POLE 223-378 // 61337-1 CREATED TO ALLOW CREW TO PUT HOT TAPS BACK ON COD-417 VER/HFP L3/HFP IDC XXXX
1132 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-10-25 21:42 | 2013-10-26 06:45 | 80 | 543 | 4963621 | 43440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD STEP-DOWN 500 KVA, PRI BURNT FROM FIRE ,CUTOUT FAILED & HOT WIRE FELL INTO STEPDOWN CAUSING FIRE WILL NEED CREW, 38830597000071 IS OUR FAULT POLE OPENED REC, AT 23.30 TO ISOLATE BACK-FEED RELEASED BY CREW 078S09 //VER/GAH L3/HFP IDC XXXX
1133 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-03-12 09:37 | 2022-03-12 15:08 | 133 | 331 | 4606651 | 43318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser Open at 144-C-191(ASSESSING CONDITION)Recloser Open at 144-C-191,Opened both Line fuses on pole 168-6,Have a Span Primary down at pole 144-C-92,Jason hawkins is on The way to help make repairsRecloser Open at 144-C-191,Opened both Line fuses on pole 168-6,Have a Span Primary down at pole 144-C-92,Jason hawkins is on The way to help make repairs.Restored Recloser at 14:53..Restored Line fuses on 168-6 @15:08.. Released by crew 074S01
1134 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-09-10 13:03 | 2018-09-10 15:46 | 329 | 163 | 4076851 | 43259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Released by crew 074S05
1135 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-08-17 07:15 | 2015-08-17 15:10 | 91 | 475 | 4141571 | 43225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STEPDOWN FUSE OUT ON POLE 108-134, LOW SIDE CUTOUT BROKE AND LAYED DOWN ON XFMR FIN BURNING A HOLE IN IT. HAVE TO REPLACE 500 KVA STEPDOWN RELEASED BY CREW 077S02 REPLACED STEPDOWN AND RESTORED POWER AT 15:10 VER/HFP L3/HFP AJB
1136 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-04-19 23:35 | 2010-04-20 08:15 | 83 | 520 | 65324-1 | 43160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND PRIMARY ON POLE 478-415 I TRIED FUSE AFTER CLEARING UP ARRESTER AND FUSE BLEW ALOT OF SMOKE COMING OUT OF UNDERGROUND 3 PIPE. THERE IS TRUCK ACCESS CABLE IS 19.9 RELEASED BY CREW 078S02..........CABLE FAULTED AT THE RISER POLE ..... MAKING SPLICE...... BLR //VER/CRB IDC XXXX
1137 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-10-06 15:08 | 2019-10-06 19:00 | 186 | 232 | 4102581 | 43152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva csp xfmr..on p- 876-98.. knocked out center phase rec on p-876-368 Released by crew 076S01 // restored @ 1900
1138 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-08-18 18:46 | 2022-08-18 21:10 | 341 | 144 | 4762201 | 43127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DDC Tags / DOL 1231387 / Recloser Open 96-C1-465(ASSESSING CONDITION)Recloser Open 96-C1-465.Bad Step Down at pole 73-B-642,Isolated step down and Restored Recloser on 96-C1-465 at 20:27..Recloser Open 96-C1-465.Bad Step Down at pole 73-B-642,Isolated step down and Restored Recloser on 96-C1-465 at 20:27..Bad 500 Step Down Crew Required Will need Flaggers Going to replace Tomorrow.CREW ON SITE. WORK COMPLETE
1139 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-02-08 07:39 | 2010-02-08 16:12 | 84 | 513 | 52894-1 | 43092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33777642 // HIGH SIDE FUSE BLOWN// "B PHASE ONLY" STEPDOWN TR BAD. CREW WILL REPLACE TR AND TRANSFER LOAD OFF B PHASE TO BALANCE.HIGH SIDE FUSE BLOWN// OPENED UP OTHER 2 PHASES AT 1306 , CC 138 , CLOSED AT 1450 COLD LOAD P.U TOOK OUT RECL OPENED NO. SW AT POLE 265-406 . CLOSED ALL RECL AT 1510 228CC 162 CC OUT UNTIL N.O. IS CLOSED. ALL CUST REST AT 1612.STS WR # 3377764 VER/PDP IDC XXXX
1140 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-04-17 16:59 | 2009-04-17 18:22 | 519 | 83 | 57340-1 | 43077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3301701//SCADA INDICATES FEEDER LOCKOUT @ 1659//COD 1263// == ARRESTERS WENT BAD ON PHASES A,B, CUT IN CLEAR AND CHANGED CUTOUT ON TAP LINE ==// VER/DBM IDCC TON1825 XXXX
1141 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-12-06 02:34 | 2013-12-06 05:50 | 380 | 196 | 4104121 | 43030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BROKE ON 3 PHASE TAP ON POLE 173-18 , WIRE FELL ON TOP OF CUTOUT AN TOOK RECLOSER OUT ON POLE 174-278. *** CREW REPAIRING WIRE NOW..CLOSED RECLOSER ON POLE 174A-278 @ 04:25 , THIS RESTORES ALL POWER , EXCEPT 3 PHASE TAP ON POLE 173A-18, CLOSED LINE FUSES ON POLE 173A-18 BACK IN @ 05:50WIRE BROKE ON 3 PHASE TAP ON POLE 173-18 , VER/HFP L3/HFP IDC XXXX
1142 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-04-25 21:54 | 2010-04-26 09:06 | 64 | 672 | 51121-1 | 43008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER DUTY SUPERVISOR WILL WAIT UNTIL DAYLIGHT TO WORK RECLOSER IS OPEN ON POLE 11-A-536, GOT PATROLLING LINE. GOT BAD CUTOUT IN CAMP CREEK, CLEARING IT NOW. FAULT WENT THROUGH RECLOSER ON POLE 35-A-1 AND OPENED RECLOSER ON POLE 11-A-536, PLEASE SEND TO PERRY FARMER TO CORDINATE. VER/KEP L3/KEP IDC LOOKS LIKE THIS SHOULD BE PH A ONLY CHANGED COUNT FROM 150 XXXX
1143 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-12-30 13:42 | 2020-12-30 16:28 | 312 | 166 | 4836221 | 42972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | broke cutout and bad insulator on pole38831039000058 open goab on pole 38831039000133 and close recloser at 1525 closed goab at 1628
1144 | South Williamson | 3411401 | DEWEY | INEZ | 2022-12-06 03:14 | 2022-12-06 07:56 | 294 | 282 | 4232091 | 42966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 1256690 // recloser open on pole 744-d-527//b phase down at pole 745-36//burned down at dead end shoe//need line crew//4/0 AL wire//opened switches on pole 745-323// Released by crew 079S01
1145 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-12-26 12:26 | 2008-12-26 13:36 | 612 | 70 | 64059-1 | 42840 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | STATION OUTAGE ***STATION SERVICER AND DIST. SERVICER DISPATCHED. FAILED STATION SERVICE CUTOUTSTATION OUTAGE STATION SERVICER AND DIST. SERVICER DISPATCHED. FAILED STATION SERVICE CUTOUT . HAD TO CODE OTHER AS 58 CODE. FOR SYSTEM TO ACCEPT.. VER/PDP IDC XXXX
1146 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-08-28 14:58 | 2017-08-28 15:44 | 930 | 46 | 4304751 | 42780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL CASE # 768126//BYPASS CUTOUT BURNING ON RECLOSER POLE 833-438. WILL REQUIRE OPENING STATION BREAKER TO REPAIR// NEEDED PERSONNEL ENROUTE//ROGER MAYNARD OPENED BREAKER TO REPLACE BURNING CUTOUT ON BYPASS SWS ON RECLOSER AT POLE 833-C-438- NO OUTAGE PRIOR TO PENING BREAKER// OPENED BREAKER AT 14:58 TO MAKE REPAIRS// CLOSED BREAKER AT 15:44 RELEASED BY CREW 076H02/// VER/DKM L3/HFP XXXHFP SJG
1147 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-10-28 05:28 | 2015-10-28 18:11 | 57 | 763 | H4384751 | 42777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT LOOPS ON POLE 305-125 GROUNDED AND TAGGED TO BOBBY TACKET,,,CLOSED RECLOSER BACK IN @ 18:17 RELEASED BY CREW 078S05 OPEN 300 AMP SWITCHS ON POLE 305-64 2 MAKEUP LOOPS @ POLE 305-125 @ 1802// VER/ ADH // DUP OF 4384751 - SEE ALSO 4389901 TIMES PER VOICE REC & FIRST CALL AFTER RECL OPENED TO ISOLATE L3/HFP AJB ?
1148 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2021-07-16 13:28 | 2021-07-16 15:38 | 329 | 130 | 4920351 | 42770 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1132377/ Released by crew 074S11/ nothing found/ transmission closed their breaker restoring burton station at 1538/ Transmission found dead end bell failed
1149 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-09-22 04:00 | 2016-09-22 04:54 | 792 | 54 | 4917111 | 42768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENING OCR AT 4:00 AM TO SPLICE BAD HENDRIX CABLE TCM/ CLOSED OCR IN AT 04:54/ VER/KEP /// VER TIMES PER SCADA L3/HFPF XXXHFP AJB
1150 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-03-31 07:35 | 2011-03-31 10:42 | 229 | 187 | 60751-1 | 42765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN AT POLE #246-183 ALSO SEE 60807-1 VER/KEP IDC XXXX
1151 | Pikeville | 3403001 | PIKEVILLE | CITY | 2009-10-19 13:28 | 2009-10-19 14:04 | 1186 | 36 | 58039-1 | 42696 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | STATION CREW ON SITE// TARGET LOSS OF COOLING// OPEN @ 1328 - CLOSED @ 1404 // VER/TOM L3/TOM IDC XXXX
1152 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2020-03-24 01:14 | 2020-03-24 09:30 | 131 | 496 | 4504181 | 42656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | recl 188-46 open 131cc/Pole top burned off bad cutout at 37830188C00038/need line crew/part by truck/opened sws at 37830188C00026 to isolate/closed recl at 0330 62 cc rest/Cut out on pole 188-38 burnt top of pole to the nuetral. Opened three solid switches on pole 37830188C00026 to isolate. Closed recloser @ pole 37830188A00416 @ 3:30 to rest ore power to pole 188-26Cut out on pole 188-38 burnt top of pole to the nuetral. Opened three solid switches on pole 37830188C00026 to isolate. Closed rec
1153 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-04-12 08:15 | 2013-04-12 15:30 | 98 | 435 | 4002611 | 42630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE PATROLING LINE POLE # 37830220000018 IS BURNED OFF ; MANUAL ,WILL NEED P.T.P. AND INSL. CUTOUT ARRESTER AND BRACKET ,,7200,, 4 MAN LINE CREW AND ROW CREW ,,CAN LOWER EVERYTHING RIGHT NOW POLE STILL BURNING LOCATED AT 12396 ,HWY 451 RELEASED BY CREW 077H02///ON SITE WORKING//COD 98// VER/DBM IDC XXXX
1154 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-05-09 01:53 | 2008-05-09 11:56 | 156 | 603 | 58762-1 | 42594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF 361-25 ISOLATED ON POLE 361-56 SOLID BLADE CUTOUTPOLE TOP BURNT OFF 337-25 REPLACED//3303903//VER/CRB IDCC IDC CNT61, TON STEP 1 XXXX MAFC CNT25 FOR STEP ON PER CONF CALL
1155 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2018-07-31 18:20 | 2018-07-31 19:55 | 448 | 95 | 4882501 | 42560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENED OCR 38830091A36106 TO SAFELY REPLACE CROSSARM ON ROAD CROSSING ON POLE 38830091A36106//EMERGENCEY OUTAGE//OPENED 1820, repaires made and closed at 19:55/ ISO 38830091A36106/ COD 448
1156 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-01-17 17:20 | 2022-01-17 22:00 | 152 | 280 | 4377111 | 42560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Reclosers open fault pole is 194-65 wire burnt down/ hot on ground/ opened reclosers ***I know nothing about this order because i only closed it. Line crew foreman said wire was broke in clear and recloser was opened. I dont know what time*-BOW****
1157 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-08-03 10:48 | 2011-08-03 13:20 | 279 | 152 | 4658561 | 42408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BASED ON TROUBLE CALLS LOOKS LIKE B PHASE RECL LOCKED OUT 279 CUSTOMERSTRIED B PHASE RECLOSER, THOIUGHT IT WAS BAD, ISOLATED IT, TRIED 100T BYPASS, IT STAY FOR ABOUT 5 MINS THEN CAME OUT, I PATROLLED AND FOUND A BAD ENCLOSED WESTING HOUSE CUTOUT AND A BAD LIGHTNING ARRESTOR, ON POLE 925-14, CHANGED CUTOUT, LIGHTNING ARRESTOR, NEED TO BE CHANGED, BUT IN THE ABNORMAL, POWER IS RESTORED TO ALL CUST VER/KEP IDC XXXX
1158 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-08-25 03:06 | 2014-08-25 03:55 | 865 | 49 | 4420091 | 42385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPENED CB @ 0306 RELATED TO TICKE 4419961 CLOSED CB @ 0355 VER/DKG L3/DKG THIS IS THE BREAKER OUTAGE IN ORDER TO MAKE REPAIRS TO HENDRIX CABLE ON OUTAGE 4419961 AJB INLT PH B OUT.
1159 | South Williamson | 3411401 | DEWEY | INEZ | 2017-05-25 15:45 | 2017-05-25 17:00 | 565 | 75 | H4858761 | 42375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RT HAND PHASE OUT `B` PHASE 21 CUST//OPENED OTHERS AT 1545RIGHT HAND RECLOSER OPEN ON 649-202//TREE FELL AT POLE 649-56 AND SMALL LIMB HANGING ON LOOP AND CROSS ARM//HAVE LIMB REMOVED//INSULATOR BAD ON POLE 649-56 WHERE THE LIMB HAD FALLEN//OPENING OTHER TWO RECLOSER TO MAKE REPAIRS//REPAIRS MADE//RESTORED ALL AT 17:00// RELEASED BY CREW 079S01 38820649B00202 38820649B00056 VER/AWD AJB
1160 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-06-27 19:20 | 2010-06-27 21:15 | 602 | 115 | 58472-1 | 42365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SECTIONLZER IS OPEN ON POLE 8-A-150...PATROLLING....BROKE CUTOUT @2301 LF FK BLACKBERRY RD...R MARCUM THERE AT POLE#......TROUBLE ISOLATED.....CLOSED SECTIONALZER @ 20:30....REPLACED BAD CUTOUT ON POLE1112-34....ALL POWER ON NOW @ 21:15....JRV....06/27/10 VER/LDA AJB
1161 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-10-12 08:14 | 2012-10-12 10:45 | 280 | 151 | 4133941 | 42280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE HOT LINE CLAMP BURNT OFF FROM BASKET (STYRUP) (280 CUSTOMERS) B PHASE RECLOSER HOT LINE CLAMP CAME OFF BASKET OR MELTED ON LOAD SIDE.. NEED LINE CREW TRUCKS OK NEED 4/0 STRANDED COPPER RISER WIRE FOR RECLOSER AND NEW BASKET SQUEEZED RELEASED BY CREW 078H22 REPLACED HOT TAP POWER RESTORED 10:45 // COD-280 ISO PO 39831098B10024 VER/HFP L3/HFP IDC XXXX
1162 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-09-07 19:18 | 2009-09-07 20:28 | 604 | 70 | H52712-1 | 42280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | MIDDLE PHASE OUT ONLY (PHASE A) // COD 437// PATROLLING LINE// TRIED RECLOSER, CAME BACK OUT. CALLING DUTY FOR HELP. CREW FOUND TROUBLE.AT POLE 179-169. REPLACED BAD INSULATOR AND RESTORED POWER AT 20:25. K. NAPIER ** NEED TO SHOW BANK OF SECTIONALIZERS ON POLE 204-1 ENTER M.D . MIKE LASSLO WILL CALL WITH UPDATE TOMORROW. VER/PDP IDCC DUP TO OPEN GOAB XXXX
1163 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-11-27 11:00 | 2019-11-27 14:56 | 202 | 236 | 4073781 | 42212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop burned into on switch two poles back from recloser on pole 746-b-55///B phase is all that is out//crew enroute to make repairs//also have span of wire down at 745-83//opened switch on 745-127 to isolate//can restore up to this pole when crew repairs loop on 746-55//cod 193//
1164 | Hazard | 3303901 | LESLIE | HYDEN | 2022-04-10 18:36 | 2022-04-11 21:17 | 338 | 260 | 4745601 | 42107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 1197101//SCADA INDICATED CB L/O AT 1836/POLE FIRE AT 37830388B00166/ISOLATING AND IN PROCESS OF RESTORING FROM ALTERNATE SOURCES/SCADA INDICATED CB L/O AT 1836/CREWS EN ROUTE TO ASSESS Released by crew 077S07 times corrected from log//
1165 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-06-08 06:36 | 2010-06-08 12:00 | 144 | 324 | 58576-1 | 42066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REC. IS OPEN ON POLE256-231, POLE 256-32 IS BROKEN ANND 6A CU PRIMARY IS DOWN. JEFF COMBS ASSIGNED TO JOB. // INSTALLED NEW SOLID BLADE ON POLE`-119 AND RESTORED UP TO THAT POINT//POWER RESTORED AT 12:00 6/08/2010 //COD 144// VER/DBM IDC XXXX
1166 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-01-03 20:40 | 2015-01-03 23:41 | 232 | 181 | 4900931 | 41992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED WITH ETA OF 2048//SERVICER OPENED RECLOSER 94-D2-6503 TAGGED TO KYDDC, DUE TO POLE FIRE / OPEN AT 2040 CLOSE AT ____. POLE FIRE 118-4020 BAD CUTOUT 8FT. ARM RELEASED BY CREW 078S08/CREW ON SITE/FETR 0030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2341/PLEASE CLOSE TICKET/THANKS/VEM VER/SEF AJB INTL CUST CALL WAS HOUSE FIRE ONE CUST AFFECTED.
1167 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-01-14 03:07 | 2008-01-14 05:51 | 256 | 164 | 56488-1 | 41984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303// MIDDLE PHASE CUTOUT BURNT UP ON POLE 1112-146// COD- 256 // WILL HAVE TO HAVE SOMEONE BRING NEW CUTOUT 19.9KV //, ON SITE, CALLED J REED FOR HELP//VER/CRB IDCC CNT253 XXXX
1168 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-10-01 18:38 | 2022-10-02 01:10 | 134 | 392 | 4962451 | 41778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole top burnt off @ 600-8///////Isolated on pole 600-28 & placed ground&tag to Rick M. Rec-576-140 back in @ 2100 crew required Released by crew 078S11/arrived RM power on @01:10 please close tic RM
1169 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-05-31 02:14 | 2009-05-31 12:28 | 68 | 614 | 52419-1 | 41752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ON SITE, PATROLLING LINE//FOUND BAD ARRESTER//COD 68// VER/DBM IDC XXXX
1170 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-09-10 09:31 | 2018-09-10 12:27 | 237 | 176 | 4074141 | 41712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE 37830221000158//COD 237// bad cutoutbad cutout on37830196D00035. Power restored at 12:27
1171 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-09-26 17:31 | 2010-09-26 22:18 | 171 | 287 | 53778-1 | 41622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE THE TOP OF POLE 760-11 BURNT OFF. // FUSE BLEW ON POLE 784-40.// I ISOLATED RECLOSER ON POLE 784-200 AND CLOSED IN FUSE ON POLE 784-40 AT 18:45 MAKING LINE ENERGIZED UP TO RECLOSE POLE 784-200.// CREW ENROUTE.///CREW MADE REPAIRS/// CLOSED RECLOSURE ON POLE 784-200 @ 22:18 RESTORING ALL CUST. //VER/GAH IDC XXXX
1172 | South Williamson | 3411401 | DEWEY | INEZ | 2018-04-01 03:36 | 2018-04-01 07:15 | 190 | 219 | 4160801 | 41610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary burned down at stirrup on recloser pole 768-225///crew enroute//repairs made//restored at 7:15//complete//em///opened step-down transformer at 768-D2-418 /// opened stepdown for visible open point - no additional customer - L3/HFP
1173 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-12-24 17:08 | 2014-12-25 03:02 | 70 | 594 | 4880171 | 41580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER IS OPEN ON 502-180 PATROLLING LINE, PRIMARY DOWN FROM502-353 TO 76, 6A LINE AND TREECREW REQUIRED. CREW WILL NEED TO DO OWN TESTING&GROUNDING. THIS IS AT GASPUMP STATION WILL NEED TO CUT LOCK RELEASED BY CREW 078S11---1 SPAN #6A PRIM DOWN---FAILED SLEEVE---MADE REPAIRS---PWR RESTORED @ 03:02---TBL TKT COMP VER/DKG L3/DKGXXXX VER/SEF AJB
1174 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-08-15 14:33 | 2013-08-15 16:15 | 407 | 102 | 4668871 | 41514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON POLE 398-384, BAD INSULATOR ON 421-97.. MADE REPAIRS RESTORED POWER AT 16:15. VER/CRB L/3 CRB
1175 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-09-23 06:45 | 2011-09-23 14:59 | 84 | 494 | H4907411 | 41496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 171-9 BURNT AT ARMS, ONLY 1 OF POLE TOP LOST, 2 PHASE DOUBLE DEAD END ON AN ANGLE WITH CUTOUT AND ARRESTER ON ARM, TRANSFORMER, SERVICE DROP AND GUY WIRE. NO TRUCK, SHOULD BE ABLE TO LOWER, NEED 2 8 ARMS AND BRACES, CUTOUT, ARRESTER. STATION BUCKET MAY REACH, ONLY C PH//@ 0645 OPENED OTHER PH A//SEND TO V MULLINS //CREW ON SITE/SETTING POLE/DIFF LOCATION/TRACK EQUIP TO SITE /FETR1600/ VEM/REPAIRS MADE POWER RESTORED TO ALL CUST 1459/PLEASE CLOSE /VEM//COD 164// VER/DBM IDCC DUPT TO OPEN PH A XXXX
1176 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-07-18 03:05 | 2015-07-18 10:15 | 98 | 430 | 4905021 | 41440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REC. OPEN ON POL E37830246D00450 . PATROLLING LINE.--- BAD 500 KVA STEPDOWN TRANSFORMER, OIL SPILL, TRUCK ACCESS, RESTORED TO POLE 37830246D00458 @ 07:55.. POWER RESTORED. VER/KEP AJB
1177 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2021-01-17 17:06 | 2021-01-18 02:23 | 77 | 557 | 4874091 | 41434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Pole 253/50 top set of arms on buck arm pole broke pole 253/51 8 foot arm broke calling for duty supervisor open ocr on 230/253 at 20:09 took loops off at 21:13 230-177 tagged to R.Maggard closed ocr on 230/256 at 21:21..opened recloser 02:18 placed clamps on 230-177 restored power at 02:23..
1178 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-03-29 12:24 | 2019-03-29 14:54 | 276 | 150 | 4034931 | 41400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | opened ocrs at 1224 to change arms repairs made and power restored at 1454
1179 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-11-16 15:45 | 2022-11-16 17:56 | 316 | 131 | 4150241 | 41396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DDC TAGS// DOL#1252639reclosers at 38830379000167 opened at 1545 cutout is cracked and cause pole 739/163 to catch fire. can cut pole top off and lower arms. by squirt boom Released by crew 078S12 crewon site FETR17:45 LRM
1180 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-03-11 19:18 | 2014-03-11 23:38 | 159 | 260 | 4469301 | 41340 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | STATION REQUIRED AIR BREAK SWITCH 33 OPEN AT 2005 HRS STATION IN ROUTE RELEASED BY CREW 078S03 //PH 3 S.A. FAILED ON 12KV SIDE OF 69-12KV TR AT GRAHN // 1918 - PH 3 69KV FUSE BLOWN (128 CUSTS). 2003 OPENED LEON-MOREHEAD CKT INTERRUPTING 256 CUSTS // PER B.O. ONLY C PHASE CUST REPORTING NO POWER - 159 CUST //VER/GAH L3/HFP HFPC CDC92 CNT256 IDCC XXXX
1181 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-08-22 17:02 | 2020-08-22 19:23 | 462 | 141 | 4358301 | 41250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 38830164A13663 ug dip pole fired up and needing reworked-isolated-station breaker in at 18:30 Released by crew 078S01 // repairs made and power restored @ 1923
1182 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-06-22 16:27 | 2012-06-22 21:06 | 1101 | 279 | 4948231 | 41221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER JOHNNY SHEPHERD HE SAW A FLASH HERE POLE 37830023D40091 AND YOU WILL NEED A TREE CREW /// LEAD HAS BLOWN OUT OF CSP XFMR /// EVERYTHING IS IN THE CLEAR GOING TO TRY BREAKER /// BREAKER CLOSED IN @ 17:04 RELEASED BY CREW 074H18//LAST CUSTOMER ON AT 21:06 TIM MCCOY RELEASED BY CREW 074H10 ///VER/CRB L/3 CRB AJB PER DISP LOG.
1183 | Hazard | 3311103 | STINNETT | WENDOVER | 2017-10-08 09:06 | 2017-10-08 16:32 | 519 | 446 | 4420491 | 41108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKE OUTSIDE PHASE ON ARM RELEASED BY CREW 077S01 VER/ARN ACB
1184 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-02-27 00:36 | 2014-02-27 07:05 | 365 | 389 | 4436881 | 41071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED. WILL NEED TO CHANGE POLE 143-321 3-PHASE RECLOSER IS OPENED ON POLE 37830143C40411. I AM PATROLLING LINE NOW. CUTOUT ON POLE 37830143A00321 BROKE DOWN AND BURNED TOP OF POLE OFF. I LIFTED HOT TAP ON POLE 143-152 TO ISOLATE FAULT. I AM GOING TO CLOSE RECLOSER AT 143-411 BACK IN. I CLOSED RECLOSER IN AT 02:27 AND IT STAYED. THIS LEAVES 3 CUSTOMERS OUT. WE CHANGED POLE AND GOT LINE HOT AT 07:05//???? IDC XXXX
1185 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2010-10-26 15:28 | 2010-10-26 18:04 | 263 | 156 | 64387-1 | 41028 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | SSTATION OUTAGE //, LINE DISC TO BELLEFONTE 12KV CB AT BELLEFONTE BURNT OFF & FLATWOODS 12KV CB TROUBLE IDC XXXX
1186 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-09-28 14:59 | 2016-09-28 19:12 | 162 | 253 | H4936651 | 40986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | RELATED TO 4936651//CREW FOUND BROKE POLE 1061-A-24//OPENED 1061-B-3 TO REPAIR//COD 162//FROM 1062-9 ALREADY OUT//SEE DOL 691365 // VER/DBM L3/HFP XXXHFP AJB SEE 4936651.
1187 | South Williamson | 3411401 | DEWEY | INEZ | 2019-10-16 05:28 | 2019-10-16 06:37 | 593 | 69 | 4143911 | 40917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 962926 //SCADA indicates RECL L/O @ 0528 //cod 593 //servicer found failed cutout on associated order 4143671, possible cause of RECL outage//will attempt to repair or isolate //patroling//broke cutout on pole 744b-78//i isolated cut//
1188 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2016-06-21 18:59 | 2016-06-22 02:44 | 89 | 465 | 4401061 | 40863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WIRE OFF OF INSULATOR ON POLE 37830321D00346, MANUAL, NEED 4 MAN LINE CREW AND ROW CREW, 5 - 34.5 INSULATORS, 4 ANGLE PINS AND POLE TOP PIN GOAB OPENED & TAGGED TO KYDDC AT 321-D-630.G SHOUSE GIVEN PERMISSION TO REMOVE DDC TAGS AND REPLACE WITH OWN.KYDDC HOLD TAGS RELEASED BY CREW 077S04 WIRE OFF OF INSULATOR ON POLE 37830321D00346, MANUAL, NEED 4 MAN LINE CREW AND ROW CREW, 5 - 34.5 INSULATORS, 4 ANGLE PINS AND POLE TOP PIN GOAB OPENED & TAGGED TO KYDDC AT 321-D-630. VER/KEP AJB
1189 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-20 18:24 | 2018-06-20 23:09 | 234 | 285 | 4630901 | 40851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 STEPDOWN FUSE IS OUT,B PHASE,WILL CHECK FOR PROBLEMS/////NOTHING EVIDENT,WILL RE-FUSE////////19.9 STEPDOWN CUTOUT BROKEN ,NEEDS REPLACED.BIG BUCKET ,2 MEN .1 8FT XARM WILL HAVE TO SET UP AT EDGE OF ROAD .NEED FLAGGERS//////////MADE REPAIR &RESTORED. OFf @ 22:45 ,ON @23:09 Released by crew 074S06/// 1 customer was transferred to outage 4631781.
1190 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2014-05-06 14:17 | 2014-05-06 16:05 | 377 | 108 | 4668321 | 40716 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | 2206403// ****HOIS CREATED DUPLICATE. ORDER HAS ALREADY BEEN VERIFIED**** HAD TO DE-ENERGIZE TR # 2 AND BUS # 2 TO REPLACE FAILED INSULATOR AT SOUTH NEAL. OPEN CB AT 1417 INTERRUPTING 794 CUSTOMERS. CLOSE CB AT 1605 PU 794.// VER/RSL VER/DD AJB OPCO/ST CROSSER. SEE SAME ORDER NUMBER.
1191 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-10-02 19:22 | 2021-10-02 21:35 | 306 | 133 | 4310931 | 40698 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ooPH C ONLYoo Line side riser failed on phase C recloser. Made repairs and restored PH C REC on 876-28 @ 21:35. sh only 306 customers out /// 295 single phase and 11 3 phase customers
1192 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-11-30 21:43 | 2010-12-01 05:15 | 98 | 452 | 61476-1 | 40552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 37937925 // RECLOSER IS OPEN ON POLE 547-177 PATROLING LINE // CLOSED OCR ON 547-177 @ 0239 ENERGIZED UP TO OPEN BLADE ON 572-3 // BAD CUTOUT ON 572-3, BAD PIN INSUL ON 572-4, OPEN WIRE SEC WRAPPED 572-6/CREW ON SITE/FETR 0630/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0515/PLEASE CLOSE TICKET/THANKS/VEM VER/TOM IDC XXXX
1193 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-05-16 09:28 | 2010-05-16 21:20 | 102 | 712 | 63175-1 | 40524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER OUT ON 547/177; PATROLLING LINES; PRIMARY DOWN AT POLE 571/32 (SQUEEZE-ON FAILED); CREW NOTIFIED; LOOP CUT AT POLE571/26 AND GROUNDED ALSO GROUNDED AT 547/128; ALSO BURNT POLE AT 596/22 40 CLASS 5 DOUBLE DEAD-END, AND TAP, SPAN GUY, ALSO NEUTRAL DOWN ACROSS ROAD--CUT IN CLEAR; LIFTED HOT LINE CLAMP POLE 595/8 TO ISOLATE; BACKFED LINE AT POLE 572/94 AT 1225 HRS; RELEASE TO LINE CREW RELEASED BY CREW 078S12//CREW ON SITE PRT//REPAIRED 6A AT 572-32//CALL TREE CREW TO CLEAR//COM.21:20 IDC XXXX
1194 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-06-20 12:40 | 2011-06-20 15:10 | 270 | 150 | 4352741 | 40500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE ONLY OUT 154 CC. CREW PATROLLING CKT HAVE CPHASE RECL. LOCKED OUT.C/O BAD ON POLE 1130-76 ABOUT 1 MILE UP FROZEN CREEK IDCC CNT643 ESTIMATED CUSTOMER COUNT LOOKS LIKE PH C AND MANY MISSMAPPED CUSTOMERS XXXX
1195 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-21 17:27 | 2011-06-21 20:05 | 256 | 158 | 4366921 | 40448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RELEASED BY CREW 078S01 CLOSED REC. AT 20:05//COD 256 //RECLOSRE 142-144 FAILED TO ISOLATE TROUBLE AND THIS RECLOSER OPENED//AFTER MANUALLY OPENING 142-144 AND PATROLLING THIS SECTION OF LINE, CLOSED IN UP TO 142-144 (ISOLATED IN TRBLE ORDER 4374391)// VER/DBM IDC XXXX
1196 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-06-15 14:46 | 2017-06-15 15:49 | 1102 | 63 | 4973751 | 40354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B AND C PHASE BLOWING TOGETHER ON POLE37830223B00229/ SCADA OPENED AT 1446 CLOSED BREAKER 1503 RESTORING 633 CUSTOMERS/ SJGC TOF14:47, STEP1 TON15:03 PER DOL, STEP2 CNT0, PN 37830223B21253
1197 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-07-06 14:05 | 2022-07-06 18:02 | 279 | 237 | 4398571 | 40248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Phase B burned off at 38831027C00404 and going to open Recl 38831027C00604 to make repairs//opened Recl at XXXX Released by crew 074X05Phase B burned off at 38831027C00404 and going to open Recl 38831027C00604 to make repairs//opened Recl 38831027C00604 @1750 closed @1802 restoring all Released by crew 076S02
1198 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2011-11-01 20:53 | 2011-11-02 00:02 | 373 | 189 | 4043521 | 40247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKEN CROSSARM..ONE OUTSIDE PHASE FLOATING DOWN INTO NUETRAL & TV & PHONE CABLES AT 1089B370..NEED CREW..CAN USE BUCKET..556 WIRE NOT BROKE..CAN SECTIONALIZE & GET SOME CUSTS ON..CC 373.// NEED 9` ARMS (BRING 8` ALSO) BRACES, INSULATORS & TIE WIRE & BIG BUCKET// 2201 CB CLOSED, 250 CC RESTORED. --- SDB / 0002 / SWS AT POLE 428 CLOSED. REST 123 CC. VER/SDB IDC XXXX
1199 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-01-18 08:39 | 2011-01-18 10:35 | 383 | 116 | 62121-1 | 40213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 38478215 // BAD INSULATORS ON POLE 247-D-446, CREW ENROUTE. SECOND TIME TODAY /// COD-383 37830247C31354 VER/HFP L3/HFP IDC XXXX
1200 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-05-21 23:05 | 2014-05-22 20:00 | 32 | 1255 | 4735261 | 40160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 440-6 IS BROKEN, NEED 45-2, 5 CLEVIS, PTP,INS, 25 KVA, C/O & BKT, 1/0 SEC DEADEND, 6A & 8A COPPER SLEEVES & WIRE TRUCK ACCESS, RELEASED BY CREW 074E11 - POWER RESTORED AT ROUGHLY 2000 CAN CLOSE MWL VER/SEF AJB TON17:25 5/18
1201 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-01-31 22:31 | 2009-02-01 04:00 | 122 | 329 | 53775-1 | 40138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY HAS BURNED APART WHERE CONNECTIONS FROM REGULATOR GO ON LINE AT POLE 401-89, NEED 2 LINEMAN, BIG BUCKET AND FLAGGING CREWPRIMARY HAS BURNED APART WHERE CONNECTIONS FROM REGULATOR GO ON LINE AT POLE 401-358, NEED 2 LINEMAN, BIG BUCKET AND FLAGGING CREW MLR OK
1202 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-01-10 01:24 | 2015-01-10 04:20 | 228 | 176 | 4925071 | 40128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN @ 206A-43 TO 206A-42, RECLOSER OPEN & TAG TO DDC GROUNDS PLACED @ 206A-42 NEED LINE CREW TO REPAIR TRUCK OK RELEASED BY CREW 078S05,,CREW ON SITE..REMOVED DDC TAGS AT 03:05,,ALL REPAIRS MADE, ALL POWER RESTORED /// TALKED TO SERVICER # 4 CU BURNT OFF / FAILED AT STIRRUP (BASKET) AT RECLOSER VER/HFP L3/HFP AJB
1203 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-09-18 15:18 | 2012-09-18 17:33 | 297 | 135 | 4063821 | 40095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TIM SMITH, WALLACE MELTON & BRIAN CLEMONS // OPENED RECLOSERS ON POLE 37830249C20349 @ __15:18_____ TO ISOLATE POLE THAT IS ON FIRE // ////VER/CRB L/3 CRB IDC XXXX
1204 | Hazard | 3303901 | LESLIE | HYDEN | 2022-04-06 19:16 | 2022-04-06 22:16 | 855 | 166 | 4732641 | 39990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 1196260/ Leslie-Hyden CB E Tripped @ 1916, top of pole is broke, and guy wire is on c phase, pole 388-b-166 top is broke on ASH LN off of old 80
1205 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-07-20 21:22 | 2010-07-21 02:18 | 135 | 296 | 54345-1 | 39960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN FROM RECLOSER POLE , WILL REQUIRE FLAGGING CREW TO PUT BACK UP C PHASE IS DOWN BURNT INTO AT POLE , WILL HAVE TO OPEN OTHER TWO PHASES WHEN WE PUT BACK UP . PUT WIRE BACK UP OPEN ED OTHER TWO PHASES AT 0130 , RESTORED POWER TWO ALL CUSTOMERS AT 0218 . 1/0 ACSR APEARED TO HAVE HAD A BAD PLACE AT A STIRRUP JKC//VER/CRB IDCC CNT469 INITIALLY PH A NOT C XXXX
1206 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-02-06 03:57 | 2010-02-06 06:47 | 235 | 170 | 65821-1 | 39950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEADEND BELL BAD ON POLE 470-16 RECLOSER OPEN ON 470-46 , REPLACED DEADEND BELL RESTORED POWER AT 06:47 IDC XXXX
1207 | Hazard | 3302704 | HAZARD | KENMONT | 2009-06-19 00:56 | 2009-06-19 19:55 | 35 | 1139 | 50961-1 | 39865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP CONFIRMED FUSE OUT PATROLLING LINE//REMOVED TREE FROM PRIMARY AT POLE 37830297000081//LINE CAME BACK OUT PATROLLING AGAIN//OPENED A LOOP AT POLE 37830297000084 TRYING A PARTIAL RESTORE//FOUND BAD DEAD END INSULATOR AT POLE 37830297000062//RESTORED COMPLETE 19:55 061909 077S04 L3/HFP IDC XXXX
1208 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-01-15 22:08 | 2012-01-16 01:05 | 225 | 177 | 4263241 | 39825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | <<C PHASE RECLOSER ONLY>> OPEN ON 38830785D40121 DUE TO PRIMARY CONDUCTOR BREAKING AT STIRRUP ON LINE SW POLE 809-81. OPENED SWITCHES ON 809-81 @ 00:40, COMPLTED REPAIRS AND CLOSED SW @ 1:00. CLOSED PH C REC ON 785-121 @ 1:05 RESTORING ORIGINAL OUTAGED CUSTOMERS. SH RELEASED BY CREW 076S02 IDC XXXX
1209 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-12-22 02:34 | 2008-12-22 05:46 | 207 | 192 | 62145-1 | 39744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE HAS BURNED DOWN ON POLE 356-89 WILL NEED 3 MEN AND A HAND COIL OF # 4 COPPER "B" PHASE ONLY COD-207 OPENED "A"&"C" @ 0502 COD-198/ ALL POWER RESTORED @ 0546 PUT WIRE BACK AND CLOSED RECLOSERS BACK IN AT 0546 VER/KEP L3/KEP IDC XXXX
1210 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-02-28 04:24 | 2013-02-28 11:11 | 655 | 407 | 4861981 | 39735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3417602--**KY CUSTS**--NEW CAMP/ARH 12KV CKT LOCKED OUT CC1156 **655 CUSTS IN KY**--POLE FIRE AT 942-B-1459 ON WV SIDE OF TUG FORK--OPENED SWS AT POLE 942-1400 *NOT ON PO MAPPING*--CLOSED CB AT 0522 REST 650 KY CUSTS--505 CUSTS REM OUT--KYDDC ISSUED HOLD ORDER TO ROADDC ON SWS AT POLE 942-1400--ISOLATED FAULT--REST 201 WV CUSTS AT 0825--REST 282 WV CUSTS AT 0850--22 CUSTS REM OUT--HOLD ORDER ISSUED--REST 5 KY CUSTS AT 1111--REST 17 WV CUSTS AT 1120 //VER ANM IDC XXXX
1211 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-10-08 20:07 | 2021-10-08 22:24 | 290 | 137 | 4333211 | 39730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser open at 190-C3-459 showing Ground fault on B Phase(ASSESSING CONDITION)Broke cutout at 190-C-104 made repairs and restored at 22:24.
1212 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-19 16:15 | 2008-12-19 17:02 | 845 | 47 | H60467-1 | 39715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308401// B PHASE OUT ON POLE # 204-264, PATROLLING LINE // FOUND 2 PHASES CAME OFF INSULATORS // COD 612 - GOING TO HAVE TO OPEN OTHER PHASE WILL OUTAGE 560 ADDITIONAL CUSTOMERS// OPENED OTHER PHASE @ 1615 -- 3308401// B PHASE OUT ON POLE # 204-264, PATROLLING LINE, FOUND PHASE OFF INSULATOR ON POLE 204-232. TOOK ALL POWER OFF AT 16:15, RESTORED ALL AT 17:02 PLEASE CLOSE ORDER...THANKS HFP VER/KEP L3/KEP IDC CHANGED COUNT FROM 560 XXXX
1213 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-03-02 07:02 | 2013-03-02 14:00 | 105 | 418 | H4866171 | 39710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASE REC POLE 224-7 OPEN - 105 CUST //, PATROLLING LINE. //OPENED PH 3 RECL AT 0702 - 105 CUST, THEN OPENED SWS AT POLE 225-28// CLOSED A & B RECLS AT 0725 RESTORING 40 CUSTS // PHASE 3 RECL WOULD NOT CLOSE // WILL CLOSE PH 3 BYPASS WHEN GETS BIG BUCKET //HICKMAN, CLEMONS, AKEMON & EMBERTON TO ASSIST //COLLETT FOR STORES //@ 1020, CLOSED C PHASE BYPASS ON RECLOSER 224-7, RESTORING 19 CUST//AED CREATED FOR BAD RECLSOER// POWER RESTORED AT 1400 RELEASED BY CREW 077S04 IDCC DUP TO OPEN PH C XXXX
1214 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-07-11 22:32 | 2022-07-12 03:55 | 806 | 323 | 4463311 | 39704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DOL 1221345/ DA Scheme Outgae/ Load Transfer/
1215 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-07-08 14:45 | 2016-07-08 20:36 | 113 | 351 | 4586871 | 39663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RECLS OPEN ON POLE 38821012A00229 A AND B PHASE REC BYPASSED//THEY ARE IN ABNORMAL DATA BASE//DOORS BURNT UP IN BOTH SWITCHES//REFUSED AT 20:36 POWER RESTORED//LEADS ARE NOT REMOVED HANDLES AND POLE TAGGED TO DDC ISO 38821012D00055 VER/AWD AJB
1216 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-07-12 05:18 | 2011-07-12 10:01 | 150 | 283 | 4526271 | 39631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED SW AT POLE 43-40 TO REPAIR AN OPEN LOOP, OPENED SW AT 43-40 AT 9:32, ORIGINAL OUTAGE HAD LOOPS BURNT OPEN AT 43-50. THE TWO TAPS AND TRANSFORMER WAS ON WHEN WE ARRIVED AT POLE 43-50.//GAB
1217 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-11-30 12:45 | 2018-11-30 14:07 | 483 | 82 | 4493931 | 39606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | EMERGENCY OUTAGE TO REPLACE CROSSARM // ISO OCR 37830426C00563 OFF@ ON@ rotten xarm, outside phase fell out and on to the ground. I need a crew and a 8ft. xarm to make repairs. we will have to open up recloser 426-563 . opened at 12:45rotten xarm, outside phase fell out and on to the ground. I need a crew and a 8ft. xarm to make repairs. we will have to open up recloser 426-563 . opened at 12:45 closed @ 1407
1218 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-09-20 03:05 | 2012-09-20 10:45 | 86 | 460 | 4070791 | 39560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSER ON 453-91 IS ON. PRIMARY BROKE ON 453-97, SUSPENDED IN AIR BY FUSE LOOKING AT 453-102. PLEASE HAVE ADDED TO MAPS. VERY POSSIBLE TO WORK WITH TRUCK. RELEASED BY CREW 078S11/ CREW ON SITE STARTING REPAIRS TCM// OPENED OCR ON 453-91 AT 09:45 , REPAIRS MADE CLOSED IN AT 10:45 TCM// ALSO NEED TO SEND A COPY TO ENGINEERING NEUTRALS STOLEN FROM 453-97 TO453-104, ALSO SEND COPY TO R/W LARGE DEAD TREE AT 453-97 IF FALLS ON LINE WILL BREAK SEVERAL POLES, NEEDS CUT ASAP ! VER/KEP IDC XXXX
1219 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2017-11-18 23:25 | 2017-11-19 14:24 | 44 | 899 | 4575271 | 39556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Bad recloser 55-223 isolated/tagged to KYDDC./ ISO 37830055000223/ COD 44
1220 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-07-08 18:43 | 2016-07-08 19:10 | 1465 | 27 | 4584201 | 39555 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | T-LINE OUTAGE RESTORED 1910/// VER/DKM AJBC MCCST
1221 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2020-06-28 12:01 | 2020-06-28 14:39 | 250 | 158 | 4083851 | 39500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 1031433 // Ph A conductor burnt open at SW pole 69-A3-1056 //cod 250 // Primary down from 69-A3-1056 to 69-A3-1052. Trucks to pole. //,repairs made all cust restored @ 1439 please close ticket thanks.bt // cod 250
1222 | South Williamson | 3200302 | BELFRY | TOLER | 2015-06-26 23:43 | 2015-06-27 03:00 | 200 | 197 | 4669351 | 39400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 079H03 LEAD BURN OFF A PHASE ON THREE PHASE RECLOSER WILL OPEN TO MAKE REPAIRS R THOMAS//OPENED OTHER PHASES @ 0234//THIS OUTAGED YHE OTHER 335 CUSTS //ORGINALLY 200// VER/CRB AJB
1223 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-11-08 07:14 | 2011-11-08 08:55 | 390 | 101 | 4058261 | 39390 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | TRANSFORMER OUTAGE - TDC NOTIFIED STATION PERSONNEL ENROUTE / DISTRIBUTION SERVICER ENROUTE - PH 3 34KV BUS POT TR FAILED AT SUBSTATION VER/TOM L3/TOM IDCC TOF0718, TON0905 XXXX
1224 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-07-14 13:09 | 2016-07-14 14:07 | 678 | 58 | 4629841 | 39324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKE CROSSARM OPENED 0N POIE 185 AT 13:09 REPAIRS MADE AND POWER RESTORED AT 14 :07 AJB
1225 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-05-11 22:13 | 2011-05-13 12:45 | 17 | 2312 | 4079281 | 39304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE
1226 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-09-16 00:36 | 2018-09-16 09:34 | 73 | 538 | 4103381 | 39274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | will check in the AM per latenight guidelines sts had sturrip burned off on recloser pole L3/HFP
1227 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2013-08-09 20:49 | 2013-08-09 23:00 | 299 | 131 | 4641641 | 39169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT ON PHASE A.//COD 299// VER/DBM IDC XXXX
1228 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-06-11 13:15 | 2014-06-12 17:30 | 23 | 1695 | 4042451 | 38985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ROTTED OFF LAYING OVER PHONE COMPANY OWNED/INLINE SINGLE PHASE WITH OPEN WIRE SECONDARY/POLE 1124-3124 AND POLE 1124-3060 BACK YARD NO TRUCKS/CREW REQUIRED/OPEN AND TAGGED TO DDC/OPEN FUSE 1124-3059 AND TAGGED AT 1315 HRS RELEASED BY CREW 078S03.. AJB TOF09:44
1229 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2019-05-19 19:25 | 2019-05-20 00:30 | 140 | 305 | 4301511 | 38764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | crew required #4 copper primary /no trucks will have to open recloser to make repairs/968 is address//no tag/grounds on place//opened RECL 38830251000116 at 2331 to make repairs //cod 124 (+16)////ISO 38830250000174 ¦¦ VERIFIED TIMES PER VOICE RECORDER - L3/HFP
1230 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-12-20 12:00 | 2012-12-20 13:35 | 408 | 95 | 4486861 | 38760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER IS OPEN ON POLE 103-210 WILL BE PATROLLING CLOSED IN RECLOSER@13:35 AND IT STAYED IN THIS OPENED THREE TIMES THIS DAY ALL LATER FOUND RECLOSER WAS OPENING AND NOT OPERATING CHANGED CODES TO EQUIP FAIL ON ALL OF THEM AND ENTERED AED VER/KEP IDC CHANGED CAUSE FROM UNKNOW XXXX
1231 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2021-06-07 01:11 | 2021-06-07 04:20 | 205 | 189 | 4677431 | 38745 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | 138/34kV TR 1 tripped from service affecting 205 CC, Station & Line Enroute no cause at this time /// Crews found failed L/A on 34kV Bus FETR 0430
1232 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-12-13 17:18 | 2009-12-13 20:45 | 300 | 207 | 53091-1 | 38692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#33055524//POLE FIRE/CREW ON SITE/WILL NEED TO INSTALL NEW COSSARM FETR2200/ VEM/NEW FETR2130/VEM/NEW FETR2100/VEM/ALL REPAIRS MADE AND POWER RESTORED TO ALL CUST 2045/INSTALLED 100 AMP SOLID BLADES ON 70-524/PLEASE NOTE TO MAPPING/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 M/D CREATED . IDC XXXX
1233 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-11-01 04:27 | 2010-11-01 05:50 | 466 | 83 | H50534-1 | 38678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MIDDLE PHASE BROKE RIGHT AT THE STIRRUP ON RECLOSER POLE *CC 114 SERVICER WILL NEED TO OPEN ALL RECL WHEN REPAIRS START.MIDDLE PHASE BROKE RIGHT AT THE STIRRUP ON RECLOSER POLE..PUT UP WIRE CLOSED REC AT 550...BB IDCC DUP TO OPEN RECLOSERS XXXX
1234 | Hazard | 3310502 | HADDIX | CANOE | 2020-07-19 20:06 | 2020-07-19 21:16 | 552 | 70 | 4184751 | 38640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 2006 OCRS at 37830051000058 tripped from service affecting 800 CC, DA Loop scheme auto reconfigured & restored 248 CC from alternate source at pole 37830169D00305, servicer patrolled line & found no cause. closed reclosers in at pole 37830051000058 at 2116 restoring all customers Bypassed Reclosers due to possible problem with reclosers on pole 37830051000058 opening up without a fault. bypassed recloser Released by crew 077S10
1235 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-06-04 08:35 | 2015-06-04 13:30 | 312 | 295 | 4509551 | 38640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSERS OPEN ON POLE 425-493, BAD CUTOUT ON POLE 425-124 BURNT POLE OFF.OPENED SOLID BLADES ON POLE 425-411 TO ISOLATE & PLACED TAGS FOR GEORGE WHITAKER..CLOSED RECLOSERS IN AT 10:10. RELEASED BY CREW REP077S11 REPLACED POLE POWER RESTORED AT 13:30// VER/ ADH L3/HFP HFPC FP37830425000124 AJB
1236 | South Williamson | 3411401 | DEWEY | INEZ | 2014-02-01 15:04 | 2014-02-01 16:59 | 336 | 115 | 4335141 | 38640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO POLE 38830744D20527//COD 333////PATROLED FOUND NOTHING//WOULD LIKE TO TRY VIA SCADA//CLOSED IN AND STAYED AT 16:19// DROPPED OPEN AGAIN/FOUND CUTOUT BROKE ON 768-235//HAVE REPAIRS MADE//RESTORED AT 16:55//COMPLETE//EM RELEASED BY CREW 079S01 VER/KEP L3/HFP HFPC TON1655 IDCC XXXX
1237 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-10-09 16:46 | 2015-10-09 19:52 | 207 | 186 | 4333681 | 38502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN FEEDING UNDERGROUND RISER ON 37820008C000115 REPLACED ROAD SIDE CUTOUT ON 37820008C00115 RESTORED POWER AT 19:52//MADE MDC TO SHOW 100T L/F//A PHASE COD 207 VER/CRB // BUSINESS OBJECTS ALSO SHOWS ALL CALLS ON `A` PHASE & SCADA REFLECTS SAME = L3/HFP XXXHFP AJB
1238 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-12-19 15:15 | 2012-12-19 16:17 | 621 | 62 | 4483491 | 38502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | PRIMARY CONDUCTOR ON CROSSARM AT POLE 224-D-106 // STA BREAKER OPENED AT 1515 & REPAIRS WILL TAKE APPROX 1 HOUR //VER/GAH IDC XXXX
1239 | South Williamson | 3200302 | BELFRY | TOLER | 2008-07-29 12:09 | 2008-07-29 15:20 | 201 | 191 | H61762-1 | 38391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ON SITE, POLETOP BROKE OFF , POLE#1064-67, MAKING REPAIRS, TWO PHASES ALREADY OUT, OPENED OTHER PHASE AT 1346// BACK ON @ 1520 IDC BELFRY TOLER CUSTOMERS WERE TRANSFERED TEPORARILY TO BARENSHEE POUNDING XXXX
1240 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-09-21 12:08 | 2021-09-21 14:14 | 407 | 126 | 4263621 | 38386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on 287/9 C phase recloser open on 214/944.//Isolated TR on 287-9 to isolate the failed cutout and restored Recl on 214-D4-944 at 1342-will be changing cutout
1241 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-11-07 10:17 | 2008-11-07 10:58 | 936 | 41 | 62985-1 | 38376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001101// CREW OPENED BREAKER TO SAFELY REPLACE CUTOUT ON POLE 67-D-103 VER/LDA IDC REPLACING BURNT OFF CROSSARM IN STATION ZONE XXXX
1242 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-06-15 17:05 | 2022-06-15 21:05 | 283 | 240 | 4129141 | 38345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Opened A&B at 1954 175 cc/closed all 3 at 2051/changed out stepdown
1243 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-08-08 11:32 | 2018-08-08 13:40 | 299 | 128 | 4925351 | 38272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on37830189D00144.cutout broke on pole 37830189D00144.. made repairs. L3/HFP
1244 | Hazard | 3420001 | SOFT SHELL | VEST | 2016-01-24 04:30 | 2016-01-24 11:25 | 92 | 415 | 4646371 | 38180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PATROLLING LINE, PRIMARY AND NEUTRAL DOWN AT POLE 108-28,# 4 SOL CU, WILL NEED BIG BUCKET AND CREW/ ISO 37830108000116/ COD 92/ VER/BOW AJB
1245 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-08-07 06:46 | 2017-08-07 12:46 | 106 | 360 | 4232481 | 38160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | A PHASE AND GROUND SHOWS FAULTS (206 CUST), PATROLLING LINE. CROSSARM BROKE ON POLE 179-14, WILL NEED LINE CREW AND MANUEL R-O-W CREW // OPENED B&C PHASES @ (269 CUST), POWER RESTORED. OPENED RECLOSER AT 09:33 VER/ARN /// PER B.O. C INITALLY OUT - 106 CUST = L3/HFP HFPC FP37830179B00194 SJG
1246 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-04-02 00:55 | 2012-04-02 02:40 | 363 | 105 | 4638351 | 38115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 115-83 BAD 19.9 CUTOUT CHANGE POLE 115-633 REC. OUT REPLACED BAD CUTOUT AND LA IDC XXXX
1247 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-02-09 16:46 | 2022-02-09 19:40 | 219 | 174 | 4462781 | 38106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 199-41 crew required big bucket hot tap burnt off Released by crew 078S03///Repairs made recloser in @ 19:40///Complete BR Released by crew 078H22
1248 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-09-03 02:00 | 2012-09-03 05:13 | 220 | 193 | H4998231 | 37938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | "A" PHASE ONLY COD-144THERE ARE 3 SINGLE RECLOSERS ON POLE 143-411. ONLY THE A PHASE RECLOSER IS OPEN. ALL THREE REC OPEN AT 0200. I AM PATROLLING LINE NOW. I CLOSED RECLOSER IN AND IT STAYED. RECLOSER STAYED IN ABOUT 2 MIN. AND THEN OPERATED A FEW TIMES AND THEN ALL 3 RECLOSERS OPENED UP DUE TO FAILED INSULATOR AT POLE 143-70. THIS WAS AT 2:00 AM.--- SDB / 0300 / 88 CC REST. --- SDB / 0513 / 276 CC REST IDCC DUP TO OPEN RECLOSERS XXXX
1249 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-12-03 01:41 | 2009-12-03 06:22 | 135 | 281 | 61787-1 | 37935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW WORKING ORDER 59046-1/REPAIRS MADE ON THAT ORDER NEW PROBLEM WALKING AROUND HILLSIDE TO FIND IT VER/KEP L3/KEP IDC XXXX
1250 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-02-08 07:39 | 2010-02-08 15:10 | 84 | 451 | 52894-1 | 37884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33777642 // HIGH SIDE FUSE BLOWN// "B PHASE ONLY" STEPDOWN TR BAD. CREW WILL REPLACE TR AND TRANSFER LOAD OFF B PHASE TO BALANCE.HIGH SIDE FUSE BLOWN// // OPENED UP OTHER 2 PHASES AT 1306 , CC 138 , CLOSED AT 1450 COLD LOAD P.U TOOK OUT RECL OPENED NO. SW AT POLE 265-406 . CLOSED ALL RECL AT 1510 228CC 162 CC OUT UNTIL N.O. IS CLOSED. ALL CUST REST AT 1612.STS WR # 3377764 VER/PDP IDC XXXX
1251 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-05-30 05:14 | 2011-05-30 11:25 | 144 | 371 | 4208281 | 37875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER IS OPEN ON 453-331 PATROLLING // FOUD WIRE BURNT DOWN - ISOLATED AT STEPDOWN AT POLE 429-67, CLOSED OCR 453-331 @ 0752 // RELEASED BY CREW 078S11//CREW ON SITE//REPAIRED CONDUCTOR POWER RESTORED 11:25 PRT// RELEASED BY CREW 078H03//VER/CRB IDC XXXX
1252 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-12-29 23:41 | 2022-12-30 07:29 | 83 | 468 | 4377101 | 37848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | line is currently being reconducted so reclosure is not on pole 1040-18, 3 cutouts on pole 1040-51 which is not maped, fuses on 1040-51 are still closed in wire is broke in the clear on pole 1040-53. wire down on pole 1040-53 to pole 1040-94 . need line crew and manual row crew, #2 wire Released by crew 077H24..opened line fuse at 05:13 to make repairs rstored @ 07:29 Released by crew 077H03
1253 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-01-09 08:20 | 2008-01-09 11:21 | 209 | 181 | 55056-1H | 37829 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND 3 PHASE POLE BURNT OFF ,OPENING REMAINING RECLOSERS , FRAMING DOWN ON POLE//3409303 , MADE BACK HOT AT 11:14//3409303)//VER/CRB IDC DUP FOR OPENING OTHER 2 PHASES XXXX
1254 | Hazard | 3303902 | LESLIE | WOOTON | 2019-03-25 01:38 | 2019-03-25 12:17 | 59 | 639 | 4021671 | 37701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HELD ¦¦ BROKE CROSSARM ON 341-20 Released by crew 077S01 // COD 59
1255 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-04-19 05:44 | 2012-04-19 14:00 | 76 | 496 | 4686271 | 37696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OUTAGE RESTORED BY ACCIDENT... PRED. RECLOSER OUTAGE AT POLE 1098-606 ///VER/CRB IDC XXXX
1256 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-04-30 17:10 | 2013-04-30 21:07 | 159 | 237 | 4060601 | 37683 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE OUT AGAIN 159 CUSTCOND OFF INSULATOR,NEED 2 MEN,CUTOUT,ARRESTOR,TIEWIRE /// SEE ASSIGN TAB - INSTRUCTIONS TAB FOR MORE DETAILS. VER/HFP L3/HFP IDC XXXX
1257 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-12-08 14:30 | 2013-12-08 16:30 | 314 | 120 | H4115171 | 37680 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | OPENED CB @ 1430, FUSE BLOWN AT STATION EARLIER, CREW IS MAKING REPAIRS NOW.ARRESTER ON LOW SIDE OF STATION TRANS. IS BAD. SUBSTATION CREW IS ON SITE. CLOSED CB @ 1630ARRESTER ON LOW SIDE OF STATION TRANS. IS BAD. SUBSTATION CREW IS ON SITE. WE CHANGED ARRESTER AND GOT STATION BREAKER BACK ON AT 16:30 BASED ON ADX LOOKS LIKE A PHASE OUT AT APROX 1131 - 181 CUST - THIS RECORD FOR WHEN CB OPENED FOR B & C PHSE CUST WHEN CB OPENED VER/HFP L3/HFP IDC OPENED PH C AND A XXXX
1258 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-01-06 19:29 | 2010-01-06 21:44 | 279 | 135 | 64388-1 | 37665 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE OPEN @ 1929 // DROPPED REMAINING CUSTOMER @ 2053 - THEN CLOSED IN THE 46KV CB "A" AT ELKHORN CITY AND PICKED UP HENRY CLAY/ASHCAMP @ 2144 // IDC REMAINING CUSTOMERS ON 64093-1 XXXX
1259 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-11-01 23:12 | 2020-11-02 04:48 | 119 | 336 | 4627311 | 37657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | C phase fuse open @1110-C-21, checking. Couldnt find any trouble isolated line section for cold load @1110-D-35 and 37, closed L/F in @1110-C-21 @0355. Closed L/F @1110-D-35 @0422. Changed the 20-T @ pole 1110-C-21 to a 30-T, picked everything up @0448. Released by crew 074S05
1260 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-06-22 21:09 | 2016-06-23 19:48 | 169 | 1359 | 4411341 | 37647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE RECLOSER OUT ON 1073-2513.CREW REQ, FOUND 454 POLE BURNTED OFF, LIFTED HTSP ON POLE 1121-14, NO TAG OR GROUNDS, JUST SINGLE POLE LINE EXT, UP ON HILLSIDE ACROSS FROM IMELS GREENHOUSE WELL NEED TO HAVE TECH LOOK AT THIS CAN WAIT TILL TOMMORROW, NO ONE IS LIVING IN TRAILER, BUT IS ACTIVE ACCT BY AMGCREW REQ, FOUND 454 POLE BURNTED OFF, LIFTED HTSP ON POLE 1121-14, NO TAG OR GROUNDS, JUST SINGLE POLE LINE EXT, UP ON HILLSIDE ACROSS FROM IMELS GREENHOUSE WELL NEED TO HAVE TECH LOOK AT THIS AJB
1261 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-06-20 07:24 | 2015-06-20 14:00 | 95 | 396 | 4615251 | 37620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE SPAN #4 ACSR PRIMARY DOWN FROM POLE 209-92 TO 209-40. MIGHT GET SMALL BUCKETT TO POLE 209-92. NEED LINE CREW .WIRE BROKE AT BACKETT. RELEASED BY CREW 078S01..RE=OPENED 209-6 AT 12:54 CLOSED AT 14:00,,,BLR RELEASED BY CREW 078H07 AJBC LCD38830209000006
1262 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-05-22 11:03 | 2011-05-22 14:00 | 213 | 177 | 4121671 | 37611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | B PHASE OPEN ONLY//COD 213//LEFT HAND RECLOSER OUT ON POLE 746-243. PATROLLING NOWLEFT HAND RECLOSER OUT ON POLE 746-243. PATROLLING NOW. CLOSED RECLOSER AT 13:54. CLOSED LINE FUSE ON POLE 746-65 AT 14:00. //COD 213//AED CREATED// VER/DBM IDC XXXX
1263 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-01-28 17:45 | 2008-01-28 19:35 | 347 | 110 | 60517-1 | 37606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409002//B PHASE RECLOSER OPEN ON POLE 785-1297, ALSO B PHASE HOT LINE CLAMP LEAD BURNT OFF AT TOP OF CUTOUT AND WENT PHASE TO PHASE AT POLE 44, C PHASE FUSE OPEN ON POLE 44//COD 347// REPAIR IN PROGRESS. REPAIRED HOTLINE CLAMP ON B PHASE FUSE AND CLOSED LINE FUSES ON POLE 44 AT 19:23 PICKING UP ALL PHASE C CUSTOMERS(47 CUST)// CLOSED B PHASE RECLOSER ON POLE 1297 AT 19:35 PICKING UP REMAINING 300 CUSTOMERS. SH// VER/DBM IDCC CNT47 XXXX
1264 | Hazard | 3311103 | STINNETT | WENDOVER | 2019-11-12 04:52 | 2019-11-12 11:45 | 91 | 413 | 4022401 | 37583 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 37830412B00296 BURNT OFFPOLE 37830412B00296 BURNT OFF, truck acess, need pole top ext candle stick insulator, no wire broken, will open high side step down to get visible opening not able to get to step down or recloser with truck also need 7200 cutout t-bracket arrester, tagged to ddc no grounds placed Released by crew 077H14..changing pole now..all power restored @11:45..p.hicks L3/HFP
1265 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-03-26 03:52 | 2021-03-26 09:27 | 112 | 335 | 4376751 | 37520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed, burned the top of p-876-379..50 class 2, no truck access. maybe able to use pole top ext.. rec out on 876-102.. grd and tagged on p-876-102 for Austin Preese
1266 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-02-15 19:37 | 2018-02-16 01:05 | 114 | 328 | 4845981 | 37392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HOLD ORDER REQ'D // DOL 804388// DA load xfer//B phase loop burnt open on 37830171000188 // cod 114 // ISO// Released by crew 077S05//see also 4846901 & 4846031
1267 | Hazard | 3309302 | VICCO | JEFF | 2011-12-21 08:01 | 2011-12-21 08:57 | 667 | 56 | 4192301 | 37352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | PIECE OF THE ARM DROPED OFF LAYING ON PHASE == REMOVED == PUT POWER ON // COD 667// VER/DBM IDC XXXX
1268 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-05-03 13:51 | 2019-05-03 18:36 | 131 | 285 | 4207901 | 37335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830209000013 ROTTED OFF & FELL OVER ¦¦ NO OUTAGE AT THIS TIME..primary approx twelve feet off the ground, opened reclosure on 209-6 @ 13:51 to safely replace broken pole//CLOSED RECLOSER @ 1836 L3/HFP
1269 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-02-11 11:05 | 2019-02-11 11:45 | 933 | 40 | 4777571 | 37320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened recloser to safely isolate transformer on pole 1057-A-49/ PO 4776611/short outage
1270 | South Williamson | 3411401 | DEWEY | INEZ | 2019-10-27 01:48 | 2019-10-27 11:02 | 303 | 554 | 4202911 | 37293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | recloser locked out on 744-527//found line fuse blown on 768-1 with broke cutout on 768-108 on that tap//also found broke cutout on xfmr bank on pole 745-a-48//this is at carlot//pieces of cutout has fell on hood of truck//isolated cutout on pole 745-48//will need big bucket//replaced cutout on 768-108 and restored tap//all that remains out is xfmr bank on 745-48//this is a vacant building//please send to damage claims because cutout fell on truck hood// opened l/f 1000 ALL RESTORED 1102//OPENED L/F 38820745A00157 UP @ 1000 TO CHANGE IT AS WELL
1271 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-07-09 08:24 | 2012-07-09 14:48 | 97 | 384 | 4634941 | 37248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON 90-10 HOT TAP AND BASKET BURN OFF RISER ON RECLOSER NO TR. ,REMOVED HOT TAP ON 90-154 GROUND LINE AND FLAGED NEED POLE 40-5 TR. TO POLE 90-318 LINE CREW DEADEND XFORM POLE POSSIBLE MAYBE LOWER EVERYTHING? CUT A FLOATING DEADEND ON 90-362 REMOVED GR. PUT HOT TAP BACK ON AT 90-154 REPAIRED RECLOSER LEAD MADE LINE AT 14:40 POWER RESTORED EXCEPT 1 CUST WHERE POLE IS BURN RELEASED BY CREW 078S04 IDC SEE 4648381 FOR LAST CUSTOMER XXXX
1272 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-05-23 08:23 | 2011-05-23 13:37 | 133 | 314 | 4139171 | 37247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQUIRED: POLE 833B-100, #4 CU BROKEN FROM DEADEND, WIRE UP BUT LOW // POLE 856-9 TO POLE 856-14 PRIMARY NEUTRAL DOWN // 856-18 TO POLE 19 PRIMARY NEUTRAL DOWN // CLOSED NO SWTCH AT POLE 880-47 AT 11:28 EN-ERGIZED TO POLE 880-30. HOLD ORDER REQUIRED FROM DDC. RESTORED ALL CUST 1337. OPENED N.O. AT 1405 INTERRUPTED 35 CUST, CLOSED POLE 880-30 AT 1410 RESTORE 35 CUST DUE TO OUT OF PHASE SWITCHING //VER/GAH AJB
1273 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-01-25 06:25 | 2009-01-25 10:09 | 166 | 224 | 59704-1 | 37184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND RECLOSER TO STILL BE IN WHEN I ARRIVED, THEN FOUND A SPAN OF #4 CU, PRIMARY DOWN ON POLE 1024-88, OPEN RECLOSER AND ISOLATED AND GROUNDED IT, AND THEN CLEARED PRIMARY OUT OF THE ROAD, HAVE CALLED FOR CREW TO BUT THIS BACK, ALSO CAN USE TRUCKS, LOOKS LIKE IT PULLED OUT OF SLEEVE RELEASED BY CREW 078S06//COD 166 VER/KEP L3/KEP MLR OK
1274 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2010-08-02 16:53 | 2010-08-03 06:04 | 47 | 791 | 60579-1 | 37177 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 3002105 STS WR # 36256284 /// POLE 45-4070 167 KVA TRANS OUT CALLED CREW SEND TO VERNON M. RELEASED BY CREW 078S08/LOADING XFMR/FETR 2211/VEM VER/HFP L3/HFP IDCC FP NULL HAD TO OPEN TRANSFORMER TO SPLIT WINDINGS, THE TRANSFORMER TOP MISSHAPED CAUSING THE LID TO NOT FIT. HAD TO GET A 167 FROM PIKEVILLE. LOCAL STORES ISSUE ADDRESSED XXXX
1275 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-08-10 03:43 | 2012-08-10 04:38 | 1149 | 55 | H4921661 | 37176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD TO OPEN STATION CB TO SAFELY OPEN SWS TO ISOLATE OPEN LOOP CONDITION// THIS OUTAGED 1149 CUSTOMERS// 698 WILL BE RESTORED WHEN BREAKER CLOSED/ REMAINING WILL BE OUTAGED FOR DURATION OF REPAIRS - OPEN CB AT 0343 CLOSED 0349 IDC XXXX
1276 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2018-11-14 14:32 | 2018-11-14 17:06 | 241 | 154 | 4398961 | 37114 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 2150502//At 1432, opened the Nolan 12kv cb at Borderland due to a defective line disc at station//cc1118//isolated the Chattaroy 12kv Cb G and closed the Nolan cb at 1448 rest 312 custs//ckts tied thru transfer bus//806 custs remain out//crew enroute to make repairs//ckt restored at 1706//// 566 of the 806 Customers on Chattaroy are Apco custs. Two different clearing devices due to opening up Nolan cicruit. Those customers were not out, or feed from Chattaroy circuit, so it is no abnormal feed. ACB
1277 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-06-02 17:50 | 2009-06-03 02:55 | 68 | 545 | 60908-1 | 37060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CANNOT GET LINE CUTOUT CLOSED...NEED TO REPLACE CUTOUT....NEED 2 MEN AND 19.9 CUTOUT AND BIG BUCKET...D LEWIS 6-2-09 ESTIMATED RESTORATION 20.00 RELEASED BY CREW 074H08//VER/CRB MLR OK
1278 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-02-18 01:44 | 2022-02-18 16:05 | 43 | 861 | 4504681 | 37023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HELD TILL AM BECAUSE OF WEATHER CONDITIONS//line fuse open on pole 38830878000038 patroling..primary down on pole 38830878000052 one span. climb one pole to splice.. can pull with truck.. check open wire when climb pole #4 copper..line crew required..RN Released by crew 074E02// Made repairs and restored @16:05
1279 | Cannonsburg | 3001401 | LOUISA | CITY | 2014-10-09 05:01 | 2014-10-09 05:45 | 841 | 44 | 4577731 | 37004 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP L3/HFP AJB CCTIN
1280 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-02-22 01:06 | 2009-02-22 06:48 | 108 | 342 | 50138-1 | 36936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801 - PREDICTED RECLOSER AT POLE 245-12 NOT OPEN. FOUND SOLID BLADE DISCONNECT FAULTED AT POLE 245-1 WHICH HAS 108 CUSTOMERS INTERRUPTED. 3000801 -CREW REQUIRED NO TRUCKS NEED TO OPEN RECLOSER AT POLE 245-12 TO REPAIR CUTOUT. THIS WILL INTERRUPT 17 ADDITIONAL CUSTOMERS RELEASED BY CREW 078S03/CREW ON SITE/FETR0730/VEM/ALL CUST RESTORED 0648/PLEASE CLOSE TICKET/THANKS/VEM IDC DUPLICATE CREATED TO OPEN RECLOSER XXXX
1281 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-19 21:44 | 2022-01-19 23:50 | 293 | 126 | 4388361 | 36918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | repairs made and restored @ 2350
1282 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2014-06-14 17:15 | 2014-06-14 20:05 | 217 | 170 | 4091811 | 36890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX CABLE BURNT DOWN (A PHASE INITALLY OUT 59 CUST// MILLER & MAYNARD & NEWSOME // OPENED SWS @ 1815 ON POLE (299 CUST) 785-D-3314/0 HENDRIX CABLE BURNT DOWN. CREW ENROUTE TO REPAIR. OPENED SWITCHES ON 785-331 @ 18:15 TO ISOLATE.4/0 HENDRIX CABLE BURNT DOWN. CREW ENROUTE TO REPAIR. OPENED SWITCHES ON 785-331 @ 18:15 TO ISOLATE.COMPLETED REPAIRS AND CLOSED SWITCHES ON 785-331 @ 20:05. SH VER/HFP L3/HFP AJB TOF17:09 INLT CUST CALL 911. CNT59 217 PH A.
1283 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-01-04 19:13 | 2022-01-05 01:01 | 213 | 334 | 4303281 | 36855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | DOL 1173550 // ISO 38830019C00050 //1 span primary down big bucket should reach recloser is still in wire broke in the clear crew will need to open recloser 1147d187 upon arrival38830019C00050 Released by crew 078S09///Waiting on Flaging Crew Released by crew 078H22
1284 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-07-15 02:34 | 2017-07-15 04:50 | 351 | 136 | 4125991 | 36632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON POLE 143-411////WILL PATROL///CUTOUT BROKE ON POLE 143B-278///LIFTED HOTTAP ON POLE 143-198 TO ISOLATE AND CLOSED REC. BACK IN @ 04:18..WILL MAKE REPAIRS.REPAIRS MADE.RESTORED RELEASED BY CREW 074S01 VER/ARN MLRC FP 37830143C40411
1285 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-12-02 21:22 | 2009-12-03 04:00 | 92 | 398 | 60546-1 | 36616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN BETWEEN POLES 108-20 & 108-116, HIGHSIDE FUSE BLOWN ON STEPDOWN ON POLE 108-134. DONT KNOW WHAT TOOK WIRE DOWN, BROKE AT CLAMP.//COD 170//ISO 37830108D20134// IDCC PN116 CNT248 XXXX
1286 | Whitesburg | 3308402 | BECKHAM | CARR CREEK | 2009-12-08 16:53 | 2009-12-08 19:57 | 199 | 184 | 57666-1 | 36616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830230C00203 WE HAVE BAD DEADEND INSULATOR, HAVE CALL CREW TO BRING INSULATORS AND HEAD THIS WAY. RELEASED BY CREW 077S08 AJBC TOF16:54 PER SCADA AND OUTAGE REPORT.
1287 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-04-06 18:51 | 2010-04-06 20:53 | 300 | 122 | 59922-1 | 36600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | EMERGENCY SCHEDULED OUTAGE TO MAKE REPAIRS TO CONNECTIONS ON POLES OUTSIDE STATION AND REPLACE FAILED INSULATOR. / ETR SHOULD BE BY 2100 HRS IF ALL GOES WELL / WR#34547024/ VER/LDA L3/DKG CORRECT AJB IDC PER DISP LOG CHANGED FROM SCHEDULED XXXX
1288 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-10-09 10:30 | 2010-10-09 13:42 | 527 | 192 | H58245-1 | 36584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TWO PHASES BURNT IN TWO ON 4/0 HENDRIX OVERHEAD. ALL THREE RECLOSERS ON 654-529 ARE IN AND ALL PHASES ARE ENERGIZED UP TO FAULT POLE 654-91. OPENED AND ISOLATED ALL THREE REC ON 654-529 @ 10:30. REDUCED OUTAGE NUMBER FR 623 TO 198 @ 11:10 (SWITCHING). REPAIRS UNDERWAY. REPAIRS COMPLETE. RESTORED @ 13:42. SH IDC XXXX
1289 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-12-20 20:49 | 2012-12-21 00:24 | 170 | 215 | 4493161 | 36550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE LOOP BURNT IN CLEAR ON 454-1651, WAITING ON LINECREW ASSISTANCE,,//COD 170 (+ 342 ONCE SWS ON POLE 454-D1-1651 ARE OPENED FOR REPAIRS)//OPENED SWS 454-1651 @ 1208(SEE H4493161)//CLOSED EVERYTHING BACK @ 1224//ISO// VER/DBM IDC XXXX
1290 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-12-10 14:45 | 2008-12-10 18:00 | 193 | 195 | 56222-1 | 36517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP 3411801// OPENED SOLID BLADES ON POLE 1011-528 -TAGGED AND GROUNDED// BROKEN CROSS ARM @ 1011-28//CROSS ARM BROKE ON POLE 1011-28, NEED TO OPEN SWITCHES ON POLE 38821011B00028 1634 RESTORED 62 CUST @ 1800 REMAINING CUST RESTORED. L3/WHV IDCC PN1, CNT127, TOF1115 XXXX
1291 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-08-19 12:21 | 2009-08-19 15:37 | 302 | 196 | 50785-1 | 36475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP BAD POST TYPE INSULATORS ON POLE # 178-16, HELP ON THE WAY, CAN OPEN GOAB ON POLE 178-297 WHEN HELP ARRIVES AND THEN CLOSE RECLOSER ON 194 @ 1416 REST 111 CUST//BAD POST TYPE INSULATORS ON POLE # 178-16, HELP ON THE WAY, CAN OPEN GOAB ON POLE 178-297 WHEN HELP ARRIVES AND THEN CLOSE RECLOSER ON 194. CLOSED RECL AT 14:06 AND GOAB AT 14:30 L3/HFP IDC LOOKS LIKE PH A OUT INITIALLY XXXX
1292 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-05-11 02:51 | 2015-05-11 03:43 | 700 | 52 | H4407901 | 36400 | DISTRIBUTION STATION | EQUIPMENT FAILURE | NONE | SCADA INDICATED 69-12KV TR 1 @ SOUTH PIKEVILLE DE-ENERGIZED. THIS HAS STATION INTERRUPTED AND APPROX 1786 PIKEVILLE AREA CUSTOMERS// STATION SERVICER AND D-LINE SERVICER CALLED IN//TOM WILL UPDATE AS INFORMATION BECOMES AVAILABLE//TOM ***UPDATE @ 1135 DETERMINED STATION TRANSFOMER HAS FAILED - LOOKING AT LOAD TRANSFER OPPORTUNITIES AND WILL NEED A MOBILE TRANSFOMER INSTALLED - ALL NECESSARY PARTIES NOTIFIED//TOM - ALL CUSTOMERS RESTORED FROM PIKEVILLE/MAIN STREET @ 1620 VER/KEP AJB
1293 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-01-26 14:16 | 2016-01-26 18:20 | 149 | 244 | 4651721 | 36356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER IS OPEN //COD 92//////FOUND BAD CUTOUT ON POLE 104-11.THIS FEEDS A VACANT SCHOOL BUILDING...ISOLATED HOT TAP ON POLE 104-92..// VER/ ADH AJB
1294 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2018-09-27 11:03 | 2018-09-27 16:15 | 116 | 312 | 4166171 | 36192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Opened Reclosers @ 1103 // no outage until recl was opened // B phase switch on pole 38820868D00183 was arcing and needed changed
1295 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-24 02:26 | 2011-06-24 15:50 | 45 | 804 | 4406981 | 36180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN ON POLE 140-C-132. POLE IS IN HOLLOW BELOW MCCARTYS. NO TRUCK. SGM. RELEASED BY CREW 078E01// A PHASE//LMR/ WILL HAVE TO TAKE OUTAGE TO REPAIR J. HEMLEPP/ WILL OPEN 3 STEPDOWNS @ 13:10116-6001/116-707/116-708 TO MAKE REPAIRS.OPEN @13:10 A&B PHASE CLOSED//@ 15:50 C PHASE WOULD NOT HOLD COD 73 IDC XXXX
1296 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-01-24 04:12 | 2014-01-24 07:00 | 494 | 168 | 4305521 | 36157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE LOAD SIDE LEAD BURNT OFF TO RECL AT POLE 272-B4-477 (494 CUST)// OPENED RECL POLE 272-B4-477 TO REPAIR LEAD @ 0506 (598 CUST) // ON 0525 // LAST CUST ON @ 0700 === RECLOSER STILL CLOSED === OPEN RECLOSER TO MAKER REPAIRS === BOPEN AT 5:05 CLOSED AT 5:25 === POWER OK === ALSO GOT BAD TRANSF ON POLE 37830272A40421 === NEED 1MAN BIG BUCKET AND 50 KVA 7200 === GOT POWER TO TRANSF AT 7:00 ==LOAD SIDE LEAD BURN OFF RECLOSER VER/HFP L3/HFP IDC ADDED 1 CUSTOMER STEP AS IN NOTE XXXX
1297 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-01-04 03:20 | 2020-01-04 04:21 | 592 | 61 | 4209831 | 36112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EMERGENCY OUTAGE NECESSARY TO REPLACE FACILITIES/OPENED RECLOSERS ON 38830876B00028 AT 0320/SAME AS 4209621/ON 0421 L3/HFP
1298 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2014-01-06 06:57 | 2014-01-06 15:15 | 87 | 498 | 4234721 | 36066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "B" PHASE ONLY COD-87POLE 211B101 BURNT IN TWO NEED CROSS ARM CREW 8A WIRE. I HAVE A LOOP OPEN ON POLE 211-416. CREW REQUIRED. CLOSED IN RECLOSER ON POLE 187-362 AT 11:05 UP TO IOS POLE 211-416 B PHASEB PHASE ONLY COD-87 POLE 211B101 BURNT INTO NEED CROSS ARM CREW 8A WIRE. I HAVE A LOOP OPEN ON POLE 211-416. CREW REQUIRED. CLOSED IN RECLOSER ON POLE 187-362 AT 11:05 UP TO IOS POLE 211-416 B PHASE RELEASED BY CREW 074S11 MD FILED ON 211-416//COD 87// IDCC CNT146 XXXX
1299 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-03-19 07:13 | 2018-03-19 08:42 | 405 | 89 | 4025481 | 36045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Emergency outage-opened reclosers on 38830206A31122 to safely replace equipment on pole 38830206C02491. Released by crew 078S05 0713-0842
1300 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-01-06 19:29 | 2010-01-06 21:35 | 286 | 126 | H64192-1 | 36036 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE OPEN @ 1929 // DROPPED REMAINING CUSTOMER @ 2053 - THEN CLOSED IN THE 46KV CB "A" AT ELKHORN CITY AND PICKED UP DRAFFIN STATION @ 2135 // IDC NEED SEPARATE OUTAGE FOR REMAINING CUSTOMERS IDC NO CUSTOMERS OUT TILL 1929 PH A THEN REMAINING OUT WHEN TRANSMISSION OPENED AT 2054 XXXX
1301 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-12-21 08:24 | 2010-12-21 12:43 | 163 | 259 | 54711-1 | 36016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN AT POLE 38830231000012, PRIMARY OPEN AT THAT POINT, 1 SPAN #2 ACSR PRIMARY. NO TRUCK, CREW REQUIRED//ISO //COD 163 // WIRE DOWN AT POLE 38830231000012, PRIMARY OPEN AT THAT POINT, 1 SPAN #2 ACSR PRIMARY. NO TRUCK, CREW REQUIRED RELEASED BY CREW 078S05/OPEN RECL.@10:20///LOAD ISSUES OPEN 232-1 AND CLOSED@232-228 AT 11:40CLOSED 40T ON 232-1@12:10//CLOSED RECL.@12:43ON232-1//ALL POWER RESTORED PRTOLLIVER// VER/DBM IDC XXXX
1302 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2012-10-19 03:13 | 2012-10-19 11:42 | 472 | 509 | 4155631 | 35953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATED FEEDER OUTAGE - SERVICER DISPATCHED AND ON SITE AT 0328 ISOLATING FAULT *POLE FIRE AT POLE 954-1138. CALLING OUT CREW. LOOPS OPEN AND TAGGED AT POLE 954-B4-194 VER/DKG MADE H4155631 FOR OPENING SWITCH TO MAKE UP LOOPS PER OUTAGE REPORT IDC XXXX
1303 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-02-09 22:11 | 2010-02-10 01:58 | 158 | 227 | 54669-1 | 35866 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, PATROLLING LINE, LOOP BURNT OPEN AT 2 HOLE PAD AT GOAB SWITCHAT POLE#1137-D-753, CALLED R MARCUM FOR HELP//RIGHT HAND PHASE ONLY IS OUT//COD 158// RELEASED BY CREW 080S01 VER/TOM L3/TOM IDC XXXX
1304 | South Williamson | 3411401 | DEWEY | INEZ | 2009-05-06 11:45 | 2009-05-06 13:51 | 414 | 126 | 59108-1 | 35844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29695877 // SWITCH 746-B-218 CLOSED @ 1145 FAULT POLE 38830768A00190 L3/HFP IDC XXXX
1305 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-04-09 17:23 | 2012-04-09 18:21 | 988 | 58 | 4658581 | 35820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RESTORED CB @ 1756//LINES SAGGED TOGETHER ABOUT 3 SPANS ABOVE THE REC PER M ISON//RELEASED BY CREW 077S12///VER/CRB IDC XXXX
1306 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-08-12 02:37 | 2009-08-12 06:58 | 137 | 261 | 60012-1 | 35757 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE IS DOWN AND HAS BROKE IN THE CLEAR RECLOSERS ARE IN AT THIS TIME I HAVE HELP COMING WE WILL OPEN RECLOSERS WHEN WE PUT WIRE BACK UP AT 0630 CREW HAS OPEN B PHASE IS DOWN AND HAS BROKE IN THE CLEAR RECLOSERS ARE IN AT THIS TIME I HAVE HELP COMING WE WILL OPEN RECLOSERS WHEN WE PUT WIRE BACK UP WE OPENED RECLOSERS AT 0618 AND CLOSED BACK AT 0658// IDC RECL ON SEPARATE OUTAGE XXXX
1307 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-02-13 08:05 | 2014-02-13 17:15 | 65 | 550 | 4378981 | 35750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CREW REQUIRED AND ROW CREW TO CLEAR WAY TO POLE-- PRIMARY WIRE DOWN BETWEEN POLE 338-32 TO 338-33.NETURAL UP-- UP OSBORNE FRK TO MAIL BX1546--TURN LEFT DOWN DRIVE TO POLE.NOT TRUCK ACCESSIBLE--MANUAL RELEASED BY CREW 077M01 - CAN CLOSE POWER RESTORED AT 1715 MWL //???? IDC XXXX
1308 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-08-29 19:04 | 2018-08-30 12:45 | 1007 | 1061 | 4012891 | 35656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr, 25 kva 19.9kv, we need 3 or 4 men and a manual row crew. I talked with George Whitaker ds we will wok in the morning. //OPENE FUSES @ 1009 (2CUST) EMERGENCY OUTAGE REQUIRED = CREW FOUND BROKEN TIE WIRE ON POLE 37830374D00041 NO TRUCK ACCESS OPENED RECL @ 1115 1002 CUST ALL ON @ 1245
1309 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-03-16 05:47 | 2017-03-16 08:40 | 206 | 173 | 4561131 | 35638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE BURNT DOWN @ RECL - 206 CUST // OPENED A & B @ 0715 (310 CUST) TO MAKE SAFE. MADE REPAIRS AND CLOSED ALL 3 REC. BACK IN @0840. DUPLICATE IN HOIS // SCADA INDICATES INITAL C PHASE OUTAGE = VER/HFP L3/HFP AJB
1310 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-05-21 17:39 | 2018-05-22 00:25 | 111 | 406 | 4388341 | 35606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Bad Insulator on pole 38820841B00129/ Closed Recl 38820841A00146 @ 2035/ closed SW 38820841B00073 @ 0020/ Closed RECL 38820865A00020 @ 0025
1311 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2022-06-27 04:22 | 2022-06-27 07:02 | 472 | 160 | 4328591 | 35592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 1217486/0422 SCADA INDICATED 12KV INTLR 1099-B3-6965 L/O//Crew patrollingDOL 1217486/0422 SCADA INDICATED 12KV INTLR 1099-B3-6965 L/O.broken x arm @ 1099d274DOL 1217486/0422 SCADA INDICATED 12KV INTLR 1099-B3-6965 L/O.opened disc @ 1099-77..broken x arm @ 1099d274DOL 1217486/0422 SCADA INDICATED 12KV INTLR 1099-B3-6965 L/O.opened disc @ 1099-77..broken x arm @ 1099d274 Released by crew 078S07 Released by crew 078H22
1312 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-04-03 05:19 | 2015-04-03 11:45 | 92 | 386 | 4262101 | 35512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | B PHASE SOLID BLADE SWITCH BURNT OFF ( 92 CUSTOMERS B PHASE)//OPENED ALL 3 RECLOSER ON POLE 235-173 IN ORDER 4264001 (227 CUSTOMERS MORE)// CLOSED RECLOSER 235-173 BACK IN @ 0710 DID NOT AFFECT CUST COUNT//CREW REQUIRED//WILL NEED 600A CUTOUT//TRUCK OK(BIG BUCKET, BUT WILL NEED EXTRA MEN TO FLAG TRAFFIC)// L3/DKGXXXX THIS IS FOR THE 92 CUST THAT WERE OFF FOR DURATION VER VOICE RECORDER AJB
1313 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-03-25 02:00 | 2013-03-25 11:42 | 61 | 582 | 4953581 | 35502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON POLE 37830179C00232, CHECKING LINE ///// POLE 37830179C00251 HAS TOP OF POLE BURNT OFF, CUTOUT BAD. 45/4 POLE WITH LASH AND XFMR. NEED FLAGGERS, WILL HAVE TO SET IN RD. TRUCK ACCESSABLE. MIGHT GET BY USING POLE EXTENSION.,,ON SITE WORKING REPLACED POLE AND RESTORED POWER AT 11:42 COD-61 ISO OCR 37830179C00232 VER/HFP L3/HFP IDC XXXX
1314 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-10-21 04:33 | 2016-10-21 05:16 | 825 | 43 | 4035531 | 35475 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | FAILED STATION SERVICE CUTOUT OUTGAE FOR CREW TO SAFELY REPLACE VER/KEP // VER TIMES PER SCADA & DOL L3/HFP XXXHFP AJB
1315 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-03-24 16:02 | 2018-03-25 10:30 | 32 | 1108 | 4050101 | 35456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire down at pole 880-21 to pole 880-22. pulled out of sleave. fuse door burnt up on pole 880-12. ned three man line crew and small piece #4 copper.. can truck. rn Released by crew 076H03 Service restored at 10:30 AM by R Blair 38830880000021
1316 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-12-26 14:45 | 2009-12-26 15:47 | 571 | 62 | 50851-1 | 35402 | TRANSMISSION LINE | EQUIPMENT FAILURE | STATIC WIRE | OPENED FEEDER CB FOR TRANSMISSION CREW TO REPAIR STATIC WIRE. / COD-1070 / MLR BOTH WV AND KY IDC CHANGED START DATE FROM 12/21 PER ALARM LOG IDC XXXX
1317 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-03-03 12:12 | 2014-03-03 12:39 | 1311 | 27 | 4447391 | 35397 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/KEP IDC OPENED BREAKER TO ISOLATE BURNING POLE XXXX
1318 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-11-04 00:29 | 2018-11-04 04:20 | 153 | 231 | 4361051 | 35343 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | (TIME MODIFIED BY DST CHANGE)B phase off insulator on pole 514B-44.B phase off insulator on pole 514B-44. power restored at 4:20 // PER TROUBLE CALLS THIS WAS A C PHASE OUTAGE --- L3/HFP
1319 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-01-25 08:10 | 2012-01-25 09:40 | 392 | 90 | 4291181 | 35280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKE AND POLE LEANED OVER INTO TREE/RESTORED 0940 VER/KEP IDC XXXX
1320 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-08-27 21:21 | 2012-08-28 10:24 | 45 | 783 | 4978691 | 35235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE BLOWN ON 57A3.IT WAS FUSED W 25T..CHANGED TO A 40T.CLOSED IN UP TO 57A6 @ 23:50.BOTH CUTOUTS OPEN ON UG..CLOSED 30T IN ON 57A6..FUSE BLEW.BAD UG.CAN GO BACK WITH OVERHEAD.COAL BELTLINE THAT USED TO CROSS OUR LINE NO LONGER HERE.NEED 3 MAN CREW.DEAD END INSULATORS & ALUM WIRE FOR A 240 FT SPAN OF PRI & NUETRAL..ALL TRUCK APPROACH & OFF HIGHWAY. COD-45 ISO LF 37820057A00006 VER/HFP L3/HFP IDC XXXX
1321 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-04-12 17:31 | 2011-04-12 19:11 | 857 | 100 | 56021-1 | 35196 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | OPENED CKT FOR ROANOKE DDC DUE TO 34KV SWITCH BURNING AT MIDDLE BURNING CREEK STATION --- SDB / 1812 / 856 CUSTOMERS RESTORED VIA FIELD TIE. --- SDB / 1911 / CB CLOSED, RESTORING 1 CUST. --- SDB / 1950 / SWITCHING COMPLETE, CKTS NORMAL. VER/SDB AJB
1322 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-09-09 02:02 | 2018-09-09 03:40 | 359 | 98 | 4061521 | 35182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Both fuses open on pole 38830091D00587, Bad arrestor. Replaced equipment. Reclosure on 38830115C00633 back in at 03:40
1323 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-08-04 02:39 | 2017-08-04 10:28 | 75 | 469 | 4222851 | 35175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID BLADE 300 AMP C/O BAD ON C PHASE @72-A-78, WILL HAVE TO OPEN ALL 3 REC. @72-A-80 TO MAKE REPAIRS, ALSO NEED A MANUAL R.O.W. CREW TO CUT UP TO POLE, NO TRUCK ACCESS. OPENED ALL 3 REC. @0936, MADE REPAIRS AND CLOSED BACK IN @1028. C COD 75/AB COD 214 37830072A00080 VER/AWD SJG (C-PH)
1324 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-05-13 02:56 | 2021-05-13 05:30 | 228 | 154 | 4582041 | 35112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B Phase OCR open (228 CC) servicer patrolling line for cause found 1 span of neutral down from pole 38830381A20315 to 38830381A20027A that crosses the road. was unable to find any reason for outage B phase recloser in at 0530
1325 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-06-16 18:51 | 2012-06-16 21:13 | 247 | 142 | 4921381 | 35074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER AT 30-6 CASUED OCR AT 29-186 TO OPEN 247 COD// RESTORED AT 2113 IDCC TON2213 XXXX
1326 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-04-05 02:57 | 2011-04-05 11:40 | 67 | 523 | 65052-1 | 35041 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSERS ON 1036-B1-315 NOT OUT...BURNT OFF CROSSARM (BAD XFMR CUTOUT) BACK ON 1012-B-150...PHASE C OFF OF ARM...CROSSARM & CUTOUT NEED REPLACED....CREW REQUIRED...TRUCK APPROACH....C PHASE RECLOSER LOCKED OUT ON POLE 1012-A-229...OTHER 2 RECLOSERS STILL HOT....WILL HAVE TO BE DE-ENERGIZED TO REPLACE ARM...//..NEED 8 CROSS ARM, 2 BRACES, 3 ARM PINS, 3 INSULATORS, & CUTOUT...// RELEASED BY CREW 080S01 THIS TICKET NEEDS TO ROLL UP INTO 65052 WHERE WE HAVE C PHASE RECLOSER LOCKED OUT ON 1012A229 IDC XXXX
1327 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-10-03 11:18 | 2009-10-03 12:31 | 480 | 73 | H66273-1 | 35040 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | CUSTOMER IS OUT DUE TO THE STATION OUTAGE CUSTOMER POLE WAS LEANING OUR EQUIPTMENT IS GOOD SHAPE NO POLE LEANING AT THE ADDRESS. TIM MCCOY RELEASED BY CREW 074H10//LOW SIDE SURGE ARRESTOR TO 69-12KV TR IN STATION FAILED CAUSING HIGH SIDE FUSE TO 69-12KV TR TO BLOW. //VER/GAH IDCC DUP TO OPEN TRANFORMER XXXX
1328 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2013-09-28 16:52 | 2013-09-28 18:30 | 357 | 98 | H4894681 | 34986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 HENDRIX BURNED DOWN AT INSULATOR..1 PHASE DOWN.CREW CALLED..785-264 HANGING DOWN ON BOTH SIDES.2 FEET OFF GROUND. @ 1652 OPENED SWS AT POLE 785-D-331 ** SWS AT POLE 785-B-1571 OPENED ON MAP BY MISTAKE. .WIRE UP CLOSED SWICHES AT 18.30 RELEASED BY CREW 076S01 DUP FROM 4894681 VER/HFP L3/HFP IDCC CCERF XXXX
1329 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2018-04-02 06:35 | 2018-04-02 14:09 | 77 | 454 | 4163391 | 34958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2150501--Line crew required, pole top is burned off at 38820869A10111. Need 45/4 pole, 8 foot arm with braces, ridge pin, 2 arm pins, 3 7200 insulators, 7200 cutout and arrester & bracket. Recloser is isolated and tagged to Dave Sammons, No grounds are placed. Emergency locate #1804020302 Released by crew 079S02repairs made on aat 14:09 d sammons
1330 | Pikeville | 3407103 | TOPMOST | KITE | 2008-04-26 06:04 | 2008-04-26 07:35 | 384 | 91 | 54258-1 | 34944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | 3407103// SCADA INDICATED THE CB LOCKED OUT @ 0604, SERVICER ENROUTE TO STATION. VER/HFP IDC XXXX
1331 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2021-07-12 13:45 | 2021-07-12 14:12 | 1292 | 27 | 4899271 | 34884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Off at 1345 due to failed insulator at 38830045D47508 Closed station bker at 1412 Released by crew 078S07 Note: Portion of 47th Street/39th Street was transferred to this Ckt at time of Lockout (Was not modeled in POR) Making CC 1292
1332 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-02-02 19:23 | 2014-02-02 20:05 | 830 | 42 | 4337941 | 34860 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION OUTAGE TO SAFELY INSTALL MOBILE TR FW-25-1/SOS 2783 REV 57 OPENED AT 1923 15 MIN OUTAGE OR LESS STATION PROBLEM RAN OUTAGE TIME OVER AND ADD. OUTAGE WILL BE NEEDED LATER TONIGHT. OUTAGE NECESSARY TO ALLOW CREWS TO REMAIN SAFE. IDC XXXX
1333 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-12-22 03:27 | 2013-12-22 05:03 | 363 | 96 | 4185821 | 34848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3-PHASE RECLOSER IS OPEN ON POLE 143-411. I AM PATROLLING LINE NOW. CUTOUT BROKE ON POLE 143-363. I AM GOING TO CHANGE CUTOUT. WE CHANGED CUTOUT AND CLOSED RECLOSER AT 05:03 VER/HFP L3/HFP IDC XXXX
1334 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-05-03 22:22 | 2009-05-04 01:24 | 303 | 182 | 64680-1 | 34843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 964-125 IS OPEN,WILL PATROL.WIRE DOWN AT RECL POLE 939-20 .MADE REPAIRS AND RESTORED VER/ARN IDCC IDCC TON0124 FIRST STEP 0130 SECOND STEP XXXX
1335 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-12-31 18:53 | 2010-12-31 19:51 | 600 | 58 | 57429-1 | 34800 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | EMERGENCY OUTAGE TO REPAIR LTC IN INDEX STATION // 600 CUST VER/ARN IDC XXXX
1336 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-05-25 21:51 | 2018-05-26 01:00 | 184 | 189 | 4497781 | 34776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A phase rec. open on pole 190-280/////will patrol///found bad 19.9 cutout on xfm. pole 167-274///repairs made.tried rec. operated twice opened back up and found 19.9 deadend insulator bad also on pole 167-274..repairs made////restored///Trouble tickets showing all phases out
1337 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-10-20 21:36 | 2018-10-21 10:45 | 44 | 789 | 4277501 | 34716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 38830165C00169 rec open--38830165C00041 has a loop burnt and arcing rec did not operate but loop will need repaired--open rec back up --ds102118--crew req nbt Released by crew 078S01
1338 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-10-08 14:00 | 2008-10-08 14:52 | 667 | 52 | 54347-1 | 34684 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP MIKE LASSL0 REPORTED TROUBLE AT TDC STRUCTURE # 333-2 (STRUCTURE DOWN) DISTRIBUTION POLE 37830296C20233 WHICH IS IN THE HAZARD/BLACKGOLD CKT. THIS IS UNDERBUILD. PER MIKE WILLIAMS & P PARSONS - TRANSMISSION CROSS ARM BROKE WILL NEED TO VERFIY IDC XXXX
1339 | Hazard | 3302703 | HAZARD | HAZARD | 2010-11-23 11:14 | 2010-11-23 13:42 | 692 | 148 | 59006-1 | 34586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED LEAD BURNT UP ON POLE 272-337 OPENED AT 272-337 AND CLOSED BREAKER AT 1200 ARRESTOR BLOWN ON POLE 272-337 CUTOUT BAD ALSO,CREW REQUIRED. REPAIRED AND RESTORED POWER TO REMAINING CUSTOMERS AT 1342 JKC VER/KEP L3/KEP IDC XXXX
1340 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-09-06 22:08 | 2014-09-07 02:15 | 140 | 247 | 4475851 | 34580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OFF ON POLE 356-91, (B PHASE PER SCADA & B.O.) I WILL HAVE TO OPEN ALL THREE RECLOSERS ON POLE 356-36 TO MAKE REPAIRS WHEN I GET SOME HELP// 140 CC AFFECTED// WHEN OCR OPENED WILL HAVE ADDITIONAL 250CC// SEE 4476161 FOR RECL OUTAGE TO MAKE REPAIRS // VER/HFP L3/HFP AJB
1341 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-05 01:43 | 2008-07-05 07:35 | 98 | 352 | 62504-1 | 34496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE #204-175...TOP OF POLE BURNED OFF #204-126..CLAMP OFF ON POLE #204-125 & GROUNDED RELEASED BY CREW 077H15 POLE HAD ENOUGH CLEARENCE TO LOWER , RESTORED POWER IDC XXXX
1342 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-02-12 00:48 | 2009-02-13 17:50 | 14 | 2462 | 60040-1 | 34468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08/ SEE IF CUSTOMER IS STILL OUT HOT TAP LEAD BROKEN OFF FIXED LEAD CUST ARE RESTORED 2-13-09 RELEASED BY CREW 078S09 IDC LOOKS LIKE MAY HAVE WENT OUT ON 12TH XXXX
1343 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2016-05-27 14:08 | 2016-05-27 19:30 | 107 | 322 | 4265141 | 34454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON 991-266/// CUTOUT BROKE ON38820991D10303//REC. OPEN ON 991-266/// CUTOUT BROKE ON 991-303// REPAIRS MADE // POWER RESTORED @ 19:30 VER/CRB AJB
1344 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-03-24 05:25 | 2011-03-24 06:25 | 574 | 60 | 58445-1 | 34440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | WR#39290087//CREW OPENED RECLOSER TO SAFELY RELPACE B PHASE SWITCH AT POLE#68-35 OPEN REC, POLE 44-116 5;25 06;25 VER/KEP IDC XXXX
1345 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-12-26 06:31 | 2012-12-26 08:52 | 244 | 141 | 4517461 | 34404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REC. ON POLE 37830177D00064 OPEN, PATROLLING LINE. == CUT BAD ARRESTOR IN CLEAR ON POLE 37830178A00360, POWER RESTORED AT 08:52 //VER/GAH IDC XXXX
1346 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2010-08-13 17:34 | 2010-08-14 13:20 | 29 | 1186 | 54422-1 | 34394 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLED THE LINE AND DIDN`T FIND ANYTHING, GOING TO FLY IT IN THE MORNING WHEN THEY CAN SEE BETTER./// BEAVER CR-MCKINNEY #1 46KV CKT LOCKED OUT VER/ARN
1347 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-02-21 12:19 | 2017-02-21 13:04 | 764 | 45 | 4411811 | 34380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | PRIMARY HANGING OFF CROSSARM/// CREW ON SITE WILL NEED TO OPEN LINE TEMP TO MAKE REPAIRES, OPENED AT 38830478D10090 AT 1219 FETR 1330, GROUNDED & TAGGED TO DWEST AT 478-90/ RESTORED 1304/ ISO 38830478D10090/ COD 901/ VER/BOW // 2 RECORDS FOR THIS OUTAGE 764 KY CUST & 137 WV CUST = L3/HFP HFPC TOF1101 AJB
1348 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-08-18 14:48 | 2011-08-18 19:06 | 133 | 258 | 4725081 | 34314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RCLOSERS ON POLE 345//PHASE OPEN SOMEWHERE//CREW ONSITE//PATROLING//LOOP OPEN ON POLE 868-1127////VER/CRB IDC DIFFICULT TO FIND AND NOT BY TRUCK XXXX
1349 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-04-02 20:49 | 2010-04-02 21:19 | 1139 | 30 | 57728-1 | 34170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPEN GIBSON 34KV CB A AT MCKINNEY STATION DUE TO TRANSFORMER FIRE ON P.O. TROUBLE ORDER #57693-1. TERRY FIELDS REPORTED AFTER FIRE IS PUT OUT AND HE ISOLATES TRANSFORMER AT POLE 67-A-83 WILL BE ABLE TO RESTORE STATION CB. CLOSED STATION CB 2119 //VER/GAH AJBC CCSCO IDCC XXXX
1350 | Pikeville | 3413402 | GARRETT | LACKEY | 2009-06-11 07:11 | 2009-06-11 08:07 | 610 | 56 | 56763-1 | 34160 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | @ 0712 SCADA INDICATED THE BEAVER CREEK - MCKINNEY 46KV CIRCUIT LOCKED OUT INTERRUPTING GARRETT STATION MLR OK PER LOG VER/ARN IDC XXXX
1351 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-01-09 11:32 | 2013-01-09 13:25 | 302 | 113 | 4580881 | 34126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | ARRESTOR BLOWN ON POLE 165-65. GUY ROD LAYING ON RISER GOING DOWN TO CUTOT REMOVED GUY WIRE AND LET ROD FALL ON TOWARD POLE EVERYTHING CLEAR. SEND COPY TO ENG GUY WIRE WAS REAL SLACK AND COVERED UP WITH BRUSH POLES OK MAY WANT TO BUT GUY WIRE AND ANCHOR BACK AT SOMETIME // COD-302 ISO OCR 37830167A00428 VER/HFP L3/HFP IDC XXXX
1352 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-01-18 05:51 | 2011-01-18 07:20 | 383 | 89 | 62064-1 | 34087 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER ON POLE 247-1354 OPEN PATROLLING LINE----POWER RESTORED AT 0720-- NO PROBLEM FOUND. // COD-383 ISO RECL 37830247C31354 VER/HFP L3/HFP IDC FOUND BADE INSULTATORS LATER, CHANGED FROM WEATHER UNKNOWN XXXX
1353 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-01-16 21:07 | 2009-01-17 01:00 | 150 | 233 | 56429-1 | 34056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401101// HAVE A PHASE WIRE DOWN @ POLE 806-202// 150 COD - // CREW ENROUTE. SHOULD START RESTORING IN SECTIONS BY 01:00. OP PH B&C ON 202 AT 23:57. REPAIRS COMPLETE. CL SW ON POLE 202 AT 00:26 PICKING UP ALL CUST ON PH B&C AND CUST ON PH A UP TO OPEN RECS ON POLES 806-6 AND 806-186(COLD LOAD PICKUP) CLOSED REC ON 186 AT 00:38. CLOSED REC ON 806-6 AT 1:00 RESTORING REMAINING CUSTOMERS. SH// 150 CUSTOMER ON SWITCH - 3 MISMAPPED// VER/TOM L3/TOM AJBC PHASE A. LCD: 38830806000198
1354 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-12-29 04:11 | 2012-12-29 16:07 | 113 | 716 | 4547811 | 34048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | B PHASE RECLOSER IS OUT ON POLE 38830044A00606--CREW REQUIRED PRIMARMY DOWN AT POLE 38830019B00021 AT INTERSECTION OF 1468 AN BIG BLUE LANE--TRUCK TO POLE--LIFT HOT TAP OA HUNG TAG AT POLE 38830019B00155--HOT TAP JUMPER BROKE OFF////CLOSED B PHASE RECLOSER IN ON POLE38830044A00606- AT 09:01 - RESTORED 110 CUSTOMERS// C PHASE OUT DUE TO UPSTEAM DEVICE//REPAIRS MADE AND POWER RESTORED TO REMAINING CUST 1607/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/TOM L3/TOM IDC XXXX
1355 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-02-03 19:11 | 2009-02-04 14:45 | 29 | 1174 | 55268-1 | 34046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3000801// DUE TO ROAD CLOSINGS AND HAZARDOUS ROAD CONDITIONS TROUBLE CALLS ARE BEING HELD UNTIL TOMORROW//CALLED FOR 2 CREWS AND 2 BOXES OF INSULATORS AND 6 WHEELER/CHGED INSULATOR CUT TREE LIMB//VER/CRB IDC THIS APPEARS TO BE CORRECT, I SAW AT LEAST ONE TICKET SAY THIRD TIME OUT IN 4 DAYS XXXX
1356 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-04-29 15:28 | 2017-04-29 16:27 | 577 | 59 | 4695191 | 34043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DKM/OPENED UPPER ROCKHOUSE 34KV CB K AT 1528 THEN ROGER AMBURGEY OPENED 34KV LINE SWS AT POLE 37830352A00297 AT 1528 THEN CLOSED BREAKER AT 1533 SO HE COULD REPLACE CROSSARM AT POLE 37830352A00085---SEE DOL 737958///ORIGINAL OUTAGE RECORD//// VER/DKM /// TIMES PER SCADA - L3/HFP XXXHFP AJB
1357 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-07-12 09:13 | 2011-07-12 14:50 | 101 | 337 | 4527711 | 34037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RECLOSER IN AT 356-36 RECLOSER WAS NEVER OPEN, LOOPS BURNED IN TWO AT 356C-87, ONLY ONE PHASE IS OUT OF POWER (WILL NEED TO ADJUST CUSTOMER COUNT), LOOPS ALSO BURNED ON POLE 356-89.//VER/CRB
1358 | South Williamson | 3411401 | DEWEY | INEZ | 2009-03-03 10:22 | 2009-03-03 13:26 | 289 | 184 | H54432-1A | 34034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3411401// WHILE RETURNING CIRCUIT TO NORMAL FROM A DA OPERATION/ A SWITCH THAT WAS BURNT OPEN CAUSED A SINGLE PHASE CONDITION WHICH LOCKED CIRCUT OUT FROM POLES 767C-111,768A-225 TO 746B-218. TOTAL CUST COUNT OF 2746 CUST/THIS LEFT 289 CUST IN SERVICE FROM THE BRK TO THE OPEN REC AT 111 AND 225. THE 289 CUST WILL BE REPORTED ON ANOTHER OUTAGE SEE H54432-1A OPENED BRK AT 1022 INTERRUPTED 289 CUST/ 289 CUST IS PHASES A & C FROM BRK TO REC ON 111 AND 225 VER/DKG IDC CHANGED FROM DSTATION 5/19/09 XXXX
1359 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-08-18 00:17 | 2021-08-18 14:48 | 39 | 871 | 4095451 | 33969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Load side fuse out on step down pole 191-409 will patrol///Tried fuse it came back out will need ROW crew///Crews are enroute//Bad arrester on pole 191-197 changed bad arrester///Refused load side fuse @ 14:48 and restored service
1360 | Hazard | 3309302 | VICCO | JEFF | 2019-01-23 20:49 | 2019-01-24 12:32 | 44 | 943 | 4713261 | 33959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | //insulator on 323-67 is bad ALL LINE FUSES SHOWS TO BE IN BUT 1 OF THE GATES LOOKS LIKE IT TRACKING. AS PER DUTY TO REPAIR IN THE MORNING TO CHANGE CUTOUT 0N 323-589 Released by crew 077S01.open remaining two phases @ 10:46 hrs.p.hicks ON @ 1232
1361 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-11 17:15 | 2009-06-12 12:46 | 29 | 1171 | 55745-1 | 33959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN SOLID BLADES ON THIS POLE TO MAKE REPAIRS TO BAD HOT TAP LEADS ON POLE 1124-65 WHICH IS OPEN POINT FOR 63030-1// N MLR OK
1362 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-03-18 03:45 | 2017-03-18 12:04 | 68 | 499 | 4566491 | 33932 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED WITH A TECH ALSO POLE BURNT OFF /TAGGED POLE 246-54 TO B TACKETT NO GROUNDS AT THAT LOCATION,REPAIRS MADE ALL CUST RESTORED @ 1204 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830246000054/ COD 68/ VER/BOW AJB
1363 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-07-12 23:30 | 2010-07-13 02:58 | 163 | 208 | 65773-1 | 33904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNT OFF THREE PHASE POLE JUST BELOW XARM BRACES, MIGHT BE ABLE TO LOWER TEMP . TRUCKS TO POLE OPENED AND REMOVED SOURCE SIDE LEEDS ON REC. POLE 310-2031 AT 00:20, PLACED TAGS AND FLAGED POLE. FAULT POLE 310-57.BAD CUTOUT BURNT OFF THREE PHASE POLE JUST BELOW XARM BRACES, MIGHT BE ABLE TO LOWER TEMP . TRUCKS TO POLE OPENED AND REMOVED SOURCE SIDE LEEDS ON REC. POLE 310-2031 AT 00:20, PLACED TAGS AND FLAGED POLE. /WR#35958562/ VER/LDA IDC XXXX
1364 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-04-20 10:04 | 2015-04-20 15:00 | 220 | 296 | 4339721 | 33876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B & A (220 CUSTOMERS) / XFMR CUTOUT FAILED AND BURNT CROSSARM OFF 834-970/ OPENED SW ON 834-175 TO ISOLATE FAULT AND CLOSED REC 834-970 @ 12:34. CREW ENROUTE TO MAKE REPAIRS. RELEASED BY CREW 076S02// WORK COMPLTED, RESTORED AT 15:00 / ISO 38830810A30782/ COD 220 /SCADA INDICATES A & B PHASE OUTAGE/ VER/HFP L3/HFP AJB
1365 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-01-08 22:00 | 2015-01-08 22:28 | 1209 | 28 | 4921941 | 33852 | TRANSMISSION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | SDB / EMERGENCY STATION OUTAGE TO SAFELY ISOLATE FAILED 69KV BUS POT TR. 1210 CC OFF @ 2200 ON @ 2228 // TIMES PER TDC LOG - CUST NOTIFIED PER COINS VER/HFP L3/HFP AJB
1366 | Pikeville | 3421001 | BREAKS | CITY | 2020-04-24 00:59 | 2020-04-24 12:44 | 48 | 705 | 4743651 | 33840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.////line fuse blown on pole 220-97////patrolling..cutout broke on pole 220-97////will need line crew and flaggers to make repairs..repairs made..restored
1367 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2012-05-29 16:20 | 2012-05-29 17:05 | 752 | 45 | 4843011 | 33840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON 1013B14.CROSSARM BURNT OFF..1 PHASE LAYING ON INSULATED GUY BREAKER..NO POWER OFF YET..WILL OPEN LINE ON 1012D198..CREW ENROUTE..//..OPENED SWITCHES ON 1012D198 @ 16:20..CREW MADE REPAIRS..CLOSED SWITCHES ON 1012D98 @ ...JRV..05/29/12//COD 752// VER/DBM IDC XXXX
1368 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-12-16 08:42 | 2008-12-16 15:20 | 85 | 398 | 58876-1 | 33830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 27698910 /// PLEASE DON`T FORGET THE FETR...THANKSSTS WR # 27698910 /// PLEASE DONT FORGET THE FETR...THANKS POLE FIRE , CREW IS ON WAY TO CHG POLES TS WR # 27698910 /// PLEASESEND THIS TO WILLIE ROBINSON CREW REQUESTED FETR UPDATED TO 1530 VER/HFP L3/KEP IDC XXXX
1369 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-10-19 15:57 | 2011-10-19 18:30 | 221 | 153 | 4999801 | 33813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | . . CLOSED AT POLE 505 AT 18:30 , ALL CUSTOMERS RESTORED, ALL WORK COMPLETE / GXJ ///VER/CRB IDC XXXX
1370 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-07-28 17:15 | 2017-07-28 20:41 | 164 | 206 | 4196291 | 33784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CONDUCTOR OFF INSULATOR//SERVICER ATTEMPTED TO OPEN SWS 38830068B00123 BUT PH C FELL APART //COD 164// SEE ALSO 4197081 (OPENED NEXT SET OF SWS BACK TO ISOLATE)//GOT ALL 3 PHASES 68-123 OPENA AND TAGGED TO KYDDC @ 1715//XFERED 221 CUST FROM 4197081//TOTAL COD 385//POLE 68-433 PIN EN. BAD POLE 68-123 BAD 600A SOLID BLADE/ON SITE RM VER/ARN SJG
1371 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-02-16 21:45 | 2018-02-17 02:20 | 133 | 275 | 4853371 | 33748 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 1108-222,LEAD BURNED OFF A SOLID BLADE HERE,NEED 1 A-LINEMAN,BUCKET////////OPENED RECLR@02:02 TO MAKE REPAIR,CLOSED RECLR@02:12 Released by crew 074S06
1372 | Paintsville | 3401802 | INDEX | HOSPITAL | 2008-06-02 22:05 | 2008-06-03 01:50 | 195 | 225 | 54743-1 | 33715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | 3401802//SERVICER IS PATROLLING LINE//B PHASE OUT...UNKNOWN REASON AT THIS TIME..PAINSTVILLE CREWS ON THE WAY TO HELP WALK LINE THROUGH THE MTNS..BB LOOP OPEN ON MT B PHASE ONLY *** FEEDER NOT OUT. SERVICER CHANGE TAPS ON FOLLOWING POLES TO RESTORE CUST. 654-114 5 CC 5 AT 2334 - 654-118 CC 79 AT 2350 AT 0142 OPENED CB _BYPASSED B PHASE REG CLOSED CB AT 0150 ALL CUST RESTORED. DKG/OPEN REG HAD B PHASE OUT THIS IS FOR ORIGINAL OUTAGE VER/PDP
1373 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2020-11-30 05:15 | 2020-11-30 07:22 | 281 | 127 | 4729691 | 33703 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | B ph only is open // cod 248,,,,B PHASE only open on 206-84 servicer patrolling // fault caused A Phase Line fuse on 38830206A10043 to open closed @ 07:22,, B PHASE RECLOSER in @ 07:13 all customers restored complete Released by crew 078S05
1374 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2011-05-26 10:43 | 2011-05-26 13:09 | 230 | 146 | 4172521 | 33580 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | BEEFHIDE STATION TRIPPED OUT // PH 3 12KV SA FAILED // CUT SAME IN CLEAR //VER/GAH
1375 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-11-29 08:35 | 2015-11-29 13:55 | 140 | 320 | 4491201 | 33580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 PH. POLE 140-C-5010 TOP BURNT OFF//CLOSED STEP-DOWN @ 1015 UPTO OPEN PT 38830140C0012//RESTORED 51 CUSTS//3 PH. POLE 140-C-5010 TOP BURNT OFF.. LOOPS CUT @ 140-125, 3 STEPDOWNS RESTORED @ 10:15 RELEASED BY CREW 078S07.. CREW ON SITE TO MAKE REPAIRS LOOPS CUT AND GROUNDS TAGGED TO YOUNGMAN AT POLE 140-125 ETR 14:30.. OPENED STEP DOWN ON 116-6001 AT 13:35 TO MAKE UP LOOPS.. CLOSED BACK IN AT 13:55 AND TICKET COMPLETE CAY RELEASED BY CREW 078H22 VER/CRB
1376 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-11-24 04:16 | 2008-11-24 09:44 | 111 | 328 | 51451-1 | 33558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// PHASE C RECLOSER OPEN 182C-257// COD-114//, CROSSARM BURNT OFF ON POLE 158-6// //VER/CRB MLRC CNT 200 IDCC XXXX
1377 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-06-05 06:24 | 2010-06-05 11:30 | 316 | 306 | 57107-1 | 33470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830833D00583 IS BURNED OFF HAVE THIS ISOLATED @ 833-581 CLOSED RECLOSURE ON POLE 400 CPHASE @08:08ALL ON BUT 3 COUST @ 08:08,LAST 3 ON @ 11:30 VER/ARN IDCC CNT319 XXXX
1378 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-07-24 04:45 | 2022-07-24 13:16 | 92 | 511 | 4565481 | 33451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | checking now Released by crew 076H06 // Crews found bad cable between 38830784C21592 & 38830784C20343 isolated & tagged to DDC, All customers restored
1379 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-01-04 01:56 | 2008-01-04 05:58 | 138 | 242 | 53455-1 | 33396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3300602///FUSE IS OPEN PATROLLING LINE// WIRE DOWN SLEEVE PULLED LOOSE CALLING FOR CREW VER/ARN IDC XXXX
1380 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2019-09-27 16:43 | 2019-09-27 19:36 | 296 | 173 | 4065501 | 33374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 957878/crossarm broke letting C phase fall on tap conductors on 966D339 replaced arm on 966D339 and switch on 966B596,restored power at 19:36 Released 38820966D00339
1381 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-02-11 04:55 | 2020-02-11 10:49 | 94 | 354 | 4390961 | 33276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308402/gaj/0457/all out disp K Napier Trk 3142 one recloser open on 278-335, patrolling, found bad insulators on pole 37830279000010, will need crew to make repairs Released by crew 077S023308402/gaj/0457/all out disp K Napier Trk 3142 one recloser open on 278-335, patrolling, found bad insulators on pole 37830279000010, will need crew to make repairs .
1382 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-11-01 13:59 | 2013-11-01 16:03 | 268 | 124 | 4985591 | 33232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE #1108-442 ROTTED OFF AND BROKE CROSSARMS ON TAKEOFF POLE, GOT CREW COMMING TO CHANGE OUT. NO OUTAGE UNTIL WE GET STARTED ON CHANGING POLE OUT // CREW OPENED RECLOSER @ 1359 TO MAKE REPAIRS ON @ _____POLE #1108-442 ROTTED OFF AND BROKE CROSSARMS ON TAKEOFF POLE, GOT CREW COMMING TO CHANGE OUT. NO OUTAGE UNTIL WE GET STARTED ON CHANGING POLE OUT OPEN RECLOSER 1359 AND CLOSED AT1603 RELEASED BY CREW 077S05 ON @ 1603 ///COD-258 ISO OCR @ 38831108A00431 VER/HFP L3/HFP IDC XXXX
1383 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-10-03 09:52 | 2009-10-03 12:31 | 209 | 159 | 66273-1 | 33231 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | CUSTOMER IS OUT DUE TO THE STATION OUTAGE CUSTOMER POLE WAS LEANING OUR EQUIPTMENT IS GOOD SHAPE NO POLE LEANING AT THE ADDRESS. TIM MCCOY RELEASED BY CREW 074H10//LOW SIDE SURGE ARRESTOR TO 69-12KV TR IN STATION FAILED CAUSING HIGH SIDE FUSE TO 69-12KV TR TO BLOW. //VER/GAH IDC XXXX
1384 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-06-13 12:50 | 2013-06-14 14:00 | 22 | 1510 | 4274891 | 33220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ROTTED OFF POLE 56-35-ALL MANUEL---STR LINE 12KV -1ARM ,BRACES,3 PIN ,3 INS 1 CLEVIS ,-6A AND 4 COPPER-OPEN AT POLE56-102---OPENED 55-223 AT 1515-CLOSE UP TO 102 AT 1535--WILL NEED RW CREW ALSO---JIM RELEASED BY CREW 077S06 CANNOT COMPLETE TONIGHT DUE TO DIFFICULT LOCATION, CREWS WLLL RETURN FIRST THING FRIDAY MORNING TO REPLACE POLE - GLEN COMBS //COD 22// VER/DBM IDC XXXX
1385 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-03-28 17:59 | 2008-03-28 22:54 | 317 | 295 | 61681-1 | 33131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200204// HAD TO OPEN RECLOSER ON POLE 1065B-275 TO DE-ENERGIZE 3 PHASE POLE THAT IS NEARLY BURNT IN HALF// CALLED CREW, FAULT POLE#1065-B-238 IN PROCESS OF SWITCHING TO ALT SOURCE AT 1926 OPENED SB SW AT POLE 1065-237 AND CLOSED N.O. SB SWS AT POLE 1064-C-200 AT 1930 CC 21 STILL OUT.IN PROCESS OF SWITCHING TO ALT SOURCE AT 1926 OPENED SB SW AT POLE 106 VER/PDP IDCC PN80, TOF1713 XXXX 4/30 CHANGED CIRCUIT FROM 3200203 XXXX
1386 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-11-04 14:41 | 2020-11-04 15:22 | 808 | 41 | 4642971 | 33128 | TRANSMISSION LINE | EQUIPMENT FAILURE | STATIC WIRE | Static wire down on transmission line short outage to make repairs/ Open 1441/ Close 1522/ 808cc/
1387 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-02-23 10:08 | 2008-02-23 10:38 | 1104 | 30 | 66483-1 | 33120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501//OPENED REC#4-269//COD 1083//TO SAFELY CHANGE OUT CUTOUT//VER/CRB IDC 27 CUSTOMERS AND 1 CUSTOMERS SUBTRACTED DUE TO OTHER OUTAGES XXXXX
1388 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-04-25 13:44 | 2011-04-25 17:40 | 140 | 236 | 64223-1 | 33040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OPED UP ONE PHYSE AT 15:20-- WIRE DOWE (B PHASE PER TROUBLE CALLS) VER/HFP L3/HFP IDCC TOF1520, MAY HAVE OPENED ANOTHER PHASE AT 1540 XXXX
1389 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2018-06-19 19:41 | 2018-06-20 00:45 | 335 | 304 | 4624871 | 32960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Released by crew 074S07 sectionalizer due to bad transformer pole 211-217. i have transformers iso closed sec on pole 187-363 at21:15 Released by crew 074S11//REPLACED TRANS 37830211C00217 @ 0045//ALL CUSTS RESTORED
1390 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-08-11 17:36 | 2010-08-11 22:25 | 114 | 289 | 52801-1 | 32946 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WR# 36402711///CONFIRMED C PHASE ONLY IS OUT PATROLLING LINE//8 ARM ROTTED OFF AT 37830225B00040 OPENING ALL 3 PHASES TO MAKE REPAIRS RELEASED BY CREW 077S04 RESAGGED CONDUCTORS REPLACED CROSSARM POWERRESTORED AT 2225 CREW 077H01//VER/CRB IDC XXXX
1391 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2020-11-15 11:41 | 2020-11-15 16:11 | 122 | 270 | 4680111 | 32940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | recloser is open on 1087-D3-504// patroling/// broke 300 amp switch on pole 1087-D-91// will be making repairs
1392 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-01-14 08:16 | 2020-01-14 10:41 | 763 | 145 | 4302591 | 32911 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401703/gaj/0816/CB open at Station affecting 764 customers, Line servicer patrolling Ckt for cause -- gaj/0855/servicer reports failed cutout at 37820217D00057, needs crew to replace /// gaj/0859/CB closed restoring 762 customers//Replaced bad cutout and restored service @ 10:41 Released by crew 074S02 L3/HFP
1393 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-06-15 13:47 | 2016-06-15 14:20 | 997 | 33 | 4349661 | 32901 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | RELATED TO 4348081 (ORIGINAL ORDER) CREW OPENING RECLOSER TO ALLOW THEM TO SAFELY REPLACE BROKEN POLE 38830269B00079 OFF @ 1347 ON @ 1420 VER/HFP L3/HFP AJB
1394 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2021-07-17 11:38 | 2021-07-17 13:18 | 329 | 100 | 4923961 | 32900 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1132518 / Transmission line outage/ she on deadend bell failed on 46kv line/restored 1318/ Transmission found dead end bell failed
1395 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-04-27 10:08 | 2011-04-27 13:40 | 155 | 212 | 65980-1 | 32860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | //IT FORCE CLOSED IDC USED TICKETS AND MAPS TO ESTIMATE OUTAGE INFO XXXX
1396 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-12-20 20:33 | 2012-12-21 02:34 | 91 | 361 | 4492471 | 32851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RESAGGING PRIMARY COND. PRIMARY WAS GOING PHASE TO PHASE, CONDUCTORS RESAGGED AND APR AT 0234 CLOSE TICKET. DWEST VER/PDP IDC XXXX
1397 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2021-02-07 04:06 | 2021-02-07 14:13 | 54 | 607 | 4942491 | 32778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | line fuse out on pole 447-83. primary conductor burnt down on pole37830447000017 feeding to pole 449-16.. one span down.. #4 copper conductor Released by crew 077S11 Released by crew 075H03
1398 | South Williamson | 3200302 | BELFRY | TOLER | 2011-06-07 07:01 | 2011-06-07 10:08 | 175 | 187 | 4243921 | 32725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PHASE "A" LOOP BURNT OPEN ON 991-B-10//COD 175//LOOP OPEN ON POLE 991-10,WILL HAVE TO OPEN AT 990-458 WHEN READY TO REPAIR(SEE 4244651)//ISO// VER/DBM IDC XXXX
1399 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-01-13 02:30 | 2018-01-13 08:45 | 87 | 375 | 4741541 | 32625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | C phase rec. open on pole 37820073B00644////will patrol...//COD 87 AT THIS TIME//CREW HAS ARRIVED//WALKING LINE OUT//C phase rec. open on pole 73-644////will patrol...found bad arrester on csp xfm. on pole 37820121000203 .lifted hot tap and cleared up .will make repairs on ops order Monday 1-15-18 .no one living in home.//OPS # .034310812
1400 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-03-26 08:17 | 2014-03-26 11:33 | 249 | 196 | H4525951 | 32580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER MYLES B PHASE OUT ONLY COD 97// POLE 26-88 HAS BURNED IN TWO DUE TO BAD CUTOUT// OPENED RECS ON 49-D2- 331 @ 8:17// OPENED SWITCHES @ 49-70// TAGGED TO MYLES// COLSED REC.S ON 49-D2-331 @ 8:44// CREW ENROUTE//CLOSED @ 49-70 @ 11:33 / **** MAKE DUPLICATE TICKET IN HOIS FOR ADDITIONAL B & C PHASE CUSTOMERS FROM 0817 TILL 0844****** VER/SEF IDCC CNT REVERSED XXXX
1401 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-11-30 21:45 | 2022-12-01 04:57 | 193 | 432 | 4215451 | 32512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | @ 38830523000036 lifted hot line clamp and tagged to k. griffith. burnned off pole top at pole 38830523000099 by truck need small pole top extintion. C phase recloser 183 in @ 0025 Released by crew 078S12 Repairs made, energized on pole 523-36 at 04:57. Ticket complete.
1402 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-01-05 05:38 | 2016-01-05 08:30 | 189 | 172 | 4585671 | 32508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE DOWN BETWEEN POLE#448-122 AND 448-299 COD-189 /OPENED ALL 3 RECLOSERS 448-365 AT 0606 TO ISOLATE FAULT AND MAKE SAFE OUTAGED ADDITIONAL 384 CUSTOMERS/CREW ENROUTE/ POWER RESTORED AT 08:30 RELEASED BY CREW 075H03 VER/CRB AJB
1403 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-01-13 23:18 | 2012-01-14 03:03 | 144 | 225 | 4260051 | 32400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED 4 MAN CREW PLUS FLAGGERS--OPENEN AN -TAGED C PHASE RECLOSER PRIMARY DOWN BETWEEN POLES 38830068A00096 AND 38830068A00095 RELEASED BY CREW 078S07 144 CUSTOMERS AT THIS TIME/ HAD C PHASE DOWN BACK ON AT 3:03 VER/ARN IDC XXXX
1404 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-10-27 20:13 | 2011-10-27 22:05 | 289 | 112 | 4028421 | 32368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | //PATROLLING LINE, FOUND NOTHING, CLOSED RECLOSER AND IT STAYED//COD 554 IDC FOUND BAD CONTROL ON DOWNSTREAM RECLOSER XXXX
1405 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-04-14 15:27 | 2019-04-15 16:49 | 105 | 1522 | 4109171 | 32319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | /OTAGE STARTED @1527 ON 04-14-2019//39 CUSTS FROM THE BEGINNING//OPENED GOAB ON POLE 37840552B40508 @ 1448//LOOP BURNT ON POLE 37840576000130///found open loop on A phase on buckarm pole# 576-130, open goab on 552-b4-508 @15:07 to make repaires, closed goab @ 16:49, all power restored. p.hicks//// only A phase from start of outage ACB
1406 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2019-11-12 00:53 | 2019-11-12 03:36 | 198 | 163 | 4022001 | 32274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 37820032C00003/ ISO 37820008D00093/ COD 198 .replaced cutout,restored power at 03:36. L3/HFP
1407 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-03-14 19:01 | 2016-03-15 03:49 | 61 | 528 | 4846851 | 32208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | RECLOSER IS OPEN ON 644-14, POLE 644-79 BROKEN TRUCK OK, CREW WILL NEED TO ISOLATED AND GROUND SAFE AT THIS TIME////CREW REQUIRED RELEASED BY CREW 078S11---CREW ON SITE--ISOL OCR AT 644-14-GND, TAG TO CREW--ALSO PRIM DOWN BETWEEN PL 644-16 AND 17---ALL REPAIRS MADE---TBL TKT COMP---RMV//COD 61 VER/AWD IDCC L3/IDC AJBC CCWU FEC57
1408 | Whitesburg | 3309302 | VICCO | JEFF | 2009-03-09 04:49 | 2009-03-09 10:00 | 124 | 311 | 56422-1 | 32144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3309302 // PATROLLING LINE, SHOT LINE AND IT CAME BACK OUT.// OPENED RECLOSERS @ 397-177 AND 373-189 // TRIED 373-194 AND CLOSED IN AND HELD @ 0840// 3309302 // PATROLLING LINE,// TRIED 373-194 AND CLOSED IN AND HELD @ 0840// 3309302 // PATROLLING LINE, SHOT LINE AND IT CAME BACK OUT. WIRE DOWN ON POLE 396-16. SLEEVE PULLED OUT. POWER RESTORED// VER/TOM L3/TOM IDC XXXX
1409 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-04-04 13:41 | 2009-04-04 14:34 | 606 | 53 | 65124-1 | 32118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3301701//CREWS OPENED RECLOSER IN ORDER TO SAFELY REPLACE BURNT CROSSARM//COD 606//SEE ORDER 64993-1// VER/DBM AJB
1410 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2009-10-19 13:28 | 2009-10-19 14:04 | 892 | 36 | 58038-1 | 32112 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | STATION CREW ON SITE// TARGET LOSS OF COOLING// OPEN @ 1328 - CLOSED @ 1404 // VER/TOM L3/TOM IDC XXXX
1411 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-01-03 02:33 | 2008-01-03 09:59 | 72 | 446 | 53053-1 | 32112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3000201/// SPLICED FAILED ON PRIMARY. NEEDS CREW, 6A COPPERWELD , RELEASED BY CREW 078S04/CREW ON SITE/FETR1030/REPAIRS MADE/POWER RESTORED AT 0959/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
1412 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2011-03-31 03:51 | 2011-03-31 07:42 | 139 | 231 | 60698-1 | 32109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 351-63 BURNT TOP OF POLE OFF WILL NEED BIG BUCKET & 2 MEN, MADE REPAIRS RESTORED POWER AT 07:42 COD-139 ISO OCR 37830351C00269 VER/HFP L3/HFP IDC XXXX
1413 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-09-04 08:27 | 2020-09-04 10:33 | 409 | 126 | 4429791 | 32032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE OFF FROM BEGINNING OF OUTAGE COD 210//B Ph. Load side Stirrup/Hot Line Clamp burnt off at OCR 141D252--will be opening OCR to de energize A&C Ph. to make repairs--Open @B Ph. Load side Stirrup/Hot Line Clamp burnt off at OCR 141D252--will be opening OCR to de energize A&C Ph. to make repairs--Open @ 10:05 On @ 10:33---Tbl tkt compB Ph. Load side Stirrup/Hot Line Clamp burnt off at OCR 141D252--will be opening OCR to de energize A&C Ph. to make repairs--Open @ 10:05 On @ 10:33---Tbl tk
1414 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2018-06-14 08:01 | 2018-06-14 10:15 | 239 | 134 | 4600271 | 32026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SAME AS 4599401//// recloser was opened at 08:01, there were 9 customers were already out on outage 4599401
1415 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-01-22 08:15 | 2013-01-22 11:00 | 194 | 165 | H4726681 | 32010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FROM ORDER 4726681 BAD PLACE IN CONDUCTOR AT 171-131 CAUSED WIRE TO BURN DOWN.. 96 (100 ON A PHASE FROM FAULT POLE ) CUSTOMERS ORIGINALLY OUT ON RECLOSER ON POLE 37830147000054 A PHASE - OPENED RECLOSER ON POLE 37830171000233 @ 0815 INTERRUPTING ADDITIONAL 194 CUST . THIS IS THE RECLOSER OUTAGE ON B & C PHASES 194 CUST VER/HFP L3/HFP IDC XXXX
1416 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-04-25 12:00 | 2010-04-25 13:50 | 291 | 110 | 50748-1 | 32010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER AT POLE 1127-A2-821 @ 1200 TO EXTINGUISH POLE FIRE AT POLE 1103-242 IN ORDER 50729-1 VER/HFP L3/HFP IDC XXXX
1417 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-09-12 13:25 | 2017-09-12 20:15 | 78 | 410 | 4353681 | 31980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE REPORTED PER CSC AT 37830220000035. 13438 KY HIGHWAY 451, HAZARD, KY 41701-8147//OPEN GOAB ON POLE37830220000143 AT 13:25,TOP OF POLE BURN OFF LAYING ON TRANSFORMER,NEED 4 MAN LIN CREW RELEASED BY CREW 077S04 POLE REPLACED AND POWER RESTORED AT 2015 VER/AWD L3/HFP XXXHFP SJG
1418 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-06-20 09:37 | 2009-06-20 12:58 | 159 | 201 | 63223-1 | 31959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER BAD ON APPALACHIAN SIDE VER/ARN AJB ADDED CLEARING DEVICE PER SDS.
1419 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-01-07 00:24 | 2014-01-07 08:00 | 70 | 456 | 4243591 | 31920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQ, #4 CU PRI DOWN, BESIDE ROAD, RECLOSER IS ISLOTATED AND GROUNDED AND TAG TO DDC, MAY NEED A LITTLE WIRE RELEASED BY CREW 078S06//COD 70// VER/DBM IDC CHANGED FROM WEATHER UNKNOWN XXXX
1420 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2022-04-30 00:43 | 2022-04-30 07:32 | 78 | 409 | 4816881 | 31902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | reclosers on pole 38830068C00214 are //2 poles down 38830068C00216 broke in half 45-4 3phasedouble 10ft arms 7200v// 10kv transformer with 1 service drop this will be line crew and and flagging crew required Released by crew 078S09 Closed rec on 68-c-214 at 07:32 Ticket complete.
1421 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-12-27 18:00 | 2015-12-28 01:49 | 68 | 469 | 4565131 | 31892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF @ POLE 523-18 REPAIRS MADE TO HOT TAP,TREE FELL @ POLE 523-122 TO 523-131 NEED LINE CREW & TREE CREW WILL NEED 25KVA 7200 XFMR & CUTOUT TAG TO RON VIRGIN @ 523C2-383///CREW ON SITE---OCR 523C2-383 ISOL,TAGD AND GNDD TO R VIRGIN---DIFF. LOC..---CHANGED XFMR TO 15KVA--CUTOUT---PTP AND INSOL--#2AA PRIMARY---OCR IN ON PL# 523C2-383 @ 01:49---TBL TKT COMP---RMV VER/TOM L3/TOM AJB
1422 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-12-02 15:42 | 2009-12-02 18:59 | 200 | 197 | 58165-1 | 31864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CENTER PHASE RECLOSER HAS STIRRUP BURNT OFF, PATROLING LINE NOW TO CHECK HAZARDS....P.HICKS. PLEASE UPDATE TO CORRECT CUSTOMER COUNT...........CLOSED RECLOSER ON B PHASE , POLE 419-72 @17:57HRS, PICKING UP CUSTOMERS TO OPEN RECLOSER ON POLE 468-179,..........CLOSED RECLOSER ON POLE 468-179 @18:22HRS, RESTORING POWER UP TO OPEN RECLOSER ON POLE 469-235..........CLOSED RECLOSER ON POLE 469:235 @ 18:59 HRS, RESTORING ALL POWER.....P.HICKS IDCC CNT514 XXXX
1423 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2010-03-26 05:20 | 2010-03-26 13:42 | 285 | 502 | 54553-1 | 31851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34409274 // COD-285 / FOUND POLE BURNTED OFF , NUMBER 926-117, 405 POLE, NEED CREW AND AWP, MATERIAL NEED NEW CUTOUT AND ARRESTOR, AND NEW POLE, EVERY THING ESLE WILL WORK BACK, IS RIGHT IN FRONT OF EMMANUEL FREEWILL BAPTIST CHURCH, ON SHUTLZ RD, HAVE HOT TAP LIFTED ON POLE 926-35, AND LINE IS GROUNDED AT THIS POINT.---------ALL POWER ON @ 13:42 VER/HFP L3/HFP IDC XXXX
1424 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2012-08-08 18:54 | 2012-08-09 01:00 | 87 | 366 | 4913441 | 31842 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FOUND PRI POLE, ROTTEN AT THE GROUND AND FALL OVER, I OPEN UP LINE FUSE AT 1854 ON POLE 901-5574, WELL NEED TECH ON THIS ON, WINDSTREAM POLE, ACCORDING TO THE MAP, CREW REQ, LOOKS TO BE A 355 POLE, GO BACK WITH A 405, SINGLE PHASE 7200 ON CROSSARM, WELL NEED 2/3 SERVICE DROP AND 4/3 SERVICE DROP TO SLICE WITH, EVEYTHING ELSE WITLL BE OK TO GO BACK RELEASED BY CREW 078S06//NO OUTAGE TIL FUSE WAS OPEN (WAITING ON WINDSTREAM TO SET POLE);ALL POWER RESTORED AT 01:00 //VER/GAH IDCC TOF1740 XXXX
1425 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-06-21 20:04 | 2016-06-21 22:40 | 204 | 156 | 4401871 | 31824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD BURNT OFF SOLID BLADE ON RECLOSER POLE 184-266, ALL POWER RESTORED VER/AWD AJB
1426 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-09-22 14:37 | 2021-09-22 23:55 | 57 | 558 | 4276201 | 31806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | windstream pole 901-7055 fell over. crew reqd. beside road. Released by crew 078S07 crew on site FETR 22:00 LRM fert 23:55 new fetr//opened fuse 39830901C45602 @ 2130 // all pwr restore 23:55 please close LRM //iso 39830901C45602 LR- The 1st All Out call came in at 14:37
1427 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-05-18 12:18 | 2018-05-18 17:18 | 106 | 300 | 4370691 | 31800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE UNTIL FUSE OPENED ON POLE 37830247D00764(106 CUST)//OPENED @ 1218//Opened line fuse at 12:18// got help coming pole brunt off at 37830247D00769 Released by crew 077S03//RESTORED 1718
1428 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-10-09 08:11 | 2010-10-09 13:42 | 96 | 331 | 58245-1 | 31776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TWO PHASES BURNT IN TWO ON 4/0 HENDRIX OVERHEAD. ALL THREE RECLOSERS ON 654-529 ARE IN AND ALL PHASES ARE ENERGIZED UP TO FAULT POLE 654-91. OPENED AND ISOLATED ALL THREE REC ON 654-529 @ 10:30. REDUCED OUTAGE NUMBER FR 623 TO 198 @ 11:10 (SWITCHING). REPAIRS UNDERWAY. REPAIRS COMPLETE. RESTORED @ 13:42. SH IDC USED RECLOSER POLE AS CLEARING DEVICE POLE NUMBER XXXX
1429 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-10-20 19:59 | 2016-10-21 06:10 | 75 | 611 | 4033911 | 31764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SECTIONALIZING AND PATROLLING FOUND AND REPLACED BAD XFMR CUTOUT ON 904-43. RELEASED BY CREW 076S02 VER/KEP L3/HFP XXXHFP AJB
1430 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-04-27 00:49 | 2010-04-27 05:30 | 113 | 281 | 51765-1 | 31753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR ON 851-134 CRACKED..4 SPANS TREES ABOVE PRIMARY..BRIAN RAMEY CALLED OUT TO CHG INSULATORS..TREES NEED CUT CHG OUT 1 INS. 851-136 2 ON 851-134...BB VER/LDA IDCC FP18 XXXX
1431 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-07-20 16:23 | 2015-07-20 20:35 | 126 | 252 | 4918611 | 31752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "C" PHASE ONLY COS-62/TRIED REC ON 37830482C00151, CAME BACK OUT, BAD ARRESTOR ON 482-310, POWER RESTORED AT 20:35 VER/KEP AJB
1432 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-03-26 01:49 | 2010-03-26 06:35 | 111 | 286 | 54533-1 | 31746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34409227 / COD-109 / /PATROLLING LINE, SOLID BLADE LINE CUTOUT BROKE DOWN ON 72-78/ @ ____ OPENED RECLOSER ON POLE 72-A-80 (COD-176) TO REPLACE BAD CUTOUT., OFF AT 6:08 ON AT 06:35 (*_&*)&()*^&(*^&)*(&_)+*+ IDC LOOKS LIKE ALL 3 PHASES WERE OUT? AJB LEAVE FOR DALE.
1433 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2013-01-28 18:40 | 2013-01-28 20:58 | 230 | 138 | 4749051 | 31740 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | PH 3 34KV BUS POT TR AT BEEFHIDE STATION FAILED - SAME CUT IN CLEAR AND SECONDARY FEED TO PH 3 JUMPERED TO PH 2. RELEASED BY CREW 077S12 //VER/GAH IDC XXXX
1434 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-04-03 03:28 | 2009-04-03 07:52 | 120 | 264 | 64363-1 | 31680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DUTY SUPERVISOR ASSISTING IN TRYING TO FIND PROBLEM. FOUND BAD XFMR CUTOUT. REPLACING. REPAIRS CP. CL PH B REC ON POLE 53 AT 07:46 RESTORING UP TO REC 832-33 (26 CUST) (WE OPENED WHILE TROUBLE-SHOOTING LINE, SEE H64363-1). CL POLE 33 REC AT 07:52 RESTORING REMAINING CUST. SH// VER/DBM AJB INT OUTAGE ON OCR 832/33 W/120 CUST, @5:07 OP B PH OCR 833D/53 W/26 CUST. @7:46 CL 833D/53 REST 26 CUST, @7:52 CL 832/33 REST 120 CUST. SEE H64363-1 FOR 833D/53 OUTAGE, SEE 64363 FOR 832/33 OUTAGE.
1435 | Hazard | 3311101 | STINNETT | REDBIRD | 2013-01-30 10:38 | 2013-01-30 17:15 | 270 | 397 | 4757271 | 31665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT @ 553-61 RESTORED POWER ON MAIN LINE @ 1230 ANOTHER CUTOUT IS BAD ON 553-39 WILL NEED TO REPLACE RELEASED BY CREW 077S01 COD-270 ISO OCR 37830529000143 VER/HFP L3/HFP IDC LOOKS LIKE STEP TIME WRONG AT 1230 XXXX
1436 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-08-31 14:04 | 2013-08-31 21:21 | 135 | 437 | 4805991 | 31619 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREE BURNED DOWN PRIMARY--875-210 211..CUTOUT ON 875 208..BURNED UP.REC BACK ON 17.25 //C PHASE ONLY 135.BACK ON AT 21.21 RELEASED BY CREW 076S01 //VER/GAH L3/HFP IDC XXXX
1437 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2013-05-06 03:48 | 2013-05-06 10:40 | 231 | 412 | 4075191 | 31560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED DUNHAM 34KV CB B LOCKED OUT// ARCOS SERVICER// 0427 - SERVICER ENROUTE// 0538 - BAD CUTOUT FOUND AT POLE 357-231, ISOLATED AND GOING TO STATION//SCADA INDICATED DUNHAM 34KV CB B LOCKED OUT// ARCOS SERVICER//. BAD CUTOUT ON POLE 357-231 ISOLATED CUTOUT,CLOSED BREAKER AT 06:04 COD-231 ISO FB VER/HFP L3/HFP IDCC TOF349 XXXX
1438 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-01-03 16:27 | 2012-01-03 17:20 | 595 | 53 | 4229891 | 31535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | CLOSED & BYPASSED RECLOSURE. PLACED HOLD TAG FOR DDC /// COD-595 ISO OCR 38831100D40325 VER/HFP L3/HFP IDC XXXX
1439 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-12-16 22:35 | 2008-12-17 01:20 | 191 | 165 | 59315-1 | 31515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3007904//SWITCH ON POLE 549-97 WAS ON FIRE PHASE CLOSER TO THE ROAD. I OPEN RECLOSER ON POLE 501-337,,,DHE CREW ON THE WAY , 34KV SW AT POLE 459-97 WAS NOT FULLY CLOSED, OPENED & RECLOSED SWITCH THEN AT 0120 CLOSED 34KV RECLOSER AT POLE 501-337 //VER/GAH "A" PHASE OPEN TILL RECLOSER OPENED L3/KEP IDC CHANGED TOF XXXX
1440 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-04-03 08:26 | 2015-04-03 14:25 | 515 | 359 | 4262821 | 31498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN ON POLE 38821137A00331. C PHASE & GROUND FAULT, PATROLLING THE LINE. ISOLATED BAD CUTOUT ON POLE 37820009C00024. CLOSED THE RECLOSER ON POLE 38821137A00331 AT 09:26. NEED ONE MAN TO HELP REPLACE THE CUTOUT. RELEASED BY CREW 079S02/ ISO 38821137A00331/ COD 515 VER/HFP L3/HFP AJB
1441 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2021-07-12 14:10 | 2021-07-12 15:36 | 366 | 86 | 4899871 | 31476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Failed insulator 38830045D47608 Opened SWS at 38830045D47516 Off at 1448 On at 1536
1442 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2009-02-18 05:24 | 2009-02-18 12:12 | 77 | 408 | 63604-1 | 31416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID BLADE DISCONNECT BADON POLE 37830235000053 (PHASE A ONLY)//COD 77//CREW IS ON WAY TO REPLACE ALL 3 RELEASED BY CREW 074S04-------REPLACED 3 300AMP SOLID BLADES OPENED LINE AT 11:27 (INTERRUPTING 76 MORE CUSTOMERS, SEE H63604-1)//CLOSED 12:12////ISO// VER/DBM IDC XXXX
1443 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-12-06 09:40 | 2009-12-06 11:21 | 311 | 101 | 61741-1 | 31411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP RELATED TO ORDER 60660-1 THIS IS FOR 311 CUSTOMERS WHEN RECLOSERS OPENED @ 0940 L3/HFP IDC XXXX
1444 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-04-08 11:31 | 2010-04-08 17:05 | 94 | 334 | 60944-1 | 31396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ONLY A PHASE LOOP OPEN @ 37830021000031 WILL OPEN RECLOSER @37830021000031 WHEN READY TO MAKE REPAIRS & WILL TAKE APROX 45 MIN. VER/HFP L3/HFP IDCC CCO HAD INITALLY HAD A 3 OR 4 DIM LIGHTS CALL BUT LOOKS LIKE THAT IT WAS MORE AN OUTAGE XXXX
1445 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2008-04-10 21:55 | 2008-04-10 22:38 | 730 | 43 | 65931-1 | 31390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001402//SERVICER HAD TO OPEN BREAKER TO CLEAR UP BROKEN CUTOUT THAT HAD DROPED INTO PRIMARY//,,,,CLOSED BREAKER BACK IN AT 22:38,,, NEW CUTOUT LOOKS FINE//VER/CRB MLR OK IDC XXXX
1446 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-03-31 18:00 | 2016-03-31 23:20 | 98 | 320 | 4011701 | 31360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECL @ 1800 GROUNDED LINE RELEASED BY CREW 078S08.. CREW ON SITE LOWERING CONDUCTORS ON BURNED POLE..ETR 2200.. NEW ETR 00:15.. RESTORED RECLOSER AT 23:20 TICKET COMPLETE..CY// VER/ ADH AJB
1447 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-03-27 23:53 | 2009-03-28 01:35 | 307 | 102 | H62227-1 | 31314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE PULLED OUT OF SLEEVE AT 38830351000034, HOT ON GROUND, OPENED C PHASE SWITCH ON POLE 38830351000032, C PHASE ONLY OUT,//CALLED BILL LYNCH AT 2156//COD 156 RELEASED BY CREW 078S05--- @ 2345 - WILL HAVE TO OPEN SWITCHES ON POLE 32 FOR APROX 90 MINUTES TOPUT UP WIRE DUP IN HOIS. ALL CUST RESTORED AT 0135 **** RECL *** PHASE ISSUES. PLEASE FIX , STRANDED CUSTOMERS ..PAUL PARSONS. IDCC DUP TO OPEN SWITCHES XXXX
1448 | South Williamson | 3411401 | DEWEY | INEZ | 2015-12-01 07:05 | 2015-12-01 09:15 | 335 | 130 | 4497781 | 31303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER ON 74-527 LOCKED OUT//PATROLING//COD 335//FAILED CUTOUT ON POLE 768-C-8, LIFTED HOTTAP AND ISOLATED XFMR//RESTORED RECLOSER VIA SCADA @ 0838//RECLOSER ON 74-527 LOCKED OUT//PATROLING/CUTOUT BROKE ON 768-8//ISOLATED CUTOUT AND RESTORED RECLOSER AT 8:38//BIG BUCKET ENROUTE TO CHANGE CUTOUT// VER/DBM AJB
1449 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-02-24 15:47 | 2011-02-24 19:00 | 427 | 193 | 60819-1 | 31291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38936184 // RELEASED BY CREW 074S02 // COD-427 ISO RECL 37820103B00210 VER/HFP L3/HFP IDC XXXX
1450 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-01-18 13:40 | 2011-01-18 15:46 | 281 | 126 | 62278-1 | 31288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 38483912 // BAD INSULATORS ON POLE 37830247C00505 -- CREW ENROUTE.STS WR # 38483912 // BAD INSULATORS ON POLE 37830177A00246 -- CREW ENROUTE. POWER RESTORED.--- SDB / 1435 / 58 CUST RESTORED VIA SW AT POLE 272A1/1135 ---- SDB / 1546 / 223 CUST RESTORED. VER/SDB IDC XXXX
1451 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-01-29 21:03 | 2014-01-30 00:43 | 142 | 220 | 4325941 | 31240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | A PHASE LOOP BURNT OPEN @ GOAB 169-41 COD 142 WE OPENED RECLOSER AT 194-115 AT 00:26, JUMPERED CENTER PHASE ON GOAB AT 169-41 , AND CLOSED RECLOSER BACK IN AT 00:43. RELEASED BY CREW 074S01 MD FILED VER/KEP IDC XXXX
1452 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2015-02-22 06:13 | 2015-02-22 14:25 | 75 | 492 | 4069981 | 31220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF NEED 50 CLASS 2 POLE, ONE CROSS ARM AND THREE ANGLE PINS AND INSULATORS, CUTOUT & ARRESTER WITH STANDOFF BRACKET.. FOUR MAN LINE CREW, AWP FLAGGERS. ALL THREE RECLOSERS ON POLE 38820796B41764 ARE OPEN, I CANNOT ISOLATE TILL AWP IS HERE. RELEASED BY CREW 079S02///CHANGE ISO POLE TO 1764****//POLE TOP BURNED OFF NEED 50 CLASS 2 POLE, ONE CROSS ARM AND THREE ANGLE PINS AND INSULATORS, CUTOUT & ARRESTER WITH STANDOFF BRACKET.. FOUR MAN LINE CREW, AWP FLAGGERS. VER/HFP L3/HFP AJB
1453 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-01-21 13:20 | 2013-01-21 14:05 | 693 | 45 | 4719951 | 31185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | EMERGENCY OUTAGE TO ALLOW CREW TO SAFELY REPLACE BROKEN CROSSARM /// COD-693 ISO PO @ 37820122C20236 ON @ 1405EMERGENCY OUTAGE TO ALLOW CREW TO SAFELY REPLACE BROKEN CROSSARM /// COD-693 ISO PO @ 37820122C20236 OPENED GOAB AT 1320 VER/HFP L3/HFP IDC XXXX
1454 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-12-23 16:12 | 2020-12-23 17:15 | 493 | 63 | 4797841 | 31059 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKEN CROSSARM ON POLE 37830402C00348//WILL HAVE TO OPEN RECLOSER 37830426C00563//COD 493//OPENED @ 16:12 CLOSED BACK IN @ 17:15
1455 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-03-13 15:01 | 2009-03-13 15:36 | 887 | 35 | 58204-1 | 31045 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN BUSSEYVILLE - LOUISA// THIS DE-ENERGIZED LOUISA STATION - DUE TO POLE FIRE// SWITCHING TO ALT SOURCES IF AVAIL. DKG/CLOSED BRK POWER RESTORED AT 1531 // VER/TOM IDCC TOF1506, TON1531 XXXX
1456 | Hazard | 3303901 | LESLIE | HYDEN | 2008-03-31 23:38 | 2008-04-01 18:06 | 28 | 1108 | 62612-1 | 31024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303901// POLE IN A BAD LOCATION, CREW TO MAKE REPAIRS IN THE MORNING. POLE BURNT OFF 342-164 RELEASED BY CREW 077S01 REPLACED POLE AND RESTORED POWER AT 1806 --------- JEFF COMBS VER/HFP IDC XXXX
1457 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-10-09 06:46 | 2016-10-09 11:00 | 122 | 254 | 4976541 | 30988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE RECLOSER OUT ON POLE 269D-356 . HOT LINE CLAMP BURNET OF . CLOSED RECLOSER BACK @ 11:00. VER/CRB /// ENTERED MD FOR B PHASE TAP FROM FUSE ON POLE 37830293000003 SHOULD BE C PHASE L3/HFP XXXHFP AJB
1458 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-12-23 07:14 | 2009-12-27 14:30 | 5 | 6196 | 65241-1 | 30980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2237 12/23 B JOHNSON REPORTED HE TRIED TO REFUSE TR AND FUSE CAME BACK OUT NEED TRANSFORMER REPLACED MAP SHOW 15KVA SERVING 5 CUSTOEMRS NEED A 50 KVA 19.9 TR PER BILL JOHNSON @ 0643 12/25 REPLACED 15 W/A 50 KVA 12/27 ON AT 14:30 D SAMMONS
1459 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-06-08 18:03 | 2015-06-08 23:36 | 93 | 333 | 4533281 | 30969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN @ 183D-122 TO 183D-124 NEED LINE CREW NO TRUCK ISO RECLOSER & TAG TO KYDDCRELEASED BY CREW 078S05/1005 REMOVE DDC TAG/PRIMARY DOWN @ 183D-122 TO 183D-124 NEED LINE CREW NO TRUCK ISO RECLOSER & TAG TO KYDDCRELEASED BY CREW 078S05///REPAIRS MADE 1SPAN #4ACSR////PRIMARY DOWN @ 183D-122 TO 183D-124 NEED LINE CREW NO TRUCK ISO RECLOSER & TAG TO KYDDCRELEASED BY CREW 078S05///REPAIRS MADE 1SPAN #4ACSR////OCR RESTORED @ 23:36///COMP AJB CNT161 PFL38830183D26091
1460 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-06-21 15:59 | 2011-06-21 17:40 | 305 | 101 | 4364581 | 30805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED OFF AT RECLOSER POLE 306-148, WE HAD TO OPEN THE RECLOSER AT// 17:25 TO MAKE REPAIRS WE CLOSED IT BACK AT 17:40 AFTER REPAIRS MADE, STIRRUP WAS ON C PHASE //COD 178+463// IDCC CNT641 XXXX
1461 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-02-27 02:31 | 2021-02-27 05:20 | 182 | 169 | 4259551 | 30758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Reclosers open (ASSESSING CONDITION)..We have a bad cutout on 167-B-152,It also blowed line fuse feeding towards 167-B-481,Made repairs and restored at 05:20.//cod 106//C Ph recl only //
1462 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-06-26 17:46 | 2018-06-26 20:49 | 516 | 183 | 4673461 | 30715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | two outside phases are hot middle is out. checking for open loop or cutout now. riser open @ 955-674 on center phase.//COD 167 FROM BEGINNING OF OUTAGE//two outside phases are hot middle is out. checking for open loop or cutout now. riser open @ 955-674 on center phase.hot tap broke.opened a and c phase @20:35 closed @20:49//// trouble tickets showing A and C phase out from the beginning and B phase went out later.
1463 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-12-12 17:25 | 2020-12-12 20:15 | 826 | 170 | 4763741 | 30695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1075773 // servicer opened Louisa-City 12kV Intellirupter 7783 in due to pole fire at pole 38830454B22517 //opened @ 1727 // crew enroute // servicer isoalted failed cutout on fault pole//clsoed CB @ 1802 // Released by crew 078S11// repaired and restored @2015
1464 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-12-25 11:50 | 2020-12-28 12:55 | 7 | 4385 | 4815531 | 30695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL DOWN BETWEEN POLE# 101-20 AND 101-21, FUSE IS OPEN ON POLE# 101-8, NEUTRAL IS NOT TRUCK ACCESSIBLE Released by crew 077F01// 6A WIRE DOWN ON POLE 37830101000023 LARGE PINE TREE HAS NEUTRAL PINNED DOWN ALL MANUEL ON HILLSIDE Released by crew 074R01 // repaired and restored at 1255
1465 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-09-03 00:50 | 2012-09-03 05:13 | 144 | 263 | 4998231 | 30690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | "A" PHASE ONLY COD-144THERE ARE 3 SINGLE RECLOSERS ON POLE 143-411. ONLY THE A PHASE RECLOSER IS OPEN. ALL THREE REC OPEN AT 0200THERE ARE 3 SINGLE RECLOSERS ON POLE 143-411. ONLY THE A PHASE RECLOSER IS OPEN. I AM PATROLLING LINE NOW. I CLOSED RECLOSER IN AND IT STAYED. RECLOSER STAYED IN ABOUT 2 MIN. AND THEN OPERATED A FEW TIMES AND THEN ALL 3 RECLOSERS OPENED UP DUE TO FAILED INSULATOR AT POLE 143-70. THIS WAS AT 2:00 AM.--- SDB / 0300 / 88 CC REST. --- SDB / 0513 / 276 CC REST IDCC CNT364 XXXX
1466 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-11-08 11:24 | 2016-11-08 12:45 | 507 | 81 | 4084251 | 30648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 1124 SCADA INDICATED CB OPEN/,,RECL 38830138D00177 HAS A BLACKENED SOURCE SIDE BUSHING,,ISOLATED RECL,,MEN AND EQUIP IN CLEAR,,TAGGED REC TO DDC,,PATROLED LINE AND FOUND NO HAZARDS // VER/ ADH /// VER TIMES PER SCADA & DOL L3/HFP XXXHFP AJB
1467 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-12-02 09:31 | 2010-12-02 11:46 | 318 | 135 | 62372-1 | 30639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSURE ON POLE #37830021000156 IS OUT . WILL PATROL LINEOPNED @ 45-92 CLOSED 21-156 POLE FIRE @ 37830068000082 HAVE ISOLATED IT $ E. YOUNG IS WRITING JOB TO REM INACTIVE POLES.CLOSED @45-92 @ 11:46 VER/KEP L3/KEP IDC XXXX
1468 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-02-15 02:53 | 2013-02-15 07:00 | 124 | 247 | 4820711 | 30628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE WIRE BURNT DOWN AT POLE 356-108 - 124CC//NO TRANSFER OPPORTUNITY// FLAGGERS CALLED// 2 MAN CREW CALLED// WILL HAVE TO OPEN RECLOSER ONCE CREW STARTS TO MAKE REPAIRS// VER/ARN IDC XXXX
1469 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-06-15 20:21 | 2013-06-16 07:23 | 50 | 662 | 4346061 | 30622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | THERE IS A FAULT SOMEWHERE IN UG. WILL START ISOLATING AND TESTING. CREW ENROUTE TO ASSIST. CLOSED FUSE ON 784-286 @ 00:30 ENERGIZING UP TO AND INCLUDING 784-1553. TESTING UG CABLE PAST THAT XFMR. FAULT LOCATED - CREW WORKING TO REPAIR. REPAIRS COMPLETE. RESTORED REMAINING OUTAGED CUSTOMERS AT 7:23. SH RELEASED BY CREW 076S02//OPEN PT ON PAD "-1553 WONT ALLOW ITSELF TO BE REMOVED FROM MAP//ASSIGNING TO PO ADMIN//IT FORCE CLOSED IDCC CNT136, PH C ONLY, CDC83 XXXX
1470 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-12-11 15:53 | 2022-12-11 22:29 | 83 | 396 | 4250521 | 30611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | reclosure 1040-18 open . wire off the insulator on pole 1065-5 . opened solid blade line fuse on pole 1064-78, tagged to myself placing grounds for crew to make repairs on pole 1064-78 as well . restored reclosure @ 21:28 up to pole 1064-78 .restored power on pole 1064-78 @ 22:29
1471 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-10-20 21:54 | 2018-10-21 13:50 | 32 | 956 | 4279091 | 30592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Fuse is open on 600-8 Wire dn at 599-34to35#2 alum. Also primary needs resagged 600-9. Linecrew required Released by crew 078S11.power restored at 13:50
1472 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-03-12 08:14 | 2021-03-12 10:50 | 196 | 156 | 4329021 | 30576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Rec. open @1056-D-299, checking. Bad dead end insulator @1080-24, will be making repairs. Got dead end replaced and rec. closed back in @1050.
1473 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-01-04 01:23 | 2008-01-04 09:20 | 64 | 477 | 53451-1 | 30528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2206403///NEED CREW CREWON WAY #4 SOLID COPPER NO TRUCKS RELEASED BY CREW 078H04// RECLOSER ON POLE 214-51 WAS NEVER OUT// PRIMARY BROKE IN THE CLEAR @ 213-247// ADJUSTING OUTAGE//CREW ON SITE/FETR1045/VEM/RECLOSER OPEN AT 0751/REPAIRS MADE/POWER RESTORED 0920/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 - RECLOSER OUTAGE ON ANOTHER ORDER// VER/TOM IDC XXXX
1474 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-07-22 17:23 | 2013-07-22 22:51 | 93 | 328 | 4577231 | 30504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | REC IS OPEN ON 620-342 PATROLLING. PRIMARY TIE BROKE AND PRIMARY LAYING ON EXT LINK, PLEASE REPLACE CUTOUT AND BLOWN ARRESTER 12KV, ISOLATED & GROUNDED, TAGGED TO VENRON M. AT 620-342 RELEASED BY CREW 078S11/CREW ON SITE/FETR2330/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2251/PLEASE COPY TICKET TO TECH TO WRITE JOB TO CHG POLE 619-27/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP IDCC CCWU XXXX
1475 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-06-25 21:55 | 2016-06-26 10:57 | 39 | 782 | 4475691 | 30498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7.2KV CUTOUT BURNT THE TOP OF THE POLE OPEN OCR@2155 WILL NEED TO REPLACE 40FT POLE NO TRUCK ACCESS MAYBE ABLE TO PUT LONG POLE EXTION ON THIS RELEASED BY CREW 077S01 NEED 4 MAN CREW AND MANUAL ROW CREW7.2KV CUTOUT BURNT THE TOP OF THE POLE OPEN OCR@2155 WILL NEED TO REPLACE 40FT POLE NO TRUCK ACCESS MAYBE ABLE TO PUT LONG POLE EXTION ON THIS RELEASED BY CREW 077S01 NEED 4 MAN CREW AND MANUAL ROW CREW REPLACED POLE POWER RESTORED AT 1057 VER/CRB AJB
1476 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-07-03 17:38 | 2019-07-03 19:22 | 293 | 104 | 4649541 | 30472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER DOL 935830/ Bad crossarm 38830852000102/ Had to open switch 38830875A00131 to shed load for a load transfer on the circuit breaker outage/ ISO 38830875A00131/ COD 293/ off 1738 on 1922 L3/HFP
1477 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2014-10-04 12:55 | 2014-10-04 18:25 | 613 | 330 | 4552621 | 30460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX CABLE BURNT DOWN AT POLE 46-2310, OPENED BREAKER AT 1255, OPENED SWITCHES AT POLE 46-A-165 AT 1305, AND CLOSED IN BREAKER AT 1310 RELEASED BY CREW 078Q04 VER/KEP AJBC CCU FEC57
1478 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-01-26 08:01 | 2011-01-26 11:10 | 161 | 189 | 64389-1 | 30429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38578066 //.--- NEED TO REPLACE BAD CUTOUT AND ARRESTOR COD-161 ISO RECL 37820026000237 VER/HFP L3/HFP IDC I CAN NOT TELL FROM VOICE RECORDING IF THIS SHOULD BE JUST ONE PHASE INSTEAD OF ALL THREE. LEFT AS ALL THREE XXXX
1479 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-09-14 11:40 | 2008-09-14 18:15 | 77 | 395 | 62331-1 | 30415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310501//NEED TWO MEN AND BIG BUCKET MLR OK
1480 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-07-09 08:14 | 2010-07-09 20:00 | 43 | 706 | 63853-1 | 30358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 35918201 // UG FUSE IS OUT,TOLD TO RE-FUSE////////RE-FUSED,FUSE CAME BACK OUT.WILL CALL FOR CREW,TALKED TO MASSEY,HE IS GETTING HELP ENROUTE.NOTE NEW FETR // WR/35918201. // RELEASED BY CREW 074S06 VER/HFP L3/HFP IDC XXXX
1481 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-03-31 07:23 | 2017-03-31 09:56 | 285 | 153 | 4600801 | 30304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE 37830344000144 === BAD CUTOUT ON POLE 37830318D00044 ICEULATED CUTOUT == PUT MAIN LINE ON AT 9:09 === CALLED FOR BIG BUCKET ===REPLACED CUTOUT ON TRANSF == CLOSED CUTOUT 9:56 ALL ON // COD-285 ISO OCR 37830344000144 VER/HFP L3/HFP AJB
1482 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-07-26 09:02 | 2009-07-26 19:20 | 49 | 618 | 51260-1 | 30282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | THIS IS AT MARINA FOUND BAD SECTION OF CABLE GOING TO PAD MOUNT 759-16 TCM// CABLE TESTED GOOD, FOUND BAD 167 KVA PADMOUNT CHANGED OUT TCM// VER/KEP L3/KEP IDC XXXX
1483 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-07-24 16:42 | 2017-07-24 21:30 | 105 | 288 | 4174591 | 30240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 075H04 . FOUND LOOP BURNED INTO ON POLE 1110-4 . NEED 3 MAN LINE CREW , CAN USE SIDE BY SIDE TO GET TO POLE . WILL NEED TO REPAIR DEADEND . 6A COPPER WIRE ALMOST INTO OPENED RECLOSER ON 4175841.RELEASED BY CREW 075H04 . FOUND LOOP BURNED INTO ON 1110-4 . NEED 3 MAN LINE CREW , CAN USE SIDE BY SIDE TO GET TO POLE . WILL NEED TO REPAIR DEADEND . 6A COPPER WIRE ALMOST INTO . RELEASED BY CREW 075H04 OPENED ON POLE 151 AT 20:55 POWER RESTORED AT 21:30 RELEASED BY CREW 077H02 3 VER/AWD SJG
1484 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-05-09 07:06 | 2020-05-09 16:05 | 56 | 539 | 4815781 | 30184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | low side fuse blown on pole 1137-343//top of pole burnt off on 1137-402//no truck approach//will need line crew// need two 7200 cutouts,arrestors and brackets//7200 corner shoe and deadend ins.//7200 deadend material for side tap//guy attachment///can lower down on pole//plenty of spacing//no tags or grounds Released by crew 079S01. CREW ON SITE. ON AT 16:05 WORK COMPLETE.
1485 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2018-04-15 18:58 | 2018-04-16 00:05 | 118 | 307 | 4231421 | 30090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Broken solid blade cutout on 38820868D00183.VOLTAGE GOOD@RECLRS,1 DEAD PHASE@868-75//////////BROKE SOLID BLADE 868-183,CREW ENROUTE TO HELP////NEED OUTAGE TO REPAIR
1486 | South Williamson | 3411401 | DEWEY | INEZ | 2009-02-22 11:45 | 2009-02-22 12:22 | 812 | 37 | 50287-1 | 30044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED RECL @ 1145 CLOSED @ 1222TOP BLOWED OFF TRANSFTOP BLOWED OFF TRANSF RELEASED BY CREW 079S01// CREW ON SITE CHANGING POT OUT TCM//WAITING ON 2-HOLE PADS FROM PIKEVILLE// RESTORED AT 2032 //VER/GAH IDCC CNT814, PN277, CDC92 DUPLICATE CREATED FOR ORIGINAL TRANSFORMER OUTAGE XXXX
1487 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-08-15 15:13 | 2016-08-15 20:58 | 87 | 345 | 4780561 | 30015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 45-3638 HOT TAP & BASKET BURN UP ON LINE FUSE ON HENDRIX ACROSS FROM 1917 BLACKBURN AVE ACROSS FROM HIGHLAWN AVE. FLAGGERS , LINE CREW NEEDED TR. OK RELEASED BY CREW 078S04, OPEN RECLOSER 45-2609 TO MAKE REPAIRS.DEENERGIZED AT 20:35. POWER RESTORED AT 20:58 SEE H4780561 FOR REC OUTAGE VER/HFP L3/HFP AJB CNT157 PH A.
1488 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-03-24 16:45 | 2018-03-25 10:00 | 29 | 1035 | 4051231 | 30015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | fuse open on pole 811-33. primary down at pole 811-164. need three men crew and small piece of #4 copper.. can truck. could use flaggers if got them. if not could block road..rn Released by crew 076H03. Restored at 10:00.
1489 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2021-07-16 16:10 | 2021-07-16 17:41 | 329 | 91 | 4921691 | 29939 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1132377/ restored 1741/ Transmission found dead end bell failed
1490 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-01-01 11:47 | 2009-01-01 13:39 | 267 | 112 | 50519-1 | 29904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3312202//SOURCE SIDE CONNECTION ON RECLOSER CAME LOOSE3312202// LED BURNT INTO//VER/CRB L3/KEP IDC XXXX
1491 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-02-27 00:55 | 2008-02-27 09:05 | 61 | 490 | 50757-1 | 29890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000701 / HAVE RECLOSER ON POLE 1071-126, ISOLATED AND GROUNDED, I HAVE A 45-CLASS4 POLE BURNT OFF, POLE NUMBER IS 1071-30, NEXT POLE UP FROM THE RECLOSER, CAN USE TRUCK, NEED A POLE AND CUTOUT AND L/A, CUTOUT FAILED CAUSING THIS FIRE, RELEASED BY CREW 078S06 //VER/CRB IDC XXXX
1492 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-07-12 14:53 | 2011-07-12 21:02 | 81 | 369 | 4534231 | 29889 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF // COD 144 // IDC LOOKS LIKE PH C ONLY CHANGED COUNT FROM 144 XXXX
1493 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-07-08 18:43 | 2016-07-08 19:12 | 1029 | 29 | 4567571 | 29841 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | T-LINE OUTAGE RESTORED 1912/// VER/DKM AJBC TOF1416 MCCST CCO PER DOL LCD38830810D00066
1494 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-02-02 16:50 | 2013-02-02 20:08 | 320 | 198 | 4786711 | 29709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY TAP CUTOUT FAILED, AND BURNED POLE TOP OFF. RELEASED BY CREW 079H06 RELEASED BY CREW 079H07 VER/KEP IDCC CDC88 XXXX
1495 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-10-19 14:03 | 2022-10-20 01:18 | 44 | 675 | 4043801 | 29700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole top has rotted off and primary is in open air. reported by gerald combs Crew onsite making repairs.
1496 | Hazard | 3303902 | LESLIE | WOOTON | 2015-07-25 00:54 | 2015-07-25 08:45 | 63 | 471 | 4940201 | 29673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REC IS OPEN ON POLE 413-426, WILL BE LOOKING LINE OVER/// WE HAVE TOP OF POLE BURNT OFF POLE 437-1, I BELIEVE WE CAN LOWER AND NOT HAVE TO CHANGE OUT POLE. TALKED TO JEFF HE HEADING THIS WAY.HORNETS ON STEPDOWN HAVE EXTENDED THE OUTAGE// WIRE UP GROUNDS REMOVED, POWER RESTORED VER/KEP AJB
1497 | Whitesburg | 3309302 | VICCO | JEFF | 2009-05-05 06:18 | 2009-05-05 08:50 | 340 | 152 | 54022-1 | 29645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3309302 - BAD ARRESTER CUTOUT ON POLE 348A-282 TOOK OFF LINE == REPLACED CUTOUT ON POLE 282 == POWER ON VER/KEP L3/KEP IDC XXXX
1498 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-10-25 03:17 | 2020-10-25 04:05 | 617 | 48 | 4582291 | 29616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 0317 SCADA Opened at 39831098B16133 due to telephone pole laying energized on 3 phase at 38830018000007 affecting 617 CC /// Closed at 0405 restoring all customers
1499 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-12-14 18:35 | 2010-12-14 21:15 | 220 | 160 | 50164-1 | 29600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PHASE A OPEN // WIRE DOWN ON 71-54//OPENED OTHER 2 PHASES @ 1935// OPENED SWITCHES ON POLE 71-50//CLOSED RECLOSERS UP TO OPEN SWITCHES @ 2115 // WIRE APPEARED TO BURN DOWN UNDER OLD COMPRESSION SLEEVE//COD 161 (+ 311, SEE H50164-1)// VER/DBM IDC PHASE B IS OUTSIDE PHASE CHANGED COUNT FROM 161, CHANGE EQUIPMENT FROM CONDUCTOR XXXX
1500 | Hazard | 3303902 | LESLIE | WOOTON | 2013-04-17 08:51 | 2013-04-17 10:29 | 302 | 98 | 4017561 | 29596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIGHTNING HIT CUTOUT VER/KEP IDC XXXX
1501 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-02-23 21:12 | 2019-02-24 09:00 | 55 | 708 | 4851181 | 29588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | \\ Lead on hot tap burnt open on pole239-57/// this is on side of the hill and the creek is up here//// will need to wait till daylight ///will need aout 2 men Released by crew 074S02///opened recl 239-C3-362 at XXXXLead on hot tap burnt open on pole239-57/// this is on side of the hill and the creek is up here//// will need to wait till daylight ///will need aout 2 men /// Opened recloser up @ 08:20 to make repairs0900
1502 | Hazard | 3309302 | VICCO | JEFF | 2015-03-19 18:06 | 2015-03-19 20:17 | 225 | 131 | 4210701 | 29475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKEN, NEED 1-8FT CROSSARMAND BRACES, 2- STRAIGHTLINE ARM PINS AND INSULATORS, C/O AND ARRESTOR AND ARM BRKT. 3-MAN LINE CREW, FLAGGERS. 7200KV.////RELATED TO ORDER 4210551/ OPENING RECLOSER 323-D3-790 TO SAFELY ISOLATE TROUBLE/RECLOSER AND LOWSIDE ON STEP ON POLE 323-D3-790 TO GREG SHOUSE/OPENED1806/CLOSED 2017/COD 225// VER/ ADH AJB
1503 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-08-27 05:04 | 2008-08-27 16:00 | 72 | 656 | 55635-1 | 29472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003703//BURNT OFF POLE 235-68 (40-2) NO TRUCKS TO POLE , LIFTED HOT ON POLE 235-38. NEEDS LINE CREW .. NEEDS LINE CREW . RELEASED BY CREW 078S01 IDCC PN68 XXXX
1504 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-06-29 17:43 | 2008-06-30 00:50 | 69 | 427 | 59622-1 | 29463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT/ CALLED CREW // VER/TOM AJB
1505 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2016-07-04 19:19 | 2016-07-05 09:45 | 34 | 866 | 4527191 | 29444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE C LOOP OPEN ON PRIMARY BREAKER IN SPAN AT POLE 37820147A00026. PATROLLED ALL, R/W BAD IN SOME PLACES. WILL NEED BIG BUCKET TO REACH. ELLIOT HAS NEW POLE SET NEXT TO THIS LOCATION. UPPER END OF MTN WATER LOT. BJ RELEASED BY CREW 074E04. REPAIRED LOOP 0N PL#147-26 WILL CLOSE C PHASE FUSE ON NEXT PL# 147-26 AND PICK UP REMAINING CUSTS AJB
1506 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-06-08 17:50 | 2015-06-09 10:42 | 67 | 1012 | 4539151 | 29435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | \\FUSE OUT POLE 1099A-106// BAD CSP XMER AT POLE 1098-D-593 REPLACING TRANS. INSTALLING NEW CUTOUT AND FIBERGLASS BRACKET..ALL POWER RESTORED AT 10:42 RELEASED BY CREW 078Q09 VER/CRB AJB
1507 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-05-06 01:21 | 2019-05-06 02:49 | 441 | 88 | 4229391 | 29412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire down at pole 37830024A40047 // working to isolate fault//cod 441// Rec. open @23-D4-594, isolated wire down with a clamp 24-A4-46, closed rec. back in @0222. Made repairs and closed rec. 24-A4-47 @0249, all power restored. ¦¦ SENT ENGINEERING EMAIL ABOUT THIS OUTAGE - L3/HFP
1508 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2011-12-15 23:10 | 2011-12-16 02:00 | 173 | 170 | 4181331 | 29410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REPLACING POLE IDC XXXX
1509 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-09-30 19:46 | 2012-09-30 23:06 | 147 | 200 | 4101031 | 29400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SINGLE PHASE WIRE DOWN AT POLE 1147-282 PER JIM LINKOUS POLE 1147-282 PRI. AND NU. BURNT DOWN REC. OPEN ON 1147-237 A PHASE (147 CC) OPENED B PHASE 21;25 (64 CC) TO DO WORK RELEASED BY CREW 078S08/ FETR 23:15// JEH// REPAIRS COMP. ALL POWER RESTORED @ 23:06 ////JEH //VER/GAH IDC XXXX
1510 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-04-28 06:46 | 2013-04-28 11:46 | 98 | 300 | 4052991 | 29400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WIRE OFF INSLATOR/ ///VER/CRB L/3 CRB IDC XXXX
1511 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-01-10 00:43 | 2016-01-10 11:07 | 47 | 624 | 4598231 | 29328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" & "C" PHASE OPEN COD-47/DID NOT SEE ANYTHING ON LINE, VERY FOGGY AND RAINING, TRIED REC. CAME BACK OUT, A LOT OF THIS IS ON HILLSIDE, HOLD TILL DAYLIGHT. ...2 BAD CUTUOTS ON POLE 37830318A00115./OPENED "B" PHASE AT 0911 COD-50/. ...2 BAD CUTUOTS ON POLE 37830318A00115.. 4 BAD CUTOUTS AND INSULATOR..POWER RESTORED @ 11:07 VER/KEP AJB
1512 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-03-23 07:05 | 2022-03-23 09:33 | 198 | 148 | 4660141 | 29304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Tree fell through line and has center phase conductor is laying on arm at 38831080000011-looking for place to isolate///// 3 PHASE REC STILL OPENEN///BYPASSED @ 9:33////INFORMED DOUG ABOUT REC NOT CLOSING
1513 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-02-25 21:36 | 2011-02-26 02:41 | 96 | 305 | 63069-1 | 29280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38955877 //BAD 500 KVA STEPDOWN AT POLE 547D3/183 CALLING CREW @ 2227 // NEED CLEANUP MATERIALS AND SOMETHING TO HAUL THE OLD TR IN....ITS A MESS/CREW ON SITE/FETR0400/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0241/PLEASE CLOSE TICKET/THANKS/VEM VER/SDB IDC XXXX
1514 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-11-15 07:54 | 2022-11-15 12:25 | 108 | 271 | 4143491 | 29268 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | phase burnt in 2 at connector, manual ROW on way to clear ROW so we can safely make repairs// had to open rec on pole 1103-128 to cut trees that were in primary, opened @ 11:11 closed @ 12:25// send a copy to Bill Johnson pole needs changed out and send a copy to corey farmer, need to have ROW cleared// Email sent to B Johnson and C Farmer
1515 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-05-11 22:20 | 2009-05-12 05:43 | 66 | 443 | 63088-1 | 29238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER IS OUT ON POLE 213-15. I AM PATROLLING LINE NOW. OPENED SWS AT POLE 213-30 SHOT RECL DID NOT HOLD .. WILL CONT. PATROL. AND OR CALL FOR HELP. AT 0500 CREW UPDATE . FOOT PATROL OF LINE MAY NEED TO WAIT UNTIL DAYLIGHT TO FIND TROUBLE. MLR OK
1516 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-12-24 18:32 | 2011-12-24 21:20 | 174 | 168 | H4200461 | 29232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE OUT 105 CUST /// HAVE WIRE DOWN @ 37830047D00006CENTER CONDUCTOR AT RECLOSER POLE 47-6 ON LOAD SIDE BURNED DOWN. IT BURNED INTO AT BELL. OPENED 2 ADDITIONAL RECLOSERS TO MAKE REPAIRS OPEN AT 2120 - CLOSED ALL 3 AT 2138 // A=102, B=94, C=80, AB=3 -- VER/TOM L3/TOM IDCC TOF1832 XXXX
1517 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-11-01 07:46 | 2020-11-01 10:43 | 165 | 177 | 4611111 | 29205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | rec on 1024-211, was moved to pole 1024-4, upon arrival found rec to be in but l/f was blown which the rec was on same phase, patrolled found #2 alum pri down on 1024-74, can get truck to this pole, also found pri was out of run around shoe, next pole, no trucks to this pole, CREW REQ, have tg and grd to Rick Morgan, and rec islolated at 1024-4 Released by crew 078S06//arrived RM recloser &fuse in @10:43 please close tic RM
1518 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-08-07 07:17 | 2011-08-07 11:47 | 108 | 270 | 4674231 | 29160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER OPEN ON POLE 176-174, PATROLLING LINE. -- BROKEN CUTOUT ON POLE 37830152000022, DUTY SUPERVISOR NOTIFIED. -- ALL POWER RESTORED AT 11:47 63 CC VER/PDP IDCC CNT63 XXXX
1519 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-01-06 20:54 | 2010-01-06 21:44 | 582 | 50 | 64093-1 | 29100 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE OPEN @ 1929 // DROPPED REMAINING CUSTOMER @ _____ IDC LOOK AT 64388 ALSO ONE ODD CALL AT 1504 AND NO REAL OUTAGE UNTIL WE OPENED 46 BREAKER AT ELKHORN CITY, THEN WE HAD ONE PHASE OUT IDC NO CUSTOMERS OUT UNTIL 1929 SEE 64388-1 THESE CUSTOMERS SEEING OPERATIONS EVERY 5 MIN. UNTIL PH A OUT AT 1929 SEE 64388-1 AND THE REMAINING OUT AT 2054 XXXX
1520 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-02-23 06:37 | 2014-02-23 10:13 | 146 | 216 | 4427561 | 29088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICER PATROLLING LINE. A PHASE HAS BURNED DOWN AT A SPLICE MID SPAN. NEED TWO MEN AND BUCKET TRUCK. OPENED DISC AT POLE 38821041B00010 TO ISOLATE TROUBLE. CLOSED RECLOSER BACK IN AT 07:49. CLOSED IN AT POLE 1041-B-10 AT 10:13. RELEASED BY CREW 079S02//COD 50// VER/DBM
1521 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-12-01 23:44 | 2010-12-02 11:00 | 43 | 676 | 62296-1 | 29068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR #37957224 // BAD 25KVA PADMOUNT // ADDITIONAL HELP COMING OUT TO REPLACE TRANSFORMER. NO 25 KVA ON LOT, WILL HAVE CREW OUT IN THE MORNING TO REPLACE TRANSFORMER. RELEASED BY CREW 074S05//I HAVE TO GO TO PAINTSVILLE TO GET XFMR. CREW IS OIN ROUTE TO SITE./// REPLACED BAD XFMR AND RESTORED POWER AT 11:00. TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDCC CDC83, INCORRECT FALT POLE XXXX
1522 | Whitesburg | 3409503 | BURDINE | JENKINS | 2021-06-19 13:45 | 2021-06-19 16:30 | 176 | 165 | 4771371 | 29040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | rotten pole fell, we changed it out. I opened the switches on pole 358-317 at 13:45 and closed back at 16:30
1523 | Pikeville | 3402003 | KEYSER | MULLINS | 2020-06-01 06:18 | 2020-06-01 10:24 | 611 | 246 | 4937671 | 28977 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE LOOP BURNT OPEN @ POLE 38831127B00599. NEED CREW & FLAGGING CREW // Opened recloser on 38831127B10954 to safley make up loops opened @0959 closed back in restoring everyone @1024
1524 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2015-08-04 18:09 | 2015-08-04 21:45 | 134 | 216 | 4977331 | 28944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER BYPASS JUST OUTSIDE OF STATION FAILED CAUSING 46KV HISH SIDE FUSE TO BLOW OPENED VER/SEF ///CHANGED TIME OFF TO WHEN RECLS OPENED @ 1809 PER DISPATCH LOG & HISTORICAL OUTAGE - CUSTOMER TICKETS ON OMD - CUST HAD POWER (ALTHOUGH NOT FULL) UNTIL THEN -- L3/HFP HFPC TOF1639 AJB
1525 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-11-24 00:48 | 2018-11-24 12:00 | 43 | 672 | 4471181 | 28896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | will work in the AM 11/24/18 per late night guidelines-bad 6 in disk-pole1135/1---send vhurt fetr 1130 L3/HFP
1526 | Hazard | 3311103 | STINNETT | WENDOVER | 2014-03-16 20:21 | 2014-03-16 21:15 | 535 | 54 | 4498801 | 28890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW MAKING REPAIRS NOW C PHASE CUTOUT @ POLE 411-1 FAILED.BAD CUTOUT ON POLE 411-1 RELEASED BY CREW 075H04 VER/ARN VER/HFP L3/HFP IDC XXXX
1527 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-08-29 13:52 | 2022-08-29 18:33 | 802 | 281 | 4808711 | 28808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crew required ,,,trucks to pole 327-266,,,broke 8 ft cross arm ,,,line fuse is blew becuase of arm ,,,flaggers required in curve Released by crew 078S05.. Line fuse feeding both directions MDR submittedcrew required ,,,trucks to pole 327-266,,,broke 8 ft cross arm ,,,line fuse is blew becuase of arm ,,,flaggers required in curve Released by crew 078S05//on site RM open 600 amp switches to make repairs at 327A265 open @ 17:58crew required ,,,trucks to pole 327-266,,,broke 8 ft cross arm 1833
1528 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2015-04-26 06:12 | 2015-04-26 15:05 | 54 | 533 | 4366441 | 28782 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 21-8293 B PHASE UNDERGROUND FUSE OUT 65T RELEASED BY CREW 078S08/CREW ENROUTE TO TEST UNDERGROUND CABLE/VEM/CREW ON SITE/CAN NOT GIVE FETR UNTIL CABLE IS TESTED/VEM/BAD PARKING STAND/ELBOW@21-8295/CREW ISOLATING CABLE/FETR1600/VEM/ALL B PHASE CUST RESTORED 1505/WILL HAVE DDC CREATE ABNORMAL/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/ARN L3/HFP XXX AJB PH B.
1529 | South Williamson | 3411401 | DEWEY | INEZ | 2021-07-09 13:01 | 2021-07-09 15:55 | 175 | 174 | 4879011 | 28662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Tap burnt off at 38830792C00009 (163 CC) OFF @ 1301 Opened SW at 38830792C00004 (additional 12 CC) Off at 1530 On at 1555
1530 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-08-21 20:33 | 2016-08-22 01:55 | 89 | 322 | 4823091 | 28658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PAT LINE BAD CUTOUT ON P 404-198 FEEDING UP RAVEN ROCK FETR 2:00 LRM CREW ON SITE GOING TO OPEN TAG AND GRND AT P428-296 TO REPLACE CUTOUTS SAFELY REC. BACK IN AT 1:55 LRM RELEASED BY CREW 078H06 VER/KEP /// SEE 4823351 OUTAGE ON RECL TO REPLACE SW SAFELY L3/HFP XXXHFP AJB
1531 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-09-02 20:35 | 2010-09-02 21:05 | 955 | 30 | 63033-1 | 28650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | EMERGENCY OUTAGE TO ISOLATE A SWITCH THAT HAS FAILED AND IS BURNING OUTAGE SHOULD BE NO LONGER THAT 30 - 40 MINUTES // RELATED TO ORDER 63016-1 // COD-955 VER/PDP IDC XXXX
1532 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-03-05 01:30 | 2010-03-05 06:38 | 156 | 308 | 63001-1 | 28626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | "B" PHASE FUSE BLOWN INTERRUPTING 126 CUSTOMERS CLOSED AT 03:00 FM 71-50 TO OPEN OCR AT 47-6. RESTORED 26 CUSTOMERS. OPENED RECL AT POLE 70-151. THEN CLOSED RECL AT POLE 47-6 AT 0407. CLOSED OCRS A & B ON POLE 70-151 AT 06:38. HAVE TAPS 46-30 & 46-23 ISOLATED. AJB NEED SW. IDC XXXX
1533 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-08-21 16:48 | 2009-08-21 17:52 | 447 | 64 | H59391-1 | 28608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 600 AMP SWITCH NEEDS TO REPLACED "A"PHASE IS OUT COD-245 RELEASED BY CREW 077S01 OPENED OTHER 2 RECLOSURE AT1648 COD-569 MADE REPAIRS AND RESTORED POWER TO ALL CUSTOMERS AT 1752 CREW 077H01 VER/KEP L3/KEP IDC XXXX
1534 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-10-09 05:01 | 2014-10-09 05:45 | 650 | 44 | 4577681 | 28600 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP L3/HFP AJB CCTIN
1535 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-09-30 16:19 | 2014-09-30 17:17 | 493 | 58 | 4539761 | 28594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | C PHASE REGULATOR BLOWN ITS TOP ON POLE 858-421 //COD 493// VER/ARN L3/HFP AJB
1536 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-03-26 22:23 | 2013-03-27 03:27 | 94 | 304 | 4960741 | 28576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SOUTHSIDE 12KV CB A OPERATED AND RECLOSED SUCCESSFULLY. LOOP BURNT OFF BETWEEN 966-644 AND 966-1165 STEEL TOWERS NOT ON MAP RELEASED BY CREW 079S02 IDCC FP NULL XXXX
1537 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-08-09 23:59 | 2014-08-10 04:50 | 98 | 291 | 4349171 | 28518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 075H01CONDUCTOR PULLED OUT OF A # 4 SLEEVE AJB
1538 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-01-06 22:21 | 2022-01-07 11:10 | 37 | 769 | 4317311 | 28453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOLDING DUE TO HAZARDOUS ROAD CONDITIONS..line fuse blown on pole 151-69..will patrol..small tree fell between poles 150-24 and 150-282 and broke pri.////will need bucket truck to make repairs..restored.
1539 | Hazard | 3302704 | HAZARD | KENMONT | 2014-04-04 00:01 | 2014-04-04 11:00 | 43 | 659 | 4571051 | 28337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER AFTER HOURS GUIDE LINES THIS TROUBLE WILL BE CHECKED ASAP 04/04/14 === STEPDOWN TRANSF BAD ===- 333 KVA STEPDOWN BAD === NEED LINE CREW AND FLAGERS AND 333 KVA STEPDOWN //ONLY CENTER PHASE OPEN//OPENED OTHER 2 PHASES @ 0901//COD 3 + 43// IDCC CNT46, CDC92, INITIALLY PH A XXXX
1540 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-07-04 17:10 | 2012-07-07 12:37 | 7 | 4047 | 4571641 | 28329 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NU,BURNT OFF ON POLE VER/HFP L3/HFP
1541 | South Williamson | 3411401 | DEWEY | INEZ | 2008-07-31 12:40 | 2008-07-31 15:20 | 177 | 160 | 62889-1 | 28320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401//SEE 62833-1//SERVICER OPENED LINE FUSE DUE TO POLE FIRE//COD 177// VER/DBM IDCC TOF1129 XXXX
1542 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-02-17 23:17 | 2022-02-18 04:37 | 110 | 320 | 4499681 | 28240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 92-510 b phase tie broke primary laying arm b,c phase open and a phase still energized crew required no truck Released by crew 078S09 A phase rec opened at 04:07 Closed on 92-B-93 at 04:37. Ticket complete Released by crew 078H11
1543 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-09-29 17:41 | 2015-09-29 17:57 | 1764 | 16 | 4289601 | 28224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED AT 1741 CLOSED AT 1757 VER/ARN L3/DKG
1544 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-22 09:44 | 2011-06-22 17:00 | 76 | 436 | 4388881 | 28186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOW SIDE OF STEP DOWN OUT ON POLE 268//PATROLLING NOW//OPENED RECLOSER ON POLE 672-133 RIGHT HAND PHASE// CLOSED STEPDOWN ON POLE 268// GOING TO DO SOME MORE PATROLLING//CLOSED RECLOSER ON POLE 133 UP TO OPEN SWITCH ON POLE 648-51 AT 15:30// HAVE ONE MORE SECTION OF ROUGH LINE TO PATROL//BAD CUTOUT ON POLE 648-51//CHANGED OUT ALL CUSTOMERS RESTORED AT 1700//COMPLETE//EM RELEASED BY CREW 079S01 IDC XXXX
1545 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-06-20 14:05 | 2014-06-20 18:55 | 97 | 290 | 4123101 | 28130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE APHASE RECLOSER IS OPEN ON 428-296 PATROLLIN LINE //DC CHANGED COUNT TO 97. FOUND PRIMARY DOWN AT 428-58, ISOLATED GROUNDED&TAGGED TO DWEST ON 428-296 LINECREW REQUIRED. APR AT 1855 CLOSE TICKET//COD 97 AJB PH A.
1546 | Hazard | 3310502 | HADDIX | CANOE | 2017-11-09 23:07 | 2017-11-10 11:47 | 37 | 760 | 4545801 | 28120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | on pole 37840168000014 wire has broke at de shoe and hot line clamp is holding primary wire up need de shoe and #2 al up on side of hill Released by crew 077S05 temp low forecast for area 33 degrees
1547 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-09-08 11:48 | 2017-09-08 17:03 | 89 | 315 | 4340651 | 28035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ROTTENED OFF AT GROUND 809-523.ROGER MAYNARDS CREW ON SITE..811 DIG CALLED AT 11.18 AM..#1709080744.OPENED SWITCHES ON POLE 785-48 AT 11:48 GRD TAGGED.. RELEASED BY CREW 076S01// CREW ON SITE STARTING REPAIRS// REPAIRS COMPLETE, GROUNDS REMOVED// RESTORED AT 17:03 38830785D20048 38830809C10523 VER/AWD L3/HFP XXXHFP SJG
1548 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-08-19 10:03 | 2017-08-19 11:30 | 322 | 87 | H4278161 | 28014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 PHASE (A PHASE COD-31) OF HENDRIX BURNT DOWN AT POLE 785-273/ OPENED GOAB 785-D2-331 AT 1003/ MADE REPAIRS AND CLOSED 785-331 @ 11:30. SH RELEASED BY CREW 076S02 VER/KEP SJG
1549 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-11-12 13:06 | 2015-11-12 14:23 | 363 | 77 | H4435541 | 27951 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 600 AMP DISC HAS FAILED OUTSIDE JACKSON STATION// SERVICER ON SITE AND CREW ENROUTE// WILL REQUIRE BREAKER OUTAGE TO MAKE REPAIRS// APPROX 90 MINUTES TO MAKE REPAIRS - CREWS ON SITE MAKING REPAIRS @ 1500//TOM - CLOSED STATION CB @ 1545//600 AMP DISC HAS FAILED OUTSIDE JACKSON STATION// SERVICER ON SITE AND CREW ENROUTE// WILL REQUIRE BREAKER OUTAGE TO MAKE REPAIRS// CREATED H4435541 DUE TO DOL COMMENTS & SCADA SHOWING LOAD DROPPING OFF `A` PHASE (363 CUST) @ APROX 1306 PER SCADA VER/HFP L3/HFP AJB
1550 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-04-04 17:48 | 2014-04-04 22:55 | 91 | 307 | H4574831A | 27937 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHECKED LINE BACK UP TO REC. ON POLE 204-264, WE HAVE ONE REC. LOCKED OUT BELIEVE ITS B PHASE//COD 276// PRIMARY IS OFF INSULATOR, UP IN TREES WILL OPEN GOAB ON POLE 178-297 WILL GO BACK TO REC POLE179-194 ONE REC IS OPEN AND WILL CLOSE CLOSE IT THEN GO TO REC. POLE 204-264 AND ENERGIZE DOWN TO GOAB OPEN POINT. OPENED GOAB AT 17:48.///CLOSED REC ON POLE 37830204000264 // THIS IS FOR THE A PHASE OUTAGE ON SW 178-297 VER/HFP L3/HFP
1551 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2022-07-26 18:11 | 2022-07-27 13:35 | 24 | 1164 | 4589401 | 27936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | BAD STEPDOWN DIFFICULT LOCATION WILL GET STEPDOWN FROM HAZARD IN THE MORNING TO REPLACE
1552 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-09-04 20:35 | 2011-09-05 01:00 | 195 | 265 | 4811751 | 27925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PHASE LAYING ON CROSSARM//POLE ON FIRE//CREW ENROUTE//ONLY B & C PHASE OPEN//COD 195//OPENED PHASE "A" @ 2115 (COD +361)//TOTAL COD 556//ARM BURNT OFF NO TRUCKSARM BURNT OFF NO TRUCKS RELEASED BY CREW 078S08 //VER/GAH IDC XXXX
1553 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-12-31 10:35 | 2009-12-31 12:15 | 389 | 100 | 52522-1 | 27900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER OUT//COD 239//FOUND BAD CUTOUT ON 1130-278,OPENED SWITCH ON 1130-40 TO ISOLATE FAULT,WILL REPLACE CUTOUT///MADE REPAIRS AND RESTORED AT 1130-40 IDC CALLS CAME IN EQUALLY ON PH B AND C. ESTIMATED COUNT XXXX
1554 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-05-02 14:12 | 2020-05-02 17:18 | 152 | 186 | 4787901 | 27864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | recloser on 514-19 is open//CLOSED RECLOSER UP TO RECLOSER 37830538000010//recloser on 514-19 is open, closed recl 514-19 @ 17:10..then closed single phase recl on pole 538-10 @17:18..all power restored p.hicks Released by crew 077H09
1555 | South Williamson | 3411401 | DEWEY | INEZ | 2009-02-18 01:44 | 2009-02-18 06:17 | 102 | 273 | 63512-1 | 27846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTING ARRESTER BAD ON POLE 768-D-109 A CC 102 PHASE ONLY OUT UNTIL AT 0600 ALL RECLS OPENED RECLS AT POLE 768-C-184 THEN CLOSED AT 0617. MADE DUPLICATE TICKET TO SHOW ABOVE RECLS OPEN. VER/PDP IDC XXXX
1556 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-07-30 08:36 | 2012-07-30 10:50 | 207 | 134 | 4863881 | 27738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX PRIMARY BURNT DOWN. OPENED SW ON 785-331 @ 9:18 TO ISOLATE. COMPLETED REPAIRS AND CLOSED 3 - 600 AMP SWITCHES ON 785-331 @ 10:50 RESTORING ALL OUTAGED CUSTOMERS. SH VER/ARN IDC XXXX
1557 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-08-10 16:17 | 2012-08-10 23:30 | 64 | 433 | 4925491 | 27712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON POLE 278-176 "C" PHASE ONLY COD-64 CUTOUT BROKEN 278-176 IDCC CNT170 XXXX
1558 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-12-05 08:22 | 2012-12-05 12:00 | 127 | 218 | 4443411 | 27686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 PHASE POLE TOP BURNT OFF ON POLE 166-159, (45/4 ) XFORMER INSTALLATION. AND TELPHONE. NEED LINE CREW AND TECH. TRUCKS TO POLE. MAY BE ABLE TO TRANSFER MATERAL.OPENED RECLOSERS ON POLE 166-123, PLACED GROUNDS AND TAGED TO DDC. ALSO REMOVED SOURCE SIDE LEADS. RELEASED BY CREW 078S01 ///VER/CRB L/3 CRB IDC XXXX
1559 | South Williamson | 3411401 | DEWEY | INEZ | 2019-08-28 02:24 | 2019-08-28 08:28 | 329 | 347 | 4954021 | 27663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on pole 696-a-164//fell down and burned hole in stepdown/pouring oil///will need 500 stepdown//line crew Released by crew 079S01///// Made changes per DOL
1560 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-03-04 11:23 | 2008-03-05 00:33 | 54 | 790 | 52622-1 | 27660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904//RECLOSER OPENED DUE TO POLE FIRE.. SEE ORDER 52599-1//SERVICER ISOLATED AND RESTORED POWER UP TO FAULT POLE//COD 54// RELEASED BY CREW 078H02 VER/HFP IDC XXXX
1561 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-11-17 09:18 | 2014-11-17 14:57 | 84 | 339 | 4734381 | 27656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GROUND AT 44-4513 TO DDC.REC POLE 44C24513 OPEN, POLE 44C24519 BURNTOFF. // RECLOSER CLOSED AT 14:47 TRANSFORMER ON POLE 44-4519 BACK ON AT 14:57 DID NOT DO AS BUILT WORK ORDER WRITTEN BY BRENT PARSONS RELEASED BY CREW 078Q09// COD 82+2 VER/HFP L3/HFP AJB
1562 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-08-21 15:40 | 2018-08-21 21:30 | 79 | 350 | 4982111 | 27650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | no outage until switch opened @ 1540Pole 38830069D20067, one phase 4/0 wire came off arm and burnt in two. transmission overbuild Switches open on pole 38830069D47614. No grounds or tags. Need flaggers to set up and ground and tag. May get service bucket to pole. Wire down across from 3947 Boy Scout Road. Released by crew 078H04 L3/HFP
1563 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2008-03-30 09:32 | 2008-03-30 12:56 | 441 | 204 | 62097-1 | 27626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404301// COD-441 // SERVICER ENROUTE TO SIDNEY STATION// STATION FEEDER CLOSED AT 1034 // OPENED HOT TAP ON 963-1 // VER/LDA IDC RECLOSER ON POLE 964B-125 FAILED TO OPEN XXXX
1564 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-06-30 17:52 | 2009-06-30 19:52 | 230 | 120 | 55840-1 | 27600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP 3401703//CONTRACTOR FOUND BROKEN CROSSARM ON POLE 266-15//UNSURE OF WHAT BROKE IT AT THIS TIME//OPENED RECLOSER IN ORDER TO MAKE REPAIRS//COD 230 RESTORED @ 1952 L3/HFP IDCC TON2008 XXXX
1565 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-10-02 12:24 | 2022-10-02 20:22 | 94 | 478 | 4965921 | 27592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed on 853-77 and burnt pole off. Fault current burnt one phase down at 852-47. Crews enroute. Opened sw 853-70, made repairs at 852-47 and restored up to open sw @ 15:33. Made repairs and closed sw 853-70 at 20:22 restoring remaining customers. sh Released by crew 076S02
1566 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-05-14 13:14 | 2012-05-14 13:31 | 1622 | 17 | 4791911 | 27574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN LOWER ROCKHOUSE 34KV CB J VIA SUPERVISORY CTRL TO ALLOW DISC TO BE JUMPERED AT BAD 34KV REGULATOR DISC. OUTAGE APPROX 45 MINUTES// RESTORED AT 1331// CHECKED BY DKG HAD TO OPEN BRK TO JUMPER DEFECTIVE LINE REGULATORS DISCONNECTS IDC XXXX
1567 | Hazard | 3302703 | HAZARD | HAZARD | 2015-10-13 14:02 | 2015-10-13 18:22 | 106 | 260 | 4345671 | 27560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST REPORTS FIRE FLEW FROM TRANS//ONE PHASE OF HENDRIX BURNT DOWN AT POLE 37830296A30748, LOOPS OPEN AT 37830296A30741 AJBC CNT1224 LCD37830296A30772. SEE 4344691.
1568 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-09-26 19:01 | 2015-09-27 00:33 | 83 | 332 | 4276041 | 27556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1148-B3-709 HENDRIX BURNT INTO ON "C" PHASE COD-83POLE 1148-709 HENDRICK BURNT INTO TRUCK TO POLE LOOKS LIKE 4/0 PRI. CAN ON LINES ON 1148-326POLE 1148-709 HENDRICK BURNT INTO TRUCK TO POLE LOOKS LIKE 4/0 PRI. CAN ON LINES ON 1148-326 VER/KEP L3/DKG THIS OUTAGE FOR C PHASE ONLY AJB
1569 | Hazard | 3303901 | LESLIE | HYDEN | 2014-07-20 11:49 | 2014-07-20 15:55 | 112 | 246 | 4265801 | 27552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED BAD SPAN OF PRIMARY//COD 112// VER/DBM AJB CCO FEC57
1570 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2018-03-19 21:53 | 2018-03-20 01:46 | 118 | 233 | 4028541 | 27494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B Phase Only (118 customers)38830190009001 b phase rec open--38830215B00023 broke c/o--replaced--rec in at 01:46--allgood-ds032018
1571 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-03-18 13:59 | 2013-03-18 14:21 | 1249 | 22 | 4916091 | 27478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED 2 POLES OUT OF THE STATION ISOLATED CUTOUT FOR INACTIVE TRANS AND RESTORED BREAKER AT 1421 VER/KEP IDC XXXX
1572 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-01-13 16:28 | 2015-01-13 17:22 | 731 | 54 | 4933451 | 27468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR SHORTED OUT ON POLE 37830215D40523 AND BURNED CROSSARM INTO. POWER IS STILL ON. DAVE SAMMONS IS ON THE WAY WITH MATERIAL. WE WILL HAVE TO OPEN 3-PHASE RECLOSER AT POLE 37820193D00390B LONG ENOUGH TO OPEN SWITCHES ON POLE 37830215D40523 TO ISOLATE FAULT.//OPENED RECLOSER @1628 CLOSED IN 1636//THIS LEFT 470 COD //OPENED RECLOSER BACK UP AT 1719 AND CLOSED AT 1722 PICKING ALL CUSTS UP VER/CRB L3/HFP HFPC STP AJB
1573 | Hazard | 3302704 | HAZARD | KENMONT | 2017-05-18 15:45 | 2017-05-18 19:21 | 127 | 216 | 4813171 | 27432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING LINE, FOUND BAD INSULATOR ON POLE 37830320C00367 VER/CRB AJB
1574 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-03-04 20:17 | 2008-03-05 05:25 | 50 | 548 | 53250-1 | 27400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310501 RECL OUT ON POLE 1039-23 1 SPAN WIRE DOWN RELEASED BY CREW 077S09 CLOSED RECLOSER AT 1528 IDC VERIFIED THROUGH RECORDING XXXX
1575 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-01-04 08:51 | 2020-01-04 11:35 | 167 | 164 | 4210391 | 27388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | sectionalizer out on 9-D-232,due to failed cutout on33-C-8.replaced cutout,restored power at 11:35. Released by crew 079S03 L3/HFP
1576 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-06-13 14:21 | 2012-06-13 15:42 | 338 | 81 | 4912251 | 27378 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | PHASE 3 OUT AT 1421 DUE TO BUS REGULATOR DISC... MANUALLY OPENED CIRC BRK AT 1535. CLOSED AT 1542 IDC XXXX
1577 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-05-22 06:28 | 2014-05-22 10:39 | 268 | 251 | 4736731 | 27371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUNDBAD CSP ISOLATED , FOUND SECTIONALIZER OPEN ON 880-47, WILL CLOSE OCR , THEN CLOSE SECTIONALIZER, WILL CHANGE BAD CSP, TCM// CLOSED OCR IN AT 07:48, CLOSED SECTIONALIZER IN AT 09:08, CHANGING POT NOW TCM/ POT BACK ON AT 10:39 TCM//COD 268 IDCC CNT464, TON XXXX
1578 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2011-06-29 03:06 | 2011-06-29 14:30 | 40 | 684 | 4434651 | 27360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKEN AT POLE 149-137 ON "C" PHASE - "C" PHASE RECLOSER OPEN ON POLE 149-C4-248 - 40 CUSTOMER INTERRUPTED // RELEASED BY CREW 074S02 // NOTIFIED DUTY SUPV WHO REPORTED WILL MAKE REPAIRS AT REGULAR WORKTIME / C PHASE RECLOSER OPEN ON POLE 149-C4-248 - 40 CUSTOMER INTERRUPTED // RELEASED BY CREW 074S02 // NOTIFIED DUTY SUPV WHO REPORTED WILL MAKE REPAIRS AT REGULAR WORKTIME //WE HAVE HAD PROBLEMS GETTING ARMS OFF WE ARE TRANSFER. COND. NO//VER/CRB IDC XXXX
1579 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-07-26 00:42 | 2009-07-26 09:18 | 53 | 516 | 61601-1 | 27348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN POLE #102-80 #4 SOLID COPPER PRIMARY & NUT RELEASED BY CREW 077S10// BROKE IN THE CLEAR - LINE IS ENERGIZED UP TO POLE 102-80// IS SAFE// TRIED TO CALL FAA TO ADVISE WOULD BE OUT UNTIL MORNING NO ANSWER. OPENED RECLOSER 0909 CLOSED 0918 MADE H OUTAGE FOR RECLOSER VER/KEP L3/KEP IDC XXXX
1580 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-03-28 18:29 | 2012-03-28 19:25 | 488 | 56 | 4628321 | 27328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | ON SITE CROSS ARM BRACES BROKE WILL TRY TO FIX.////NUT CAME OFF BRACE BOLT AND LET ARM TILT INTO CUT OUT, REPLACE BOLT AND FIX BRACES.. VER/HFP L3/HFP IDCC TOF1805 XXXX
1581 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-07-23 01:55 | 2009-07-23 11:49 | 46 | 594 | 64048-1 | 27324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP MIDDLE PHASE LINE DOWN ON HILL - 3RD AND 4TH SPAN FROM RECLOSER BEHIND 289 FRASURE BR // COD-46 //OPENED OTHER 2 PHASES AT 0905 - 56 CUSTOMERS DUPLICATING FOR CUSTOMERS INTERRUPTED @ 0905 L3/HFP IDC LOOKS LIKE THESE CUSTOMER OUT SINCE FIRST OUTAGE CHANGED START TIME FROM 0354 ALSO APPEARS TO BE MAPPING ISSUES XXXX
1582 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-02-14 02:01 | 2008-02-14 09:35 | 68 | 454 | 63077-1 | 27194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401002//250 AMP STEPDOWN TRANS ON POLE 213-155 IS BAD. OIL IS ALL OVER TANK. I AM CALLING WILLIE { DUTY SUPERVISOR }. WILLIE WILL WOULD GET A CREW HEADED THIS WAY.//CHANGED STEPDN AND TRIED TO CLOSE, DID NOT HOLD, RECLOSER BELOW STEPDN OPENED//COLD LOAD PICKUP PRBLM//SECTIONALLIZED BY OPENING FUSE ON POLE 213-30 (NOT ON MAP, SENT TO MAPPING)///CLOSED RECLOSER @ 0755//37 CUST REMAIN OUT//OPEN 213-34 & CLOSE 213-30 @ 0918//3 CUST REMAIN OUT//CLOSE 213-34 @ 0935//ALL POWER RESTORED// VER/DBM IDCC CDC XXXX
1583 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-05-22 12:25 | 2016-05-22 16:04 | 124 | 219 | 4247591 | 27156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN AT POLE 64-40 A PHASE OPEN AT THAT POINT. EVERYTHING OK ON B AND C PHASE. REPAIRED LOOP ON POLE 64-40 AND CLOSED SWITCH IN ON POLE 64-232 AT 16:00 EVERYTHING SHOULD BE BACK ON OPENED 64-232 INSTEAD OF OPEN POINT. COD 124 OUT TOTAL. VER/AWD AJB
1584 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-09-27 10:44 | 2008-09-27 13:45 | 150 | 181 | 51342-1 | 27150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP STS WR #26493862 -- A PHASE RECLOSER PREDICTED OUT ON POLE 37830369D00283 - 150 CUSTOMERS /// @ 1318 CREW ON SITE SETTING UP TO MAKE REPAIRS TO LEAD BURNT OFF FROM RECLOSER MLR OK IDC XXXX
1585 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-04-17 11:29 | 2014-04-17 11:56 | 1005 | 27 | 4614511 | 27135 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | BAD REGULATOR ON "B" PHASE IN STATION OPENED CB TO ALLEVIATE HIGH VOLTAGE/TRANSFERRED LOAD VIA N.O. 1083-186 TO PANBOWL VER/KEP IDC XXXX
1586 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-07-15 15:18 | 2015-07-17 08:24 | 11 | 2466 | 4881641 | 27126 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PART POWER BAD UNDERGROUND NEEDS CREW ASAP OLDER CUST RELEASED BY CREW 078S08 RESTORED 7/16/15 11:59PM BLR
1587 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-05-01 05:28 | 2009-05-01 08:40 | 213 | 192 | 61563-1 | 27116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#29620552//3008701//BILL LYNCH AND BOBBY REYNOLDS WITH SERVICER RUNNING LINE OUT//WR#29620552//3008701// BAD 19.9 CUTOUT ON POLE 212-106, NEEDS LINE CREW.WR#29620552//3008701// BAD 19.9 CUTOUT ON POLE 212-106, NEEDS LINE CREW. RELEASED BY CREW 078S01---CREW ON SITE---CUST ON 08:40//VER/CRB IDC XXXX
1588 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-07-30 10:03 | 2010-07-30 10:31 | 966 | 28 | 59465-1 | 27048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401302// CREW TRANSFTERING CONDUCTOR TO A NEW POLE FOUND A BROKERN INSULATOR ON A CROSSARM AND HAD TO OPEN THE STATION BREAKER TO MAKE IT SAFE. POWER SHOULD BE RESTORED AROUND 1100HRS IDC XXXX
1589 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-05-04 12:31 | 2015-05-04 14:03 | 294 | 92 | 4388521 | 27048 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | ARRESTOR FAILED ON THE 69-34KV TR AT PRINCESS // STATION DEPT ON SITE REPLACING ARRESTOR // RESTORED @ 1403 VIA XFER BUS /// COD-294 // TIMES PER LOG & SCADA VER/HFP L3/HFP AJB
1590 | South Williamson | 3411401 | DEWEY | INEZ | 2018-05-19 16:59 | 2018-05-19 19:05 | 287 | 126 | 4378631 | 27046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CK SWITCHES ON POLE 38830743D00021//B PHASE CUTOUT ON SWITCH IS OPEN COD 181// CK SWITCHES ON POLE 38830743D00021//left hand switch broke on pole 743-21///will have to open other two phases to replace cutout//repairs made///restored at 19:05///opened other 2 switches at 18:25///complete//em
1591 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-03-28 10:31 | 2021-03-28 14:00 | 309 | 209 | 4390701 | 27045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A phase out stirrup burnt off @ pole 328-D-17.. open other phases on recloser to make repairs open @ 13:35 closed @ 14:00
1592 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-09-18 19:18 | 2009-09-18 21:14 | 233 | 116 | 53405-1 | 27028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN AT POLE 470-46 ...DEADEND INSULATOR ON B& C PHASES HAVE MELTED ON POLE 470-16, REPLACED INSULATORS RESTORED POWER AT 21:14 VER/KEP L3/KEP IDC XXXX
1593 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-03-14 17:24 | 2015-03-15 00:33 | 63 | 429 | 4194531 | 27027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE BROKE AT BASKET ON POLE355-40 NO, 4 CU AND SIX WHEELER TO POLE, WILL NEED TO OUTAGE WHOLE LINE AT SOLID BLADE,ON POLE 379-80 PATROLED TO RECLOSED PAST BREAK STILL CLOSED KWB SEE PO#`S 4194141 & 4192721 SUBTRACT THESE CUSTOMERS FROM THOSE OUTAGES/CREW ON SITE/FETR2345/VEM OPENED SWS ON PO#4195081 VER/KEP AJB TOF
1594 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-06-23 11:59 | 2011-06-23 13:09 | 386 | 70 | 4399361 | 27020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2206403 / OPEN CB TO CLEAR FAILED RECLOSER ON KY SIDE. *** UPDATE AT 1226 , CREW FOUND BAD INSULATOR AND WILL EXTEND OUTAGE BY 10 MIN. P.P. / CB CLOSED @ 1309 VER/JAK IDC XXXX
1595 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-12-24 17:04 | 2014-12-25 13:32 | 22 | 1228 | 4880051 | 27016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | PATROLLING LINEFUSE IS OPEN ON 547-27, FOUND LINE DOWN FROM 547-26 TO 32 LINE&MANUAL TREE CREW REQUIRED 6A&ALUM. LINECREW WILL HAVE TO DO OWN ISOLATING AND GROUNDINGFUSE IS OPEN ON 547-27, FOUND LINE DOWN FROM 547-26 TO 32 LINE&MANUAL TREE CREW REQUIRED 6A&ALUM. LINECREW WILL HAVE TO DO OWN ISOLATING AND GROUNDING RELEASED BY CREW 078S11 RELEASED BY CREW 078H16 BROKEN 35-5POLE #547-30 REPLACE WITH 40-4 NO TRUCK OFF ROAD RELEASED BY CREW 078Q04/ ISO 38830547000027/ COD 22/ VER/BOW AJB
1596 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2020-01-04 04:38 | 2020-01-04 13:10 | 92 | 512 | 4209891 | 26854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BURNT OFF POLE 39831147D10971windstream pole 1147-971 burnt off. back yard no trucks, yard dog? 45/4 w/ug servicerec open @ 1147-149, restored @ 06:25. loop cut at 1147-966. windstream pole 1147-971 burnt off. back yard no trucks, yard dog? 45/4 w/ug service Released by crew 078S07 Released by crew 078H07 L3/HFP
1597 | South Williamson | 3411401 | DEWEY | INEZ | 2019-08-23 04:25 | 2019-08-23 07:05 | 328 | 160 | 4934461 | 26839 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop open on middle phase at pole 767-1//will have to open switches on pole 767-185 to make repairs// Released by crew 079S01 dol 948899 L3/HFP
1598 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-01-09 07:03 | 2008-01-09 11:21 | 104 | 258 | 55056-1 | 26832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND 3 PHASE POLE BURNT OFF ,OPENING REMAINING RECLOSERS , FRAMING DOWN ON POLE//3409303 , MADE BACK HOT AT 11:14//3409303)//VER/CRB IDCC CNT313 CREATED ORDER TO OPEN OTHER PHASES XXXX
1599 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-10-28 03:58 | 2012-10-28 04:29 | 865 | 31 | 4177521 | 26815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SDB / 0358 / CB OPENED TO SAFELY MAKE EMERGENCY REPAIRS TO REPLACE INSULKATOR AT POLE 785-1379. 865 CC OUTAGED. --- SDB / 0429 / CB CLOSED, 922 CC RESTORED. ASSOCIATED W/ ORDER 4177031. VER/SDB IDC XXXX
1600 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-01-03 18:34 | 2011-01-03 22:51 | 120 | 257 | 58391-1 | 26808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PATROLLING LINE. #4 COPPER PRIMARY CONDUCTOR BROKE AT STIRRUP. CREW ENROUTE TO ASSIST WITH REPAIRS. REPAIRS COMPLETE. SH RELEASED BY CREW 076S02//COD 120// VER/DBM IDC XXXX
1601 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-10-28 01:04 | 2008-10-28 02:21 | 348 | 77 | 59758-1 | 26796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116703/// HOT TAP BURNT OFF SEND NOTE TO RAYBURN BASKET NEEDS REPLACED AT RECL POLE 1123-6526 VER/JHM IDC XXXX
1602 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2015-10-30 04:28 | 2015-10-30 09:47 | 84 | 319 | 4395831 | 26796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | KY DDC NOTIFIED APCO DDC// ROANOKE TO DISPATCH - //TOM MAY BE ASSOCIATED WITH APCO OUTAGE/ RISER HAS BURNED OUT OF B PHASE (18 CUST) HOT TAP. WILL NEED TO OPEN A AND C PHASE (81 CUST) TO MAKE REPAIRS.I OPENED ALL THREE PHASES ON POLE 38820917C00383 AT 09:17 (A&C 81 CUST) B WAS ALREADY OUT./ ALL CUST ON 0947/ 80T ON 917-9014 MD DONE/ ISO 38820917C09014/ COD 99/ VER/BOW //SEE ALSO H4395831 / PER B.O. ALL CALLS` A` PHASE ON 2 ON `B` - CHANGING INITAL OUTAGE TO`A` PHASE 84 CUST L3/HFP HFPC CNT18 AJB
1603 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-03-03 16:06 | 2014-03-03 19:55 | 117 | 229 | 4448091 | 26793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ISOLATED LINE TO SAFELY REPLACE POLE 1072-5565 (116 CC) /LOAD TRANSFER/DAVOX SENT/ALSO SEE PO#4447211 // CLOSED SW AT POLE 1072-5521 AT 1955 RESTORING ALL CUSTOMERS//IT FORCE CLOSED IDCC TOF1602, TOF0930 XXXX
1604 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-05-13 12:30 | 2010-05-13 16:35 | 149 | 245 | 61468-1 | 26785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830174000007, TRUCK OK, 45-4 RECLOSURE POLE, ISOLATED AT 38830198000018, NOT GROUNDED, B PHASE RECLOSURE ONLY, CLOSED AT 13:35, TRUCK OK, RECLOSURE POLE,, SEND TO V MULLINS RESTORED REMAINING CUST AT 1635 VER/KEP L3/KEP IDCC CNT161, PH C ONLY XXXX
1605 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-09-23 08:11 | 2022-09-23 12:35 | 292 | 264 | 4913051 | 26778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary down at 166-36,Will need Line crew to make repairs Manual Pole.Open Reclosers at 166-230 and Restored Recloser 167-A-428 at 09:20..Restored Recloser at 166-230 12:35.. Released by crew 074S01
1606 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2012-10-28 12:55 | 2012-10-28 14:10 | 357 | 75 | 4178181 | 26775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | <<PHASE B ONLY>> HENDRIX BURNT DOWN @ SPACER. MAP SHOWS WIRE SIZE AS 556. CREWS WORKING TO REPAIR. REPAIRS COMPLETE. CLOSED SW ON 978-155 @ 14:10 RESTORING OUTAGED CUSTOMERS. SH// VER/DBM IDC XXXX
1607 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-05-27 17:55 | 2017-05-28 12:38 | 99 | 1123 | 4870991 | 26772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED RECLOSER 39831147C35089 IN @ 2005//GOT BROKE CUTOUT ON POLE 38831065000112 TAKES BIG BUCKET 19.9 CUTOUT, TOOK CLAMP OFF AND GOT RECLOSER IN AT2005 AND GOT LINE FUSE ON POLE 38831065D40129 IN AT 2101 RELEASED BY CREW 077S05CLOSED RECLOSER 39831147C35089 IN @ 2005//GOT BROKE CUTOUT ON POLE 38831065000112 TAKES BIG BUCKET 19.9 CUTOUT, TOOK CLAMP OFF AND GOT RECLOSER IN AT2005 AND GOT LINE FUSE ON POLE 38831065D40129 IN AT 2101 GOT CUTOUT CHANGE AND POWER RESTORED ON POLE 1065-112 AJB
1608 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-12-16 00:37 | 2008-12-17 04:30 | 16 | 1673 | 59341-1 | 26768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802// FULL POWER WHEN I ARRIVED. OPENED LINE FUSE ON POLE 738-77 AT 00:37 TO ISOLATE. CREW ENROUTE TO REPAIR BURNT POLE. CREW ON SITE. REPAIRS COMPLETE. CLOSED LINE FUSE AT 4:30. SH //VER/GAH L3/KEP IDC XXXX
1609 | Whitesburg | 3309302 | VICCO | JEFF | 2022-05-06 13:00 | 2022-05-06 16:43 | 120 | 223 | 4845321 | 26760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Recloser opened on pole 372-194. Tie wire lose at pole 373-120. Need big bucket. Recloser closed in at 16:43 power restored.
1610 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-06-20 12:44 | 2015-06-21 01:07 | 38 | 743 | 4616871 | 26754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE/23 ONLY/B PHASE IS ALL THAT IS OUT RELEASED BY CREW 077S01B PHASE IS ALL THAT IS OUT BAD R/W RELEASED BY CREW 077S01 BAD CUTOUT ON POLE 56-44 ALL POWER RESTORED AT 1:07 RELEASED BY CREW 077H20//COD ??? AJB
1611 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-02-07 05:53 | 2021-02-07 09:04 | 140 | 191 | 4942921 | 26740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser is open (PATROLLING).at pole 310-151 wire has slipped through deadend shoe bellying down into Neutral going to isolate and ground and resagg Primary.Restored at 09:04...
1612 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2022-07-21 14:26 | 2022-07-22 10:41 | 22 | 1215 | 4543631 | 26730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 2 fuses out on 3 phase line up hollow, fuses are on pole# 329-215 at mouth of hollow, truck accesible Released by crew 077F01 2 fuses open on 3 phase line in hollow, fuses on pole 329-215 at mouth of hollow, truck accesssible Released by crew 077F01
1613 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-11-15 18:21 | 2018-11-15 20:43 | 188 | 142 | 4428881 | 26696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | LOAD SIDE FUSE BLOWN ON STEPDOWN AND RECLOSER AT 37830096C30395A. Recloser battery dead calling for meter elec/ Replaced recloser batteries. Recloser is good now. L3/HFP
1614 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-09-18 13:34 | 2014-09-18 16:55 | 156 | 201 | 4509201 | 26670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SINGLE PHASE RECLOSER ON 167-598 IS OPEN.SINGLE-PHASE RECLOSER IS OPEN ON POLE 167-598. I AM PATROLLING LINE NOW.SINGLE-PHASE RECLOSER IS OPEN ON POLE 167-598. I AM PATROLLING LINE NOW. WE OPENED LINE FUSE AT 191-18 SERVING SARAH BRANHAM HOLLER AND CLOSED RECLOSER IN AT 16:22 AND IT STAYED. VER/CRB L3/HFP AJB
1615 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-11-22 23:37 | 2020-11-23 12:19 | 35 | 762 | 4716481 | 26670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole151-82 has burnt off 3 phase pole/// Opened line fuses on pole 151-45 @ 00:28 to make safe//This is no truck//Will have to change pole 45-4/// Rick Ray is getting digs done and material list//hold till daylight this is difficult location// will need yard dog and ROW crew///Tagged line fuses 151-45 to DDC/dig# 2011230005/ LR- The first customer All Out call came on 11/22/20 @ 23:37
1616 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2015-07-08 00:40 | 2015-07-08 03:49 | 141 | 189 | 4742071 | 26649 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTER AT POLE 234-184 AND CLOSED AT POLE 235-175 @0 349, ALL WORK COMPLETE / GXJ VER/SEF AJB
1617 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-10-30 11:45 | 2010-10-30 13:27 | 261 | 102 | 50222-1 | 26622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37556848// REC. OPEN ON POLE 221-258//// MIDDLE PHASE LOAD SIDE LEAD FELL OFF LINE, CONTACTING GROUND ON ARRESTOR OPENING REC. POWER RESTORED. LOOSE CLAMP. VER/HFP L3/HFP IDC XXXX
1618 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-05-01 14:43 | 2020-05-01 15:38 | 484 | 55 | 4784631 | 26620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | will have to open recloser to change xarm. crew required to change arm Released by crew 077S12//RECLOSER 37830426C00563 OPENED @ 1443 COD 484//NO OUTAGE TILL THENwill have to open recloser to change xarm. crew required to change arm Released by crew 077S12 OPEN RECLOSER ON PL 426-563 AT 14:43 CLOSED AT 15:38 Released by crew 075H03
1619 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-09-15 09:12 | 2010-09-15 16:28 | 61 | 436 | 66606-1 | 26596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILLOPEN LINE FUSES ON POLE 47-420 TEMP TO OPEN CUT OUT WHERE THE POLE IS ON FIRE.. OPEN AT 09:12 RELEASED BY CREW 074S05 REPLACING 50 CLASS 2 ON SIDE OF HILL//COD 61// VER/DBM IDCC PN435 XXXX
1620 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-09-24 11:23 | 2010-09-24 14:30 | 166 | 187 | 53105-1 | 26577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN TWO LOCATION POLE 1150-39 AND 1150-119 OPEN LINE AND GROUNDED ON POLE . MADE LINE HOT UP TO POLE 1150-14 AT 12:55 VER/KEP L3/KEP IDC XXXX
1621 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-01-03 01:21 | 2020-01-03 06:36 | 270 | 315 | 4206181 | 26460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | recloser on pole 202-208 is out, C phase//cod 53//2 cutouts are bad on pole 37830227A00251, need to replace them all, calling for help// opened other 2 reclosers at 0545 hrs to make repairs, closed all 3 in at 06:30 // cod 53 (+217)
1622 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-07-19 17:59 | 2008-07-20 01:35 | 58 | 456 | 54223-1 | 26448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008702// A PHASE RECLOSER ONLY THING OUT// 58 COD//STEP DOWN XFR BURNED UP WILL NEED MORE MEN TO CHANGE// CALLED IN DHE CREW TO ASSIST/OPENED OTHER 2 PHASES AT_____ COD-109 THEN OPENED LATERAL FUSE`S AT POLE 91(ORDER 54275)STEP DOWN XFR BURNED UP WILL NEED MORE MEN TO CHANGE/CALLED D/E CREW TO HELP WITH DROPING LOAD AND CHANGING 500 STEP DOWN ON PLATFORM HAD TO OPEN B & C PHASE TO MAKE SAFESTEP DOWN XFR BURNED UP WILL NEED MORE MEN TO CHANGECLOSED FUSE AT 0135. VER/KEP MLRC MCC DIS
1623 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-02-07 07:15 | 2020-02-07 07:53 | 696 | 38 | 4375011 | 26448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Had a cutout on pole 214-B-151 broke,While trying to make it safe to repair it operated recloser on pole 190-D-313,I made my repairs and restored service at the recloser at a time of 07:53..
1624 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2022-02-11 15:52 | 2022-02-11 21:50 | 87 | 358 | 4473431 | 26416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C phase recl 104-2 open (87 COD) due to broken crossarmsC phase recloser open on 104-2 due to duoble arm broke @ 104-92//This is a 3 phase tap that feeds a junk yard///I can isolate to clear up fault///will need double arms and cutout for xfm///can use truckCREW REQUIRED///C phase recloser open on 104-2 due to double arm broke @ 104-92//This is a 3 phase tap that feeds a junk yard///I can isolate to clear up fault///will need double arms and cutout for xfm///can use truck//Closed c phase reclos
1625 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-08-27 00:49 | 2008-08-27 04:20 | 125 | 211 | 55509-1 | 26375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3402802//TREE GROWN OVER PRIMARY SAGGED DOWN IN RAIN AND BURNT IN 3 PHASE. WE CUT LIMBS TO GET ABOUT 6 INCHES CLEARANCE OVER PRIMARY. WILL TRY RECLOSER. RELEASED BY CREW 076S02 BAD CSP ON POLE 738-237 ISOLATED ON POLE 738-236 NO CUSTERMER OUT FEEDS TWO DD LIGHTS.WILL FIX LATER//VER/CRB IDC XXXX
1626 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-03-16 07:15 | 2017-03-16 08:40 | 310 | 85 | H4561131 | 26350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE BURNT DOWN @ RECL - 206 CUST // OPENED A & B @ 0715 (310 CUST) TO MAKE SAFE. MADE REPAIRS AND CLOSED ALL 3 REC. BACK IN @0840. DUPLICATE IN HOIS // SCADA INDICATES INITAL C PHASE OUTAGE = VER/HFP L3/HFP AJB
1627 | Hazard | 3303901 | LESLIE | HYDEN | 2021-10-06 11:18 | 2021-10-06 22:00 | 41 | 642 | 4323091 | 26322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad Step down. Willard Jones enroute with material to make repairs. Released by crew 077S06
1628 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2008-02-13 06:01 | 2008-02-13 09:09 | 140 | 188 | 62075-1 | 26320 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | 2150105//CC=1568///0639 PATROLLING LINE///BAD INSULATOR ON STEEL INSIDE STATION 290 KY CUSTOMERS VER-MF IDCC 140 CUSTOMER XXXX
1629 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-11-18 23:40 | 2017-11-19 11:40 | 134 | 720 | 4577731 | 26280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Check tags38821108000022-(3PH OCR POLE)- STIRRUP BURNT OFF ON LOAD SIDE ON C PHASE. OCR IS IN. BJ Released by crew 074E04/open recloser 1108-22/1108-21 open transfer due to secondary running towards recl/ C phase 34 cust out originally/ xfmr 38821108000021 (no add customers) opened 1123 closed 1141/ recl 38821108000022 A&B phase(100 cust) opened 1122 closed 1140
1630 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-01-11 10:50 | 2013-01-11 12:30 | 655 | 100 | 4595711 | 26260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WAS PATROLLED LINE FOUND CROSSARM SMOKING, HAD TO OPEN UP RECLOSERS ON POLE 1098-24, OPENED UP AT 1050, CLEAR UP TRANSFORMER CUTOUT ON 1122-39, CLOSED IN RECLOSER AT 1130, RESTORED POWER TO ALL CUST, BUT ONE, CREW REQ, LOC BETWEEN LAKESIDE DR AND JUANITA RD, YELLOW DBLWIDE, NO TRUCKS TO POLE RELEASED BY CREW 078S06 ///VER/CRB L/3 CRB IDC XXXX
1631 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-10-22 11:33 | 2016-10-22 15:53 | 101 | 260 | 4044541 | 26260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 38830234000069 POLE TOP BURNT OFF .DBL DE W/RIDGE PIN--NEED 2 POLY INS, RIDGE PIN INS--CREW REQ--DS102216 RELEASED BY CREW 078S01/CREW ON SITE/FETR1630/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1553/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830234D20140/ COD 101/ VER/BOW L3/HFP XXXHFP AJB
1632 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2009-12-08 20:52 | 2009-12-08 23:35 | 235 | 163 | 58458-1 | 26241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER ENROUTE R. MARCUM ON WAY TO CHANGE CUTOUT. CLOSED STA BKR AT 22:44 RELEASED BY CREW 079S01. ON SITE TO CHANGE CUTOUT.POWER BACK ON AT 23:35 IDC XXXX
1633 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-02-26 12:43 | 2013-02-26 14:30 | 245 | 107 | 4850051 | 26215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | MIDDLE PHASE OFF OF INSULATOR AT POLE 37830177D00008, POWER RESTORED AT 14:30//COD 245//EMAILED TO GLENN COMBS// VER/DBM IDC XXXX
1634 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-07-10 11:46 | 2010-07-10 14:27 | 165 | 161 | 64679-1 | 26202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT INTO , OPENING LINE NOW...OPEN HIGH SIDE OF STEPDOWNS 0N 362-5 @11:46 HRS//ISO 37830362000005//COD 165 //...REMOVED CLAMP ON 362-38 AND MADE STEPDOWNS HOT @ 12:26 HRS..OPEN STEPDOWNS BACK UP @ 14:22 TO REPLACE CLAMP & RE-ENERGIZED THEM @ 14:27HRS RESTORING ALL POWER. P.HICKS IDCC PN40, TOF0801, CNT168 XXXX
1635 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-09-30 15:15 | 2015-09-30 15:35 | 1309 | 20 | 4296111 | 26180 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | OPENED @ 1515 CLOSED @ 1535 RESTORING CKT NORMAL RELATED TO ORDER 4283441 (ORIGINAL OUTAGE) --- VERIFIED TIMES PER DISPATCH LOG (DOL) VER/HFP L3/HFP AJB
1636 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-05-01 08:52 | 2020-05-01 13:21 | 136 | 269 | 4784081 | 26168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WIRE BROKEN IN CLEAR AT POLE 37830424000084 ¦¦ OPENING RECL @ 37830424A30333A (50 CUST) @ 0924 ¦¦OPENED SWITCH 37830424A32257 @ 0940//CLOSED RECLOSER @ 1018// Released by crew 077H08.. made repairs restored power at 13:21 Released by crew 077S11
1637 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-10-29 14:27 | 2012-10-29 16:41 | 246 | 134 | 4183491 | 26160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE ONLY OUT 246 CUSTOMERS (RESTORED 84 @ 1520 - 162 OUT) VER/HFP L3/HFP IDC XXXX
1638 | Hazard | 3310502 | HADDIX | CANOE | 2022-11-28 17:01 | 2022-11-28 19:13 | 198 | 132 | 4198951 | 26136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER // crew found broke set of crossarms at pole 37830169C00276 // crew opened RECL 37830145000094 in order to make repairs // cod 198 //
1639 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-01-09 01:51 | 2008-01-09 04:05 | 195 | 134 | 54905-1 | 26130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER RECLOSER OUT..876-368..PATROL LINE CC/218..876-43...LIGHTNING ARRESTOR AND CUTOUT BAD... COD-195 VER/KEP IDCC CDC83 XXXX
1640 | South Williamson | 3200301 | BELFRY | BELFRY | 2018-06-27 08:32 | 2018-06-27 18:10 | 47 | 565 | 4676611 | 26085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 837930/// Replacing pole 1014-C2-60
1641 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-05-06 12:53 | 2022-05-06 16:05 | 342 | 192 | 4845221 | 26085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recl 37830067A00261 was never open--A phase cutout failed at 37830067A30062//OPENED SOLID BLADE ON POLE 37830067A00010 @ //105 COD FROM BEGINNING OF OUTAGERecl 37830067A00261 was never open--A phase cutout failed at 37830067A30062 opened a pole 67-A-10 at 15:40 and restored at pole 67-A-10 16:05
1642 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-10-17 14:07 | 2011-10-17 18:20 | 103 | 253 | 4991461 | 26059 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | SINGLE PHASE RECLOSER AT POLE 167-598 IS OPENED. I AM PATROLLING LINE NOW. GUY WIRE BROKE AT POLE 191-25 AND LANDED ON PRI. CONDUCTOR, BURNING IT DOWN. I HAVE CALLED FOR HELP. WE PUT WIRE UP AND CLOSED RECLOSER IN AT 18:20. SEND TO ENG. DEPT. AND TREE CREW {CORY FARMER }.WE NEED TO CHANGE BAD POLE 191-25 AND BURY NEW ANCHOR. LINE CROSSES 4-LANE. ALSO R/W IS 8 ABOVE PRI. COND. IN PLACES ON THIS LINE. NEEDS CUT BADLY. VER/KEP IDC XXXX
1643 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-07-16 19:27 | 2011-07-16 23:45 | 101 | 258 | 4554441 | 26058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE REC. OPEN ON 38831125B00772// PATROLING// WIRE DOWN ON 1124-11 AT 2205- SERVICER OPENED A-C RECL TO MAKE REPAIRS. CLOSED AT.//23:45// REPAIRS MADE// POWER RESTORE DUP FOR HOIS. VER/PDP IDC APPEARS FROM TICKETS THAT PHASE B WAS OUT AND THERE COULD BE A PHASING ISSUE CHANGED COUNT FROM 90 XXXX
1644 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2019-01-13 00:56 | 2019-01-13 06:14 | 101 | 318 | 4662701 | 25986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 888729 // Feeder L/O at 0056 per SCADA//cod 101//,..pole 21-84 hot tap burnt off & hendrix on top cut out Released by crew 078S07 Released by crew 078H07//cod 101 ¦¦¦¦¦ VERIFIED TIMES PER SCADA & DOL= L3/HFP
1645 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-01-29 23:49 | 2008-01-30 07:50 | 54 | 481 | 60947-1 | 25974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402204// HOT TAP BURNED OPEN ON STEP-DOWN BANK, NEED HOTTAP, STIRRUP, AND 2-3 MEN, NO TRUCK ACCESS, WILL NEED TO ISOLATE BANK / GXJ RELEASED BY CREW 074S03 ///ONLY ONE PHASE WAS OUT, HAD TO OPEN THE OTHER TWO PHASES AT 0640 ON 1-30-08// CLOSED @ 0750// A/C PHASE CUSTOMER OUTAGED ON H60947-1// VER/TOM IDC APPEARS PH A WAS OUT ORIGINALLY ACCORDING TO CALLS CHANGED COUNT FROM 24 XXXX
1646 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-02-02 19:22 | 2014-02-02 21:20 | 411 | 118 | 4337871 | 25948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMERS SEEING FLICKERING DUE TO TROUBLE ON ORDER 4337901 PER GEORGE WHITAKER, ARCING IS NEAR POLE 446-49////. RECLOSER OPEN ON POLE 446-300, BAD CUTOUT ON POLE 446-50, ISOLATED CUTOUT CLOSED RECLOSER AT 20:25 VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 1757 ESTIMATED TIME OFF XXXX
1647 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-08-17 14:05 | 2016-08-17 17:05 | 144 | 180 | 4802311 | 25920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S01FOUND CLAMP BURNED OUT OFF STIRRUP ON POLE 362:38 WILL OPEN RECL. 0N POLE 368 TO MAKE REPAIRS OPENED AT 16:41 CLOSED BACK AT 17:05 ALL POWER RESTORED VER/AWD /// SEE H4802311 FOR RECL OUTAGE TO MAKE REPAIRS L3/HFP HFPC DUP CDC86 CNT 147 AJB
1648 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-05-18 03:08 | 2010-05-18 09:08 | 72 | 360 | 64386-1 | 25920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 35165100 // LOOKS LIKE C PHASE OUT//--L MCARTY ASSISTING--NEED CREW--BAD ARRESTOR ON CSP TRANSFORMER NEEDS REPLACED--RECLOSER ON POLE 38830140A00154 ONLY OPERATING TWICE BEFORE LOCKOUT--E MAIL TO G BELL AND L RAYBURN COD-72 VER/HFP L3/HFP IDC XXXX
1649 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-09-16 09:40 | 2009-09-16 11:40 | 216 | 120 | 60966-1 | 25920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3310501// RIGHT HAND PHASE AT SWITCH POLE 1084-25 HAS HOT LINE CLAMP FAILED AND HANGING LOOSE ON THE LOAD SIDE//COD 209// SERVICER MAKING REPAIRS// VER/TOM L3/TOM IDCC FP NULL XXXX
1650 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-09-14 22:15 | 2008-09-15 13:40 | 28 | 925 | 63852-1 | 25900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30003703//FOUND DEAD TREE ON PRIMARY AND NEUTRAL AT POLE 331-75 I REMOVED TREE,,, CUTOUT BROKE ON POLE 308-27 ALSO I WILL REPLACE,,,BACK ON//COD 28// VER/DBM MLR OK
1651 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-10-03 02:36 | 2014-10-03 07:27 | 89 | 291 | 4546231 | 25899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP OPENED ON POLE 478-95. CAN GET TRUCK TO POLE BEFORE IT RAINS. HAY FIELD JUST CUT.NEED LINE CREW. RELEASED BY CREW 078S01 "B" PHASE ONLY COD-89LOOP OPENED ON POLE 478-95. CAN GET TRUCK TO POLE BEFORE IT RAINS. HAY FIELD JUST CUT.NEED LINE CREW. RELEASED BY CREW 078S01 B PHASE ONLY COD-89,,OPENED REC 478-90 AT 07:22, CLOSED AT 07:27, ALL POWER RESTORED RELEASED BY CREW 078H03//RECLOSER ON TIX 4546411 VER/CRB AJB LCD 38830478C17192
1652 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-07-16 23:58 | 2008-07-17 04:00 | 107 | 242 | 53473-1 | 25894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3308002 STS GOT SPAN OF WIRE BURNED DOWN ON RECLOSER POLE 1083-888, GOT GREG FUGATE COMMING TO HELP POWER RESTORED AT 0400HRS DKG/FIX IN HOIS/CANNOT CLOSE ORDER IDCC CNT60 XXXX
1653 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-06-14 15:36 | 2019-06-14 19:23 | 300 | 227 | 4507701 | 25870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A phase rec. open on pole 48-800////will patrol..cross arm insulator broke and has phase floating on pole 37820025A00046 .will need big bucket and flagging crew with new pin insulator to make repairs..//95 COD FROM BEGINNING OF OUTAGE//OPENED B & C PHASES @ 1902/ RESTORED @ 1923 L3/HFP
1654 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-02-26 00:21 | 2009-02-26 07:25 | 61 | 424 | 51569-1 | 25864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE TOP BURN OFF AT 38830254B00238, PRIMARY AND NEUTRAL DOWN AT 38830254B00236, CREW HAS BEEN NOTIFIED/CREW ON SITE/FETR 0730/VEM, ALL REPAIRS MADE, ALL CUSTOMERS RESTORED//COD 61// VER/DBM IDC XXXX
1655 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-07-23 12:56 | 2010-07-23 16:09 | 134 | 193 | 55969-1 | 25862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE SIDE RECLOSURE LEED HAS BURNT AT THE HOT TAP C PHASE RECLOSURE IS THE ONLY ONE OUT AT THIS TIME // CREW ON THERE WAY "C" COD-37 // REPAIRS COMPLETE POWER RESTORED AT 1609.//VER/CRB IDC DCMT PH A NOT C CHANGED COUNT FROM 39 XXXX
1656 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-10-16 13:59 | 2019-10-16 20:30 | 89 | 391 | 4148951 | 25859 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got pole 1064-40 burned off going to open solid blade on pole 1064-33 to get line in up to this pole, call hazard with material list , closed recloser in at 1532 //repairs made and power restored at 2030 closed in on pole 1064 -33 //cod 89
1657 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-08-12 20:21 | 2010-08-13 10:15 | 31 | 834 | 54142-1 | 25854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 36423259 // HOLDING UNTIL 12:00 ON 8/13 . OPENED SWS AT POLE 151-258 TO REPLACE BROKEN INS AT POLE 127-129 RELEASED BY CREW 077H02 VER/HFP L3/HFP IDCC PN46, FPNULL MAYBE NEED 2 OUTAGES
1658 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-02-19 18:30 | 2013-02-19 22:00 | 123 | 210 | 4832451 | 25830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX PRIMARY BURNT IN TWO ON 978-170. <<PHASE C ONLY>>.//COD 113 // ISO 38830978A30170 // REPAIRS COMPLETE. PREPARING TO CLOSE GOAB 954-100 (SEE 4832671). CLOSED @ 22:00. RELEASED BY CREW 076S02// VER/DBM IDC XXXX
1659 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2009-03-13 15:01 | 2009-03-13 15:36 | 738 | 35 | 58207-1 | 25830 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ABOUT 45 CLASS 5 POLE THREE PHASE 19.9 4/0 PRIMAY AND 1/0 NEUTRAL. HAS 19.9 25 KVA TRANSFORMER ,,SINGLE 8 FOOT ARM ,,POLE # IS 477-262 DKG/CLOSED BRK AT 1531 // VER/TOM L3/TOM IDCC TOF1510 XXXX
1660 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-03-07 10:47 | 2008-03-07 16:25 | 97 | 338 | 54531-1 | 25757 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN PATROLING LINES/IIOSOLATING ON 174-67/CREW REQUIRED/COULD NOT IOSOLATE ON 67 WENT TO 174-102 FOR SAFETY/174-163 BACK ON AT 1252 HRS//...............POWER ON @ 16:25// VER/DBM IDC XXXX
1661 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-19 21:44 | 2022-01-19 22:48 | 402 | 64 | 4388181 | 25728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout at pole 190-C-171,Got my Trans Isolated and got Recloser back in at 190-D3-406 22:48,Going to go change cutout..
1662 | Hazard | 3311103 | STINNETT | WENDOVER | 2011-11-27 09:44 | 2011-11-27 10:47 | 408 | 63 | 4116911 | 25704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FEEDER BREAKER LOCKOUT @ 0944 PER SCADA //..PATROLING NOW..P.HICKS.POLE 411-241.REMOVED BAD ARRESTOR ON POLE 411-241..ALL POWER RESTORED @ 10:47 HRS.P.HICKS VER/PDP IDC XXXX
1663 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-01-06 13:37 | 2014-01-06 17:30 | 112 | 233 | 4238021 | 25700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 HENDRIX CONDUCTOR, (PHASE C), BURNT DOWN AT A SPACER. CREWS WORKING TO REPAIR. COMPLETED REPAIRS. CLOSED GOAB 954-100 (SEE ORDER 4238361) @ 16:46 ENERGIZING UP TO SW 978-152. (COLD LOAD PICKUP) CLOSED SW ON 978-152 @ 17:30 RESTORING REMAINING OUTAGED CUSTOMERS. SH RELEASED BY CREW 076S02//COD 112//ISO// VER/DBM IDCC CCWU XXXX
1664 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-05-13 13:35 | 2011-05-13 16:15 | 264 | 160 | 4083961 | 25668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LEFT HAND RECLOSER OPEN ON POLE 746-243//CUT OUT BROKE ON POLE 673-41// HAVE HOTLINE CLAMP LIFTED ON POLE697-31 TO ISOLATE TROUBLE//CLOSED RECLOSER AT 1447//REPAIRS MADE//CUSTOMERS RESTORED AT 16:15//COMPLETE//EM RELEASED BY CREW 079S01//COD 264// VER/DBM
1665 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-01-20 02:20 | 2022-01-20 04:41 | 182 | 141 | 4388871 | 25662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 69-277, will be making repairs Closed Via SCADA @ 0441
1666 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2015-03-02 15:38 | 2015-03-02 16:45 | 383 | 67 | 4092261 | 25661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SERVICER FOUND BAD CROSS ARM ON POLE 418-123, CREW ENROUTE/NO OUTAGE AT THIS TIME/OPENING RECLOSER 418-6 TO SAFELY MAKE REPAIRS/COD 383/SERVICER FOUND BAD CROSS ARM ON POLE 418-123, CREW ENROUTE/NO OUTAGE AT THIS TIME/ TOOK POWER OFF 15:38 TO 16:45 TO REPAIR CROSS ARMS AND TO CHANGE CUTOUT === POWER BACK AT 16:45// VER/ ADH // SCADA AGREES WITH TIMES = L3/HFP XXX AJB
1667 | Pikeville | 3407101 | TOPMOST | DEMA | 2019-02-20 11:25 | 2019-02-20 12:14 | 523 | 49 | 4815091 | 25627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 899135/EMERGENCY OUTAGE TO REPAIR CONDUCTOR OFF INSULATOR L3/HFP
1668 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-02-20 02:30 | 2015-02-20 19:35 | 25 | 1025 | 4046181 | 25625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 //// TRANSFORMER WAS BOILING AND SMOKING ABOUT READY TO BLOW LID OFF//// OPENED CUTOUT @ 2:30 TO MAKE SAFE/// CAN USE TRUCK ,BUT STREET IS NARROW AND SNOW COVERED RELEASED BY CREW 074H17 RELEASED BY CREW 074H10 VER/HFP L3/HFP AJB
1669 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-05-13 10:10 | 2017-05-13 12:35 | 176 | 145 | 4794581 | 25520 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | SEE DOL CASE 741489///BELFRY - BELFRY ISOALTION FOR BUS DISCS REPLACEMENT///ORIGINAL OUTAGE RECORD FOR OPENING BELFRY - BELFRY 12KV CB A FOR ISOLATION--FOR RECL AT 989-D-18 THAT WAS ISOLATED/// VER/DKM L3/HFP HFPC MCCDL CDC82 FP AJB
1670 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-06-19 18:02 | 2014-06-19 19:23 | 315 | 81 | 4114811 | 25515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RELATED TO ORDER 4113291 -- EMERGENCY OUTAGE TO REPAIR BROKEN CROSSARM // PARTIAL LOAD TRANSFER TO REDUCE NUMBER OF CUST INTERRUPTED // AJBC TOF18:15
1671 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-05-17 08:49 | 2014-05-17 14:20 | 77 | 331 | 4718281 | 25487 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE DISC ON POLE 68-A-58 DUE TO POLE TOP BURNT OFF ON POLE 68-A-240 ON ORDER 4718121 //COD 77// VER/DBM L3/HFP IDC XXXX
1672 | Hazard | 3310502 | HADDIX | CANOE | 2016-12-16 02:31 | 2016-12-16 05:37 | 137 | 186 | 4199361 | 25482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD CUTOUT ON POLE 37830169C00185 BROKE AND SOLID BLADE IS CUTOUT WITH 100 T FOR SOLID BLADE RELEASED BY CREW 077S05/ A PHASE OUT CC 137/ B&C CC 83 OPEN AT 0534 CLOSED 0537 ALL CUST RESTORED 0537 VER/KEP AJB
1673 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2016-04-23 15:53 | 2016-04-23 17:40 | 238 | 107 | 4119731 | 25466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL SWITCHES OPENED ON POLE 37830425C40463 @ 1553// X-FMR CUT-OUT IS GOING BAD ON POLE 401D-27. HAS BURNT CROSSARM IN TO. NO POWER IS OFF AT THIS TIME. WILL NEED ONE MAN AND A BIG BUCKET AND A FLAGGING CREW. WILL HAVE TO BLOCK ROAD TO MAKE REPAIRS. WILL NEED 8FT CROSSARM. OPENED SWITCHES ON POLE 425-463 AT 15:53//CLOSED 1740 VER/CRB AJB
1674 | Hazard | 3303901 | LESLIE | HYDEN | 2015-09-05 18:07 | 2015-09-06 04:27 | 41 | 620 | 4207911 | 25420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD HIGH SIDE CUTOUT ON STEPDOWN 37830412C00176.. CREW REQUIRED. RELEASED BY CREW 077S04REPAIRS MADE AND POWER RESTORED AT 0427 VER/TOM L3/TOM AJB
1675 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-02-19 23:39 | 2015-02-20 09:30 | 43 | 591 | 4045971 | 25413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY DOWN @ POLE 352-16 TO 352-17 NEED LINE CREW TO REPAIR NO TRUCK #4 COPPER,RECLOSER ISO & TAG TO DDC @ POLE 351-76 RELEASED BY CREW 078S05 REPAIRED PHASE AT PN 352-17 AND RESTORED POWER AT PN 351-76 AT 9:30 PLEASE CLOSE TICKET THANKS DWW/ FAILED SLEEVE/ ISO 38830351000076/ COD 43/ VER/BOW L3/DKGXXXX AJB
1676 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-05-02 16:50 | 2022-05-03 01:07 | 747 | 455 | 4825191 | 25383 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ORDER // DOL 1202552 // contractor found broke 3 phase pole // requires outage to safely change pole // will transfer as many customers as possible and issue hold order //
1677 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-05-29 15:01 | 2019-05-29 19:05 | 104 | 244 | 4364901 | 25376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 074S02. Closed in at 19:05. L3/HFP
1678 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-11-29 13:06 | 2022-11-30 14:38 | 188 | 171 | 4201901 | 25344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Hold Order/ DOL 1255196/ A and C phase Load side of the Step down open @96-C3-395A, checking. (COD 148) Bad ground based Step Down @96-C3-395A.
1679 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-03-03 18:02 | 2016-03-04 02:00 | 53 | 478 | 4809451 | 25334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 COPPER PRIMARY WIRE PULLED OUT OF SLEEVE ON 912-9 STILL HOT TO 912-9 WIRE DOWN BETWEEN 912-9 AND 912-22 NEED LINE CREW AND FLAGGERS TRK APPROACH // PULLED RECL OFF AT 01:03 TIM MCCOY SEE 4813141 FOR RECL OUTAGE TO MAKE REPAIRS /// COD-53 ISO AJB
1680 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-02-17 20:04 | 2018-02-18 16:34 | 28 | 1230 | 4856761 | 25314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | close "A" phase (cod-28)recloser and it stayed for 5 seconds and open up. hold till daylight//call for tree crews will have walk line on hillside//wire down on pole37830318B00297 all manual,need 4man line crew and #2 alum. 19.9 kv cutout and arrester complete with bracket/ ISO 37830294000275/ 37830318B00134
1681 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-12-24 07:02 | 2008-12-24 08:18 | 333 | 76 | 63282-1 | 25308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 27798781 // POLE 116-17 CROSS ARM BAD INSULATOR VER/KEP L3/KEP IDC XXXX
1682 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-05-21 11:48 | 2016-05-21 12:52 | 412 | 64 | 4244011 | 25300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | FAILED NC GOAB 164-C-250/CREW TO REMOVE GOAB AND MAKE SOLID/HOLD ORDER REQ/NO CUST OUT AT THIS TIME/VEM//164-275 @ 1231 INTERRUPTS 322 CLOSED 165-A-267 @ 1239 CLOSED 164-275 @ 1239//// REFERENCE ORDER SWITCHING TO NORMAL ORDER 4245811 AJBC 1919
1683 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-12-24 07:45 | 2009-12-24 11:35 | 110 | 230 | 51115-1 | 25300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | 3001102//C PHASE OPEN BAD REGULATOR 90-262 MLR IDC XXXX
1684 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2010-05-31 01:29 | 2010-05-31 09:45 | 51 | 496 | 54029-1 | 25296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED UP BAD ARRESTER ON POLE 214-230..//VER/CRB IDC XXXX
1685 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-08-09 06:49 | 2009-08-09 08:45 | 218 | 116 | H65243-1 | 25288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401802//HENDRIX BURNT IN TWO ON POLE 654-600 CALLED MILLER DISPATCHING CREW/// C PHASE RECLOSURE OUT ON POLE 654-529 WILL NEED TO OPEN ALL THREE RECLOSURES WHEN CREW ARRIVES//HENDRIX BURNT IN TWO ON POLE 654-600 CALLED MILLER DISPATCHING CREW/// C PHASE RECLOSURE OUT ON POLE 654-529 OPENED A AND B PHASE ON 654-529 AT 0649// CLOSED ALL THREE RECLOSURES IN AT 0845 //VER/GAH IDC XXXX
1686 | Hazard | 3310502 | HADDIX | CANOE | 2013-06-04 17:43 | 2013-06-04 21:15 | 119 | 212 | 4220361 | 25228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE BURNT DOWN AT RC POLE --FUGATE IN RT-FETR2330--IF NO OTHER ISSUES//COD 119// VER/DBM IDC XXXX
1687 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-12-05 00:07 | 2021-12-05 01:52 | 240 | 105 | 4148821 | 25200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Recloser open at 215-D-429 will not close back in from controls,Going to bypass recloser and restore service..Restored at 01:52.
1688 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-03-03 03:23 | 2009-03-03 13:00 | 47 | 577 | 54383-1 | 25184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 65T FUSE LINK BROKE. TRIED FUSE AND IT BLEW. WILL INVESTIGATE FURTHER. ISOLATING AND TESTING TO DETERMINE TROUBLE LOCATION. RELEASED BY CREW 076S02/// CABLE BAD AT 784-339// ISOLATED AND BACK FEED .// ALL CUSTOMERS RESTORED AT 12:40//VER/CRB IDCC CDC83 XXXX
1689 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-03-21 13:09 | 2011-03-21 18:18 | 148 | 309 | 56325-1 | 25173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STS WR # 39242224 // 1 PHASE OPEN "A"PHASE ( 148 TOTAL CUSTOMERS)STS POLE 1129-35 IN BURNING FK BROKEN,HAVE CONTACTED D HAMILTON ABT NEEDS.OPENED RECL 1129-254,CLOSED 1129-271 AT 13:51.ONLY BURNING FK STILL OUT.CREW ENROUTE SHORTLY (SEND TO STEVE RAY ))//VER/CRB IDC NOT BY TRUCK 4 SPANS OF WIRE XXXX
1690 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-06-22 00:54 | 2011-06-22 02:01 | 375 | 67 | 4381871 | 25125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ASSOCIATED WITH 4377221 - WILL HAVE TO OPEN TO MAKE REPAIRS // SERVICER TO ADVISE PRIOR TO OPENEING // COD 442// VER/DBM IDC XXXX
1691 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-03-02 19:34 | 2020-03-02 23:20 | 111 | 226 | 4445491 | 25086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 span primary down 876-50 // rec open 876-102..isolated grd and tagged for rec back on at 23:20 // cod 111 // fused tap off of this pole not under RECL //
1692 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-06-13 14:21 | 2012-06-13 15:05 | 570 | 44 | 4912001 | 25080 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | REGULATOR | ONE PHASE ON BUSSEYVILLE - LOUISA CIRC OUT ..MANUALLY INTERRUPTED LOUISA STATION AT 1431 AND RESTORED AT 1505 IDC XXXX
1693 | Hazard | 3303902 | LESLIE | WOOTON | 2019-06-30 22:36 | 2019-07-01 03:20 | 88 | 284 | 4624841 | 24992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced braces on pole 336-200, also changed cutout complete . power restored at 3:20 L3/HFP
1694 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2011-06-29 11:00 | 2011-06-29 14:30 | 119 | 210 | H4434651 | 24990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKEN AT POLE 149-137 ON "C" PHASE - "C" PHASE RECLOSER OPEN ON POLE 149-C4-248 - 40 CUSTOMER INTERRUPTED // RELEASED BY CREW 074S02 // NOTIFIED DUTY SUPV WHO REPORTED WILL MAKE REPAIRS AT REGULAR WORKTIME // WE HAVE HAD PROBLEMS GETTING ARMS OFF WE ARE TRANSFER. COND. NO//VER/CRB IDC DUP TO OPEN OTHER PHASES ESTIMATED TIME OFF XXXX
1695 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-03-03 03:30 | 2011-03-03 05:15 | 238 | 105 | 66030-1 | 24990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE RECLOSER ONLY OPEN //COD- 238 - POLE 1098-172 HOT TAP BURNT OFF REPAIRED ACO //VER/GAH IDC XXXX
1696 | Hazard | 3303901 | LESLIE | HYDEN | 2009-04-05 16:49 | 2009-04-05 20:40 | 108 | 231 | 65451-1 | 24948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 1309 INSULATOR//COD 108// VER/DBM IDC XXXX
1697 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-05-30 14:12 | 2013-05-30 15:18 | 378 | 66 | 4197921 | 24948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 2206403--**KY SIDE**--NO ORIG OUTAGE--BROKEN XARM AT 190-C97--NEED 8 XARM, INSULATORS AND FLAGGERS--OPENED CB AT 1412--CC788 **378 CUSTS ON KY SIDE**--HOLD ORDER ISSUED TO ROBERT QUICK--RESTORED ALL CUSTS AT 1518 //VER ANM L3/DNW IDC XXXX
1698 | Pikeville | 3407101 | TOPMOST | DEMA | 2011-10-02 01:45 | 2011-10-02 11:28 | 58 | 583 | 4939281 | 24934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3407101 -POLE BURNT OFF I OPENED RECLOSER 186-18 AT 01:45 OPENED SOLID BLADE 210-1 CLOSED RECLOSER POLE 186-18 AT 02:00 TO SOLID BLADE 210-1. POLE FIRE OUT. CREW REQUIRED NEED FIBERGLASS POLE EXSTENSION CUTOUT ARRESTER GAS DRILL. ROW CREW. NOT BY TRUCK. NEED TO ISO AND GROUND I JUST HAVE SOLID BLADE ON 210-1 OPEN AND TAGED RELEASED BY CREW 074S11CLOSED SOLID BLADE IN AT 11:27 COMPLETE // COD-59 ISO OCR 37830186000018 VER/HFP L3/HFP IDC CHANGED TOF FROM 0016 MADE DUP FOR THAT ONE CUSTOMER XXXX
1699 | South Williamson | 3411401 | DEWEY | INEZ | 2019-01-21 09:04 | 2019-01-21 11:20 | 188 | 136 | 4699041 | 24920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary burnt into at pole 792-4///burnt in clear //going back to open recloser and isolate//crew enroute to assist//opened recloser at 10:25 (8 CUSTOMERS) // ALL REST @ 1120
1700 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-03-07 23:31 | 2008-03-08 01:34 | 204 | 123 | 54790-1 | 24920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308001// COD-204 // STIRRUP BURNT OFF MAIN LINE ON PHASE C // STIRRUP BURNT OFF MAIN LINE CLOSED RECLOSER ON POLE 1108-1 AT 0130 AND RECLOSER ON POLE 1108-431 AT 0134 VER/LDA IDC XXXX
1701 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-08-22 01:06 | 2011-08-22 09:45 | 48 | 519 | 4740211 | 24912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | LINE FUSE IS BLOWN ON POLE 284-91. I AM PATROLLING LINE NOW. I CLOSED LINE FUSE IN AND IT CAME BACK OUT. GIVE THIS TO DAY SHIFT SERVICER. IT IS SO FOGGY I CAN NOT EVEN SEE THE LINE THIS MORNING. I THINK MYLES ROBINETT IS WORKING TROUBLE IN MY AREA TOMORROW. I AM ON EVENING SHIFT THIS WEEK. RELEASED BY CREW //VER/CRB074S01///PATROLING// BAD CUTOUT ON 284-27 WILL CHANGE// CHANGED CUTOUT//REFUSED//POWER IS RESTORED IDC XXXX
1702 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-04-12 18:00 | 2016-04-12 18:29 | 859 | 29 | 4086381 | 24911 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | WHILE SWITCHING SOS 3269 REV 26 AN INUSLATOR FAILED IN THE STATION//EMERGENCY OUTAGE REQUIRED TO REPLACE//SEE DOL CASES 649416 & 649458 // AJB
1703 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-09-28 17:01 | 2015-09-28 17:20 | 1310 | 19 | 4283441 | 24890 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | ****EMERGENCY OUTAGE****OPENED GRAPEVINE34KV CB A AT ENGLE DUE TO LINE SIDE DISCONNECTS OF SAME BURNING @ 1701// TRANSFERRED ALL CUSTOMERS TO INDUSTRIAL PARK 34KV CB B VIA NO 34KV SW @ 150-152//TOM L3/DKG VERIFIED WITH SWITCHING ORDER AJB
1704 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-01-27 02:49 | 2013-01-27 07:36 | 99 | 287 | 4743671 | 24885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3-PHASE RECLOSER IS OPEN ON POLE 214-44. I AM PATROLLING LINE NOW. I CLOSED RECLOSER IN AT 04:40 AND IT STAYED IN ABOUT 5 MIN. AND OPENED BACK UP. I OPENED RECLOSER AT 238-182 TO ISOLATE TIPPLE. I AM GOING TO TRY RECLOSER AT 214-44 AGAIN. IT CAME OUT AGAIN. METER ELECT. IS ON WAY TO HELP. WE CLOSED RECLOSER IN AND TURNED CONTROLS OFF. RECLOSER WAS PUT IN ABNORMAL DATA BASE. METER ELECT. WILL CHANGE CONTROL THIS WEEK. RELEASED BY CREW 074S01 VER/KEP IDC XXXX
1705 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2022-10-16 04:05 | 2022-10-16 11:37 | 55 | 452 | 4031941 | 24860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | rolled to fuse at 0501 //riser on step down broke. Making repairs now (0734)rolled to fuse at 0501 //riser on step down broke. Have a Bad Step Down at pole 241-283,Crew making repairs..
1706 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-01-25 11:03 | 2022-01-25 11:53 | 497 | 50 | 4403281 | 24850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | New pole set between 207-B-189 and 207-B-190 and insulator broke off layout arm and B phase line came in contact with pole///lay out arm failed causing middle phase to get into arm, Elliot making repairs
1707 | South Williamson | 3411401 | DEWEY | INEZ | 2013-05-16 13:16 | 2013-05-16 15:37 | 176 | 141 | 4121931 | 24816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "B" PHASE CAME LOOSE AT POLE 649-63HOT TAP CAME OFF AT POLE 649-63///CABLE COMPANY PULLING IN CABLE IN AREA,MAY HAVE SHOOK POLES TO CAUSE IT TO COME OFF//GOING TO OPEN RIGHT HAND RECLOSER ON 649-202 TO PUT HOT TAP BACK ONHOT TAP CAME OFF AT POLE 649-63/////OPENED RECLOSER AT 15:02,CLOSED BACK RESTORING ALL CUST. AT 15:37//COMPLETE VER/KEP IDC XXXX
1708 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-08-28 01:50 | 2018-08-28 02:17 | 919 | 27 | 4006641 | 24813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | GOAB burning at pole 37830376D00395///GOAB pole 376-D-395 on collier smoot was firing up. ddc opened station breaker allowing to open GOAB and close underslung switches on 376-D-395 picking all customers back up.. GOAB 376-D395 tagged to DDC and also in abnormal database // VERIFIED TIMES PER SCADA = L3/HFP
1709 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-03-28 08:36 | 2008-03-28 10:35 | 208 | 119 | 61481-1 | 24752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401103//REC BACK ON AT POLE 900-104 RELEASED BY CREW 076S01// BAD CUTOUT @ POLE 900-104 ALL RESTORED @ 1035// VER/TOM IDC XXXX
1710 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-12-15 08:57 | 2022-12-15 11:03 | 277 | 126 | 4262691 | 24690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37820003000029 broken 19.9 c/o, isolated xfmr lifting hot tap // crew enroute to make repairs // restored rec on 26-2 @ 10:26 // c/o repairs made and RESTORED XFMR ON 3-29 @ 11:03 Released by crew 074S06
1711 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-06-10 21:56 | 2020-06-11 03:25 | 75 | 329 | 4997341 | 24675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patroled line, found broke cutout on pole 47-D-166 will make repairs.
1712 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-03-09 22:34 | 2015-03-10 03:05 | 91 | 271 | 4175091 | 24661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO SAFELY REPLACE BROKEN CUTOUT ON MANUAL POLE// ASSOCIATED WITH POWERON ORDER 4174921// ONCE OUTAGE STARTS SHOULD BE APPROX 45-60 MINUTES TO MAKE REPAIRS AND RESTORE POWER//TOM - OPENED @ 0227 - CLOSED @ 0256 AJB
1713 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-05-30 09:25 | 2008-05-30 17:48 | 49 | 503 | H52738-1 | 24647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3308503// 3 PHASE POLE BROKE AT PHONE //POLE 318-34= C PHASE RECLOSER OPEN, CONTRACTORS ARE IN THE PROCESS OF RUNNING NEW LINES NEED TO WAIT TILL SUNRISE TO SAFELY TRACE OUT LINES AND REPL POLE//COD 25//OPENED AB PHASES @ 0925 TO WORK SAFELY//THIS INTERRUPTED 49 MORE CUST//RESTORED ALL CUSTOMERS 1748// VER/DBM IDC XXXX
1714 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-08-14 09:55 | 2010-08-14 11:15 | 308 | 80 | 54627-1 | 24640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SERVICER HAD TO OPEN RECLOSERS TO SAFELY ISOLATED AN ARRESTOR THAT IS CAUSING CIRCUIT TO OPERATE - REPORTED IN TROUBLE ORDER 54616-1 /// COD-308 VER/HFP L3/HFP
1715 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2020-11-15 11:55 | 2020-11-15 21:13 | 44 | 558 | 4688451 | 24552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | KYDDC TAGS // Opened loop and tagged to KYDDC at pole 38821016D00061 wire down at pole 38821016D00147/// REPAIRS MADE @ 21:13
1716 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-12-28 12:33 | 2018-12-28 17:13 | 91 | 280 | 4609561 | 24531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | a phase step down high side fuse blown on pole 38830166B10359 tree down at 190-5 ( 2 spans of wire down not by truck cross arm braces broken as well ( openning38830166D00260 Released by crew 078H01,open @ 1600 ,recloser @364 in @ 1700,recloser @ 365 in 1713 all cust restored please close ticket thanks.bt Released by crew 078H02 // 6 customers transferred to another outage 4610411/// Trouble tickets show all phases out.
1717 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-03-03 04:59 | 2014-03-03 17:12 | 64 | 733 | 4445821 | 24482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN AM HOURS WHEN ROADS ARE SAFE // B PHASE ONLY OUT COD 64 WILL CHECK IN AM HOURS WHEN ROADS ARE SAFE // FAULT POLE 1148-D-6537 OPEN 600 DISS CONN AT PL,1148-6546 AT 9;00 AN RELEASED BY CREW 078S09/CREW ON SITE/HOLD ORDER ISSUED @1054/VEM/JOB GOING WELL/FETR 1745/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1712/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP IDCC CNT68 XXXX
1718 | South Williamson | 3411401 | DEWEY | INEZ | 2020-04-25 20:38 | 2020-04-25 22:53 | 181 | 135 | 4750241 | 24435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfmr cutout on pole 672-106//i replaced cutout//restored at 22:53//complete//em
1719 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-06-20 10:29 | 2010-06-20 15:24 | 93 | 295 | 51726-1 | 24411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 35643549 //851-18 FUSE BLOWN HAD A 50 T IN IT SHOULD HAVE BEEN A 65 T..CLOSED 18 BACK IN AT 1300..ROGER MAYNARD ENROUTE TO CHG 2 INS. POLE 851-136.. RELEASED BY CREW 076S01// CHANGED 2 DISC INSULATORS AND ARRESTER ON POLE 851-136 // CLOSED IN FUSE ON 851-18 AT 15:24, 50T FUSE. VER/HFP L3/HFP PAF
1720 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-06-18 17:42 | 2015-06-18 23:33 | 135 | 351 | H4604961 | 24395 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION XFMR LTC FAILED//OPENED FEEDER BREAKER AT 1842//OPENED RECLOSER 1151-D-444 AND BACKFED FROM PIKEVILLE-CEDAR AT N.O. RECLOSER 24-A2-35 @ 2006//RESTORED 261 CUST//REPAIRS MADE ON LTC AND FEEDER RESTORED AS OF 2334//NORMAL FEED RESTORED @ 0108// TIMES PER SCADA & LOG DUP FOR INITAL C PHS OUTAGE // VER/HFP L3/HFP AJB
1721 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-12-27 10:30 | 2009-12-27 13:33 | 133 | 183 | 53821-1 | 24339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN OCR TO MAKE REPAIRS // SHOULD BE LESS THAN 20 MINUTES MLR DATE
1722 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2018-05-30 13:43 | 2018-05-31 12:15 | 18 | 1352 | 4520701 | 24336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 350 COPPER RISER BURNT INTOReleased by crew 078H04 350 copper riser burnt up on pole 21-d2-6649, need new 350 riser. Crew required, truck to polereplaced riser wire and energized. fuse blowed we have a bad kva on bank. we are in route to get new transformerreplaced riser wire and energized. fuse blowed we have a bad kva on bank. we are in route to get new transformer. found bad arrester changed and restored power at 12:15 Released by crew 078Q01
1723 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-02-29 16:49 | 2012-02-29 20:10 | 121 | 201 | 4521391 | 24321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A PHASE REC. LOCKED OUT, PATROLLING LINE.----WIRE OFF INSULATOR AT POLE 37830222D00366//COD 195 // VER/DBM AJB CNT195 PH A.
1724 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2017-05-09 19:00 | 2017-05-09 20:42 | 238 | 102 | 4773601 | 24276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SIDE TAP CUTOUT FAILED ON POLE 38820941C30256 AND COUGHT IT POLE ON FIRE. FIRE DEPT PUT IT OUT FOR US, BUT THE POLE WILL NEED REPLACED. SEND A E-MAIL TO CLIFF FREEMAN TO HAVE A JOB WROTE FOR THIS./ ISO 38820893A00304/ COD 316/ VER/BOW AJB
1725 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-01-26 11:20 | 2015-01-26 15:30 | 115 | 250 | H4964771 | 24256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT OFF POLE @ 326-53 NO TRUCK NEED LINE CREW TO REPLACE,OPEN SWITCH @ 326-11 @ 1120 CLOSED SWITCH @ 11:56/ ISOLATED GROUNDED AND TAGGED TO DDC AT POLE 38830326000120/ RELEASED BY CREW .. CREW ON SIGHT MAKING REPAIRS FETR 15:30 078S05.. OPENED XFMR ON 326-120 AT 15:20 BACK ON AT 15:30.. SOLID BLADE ON POLE 326-120 RESTORED AT 15:30 // SEE DUP H4964771 & HA4964771FOR ADD OUTAGE - PER SERVICER ONLY 1 CUST INITALLY OFF //VER/HFP L3/HFP AJBC LCD 38830326000012
1726 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-02-03 09:01 | 2022-02-03 11:12 | 185 | 131 | 4427491 | 24235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | two broke cutouts, one on pole 184-83 and 1 on 184-144. closed recloser on pole 184-266 back in at 11 :12 hrs, crew coming to replace cutouts Released by crew 077S02
1727 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-04-16 03:43 | 2011-04-16 07:10 | 117 | 207 | 57608-1 | 24219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OUT POLE 157-298///// BROKEN C/O ON POLE 156-237/// C/O OFF LINE, REC. CLOSED. POWER RESTORED. CC= 117. VER/SDB IDC XXXX
1728 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2018-07-15 16:13 | 2018-07-15 18:52 | 158 | 159 | 4775681 | 24212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | a ph stepdown out on cod 158. opening recl on 38831121D00238 & 38831121D30415. 1121-415 cod 130 closed @1845 /1121-238 cod 28 closed @ 1852 opened A phase ocrs at pole 1121D-238 and 1121D3-415 . replaced A phase cutout at pole 1121-408 and restored customers pole 1121-415 @ 18:45 and pole 1121-238 @ 18:52 / ALL WORK COMPLETE / GXJ Released by crew 074S03 L3/HFP
1729 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-07-15 22:34 | 2015-07-16 12:01 | 30 | 807 | 4888871 | 24210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-2027 BAD CUTOUT CHAGED 6T FUSE AJB
1730 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-10-20 10:11 | 2016-10-20 18:15 | 50 | 484 | 4030951 | 24200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE OPEN ON POLE 37830343C00223 ==== POLE 37830343D00026 TOP BURNED OFF === MANUAL UP ON HILL SIDE NEED LINE CREW AND ROW CREW === NEED 40 FT POLE POLE TOP PIN CUTOUT AND 25 KVA 7200 === RELEASED BY CREW 077S03 REPAIRS MADE AND POWER RESTORED AT 1815 VER/CRB L3/HFP XXXHFP AJB
1731 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-06-14 01:05 | 2012-06-14 14:48 | 42 | 823 | 4913761 | 24198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG FUSE AT TAKE-OFF POLE IS OUT,WILL RE-FUSE///////FUSE BLEW,TALKED TO SAMMONS,HE SAID WE WILL WORK ON THIS IN THE A M RELEASED BY CREW 074S06 HAVE ALL CUST. ON AT 10:00 AM EXCEPT 71-207 AND 71-208 HAVE PRI. BAD BUD RIFE IS ON HIS WAY ABOUT 5 FT. COD-42 ISO DF 37830071000162 VER/HFP L3/HFP IDC XXXX
1732 | South Williamson | 3200301 | BELFRY | BELFRY | 2012-01-09 20:38 | 2012-01-10 04:23 | 52 | 465 | 4243801 | 24180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIREPHASE B RECLOSER LOCKED OUT ON 989DS18.. .POLE 990A44 BURNT OFF.JUST ABOVE XFMR..BAD CUTOUT.WILL HAVE TO REPLACE POLE..SEND TO J REED RELEASED BY CREW 080S01 // UPDATED FETR DUE TO FIELD CONDITIONS - UPDATED TO 0500 // CLOSED OCR AT 0423 - XFMR ON POLE 990-A-44 CLOSED AT 0444 // IDCC CNT189 XXXX
1733 | Hazard | 3309302 | VICCO | JEFF | 2014-01-01 17:24 | 2014-01-01 22:30 | 79 | 306 | 4217421 | 24174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE B HAS FELL DOWN IN ROAD, IN BETWEEN POLES 276-74 AND 276-75, COD-79 PULLED OUT OF SLEEVE, WILL NEED BIG BUCKET, 2 MEN AND FLAGGING CREW. OPENED RECLOSERS ON POLE 299-254 AT 19:00 HRS, COD-46 CLOSED AT 22:30 VER/KEP IDC XXXX
1734 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-07-08 14:11 | 2016-07-08 18:52 | 86 | 281 | 4562101 | 24166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE (WITH BACK TO STATION) RECLOSER OPEN ON POLE 883-438///PATROLLING///FOUND BROKE CUTOUT ON POLE 834-387///REPAIRS MADE///CLOSED RECLOSER IN @ 18:52///ALL CUST RESTORED///COMPLETE AJB
1735 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2012-10-05 18:31 | 2012-10-05 19:37 | 366 | 66 | 4117571 | 24156 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | TRANSMISSION LINE DOWN IN TWO SPANS AT POLE #38821089C00407. HAVE TALKED TO CRAIG WALTERS HE IS ON HIS WAY. MAY HAVE TO DROP THE FREEBURN CIRCUIT TO CLEAR TRANSMISSION LINE. RELEASED BY CREW 079H06 // OPENED CB TO ALLOW CREWS TO SAFELY MAKE REPAIRS TO TRANSMISSION LINE // OFF @ 1831 RESTORED @ 1937 VER/ARN IDC XXXX
1736 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-09-24 00:43 | 2018-09-24 16:45 | 42 | 962 | 4147851 | 24121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Dispatched in accordance with KYPCo Late Night Callout Guidelines///primary burn down at hot line clamp,at pole 37830222B00041,all manual, need line crew and 2 r/w crews Released by crew 077S04//will have to open rec to make repairs//will make new order//OPENED 1500 CLOSED 1645 L3/HFP
1737 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2022-04-06 21:08 | 2022-04-06 22:57 | 460 | 109 | 4733481 | 24119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1196269/ broke 19.9 cutout on pole 38830164B43561. Released by crew 078S12 crew on site going to put up neutral fetr 11:45 LRM Released by crew 078H06
1738 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-08-29 03:22 | 2009-08-29 15:44 | 41 | 742 | 55661-1 | 24080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUTS BAD POLE 901-4616 AND POLE 901-7054 UNDERGROUND MAYBE BAD OR XFORMER TRUCK OK RELEASED BY CREW 078S11// CHANGING 2 CUTOUTS HAVE U.G OPEN WILL CLOSE AFTER MAIN LINE IS HOT// MADE FUSE POLE 901-4616 / CABLE BAD FROM 5700 TO 5702 OLD FAULT NOT TAGGED OR IN ABNORMAL NEW FAULT BAD FROM RISER 5650 TO XFR 5701 CANT REACH HUFF OR IKE// CONTRACTOR ON WAY WITH TRACKHOE @ 13:00// ALL CUSTOMERS BACK ON @ 15:44 BOTH RUNS OF CABLE BACK TO NORMAL L3/HFP IDC CHANGED COUNT FROM 46 PH C ONLY XXXX
1739 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-08-06 07:22 | 2015-08-06 10:46 | 118 | 204 | 4102581 | 24072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | C PHASE RECLOSER OPEN @ 327-27///PATROLLING///#4 SOLID COPPER C PHASE DOWN 327-46 TO 327-71.CREW REQUIRED NO TRUCKS PULLED OUT OF SLEEVE///A&B RECLOSER STILL IN @ 327-27 RELEASED BY CREW 078S05,OPEN A& B RECLOSERS @ 1005 REPAIRS MADE A,B & C RECLOSERS IN @ 1046 PLEASE CLOSE TICKET THANKS.BT/DUPLICATE IN HOIS// VER/ ADH //// SEE H4102581 FOR A & B PHASE OUTAGE 70 CUST - VER TIMES PER VOICE REC -- L3/HFP HFPC DUP CCU FP38830327B00027 AJB
1740 | Pikeville | 3408103 | SALISBURY | MARTIN | 2022-02-17 12:32 | 2022-02-17 14:48 | 177 | 136 | 4491551 | 24072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had bad cutouts on b phase and c phase at pole 1074-A-339.///// had to open up reclosers at pole 1074-A-32 at time of 14:00 to replase all 3 cutouts.////// shawn gobles crew is helping with repairs.///// got repairs made and reclosers back in at 14:48
1741 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-01-15 15:29 | 2013-01-15 17:11 | 236 | 102 | 4607591 | 24072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR//CONDUCTOR OFF OF INSULATOR LAYING ON CROSSARM//OPENED RECLOSER TO MAKE REPAIRS//COD 231// VER/DBM IDCC CNT231 XXXX
1742 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2009-06-11 17:36 | 2009-06-12 16:31 | 219 | 1375 | 63208-1 | 24047 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STATION BRK LOCKED OUT DUE TO POLE FIRE THAT IS REPORTED ON ORDER 61889-1 - - CROSSARMS BAD - CREW REQUIRED -GLEN 2 ELLIOT CREW WILL BE WORKING TUCKER AND ANDERSON. VER/ARN IDCC TON1940 XXXX
1743 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2019-03-10 10:27 | 2019-03-10 12:02 | 253 | 95 | 4967151 | 24035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Found at 38830454D16188 where center phase and span guy had been making contact. problem corredcted. apr at 1202 close ticket L3/HFP
1744 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-12-08 17:34 | 2015-12-08 22:46 | 77 | 312 | 4519331 | 24024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD 77//LOOP ON38830020A41539 BURNT OPEN// RELEASED BY CREW 078S07---BURNT LOOP--CREW TO JOB SITE TO MAKE REPAIRS//MADE MDC ON POLE 20-A4-1537 TO SHOW 3 L/F INSTEAD OF 2//COD 77//LOOP ON38830020A41539 BURNT OPEN// RELEASED BY CREW 078S07---BURNT LOOP--CREW TO JOB SITE TO MAKE REPAIRS---OPENED OTHER 2 OCR ON PL 20-3024 AT 21:38 A& C COD 21 CLOSED 2246 VER/CRB AJB B PH INLT OUT.
1745 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-07-26 19:08 | 2009-07-27 10:32 | 26 | 924 | 55044-1 | 24024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT, REFUSED LINE IDCC CNT7, PN59 XXXX
1746 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-12-16 13:29 | 2009-12-16 14:27 | 414 | 58 | 65808-1 | 24012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW HAD TO TAKE EMERGENCY OUTAGE TO REPAIR CROSSARM AND RETIE PHASE THAT IS BURNING IN THE TREES.BROKE CROSS ARM OPEN ATBROKE CROSS ARM OPEN AT 1329 VER/HFP L3/HFP MLR
1747 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-11-20 22:27 | 2012-11-20 22:53 | 923 | 26 | 4412191 | 23998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN RECLOSERS TO ISOLATE BAD CUTOUTS ON 45-6777/FETR2245/VEM/RECLOSERS OPE AT 2227/BACK IN AT 2253/POWER RESTORED TO ALL CUST/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB IDC XXXX
1748 | Hazard | 3309302 | VICCO | JEFF | 2019-07-22 20:57 | 2019-07-23 02:12 | 76 | 315 | 4770741 | 23940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE RECLOSER OUT ON POLE 37830323D30790//COD 76//Released by crew 077S01.found broken cutout on pole 37830299C00084. changed cutout../ ISO 37830323D30790/ COD 76
1749 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-10-08 09:00 | 2008-10-08 09:25 | 955 | 25 | 54114-1 | 23875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW OPENED RECLOSER @ 0900 DUE TO POLE TOP BURNING AT POLE 38830141A00067 IDC XXXX
1750 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-10-01 22:40 | 2012-10-01 23:35 | 434 | 55 | 4105611 | 23870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4104221 CREW OPENED RECLOSER AT 2150 TO ALLOW THEM TO SAFELY REPLACE CROSSARMS COD-434 ISO OCR 37830065A00476 VER/HFP L3/HFP IDC XXXX
1751 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-07-20 14:32 | 2011-07-20 23:56 | 84 | 564 | 4568501 | 23856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RELEASED BY CREW 078S11 ------ SWITCHING CABINET BAD--478-576 // RESTORED @ 2356 IDCC CNT84 XXXX
1752 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-05-30 03:26 | 2014-05-30 09:22 | 67 | 356 | 4952551 | 23852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER PATROLLING CKT. === POLE 37830554000010 LOOP BURN OFF === NEED BIG BUCKET AND LINE CREW AND FLAGERS === CALLED BRUCE FOR LINE CREW === RELEASED BY CREW 077S03 VER/KEP IDC XXXX
1753 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2016-03-04 08:47 | 2016-03-05 08:10 | 17 | 1403 | 4814471 | 23851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 429-B0-30.BAD CUTOUT ON 429-30, ALSO GUY STUB POLE 453-272 CRACKED BAD WILL NEED REPLACED AT LATER DATE PLEASE SEND COPY TO TECH TO GET JOB WROTE, APR AT 0810 CLOSE TICKET VER/KEP L3/HFP XXXHFP
1754 | Hazard | 3310502 | HADDIX | CANOE | 2016-04-03 19:30 | 2016-04-03 22:00 | 159 | 150 | 4043921 | 23850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 97-14 ROTTED OFF 1977? LINE HOT WILL HAVE TO KILL WHEN WE ARE READY-ENOUGH MEN ALREADY OUT--RONNIE TO BRING POLE-SEND TO TIM RELEASED BY CREW 077S06POLE 97-14 ROTTED OFF 1977? LINE HOT WILL HAVE TO KILL WHEN WE ARE READY-ENOUGH MEN ALREADY OUT--RONNIE TO BRING POLE-SEND TO TIM RELEASED BY CREW POLE REPLACED AND POWER RESTORED AT 10:00 RELEASED BY CREW 077H02 VER/ARN AJB
1755 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-08-11 18:40 | 2010-08-11 22:25 | 106 | 225 | H52801-1 | 23850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WR# 36402711///CONFIRMED C PHASE ONLY IS OUT PATROLLING LINE//8 ARM ROTTED OFF AT 37830225B00040 OPENING ALL 3 PHASES TO MAKE REPAIRS RELEASED BY CREW 077S04 RESAGGED CONDUCTORS REPLACED CROSSARM POWERRESTORED AT 2225 CREW 077H01//VER/CRB IDCC DUP TO OPEN OTHER 2 PHASES XXXX
1756 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-05 01:58 | 2010-01-05 07:29 | 72 | 331 | 60687-1 | 23832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE FAILED CREW ON SITE REPAIRING; OPEN OCR ON POLE 428-453 AT 05:56 CLOSED IN AT 07:29 VER/KEP L3/KEP IDC XXXX
1757 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-05-11 12:49 | 2011-05-12 17:09 | 14 | 1700 | 4059861 | 23800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN ON POLE 118-4556, FUSE BLOWN NON POLE 118-144, NEED ROW CREW AND LINE CREW. TRUCK ACCESS RELEASED BY CREW 077M02 RELEASED BY CREW 078M01
1758 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-14 23:07 | 2008-12-14 23:18 | 2155 | 11 | 58400-1 | 23705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308401-- 2307 ORDER CREATED TO SHOW CUSTOMERS OUTAGED TO MAKE LOOPS UP ON POLE 206-27 APPROX 30-45 MINUTE OUTAGE. ON ORDER 58325-1 BECKHAM/HINDMAN OUTAGE. SORRY ORDER HOSED UP.. THANKS PP PAGED OMS AT 2357 ALL CUSTOMERS RESTORED AT 2318 VER/KEP L3/KEP IDC XXXX
1759 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2021-07-29 23:29 | 2021-07-30 09:52 | 38 | 623 | 4980441 | 23674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad pothead on pole 38830021B43577, crew required, trucks to pole Released by crew 078S02 crew on site FETR 10:00 LRM all pwr restored 09 52 please close ticket
1760 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-01-23 03:39 | 2022-01-23 08:38 | 86 | 299 | 4397571 | 23556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | recloser 184-111 open patrolling,,,,1 span primary down 160-58 to 160-59,,700ft span ,no truck to poles maybe mid span with big bucket,,,,OPENED SOLID BLADE 185-79 NOT ON MAPS,,RECLOSER 184-111 back in @ 05:52 up to open solid blade///Complete BR//cod 86
1761 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2021-08-17 04:03 | 2021-08-17 13:13 | 267 | 550 | 4083711 | 23545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | left-hand phase out (ph A per maps, but most calls are on C) // cod 90? // at pole 989-a-271 tap is made up soild on three phase and has line out to recloser // crew required need 8ft arms and 7200 cutout and #2 alum conductor// tap lifted on pole 38820989A00085 // recloser back in @0816 // HAVE TO OPEN GOAB ON POLE 38820965C20583 TO CLIMB POLE AND INSTALL CUTOUT OFF@1220 ON@1313
1762 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-08-23 16:10 | 2020-08-23 17:43 | 253 | 93 | 4361271 | 23529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Bad B phase insulator on pole 223-A-170, will need to open up reclosers on pole 37830223B11259 to make repairs and to prevent this pole from burning any further. Released by crew 077H20 opened recl @ 1610 back on @ 1743
1763 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-10-19 16:57 | 2009-10-19 22:55 | 73 | 358 | 58781-1 | 23521 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER PATROLLINGBAD CUTOUT TOP HILL LINE GOING TO BE REBUILT , WE ARE TO JUMPER CUTOUT FOR NOW POLE # 244-49 VER/KEP L3/KEP IDC XXXX
1764 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-02-26 22:10 | 2008-02-27 02:50 | 84 | 280 | 50727-1 | 23520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308502// COD-84 / NEED TWO MEN AND FIBERGLASS POLE TOP EXTENTION / 3308502// TOP OF POLE BURNED OFF POLE 199B-26 === NEED 2 MEN VER/LDA IDC XXXX
1765 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-08-13 11:05 | 2014-08-13 13:05 | 196 | 120 | 4365671 | 23520 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT INTO ON B PHASE OPEN OCR @ 1255 AND CLOSED @ 1305 (SEE 4366261)RELEASED BY CREW 077S01//COD 210//ISO// VER/DBM AJB CNT210 PH B = 196.
1766 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-11-19 06:50 | 2022-11-19 09:38 | 140 | 168 | 4161171 | 23520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire down from pole 38830018000011 to pole 38830018000010. Released by crew 078H19//B PHASE OCR OPEN ON POLE 38830018000011 ( COD 140)wire down from pole 18-11 to pole 18-10. Released by crew 078H19,repairs made all cust restored @ 0938 please close ticket thanks.bt
1767 | Hazard | 3303901 | LESLIE | HYDEN | 2014-09-14 06:12 | 2014-09-14 09:45 | 110 | 213 | 4497491 | 23430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 077H14--WIRE DOWN 267-30 IN ROAD LOOKS TO BE OLD 4ACSR BURNT INTO-LOOKED TO NEXT RC NOTHING ON AT0945---THINK MAY BE ISSUE SOMEWHERE ON LINE BUT OK NOW--JIM VER/CRB AJB TOF00:54
1768 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-05-17 19:53 | 2016-05-17 22:38 | 142 | 165 | 4227861 | 23430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL NEED LINE CREW , 40 POLE , OPENED RECLOSER ON POLE 102-219 @ 19:53. PLACED GROUND FOR PAUL H./ OPENED RECLOSER ON POLE 102-219 @ 19:53/ ISO 37830102000219/ COD 142/ MADE REPAIRS AND RESTORED POWER AT 2238/ VER/BOW AJB
1769 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-08-19 02:35 | 2015-08-19 07:39 | 77 | 304 | 4150821 | 23408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | "C" PHASE ONLY/FAILED INSULATOR 25-B-2/NEED BIG BUCKET/C PHASE ONLY/FAILED INSULATOR 25-B-2/NEED BIG BUCKET// REPAIRS MADE // POWER RESTORED @ 07:39//DO NOT THINK THIS CUST COUNT TO BE CORRECT //COULD BE 77//CHANGED COD TO 77// VER/CRB // VER PER BUS OBJ ALL C PHASE CALLS L3/HFP XXXHFP AJB
1770 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-02-10 09:10 | 2020-02-10 13:33 | 90 | 263 | 4387111 | 23397 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 30-43,SOLID BLADE CUTOUT IS BROKEN,BOTH ENDS HANGING.STEVE RAY SENDING CREW.MAY HAVE TO OPEN@RECLRS TO REPAIR,MAYBE.¦ OPENED RECL 1302 CLOSED @ 1312 (13 CUST) ¦¦ ALL RESTORED @POLE 30-43,SOLID BLADE CUTOUT IS BROKEN,BOTH ENDS HANGING.STEVE RAY SENDING CREW.MAY HAVE TO OPEN@RECLRS TO REPAIR,MAYBE.RECLR OPEN13:02,CLOSED @13:12/////////MADE REPAIRS&CLOSED SOLID BLADES@13:33/////REPLACED 3 SOLID BLADE CUTOUTS ¦¦¦ NEED TO KNOW WHICH PHASE WAS BROKEN ???
1771 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-05-19 15:57 | 2013-05-19 20:15 | 135 | 258 | 4133841 | 23391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE ONLY 135..OPENED OTHER 2 REC AT 17.45 ISOLATED ON POLE 875-245 ..GRD TAGGED..REC ON P 875-206 BACK ON 18.12.. RELEASED BY CREW 076S01 IDCC CNT204 42 XXXX
1772 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-07-12 23:10 | 2011-07-13 16:05 | 23 | 1015 | 4538531 | 23345 | PARTIAL POWER | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | C PHASE OUT // PATROLING//C PHASE REC. BAD // BYPASSED REC. WITH A 50T FUSE // POWER RESTORED CCC COD-23 ISO OCR 38831100A30130 VER/HFP L3/HFP IDC XXXX
1773 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-02-26 10:32 | 2013-02-26 12:07 | 245 | 95 | 4847681 | 23275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON LOW SIDE OF STEPDOWN ON POLE 37830177D00346, OPENED HIGH SIDE AND TAGGED FOR DDC. POWER RESTORED AT 12:07//COD 245//AED ENTRY CREATED// VER/DBM IDC XXXX
1774 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-11-09 04:58 | 2018-11-09 09:25 | 87 | 267 | 4381461 | 23229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | ooPH C rec onlyoo Patrolling.//COD 87 FROM BEGINNING// Found xfmr fuse 38830737000150 blown. Recloser opened but, due to malfunction, did not close back. Meter electrician enroute to repair. Closed ph C bypass on 761-290 @ 9:25. DDC Hold tag placed on rec ctrl. sh
1775 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-04-10 04:41 | 2015-04-10 17:35 | 30 | 774 | 4300971 | 23220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | TAGGED TO KYDDC/POLE#38830042000117 ROTTED OFF AT GROUND /GROUNDS IN PLACE AT 42-10 BY ROAD/1 SPAN 6A WIRE BROKEN BETWEEN POLE#42-19 AND 42-18 AT CREEK CROSSING FAIRLY WIDE HERE/ NEED #2 SERVICE WIRE TO SPLICE&SPILLBAG NEED XFMER/ YARDDOG AND LINECREW REQUIRED/,,CREW BON SITE,,POLES 42-117 AND 42-18 BROKE,,NO TRUCK,,ALL REPAIRS MADE,,ALL POWER RESTORED VER/CRB AJB
1776 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-07-23 12:20 | 2008-07-23 22:15 | 39 | 595 | 58579-1 | 23205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202//POLE BURNED OFF TAGGED 866-67 IN FIELD BUT SHOWS 866-28 IN FIELDVIEW. NEED 7.2 KV C/O, ARRESTOR AND BRACKET, 2 X-ARMS FOR BAYONET TYPE REPAIR OR 40/4 TO REPLACE POLE.,,,TOP OF POLE BURNT DUE TO CUTOUT BREAKING DOWN,, I ISOLATED ON POLE 866-84, NEED CUTOUT ARRESTER AND BRACKET,, COUPLE OF ARMS TO BANDAID POLE.// WILL SEND MAP DISC,,,TOP OF POLE BURNT DUE TO CUTOUT BREAKING DOWN,, I ISOLATED ON POLE 866-84, NEED CUTOUT ARRESTER AND BRACKET,, COUPLE OF ARMS TO BANDAID POLE. RELEASED BY// VER/DBM
1777 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-11-24 20:35 | 2008-11-25 06:23 | 170 | 588 | 51808-1 | 23190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3010602//POLE FIRE ON POLE 1124-8018 CREW REQ, ALL CUST RESTORED BUT 5 RELEASED BY CREW 078S09/CREW ON SITE/FETR 11-25-08/0730/VEM/WORK COMPLETE0623/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDCC CNT254 ADDED TWO OUTAGES FOR RESTORATION STEPS XXXX
1778 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-04-25 22:57 | 2020-04-25 23:26 | 799 | 29 | 4750721 | 23171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Opened CB affecting 799 CC to allow crews to make up jumpers at 37830426D00012 outage should last 45 mins from start FETR 2345 --- gaj/2326/CB closed restoring all customers (Note previous outage on order # 4749681 for other 128CC )
1779 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-04-27 17:03 | 2011-04-27 18:05 | 372 | 62 | 66501-1 | 23064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 446-53 TOOK RECLOSER OUT ON 446-300... REPLACED CUTOUT RESTORED POWER AT 18:05//VER/CRB IDC XXXX
1780 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-08-10 07:51 | 2013-08-10 13:57 | 63 | 366 | 4643531 | 23058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT 35-13,WILL REPLACE,THEN CLOSE LINE BACK IN//////REPLACED CUTOUT,CLOSED RECLR AND RESTORED VER/CRB L/3 CRB IDC XXXX
1781 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-08-01 01:20 | 2008-08-01 08:35 | 53 | 435 | 63203-1 | 23055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLETOP BURNT OFF, POLE#1112-B-169, XFORMER ALSO OFF BOLTS, HANGING BY LEADS, CALLED R MARCUM, GOING TO WAIT UNTIL DAYLIGHT TO MAKE REPAIRS RELEASED BY CREW 080S01 VER/HFP IDC XXXX
1782 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-08-31 01:09 | 2014-08-31 11:32 | 37 | 623 | 4439761 | 23051 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE FUSE IS BLOWN ON POLE 38820794C00246, PATROLLING THE LINE. TRIED THE FUSE CAME BACK OUT. GOING TO WAIT TILL DAYLIGHT TO PATROLL. THUNDERSTORM IN AREA& THE LINE IS UP ON THE HILL SIDE. RELEASED BY CREW 079S02C PHASE FUSE IS BLOWN ON P38820794C00246, PATROLLING THE LINE. TRIED THE FUSE CAME BACK OUT. GOING TO WAIT TILL DAYLIGHT TO PATROLL. THUNDERSTORM IN AREA&THE LINE IS UP ON THE HILL SIDE. CROSSARM IS ROTTEN AND LET THE C PH FALL ON THE SIDE TAP. NEED ONE MAN EIGHT FO VER/TOM AJB ALL PH.
1783 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-04-03 11:50 | 2009-04-03 14:37 | 141 | 167 | 64640-1 | 23037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 351-59 TOP OF POLE BURNED OFF... CUT LOOP ON POLE 351-63, WILL ENERGIZE UP TO THIS POLE AT 12:55 ... OPENED RECLOSER ON POLE 351-269 AT14:27 (SEE H64640-1) MADE LOOP UP IN POLE 351-63, CLOSED RECLOSER AT 14:37 RESTORING POWER// VER/DBM AJB
1784 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-03-11 09:18 | 2022-03-11 10:58 | 230 | 100 | 4599551 | 23000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 38830381D10259 b phase rec in at 10:58--ds031122 Released by crew 078S01
1785 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2022-02-27 15:00 | 2022-02-27 21:30 | 73 | 390 | 4550161 | 22976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew reqd/sec street light wire down will probably need tree trimmers to get back up, service down would be best to set sec pole to shorten drop/counted off about 135 foot/back yard Released by crew 078S04 crew on site will have to open 3p to repair a broke tie wire on primary Released by crew 078H06
1786 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2015-07-08 03:57 | 2015-07-08 06:55 | 141 | 178 | 4742601 | 22973 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTER AT POLE 234-184, ISOLATED ARRESTERS ON POLES 235-154 AND 234-161 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 AJB
1787 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-03-04 23:17 | 2015-03-06 09:45 | 26 | 2068 | 4104501 | 22971 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN ON 549-135 PATROLLING LINE, FOUND BURNTOFF POLE AT 573-63 ISOLATED T&G TO DDC AT 573-50 CREW REQUIRED POLE CAN BE LOWERED. RECLOSER CLOSED AT 1126 ALL CUSTOMERS RESTORED EXEPT 573-63 /LOWERED KVA POLE TOP/573-63 ON @ 945/COD23+3// VER/ ADH AJB
1788 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-09-10 08:00 | 2015-09-10 13:19 | 72 | 319 | 4221771 | 22968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO 37830143A00328//COD 72//SERVICER OPENED STEPDOWN XFMR ON POLE 143-A-328 @ 0800 TO ISOLATE POSE FIRE ON RECLOSER POLE 143-A-232// RELEASED BY CREW 074H21 VER/CRB L3/HFP HFPC TOF0700 AJB
1789 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-09-19 15:35 | 2016-09-19 17:55 | 164 | 140 | 4908901 | 22960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | LOAD TRANSFER AND OUTAGE TO SAFELY REPLACE CROSSARM AT POLE 45-2702 RELEASED BY CREW 078S05 VER/KEP /// VER PER DOL L3/HFP XXXHFP AJB
1790 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2015-01-26 15:13 | 2015-01-26 17:48 | 154 | 155 | 4965461 | 22950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE #26-237 WILL PATROL//// CUT OUT BROKE ON POLE # 50-126 ///IT HAS BURNED TOP OF POLE OFF //// GOT AHOLD OF STEVE RAY HE HAS CREW ENROUTE CAN LOWER ON POLE//OPENING GOAB ON POLE 26-148 @ 16:03/, CLOSE RECLOSER AT 1616////REPAIRS MADE////// OPENED RECLOSER UP @ 17:47 CLOSED GOAB IN ON POLE#26-148 AND CLOSED RECLOSER IN @ 17:48 AND RESTORED ALL CUSTOMERS/ ISO 37820026000237/ COD 154 // SEE RELATED ORDER 4966071 /// VER/HFP L3/HFP AJB
1791 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-02-21 11:27 | 2015-02-21 14:05 | 145 | 158 | 4063081 | 22910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /174-D-11 BAD INSULATOR BAD INSULATOR ON POLE 37830174D00011, NEED LINE CREW AND 2-19.9 INSULATORSBAD INSULATOR ON POLE 37830174D00011, NEED LINE CREW AND 2-19.9 INSULATORS RELEASED BY CREW 077S04// ISO 37830174D44391 SWITCH//COD 145// VER/DBM L3/HFP XXX AJB
1792 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-12-29 04:41 | 2013-12-29 08:30 | 100 | 229 | 4208151 | 22900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | POLE 247-5 B PHASE 600 DISCONNECT SWITCH CREW REQUIRED GOING TO ISOLATE/247-12 ISOLATED B PHASE AT 0441 HRS (100 CC) // B. FRALEY, T. EVANS, K. GRIFFITH, C. YOUNGMAN TO ASSIST // STOREROOM - C.STONE TO ASSIST //AT - 0752 A-C PHASE RECL CC CLOSED AT 0830 MADE ANOTHER OUTAGE. VER/PDP IDC XXXX
1793 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-09 06:23 | 2010-12-09 09:37 | 118 | 194 | 64618-1 | 22892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A PHASE WIRE BURNT DOWN AT STIRRUP. CREW REQUIRED. OPENED B PHASE AT 09:25 TO MAKE REPAIRS//REPAIRS COMPLETE 0937 // COD 118 (+77 SEE H64618-1) // VER/DBM IDC XXXX
1794 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-01-15 15:11 | 2016-01-15 16:50 | 231 | 99 | 4623181 | 22869 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | "C" PHASE ONLY 231 CC/ RECLOSER FAILED CLOSING WITH BYPASS FUSE (80T)LEAD BURNED OUT OF THE TOP OF RECLOSER ON 900-104.TIM MILLER ENROUTE TO FIX..BY PASSED RECLOSER.TAGGED.CLOSED BY PASS IN AT 16.50 VER/KEP AJB
1795 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-05-06 19:22 | 2022-05-07 12:41 | 22 | 1039 | 4851771 | 22858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | water is close to the road, i turned around need to check daylight Released by crew 077S05
1796 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-08-12 01:37 | 2014-08-12 13:54 | 31 | 737 | 4357391 | 22847 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR IS BAD ON POLE 20-16. TIM HALL IS TO HAVE CREW REPLACE EPOXYLATORS ON THIS POLE.RECLOSURE ON POLE#37830069000278 IS NOW BYPASSED. AT 06:36 RELEASED BY CREW 074S04.PER SERVICER HOLD TAG PLACEDON RECLOSER POLE 69-278 FOR DDC ..ENTERED BYPASS INFO AND HOLD TAG INFO TO AED/"C" PHASE ONLY COD-31/INSULATOR IS BAD ON POLE 20-16. ON @ 1354 COD-31 ISO OCR 37830045000249 VER/HFP L3/HFP AJB SEE 4358131.
1797 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-01-06 23:20 | 2014-01-07 00:45 | 292 | 85 | H4239961 | 22832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830249D00071 3PHASE POLE BURNT OFF ABOVE XFMR, HANGING IN AIR. 40/5 POLE,25KV XFMR 12KV,1- ARM AND BRACES, 2- ARM PINS AND INSULATORS, POLE TOP PIN AND INSULATOR, PRIMARY TAP OFF POLE DEADEND, 1-GUY, 2 CUTOUTS AND ARRESTORS.COMBS, HICKS, MELTON & SEXTON SWITCHES @249D-205 IN AT 00:45 VER/SEF IDC DUP TO OPEN RECLOSERS XXXX
1798 | South Williamson | 3411401 | DEWEY | INEZ | 2008-12-16 07:54 | 2008-12-16 12:50 | 77 | 296 | 58856-1 | 22792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27698064 ///COD- 77 STS WR # 27698064 ///SAM, LOOKS LIKE LINE FUSE ON POLE 38830648A00030 A 30 T MAY BE OUT POLE TOP BURNED OFF ON POLE 648-47 COD-77 L3/HFP IDC XXXX
1799 | South Williamson | 3411401 | DEWEY | INEZ | 2009-07-02 10:24 | 2009-07-02 11:45 | 281 | 81 | 61246-1 | 22761 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | PAUL MUNCY OPENED RECLOSER SO CREW COULD SAFELY REMOVE TREE FROM LINE VER/KEP L3/KEP IDC CHANGING NEUTRAL FOUND BAD CROSSARM OPENED TO MAKE REPAIRS XXXX
1800 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-01-18 08:47 | 2008-01-18 09:50 | 361 | 63 | 57535-1 | 22743 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | SECTIONALIZER OUT ON POLE 141-116. WE BY PASSED SECTIONALIZER ON POLE 141-116 AND PLACED TAGS. NEXT ISO WILL BE AT POLE 164-222. THREE PHASE RECLOSER COUNTER READING 437. VER/KEP IDC XXXX
1801 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-10-09 05:01 | 2014-10-09 05:45 | 622 | 44 | 4577461 | 22716 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP L3/HFP AJB CCTIN FEC57 PER TRANS LOG AND DISP LOG
1802 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-02-18 09:26 | 2009-02-18 13:33 | 272 | 247 | 63895-1 | 22712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308002//SERVICER OPENED RECLOSER 1083-C1-888 IN ORDER TO ISOLATE POLE FIRE//COD 107//CUT LOOP ON POLE 1059-6 AND CLOSED RECLOSER UP TO NEW ISO PT @ ##:##//STS POLE REPLACE AND TIE WIRE IN RIGHT NOWSTS POLE REPLACE AND TIE WIRE IN RIGHT NOW, GOT BUCKET STRUCK HAD TO CHANGE FETRSTS POLE REPLACE AND TIE WIRE IN RIGHT NOW, GOT BUCKET STRUCK HAD TO CHANGE FETR OPEN RECLOSER AT 1322 ( IN ANOTHER ORDER) AND CLOSED AT 1333 RELEASED BY CREW 077S05// VER/DBM IDCC TOF0817 XXXX
1803 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-02-01 13:00 | 2013-02-01 13:47 | 483 | 47 | 4782201 | 22701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN UP RECLOSERS ON POLE 1073-2513, HAD A BAD 300 AMP SOLID BLADE ON POLE 1121-12, HAVE CHANGED OUT AND ALL POWER SHOULD BE RESTORED AT THIS TIME AT 1347 ///VER/CRB L/3 CRB IDCC TOF1244 XXXX
1804 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-11-02 21:14 | 2009-11-02 23:18 | 183 | 124 | 56728-1 | 22692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP LEAD ON B PHASE-OPENED A AN C PHASE UP AT 2301 TO MAKE REPAIRS-CALLED CREW// CLOSED C AN B PHASE IN AT 2318-INSULATOR FAILED-B PHASE FUSE BLEW AT 2330-OPENED A PHASE AT 2338 // IDC XXXX
1805 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-12-22 22:27 | 2013-12-23 04:10 | 134 | 343 | 4194171 | 22687 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 209-178 BURNT OFF// WILL CALL CREW TO REPLACE POLE// WILL LIFT HOT TAP AT 209-37 TO ISOLATE AND WILL RESTORE ALL CUSTOMERS EXCEPT ONE AFFECTED DUE TO POLE FIRE// RELEASED BY CREW 078H25 VER/HFP L3/HFP IDC XXXX
1806 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-05-03 18:06 | 2010-05-03 19:52 | 214 | 106 | 55345-1 | 22684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | BOLTS ON ANGLE PINS LOSSEN UP LET INSULATORS LAY OVER ON ARMS TRACK WHEN RAINNING == OPEN GOAB SWITCH AT 18:06 CLOSED AT 19:52 == POWER OK//COD 214// VER/DBM IDC XXXX
1807 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2008-01-25 05:56 | 2008-01-25 11:20 | 70 | 324 | 59597-1 | 22680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3001001//RECLOSER OUTAGE ON POLE 305-55 (GLENWOOD BR RD)//UNBUILT LINE IN POWERON... UNSURE OF CUSTOMER COUNT//@ 0745, GOT RECLOSER ON, UP TO SWITCHES ON POLE 329-52 WHICH SERVER HAD OPENED TO ISOLATE A DOWNED LINE ON POLE 330-49//CREW REQUIRED//6A WIRE DOWN ON POLE 330-49 TO 330-47 ONE SPAN, NO TRUCKS.//THIS CUST COUNT IS APPROX GIVEN BY SERVICER////VER/CRB PLC COULD NOT LOCATE PN CNT IS APPROX
1808 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-01-06 19:29 | 2010-01-06 21:35 | 180 | 126 | 64192-1 | 22680 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE OPEN @ 1929 // DROPPED REMAINING CUSTOMER @ 2053 - THEN CLOSED IN THE 46KV CB "A" AT ELKHORN CITY AND PICKED UP DRAFFIN STATION @ 2135 // IDC NEED SEPARATE OUTAGE FOR REMAINING CUSTOMERS IDC NO CUSTOMERS OUT TILL 1929 PH A THEN REMAINING OUT WHEN TRANSMISSION OPENED AT 2054 XXXX
1809 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-03-22 02:20 | 2010-03-22 04:05 | 216 | 105 | 52446-1 | 22680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202203CUTOUT BAD ON POLE 771-388 OFF AT 0220 AND RESTORED AT 0405 PER SCADA IDC XXXX AJB
1810 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-03-05 01:11 | 2008-03-05 01:41 | 756 | 30 | 53491-1H | 22680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3401103 /// A PHASE SWITCH ON POLE 876-222 BROKEN (452 CUSTOMERS) THIS DUPLICATE IS FOR THE 756 B& C PHASE CUSTOMERS INTERRUPTED WHEN SWITCH OPENED ON POLE 3883085200193 VER/HFP DEBBIE OK IDC XXXX
1811 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-02-01 14:20 | 2016-02-01 18:53 | 83 | 273 | 4664481 | 22659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE POLE BURNT OFF NEED LINE CREW NO TRUCK,RECLOSER @ POLE 182D-6025 ISO & TAG TO V MULLINS RELEASED BY CREW 078S05/CREW ON SITE/DIFFICULT LOCATION/FETR 2000/VEM/REPAIRS MADE AND ALL CUST RESTORED 1853/PLEASE CLOSE TICKET/NO ASB WORKORDER WRITTEN/VEM/ ISO 38830182D06025/ COD 83/ VER/BOW AJB
1812 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-09-29 17:43 | 2015-09-29 18:15 | 708 | 32 | 4291011 | 22656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING RECLOSER 39831148A00053 TO REPLACE CUTOUTS ON POLE 39831147C35019 IN ORDERS 4290521 & 4289981/ ISO 39831148A00053/ COD 708/ TAGGED TO B. TACKETT/ OPEENED @ 1743REPAIRS MADE ALL CUST RESTORED @ 1815 PLEASE CLOSE TICKET THANKS/ VER/BOW L3/DKG
1813 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2012-11-27 10:33 | 2012-11-27 16:53 | 179 | 380 | 4424191 | 22648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 39831147C45511 POLE NO 45-2 BURNT CUT-OUT FAILURE CAN ISOLATE AND BACK -FEED NEED BIG BUCKET TO DO SO 120-208 TRANSFORMER BANK ONE TRANSFORMER DAM,25 KVA 2 BUSHING TRASFORMER WIRE 556 WILL NEED 6 LOOPS SLEEVES IF WE BACK FEED ** HOLD ORDER REQIRED.& ISSUED TO VERNON MULLINS. TAP OUT ON LOOP POLE 5521. FOR ENTIRE OUTAGE. VER/PDP IDCC STP MISSING XXXX
1814 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-05-18 05:35 | 2018-05-18 13:56 | 223 | 501 | 4368751 | 22623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.C PHASE L/F OPEN ON POLE 37830351C00152//COD 25//Center phase out. Tap cutout on pole 351C-152 is broke.//OPENING RECLOSER 37830352A00234 TO SAFELY MAKE REPAIRS//COD NOW 223//OPENED @1305 CLOSED @ Center phase out. Tap cutout on pole 351C-152 is broke. Opened recloser on pole 352-234 to safely change cut outs at 13:05 and restored power at 13:56. Released by crew 077H08
1815 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-06-22 15:01 | 2011-06-22 19:15 | 89 | 254 | 4393961 | 22606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RW VERY BAD---RECLEARED AROUND POLE---TR LEAD FELL OUT--ON 1915----JIM//COD 90// VER/DBM IDCC TOF 1118 XXXX
1816 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-10-02 22:21 | 2009-10-03 00:30 | 175 | 129 | 65915-1 | 22575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | HAD TO OPEN RECLOSER TO SAFELY REPLACE ARMS AND SWITCHES ON POLE 1122B-48// THESE WERE FOUND TO BE IN BAD SHAPE WHEN THERE WERE OPENED TO ISOLATE THE TROUBLE ASSOCIATED WITH OUTAGE 65367-1// VER/TOM IDC XXXX
1817 | South Williamson | 3411401 | DEWEY | INEZ | 2015-01-25 15:25 | 2015-01-25 16:45 | 282 | 80 | 4962961 | 22560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE LOOP BURNT OPEN AT SWITCH COD 282FOUND HOT TAP AAND STIRRP BURNED OFF AT POLE 697-118 ON RIGHT HAND PHASE ON SOURCE SIDE OF SWITCH///I REPLACED HOTTAP AND PUT ON SCREW ON STIRRUP//RESTORED AT 16:45FOUND HOT TAP AAND STIRRP BURNED OFF AT POLE 697-118 ON RIGHT HAND PHASE ON SOURCE SIDE OF SWITCH///I REPLACED HOTTAP AND PUT ON SCREW ON STIRRUP//RESTORED AT 16:45 RELEASED BY CREW 079S01/COD 282// VER/ ADH // SCADA AGREES WITH B PHASE OUTAGE = VER/HFP XXX AJB
1818 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2014-08-11 13:43 | 2014-08-11 15:25 | 221 | 102 | 4354221 | 22542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING CKTFOUND BAD PTP INSULATOR ON POLE 925-14, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC AT 1525/// TRANSFORMER ON 39830925000014 WAS NEVER OPEN/// VER/BOW AJB
1819 | Whitesburg | 3401301 | FLEMING | NEON | 2012-12-05 12:23 | 2012-12-05 15:58 | 289 | 215 | 4444511 | 22529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD AND BURNED TOP OF POLE OFF . I ISOLATED AT POLE 331-2 AND CLOSED RECLOSER BACK IN AT 13:40 RELEASED BY CREW 077S12 RELEASED BY CREW 075H01 ///VER/CRB L/3 CRB IDCC CDC88 XXXX
1820 | South Williamson | 3411401 | DEWEY | INEZ | 2010-06-22 13:37 | 2010-06-22 19:28 | 71 | 351 | 54621-1 | 22518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE ISOLATED ON POLE 672-86, POLE IS BURNT OFF AT 672-178, FRAMING DOWN NOW , SHOULD HAVE ON IN 2 HOURS, TCM// CLOSED RECLOSER ON 649-188 AT 1759 DOWN TO OPEN RECLOSER AT 601-9 , WILL HAVE TO REMOVE TREE BEFORE CAN GET THE REST HOT.ALSO HAVE BAD 25 KVA ON 672-178 POT IN ROUTE TCM// CLOSED RECLOSER IN ON 601-9 AT 19:28, ALSO TRANSFORMER CHANGED ON 672-178 . TCM// RELEASED BY CREW 076H04 IDC XXXX
1821 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-02-12 23:15 | 2020-02-13 03:28 | 89 | 253 | 4399791 | 22517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulator on pole 37830077000171/ ISO37830102000149/ COD 89 ¦¦¦ IF THIS TAP WAS FUSED WE WOULD HAVE ONLY HAD 2 CUSTOMERS OUT - L3/HFP
1822 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-01-14 12:56 | 2022-01-14 14:15 | 285 | 79 | 4346401 | 22515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | APHASE TO GRND FAULT INDICATED,WILL PTRL/////////NOTHING EVIDENT,WILL TRY RECLR/////////RECLR DID CLOSE BUT THERE IS AN ISSUE WITH A RELAY BOX ON THE RECLR ITSSELF.DOUG HALL IS AWARE OF THIS&WILL TAKE CARE OF THIS AT A LATER DATE.RECLR IS CLOSED THOUGH@THIS TIME14:15
1823 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-04-17 08:25 | 2008-04-17 09:21 | 402 | 56 | 51743-1 | 22512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403003//OPENED SWITCHES ON POLE 47-385 IN ORDER TO DEAL WITH POLE FIRE ON POLE 47-249//COD 402//OPENED AT 08:25, CREW ENROUTE, EXPECTS AT LEAST A FEW HRS BEFORE THEY CAN RESTORE THIS//ALL POWER RESTORED// VER/DBM MLR OK
1824 | Hazard | 3303901 | LESLIE | HYDEN | 2019-03-05 14:57 | 2019-03-05 17:00 | 183 | 123 | 4954151 | 22509 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED RECLOSER 37830316000099//COD 183//TO REPLACE BROKEN POLE 37830291000139//OFF @ ON @ opened at 1457 repairs made and power restored at 1700 L3/HFP
1825 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-07-26 05:55 | 2009-07-26 12:04 | 61 | 369 | 66240-1 | 22509 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | FOUND CUTOUT DOOR BURNED UP ON POLE 1147-101.WIIL NEED TO OPEN RECLOSURES ON POLE1123-133 TO REPLACE CUTOUT. OPENED RECLOSURE AT 11:40. RELEASED BY CREW 074H11 IDC XXXX
1826 | Hazard | 3303901 | LESLIE | HYDEN | 2010-10-03 16:58 | 2010-10-04 15:00 | 17 | 1322 | 56463-1 | 22474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PER BRUCE LINDON, THIS WILL BE HELD UNTIL DAYLIGHT TOMORROW//BOAT RENTAL NEEDED TO PATROL ROW// RESAGGED WRAPPED LINE VER/KEP L3/KEP IDC XXXX
1827 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-01-13 07:33 | 2016-01-13 11:07 | 105 | 214 | H46155111 | 22470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE OCR OPEN//110 CC// POLE 19-33 6A PRI. DOWN REC. OPEN 44-606 4:10 RELEASED BY CREW 078S08//LOOP BURNT OPEN 19-33/DIFFICULT LOCATION/FETR1230/VEM/CREW ON SITE/NEW FETR 1130/VEM//1002 GAVE V MULLINS PERMISSION TO REPLACE DDC HOLD TAG ON POLE 19-33 WITH HIS OWN//SEE DOL CASE 631660 FOR SWITCHING//SEE ALSO ORDERS 4615781 & 4616601// AJB
1828 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2011-12-15 17:30 | 2011-12-16 02:00 | 458 | 510 | 4180531 | 22470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 45` CLASS 4 POLE, 8` CROSSARM & BRACES AND CUTOUT. NEED PRC CREW, AND TECH, PRC CREW IS IN ROUTE. BEWARE MAY BE GAS LINE, WHEN SET NEW POLE. JOE HEMLEPP, CHRIS YOUNGMAN, RICK MORGAN, LUCAS MCCOY AND WES BARKER IDCC TOF1642, CNT462 XXXX
1829 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-09-12 04:24 | 2016-09-12 10:15 | 64 | 351 | 4886441 | 22464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | CROSSARM BRACE BROKEON POLE 473-122 CAUSING PHASE TO LAY ON ARM, LOOP BURNT INTO ON POLE 473-105,OPENED SOLID BLADES ON POLE 473-103 AT 09:40 TO ISOLATE..MADE REPAIRS RESTORED POWER AT 10:15. RELEASED BY CREW 077S11//A PHASE OPEN FROM START MADE MDC VER/CRB // BUS OBJ INDICATES INITAL `A` PHASE OUTAGE L3/HFP HFPC FEC44 LCD37830473000103 AJB SEE H4886441
1830 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-09-28 20:48 | 2020-09-29 00:16 | 108 | 208 | 4504701 | 22464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Recloser is open on 38830502A20361, (108 CC) one span of #4 solid copper dn @38830502000104 line crew only required. Released by crew 078S11//arrived RM isolate &grounded&taged @38830502A20361 recloser in @00:16 please close tic RM
1831 | Hazard | 3302703 | HAZARD | HAZARD | 2015-10-13 16:17 | 2015-10-13 17:05 | 468 | 48 | 4346171 | 22464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DE-ENERGIZED TO TRANSFER CUSTOMERS TO NORMAL FEED - THIS IS OUT OF PHASE SWITCHING//TOM - CREWS ON SITE WORKING TO RESTORE// ASSOCIATED WITH ORDER 4345671// 1628 - STATION SERVICER DEADING TOWARD HAZARD STATION TO CLOSE BREAKER - SCADA COMMUNICATIONS ARE DOWN - KY DDC UNABLE TO CLOSE BRAEKER. - RESTORED AT 1705 AJBC CNT517 574 -106 OUT WITH DOWN PRIMARY. SEE 4345671.
1832 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-12-14 19:35 | 2010-12-14 21:15 | 251 | 100 | H50164-1 | 22460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PART OF 50164-1//OPENED OTHER 2 PHASES @ 1935// OPENED SWITCHES ON POLE 71-50//CLOSED RECLOSERS UP TO OPEN SWITCHES @ 2115 // WIRE APPEARED TO BURN DOWN UNDER OLD COMPRESSION SLEEVE//COD 311// VER/DBM IDCC TOF1835 XXXX
1833 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-10-12 10:38 | 2011-10-12 11:35 | 394 | 57 | 4970011 | 22458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER TO SAFELY REPLACE PRIMARY CROSSARM AND TRANS CUTOUT FROM ORDER 4967531 VER/KEP IDC XXXX
1834 | Hazard | 3303902 | LESLIE | WOOTON | 2014-01-13 04:35 | 2014-01-13 10:05 | 68 | 330 | 4276191 | 22440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-68 ISO LF 37830365C00209 VER/HFP L3/HFP IDC XXXX
1835 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-11-18 08:56 | 2010-11-18 13:40 | 79 | 284 | 57789-1 | 22436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BURNT DOWN AT 1083-117 CREW ENROUTE // --- SPACER CABLE BURNED DOWN ON POLE 1083-C2-117// A & C PH BURNT DOWN ON POLE -1083-117//COD 79 //ISO 38831083C20117//WR# 37814385// VER/DBM IDCC CDC86 XXXX
1836 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-02-13 20:54 | 2021-02-14 08:35 | 32 | 701 | 4039071 | 22432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored at 08:35... changed fuse to 20t..DS. Fuse is on pole 292B-92 and feeds toward 292B-123 crosses US60.
1837 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-08-09 00:41 | 2009-08-09 08:00 | 51 | 439 | 65081-1 | 22389 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY CAME UNWRAPED GETTING INTO TREES == 6A WIRE == REPAIRED == REFUSED == POWER OK //VER/GAH IDC XXXX
1838 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-13 03:36 | 2012-02-13 08:38 | 74 | 302 | 4343871 | 22348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CENTER PHASE WIRE HAS BURNED DOWN AT RECLOSER POLE { 97-346 }. ALL 3 RECLOSERS ARE STILL IN. I AM WAITING FOR TIM HALL TO CALL ME BACK TO SEE WHAT HE WANTS TO DO. TIM SAID HE WOULD JUST WAIT UNTIL START TIME AND SEND A CREW. I WILL STAY AND WATCH WIRE. WE OPENED THE 3 RECLOSERS AT 97-346 AT 08:00, PUT WIRE UP, AND CLOSED THEM BACK IN AT 08:38. VER/KEP IDC ESTIMED COUNT FROM 44 MISSMAPPED CUSTOMERS XXXX
1839 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-12-06 12:21 | 2013-12-06 17:15 | 76 | 294 | 4107111 | 22344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW REQUIRED POLE TOP PIN INSULATOR GONE POLE 126-15 NO TRUCKS BRING 6 WHEELER POSSIBLE #4 SOLID COPPER PRIMARY AND NEUTRAL DOWN /LOW SPOT TO CROSS CREEK IF NOT HAVE TO WAIT TILL WATER GOES DOWN RELEASED BY CREW 078S03/ FETR 20:00/ JEH/POWER REST@ 17:15/ PLEASE CLOSE TICKET VER/SEF L3/HFP IDC XXXX
1840 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2008-04-28 03:20 | 2008-04-28 08:03 | 85 | 283 | 54751-1 | 22339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001402// COD-85 // FUSE OUT ON POLE 38830454D26518 //3001402//,,,, OPEN SOLID BLADE ON POLE 478-4003 CLOSED FUSE ON POLE 454-65183//001402//,,,,,,,BROKE CUTOUT, ON POLE 478-4008 ,,,,,,, BACK ON AT 08:03//MADE SEPARATE OUTAGE FOR SWITCHES//VER/CRB IDC PUT ORDERS BACK TOGETHER XXXX DEB OK
1841 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-09 00:04 | 2011-01-09 03:10 | 120 | 186 | 59981-1 | 22320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE BROKE AT SPLICE // VER/TOM IDC XXXX
1842 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-05-22 21:07 | 2013-05-23 11:30 | 29 | 863 | 4166961 | 22311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUSTOUT ON 271-608, ISOLATED AT POLE 271-567 AT 953 RELEASED BY CREW 077S04 ALL POWER RESTORED AT 11:30 CAN CLOSE MWL VER/KEP IDCC WU XXXX
1843 | Hazard | 3303902 | LESLIE | WOOTON | 2012-02-22 14:41 | 2012-02-22 21:50 | 52 | 429 | 4481031 | 22308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER IN BOTTOM OF LINE CUTOUT BURNT INTO.. ALL POWER RESTORED @ 21:50 ///VER/CRB AJB
1844 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2022-07-02 01:13 | 2022-07-02 15:30 | 26 | 857 | 4360061 | 22282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Dispatched in accordance with KYPCo Late Night Callout Guidelinesfuse blown on u/g primary. need line crew.
1845 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-05-30 11:00 | 2017-05-30 11:28 | 792 | 28 | 4881731 | 22176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENING RECLOSER ON POLE 37820194A00033 TO SAFELY MAKE REPAIRS TO GOAB ON 37820170000147 (ORDER 4880331) ADDITIONAL CUSTOMERS OUT: 792. 1100-1128 VER/AWD AJB
1846 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-05-31 14:55 | 2019-05-31 23:10 | 105 | 495 | 4397411 | 22161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STATION ZONE broke windstream pole 69-1086, line crew, flaggers, bkt tree crew/ opened single phase line fuse on 69-1086 @ 14:55
1847 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-07-19 16:51 | 2015-07-19 21:00 | 89 | 249 | 4911971 | 22161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON POLE37830147000049 VER/SEF AJB
1848 | Williamson | 3202203 | LOVELY | MT.STERLING | 2019-10-31 13:19 | 2019-10-31 18:40 | 69 | 321 | 4231441 | 22149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | found failed pin insulator on pole 820-c-90//it had cleared itself//also river crossing feeding into WV down beyond open switches on pole 820-c-90//APCO is aware of this//restored at 18:40//complete//em
1849 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-02-02 19:23 | 2014-02-02 20:05 | 526 | 42 | 4337931 | 22092 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | STATION OUTAGE TO SAFELY INSTALL MOBILE TR FW-25-1/SOS 2783 REV 57 15 MIN OUTAGE OR LESS OUTAGE NECESSARY TO ALLOW CREWS TO REMAIN SAFE. IDC XXXX
1850 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-06-13 01:15 | 2019-06-13 05:15 | 92 | 240 | 4491301 | 22080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | //Line fuse blown 785-A1-1128 will patrol///Xfmr cuout has failed on pole 716-216.This is in difficult location will need one man to help with repairs///Made repairs and closed fuse @ 05:15 power restored L3/HFP
1851 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-07-09 00:23 | 2012-07-09 09:35 | 40 | 552 | 4630861 | 22080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ALL THREE FUSES ARE OPEN ON 38830454A41611. CROSSARM BURNT INTO ON POLE 454-1671. NEED TO BRING 8 FT CROSSARM CUTOUT AND ARRESTER WITH ARMBRAKET. TWO ARMPINS AND INSULATORS 12KV, LINECREW REQUIRED. DWEST RELEASED BY CREW 078S11...CLOSED IN FUSES PER FIELD AT 9:35//MDH IDC XXXX
1852 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-04-15 06:02 | 2014-04-15 13:33 | 103 | 451 | 4605181 | 22075 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN 245-12-PRI DOWN AT 245-24 REMOVED HOT TAP TO POLE TOP BURN OFF AT 245-287 ,SHOULD BE ABLE TO LOWER EVERYTHING NEW CUTOUT ARR. AN BRK CREW REQUIRED TR. TO POLE MADE RECLOSER ON 245-12 HOT AT 09:34,SEND TO V MULLINS RELEASED BY CREW 078S04/CREW ON SITE/FETR1430/VEM/REPAIRS MADE AND POWER RESTORED TO ONE CUST@1333/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/CRB IDC XXXX
1853 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-11-01 02:55 | 2010-11-01 05:50 | 126 | 175 | 50534-1 | 22050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MIDDLE PHASE BROKE RIGHT AT THE STIRRUP ON RECLOSER POLE *CC 114 SERVICER WILL NEED TO OPEN ALL RECL WHEN REPAIRS START.MIDDLE PHASE BROKE RIGHT AT THE STIRRUP ON RECLOSER POLE..PUT UP WIRE CLOSED REC AT 550...BB IDCC CNT114 DCMT XXXX
1854 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-11-25 08:20 | 2018-11-25 11:07 | 215 | 167 | 4474921 | 22050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 span of #6 cu primary down between 24-D2-454 and 455 B phase, will have to loadbust 3 l/f @24-D2-469 to make repairs. Will keep track of open times. Opened all 3 l/f @24-D2-469 @0945-closed all 3 at 1107 L3/HFP
1855 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-08-10 23:01 | 2019-08-11 00:13 | 306 | 72 | 4870681 | 22032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crew opening to safely replace crossarm///opened at 11:06///repairs made///closed at 00:13///complete BR
1856 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-10-20 20:32 | 2008-10-21 01:56 | 68 | 324 | 57486-1 | 22032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3409302// WIRE DOWN (PHASE B) AT RECLOSER POLE. DUTY SUPERVISOR NOTIFIED AND CREW ENROUTE. RESTORATION DEPENDS ON ARRIVAL TIME OF CSX RAILROAD FLAGGERS.(WIRE CROSSES RAILS)CSX ON SITE. WORK IN PROGRESS. REPAIRS COMPLETE. SH DROPPED (PHASE A) RECLOSER FROM 0141 TO 0156 INTERRUPTING 49 CUSTOMERS FOR SAFETY CLEARANCE. //VER/GAH IDCC PN33 XXXX
1857 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2013-02-22 00:52 | 2013-02-22 05:27 | 80 | 275 | 4838941 | 22000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PHASES A & B OPEN AT POLE 992-D3-481. 80CC. OPENED C PHASE RECLOSER AT 03:48. 31 CC. ALL THREE RECLOSERS RESTORED AT 05:27. IDC XXXX
1858 | Hazard | 3309302 | VICCO | JEFF | 2014-08-22 16:33 | 2014-08-22 21:30 | 200 | 297 | 4404501 | 21988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASES ONLY//COD 200//HAD 2 RECLOSER OUT ON POLE 323D00507 B C PHASE === BAD CUTOUT ON B PHASE FUSE OUT ON OUT SIDE PHASE TOOK ALL CUTOUTS OFF LINE ==== CLOSED RECLOSER IN AT 18:22HAD 2 RECLOSER OUT ON POLE 323D00507 B C PHASE === BAD CUTOUT ON B PHASE FUSE OUT ON OUT SIDE PHASE TOOK ALL CUTOUTS OFF LINE ==== CLOSED RECLOSER IN AT 18:22 ALL ON BUT 1 CUST === GOT LAST CUST ON AT 21:30 === POWER OKHAD 2 OCR OUT ON POLE 323D00507 B C PHASE === BAD CUTOUT ON B PHASE FUSE OUT ON OUT SI// VER/ ADH AJB
1859 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2010-08-22 20:24 | 2010-08-22 21:01 | 594 | 37 | 59380-1 | 21978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED AT 2024 RESTORED AT 2101 VER/ARN IDC XXXX
1860 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-07-21 01:34 | 2022-07-21 12:37 | 104 | 663 | 4533051 | 21962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | wire loop burnt into on c phase on pole 183-14 manuel crew required// iso 37830183A00014// cod 30 //will open RECL 37830182C00008 to make repairs//opened @ 1209 // this interrupts addtl 74 cc//closed @ 1237 //
1861 | South Williamson | 3411401 | DEWEY | INEZ | 2022-11-25 18:14 | 2022-11-25 22:35 | 84 | 261 | 4180921 | 21924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | lead burnt out of bottom of cutout on pole 790-7//no truck//need couple men//going to eliminate cutout and install ptp and ins.//no need for this cutout one pole out from recloser//willopen recloser on 790-113 and isolate when crew arives to make repairs//opened recloser @ 21:15//repairsmade//restored @22:35//complete//em
1862 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-12-23 00:59 | 2014-12-23 11:55 | 42 | 656 | 4875681 | 21899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RECLR IS OUT POLE 37820004000247/,WILL PTRL////////NOTHING EVIDENT,WILL TRY RECLR///CAME BACK OUT,BELIEVE THIS IS A ROW ISSUE.NEED 2 ASPLUNDT CREWS,ALSO COMPANY CREW IN CASE PROBLEM IS SOMETHING ELSE.MASSEY SAID WILL WORK THIS IN THE MORNING RELEASED BY CREW 074S06//BAD TRANS ON POLE 37820028000009//OPENED L/F ON POLE 37820028000008 TO CUT R/W CLOSED IN RECLOSER @ 0909// VER/CRB AJB
1863 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-05-25 06:28 | 2008-05-25 11:50 | 68 | 322 | 51123-1 | 21896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3408303 - ON-SITE @ 08:25 AM.....HIGH SIDE FUSE BLOWN ON STEPDOWN XFRMER POLE 1137C343....SOME PORCELAIN ON THE GROUND...RAISING UP TO INVESTIGATE...JRV 05/23/08////BAD 250 KVA STEPDOWN XFRMER....NEED TO REPLACE///CREW REPLACED....RESTORED POWER @ 11:50 AM....JRV 05/25/08 VER//GAH IDCC CDC92 XXXX
1864 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-19 10:10 | 2016-01-19 12:35 | 151 | 145 | 4631271 | 21895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | X ARM IS BROKE ON POLE #38831027D005751 PRIMARY PHASE & NETURAL DOWN BROKE IN THE CLEAR (151 CUT)/ WILL ISOLATE @38831027D30635 (15 CUST) .WALL NEED FLAGGERS FOR 4 LANE HWY, 2 8FT. ARMS 2 MATERIAL HANDLERS 2 LINE CREWS . OPENED ON POLE # 635 @ 10:10/ ALL POWER RESTORED 1235/ ISO 38831027D00575/ COD 151 VER/ARN AJB CCU
1865 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2017-10-17 09:31 | 2017-10-17 14:04 | 80 | 273 | 4464881 | 21840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S08/ON SITE RM POWER ON @14:04 ALSO ON POLE 70A610 OPENED OTHER LINE FUSE AT 13:23 & CLOSED IN @14:10 PLEASE CLOSE TIC RM VER/AWD /// SEE 4465811 FOR 2ND OUTAGE = L3/HFP HFPC TON1410 ACB
1866 | Hazard | 3309302 | VICCO | JEFF | 2016-08-19 14:40 | 2016-08-19 18:45 | 205 | 245 | 4815701 | 21805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830323D00243 === BAD CUTOUT ON TRANSF MANUAL 19.9 === NEED LINE CREW === GOT MAIN LINE 37830323D00649 ON 16:25 (351 CUST)=== 37830323D00243 @ 1845 (2 CUST)/ VER/BOW L3/HFP XXXHFP AJB
1867 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2017-11-19 03:12 | 2017-11-19 04:19 | 325 | 67 | 4578981 | 21775 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | 2150501 cc=325/ opened Nolan 12kV CB @ 0312 for bus outage to replace broken station service cutout/ restored @ 0419
1868 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-01-20 13:39 | 2022-01-20 18:24 | 88 | 285 | 4391391 | 21774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LOW SIDE FUSE OUT@STEPDOWN,WILL PTRL/////POLE 983-56,ABT 15-20 FT BURNED OFF.SHAWN GOBLE ENROUTE,MAY BE ABLE TO TEMPORARY ENOUGH TO RESTORE POWER,IF NOT,POLE WILL NEED TO BE CHANGED // STEPDOWN RESTORED @1630/ FUSE ON POLE 1007-A-79 RESTORED @1727 TEMPORARY REPAIRS MADE,RESTORED POWER @18:24 Released by crew 074S06
1869 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-01-07 08:39 | 2009-01-07 10:12 | 234 | 93 | 52355-1 | 21762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409401// SOLID BLADE LINE CUTOUT BROKE INTO ON POLE 103-19. THIS IS C PHASE ACCORDING TO MAP.// RECLOSER WAS NOT OUT - NEED TO ADJ IN HOIS// I CHANGED CUTOUT AND CLOSED IT IN AT 10:12 - ISSUED MAP DISC FOR 3 SOLID BLADES ON MAP // // VER/TOM L3/TOM - CORRECT 234 CUSTOMER COUNT TOM// IDC XXXX
1870 | South Williamson | 3200301 | BELFRY | BELFRY | 2014-03-16 15:26 | 2014-03-16 17:38 | 288 | 132 | 4497211 | 21762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARM IS JUST ABOUT BURNED OFF FROM BAD CUTOUT ON POLE 989-19 // IM GOING TO OPEN ON POLE 38820989D00067 OK 1526// ISOLATED RECL POLE 989-18 // CLOSED N.O. AT 990-25 RESTORING 189 CUST FROM BELFRY/TOLER // //VER/GAH L3/HFP HFPC TOF1430 IDCC XXXX
1871 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-07-02 17:54 | 2012-07-02 22:16 | 83 | 262 | 4235181 | 21746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/KEP AJB
1872 | Pikeville | 3407101 | TOPMOST | DEMA | 2020-01-14 07:26 | 2020-01-14 10:55 | 104 | 209 | 4302401 | 21736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECL MOVED TO POLE 37830186000094 ¦¦looks like wire may have broken between poles 186-14 & 186-15. crew on the wayrecloser out on pole186-94 due to wire down looks like wire may have broken between poles 186-14 & 186-15. crew on the wayrecloser out on pole186-94 due to wire down looks like wire may have broken between poles 186-14 & 186-15. crew on the way. wire repaired closed recloser back in at 10:55 everyhting ok
1873 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-04-05 11:57 | 2015-04-05 13:03 | 329 | 66 | 4277151 | 21714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SUSPECTED BAD 19.9 CURRENT LIMITER @ 141-389. CREW REQD. LOW SEC VOLTAGE TO 141 C 423. RECLOSE SCHEME NOW ABNORMAL. RELEASED BY CREW 078S07//IT FORCE CLOSED L3/DKGXXX VERIFIED ALL INFORMATION WITH ALARM HISTORY ON EACH DEVICE MAF SEE H4277151 FOR MOMENTARY STEP AJB
1874 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-08-13 18:19 | 2020-08-13 19:55 | 226 | 96 | 4321431 | 21696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 37820098C00045 Replaced broke cutout and restored @ 19:55
1875 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-10-27 08:20 | 2021-10-27 14:47 | 120 | 387 | 4024271 | 21688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Line crew, flaggers (meet at birdhouse)Recloser is open on 428-234 patrolling, Primary neutral came in contact with primary at 428-79 burnning neutral cond down. Awp flaggers & linecrew required. Recloser 428-234 restored @ 1119Recloser is open on 428-234 patrolling, Primary neutral came in contact with primary at 428-79 burnning neutral cond down. Awp flaggers & linecrew required. Recloser 428-234 restored @ 1119 Released by crew 078S11///Complete BR
1876 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-06-22 14:29 | 2008-06-22 19:07 | 78 | 278 | 51955-1 | 21684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501//CUTOUT BLOWN UP ON POLE 79-33 REPLACED AND RESTORED POWER AT 1907 P HICKMAN AND P PRATT IDC XXXX
1877 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-02-03 10:00 | 2014-02-03 10:23 | 942 | 23 | 4343361 | 21666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING SWITCHES TO MAKE UP LOOP ON ANOTHER OUTAGE (4342361) OPENED @10:00 CLOSED @10:23 COD 942 VER/KEP VER/HFP L3/HFP IDC XXXX
1878 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-07-06 08:20 | 2019-07-06 13:55 | 89 | 335 | 4664211 | 21625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | P HICKS/Bad insulator on 38831065000052/opened sw on 38831064000078 to isolate/closed recl @got bad 19.9 pole top insulator on pole 38831065000052 open solid blade on pole 38831064000078 and placed grounds and closed recloser at pole 1040-18 at 1040got bad 19.9 pole top insulator on pole 38831065000052 open solid blade on pole 38831064000078 and placed grounds and closed recloser at pole 1040-18 at 1040 and closed soild blade at 1355 Released by crew 077S05 L3/HFP
1879 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-11-23 00:35 | 2011-11-23 05:05 | 80 | 270 | 4103781 | 21600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL BE CHECKED AT REG WORK TIME TODAY. CALVIN WILLIIAMS & WALLCE MELTON CALLED OUT TO ASSIT.WILL BE CHECKED AT REG WORK TIME TODAY. CALVIN WILLIIAMS CALLED OUT TO ASSIT. PATROLLING LINEWILL BE CHECKED AT REG WORK TIME TODAY. CALVIN WILLIIAMS CALLED OUT TO ASSIT. PATROLLING LINE. FOUND BAD ARRESTER ON POLE # 253-204, FAULT WENT BACK THROUGH SINGLE PHASE RECLOSER AND TOOK OUT 3 PHASE RECLOSER VER/PDP IDC CHANGED START TIME FROM 0029 FLICKERING XXXX
1880 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-12-23 18:31 | 2022-12-23 21:42 | 127 | 191 | 4331631 | 21575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD 109//B PHASE CLAMP BURNT OFF OCR 37830448C10498// A AND C PHASE OPEN AT 2100B phase Recloser clamp burnt on pole 448C1-498. Will have to open other two reclosers to make repairs. Opened reclosers at 21:08. Power Restored at 21:42.
1881 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-05-14 16:41 | 2009-05-14 19:22 | 134 | 161 | 55619-1 | 21574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD PIN INSULATOR ON POLE 402-85, ONE SPAN #4 ACSR PRIMARY NEUTRAL DOEN FROM POLE 450-3 TO 450-4. IDCC CNT205 XXXX
1882 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-05-01 03:45 | 2016-05-01 08:49 | 71 | 304 | 4148181 | 21568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | / REPLACED A FAILED HOT LINE CLAMP ON POLE 126-34. /// CHECKED TIMES PER VOICE RECORDER VER/HFP L3/HFP AJB
1883 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-01-22 07:15 | 2013-01-22 11:00 | 100 | 225 | 4726681 | 21555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD PLACE IN CONDUCTOR AT 171-131 CAUSED WIRE TO BURN DOWN.. 96 (100 ON A PHASE FROM FAULT POLE ) CUSTOMERS ORIGINALLY OUT ON RECLOSER ON POLE 37830147000054 A PHASE - OPENED RECLOSER ON POLE 37830171000233 @ 0815 INTERRUPTING ADDITIONAL 194 CUST .SEE H4726681 FOR RECL OUTAGE VER/HFP L3/HFP IDC XXXX
1884 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2018-07-30 19:06 | 2018-07-30 21:48 | 133 | 162 | 4873761 | 21546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Source Riser,righthand phase C sturrup burnt off. Will need to open recloser when crew gets here.Replaced sturrup ,opened at 21:47 and closed at 21:48.
1885 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-11-10 02:03 | 2015-11-10 10:11 | 44 | 488 | 4423221 | 21472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED: LINE CUTOUT BROKEN, NO TRUCK ACCESS, POLE 564, WILL NEED TO OPEN AT POLE 1125-63 FOR REPAIRS (NO HOT TAP ON LINE CUTOUT AT POLE 564 ) 19.9 KV RELEASED BY CREW 074S03 OPENED FUSE ON POLE 63 AT 8:55 CLOSED AT 10:11 D SAMMONS SEE DUP H4423221 VER/HFP L3/HFP AJB
1886 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-03-09 14:58 | 2015-03-09 18:08 | 113 | 190 | 4173381 | 21470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 6A PRIM & NEUT DOWN PL# 90-62 TO 197///BURNT DOWN IN STIRRUP///CREW IN ROUTE///CREW ON SC///SCENE///ISOL AND TAGD OCR TO CREW & GRND///FETR 19:30ISH///1 SPAN 6A P&N REPAIRED///OCR RESTORED @ 18:08///TBL TKT COMP VER/CRB L3/IDC XXXX
1887 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-12-24 08:59 | 2011-12-24 13:01 | 90 | 242 | 4199951 | 21470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 500KVA STEPDOWN // BILL FRALEY, MIKE PHELPS & DEAN RUGGLES & NICK MCCANN COD-90 ISO LF 38830116A00726 VER/HFP L3/HFP IDC XXXX
1888 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2015-01-02 13:17 | 2015-01-02 14:09 | 412 | 52 | 4898541 | 21424 | TRANSMISSION LINE | EQUIPMENT FAILURE | NONE | TRANSMISSION LINE OUTAGE/ OPEN 1317 CLOSED 1409 VER/KEP // NOTE: PER ROTDC LOG: DONNIE BARTLEY REPORTS TROUBLE LOCATED ON STR 2 OUTSIDE OF HENRY CLAY S.S.?CAUSED BY POLE GROUND WHICH FELL INTO OUTSIDE PHASE L3/HFP AJB
1889 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-02-21 01:24 | 2008-02-21 13:05 | 77 | 701 | 65875-1 | 21417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001/ SERVICER PATROLLING CKT. * 0256 SERVICER REPORTS FAULTED RECL AT POLE 1103-117 IN PROCESS OF CLOSING BYPASS. * @ 0256. SERV REPORTS RECL UPSTREAM L.O POLE 1127-821 . CREATED 65883-1 TO MODEL . A PHASE RECL AT POLE 1127-821 OUT AT 0256 AND REST AT 0304 ** AT 0310 UPDATE SERVICER CALLED D/S FOR HELP TO PATROL CKT .. @ 0520 UPDATE POLE TOP BURNT OFF 1103-331, ISOLATED AND CLOSED RECL AT 1103-117 AT 0545 ** DENNIS MASSEY WILL ASSIGN CREW AT REG WORK TIME..3402001/ S// VER/DBM IDCC TON XXXX
1890 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-01-13 03:00 | 2016-01-13 06:47 | 105 | 227 | 4615511 | 21417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE OCR OPEN//110 CC// POLE 19-33 6A PRI. DOWN REC. OPEN 44-606 4:10 RELEASED BY CREW 078S08//LOOP BURNT OPEN 19-33/DIFFICULT LOCATION/FETR1230/VEM/CREW ON SITE/NEW FETR 1130/VEM//1002 GAVE V MULLINS PERMISSION TO REPLACE DDC HOLD TAG ON POLE 19-33 WITH HIS OWN//SEE DOL CASE 631660 FOR SWITCHING//SEE ALSO ORDERS 4615781 & 4616601//
1891 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-12-11 22:29 | 2010-12-12 06:25 | 85 | 476 | 65434-1 | 21380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR 38077122 //ISOLATED ON 249-91/250-116 BACK IN AT 0200 HRS TO 249-91 RELEASED BY CREW 078S03 //VER/GAH IDC XXXX
1892 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-10-27 21:38 | 2015-10-28 01:23 | 95 | 225 | 4382461 | 21375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL RECLOSER OPENED//RECLOSER 38830809C10148 OPENED @ 2138//REPAIRS MADE///CLOSED RECLOSERS BACK IN AT 01:23///COMPLETE BR//COD 95//ISO L3/DKG AJB
1893 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2015-02-18 21:05 | 2015-02-19 07:55 | 33 | 650 | 4040581 | 21375 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, UG | RELEASED BY CREW 078S04//CREW IS INSPECTING TRANSFORMERS//CREW ONSIGHT FOUND UG ELBOW TAGGED A PHASE BLOWN OFF PRIMARY BUSHING INSIDE XFMR 21-3792 GOING TO 3791 IN PROCESS OF TROUBLESHOOTING.. HI POTTED CABLE IN XFMR 21-3792 CABLE IS GOOD..A PHASE PRIMARY BUSHING IS BURNED FOUND IT TO BE BAD XFMR SEND COPY TO TECH FOR JOB TO CHANGE .. ALL CUST RESTORED DUE TO SWITCHING RELEASED BY CREW 078H22 VER/ARN // VER TIMES PER DISPATCH LOG // L3/HFP HFPC MCCDL AJB
1894 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2009-06-11 07:11 | 2009-06-11 19:28 | 29 | 737 | 56880-1 | 21373 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | @ 0712 SCADA INDICATED THE BEAVER CREEK - MCKINNEY 46KV CIRCUIT LOCKED OUT INTERRUPTING SPRING FORK STATION IDC XXXX
1895 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-04-09 18:03 | 2019-04-09 19:54 | 192 | 111 | 4075741 | 21312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | B PHASE RECLOSER38831027C00590 OUT//COD 192 FROM THE BEGINNING OF OUTAGE// hot tap burned off at reclosure. need 1 a lineman & hot tap & big bucket//DID NOT HAVE TO OPEN A & C RECLOSERS// L3/HFP sjg
1896 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2008-11-22 05:55 | 2008-11-22 07:31 | 222 | 96 | 50922-1 | 21312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3200201/ "B" PHASE STEP-DOWN FAILED TRANSFERED BACK TO NORMAL FEED IDC CHANGED TOF558, TON816 LOOKS LIKE CUSTOMERS PICKED UP AT 7:31 NOT 8:16 AND SHOULD BE 222 CUSTOMERS NOT 425 XXXX
1897 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-01-19 02:08 | 2009-01-19 05:20 | 111 | 192 | 58166-1 | 21312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3400302 / WR#28113835 / "A" PHASE OUT ON RECLOSER 1077D-652 / COD-111 /3400302 // HOTTAP ON LINESIDE OF RECLOSURE HAS COME OFF LINE / REPAIRED HOT LINE CLAMP AND CUSTOMERS RESTORED AT 0520 VER/LDA L3/KEP MLR OK
1898 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-05-18 13:49 | 2020-05-18 16:40 | 127 | 171 | 4849721 | 21297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON POLE 38821108000022//OPENED SW ON POLE 38821108000222//CLOSED RECLOSER IN @ins broke on pole1108-38, making repairs,,,ins broke on pole1108-38, making repairs,,,opened sw on pole 1108-222, closed rec in on pole 1108-22 at 15:58,, closed sw on pole 1108-222 at16:40 Released by crew 074H07
1899 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-07-30 18:22 | 2012-07-31 00:05 | 62 | 343 | 4868501 | 21266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY MAKE REPAIRS TO CONDUCTOR THAT IS FLOATING OFF OF THE INSULATOR ON POLE 37830279000212/// RELATED TO ORDER 4867511 COD-62 ISO OCR 37830279B10250C// CLOSED AT VER/TOM L3/TOM IDC XXXX
1900 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-07-19 22:20 | 2008-07-20 01:35 | 109 | 195 | H54223-1 | 21255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008702// A PHASE RECLOSER ONLY THING OUT// 58 COD//STEP DOWN XFR BURNED UP WILL NEED MORE MEN TO CHANGE// CALLED IN DHE CREW TO ASSIST/OPENED OTHER 2 PHASES AT_____ COD-109 THEN OPENED LATERAL FUSE`S AT POLE 91(ORDER 54275)STEP DOWN XFR BURNED UP WILL NEED MORE MEN TO CHANGE/CALLED D/E CREW TO HELP WITH DROPING LOAD AND CHANGING 500 STEP DOWN ON PLATFORM HAD TO OPEN B & C PHASE TO MAKE SAFESTEP DOWN XFR BURNED UP WILL NEED MORE MEN TO CHANGECLOSED FUSE AT 0135. VER/KEP MLRC MCC DIS
1901 | Hazard | 3307301 | BULAN | ARY-HEINE | 2017-03-08 08:34 | 2017-03-08 13:25 | 73 | 291 | 4534351 | 21243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE LAYED OVER// OPEN RECL TO MAKE SAFE// OPENED @ 0834 37830153A40273 OPEN MAIN LINE UP AT 8:34 ==== 3 PHASE POLE LAYED OVER HOT 37830153D00154 NEED LINE CREW AND 45 POLE 2 8 CROSSE ARMS37830153A40273 OPEN MAIN LINE UP AT 8:345 ==== 3 PHASE POLE LAYED OVER HOT 37830153D00154 NEED LINE CREW AND 45 POLE 2 8 CROSSE ARMS RELEASED BY CREW 077S03/// VER/DKM L3/HFP XXXHFP AJB
1902 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-02-29 14:29 | 2012-02-29 17:05 | 136 | 156 | 4518481 | 21216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PATROLLING. SLEEVE PULLED OUT ON PRIMARY SPLICE. CREW ENROUTE TO MAKE REPAIRS. REPAIRS COMPLETE. REMOVING GROUNDS TO PREPARE TO ENERGIZE. FOUND BAD ARRESTER ON 881-131 - ISOLATING. ARRESTER ISOLATED. CLOSED REC 881-246 @ 17:05 RESTORING ALL CUSTOMERS. SH//COD 136 // VER/DBM AJB
1903 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-08-29 14:23 | 2014-08-29 17:45 | 167 | 202 | 4436441 | 21194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE ONLY IS OPEN//COD 144//POLE 90-28 NO LINE FUSE ON POLE 6A WIRE DOWN//POLE 91-6106 B PHASE OUT SEND TO BILL F.// SEND TO BILL F. 144 CUST OUT - RESTORED 142 CUST AT 1629 - 2 CUST REMAIN OUT AND RESTORED AT ____ AJBC REMOVED STP. SOME CUST CALL FROM A PH. MAP DESC WAS ENTERED.
1904 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-06-09 10:12 | 2010-06-09 10:47 | 605 | 35 | 59118-1 | 21175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT BAD ARRESTER IN CLEAR ON DOGWOOD LN / VER/LDA IDC XXXX
1905 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-05-27 06:17 | 2019-05-27 09:05 | 126 | 168 | 4347481 | 21168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp burned off riser on rec. pole 468-179. repaired and restored power at 9:05 L3/HFP
1906 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-07-24 20:50 | 2016-07-24 22:48 | 196 | 118 | 4674911 | 21160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074S02 VER/ARN AJB
1907 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-05-01 05:01 | 2016-05-01 06:33 | 230 | 92 | 4147351 | 21160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON PHASE A AT POLE 38821038A30403. CUTOUT WAS A BYPASS FOR A RECLOSER THAT HAS BEEN REMOVED, IT WAS MADE UP SOLID SO I CUT IT IN THE CLEAR. CLOSED PHASE A RECLOSER ON POLE 38821037C00291 AT 06:33. RELEASED BY CREW 079S02 VER/AWD AJB
1908 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-02-20 22:41 | 2015-02-21 12:47 | 25 | 846 | 4059761 | 21150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SECONDARY IS DOWN BETWEEN POLE#37830024D20450 &37830024D20449, WILL NEED 75 FT 1/0 TRIPLEX. & 3 MEN.IS BUCKET ACCESSABLE.ONLY 4 OUT HERE RELEASED BY CREW 074S04/ OPENENING TRANSFORMERS 24-450 AJB
1909 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-03-14 23:00 | 2015-03-15 00:18 | 271 | 78 | 4194691 | 21138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPORTED BY RECC - PRIMARY OFF INSULATOR - BURNING ON THE ARM// OPENED RECL 1083-888 @ 2300 TO ISOLATE AND REPLACE FAILED INSULATORS NO OUTAGE TILL THEN AND RELEASED BY CREW 077S05 VER/KEP AJB
1910 | Whitesburg | 3314401 | MAYKING | ERMINE | 2019-08-27 07:10 | 2019-08-27 10:54 | 332 | 224 | 4950411 | 21120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | B & C RECLOSERS BURNT UP //COD 76 FROM BEGING OF OUTAGE//B & C reclosers bad on pole 449-854B & C reclosers bad on pole 449-854//OPENED SW ON POLE 37830449D10175 THIS OUTED 256 MORE CUSTS//OFF @ 1038 ON @ 1054B & C RECLOSERS BURNT UP //COD 76 FROM BEGING OF OUTAGE//B & C reclosers bad on pole 449-854B & C reclosers bad on pole 449-854 open on pole 449-175 at 10:38 closed at 10:54 reclosers on pole 449-854 are bypassed Released by crew 075H03 L3/HFP
1911 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-08-21 18:19 | 2021-08-22 01:10 | 175 | 411 | 4133591 | 21119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C phase step down fuse blown will patrol///Bad 500 KVA step down xfm will need line crew//Will have to open A &B pase reclosers and step downs to change C phase step down safely@ 1241//Repairs made closed all 3 reclosers in @ 01:10 and restored service
1912 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-02-20 08:31 | 2015-02-20 16:30 | 44 | 479 | 4052691 | 21076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE OUT ON STEPDOWN AT 477-260 PATROLLING, BAD 250 KV STEPDOWN XMF LINECREW ONLY REQUIRED RELEASED BY CREW 078S11 CHANGED KVA CLOSED AT 16;30 PLEASE CLOSE TICKET THANKS DWW VER/HFP L3/HFP AJB
1913 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-11-30 22:40 | 2020-12-01 02:45 | 86 | 245 | 4733341 | 21070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew required 1122-78trucksok #4 copper primary/taged to mccoy Released by crew 078S03crew on site FETR 03:00 LRM all pwr restored 02:45 LRM please close ticket LRM
1914 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-09-16 00:28 | 2013-09-16 05:30 | 123 | 302 | 4856411 | 21066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 65T ON POLE#5035 MD FILED/ ADD 3 MISMAPPED CUSTOMERS COD-126/RESTORED FUSE ON 5035 AT 0130/ UNKNOWN NUMBER OF CUSTOMERS OUT FROM 5184 ON TO THE UG PADMONTS THAT FEED APT BUILDINGS MAPPING ISSUE NO CUSTOMERS SHOWN ON PADMOUNTS/CREW WORKING ON UG/PARTIAL RESTORE ENERGIZED 5199 AND 5182 AT 0530 APPROX 40 CUSTOMERS IDCC STP MISSING, TONF130 XXXX
1915 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-06-03 13:45 | 2008-06-03 16:00 | 156 | 135 | 54974-1 | 21060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308401// OPENED RECLOSER TO REPLACE CROSSARM 37830183A00030/ COD 156 ////VER/CRB
1916 | South Williamson | 3411401 | DEWEY | INEZ | 2020-06-23 13:15 | 2020-06-23 13:51 | 585 | 36 | 4063621 | 21060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1030158 // SCADA indicates RECL 38830767C00111 L/O @ 1315 // COD 585 // Released by crew 079S01/ ISO 38830767C00111/ COD 585/ On @ 1351
1917 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-11-10 02:16 | 2015-11-10 11:30 | 38 | 554 | 4423231 | 21052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3 FUSES OUT @25-391,WILL PTRL/////POLE 25-430 BURNED OFF,CAN USE TRUCK TO RE-SET OR CAN POSSIBLY FRAME DOWN,45C2 POLE W XARM,PINS,INSULATORS,ETC RELEASED BY CREW 074S06/// HAVE LOOKED AT THE TROUBLE HAVE CREW IN ROUTE, WITH HARDWARE TO MAKE REPAIRS.//REPAIRS MADE AND CLOSED BACK IN AT 11:30 TIM MCCOY RELEASED BY CREW 074H10 AJB
1918 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-05-09 03:07 | 2019-05-09 05:40 | 536 | 153 | 4242291 | 21043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | most likely cause of previous recloser outage//failed line cutout//crew to replace tonight//opened RECL 1108-C1-6119 @ 0307 in order to replace bad cutout//cod 8(+528)//closed RECL @ 0345 but original fuse on 1061-D-71 came back out//found bad insulator on pole 1061-C3-109//lifted hot tap on 1061-c-107 to isolate//closed fuse @ 0505//made repairs and replaced hottap at 0540 // ¦¦ QUESTION ABOUT NOT USING SWS TO ISOLATE TROUBLE? L3/HFP
1919 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-10-10 05:48 | 2009-10-10 07:57 | 163 | 129 | 54127-1 | 21027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD /./ VER/TOM IDC XXXX
1920 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-03 05:17 | 2010-12-03 10:56 | 62 | 339 | 62625-1 | 21018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | "A" PHASE RECL OUT ONLY (122 CUST) //GOT ONE SPAN OF #2AL DOWN POLE 77-14. WIRE CROSSES ROAD TWICE. JIM MULLINS IS GETTING CREW. CANT TELL WHAT TOOK WIRE DOWN. MIGHT PULL OUT OF SLEEVE STS OPEN OTHER PHASE AT0920 (+61 CUST, SEE H62625-1) AND CLOSED AT 1056 RELEASED BY CREW 077S05// VER/DBM IDC PHASE C NOT A CHANGED COUNT FROM 122 XXXX
1921 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2019-01-30 10:48 | 2019-01-30 12:12 | 315 | 84 | 4734061 | 21001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Load side stirrup has burnt off on center recloser riser will be opening all three and isolating to make repairs..//COD 48 FROM BEGINNING//OPENED A & C RECLOSERS @ 1141//Load side stirrup has burnt off on center recloser riser will be opening all three and isolating to make repairs.. opened @ 11:41 made repairs and closed back in @ 12:12 L3/HFP/// Trouble tickets showing B and C were off from the start of outage.
1922 | Paintsville | 3410602 | E.PRESTON | LANCER | 2019-07-15 20:22 | 2019-07-15 22:08 | 198 | 106 | 4714021 | 20988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 300 amp switch failed. ooPHASE C ONLYoo Replaced 300 amp door and closed @ 22:08. sh COD 62/// Trouble tickets show all phases out
1923 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-04-10 09:26 | 2011-04-10 15:10 | 61 | 344 | H52978-1 | 20984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 77-151 HAS ROTTED OFF, NEED 40 FT POLE 2 8FT ARMS ,15 KVA AND CUTOUT AND ARRESTOR,4 ARM PINS,4 7200 INSULATORS,1SET OF BRACES ONE 150 HPS LIGHT RELEASED BY CREW 077H02-NEED YARDDOG//C PHASE ONLY IS OUT//COD 61//OPENED PHASE A @ APPROX 0920 // AND CUTOUT AND ARRESTOR,4 ARM PINS,4 7200 INSULATORS,1SET OF BRACES ONE 150 HPS LIGHT RELEASED BY CREW 077H02-NEED YARDDOG STS OPEN A PHASE AT 0926 AND CLOSED AT 1510//COD 61 + 122 IDC DUP TO OPEN PH C XXXX
1924 | Pikeville | 3407101 | TOPMOST | DEMA | 2018-12-14 16:09 | 2018-12-14 21:53 | 97 | 344 | 4565691 | 20950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C phase rec. open on 114-B-243 will be patrolling..B and C phase cutouts on pole 113-173 have failed burning crossarm in two contacted Paul layne he and line crew are coming to make repairs.Will be opening switches on pole 89-57 to isolate and make repairs.opened C phase switch and closed rec. @ 18:54 will open other 2 switches when crew arrives.opened REC.@20:25 closed@21:53 and opened switches@20:32 closed@21:52 ¦¦¦¦¦¦ VERIFIED TIMES PER VOICE RECORDER - OUTAGE STARTED WITH C PHASE RECL OPEN ON POLE 114-B-243 (42 CUST) & B PHASE RECL ALSO OUT ON POLE 113-173 (29 CUST). L3/HFP
1925 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-07-03 16:10 | 2016-07-04 04:06 | 38 | 716 | 4518751 | 20927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG RISERF IS OUT////TRIED F,CAME BACK OUT,NEED HELP///DIG#1607030044////////GOING TO GO OVRHD W 1POLE&PRIM EXT W UG PRIM OFF IT.WILL BE ELIMINATING UG FRM 71-164TO71-165&SETTING NEW POLE BESIDE 71-165/////////ALL CUSTS RESTORED&04:06 RELEASED BY CREW 074S06 VER/KEP AJB
1926 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-09-05 05:06 | 2010-09-05 15:40 | 33 | 634 | 63752-1 | 20922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 075H01 ONE PHASE BURNT DOWN IN SPACER CABLE WILL BE OPENING GOAB ON POLE 381D3530 WHEN HELP ARIVES//ONLY PHASE A AFFECTED//ISO 37830382A20286//COD 33//OPENED GOAB 381-530 @ 1211 INTERRUPTING ADDITIONAL 84 CUST TO ISOLATE TROUBLE// IDC XXXX
1927 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-12-02 07:01 | 2015-12-02 11:10 | 84 | 249 | 4502541 | 20916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE HAS BURNT OFF, WIRE DOWN, POLE #37830204000268, NEED TO BRING FIBERGLASS POLE EXTENSION, 7.2 CUTOUT AND ARRESTOR, MATERIAL HANDLER. POLE IS LOCATED IN LOWER END OF PARKING LOT, MONTGOMERY BAPTIST RELEASED BY CREW 077S02 VER/CRB AJB
1928 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-05-08 18:58 | 2008-05-08 19:50 | 402 | 52 | 58405-1 | 20904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3403003//OPENED SWITCHES ON POLE#47-385 TO SAFELY REPAIR INSULATER AND CONDUCTER ON POLE#47-234//VER/CRB IDC XXXX
1929 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-06-12 20:20 | 2014-06-12 21:36 | 275 | 76 | 4080281 | 20900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOOP BURNTINTO ON POLE 38821062C00030 OPENENED CUTOUTS ON POLE 1062 C40 AT 20:20 AND CLOSED CUTOUTS ON POLE 40 BACK IN CAT 21:36 CUTOUT WAS OK LOOP BURNT INTO BY ARM PIN RELEASED BY CREW 079H03 VER/CRB AJB
1930 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-09-22 19:02 | 2018-09-22 20:30 | 482 | 88 | 4142491 | 20883 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 861750 // pole 38820941D00264 on fire//opened GOAB 38820941D00263 to isolate fault// looking at possible load xfers // cod 482// 3 solid blade cutouts on fault pole 38820941D00264, the right-hand phase cutout had failed//sent to engineering to have pole checked// NEED TO KNOW IF SWS ARE FEEDING LINE TOWARD POLE 38820941D00472 IF SO WE HAD 129 CUST OUT (C PHASE & 3 PHASE CUST) UNTIL SWS OPENED ON POLE 38820941D00263, WHICH WOULD HAVE INTERUPTED 353 CUST.... HFP /// TALKED TO ED MATNEY & HE CONFIRMED THIS... I ENTERED MD ... HFP L3/HFP
1931 | Paintsville | 3401102 | FALCON | SALYERSVI | 2011-02-28 08:09 | 2011-02-28 10:46 | 133 | 157 | 63732-1 | 20881 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 38965310 // A PHASE RECLOSER OUT PATROLLING.<<<<A PHASE ONLY 133 CUST>>>> PATROLLING. FOUND ARRESTER BLOWN ON 875-543 AND CLEARED IT UP. PATROLLING. FOUND ARRESTER BLOWN ON 875-543 AND CLEARED IT UP. CHECKING NEW HAZARDS THAT HAVE BEEN CALLED IN.> PATROLLING. FOUND ARRESTER BLOWN ON 875-543 AND CLEARED IT UP. CHECKING NEW HAZARDS THAT HAVE BEEN CALLED IN. RESTORED PH A RECLOSER ON 875-541 @ 10:46. SH VER/HFP L3/HFP IDC DCMT XXXX
1932 | South Williamson | 3411401 | DEWEY | INEZ | 2021-10-29 00:43 | 2021-10-29 09:10 | 294 | 507 | 4034591 | 20870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1158829/ DA RECL 744-D2-527/ cutout broke on 769-a-133//isolated with long stick//no truck///need line crew to assist//can reenergize recloser//can hold//only 2 customers out //repairs made//restored at 9:10//complete//em
1933 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-12-25 12:13 | 2009-12-25 14:00 | 195 | 107 | 54524-1 | 20865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MANUALLY OPENED "A" PHASE RECLOSER TO REPLACE FAILED CUTOUT/ COD-195 / WR#33198345 /MANUALLY OPENED A PHASE RECLOSER TO REPLACE FAILED CUTOUT/ COD-195 / WR#33198345 FOUND BAD CUTOUT AFTER CLOSING IN RECLOSER THE FIRST TIME, IT IS ON POLE 1073-88, FOUR POLES FROM RECLOSER BEHIND WHITE DOUBLE WIDE ON RIGHT SIDE OF ROAD, MAYBE BE ABLE TO USE TRUCK, ALSO MAY NEED TO TRIM OUT SOME TREES TO GET TO ITMANUALLY OPENED A PHASE RECLOSER TO REPLACE FAILED CUTOUT/ COD-195 / WR#33198345 FOUND BAD CUTOUT IDC XXXX
1934 | Hazard | 3309003 | JEFF | VIPER | 2021-11-13 09:41 | 2021-11-13 16:42 | 145 | 421 | 4087841 | 20860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | recloser on 396-408 is open 37830393B00089 isolatedrecloser on 396-408 is open,..pole 393-267, 40/4 broken cutout, burnt pole into and must be replaced. need tech, 45/4, ptp, d.e.ins. 2 cutout and 2 arr, 2 brkt.. truck acc..isolated on 393-89,..re-energized recl #369-408 @ 11:57 hrsrecloser on 396-408 is open,..pole 393-267, 40/4 broken cutout, burnt pole into and must be replaced. need tech, 45/4, ptp, d.e.ins. 2 cutout and 2 arr, 2 brkt.. truck acc..isolated on 393-89,..re-energized recl #3
1935 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-12-24 10:52 | 2008-12-24 13:30 | 132 | 158 | 63349-1 | 20856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW OPENED RECLOSER LONG ENOUGH TO ISOLATE POLE THAT HAS THE TOP BURNING RELATED TO ORDER 63308-1 ENTERED MD FOR SOLID BLADE SW-HFP L3/HFP IDC REMOVED 2 MIN STEP 192 CUSTOMERS OUT 1052 TO 1054 XXXX
1936 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-10-26 08:05 | 2009-10-26 09:48 | 202 | 103 | 53687-1 | 20806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HOT TAP LEAD BURNT OFF ON CENTER PHASE RECLOSER COD-179/190 ADDED 11 FROM MISMAPPED CUSTOMERS MD FILED VER/KEP L3/KEP IDC XXXX
1937 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-06-08 12:32 | 2020-06-08 17:25 | 71 | 293 | 4980031 | 20803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | - STEPDOWN @ 37830158D20394 FAILED ¦¦ CALLING CREW & FLAGGERS
1938 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-07-12 01:12 | 2020-07-12 07:23 | 56 | 371 | 4154031 | 20776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines./// Looks like hot tap has burnt off on pole 151-34 this is a very difficult location///Will need help/// Replaced bad hot tap stirrup and hot tap clamp and changed cutout// Closed in @ 07:23 and restored service // 56
1939 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-04-17 12:32 | 2020-04-18 15:05 | 13 | 1593 | 4710601 | 20709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 38831083D40390 -- wire down load on load side tree on primary primary and neutral broken #2 alluminate bucket truck accessable but communication line down where than can be snared by trucks
1940 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2013-03-18 02:06 | 2013-03-18 10:13 | 540 | 487 | 4913991 | 20708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0145 ETA 911 CALLBACK . AT 0206 - OPENED FEEDER STATION RTU FAILED . AT 0215 TROUBLE CLEARED AT POLE LIFTED HLCS AT 139-455 AND FEEDER CAN BE CLOSED AT STATION AT 0241 , DANNY TRAUGOTT CLOSED FEEDER AT STATION , DUE TO RTU FAILURE . POLE 139-456 45/4 POLE 139-456/CREW ON SITE/FETR1200/VEM/NEW FETR1100/VEM RELEASED BY CREW 078H14 VER/KEP IDC XXXX
1941 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-10-21 04:34 | 2016-10-21 05:15 | 505 | 41 | 4035521 | 20705 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | FAILED STATION SERVICE CUTOUT OUTGAE FOR CREW TO SAFELY REPLACE VER/KEP // VER TIMES PER SCADA & DOL L3/HFP XXXHFP AJB
1942 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-03-01 18:11 | 2018-03-02 16:32 | 35 | 1341 | 4894901 | 20701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TAGGED & GROUNDED TO KYDDC @ 38830669D30090/ Pole 669-28, pole top burnt off. No trucks, may be able to lower everything. Isolated tagged and grounded to KY DDC at pole 38830669D30090. Recloser back in at 23:43 // 1509 UPDATED FETR CREW HAVING PROBLEMS DUE TO DIFFICULT LOCATION/reopened ocr at: 1630-1632.TAGGED & GROUNDED TO KYDDC @ 38830669D30090/ Pole 669-28, pole top burnt off. No trucks, may be able to lower everything. Isolated tagged and grounded to KY DDC at pole 38830669D30090. Recloser
1943 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-08-12 16:43 | 2012-08-12 17:40 | 363 | 57 | 4930601 | 20691 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELATED TO ORDER 4929951 CREW HAD TO OPEN SWITCHES ON POLE 38830785D20331 TO ALLOW THEM TO SAFELY REMOVE A TRANSFORMER BANK THAT IS LEAKING OIL FROM THE POLE SO THEY CAN REPLACE THEM. POWER RESTORED @ 1740 COD-357 ISO PO @ 38830785D20331 VER/HFP L3/HFP IDC XXXX
1944 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-10-11 13:36 | 2014-10-11 18:27 | 71 | 291 | H4606721 | 20661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THIS REPLACES ORDER 4606051 //POLE TOP BURNT OFF NEED 3 MEN & FLAGGING CREW & 4` FIBERGLASS POLE EXTENSION & CUTOUT // OPENED STEPDOWN @ 1336 //R VIRGIN & YOUNGMAN & CANTRELL & SIMMONS // LINE OPENED & GR & TAG TO RON V AT 429D-67 R FLAGGERS TO MEET @ BIRDHOUSE 1CUST INITALLY OUT // INTERRUPTED 71 @ 1336 COD-72 ISO LF 38830429D00067 DUP OF 4606721 FOR 71 CUST /// VER/HFP L3/HFP AJB
1945 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-09-05 11:10 | 2017-09-05 17:00 | 59 | 350 | 4330641 | 20650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE BLEW AT POLE 478-202///XFMER FUSE BLEW ON 478-495///WHEN I REFUSED THE LID ON 50KVA BLEW OFF AT POLE 478-495 AND BLEW PRIMARY OFF POLE TOP AT 478-495 BLOWING THE LINE FUSE AT 478-202///CREW /REQUIRED///NEED 6 WHEELER, 50KVA 7200//// RELEASED BY CREW 078H22/ON SITE RM CLOSE FUSE IN @17:00 ALL POWER BACK ON PLEASE CLOSE TIC RM 38830478D10202 38830478D10495 VER/AWD L3/CAS SJG
1946 | South Williamson | 3411401 | DEWEY | INEZ | 2013-01-18 02:25 | 2013-01-18 10:59 | 79 | 514 | 4660441 | 20642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PLEASE HAVE CUSTOMER CK EQUIPMENT . APT BLD. ONLY ONE CALL.//LINE FUSE BLOWN ON 743-199/ONE SPAN OF PRIMARY DOWN AT 743-103//TRUCK APPROACH//WILL NEED SOME TREES TRIMMED//BUCKET TREE CREW AND CHIPPER////LIFTED HOT TAP ON POLE 103 AND GOING BACK TO FUSE POLE TO DO PARTIAL RESTORE//CLOSED FUSE AT 03:45//CREW WILL PROBABLY HAVE TO OPEN WHEN MAKING REPAIRS//TIM MILLER * D/S WILL HAVE CREW READY TO GO AT DAYLIGHT //COD 79 // VER/DBM IDC XXXX
1947 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-03-09 23:24 | 2019-03-10 06:34 | 48 | 430 | 4965791 | 20640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | open on 117-57 primary off pole top pin@ 37830141000013.Will need pole top pin insulator & copper tie wire Released by crew 074S04 ¦¦ PER VOICE RECORDER - SECTIONALIZER OUT L3/HFP
1948 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-03-09 02:57 | 2018-03-09 13:42 | 146 | 645 | 4980721 | 20575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS/ pole 37830229000138 burnt ready to fall opened recl 37830204000080 at 0422 to isolate 91cc/ opened loops at 37830229000102 Tagged to KYDDC/ Closed Recl at 0500 restored 55cc/. will need line crew and flaggers, 50cl2 pole, 25kva 19.9 xfmr, 8 arm and braces, ptp and insulator, 2 arm pins and insulators, 1 deadend, 2 cutouts, 2 brackets last customer/ Reopened recl 37830204000080 @ 1230 closed @ 1237 55cc/ restored open loop 37830229000102 1237 33cc/ restored xfmr and fuse 37830229000138 @1342
1949 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-02-13 14:28 | 2014-02-13 18:48 | 79 | 260 | 4383731 | 20540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2/13/14 AT 15:23 CUTOUT BAD BURN TOP OF POLE OFF AT 38831128000172 CAN CUT TOP OF POLE OFF MAYBE AND LOWER PRIMARY. CAN OPEN UP LINE FUSE AT POLE 38831128000047 AND CLOSE RECLOSER IN AT POLE 831128000112,GOING TO WAIT ON THIS. CREWS ON SITE AND GOING TO PICK ALL UP AT ONCE.//COD 79// DID NOT DO PARTIAL STEP, GOT EVERYONE ON AT SAME TIME// VER/DBM IDC XXXX
1950 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-04-07 23:53 | 2019-04-08 11:40 | 29 | 707 | 4067681 | 20503 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines./ Pole fire @ 38830287B00172/ truck ok thru pasture gate in front of house/ angle pole with #2 acsr/ 36 pin, ins, cutout & bracket, possibly pole top ext/ Line fuse @ 38830286000189 open & tagged to DDC// NO GROUNDS PLACED// Released by crew 078H08/ARRIVED RM removing DDC TAGS and placing with mine fuse in at 11:40 please close tic RM sjg
1951 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-05-04 04:28 | 2021-05-04 07:59 | 97 | 211 | 4519611 | 20467 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Failed Cutout at 38830378000098 (Abandoned property) Tap Lifted at 38830378000020 Closed OCR at 38830403000005 at ____Failed Cutout at 38830378000098 (Abandoned property) Tap Lifted at 38830378000020 Closed OCR at 38830403000005 at 0759 same as ticket 4519511 Released by crew 078H03
1952 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-01-24 12:42 | 2015-01-24 18:23 | 60 | 341 | 4958961 | 20460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF, POLE # 179-79, CALLING FOR CREW. WILL NEED FLAGGERS RELEASED BY CREW 077S02 ON @18:23 COD 60// VER/ ADH L3/HFP AJB
1953 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2021-02-22 07:34 | 2021-02-22 15:08 | 45 | 454 | 4214831 | 20430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke @ 37830160000042. Recloser @ 37830160D10116 not open//// Will have to open to make repairs. Opened reclosers @ 13:17. Replaced switches and restored @ 15:08
1954 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-04-12 18:00 | 2016-04-12 18:28 | 729 | 28 | 4086371 | 20412 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | WHILE SWITCHING SOS 3269 REV 26 AN INUSLATOR FAILED IN THE STATION//EMERGENCY OUTAGE REQUIRED TO REPLACE//SEE DOL CASES 649416 & 649458 // AJB
1955 | Hazard | 3303901 | LESLIE | HYDEN | 2008-07-08 11:00 | 2008-07-08 14:25 | 108 | 205 | 64275-1 | 20401 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3303901//SERVICER PATROLLING LINE//COD 108//ISOLATED ON POLE 314-10 AND CLOSED UP TO ISO PT @ 1338//BAD CSP// VER/DBM IDC XXXX
1956 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2012-11-18 12:27 | 2012-11-18 16:55 | 76 | 268 | 4406561 | 20368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPACER CABLE BURN DOWN === NEED 3 MAN LINE CREW AND BIG BUCKET === REPAIRED SPACER CABLE === CLOSED RECLOSER === POWER OK//COD76// VER/DBM IDC XXXX
1957 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-09-10 12:19 | 2018-09-11 09:40 | 37 | 1277 | 4067041 | 20352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Dispatched in accordance with KYPCo Late Night Callout Guidelines.,,CREW REQD TRACK WORK NEED 40-4 POLE IN MUDDY BARN LOT POLE #309-57 D.S.110 XFMER CAN GO BACK NEED NEW LIGHT 150W.CPS Released by crew 078E04//WILL WORK TRANS 38830309000057 TOMORROW THE 11TH// @ ON @ 0940 09/11/18
1958 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-07-25 15:33 | 2012-07-25 16:33 | 339 | 60 | 4827171 | 20340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | I HAVE A LOOP BURNT OPEN ON PHASE B AT THE REGULATOR BANK. WE WILL HAVE TO OPEN STATION BREAKER TO MAKE REPAIRS. CREWS CONTACTED. //ISO POLE 37830072A00082//PHAE B ONLY//COD 339//TIM FROM DDC OPENED BREAKER SUPERVISORY CONTROLLED AND I ISOLATED THE TROUBLE HE CLOSED BREAKER BACK IN AND EVERYTHING IS BACK TO NORMAL. REGULATOR ON POLE 37830072A00082B IS TAGGED AND IN THE ABNORMAL STATUS. TIM MCCOY RELEASED BY CREW 074H10// VER/DBM IDC XXXX
1959 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2010-02-15 18:27 | 2010-02-15 21:05 | 142 | 158 | 58186-1 | 20336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, POLETOP BURNT OFF, POLE# 991-D1-63, CALLED R MARCUM FOR HELP VER/KEP L3/KEP IDC 54 CUSTOMERS IN WV 142 IN KY XXXX
1960 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-02-04 23:43 | 2012-02-05 07:51 | 68 | 488 | 4320481 | 20332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830178000152 40/4 POLE BURNT OFF AT LINE C/O. MANUAL POLE. NEED 4 MAN LINE CREW, R/W CREW MANUAL. REC. OPEN ON POLE 178-166. POLE 37830178A00109 INSTALLED SOLID BLADE, WILL ISOLATE TROUBLE AT THIS POLE. GOING BACK TO REC. TO MAKE LINE HOT UP TO POLE 178-109. LINE ENERGIZED TO POLE 178-109 AT 02:45. VER/ARN IDCC CNT94 XXXX
1961 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-10-31 14:29 | 2008-10-31 16:41 | 154 | 132 | 61186-1 | 20328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301//B PHASE REC OUT AT 1422 COD 154//WILL HAVE TO OPEN OTHER 2 TO MAKE REPAIRS//REPLACING TWO BAD SOLID BLADES ON SITE NOW TCM// OPENED OTHER TWO RECLOSERS AT 1555 TO START REPAIRS// CLOSED ALL 3 RECLOSERS BACK IN AT 16:41 TCM/ IDCC CNT549, TOF1442, PN236 XXXX
1962 | Hazard | 3303902 | LESLIE | WOOTON | 2008-01-17 06:02 | 2008-01-17 12:30 | 59 | 388 | 57278-1 | 20327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3303902//HOT LINE CLAMP CAME LOOSE - WHILE HAD IT OPEN CHANGED CUTOUT// ISOLATION/FAULT - 37830365A00045// 57 CUSTOMERS OUT// OTHER 7 WOULD WERE COUNTED IN THE RECLOSER OUTAGE THAT WAS GENERATED TO ISOLATE THIS TROUBLE/ VER/TOM IDC XXXX
1963 | Whitesburg | 3401301 | FLEMING | NEON | 2014-04-16 06:09 | 2014-04-16 11:45 | 176 | 336 | 4610441 | 20319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 331-232 , I AM ISOLATING ON POLE331-3 , THEN I CAN GO TO THE RECLOSER ON POLE 335-624 AND RESTORE ALL BUT FOUR CUSTOMERS, THIS ALSO ISOLATED POLE 331-207 // C PHASE RECL OUT 176 CUST ON @ 1145 VER/HFP L3/HFP IDC XXXX
1964 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-07-04 02:15 | 2015-07-04 06:41 | 91 | 266 | 4718011 | 20318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWNPOLE#1062-D-39/ "A" PHASE ONLY COD-91/ CLOSED RECL AT 0359 UP TO OPEN SWS 1062-40 RESTORED 24 CUST/ OPENED OTHER 2 PHASES AT 0626 COD-206/ AND CLOSED THEM IN AT 06;41 VER/KEP AJB
1965 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2008-07-11 12:38 | 2008-07-11 13:26 | 423 | 48 | 51211-1 | 20304 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | POLE | CC423//LOVELY/WOLF CREEK OUTAGE ON KY SIDE...NEED INFO FORM KENTUCKY DDC...KENTUCKY REPORTED ROTTEN POLE/// //VER/CRB
1966 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-08-29 08:03 | 2012-08-29 11:41 | 93 | 218 | 4983161 | 20274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | "B" PHASE ONLY COD-93 HAVE BAD RECLOSER ON B PHASE I HAVE ISOLATED AND TAGGED NEEDS TO BE PUT IN THE ABNORMAL DATABASE, I RESTORED POWER AT THIS LOC, AT 1141 MD FILED PHASING WRONG ORIGINALLY PART OF SCHEDULED OUTAGE VER/KEP IDC XXXX
1967 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-05-06 10:20 | 2022-05-06 11:21 | 332 | 61 | 4843631 | 20252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DA //DOL 1203844 // Due to multiple reclosers operations, Had to SCADA Open DA Reclosers at 174-A2-4467 affecting 332 CC // found cutout breaking down on 174-B-60// broke xfm cutout at pole 174-b-60. made repairs. restored power at 11:21//
1968 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2014-12-29 11:10 | 2014-12-29 12:45 | 213 | 95 | 4889311 | 20235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SERVICER OPENING SWITCH 425-A-47, TO REPLACE BROKEN POLE 401-70//COD 213// REPLACED POLE 401-70 BROKEN OPEN AT 11:10 CLOSED AT 12:45// VER/ ADH AJB CCO
1969 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2022-05-16 06:08 | 2022-05-16 09:23 | 123 | 195 | 4894381 | 20232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C Phase Out Originally (54cc)/,recloser 305-10 in @ 8:32,,,solid blade 305-57 (53 COD) in @ 08:58 ,,replaced cutout 305-70 (2 COD) and line fuse restored @ 09:23 ,,,all customers restored complete,recloser 305-10 in @ 8:32,,,solid blade 305-57 in @ 08:58 ,,replaced cutout 305-70 and line fuse restored @ 09:23 ,,,all customers restored complete Released by crew 078S05
1970 | Pikeville | 3403001 | PIKEVILLE | CITY | 2013-08-25 20:27 | 2013-08-26 13:46 | 32 | 1039 | 4706101 | 20214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CLOSED DIP FUSE ON 37830024B30548 TO PAD 37830024B31158// BAD CABLE FROM 1158 TOO 1162// ISOLATED CABLE TO 1162 // PAD 1158 ON AT 22:15// SEND TO T. HALL RELEASED BY CREW 074S05 REPAIRS MADE ON AT 13:46 D SAMMONS VER/CRB L/3 CRB IDCC CNT18, CDC88, STP MISSING, PN1162 XXXX
1971 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-12-16 08:11 | 2016-12-16 10:02 | 182 | 111 | 4199931 | 20202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | @ 0841 PATROLLING CKT ////HOT TAP BURNT OFF@ 0841 PATROLLING CKT //HOT TAP BURNT OFF/INSTALLED A SCREW ON BASKET ALSO NO CREW REQUIRED HOT TAP OFF AT RECLOSER POLE 38830223000229 ON A PHASE 182 CUSTOMER // VER PER BUSINESS OBJECTS VER/HFP L3/HFP AJB
1972 | Paintsville | 3409302 | KENWOOD | AUXIER | 2010-03-05 16:57 | 2010-03-05 20:04 | 108 | 187 | 63232-1 | 20196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 ALUMINUM PRIMARY CONDUCTOR BROKE UP ON HILL. PROB DUE TO DAMAGE FROM PAST. DUTY SUP NOTIFIED - CREW ENROUTE. CREW ON SITE @ 18:25. REPAIRS COMPLETE. REMOVING GROUNDS AND PREPARING TO ENERGIZE LINE. RESTORED ALL CUSTOMERS @ 20:04. SH// COD 108// VER/DBM IDC XXXX
1973 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-11-15 07:50 | 2008-11-15 13:00 | 89 | 310 | 65079-1 | 20195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409401// TOP OF POLE BURN-OFF 103-62 ISOLATED AT 103-165 RESTORED RECLOSERS AT 1035 VER/KEP IDC CHANGED EQUIPMENT FAILED FROM POLE XXXX
1974 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-01-26 13:35 | 2018-01-26 17:01 | 98 | 206 | 4775551 | 20188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | pole37830222D00071 primary broke out of shoe and being held up by hot line clamp ,primary down into netural,manual, need line crew and r/w crew Released by crew 077S04 power restored at 17:01
1975 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-12-23 08:58 | 2022-12-23 19:30 | 60 | 632 | 4307811 | 20165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required///// cut out broke down and burnt top of pole off at pole 18-D-89 got recloses open at pole 18-D-184.. crew will need 2 8ft arms and 2 sets of braces, 3 deadend bells and 2 #4 copper shoes and 1 #2 shoe,1 big guy att,2- 7200 cutouts and arrester and 2T brackets//// will need a 50-class2 pole pole is a AT@T pole,pole has a bank on it and wil need a 10kva and a 25kav transformer 7200//// Released by crew 074S03///Recl 37830018D00184 closed at 1355 - taps lifted at 37830018D00118
1976 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-10-30 17:45 | 2015-10-30 18:36 | 395 | 51 | 4397671 | 20145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 19.9 APPOXILATER IS BROKE ON POLE#1150-118/// WILL HAVE TO OPEN RECLOSER UP @ POLE#1126-27 TO CHANGE APPOXITATERS//// NEED A LINEMAN AND 6 -19.9 APPOX./// OPENED RECLOSER UP @ 17:45 TO MAKE REPAIRS/ ISO 38831126B10027/ COD 395/// REPAIRS MADE AND CLOSED RECLOSER IN @ 18:36 AND RESTORED SERVICE/ VER/BOW // VER TIMES WITH SCADA L3/HFP XXXHFP AJB
1977 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-06-13 18:29 | 2014-06-13 22:44 | 183 | 255 | 4088681 | 20143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN ON POLE # 53-143 WILL PATROL//// CUT OUT BURNT UP ON POLE #53-21 WILL CHANGE /// S RAY & R WORRIX & J GARRETT //RECLOSER IS OPEN ON POLE # 53-143 WILL PATROL//// CUT OUT BURNT UP ON POLE #53-21 WILL CHANGE/ 2 SPANS OF WIRE DOWN UP IN ROUGH HOLLOW I HAVE IT ISOLATED ON POLE 53-21/// CLOSED RECLOSER IN ON POLE 53-143 @ 20:15//MADE MDCRECLOSER IS OPEN ON POLE # 53-143 WILL PATROL//// CUT OUT BURNT UP ON POLE #53-21 WILL CHANGE/ 2 SPANS OF WIRE DOWN UP IN ROUGH HOLLOW I HAVE IT IS VER/CRB AJB
1978 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-06-01 20:12 | 2012-06-02 05:31 | 36 | 559 | 4870471 | 20124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN ON 525-23, PATROLLING LINE RELEASED BY CREW 078S11/RECLOSER BACK IN AROUND 2345/CAME BACK OUT AROUND 1205/CREW PATROLLING LINE AND INSTALLING FAULT FINDERS/VEM/BAD CUTOUT ON POLE 525-210/POLE BURNING/CHANGING CUTOUT AND RE FRAME POLE/FETR 0630/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0531/PLEASE CLOSE TICKET/THANKS/VEM CC 36 VER/SDB IDC XXXX
1979 | Hazard | 3311103 | STINNETT | WENDOVER | 2022-02-24 21:30 | 2022-02-25 00:22 | 117 | 172 | 4541771 | 20124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO OUTAGE TILL RECLOSER 37830459C00235 OPENED//COD 117//ARCOSED CREW TO MAKE REPAIRS @ 2122//insulator failed at pole 435-73. phase laying hot on top of pole. opened rec 459-c-235 at 21:30. need 2 men and big bucketinsulator failed at pole 435-73. phase laying hot on top of pole. opened rec 459-c-235 at 21:30. need 2 men and big bucket.. power restored 00:22 Released by crew 077S10
1980 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-01-16 01:45 | 2009-01-16 08:26 | 53 | 401 | 55451-1 | 20121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3103101// COD-53 // WR# 28092094 // 3 SPANS OF WIRE DOWN - NEED CREW / //CREW REQUIRED TRUCKS OK 40/5 POLE TOP BROKEN OUT3103101// CREW ON SITE/CHANGING POLE/FETR0830/VEM/RELEASING TICKET BAK TO DDC TO DO STEP RESTORATION/VEM RELEASED BY CREW 078H14 VER/KEP L3/KEP AJB
1981 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-07-02 15:24 | 2012-07-04 15:18 | 7 | 2874 | 4227721 | 20118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE 40CL. 4 POLE BURNT OFF NEED C/O,FB BRACKET,2 CLEVIS,2SPOOLS,17.2 DE INSUL.,2/3 TO SPLICE WITH,25 KVA 7200,IS TRUCK APP. FUSE OPEN AT 983-49 // VER/DKG
1982 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-03-08 18:10 | 2008-03-08 21:51 | 91 | 221 | 55440-1 | 20111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409003// FOUND POLE TOP BURNT OFF ON POLE 809-37 CREW IN ROUTE WILL HAVE TO INSTALL POLE TOP EXT. VER/LDA IDCC CDC92 XXXX
1983 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-10-16 17:20 | 2019-10-16 20:41 | 100 | 201 | 4148561 | 20100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 37830144B00300 is broke @ phone cable attachment. will need two line crews to make repairs..will need 50 class 2 pole, 1 clevis with 4 inch spool, 6 angle pins, 6 19.9 insulators, 2 10ft arms, 2 sets braces and 1 guy attachment..//OUTAGE BEGAN @ 1720//cod 100//
1984 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-05-03 20:44 | 2020-05-04 11:30 | 82 | 886 | 4792261 | 20092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | this pole has three line fuse and two transformer cutouts got one line fuse broke need five 7200 cutouts flagmen and big bucket ¦¦ OPENED SWS ON POLE 38831083C20136 @ 1033 (60 CUST)this pole has three line fuse and two transformer cutouts got one line fuse broke need five 7200 cutouts flagmen and big bucket Released by crew 077S05 switches on pole 1083-136 off at 10:44 back on at 10:54 pole 1083-103 off at 10:44 back on at 11:30 Released by crew 077H02
1985 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-06-01 20:51 | 2020-06-02 00:14 | 379 | 203 | 4941791 | 20039 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE CONDUCTOR DOWN BETWEEN POLE 38830809C10148 AND 38830809C10149//COD 52 FROM BEGINNING OF OUTAGE// Opened sw 809-1006 @ 23:45, made repairs and closed sw @ 00:14. sh Released by crew 076S02
1986 | Hazard | 3309003 | JEFF | VIPER | 2015-09-10 08:27 | 2015-09-10 12:12 | 89 | 225 | H4222221 | 20025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C PHASE ONLY OUT THE A & B STILL IN ===COD 89//C PHASE ONLY 1 OUT THEA B STILL IN ===COD 89// CROSSARM BROKE === NEED LINE CREW RELEASED BY CREW 077S03C PHASE ONLY 1 OUT THE A @ B STILL IN ===COD 89//C PHASE ONLY 1 OUT THEA B STILL IN ===COD 89// CROSSARM BROKE === NEED LINE CREW RELEASED BY CREW 077S03 OPENED OTHER PHASES TO REPLACE ARM , 1039C PHASE ONLY 1 OUT THE A @ B STILL IN ===COD 89//C PHASE ONLY 1 OUT THEA B STILL IN ===COD 89// CROSSARM BROKE === VER/CRB L3/HFP XXXHFP A
1987 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2011-04-20 08:08 | 2011-04-20 20:03 | 28 | 715 | 61014-1 | 20020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | STS WR # 39643671 /// CONFIRMED THE SLEMP/DEFEATED CREEK 34KV CB A IS LOCKED OUT// SERVICERS PATROLLING // TRIED BREAKER AT 1107 - CAME BACK OUT// CALLED HAZARD ASSISTANCE == POLE GROUND FELL ON TO PHASE LINE == GOT LAST CUST ON AT 20:03 RELEASED BY CREW 077S03// IDC XXXX
1988 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-02-12 02:18 | 2013-02-12 08:15 | 56 | 357 | 4812071 | 19992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 COPPER PRIMARY PULLED OUT OF SLEEVE ON POLE 38830069B28059 56 CC. NEED THREE MAM PRC CREW--TRUCK TO POLE--WILL NEED FLAGGERS--OPENED LINE FUSE AN INSTALLED TAG FOR DDC ON POLE 38830069B28022 AT 04:37 5 CC. 0724 GAVE RON VIRGIN PERMISSION TO REMOVE DDC TAG AND INSTALL TAG FOR HIS SELF. RESTORED 65T LF @ 08:15//BAD 25KVA XFMR ON PL. 69-8059///REPLACED XFMR BACK ON @ 09:38///VOLT CK OK VER/KEP IDC XXXX
1989 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-07-16 14:41 | 2015-07-17 11:30 | 16 | 1249 | 4894021 | 19984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED LINE FUSE AT POLE355-187 AT 10:15 TO CHANGE CUTOUT ON POLE 355-411 , I CLOSED BACK IN AT 11:30 // CAN CLOSE MWL AJB LCD CNT
1990 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-10-26 14:11 | 2010-10-26 17:53 | 90 | 222 | 64145-1 | 19980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP & STURRIP BURNED IN TWO ON LOAD SIDE OF RECLOSURE ON POLE # 38831077D00001. HAVE CALLED FOR CREW & MATERIAL.CHECK COUST COUNT ONLY PHASE C OUT /// CCC COD-90 VER/HFP L3/HFP IDC XXXX
1991 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-04-30 18:50 | 2014-05-01 01:37 | 49 | 407 | 4653291 | 19943 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE IS OPEN ON 572-221 CHECKING LINEDOWN. PIMARY & NEUTRAL DOWN FROM 572-17 TO 596-92 LINECREW IN ROUTE RELEASED BY CREW 078S11//3 SPANS #6A P & N DOWN///REPAIRED///PWR ON @ 01:37///TBL TKT COMPLETE VER/ARN IDCC CDC88 CHANGED FROM WEATHER UNKNOWN PER DISCUSSION ON WEEKLY CALL XXXX
1992 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-05-24 14:07 | 2020-05-24 14:40 | 603 | 33 | 4896561 | 19899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED GOAB ON POLE 38831083D10006//COD 603//NO OUTAGE TILL OPENED//OPENED @fault 38831083D30013 , phase off insulator, on pole, open GOAB 1083-6 @ 14:07 hrs.fault 1083-13, phase off insulator, on pole, open GOAB 1083-6 @ 14:07 hrs..repaires made, closed GOAB 1083-6 @ 14:40..p.hicks
1993 | Pikeville | 3410602 | E.PRESTON | LANCER | 2015-02-20 01:10 | 2015-02-20 06:59 | 57 | 349 | 4046561 | 19893 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEAD END INSULATOR BROKE ON POLE#38830955C00072 WILL REPLACE.REPAIRS ARE MADE VER/HFP L3/HFP AJB
1994 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-02-04 11:50 | 2013-02-04 13:32 | 195 | 102 | 4789951 | 19890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WIRE HAS COME OFF INSULATOR AND LAYING ON ARM, POLE # 37830303000036, REPAIRED CONDUCTOR//COD 195// VER/DBM IDC XXXX
1995 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-06-29 18:30 | 2008-06-29 20:00 | 220 | 90 | 59573-1 | 19800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE FIRE SERVICER WILL OPEN SB SWS AT POLE 26-0043 APPROX 16 CUSTOMERS WILL BE OUT.HAD TO OPEN 600 AMP SWITCHES ON POLE 49-70, HAD TO REPLACE RIG PIN AND INSULATOR, CROSS ARM. TIME OPEN 18:30 VER/KEP AJB
1996 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2022-03-31 05:08 | 2022-03-31 21:38 | 20 | 990 | 4697631 | 19800 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE | DOL 1194580/T-LINE BEAVER CREEK-MCKINNEY #1 OUTAGE/// Transmission structure broke. Crew will be working to replace. No current ETR due to difficult location. closed 2138
1997 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-11-27 06:30 | 2009-11-27 10:47 | 77 | 257 | 66158-1 | 19789 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3308002// STS CUTOUT BAD ON POLE 1083-1087 AND BURNED POLE OFF GOT CREW COMMING TO REPAIR COD-77 ISO LF 38831083A30288 L3/HFP IDCC TOF0545 XXXX
1998 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-03-16 10:08 | 2008-03-16 14:38 | 140 | 270 | 57654-1 | 19764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201//OPENED RECLOSERS AT 1008 DUE TO POLE 38830426000073 BURNING //ISOLATED AT POLE 426-90 & GROUNDS PLACED//RESTORED RECL @ 1058/ SHOULD HAVE ALL BUT ONE CUSTOMER RESTORED BY 1300/REPAIRS MADE AND LAST CUST RESTORED 1438/VEM //HFP DELETE REST ON THIS ONE SHOULD BE 1058 RESTORED 27, @ 1250 - 112 CUST REST AND LAST CUSTOMER RESTORED AT 1438 AFTER LOOP CLOSED/ RELATED TO 57698-1 VER/HFP IDC XXXX
1999 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-08-18 20:37 | 2010-08-19 00:58 | 86 | 261 | 57896-1 | 19742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830454D26518,,,,,CREW NEEDED,,,TOP OF 45 POLE BURNT OFF. HAD TO OPEN FUSE ON POLE 478-4003,,,, CREW NEEDS 45 POLE 7200 CUTOUT AND BRACKET ,,IS TRUCK ACCESSIBLE.,,,,CREW NEEDED,,,TOP OF 45 POLE BURNT OFF. HAD TO OPEN FUSE ON POLE 478-4003,,,, CREW NEEDS 45 POLE 7200 CUTOUT AND BRACKET ,,IS TRUCK ACCESSIBLE. RELEASED BY CREW 078S02 //VER/GAH IDCC TOF2001 XXXX
2000 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-02-08 22:51 | 2011-02-09 01:00 | 153 | 129 | 55447-1 | 19737 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | WR#38748626,,, C PHASE ONLY SERVICER PATROLLING CKT.WR#38748626,,, C PHASE ONLY, PATROLED LINE AND FOUND NO HAZARDS WR#38748626,,, C PHASE ONLY, REGULATOR FAILED AT 38830351C20288, BYPASSED REGULATOR, PLEASE PUT IN ABNORMALWR#38748626,,, C PHASE ONLY, REGULATOR FAILED AT 38830351C20288, BYPASSED REGULATOR, PLEASE PUT IN ABNORMAL, SWITCHING ORDER SOS 1057 REVISION 13 AT 01:00 VER/PDP IDC XXXX
2001 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-11 08:04 | 2009-06-11 11:05 | 141 | 181 | 57360-1 | 19726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S04BAD CUTOUT ON POLE 46-133, ISOLATED ON POLE 46-7.CLOSED STEP DOWN IN @10:04 MLR STEPS OF REST
2002 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-03-24 21:42 | 2018-03-25 10:51 | 25 | 789 | 4067881 | 19725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad dad end insulator, manual,need line crew and cutout complete with arrester and dead ind insulator19 .9 kv on site working repairs made and power restored at 10:51/ ISO 37830318A00122/ COD 25***only one line fuse on pole 318-122 md done
2003 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-01-25 12:24 | 2022-01-25 17:30 | 114 | 306 | 4403641 | 19680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew required ,,1 span primary down ,,by truck ,,273-47 to 273-48,,,,,cut loop @ 273-44,,,recloser 249-94 back in @ 14:29 Released by crew 078S05 work complete loop made up and power restored @ 17:30 Released by crew 078H31
2004 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-09-04 13:30 | 2014-09-04 13:54 | 819 | 24 | 4463351 | 19656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED CB @ 1330 FOR CREW TO MAKE REPAIRS. CLOSED CB @ 1354 VER/HFP L3/HFP AJB
2005 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-08-03 21:32 | 2012-08-04 18:00 | 16 | 1228 | 4894011 | 19648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE OUT ON 24-B2-666 ISOLATE PAD 1081 TO TRY CABLE CANNOT ISOLATE PAD 1085 FENCE AND GARBAGE AROUND IT FIRST SPAN APPEARS BAD WILL NEED CABLE LOCATED FIRST ISOLATED ON POLE 24-666 NEED 4 MEN AND SUPERVISOR RELEASED BY CREW 074S10 CREWS ONSITE REPAIRS MADE TO URD PRIMARY GOING TO TRY FUSE POWER RESTORED @ 18:00 CABLE WAS FAULTED BETWEEN FUSE POLE 37830024B20666 AND PADMOUNT 37830024B21081//COD 16// VER/DBM IDCC CDC83 XXXX
2006 | Hazard | 3309301 | VICCO | REDFOX | 2008-05-05 08:35 | 2008-05-05 09:12 | 531 | 37 | 57052-1 | 19647 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | 3309301//STATION SERVICER ISOLATING EQUIPMENT THAT FAILED NOW, POTENTIAL TRANSFORMER FAILED. VER/HFP IDC XXXX
2007 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-10-07 11:52 | 2019-10-07 14:33 | 122 | 161 | 4110091 | 19642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN ARRESTOR ON POLE 37830487000056blown arresterblown arrester, cut in clear, could have restored at 14:10 but could not talk to DDC due to no radio communication or cell service
2008 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-05-04 16:11 | 2009-05-04 17:18 | 293 | 67 | 52820-1 | 19631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP FAILED. REPAIR UNDERWAY.//3409301//COD 169//C PHASE ONLY. REPAIRS COMPLETE. CLOSED PH C RECLOSER AT 17:18. SH//VER/CRB IDC LOOKS LIKE PH A NOT C, CHANGED COUNT FROM 169 XXXX
2009 | Hazard | 3302704 | HAZARD | KENMONT | 2020-09-13 07:45 | 2020-09-13 12:38 | 67 | 293 | 4456161 | 19631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Low side fuse open on stepdown pole 296-D4-216, patrolled line and didnt see anything obvious, closed in at 9:02 and it opened back up. A span of primary between poles 296-D4-258 and 296-D4-262 burnt down as a result, truck access #2 wire. Pole 292-216 grounded and tagged to Phillip Hicks. Released by crew 077H20
2010 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-12-02 23:34 | 2014-12-03 04:18 | 69 | 284 | 4828171 | 19596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER AFTER HOURS CALL OUT GUIDE LINES THIS WILL BE CHECKED IN THE MORNING OF 12/03/14 POLE BURNED OFF CREW ENROUTE VER/DKG L3/DKGXXXX TIMES CORRECT LISTENED TO VOICE RECORDER AJB
2011 | Hazard | 3302704 | HAZARD | KENMONT | 2009-01-16 05:56 | 2009-01-16 10:40 | 69 | 284 | 55515-1 | 19596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3302704// 250 KVA STEPDOWN BAD CALLING FOR CREW TO REPLACE IT RELEASED BY CREW 077S04 PLEASE CLOSE ORDER @ 1040 THANKS HFP VER/KEP L3/KEP AJBC ADDED CLEARING DEVICE PHASE A.
2012 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-13 12:15 | 2012-02-13 16:40 | 121 | 265 | H4344401B | 19585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE ON CENTER STEPDOWN TRANSFORMER ON POLE 97-346 IS OPEN. I AM GOING TO CLOSE FUSE BACK IN. 500 KVA STEPDOWN TRANSFORMER IS BAD. STEVIE RAY AND CREW ARE GOING TO BRING ONE AND CHANGE IT OUT.COD-44 ON "B"CENTER PHASE. WE OPENED THE OTHER 2 RECLOSERS ON POLE 97-346 AT 12:15 AND I ALSO HIGH SIDE FUSE ON CENTER STEPDOWN TRANSFORMER ON POLE 97-346 IS OPEN. I AM GOING TO CLOSE FUSE BACK IN. 500 KVA STEPDOWN TRANSFORMER IS BAD. STEVIE RAY AND CREW ARE GOING TO BRING ONE AND CHANGE IT OUT/ IDC XXXX
2013 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-03-15 10:30 | 2011-03-15 12:31 | 162 | 121 | 54446-1 | 19581 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MIDDLE PHASE BURNED DOWN IN CLEAR @ POLE 1065-85 //COD 152 // ISO 38821065B00085 // @ 11:24, CREWS OPENED RECLOSERS ON POLE 1065-275 (INTERRUPTING 156 CUST, SEE H54446-1)// CREWS OPENED SWITCHES ON 1065-D2-287 TO ISOLATE HAZARD @ 11:38 (SEE 54477-1)//REPAIRED DOWN CONDUCTOR// CLOSED UNDER ARM BLADES ON POLE # 1065-D2-287 @12:24........CLOSED RECLOSER ON POLE# 1065-B-275 @12:31, THIS SHOULD RESTORE ALL CUST.// VER/DBM IDC ADDED 10 FOR POSSIBLE MISSMAPPED CUSTOMERS XXXX
2014 | South Williamson | 3411401 | DEWEY | INEZ | 2011-11-13 14:05 | 2011-11-13 17:15 | 103 | 190 | 4072061 | 19570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | PATROLLING. FOUND NO PROBLEMS ON LINE. RECLOSER HANDLE WAS IN THE CLOSED POSITION WHEN I ARRIVED BUT HAD NO VOLTAGE COMING OUT. OPERATED HANDLE AND IT STILL WOULDNT CLOSE. SMACKED BOTTOM OF CAN WITH SHOTGUN STICK AND HEARD IT PICK UP. CLOSED SINCE 17:15 SO I SUSPECT RECLOSER IS GOING BAD. PLEASE SEND TO FREEMAN TO WRITE JOB TO CHANGE ASAP. SH ///VER/CRB IDC XXXX
2015 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-02-12 15:00 | 2013-02-12 15:09 | 2174 | 9 | 4814311 | 19566 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TO MAKE ADJUSTMENTS ON MOBILE TRANSFORMER OFF @ 1500 ON @ 1509 VER/ARN IDCC CCSCO XXXX
2016 | Hazard | 3302704 | HAZARD | KENMONT | 2008-08-26 13:00 | 2008-08-26 15:40 | 564 | 160 | 55070-1 | 19554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP 3302704// HAD TO OPEN GOAB ON POLE 296C2-510 (OFF @ 1300 BACK ON @ 1306)TO ALLOW LOOPS TO BE CUT @ POLE 296D4-220 ISOLATING BROKE CROSS ARM @POLE 135. IDC XXXX
2017 | Whitesburg | 3309302 | VICCO | JEFF | 2013-09-12 17:07 | 2013-09-13 00:12 | 46 | 425 | 4845691 | 19550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN AT POLE 373-189, PATROLLING. BAD C/O ON POLE 373-77, WILL BE CHANGING. CHANGED C/O, CLOSED REC. BACK IN AT 0012 VER/CRB L/3 CRB IDC XXXX
2018 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-12-24 18:32 | 2011-12-24 21:38 | 105 | 186 | 4200461 | 19530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE OUT 105 CUST /// HAVE WIRE DOWN @ 37830047D00006CENTER CONDUCTOR AT RECLOSER POLE 47-6 ON LOAD SIDE BURNED DOWN. IT BURNED INTO AT BELL. OPENED 2 ADDITIONAL RECLOSERS TO MAKE REPAIRS OPEN AT 2120 - CLOSED ALL 3 AT 2138 // A=102, B=94, C=80, AB=3 VER/TOM L3/TOM IDC XXXX
2019 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-05-05 22:33 | 2016-05-06 12:42 | 23 | 849 | 4179871 | 19527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATERS ON POLE37830563000018 WILL CHANGE OUT 5-6-2016 RELEASED BY CREW 077S03 COD-23 ISO LF 37830563000008 AJB
2020 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-09-13 18:08 | 2010-09-13 18:49 | 476 | 41 | 66185-1 | 19516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEND RECLOSERS @ 1808 IN ORDER TO MAKE REPAIRS RELATED TO ORDER 66058-1//CLOSED BACK @ 1849//COD 476 // WR# 36859196 //CHANGED 9 FOOT ARM AND THREE 300AMP SOLID BLADE CUTOUTS/WORK COMPLETE/PLEASE CLOSE TICKET/THANKS/VEM// VER/DBM IDC XXXX
2021 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-04-08 13:19 | 2008-04-08 13:58 | 500 | 39 | 65206-1 | 19500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | APPEARS ARRESTOR HAS FAULTED,WILL CLEAR IT UP THEN CLOSE RECLOSER BACK INARRESTOR FAULTED,CLEARED IT UP,THEN CLOSED RECLOSER ON POLE 52-211,ALL OK AFTERWARDS VER/HFP IDC XXXX
2022 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-08-31 16:17 | 2021-08-31 21:36 | 61 | 319 | 4186251 | 19459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1 span #4copper down at 38830355000006 the primery is hot up to this pole will need flaggers and manual tree crew Released by crew 078S12 crew on site FETR 21:30 LRM going to open at p379-2 repaired and restored @2136
2023 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-07-18 14:36 | 2022-07-18 16:00 | 294 | 84 | 4514501 | 19458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. is open will patrol///BROKEN CUTOUT ON POLE 37830189D00003, GOING BACK TO CLOSE RECLOSER 37830190C30459//CLOSED REC @ 1542//REC. is open will patrol/// Found and isolated broken xfmr cutout on 189-D-3 restoring REC. @ 15:42/// Replaced cutout and restored xfmr @16:00 Released by crew 074H06 LR- The 1st All out call came in at 14:36
2024 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-11-27 13:45 | 2012-11-27 18:27 | 69 | 282 | 4425701 | 19458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER ON 523-383 IS OPEN PATROLLING LINE. TRUCK OK CAN BE LOWERED. RELEASED BY CREW 078S11CREW ON SITE PRT//REPAIRS COMPLETE POWER RESTORED AT 18:27 CLOSE TKT PRT// ///VER/CRB L/3 CRB IDC XXXX
2025 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-03-21 17:02 | 2010-03-21 18:10 | 286 | 68 | 52267-1 | 19448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LA ON 1130-84 TOOK 1 RECL OUT,CLEARED ARRESTOR,CLOSED RECL ON 26-2,RESTORED ALL CUSTS//COD 281// VER/DBM IDC I ADDED 5 MISMAPPED CUSTOMERS XXXX
2026 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-01-30 07:28 | 2008-01-30 10:10 | 120 | 162 | 61810-1 | 19440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR BROKE AT 38830327B00023 AND SET POLE ON FIRE, REPAIRS HAVE BEEN MADE AND FIRE IS OUT, NEED TECH TO CHECK POLE, OK FOR NOW VER/ARN IDC XXXX
2027 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-04-28 08:58 | 2013-04-28 14:35 | 63 | 337 | 4053291 | 19431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830376000026, THIS IS A 45 POLE WITH NO TELEPHONE, SHOULD BE ABLE TO REACH AND LOWER WITH TRACK BUCKET, DOUBLE DEAD END #4 COPPER WITH XFMR, GUY, AND SERVICE DROP. ISOLATED TAGGED AND GROUNDED TO B FRALEY AT 376-13, 4A COPPER NOT #4. CLOSED REC AT 10:50 RELEASED BY CREW 078S05 ///VER/CRB L/3 CRB IDCC CNT110, TON STEP ONE XXXX
2028 | Hazard | 3302704 | HAZARD | KENMONT | 2016-10-21 03:03 | 2016-10-21 09:47 | 48 | 404 | 4035291 | 19392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK AT START TIME 10/21/16.STIRRUP BURT OFF OF LOW SIDE OF STEP DOWN.P.HICKS..REPLACED STIRRUP AND HOT LINE CLAMP..P.HICKS // LEFT HAND PHASE OR C PHASE ONLY PHASE OUT 48 CUST COD-58 ISO @ 37830296C21297 VER/HFP L3/HFP AJB
2029 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-02-19 11:00 | 2014-02-19 11:30 | 646 | 30 | 4400651 | 19380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TONY OPENING RECLOSERS TO CLEAR UP FAILED CUTOUTS ON XMER BANK OPENED @1100 CLOSED @1130 VER/SEF AJB
2030 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-08-20 08:06 | 2014-08-20 12:02 | 82 | 236 | 4387751 | 19352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 1056-29,BAD EPOXILATOR INSULATOR,ARE GOING TO REPLACE ALL.WILL TAKE OUTAGE WHEN READY TO REPLACE//APHASE RECL OUT AT 1056-323 BEL MO OF JOES CR///////MADE REPAIRS AND RESTORED RELEASED BY CREW 074S06// 1056-323 HAD 1 RECLOSER OPEN// OPENED OTHER 2 REC 10:24 DKG THESE COMENTS BELONG ON ORDER FOR RECLOSER THAT WAS OUT ON POLE 323 AJBC CNT216 INLT PH A OUT. SEE 4388271 FOR PH B AND C OUTAGE. SOME CUST MAY BE INCOR TIED. TOF07:44 INLT CUST CALLS REPORT TROUBLE ONLY. SEE OTHER ORDER FOR CUST CALLS.
2031 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-01-06 14:29 | 2014-01-06 17:30 | 139 | 181 | 4238361 | 19351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICER OPENED GOAB IN ORDER TO ISOLATE DOWNED HENDRIX CABLE (SEE ORDER 4238021)//COD 139//THIS INTERRUPTED 39 ADDTL C PHASE/3 PHASE CUST AS WELL AS 100 CUST ON PHASES A & B// VER/DBM L3/HFP IDCC FEC57 XXXX
2032 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2009-10-29 13:04 | 2009-10-29 13:55 | 379 | 51 | 50083-1 | 19329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP CREW HAD TO OPEN SECTIONALIZER TO MAKE EMERGENCY REPAIRS TO LOOP THAT IS ALMOST BROKEN INTO// OFF AT 13:04 ON AT 13:55 D SAMMONS COD-379 L3/HFP IDC XXXX
2033 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-24 13:10 | 2011-06-24 16:29 | 103 | 199 | H4406981 | 19327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN ON POLE 140-C-132. POLE IS IN HOLLOW BELOW MCCARTYS. NO TRUCK. SGM. RELEASED BY CREW 078E01// A PHASE//LMR/ WILL HAVE TO TAKE OUTAGE TO REPAIR J. HEMLEPP/ WILL OPEN 3 STEPDOWNS @ 13:10116-6001/116-707/116-708 TO MAKE REPAIRS.OPEN @13:10 A&B PHASE CLOSED//@ 15:50 C PHASE WOULD NOT HOLD COD 73 IDC XXXX
2034 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-06-01 22:05 | 2011-06-01 22:42 | 522 | 37 | 4221641 | 19314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER OPENED RECLOSER TO SAFELY REPAIR HOTTAPS THAT WERE ARCING/HAD FIRE DEPT TO CALL ME AND SAID WE HAD A POLE ARCHING, WHEN I ARRIVED I FOUND A HOT TAP TO BE ARCHING ON A 3 PHASE RECLOSER POLE NUMBER 1073-2061, HAD TO OPEN UP RECLSOER AT 2205 AND CLOSED THEM BACK AFTER I MADE REPAIRS AT 2242, VER/KEP IDC XXXX
2035 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-03-14 22:40 | 2013-03-15 02:27 | 85 | 227 | 4906841 | 19295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN AS PER SERVICER ON POLE 279-12 // ISO 38830279000012 // COD 85 // CREW REQUIRED // 6 A COPPER . RELEASED BY CREW 078H04/CREW ON SITE/WIRE DOWN DIFFICULT LOCATION/FETR 0345/VEM/6ACU FAILED AT SHOE/NOTE TO MAPPING INSTALLED SOLID BLADE CUTOUT ON POLE#279-12/ALL CUST RESTORED 02227/PLEASE CLOSE TICKET/THANKS/VEM IDCC PN10 XXXX
2036 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-03-01 20:43 | 2018-03-02 02:04 | 111 | 321 | 4901221 | 19291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer power is still out//SERVICER CONFIRMS C PHASE STEP-DOWN FUSE IS OUT ON POLE 37820217C00361 //COD 35//called customer power is still out//// bad 500 kva step down on c phase @ pole #217-361/ open rec A&B-37820217C00395 @00:18 76 cust closed at 02:04am
2037 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2008-10-08 10:45 | 2008-10-08 16:20 | 60 | 335 | 54248-1 | 19284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY A PHASE OUT ON POLE37830115000055 // RECL ON THIS POLE BYPASSED DUE TO EQUIPMENT TROUBLE//100T FUSE OUT ON POLE 115-55. I WILL BE LOOKING OVER LINE. SOLID BLADE CUTOUT ON POLE 91A56 IS BROKEN.100T FUSE OUT ON POLE 115-55. I WILL BE LOOKING OVER LINE. SOLID BLADE CUTOUT ON POLE 91A56 IS BROKEN. I OPENED SOLID BLADE ON POLE 91A65. I WILL TRY TO PICK UP TO THIS OPEN POINT. CLOSED IN SOLID BLADE ON POLE 91A56. EVERYTHANG OK//3403202//A PHASE ONLY COD 55//VER/CRB IDC ADDED 5 CUSTOMERS FOR MISMAPPED XXXX
2038 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-06-13 14:31 | 2012-06-13 15:45 | 423 | 74 | H4912111 | 19266 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONN/CLAMP | 2 CC & LOUISA STA REST AT1505....... 460 CC REST AT 1511.....139 CC REST AT 1545 ------------------------ VER/SDB IDC XXXX
2039 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-11-05 12:58 | 2010-11-05 13:41 | 448 | 43 | 53197-1 | 19264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OPENED STATION BREAKER TO REPLACE POLE 171-58 // //VER/GAH IDC XXXX
2040 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-06-13 14:21 | 2012-06-13 15:05 | 437 | 44 | 4911951 | 19228 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | REGULATOR | ONE PHASE ON BUSSEYVILLE - LOUISA CIRC OUT ..MANUALLY INTERRUPTED LOUISA STATION AT 1431 AND RESTORED AT 1505 IDC XXXX
2041 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-01-06 23:35 | 2022-01-07 12:24 | 25 | 769 | 4317591 | 19225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | A phase fuse out on 1126-C3-958 on arrival, cross arm broke on pole 1102-131, opened B and C phase on 1126-C3-958 @ 9:50, this crosses US 23, Beauford Napier is coming to make repairs, need 2 8ft arms, 3 dead end assemblies, 3 7200 XCO and arrestors, Switches on pole 1126-C3-958 tagged to Beauford Napier Released by crew 074S09
2042 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-06-24 | 2017-06-24 11:48 | 27 | 708 | 4031011 | 19116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WIRE DOWN IN FIELD--TO PHILLIP HICKS RELEASED BY CREW 077S06..OPEN LOOP ON POLE 171-47. ALL POWER RESTORED @ 11:48 HRS -- CAN CLOSE MWL 37830148000042 37830171000047 VER/AWD SJG CDC88
2043 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-03-24 14:15 | 2018-03-25 06:27 | 58 | 972 | 4048301 | 19116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TAGGED TO KYDDC/ Recloser open on 644-14, patrolled line and got LIMB off at 668-26, also have #2 alum dn fm 644-40to41, no grounds installed, tagged to ddc at fuse pl 668-28///recl 644-14 closed at 1657 line crew req
2044 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-04-02 22:05 | 2016-04-03 10:20 | 26 | 735 | H4029921 | 19110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER LOOSE ON LOAD SIDE OF STEP DOWN TRANSFORMER PHASE A, OPENED B & C PHASES AT 10:05 FOR REPAIRS , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 RESTORED 1020 VER/KEP L3/HFP XXXHFP AJB
2045 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-01-30 08:24 | 2013-01-30 09:15 | 374 | 51 | 4753921 | 19074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECL OUT ON 247-1354 //BAD CUTOUT ON CAP BANK AT POLE 37830272A11136BAD CUTOUT ON CAP BANK AT POLE 37830272A11136 RESTORED AT 09:15 COD-374 ISO OCR 37830247C31354 VER/HFP L3/HFP IDC XXXX
2046 | Hazard | 3303901 | LESLIE | HYDEN | 2012-07-17 15:12 | 2012-07-17 16:45 | 205 | 93 | 4749921 | 19065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 CUTOUT @267-130 COD-205 ISO OCR 37830316000099 VER/HFP L3/HFP IDC XXXX
2047 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2021-07-13 14:36 | 2021-07-13 16:45 | 421 | 129 | 4906861 | 19057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL1131563/ bad cutout on pole 39831123B00597/ line fuse open on pole 39831123B00271/ closed intellirupter 39831123B28178 @ 1514 restored 372 customer/ lifted hot tap on 39831123B00435 and tagged to Bryan Ramey/ closed line fuse 39831123B00271 @ 1535 restored 20cc///Complete BR/ all power restored @1645
2048 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-08-25 09:44 | 2012-08-25 13:45 | 125 | 241 | 4970901 | 19049 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE "A" ONLY IS OPEN//COD 125//CREW REQUIRED TRUCKS OK/BAD CONNECTION ON RECLOSER LOAD SIT BASKET /WIRE DOWN ON 351-57/#2 ALUM AND #4 COPPER. TAP LIFTED AT POLE 351-57 --- SDB / 1132 / RECL AT POLE 290 CLOSED. 78 CC RESTORED.//// VER/DBM IDC XXXX
2049 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-04-25 03:23 | 2010-04-25 12:33 | 40 | 550 | 50616-1 | 19036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | STS WR # 34818581 // POSSIBLE FUSE OUT ON POLE 37830374D00040 FEEDING ADAMS BRANCH OFF OF HWY 7 SOUTH // ENTERED MD...HFP COD-40 VER/HFP L3/HFP IDCC PN333 XXXX
2050 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-08-07 13:53 | 2021-08-07 17:57 | 78 | 244 | 4015441 | 19032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RECLOSER OPEN ON POLE 37830204000175//COD 78//PATROLLING LINE// tie wire broke on pole 204:15 and wire was laying on pin ::made repairs and restored power at 17:57
2051 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2015-10-21 07:21 | 2015-10-21 09:45 | 132 | 144 | 4365481 | 19008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | A PHAE RECLOSER OPEN ON POLE 37830296D11616//MADE MDC TO SHOW RECLOSER//CENTER PHASE BURNED OFF RECLOSR === BYPASSED RECLOSER ==== POWER OK ==== RECLOSER NEEDS REPLACED ==TALKED TO MIKE LEWIS ABOUT RECLOSER ==== TAGGED RECLOSER FOR DDC === COD 132// VER/CRB L3/HFP XXXHFP AJB
2052 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-08-06 12:45 | 2022-08-06 14:50 | 152 | 125 | 4692031 | 19000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | change loop insulator and replaced guy wire
2053 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-07-02 12:01 | 2015-07-02 19:53 | 44 | 472 | 4709331 | 18968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE OPEN ON 847-27 WIRE DWN ON POLE 866B20 OPENED CUROUT DOOR ON 866B83 AT 17:10 AND REFUSED DOOR AT 842-27 AT 17:23 RESTORING POWER TO CUSTOMERS UP TO 866B83 REPAIRED WIRE CLOSED SOLID DOOR CUTOUT AT POLE 866B83 AT 19:53 THIS SHOULD PICK UP REMAINING CUSTOMERS// VER/ ADH AJB
2054 | South Williamson | 3411401 | DEWEY | INEZ | 2019-02-08 00:13 | 2019-02-08 12:22 | 26 | 729 | 4768521 | 18954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /Line fuse blown 769-C-39 patrolling. BAD CUTOUT ON POLE 38820769C00044 HELD PER KPCO CALLOUT GUIDELINES//Line fuse blown 769-C-39 patrolling.Line fuse cutout has failed on pole 769-C-44 I will replace.Made repairs and closed fuse @ 12:22 L3/HFP
2055 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-12-11 21:57 | 2018-12-11 23:54 | 162 | 117 | 4555761 | 18954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | load side stirrup burnt off recloser 1024-211,,,replaced stirrup and hot line clamp ,,all power restored @ 23:54 complete L3/HFP
2056 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-05-16 17:12 | 2019-05-17 14:50 | 101 | 1298 | 4278381 | 18954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | recl on 144-B1-535 open C phase fault..patrolling line.a phase riser feeding pad mount trans out on 144-434.closed rec on 144-B1-535 in at 20;08 and it stayed.bad urd trans OPENDED LINE FUSE 37830144B00434 @ 1126recl on 37830144B10535 .a phase riser feeding pad mount trans out on 144-434.closed rec on 144-B1-535 in at 20;08 and it stayed.bad ur
2057 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-04-23 12:20 | 2015-04-23 14:12 | 169 | 112 | 4358771 | 18928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED OFF .MIDDLE RECLOSER.875-541..MAY NEED STIRRUP ALSO.NEED BIG BUCKET../CENTER PHASE OUT, OTHER 2 IN// VER/ ADH L3/HFP XXX AJB
2058 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-07-17 00:51 | 2011-07-17 03:58 | 101 | 187 | 4554681 | 18887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED B PHASE REC ON 1125-772// WIRE DOWN @ 1125-190 0315 OPENED -A-C RELOSERS TO MAKE REPAIRS./REPAIRED WIRE// POWER RESTORED 190 CC DUP FOR REST. VER/PDP L3/DKG IDC XXXX
2059 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-10-20 21:50 | 2018-10-21 11:31 | 23 | 821 | 4278791 | 18883 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Load side riser on stepdown was broke, all repaires made apr at 1131 close ticket
2060 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-11-13 12:29 | 2008-11-13 13:33 | 295 | 64 | H64373-1 | 18880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303903// CUTOUT WENT BAD BURNING POLE INTO, CALLED FOR CREW TO CHANGE OUT RELEASED BY CREW 077S01// HAD TO OPEN RELOSER TO SAFELY TRANSFER CONDUCTORS TO NEW POLE// MAFC ADDED OUTAGE FOR RECLOSER SEE TT H64373-1
2061 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-10-09 03:25 | 2015-10-09 06:48 | 93 | 203 | 4329931 | 18879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, FOUND BAD CUTOUT ON POLE 220-31, CUT IN CLEAR, ALL POWER RESTORED, CUTOUT WAS ON INACTIVE XFMR VER/KEP L3/HFP XXXHFP AJB
2062 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-10-31 07:34 | 2009-10-31 10:18 | 115 | 164 | 53411-1 | 18860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302//"C" PHASE RECLOSER OPEN ONLY COD 108//3307302//CONFIRMED C PHASE ONLY IS OUT PATROLLING LINE/FOUND BAD 7200 15 KV CUTOUT ON POLE 37830151000102//CLEARED CUTOUT AND CLOSED RECLOSER AT 10:18 NOTE C PHASE ONLY WAS OUTAGED VER/KEP L3/KEP IDC ADDED SOME MISSMAPPED CUSTOMERS CHANGED COUNT FROM 108 XXXX
2063 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-03-18 18:02 | 2021-03-18 22:10 | 76 | 248 | 4349411 | 18848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 37830411000219. power restored 22:10/ ISO 37830411C30385/ COD 76
2064 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-05-06 21:39 | 2016-05-07 01:18 | 183 | 219 | 4183691 | 18837 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER IS NEXT TO POLE 247-696//. RECLOSER OUT ON POLE 247-1788 , HOT LINE CLAMP BURNED OF @ POLE 247B-492 . OPENED RECLOSERS ON POLE 247B-1740 & 247B-635 . COLSED RECLOSER ON POLE247B-1788 @ 23:20 . CLOSED RECLOSERS ON POLES 247B-1740 & 247B-635 @ 01:18 , ALL POWER BACK ON . RELEASED BY CREW 075H04 VER/KEP AJB
2065 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-03-13 15:03 | 2009-03-13 15:36 | 569 | 33 | 58184-1 | 18777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BREAKER OPENED VIA SCADA AT 1501 THIS HAS LOUISA STATION OUT DKG/BAD CUTOUT ON POLE 477-262 // VER/TOM L3/TOM IDC XXXX
2066 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-07-16 00:12 | 2014-07-16 07:09 | 45 | 417 | 4252061 | 18765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WILL WORK DURING NORMAL WORK HOURS,PRIMARY DOWN FROM POLE 352-16 TO POLE 352-18 NEED LINE CREW TO REPAIR NO TRUCK,RECLOSER @ POLE 351-76 ISO & TAG TO DDC RELEASED BY CREW 078S05/CREW ON SITE/FETR0730/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST/0709/PLEASE CLOSE TICKET/THANKS/VEM AJB
2067 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2017-12-24 21:18 | 2017-12-25 15:41 | 17 | 1103 | 4672831 | 18751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Recloser is open with a fault on C phase, patrolling the line. Tried recloser, seen flash near the top of the mountain. Need utv to try and get to the line from old road at Dix Knob. Released by crew 079S02// Top of pole is burnt off 7-C-102 can lower everything and make repairs. Grnds 7-5, 7-111/ Released by crew 074H10
2068 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-08-19 16:33 | 2018-08-19 19:54 | 93 | 201 | 4974061 | 18693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | inline switch burnt down off rec. pole 238-239..this feeds priemer elkhorn prep plant.will need flaging crew and line crew to make repairs..isolated rec. here and closed back in @ rec. pole 214-44.//OCR FAILED AFTER TAKING NUMEROUS HITS FROM PRIMARY METERING// L3/HFP
2069 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-10-19 15:39 | 2022-10-19 21:18 | 55 | 339 | 4044501 | 18645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | looks like wire pulled out of sleeve, primarystill hot to pole 1040-38, primary conductor only 6 a copper Released by crew 077S07 Possibly related to 4044501
2070 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-07-17 02:08 | 2011-07-17 17:40 | 20 | 932 | 4554821 | 18640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 0235 ETA.---SEND TO B FRALEY RELEASED BY CREW 078S07 VER/ARN IDC XXXX
2071 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-07-05 21:36 | 2021-07-05 23:43 | 147 | 127 | 4859261 | 18631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire down @ 333-7 to 333-8 one phase A phase recl only 140 customers . opened solid blades on pole 332-D-139 isolating trouble. recloser made back hot up to pole 332-D-139 @ 23:05. closed solid blades on pole 332-D-139 restoring power @ 23:43 Released by crew 077S11
2072 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-11-02 17:25 | 2014-11-02 23:10 | 54 | 345 | 4693621 | 18630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ON 319-46, WILL BE OPENING RECLOSER 319-34 TO ISOLATE AND MAKE REPAIRS// OPENED @ 17:25 . NO POWER OUT WHEN ARRIVED . WILL NEED 3 MAN LINE CREW . 45 POLE , CUTOUT & TBRACKET , ANGKE SHOE & INSULATOR , AJBC TOF16:02 PER COMM AND CUST CALLS. INLT CUST CALLS WERE TO REPORT TROUBLE ONLY.
2073 | Hazard | 3303902 | LESLIE | WOOTON | 2010-12-01 02:15 | 2010-12-01 14:00 | 43 | 705 | 61639-1 | 18615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH REGULAR START TIMEWILL DISPATCH REGULAR WORK TIMEWILL DISPATCH REGULAR START TIMEWILL DISPATCH REGULAR WORK TIME BAD CUTOUT @ 510-61 CUT IN THE CLEAR RESTORED POWER @ 0900 NEED CREW RE RELEASED BY CREW 077S01//// REPLACED C/O POWER RESTORED. POWER ON 14:00//VER/CRB IDC XXXX
2074 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-06-25 19:16 | 2008-06-26 04:40 | 33 | 564 | 54399-1 | 18612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3MAN CREW 4 COPPER PRIMARY TRUCKS OK RELEASED BY CREW 078S11//6A PRIMARY DOWN NO TRUCK TO TAKE OFF POLE REPLACED BAD 6A SLEEVE AND RESAGGED CONDUCTOR.P R TOLLIVER////FOUND ANOTHER SPAN OF PRIMARY AND NEUTRAL DOWN///AT POLE 551-30 BAD 6A SLEEVE P R TOLLIVER VER/ARN AJBC LOC#38830552A00556
2075 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2018-04-15 18:47 | 2018-04-15 22:05 | 94 | 198 | 4231301 | 18612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Reclosure on pole 39831147D10149 open.patrolling Arrestor blown and transformer fuse blown at 39831147D30806. Cut in clear. Reclosure back in at 22:05 L3/HFP
2076 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-09-10 13:23 | 2018-09-10 14:25 | 300 | 62 | 4077021 | 18600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser open on pole#190-459 will patroll/// Cutout broke on pole#190-122 will make repairs/// Replaced bad cutout and closed recloser back in @ 14:25 and restored service
2077 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-08-26 19:12 | 2021-08-26 22:34 | 92 | 202 | 4159171 | 18584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | hot line clamp is burned off stirrup on stepdown, got clamp replaced and power restored 2234//cod 92 LR- Phase A is where most of the calls came from
2078 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2017-10-01 00:32 | 2017-10-01 03:15 | 114 | 163 | 4402201 | 18582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 77-34 SECETIONAL POLE HAS STIRRUP BURNT OFF77-34 SECETIONAL POLE HAS STIRRUP BURNT OFF-REPLACED CLAMP AND STIRRUP-SEND COPY TO MIKE LEWIS MAY TALK ABOUT RECLOSER HERE---JIM/// VER/DKM L3/HFP XXXHFP ACB
2079 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-08-12 16:19 | 2015-08-12 18:22 | 151 | 123 | H4128531 | 18573 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSS ARMS BROKE ON POLE 37830223C00156 === CALLED FOR LINE CREW AND ROW CREW/ A PHASE ORIGINALLY OPEN OTHER TWO PHASES @CROSS ARMS BROKE ON POLE 37830223C00156 === CALLED FOR LINE CREW AND ROW CREW ==== OPEN BAND C PHASE AT 16:19 === MADE REPAIRES ALL POWER ON AT/FIX IT IN HOIS/ DUP OF 4128531 FOR B&C PHASE OUTAGE VER/HFP L3/HFP AJB
2080 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-10-27 01:31 | 2008-10-27 06:38 | 61 | 307 | 59326-1 | 18535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400301- FUSE OUT ON POLE 1124-267 SERVICER OPENED SB ( NOT ON MAP ) ON POLE 1124-D-51 TO SECTIONALIZE. CLOSED FUSE ON 267 AT. 0638 //VER/GAH MD SUBMITTED.REPAIRED PRIMARY & RESTORED POWER IDC CHANGED FROM UNKNOWN XXXX
2081 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-05-11 03:34 | 2016-05-11 11:06 | 41 | 452 | 4196261 | 18532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK START OF SHIFT ON 5/11/16 WILL BE CHECKED AT START OF WORK ON 05/11/16 WILL WORK START TIME ON 05/11/16WILL WORK START OF SHIFT ON 5/11/16 WILL BE CHECKED AT START OF WORK ON 05/11/16 WILL WORK START TIME ON 05/11/16 RECLOSER IS OPEN AT POLE 38821110A00054. PATROLLING THE LINE.WILL WORK START OF SHIFT ON 5/11/16 WILL BE CHECKED AT START OF WORK ON 05/11/16 WILL WORK START TIME ON 05/11/16 RECLOSER IS OPEN AT POLE 38821110A00054. PATROLLING THE LINE. REPLACED BAD TRANSFORMER CUT AJB
2082 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2017-04-29 18:00 | 2017-04-30 01:10 | 43 | 430 | 4695791 | 18490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE STEPDOWN OUT @ 37830517000085 (48 TOTAL CUSTOMERS : 5 SLEMP DEFEATED CREEK, 43 DAISY LEATHERWOOD) STEPDOWN FUSE BLOWN ON POLE 517-85, REFUSED AND IT BLOWED AGAIN, WILL NEED 500KVA STEPDOWN,//CREW ON SITE - FETR 0400//TOM POWER RESTORED AT 13:10 RELEASED BY CREW 075H03 AJB
2083 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2020-11-15 14:20 | 2020-11-16 12:20 | 14 | 1320 | 4685001 | 18480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | line fuse 329-40 open,,BROKE AEP POLE 329-98,,,35-5,,,WILL NEED TRACK MACHINE Released by crew 078S05// repaired and restored @1220
2084 | Hazard | 3303901 | LESLIE | HYDEN | 2010-04-17 13:13 | 2010-04-17 20:04 | 107 | 411 | 64475-1 | 18477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830412C00446 REC. IS OPEN, PATROLLING LINES///// 412-60 WE HAVE TOP OF POLE BURNT OFF NEED CHANGED 40 CL 4. ISOLATED ON POLE 37830412C00274. TOOK HOT TAP OFF THAT GOES TO FOX LN AND OPENED XFMR. CLOSED REC. AT 15:49 GOT ALL BACK ON EXCEPT THE ONES THAT WERE ISOLATED. HICKMAN TO BRING CREW. RELEASED BY CREW 077S08 RESTORED REST OF POWER AT 2004 CREW O77H01//COD 107 IDC XXXX
2085 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-02-05 06:42 | 2009-02-05 12:00 | 58 | 318 | 55845-1 | 18444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE SPAN OF PRIMARY AND TWO SPANS OF NEUTRAL DOWN AT POLE 621-42 SHOULD BE ABLE TO PUT WIRE UP WITH BUCKET TRUCK ,,,,#6 STRANDED COPPER//3007904//,,,ONE SPAN OF PRIMARY AND TWO SPANS OF NEUTRAL DOWN AT POLE 621-42 SHOULD BE ABLE TO PUT WIRE UP WITH BUCKET TRUCK ,,,,#6 STRANDED COPPER RELEASED BY CREW 078S02//SAME AS 55791 ALL POWER RESTORED AT 1200 VER/KEP L3/KEP IDC XXXX
2086 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-06-05 06:33 | 2014-06-05 11:00 | 123 | 267 | 4982581 | 18441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE RECLOSER OPEN ON POLE 419-366, BAD CUTOUT ON POLE 420-259 BURNT TOP OF POLE OFF, ISOLATED ON POLE 420-258.CLOSED RECLOSER IN AT 09:00 RESTORING POWER . RELEASED BY CREW 077S11 VER/CRB AJB PH B.
2087 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-05-15 00:03 | 2009-05-15 01:40 | 190 | 97 | 56080-1 | 18430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308002// HAD TO OPEN RECLOSER TO SAFELY REPLACE BROKEN CROSS ARMS IDC XXXX
2088 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-10-03 07:54 | 2015-10-03 15:00 | 48 | 426 | 4307751 | 18424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1037-D-96 IS BURNED OFF AT THE TOP DUE TO BAD CUTOUT. LINE IS ISOLATED AT 1037-D-44. 811 HAS BEEN CONTACTED, TICKET NUMBER IS 1510030017. 811 SAID IT WILL BE ONE TO THREE HRS FROM 09:30 TILL SOMEONE IS HERE. RELEASED BY CREW 079S02..ENERGIZED PRIMARY ON POLE 1037D43 AT 14:14. CLOSED TRANSFORMER ON POLE 1037D96 AT 15:00. ALL CUSTOMERS RESTORED// VER/ ADH // VER TIMES PER VOICE RECORDER = L3/HFP HFPC STP AJB
2089 | South Williamson | 3200302 | BELFRY | TOLER | 2014-11-01 14:15 | 2014-11-01 18:11 | 78 | 236 | 4686381 | 18408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EDDIE OPENING RECLOSER DUE TO POLE FIRE.//COD 78/I OPENED RECLOSER ON POLE 38821015B00238 AT 14:15. I CALLED FOR A THREE MAN CREW POLE TOP HAS BURNED OFF.I OPENED RECLOSER ON POLE 38821015B00238 AT 14:15. I CALLED FOR A THREE MAN CREW POLE TOP HAS BURNED OFF. POWER BACK ON AT 18:11.// VER/ ADH AJB
2090 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-02-04 11:56 | 2009-02-04 15:30 | 86 | 214 | 55509-1 | 18404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR#28362732//6A PRIMARY AND NEUTRAL DOWN AT POLE#90-65 BURNT IN CLEAR RECLOSER WAS NEVER OPEN OPENED SWITCH AT POLE#90-197 COD-86//WR#28362732// RELEASED BY CREW 078S08//VER/CRB IDCC PN12, FPNULL XXXX
2091 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-08-03 12:59 | 2008-08-03 21:30 | 36 | 511 | 64598-1 | 18396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG PRIMARY LINE FUSE BLOWN-TRIED FUSE DIDNT HOLD-CALLING CREW STS WR # 25567245UG PRIMARY LINE FUSE BLOWN-TRIED FUSE DIDNT HOLD-CALLING CREW-SEND TO P TOLLIVER RELEASED BY CREW 078S07//FOUND BAD UG WILL REPAIR FETR 23:00//COMPLETE P R TOLLIVER//SEND TICKET TO ENGINEERING NEED TO HAVE WORK ORDER WRITTEN TO REPAIR LOOP FEED VER/ARN IDC XXXX
2092 | South Williamson | 3411401 | DEWEY | INEZ | 2008-10-16 15:52 | 2008-10-16 16:57 | 283 | 65 | 56252-1 | 18395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 742-D-75//3411401//VER/CRB IDC XXXX
2093 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-04-06 23:11 | 2009-04-07 10:42 | 38 | 691 | 50065-1 | 18390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 29264805 // PREDICTING FUSE OUT ON POLE 38830954A10988 A 40T CLOSED FUSE ON POLE 954-988 AT 01:20. STILL HAVE FUSE BLOWN ON POLE 930-133. POLE BURNT OFF DUE TO FAILED CUTOUT ON POLE 929-100. ISOLATED AT POLE 929-99. CLOSED FUSE ON POLE 133 AT 02:04 LEAV//VER/CRB IDC XXXX
2094 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-04-12 02:14 | 2015-04-12 03:02 | 383 | 48 | 4309181 | 18384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED BREAKER TO MAKE REPAIRS DUE TO MUD SLIDE ON ORDER#4309071 OPENED 0214 CLOSED 0302 VER/HFP L3/HFP AJB
2095 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-11-02 22:23 | 2020-11-03 04:19 | 68 | 356 | 4636981 | 18349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830309000008 rec open--38830261000027 to 26 pri down--38830285000020 open and isolated nc c/o--rec in up to isolated open switch 83-285/20 at 00:45--crew req--ds110320 Released by crew 078S01//on site RM solid blade in @ 04:19 please close tic RM Released by crew 078H20
2096 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2012-07-24 15:36 | 2012-07-25 14:00 | 110 | 1344 | 4812571 | 18348 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LEFT HAND PHASE ONLY IS OPEN//COD 110 // HIGH LINE FELL ON LINE === OPEN TAP ON POLE 37830418000014 === CLOSED RECLOSER IN AT 18:12 == POWER ON // ON SITE WORKING REMOVED LAST SPAN OF WIRE MADE LAST CUSTOMER HOT AT 14 00// VER/DBM IDCC MCCDL CCO XXXX
2097 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-11-11 09:03 | 2013-11-11 11:35 | 139 | 152 | 4027491 | 18347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX BURNT IN TWO AT SPACER. CREWS WORKING TO REPAIR DOWNED CONDUCTOR AND TWO DAMAGED CONDUCTORS.// OPENED GOAB AT 954D2-100 @09:55. CLOSED GOAB @ 11:08, FUSES STILL OPEN @978-168//HENDRIX BURNT IN TWO AT SPACER. CREWS WORKING TO REPAIR DOWNED CONDUCTOR AND TWO DAMAGED CONDUCTORS. REPAIRS COMPLETE. CLOSED GOAB ON 954-100 @ 11:08 RESTORING ALL BUT OPEN LATTERAL ON 978-168. CLOSED THREE 40TS ON 978-168 @ 11:35 RESTORING REMAINING OUTAGED CUSTOMERS. SH VER/SEF IDCC CNT251, TOF095. PN100 XXXX
2098 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-01-13 09:51 | 2017-01-13 10:32 | 447 | 41 | 4294591 | 18327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ***SEE 4293731*** OPENING RECLOSER TO REPLACE BAD INSULATOR ON POLE 37830150000107/ OPENED @0951_/ CLOSED @1032__/ ISO 37830150000099/ COD 447/ VER/BOW L3/HFP XXXHFP AJB
2099 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-01-25 15:36 | 2010-01-25 22:38 | 62 | 422 | 59633-1 | 18300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECL POLE 473-125 - 50 AMP RECL; PATROLLED LINE TO NEXT RECLOSER 473/28-NOTHING FOUND; TRIED RECLOSER-WOULDNT HOLD; OPENED SWITCHES POLES 473/14, 497/92,479/98 AND RECLOSER 473/28; WILL TRY ONE SWITCH AT A TIME; RECLOSER 473/125 IN AT 1615HRS; 497/14 IN AT 1830HRS; 497/92 IN AT 1858HRS; 479/98 IN AT 1905HRS; WALKED 2.5 MILES OF LINE; PRIMARY WIRE-6A CAME UNRAVELED BETWEEN POLES 449/32 AND 449/33; CUT AWAY UNRAVELLED STRANDS; ALL PWR RESTORED AT 2238HRS; CLOSE TICKET VER/KEP L3/KEP IDCC TON1830 XXXX
2100 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-04-01 15:45 | 2012-04-01 19:06 | 91 | 201 | 4637881 | 18291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT ON POLE 424-86 ,BAD CSP XFMR ON POLE 400-34 ISOLATED XFMR . CLOSED FUSE ,WIRE BURNED INTO AT HOT LINE CLAMP AT POLE 400-33 .REPAIRED WIRE REPLACED XFMR RESTORED POWER AT 19:06//NO PARTIAL RESTORATION//COD 91 IDC XXXX
2101 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-02-21 00:24 | 2020-02-21 02:55 | 121 | 151 | 4421731 | 18271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3308301/gaj/0031/all out possible step down fuse open disp 3114 R Maggard. bad arrester on pole 351-331, restored power at 02:55 L3/HFP
2102 | Hazard | 3301101 | CHAVIES | CHAVIES | 2014-03-06 14:40 | 2014-03-06 15:43 | 290 | 63 | 4457121 | 18270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE BROKEN CROSSARMS /// OPEN AT 1440 CLOSED AT 1543 COD-290 ISO OCR 37830171000233 VER/HFP L3/HFP IDC XXXX
2103 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-03-09 08:20 | 2012-03-09 12:50 | 79 | 270 | 4566101 | 18270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE REC. OPEN//COD 79//, PATROLING LINE.--- OPENED GOAB ON POLE 37830200C00088 @ 0946 (COD + 29), SEE H4566101// , TOP OF POLE 37830200C00091 IS BURNT OFF. --- CUTOUT FOR LATERAL BROKE AND BURNT TOP OF POLE OFF. CREW ON SITE.// IDC NEED 2 ORDERS// VER/DBM IDC XXXX
2104 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-03-14 17:00 | 2010-03-14 17:45 | 406 | 45 | 66649-1 | 18270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 654-219 C-PHASE// RECLOSURE OUT ON POLE 654-529 C-PHASE RECLOSURE IS OUT// CUTOUT REPAIRED CLOSING IN RECLOSURE//POWER RESTORED AT 1751//VER/CRB IDCC CDC88 XXXX
2105 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-12-11 00:30 | 2009-12-11 07:45 | 42 | 435 | 57788-1 | 18270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STEP DOWN FUSE BLOWN; CREW REQUIRED; PRIMARY AND NEUTRAL DOWN BETWEEN POLES477/58 AND 477/59, NEUTRAL DOWN BETWEEN 477/58 AND 477/57; POLES 477/57 AND 477/59 ARE TRUCK ACCESSABLE; NEED HANDCOIL 6A WIRE AND SLEEVES FOR SPLICING; NO GOOD PLACE TO SECTIONALIZE; NO GROUNDS INSTALLED RELEASED BY CREW 078S12/ WIRE ROTTEN BROKE // CLOSED IN @ 0745 IDCC FEC MISSING XXXX
2106 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-10-11 01:18 | 2018-10-11 13:00 | 26 | 702 | 4217941 | 18252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. patrolling line, gave line a shot, came back out, calling for help
2107 | Whitesburg | 3314401 | MAYKING | ERMINE | 2018-02-10 12:48 | 2018-02-10 16:05 | 143 | 197 | 4823171 | 18208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Center ph recl on 37830449D20854 open (cod: 62). Two spans primary down off 37830449D20099. 2 men needed to assist. Opened other 2 phases at 1451.I opened the two outside phases at 14:54
2108 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-01-29 23:11 | 2008-01-30 04:42 | 55 | 331 | 60850-1 | 18205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STS LOOP BURNED INTO ON POLE 170-20 VER/KEP IDC XXXX
2109 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2010-01-21 01:02 | 2010-01-21 06:14 | 61 | 312 | 57053-1 | 18204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" PHASE RECLOSER OUT ON POLE 868-C4-345 - COD-61// TOP OF 3 PHASE POLE 892-C-26 WITH DOUBLE CROSSARMS BURNT OFF 1 FT ABOVE TRANSFORMER/ ON SITE, , , CALLED FOR CREW // @0230 OPENED RECLOSER ON POLE 892-C-253 - COD29 (B&C PH)// @0247 CLOSED RECLOSER ON POLE 868-C4-345 RESTORED 31 CUSTOMERS//@0614 CLOSED RECLOSER ON POLE 892-C-253 RESTORING 57 CUSTOMERS// IDC , MADE FIRST STEP 4 INSTEAD OF 31. THE COUNTS SHOULD BE CLOSE THIS WAY. XXXX
2110 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-09-04 15:18 | 2018-09-04 23:17 | 38 | 479 | 4042301 | 18202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crew on site---Bad cutout on pole 454-6127---xarm too bad to operate cutouts---opened LF on pole 454-6016 @ 21:23--g&T to RMV--crew changing out bad x arms--repaired arms---removed G&T--energized PL 454-6016 @ 23:17---volt ck good @ 454-6127---tbl tkt comp---rmv Released by crew 078H16
2111 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-07-02 02:45 | 2012-07-02 03:00 | 1213 | 15 | 4160251 | 18195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT SURGE ARRESTOR IN CLEAR AT POLE 24-1229 RELEASED BY CREW 074F12 //VER/GAH IDC CHANGED TIME OFF FROM 7/1 1205 XXXX
2112 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-05-30 12:09 | 2011-05-30 16:25 | 71 | 256 | 4209391 | 18176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD STEPDOWN TRANSFORMER ON 429D-67; RELEASED BY CREW 078S11//VER/CRB IDC XXXX
2113 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-10-31 15:55 | 2008-10-31 16:41 | 395 | 46 | H61186-1 | 18170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301//B PHASE REC OUT AT 1422 COD 154//WILL HAVE TO OPEN OTHER 2 TO MAKE REPAIRS//REPLACING TWO BAD SOLID BLADES ON SITE NOW TCM// OPENED OTHER TWO RECLOSERS AT 1555 TO START REPAIRS// CLOSED ALL 3 RECLOSERS BACK IN AT 16:41 TCM/ IDCC DUP TO OPEN RECLOSERS XXXX
2114 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-10-03 09:52 | 2009-10-03 12:30 | 115 | 158 | 66272-1 | 18170 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | LOW SIDE SURGE ARRESTOR TO 69-12KV TR IN STATION FAILED CAUSING HIGH SIDE FUSE TO 69-12KV TR TO BLOW. //VER/GAH IDCC CDC92 ONE PHASE OUT INITIALLY XXXX
2115 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-10-31 17:12 | 2009-11-01 01:58 | 72 | 526 | 53870-1 | 18160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED; TOP 18 OF POLE BURNT OFF ANGLE POLE 524/107 ; CAN LOWER EVERYTHING ON POLE--NEW POLE NOT REQUIRED; NEED NEW 7200 CUTOUT AND BRACKET AND 15 FT OF # 2; 4 WHEEL DRIVE TRUCK ACCESSABLE BUT VERY STEEP GRAVEL DRIVEWAY; CLEARED UP AND GROUNDED ISOLATION POLE 524/189 RELEASED BY CREW 078S12 ISOAT 524-77 CLOSED TIE SWITCH 572-94 AT 2050 PICKED UP ALL BUT 8 CUST//CREW ON SITE WILL LOWER ATTACHMENTS//COMPLETE AT 01:58 ALL CUST. RESTORED.P R TOLLIVER RELEASED BY CREW 078H03 //VER/GAH IDC XXXX
2116 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-09-27 11:39 | 2018-09-27 16:45 | 426 | 306 | 4166571 | 18156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | opened 600amp switches on pole 45-24 at 15:08 due to loop burnt opened on pole 45-22 should be off about 45 min. got 600amp switches on pole 45-24 closed back in at 15:50. fuse open on pole 68-10 30t due to bad insulator on pole 68-187. changed insulator closed 30t fuse back in at 16:45 should have everyone back on Released by crew 074S11
2117 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-09-08 19:39 | 2020-09-08 21:51 | 189 | 132 | 4443311 | 18144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | fault pole 38830043000013. 4 solid copper loop burnt open. no trucks //OUTAGE STARTED @ 1834/opened recl 44-a-606 @ 2100 to make repairs/on 2151
2118 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-10-16 20:09 | 2014-10-16 23:54 | 513 | 225 | 4638561 | 18117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC OPENING SWITCH TO ISOLATE FAULT POLE 139-4004. OPENED AT 2009 CLOSED AT 2355. VER/SEF AJB
2119 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-03-26 23:59 | 2013-03-27 03:27 | 87 | 208 | 4960821 | 18096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED SOUTHSIDE 12KV CB A TO SAFELY OPEN 12KV DISCS AT POLE 942-B4-1424 TO SAFELY PATROL MOUNTAIN AREA ON FOOT. 12KV DISCS OPENED AND TAGGED TO KY DDC @ 0001// CLOSED CB AT 0003. CREW PATROLLING ON FOOT AT THIS TIME. LOOP BURNT OFF BETWEEN 966-644 AND 966-1165 STEEL TOWERS NOT ON MAP// THIS OUTAGE AFFECTED "C" PHASE CUSTOMERS FROM 966-A3-1165 TO END OF LINE 107CC RESTORED CC WHEN CB CLOSED AT 0327 IDC XXXX
2120 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-04-09 15:12 | 2010-04-09 21:35 | 69 | 383 | 61664-1 | 18086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 40 C5 POLE BROKEN 37820194B00101. CAN USE TRUCKS. #4 PRI. BROKEN AND NEUTRAL STILL TOGATHER. CLEVIS, POLETOP PIN, AND INS. OPEN 37820194C00264 //REC. ON UPTO POLE 37820194C00082 AT 17:48. RELEASED BY CREW 074S08// POLE BELONGS TO AT&T// REPLACED POLE AND CLOSED IN ON POLE 37820194C00082 AT 2122// VER/DBM IDC DURING RESTORATION OF 61664-1, SECTIONALLIZER OPENED/// MUST HAVE MIS-OPERATED//CREWS NOW RESETTING DEVICE//COD 20// VER/DBM , DC ADDED THESE AS A STEP TO THE PREVIOUS OUTAGE XXXX
2121 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-03-15 18:37 | 2018-03-15 23:59 | 56 | 322 | 4017531 | 18032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout has breakng down and got pole on fire got jeff combs crew coming to change pole out, open line fuse on pole 38831064000033 at 1837 Released by crew 077S05
2122 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-12-24 14:31 | 2018-12-24 17:30 | 187 | 179 | 4596851 | 18029 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | stirrup burnt off @ 326-2 ,,,opened reclosers 38830327B00027 @ 16:10 ,,,fetr 18:00 L3/HFP
2123 | Hazard | 3309302 | VICCO | JEFF | 2013-08-07 21:46 | 2013-08-08 00:16 | 120 | 150 | 4633951 | 18000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE ONLY//COD 120//CLAMP ON B PHASE STEPDOWN HAS BURNT OFFCLAMP ON B PHASE STEPDOWN HAS BURNT OFF.. MADE REPAIRS RESTORED POWER TA 00:16CLAMP ON B PHASE STEPDOWN HAS BURNT OFF.. MADE REPAIRS RESTORED POWER TA 00:16 RELEASED BY CREW 077S11 VER/KEP L3/HFP IDC XXXX
2124 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-28 18:07 | 2011-06-28 20:12 | 144 | 125 | 4431661 | 18000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 142-144 B PHASE IS OPEN COD-144//POLE 142-17 IN FRONT OF FIRE DEPT, BASKET ON C PHASE, BROKE///PL. 142-17 #2 SOLID CU. FAILED @ BASKET( AL BASKET ON CU. THIS IS NOT ACCEPTABLE PRACTICE) TOOK OUTAGE ON A&C PHASE RECLOSER@ 19:48 COD-77 TO MAKE REPAIRS/ REPAIRS COMPLETE ALL POWER RESTORED @ 20:12 J. HEMLEPP & CREW 078H05 VER/KEP IDC XXXX
2125 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-08-09 06:55 | 2014-08-09 12:00 | 59 | 305 | 4345401 | 17995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON 882-390..CENTER PHASE OUT.NEED 1MAN BIG BUCKET.OFF AT 11.10 BACK ON AT 12.. ISO 38830882C00390// SEE ALSO ORDER NUMBER 4347151// MAP DISCREPANCY MADE//COD 59// VER/DBM AJB MAP CUR SHOWS OCR.
2126 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-10-31 15:48 | 2009-10-31 20:55 | 84 | 307 | 53771-1 | 17988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECLOSER TO SAFELY ISOLATE BURNING POLE ON ORDER 53677 VER/KEP L3/KEP IDC SEE 53677-1 FOR COMMENTS IDC XXXX
2127 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-03-26 07:18 | 2014-03-26 11:33 | 97 | 255 | 4525951 | 17975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER MYLES B PHASE OUT ONLY COD 97// POLE 26-88 HAS BURNED IN TWO DUE TO BAD CUTOUT// OPENED RECS ON 49-D2- 331 @ 8:17// OPENED SWITCHES @ 49-70// TAGGED TO MYLES// COLSED REC.S ON 49-D2-331 @ 8:44// CREW ENROUTE//CLOSED @ 49-70 @ 11:33 / **** MAKE DUPLICATE TICKET IN HOIS FOR ADDITIONAL B & C PHASE CUSTOMERS FROM 0817 TILL 0844****** VER/SEF IDC XXXX
2128 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-07-17 20:32 | 2020-07-18 01:47 | 57 | 315 | 4177341 | 17955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse out on 37830394D00028 patrolling 37830394D00030 looks like cutout went bad burning top pole off need line crew pole top ext. 7200V insulator cutout lighting arr. and t/bracket will have to block road fuse is not isolated and no grounds no wire down Released by crew 077S03..repairs made all restored @ 01:47 hrs p.hicks
2129 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-06-28 11:01 | 2015-06-28 16:10 | 58 | 309 | 4686131 | 17922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET FOR LATERAL BURNT OFF HENDRIX. CREW REQD. 39831124B33073/ ISO 39831124B33073/ COD 58/REPAIRS WILL REQ SWITCHING/FETR1630/VEM/NOTE TO MAPPING LINE FUSE IS NOW ON B PHASE/VEM RELEASED BY CREW 078H14 LOAD TRANSFER ON LO MD FILED FOR FUSE/ VER/KEP
2130 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-24 13:11 | 2014-01-24 16:05 | 103 | 174 | H4306051 | 17922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT BAD 500 STEPDOWN ON POLE 29-196 PER B.O. & LOAD TRANSFER DONE B PHASE WAS INITALLY OUT NOT A PHASE 100 CUST (54 CUST XFERED TO CKT 3312202) // 103 C PHASE (NOT B) CUST DROPPED WHEN OTHER STEPDOWN OPENED @ 1311 VER/HFP L3/HFP IDC XXXX
2131 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-10-02 19:26 | 2015-10-03 01:00 | 88 | 334 | 4305161 | 17917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CENTER FUSE BLEW ON POLE 784-345//TRYED FUSE AND IT CAME BACK OUT///ROGER MAYNARD AND CREW ENROUTE TO TRY TO FIND FAULT IN UNDER GROUND///CLOSED LINE FUSE 784-345 AT 22:27 THIS PICKED UP TO PAD 784-336, APPROX 25 CC ///CLOSED FUSE ON 784-1585 (SHOWN AS 784-49) AT 01:00 RESTORING REST OF CUST APPROX 32 CC//PHASING IS INCORRECT HERE, AS IS MOST OF THE MAP, UNABLE TO DETERMINE CORRECT COD, ESTIMATE 57 COD//AED CREATED, CABLE ISOLATED BETWEEN 784-336 & 784-340 // NEED MORE INFO FROM ENG = VER/HFP L3/HFP AJB
2132 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-05-16 17:50 | 2010-05-16 20:47 | 102 | 177 | 63358-1 | 17909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY B PHASE FUSE OPEN//COD 96//FAILED CUTOUT //RELEASED BY CREW 074S07 LINE FUSE OUT ON POLE 332-187, RECLOSER POLE OPEN ON 333-84 BAD CUTOUT ON 333-79 ,REPLACED CUTOUT CLOSED LINE FUSE IN AT 20:42 CLOSED RECLOSER IN AT 20:47 RELEASED BY CREW 077S11//COD 96 IDCC CNT96 ADDED 3 PH CUSTOMERS XXXX
2133 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-09-06 12:55 | 2011-09-06 13:52 | 314 | 57 | H4830081 | 17898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONLY B PHASE RECLOSER OUT 224 COD// WILL HAVE TO OPEN OTHER 2 WHEN GET READY TO MAKE REPAIRS// #4 COPPER DOWN ONN CENTER PHASE . HAVE CREW IN ROUTE TO REPAIR. PULLED OTHER 2 PHASES OFF @12:55#4 COPPER DOWN ONN CENTER PHASE . HAVE CREW IN ROUTE TO REPAIR. PULLED OTHER 2 PHASES OFF @12:55BACK ON @13:52 COD-224 (1 PHASE OUT) DUP OF 4830081 VER/HFP L3/HFP IDC XXXX
2134 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2017-05-10 08:23 | 2017-05-10 18:40 | 29 | 617 | 4775141 | 17893 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATION POLE 1147-963 IS TAGGED TO CRAIG CRAMTON POLE 1147-749 BURNED OFF CREW REQUIRED 3 WAY DEAD END POLE, 2ACSR ,, BACKYARD ,CAN ACCESS OFF OF CLEARWATER WITH TRACK MACHINE, #2 SERVICE WIRE FOR SPLICING AND 37.5 TRANFSFOMER AND RISERS, 120/240V 7.2KV, AND CUTOUT AND GUYWIRE, OR POSSIBLE POLE TOP EXTENTION D/ ISO 39831147A00963/ COD 29/ VER/BOW AJB
2135 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-11-06 05:08 | 2014-11-06 11:35 | 52 | 387 | 4703791 | 17868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL WORK DURING NORMAL HOURS//////LOW SIDE STEPDOWN F IS BLOWN,WILL PTRL//////ONLY ROW ISSUES VISIBLE,WILL RE-FUSE//F BLEW,WILL LOOK CLOSER//BAD LA,CLEARED,REPAIRED,CLOSED LINE F AND RESTORED @1048 RESTORING 48, CLOSED TRANSFORMER 236-42 @ 11:35 RESORTING THE REMAINING 4 VER/HFP L3/HFP L3/IDC XXXX AJB
2136 | South Williamson | 3411401 | DEWEY | INEZ | 2012-03-09 14:36 | 2012-03-09 15:28 | 343 | 52 | 4567421 | 17836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | DA SCHEME LOCKED OUT AT 1436 // FAULT ON DA SCHEME & 34KV N.O. DA SWS AT POLE 746-B-218 NOT OPERATING PROPERLY //VER/GAH IDC XXXX
2137 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-01-09 00:54 | 2015-01-09 03:08 | 133 | 134 | 4922531 | 17822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OFF ON RECLOSER AT POLE 426-685, REPLACED CLAMP RESTORED POWER AT 03:08 VER/HFP L3/HFP AJB
2138 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-03-31 17:23 | 2022-03-31 22:25 | 59 | 302 | 4708001 | 17818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1 span 4 solid copper down crew required truck ok Released by crew 078S09 wire down at pole 38830093A00019 crew onsite FETR 22:30 LRM all pwr restored 22:25 please close LRM
2139 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2017-04-23 07:55 | 2017-04-23 12:17 | 68 | 262 | 4670491 | 17816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY BROKE IN CLEAR AT POLE 37830234000041 COD 68. OPENED RECLOSERS ON 37830234000137 TO ISOLATE @ ON ORDER 4670971. VER/AWD L3/HFP XXXHFP AJB
2140 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-08-18 13:20 | 2010-08-18 13:50 | 593 | 30 | 57652-1 | 17790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#36496278BAD CUT OUT ON PL#1127-267 WILL CHANGE ALL 3 WILL OPEN LINE AT PL#1127-48AT APPROX. 13:20 SHOULD TAKE ABOUT 30 MINS. R RAY-POWER BACK ON AT13:50/VER/CRB IDC XXXX
2141 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-08-26 18:49 | 2014-08-26 20:25 | 347 | 96 | 4426441 | 17787 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED A RECLOSER LOCKED OUT ON 141-C-423, AUTOMATED SCHEME TRANSFERRED 603CC TO PRINCESS/MEADE 34KV CKT // 1940 RESTORED 345 CC // POLE 141-69 BAD CUTOUT LA AND BRACKET 19.9 LAST TWO CUST AT 20:25 RELEASED BY CREW 078S08 VER/HFP L3/HFP AJB
2142 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-01-17 04:17 | 2022-01-17 17:10 | 23 | 773 | 4361891 | 17779 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened LF 37830065D00577 due to pole burned offOpened line fuses at pole 65-d-577. Pole 65-d-584 has burnt off below cutout bracket. Need 45-4 pole, 2 8ft arms, 6 7200 deadend insulators and copper deadends, 3 arm pins and insulators, 3 leaf cutout bracket and cutouts, 1 25kva for wye-wye bank and 2 cleviss.Opened line fuses at pole 65-d-577. Pole 65-d-584 has burnt off below cutout bracket. Need 45-4 pole, 2 8ft arms, 6 7200 deadend insulators and copper deadends, 3 arm pins and insulators,
2143 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-06-24 00:20 | 2015-06-24 01:45 | 209 | 85 | 4648651 | 17765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECL TO SAFELY MAKE REPAIRS ON PO#4646931 VER/KEP AJB
2144 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-02-06 03:38 | 2008-02-06 12:53 | 32 | 555 | 50229-1 | 17760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUT-OUT PATROL REST OF LINE235-68 FUSE POLE VER/ARN IDC XXXX
2145 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-02-11 03:04 | 2020-02-11 09:30 | 46 | 386 | 4390771 | 17756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /0304/all out possible line fuse open disp 3327 J Moreland ---0515//patrolled found no cause tried fuse at 0515 & opened back up, servicer is re-patrolling for cause --- gaj/0617/servicer reports failed insulator at 38830221000020 & primary down at 38830221000021 needs big buclet & crew to make repairs to insulator & down conductor/all out possible line fuse open disp 3327 J Moreland/wire down 221-21 to 20 primary only trucks ok All on 0930
2146 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-10-25 08:45 | 2010-10-25 14:20 | 53 | 335 | 62700-1 | 17755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ISO 38831125B00772 "A" PHASE COD-53.PHASE A ONLY WAS OUT.XARM BROKE @ 38831125B00187 HAVE CREWS ENROUTE OPENED OTHER 2 PHASES AT 1252 RESTORED 1420 MADE DUP ORDER VER/KEP L3/KEP IDCC PN180 XXXX
2147 | Hazard | 3303902 | LESLIE | WOOTON | 2015-02-19 05:14 | 2015-02-19 10:05 | 61 | 291 | 4041111 | 17751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIMARY DOWN ON 413-107 713 FT SPAN WIRE PULLED OUT FROM SLEEVE//COD 61 VER/HFP L3/HFP AJB
2148 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-11-30 01:17 | 2015-11-30 03:39 | 125 | 142 | 4493251 | 17750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830245B00212 GOING TO REPAIR BEFORE CLOSING RECLOSER BACK TOWARD STATION BE RIGHT HANDED PHASE A PHASE RELEASED BY CREW 077S05 62CC
2149 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-01-09 17:44 | 2022-01-09 18:08 | 739 | 24 | 4329931 | 17736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Failed cutout on 193-174 was operating recloser 193-390//Had to open recloser@ 17:44 to make repairs///will be making repairs//Changed bad cutout And closed recloser in @ 18:08 and restored all customers
2150 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-10-26 14:37 | 2010-10-26 21:20 | 44 | 403 | H63976-1 | 17732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STS WR # 37489285 // OPENED SWITCHES AT 1007-118/ WIRE DOWN AT 1007-120/ ONLY C PHASE OUT 95 CUSTOMERS 1 POLE BROKE(1008-81),POLE 1007-119,XARMS BROKEN,HAVE CONTACTED T HALL IN PVILLE,CREW ENROUTE SHORTLY,THEY WILL BE CALLING FOR TICKET. RELEASED BY CREW 074S06 //VER/GAH IDCC DUP TO OPEN SWITCHES XXXX
2151 | Hazard | 3309302 | VICCO | JEFF | 2017-08-15 06:16 | 2017-08-15 10:27 | 200 | 251 | 4260611 | 17728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830348B00074 TOOK MAIN LINE OUT GOT MAIN LINE ON AT 7:43 === NEED CREW TO CHANGE CUTOUT MANUAL === RELEASED BY CREW 077S03 REPAIRS MADE AND POWER RESTORED AT 1027 VER/KEP SJG
2152 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-02-22 00:04 | 2009-02-22 05:15 | 73 | 311 | 50115-1 | 17708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409002 - FOUND C PHASE RECLOSER AT POLE 784-68 OPEN INTERRUPTING 68 CUSTOMERS. WIRE DOWN - DIFFICULT LOCATION. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. CLOSED PH C REC ON POLE 68 AT 02:10 RESTORING CUSTOMERS UP TO SW ON POLE 783-118. OPENED OTHER TWO SWS AT 0400 AND RESTORED ALL CUSTOMERS RESTORED AT 0515 //VER/GAH IDCC CNT22 XXXX
2153 | Hazard | 3309302 | VICCO | JEFF | 2011-03-09 15:40 | 2011-03-09 21:34 | 50 | 354 | 52260-1 | 17700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 1540 / OPENED RECLOSER AT POLE 346-427 TO DE-ENERGIZE POLE. FAILED CUT OUT AT POLE 346D-177, POLE WILL NEED REPLACED. REPLACED POLE RESTORED POWER AT 2134 CREW 077H012134//COD 50// VER/DBM IDC XXXX
2154 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-11-08 22:01 | 2010-11-09 00:15 | 132 | 134 | 54144-1 | 17688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37679130 //BAD CUTOUT ON PHASE A ON POLE 941-D-476.....WHERE 3 PHASE FORKS.....NOT MAPPED RIGHT....CREW REQUIRED ALSO BREAKER OUTAGE REQUIRED TO REPLACE CUTOUT.....FETR 00:45 ON 11/09/10 //VER/GAH IDC XXXX
2155 | Hazard | 3303902 | LESLIE | WOOTON | 2018-07-12 04:17 | 2018-07-12 12:35 | 63 | 498 | 4764991 | 17672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole # 37830413B00382 burned off bad cutout need 40 foot pole for de pole, got clamp off and going to make recloser hot at 0834 Released by crew 077S05 // recl on @ 0834 Released by crew 077H04
2156 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-03-26 07:08 | 2009-03-26 09:34 | 121 | 146 | 61627-1 | 17666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE ONLY APPEARS TO BE INVOLVED PATROLLING LINE AND CALLING FOR ASSISTANCE FROM LINE CREW// 7200 VOLT CUTOUT FAILED AT SWITCHES ON POLE 37830249D00205 CREW AND FLAGGERS IN ROUTE//ISO 37830249D00205//COD 121// VER/DBM IDC XXXX
2157 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-01-04 05:34 | 2009-01-04 15:00 | 42 | 566 | 51175-1 | 17647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3007906//BAD UNDERGROUND I TRIED FUSE ON UNDERGROUND FUSE POLE AND IT BLEW OUT CALLED LLOYD MCCARTY SENDING UNDERGROUND CREW TO LOCATE FAULT // PHELPS, WEBB, HALL AND WEST IN CREW W/MCCARTY// FOUND BURNT OFF BUSHING @ 478-333 - ISOALTED/PARKED @ 478-311 FEED// CLOSED IN 478-203 AND ENERGIZED UP TO 478-311 RESTORING 25 CUSTOMERS// REMAINING CUSTOMER RESTORED @ 1500 WHEN ENERGIZED FROM 311 TO 333// 300790 TIME ON @ 15:00 VER/TOM L3/TOM IDC XXXX
2158 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-10-27 20:20 | 2008-10-27 23:42 | 162 | 202 | 59733-1 | 17639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309001//ONLY PHASE A IS OUT//COD 162//ISOLATED AT SWITCH POLE 394-15 AND CLOSED RECLOSER @ 2145 RESTORING 97 CUST//ISOLATED FURTHER AT RECLOSER POLE 394-B-225 AND CLOSED SWITCHES @ 2159 RESTORING 8 CUST//FOUND BAD CUTOUT ON POLE 394-387, ISOLATED TRANSFORMER AND CUTOUT AND CLOSED RECLOSER @ 2250 RESTORING 56 CUSTOMERS//FINAL CUST ON @ 2342//== REPLACED == FAULT TOOK OUT 2 RECLOSERS ==// VER/DBM IDC XXXX
2159 | South Williamson | 3200302 | BELFRY | TOLER | 2011-06-07 09:21 | 2011-06-07 10:08 | 375 | 47 | 4244651 | 17625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED 3PH RECLOSER IN ORDER TO MAKE REPAIRS TO BURNT LOOP IN ORDER 4243921 // COD 375 // VER/DBM IDC XXXX
2160 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-05-22 17:22 | 2011-05-22 18:51 | 198 | 89 | 4123261 | 17622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD LIGHTNING ARRESTORER ON POLE 42-5, HAVE ARRESTOR CUT IN THE CLEAR, AND POWER IS RESTORED TO THIS CUST AT 1851
2161 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-11-25 23:18 | 2014-11-26 00:03 | 391 | 45 | 4782311 | 17595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | RELATED TO ORDER 4782121//SWITCH ARCING ON POLE 786-773//TRANSFERED 133 CUSTOMERS TO WEST PAINTSVILLE-STAFFORDSVILLE BY CLOSING N.O. SWS 737-298 THEN OPENEING RECLOSERS 738-276//OPENED CKT BREAKER FOR MAYO-NIPPA @ 2318 // COD 391 // REPAIRS MADE AND BREAKER CLOSED @ 0003// CKT PUT BACK NORMAL, CUSTOMERS NO LONGER TRANSFERRED TO OTHER CKT// VER/DBM AJB
2162 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-10-08 06:42 | 2017-10-08 09:47 | 95 | 185 | 4419411 | 17575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE/BROKE CUT OUT ON 38830183D00148/ REPAIRES MADE/ RECLOSER ON 184-30 IN @ 0947/PLEASE CLOSE TICKET/MLH/ B PHASER ONLY/ ISO 38830184C00030/ COD 95/ VER/BOW ACB
2163 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-09-05 12:11 | 2010-09-05 15:40 | 84 | 209 | H63752-1 | 17556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 075H01 ONE PHASE BURNT DOWN IN SPACER CABLE WILL BE OPENING GOAB ON POLE 381D3530 WHEN HELP ARIVES//ONLY PHASE A AFFECTED//ISO 37830382A20286//COD 33//OPENED GOAB 381-530 @ 1211 INTERRUPTING ADDITIONAL 84 CUST TO ISOLATE TROUBLE// IDC XXXX
2164 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-08-13 09:59 | 2014-08-13 10:33 | 516 | 34 | 4364531H | 17544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE ONLY AT START COD-245/= OPENED @ 0959 AND CLOSED @ 1033 ON GOAB 483A-196 RELEASED BY CREW 077S01 VER/DKG A PHASESLEEVE PULLED OUT AT REC 459-166 A PHASE CUST OUT ENTIRE TIME VER/DKG L3/DKG THIS OUTAGE FOR CUST THAT WERE OUTAGED BY GOAB ON 483-196 VER/DKGL3/DKG THIS FOR THE OUTAGE AT GOAB AJB CNT554
2165 | Hazard | 3301401 | COMBS | COMBS | 2011-04-16 11:56 | 2011-04-16 19:37 | 38 | 461 | 58354-1 | 17518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINECLAMP BURN OFF ON POLE 37830272A20102== NEED TO MEN TO REPLACE CLAMP === RELEASED BY CREW 077S03 RELEASED BY CREW 077H02 VER/HFP L3/HFP IDC XXXX
2166 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-05-11 22:33 | 2019-05-12 12:27 | 21 | 834 | 4254641 | 17514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | line fuse out on 38820673D00086 .pole top burnt OFF 38820673C00075. line crew required.40-5 NTA with a primary tap coming off of it.need cutout arrestor and bracket,pole top pin and insulator.manual ROW crew required & flagging crew.no tags or grnds placed. Released by crew 079H03.making repairs//CUTOUT FAILED ON POLE 38820673C00075
2167 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-08-23 16:37 | 2014-08-24 14:15 | 14 | 1298 | 4414511 | 17514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VEM/TRIED FUSE @0837/CAME BACK OUT/TRIED FUSE @1139/CAME BACK OUT/LOOKING FOR A PLACE TO CUT DEAD END IN LINE/VEM/INSTALLING FLOAT DEAD END 213-2&213-3/WILL TRY FUSE TO NEW OPEN POINT/VEM/FUSE STAYED @1241/LINE HOT UP TO POLE#213-3/ VER/CRB
2168 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2022-02-16 11:33 | 2022-02-16 13:23 | 160 | 110 | 4486731 | 17500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HT burnt loose on Bphase @ pole 38830020D47630, Opened de-energized B phase reclosure on 20-d3-7813, Repaired HT and reclosure back on @ 13:23. Three 50t fuses on 20-d4-7630 off from 13:07 to 13:17. All power restored Released by crew 078S02
2169 | Hazard | 3303902 | LESLIE | WOOTON | 2013-01-23 10:36 | 2013-01-23 11:01 | 699 | 25 | 4732691 | 17475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CENTER PHASE (B) BYPASS FUSE BLEW WHILE CREW WAS REPLACING RECLOSER//SUSPECT LOAD IS THE CAUSE//PATROLLING//COD 669//SERVICER FOUND NOTHING BUT ON CLOSER INSPECTION THE FUSE LOOKED OLD AND CORRODED//REPLACED FUSE AND CLOSED BACK @ 1101 AND IT STAYED// VER/DBM IDC XXXX
2170 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-01-23 10:45 | 2008-01-23 14:15 | 83 | 210 | 59143-1 | 17430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3103101//WIRE DOWN AT ISOLATION POLE 248-15//COD 833103101// SO248-15LID BLADE OPEN ON POLE VER/KEP IDC XXXX
2171 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-10-26 15:51 | 2010-10-26 22:45 | 108 | 414 | 64446-1 | 17427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REC. OPENED ON POLE 212-180 BROKEN POLE 35/5 PRIMARY POLE WITH XFORMER ( NEED TO REPLACE 25 KVA 7200 XFORMER ) LIFTED HOT TAP ON POLE 212-31. RELEASED BY CREW 078S01//OIL SPILL WILL NEED TO CONTACT ENVIROMENTAL FOR CLEANUP IN AM.///PLEASE SEND COPY TO RAYBURN TO CALL CLEANUP CREW. POWER RESTORED @ 22:45 AT POLE 212-103 P TOLLIVER RELEASED BY CREW 078H03//VER/CRB IDC POLE ROTTED XXXX
2172 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-07-23 06:06 | 2013-07-23 10:30 | 66 | 264 | 4579781 | 17424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES // TOP OF POLE BURNED OFF,CREW WILL NEED POLE EXTENTION AND A NEW CUTOUT AND ARRESTOR AND BRACKET RELEASED BY CREW 077S12POWER RESTORED AT 1030//COD 66// VER/DBM IDC XXXX
2173 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2009-05-13 14:46 | 2009-05-13 16:03 | 226 | 77 | 52724-1 | 17402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED ARRESTOR ON POLE 328-167 AND CLOSED RECLOSER BACK IN VER/KEP L3/KEP IDC XXXX
2174 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-07-01 21:31 | 2008-07-02 20:31 | 22 | 1380 | 61132-1 | 17385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SERVICERTROUBLE SHOOTING PROBLEM UNDERGROUND. * CREW UPDATED AT 0240 , STILL LOCATING UNDERGROUND CABLE FAULT. COULD INVOLVE EXCAVATION BY HAND. SAME AS 61134-1 CREW UPDATED AT 0555 , BAD ELBOW AT JB 24-A-1235, WILL BE RESTORING CUST FROM FUSE POLE 1152-B-211 TO JB 24-A-1235 * MAP SHOWS N.O. IN JB 24-A-1235 NO CORRECT... REST 15 CUST AT 0606 FROM FUSE 1152-B-211 TO JB 1292 15 CC OUT FROM FUSE 211-TO JB 1292//BAD UG CABLE//SERVICER ON SITE TROUBLE SHOOTI IDCC CDC94, TON0930 XXXX
2175 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-07-23 09:27 | 2009-07-23 12:30 | 95 | 183 | H64523-1 | 17385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP "A" AND "B" PHASE OPEN BUSTED OPEN "C" PHASE AT 0927, BAD CUTOUT ON "B" PHASEFOUND BAD CUTOUT ON POLE 902-485, ON B PHASE, ALSO HAVE BAD CUTOUT ON 902-20, WHICH IS THE LINE FUSE POLE, HAVE CALLED FOR CREW TO BRING 6 CUTOUTS AND CHANGE THEM FOR ME, JOE H. IS ON HIS WAY, THIS RECORD FOR C PHASE L3/HFP IDC XXXX
2176 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-09-22 10:49 | 2021-09-22 16:17 | 56 | 328 | 4269471 | 17380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Recloser is open on 596-27. 6a dn & 597-31 looks like may have just pulled out of sleeve. Isolated @ S.B. on 621-42///// Recloser 596-27 in @ 1210 hot to 621-42. crew required Released by crew 078S11/ crew on site/ repairs made/ solid blade on 621-42 in @ 1617/ MLH Released by crew 078H08
2177 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-02-28 09:06 | 2019-02-28 09:55 | 849 | 49 | 4936091 | 17371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 38830141D00023/ Opened Switch 38830165A00267 @ 0911 849cc/ took xfmr off line/ closed switch 38830165A00267 @ 0915 571cc/ RECL 38830141C00423 has a comm loss on DA Scheme so when switch was deenergized recl opened/ RECL 38830141C00423 back on @ 0955 278cc/ XFMR 38830141D00023 on @ 0935 0cc
2178 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-02-13 20:50 | 2008-02-13 21:30 | 434 | 40 | 62968-1 | 17360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402002// INT OF BUCKLEYS CRK AND TOWN MTN RD// CUTOUT BAD. NO OUTAGE AT THIS TIME.// NO OUTAGE UNITL RECL ON POLE 1152-271 OPEN @ 2050// HAD TO OPEN TO ISOLATE CUTOUT THAT IS BURNING ON POLE 1129A-314// BIG BUCKET AND ONE MAN ENROUTE// VER/TOM IDC XXXX
2179 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-11-28 06:09 | 2010-11-28 08:12 | 141 | 123 | 60215-1 | 17343 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL BE DISPATCHED AFTER DAYLIGHT/OPENED 224-145 AT 0730 HRS TO MAKE REPAIRS./224-145 BACK IN AT 0812 HRS RELEASED BY CREW 078S03 141CUSTOMERS OUT OPENED 54 AT 0730 AND RESTORED ALL AT 0812 VER/ARN IDC XXXX
2180 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-09-13 23:01 | 2018-09-14 09:43 | 27 | 642 | 4095501 | 17334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolled line, found nothing , gave line a try, came back out Released by crew 077S02. bad cutout on pole 466-58, line fuse on pole 466-37 is out, made repairs restored power at 09:43.. COD-27 ISO LF 37830466000037
2181 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-12-23 01:00 | 2022-12-23 07:43 | 43 | 403 | 4288511 | 17329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 38830116B02510/repairs made. tre
2182 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-04-21 12:44 | 2022-04-21 14:03 | 376 | 79 | 4786981 | 17321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap broke on p115-633 crew in route tomake repairs fetr 14:30LRM//COD 173 FROM BEGINNING OF OUTAGE//OPEED AT 1345 CLOSED @ 1403
2183 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-06-25 18:42 | 2017-06-25 18:57 | 1154 | 15 | 4044111 | 17310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED BREAKER TO SAFELY BY REGULATORS. SJGC FEC57, FP (ADDED)
2184 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2022-04-06 14:33 | 2022-04-06 15:58 | 498 | 85 | 4730951 | 17280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Ph A only is open on source side of 37830231A00054 // cod 164 // mechanical jumper on this pole (in place for future job) has failed and A phase form this point onward is de-energized//cod 164//iso 37830231A00054//opened all 3 phases on RECL 37830231A20329 in order to make repairs // addtl 334 customers interrupted @ 1548 // restored all cust (498) at 1558 //
2185 | South Williamson | 3200302 | BELFRY | TOLER | 2021-08-18 07:18 | 2021-08-19 13:30 | 14 | 1812 | 4101711 | 17277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | bad 75kva transformer//6 CUSTS RESTORED//2 CUSTOMERS REMAIN OUT //BAD UNDERGROUND THAT CAN NOT BE LOCATED AT THIS TIME//NEED A LINE CREW AND A TECH WITH A UNDERGROUND LOCATER// line fuse was never out just the one transformer
2186 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-08-15 10:18 | 2022-08-15 17:02 | 45 | 404 | 4742751 | 17234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutouy broke on 1065-15, caused pole to burn opened xmfr @ 10:18.will need line crew and pole replaced Released by crew 077H20///Opened Recl 38831065000009 (45 COD) at 1040 restored 1702
2187 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-10-21 15:56 | 2016-10-21 20:17 | 66 | 261 | 4040481 | 17226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 66 FROM BEGINNING//POLE 1123-7126 BURNT OFF POLE 1123-7060 OPENEDFUSE 16;30 NEED TWO 8FT. CROSS ARMS AND 2-CUTOUTS SEND TO VERNONPOLE 1123-7126 BURNT OFF POLE 1123-7060 OPENEDFUSE 16;30 NEED TWO 8FT. CROSS ARMS AND 2-CUTOUTS SEND TO VERNON RELEASED BY CREW 078S08/FETR2100/VEM/REPAIRS MADE AND ALL CUST RESTORED 2017/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB AJB
2188 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-06-02 18:45 | 2015-06-02 23:10 | 65 | 265 | 4503551 | 17225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED POLE 38830272000042 NO TRUCKS #4 COPPER PRIMARY BURNT OFF AT BASKET /TAGGED 38830272000040 TO KYDDC RELEASED BY CREW 078S03. CREW ON SITEREPAIRS MADE,,ALL POWER RESTORED VER/CRB AJBC FEC44
2189 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-05-25 11:30 | 2020-05-25 17:25 | 90 | 355 | 4903401 | 17224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | C phase only down @ pole 1074-A-349 (13cc) due to incorrect sleeve that had been installed burning up./ Primary is in the clear but will need to open all three phase switches on pole 1074-A-339 when crew arrives to repair. (77cc additional)/ This is across creek on hillside but should be able to work with big bucket./ This is #2 stranded copper wire./ Opened Switches 38831074A00339 @1449 (77cc)/ all 3 switches closed at 1725 on pole 38831074A00339
2190 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-09-04 17:25 | 2020-09-04 22:07 | 61 | 282 | 4433011 | 17202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | failed switch on C phase on 38821038B00237,trk app//COD 61??//opened RECL 38821062C00279 (ph c) to make repairs @ 2158 // closed @ 2207// (cod 61)
2191 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2017-07-24 11:58 | 2017-07-24 12:09 | 1563 | 11 | 4172721 | 17193 | TRANSMISSION STATION | EQUIPMENT FAILURE | CAPACITOR | SDB / 1158-1209 / EMERGENCY 138KV BUS 1 OUTAGE TO SAFELY REMOVE 138KV CAP BANK FROM SERVICE. 1563 CC// VER/DBM . L3/HFP XXXHFP SJG
2192 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-01-11 00:57 | 2009-01-11 09:48 | 47 | 531 | 54160-1 | 17183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116101//40/5 POLE BURNT OFF CALLED FOR CREW AND TECH ALSO/TRUCKS OK/ALSO BRING 50KVA TRANSFORMER SINGLE BUSHING RELEASED BY CREW 078S03/CREW ON SITE/FETR0730/VEM/RESTORED LINE FUSE ON POLE182-207 AT 0647/FUSE MELTED OUT AT 0651/INSTALLED 30T AT 0659/CUSTS O MD FILED VER/LDA L3/KEP IDC XXXX
2193 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-09-10 13:32 | 2018-09-10 16:54 | 85 | 202 | 4077171 | 17170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RECLR IS OPEN,WILL PTRL/////////POLE 984-16,LOOP SOMEHOW WAS LAYING AGAINST POLE.PULLED IT AWAY,WILL CLOSE RECLR BACK IN///////CLOSED&RESTORED
2194 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-03-06 09:07 | 2009-03-06 09:44 | 464 | 37 | 55563-1 | 17168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3311103//SERVICER IS PATROLLING// A & C PHASE NOT MAKING CONTACT ON GOAB SWITCH ON POLE # 435-23, WILL NEED TO OPEN STATION BREAKER... MADE REPAIRS RESTORED POWER AT 09:45//VER/CRB IDCC TOF0639
2195 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-07-04 22:52 | 2011-07-05 01:00 | 134 | 128 | 4464801 | 17152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR? ON POLE 37830296B31286---- BROKEN GUY LAYING ON TRANSFORMER LEAD, TRANSFORMER FUSE BLOWN AND ARRESTOR BLOWN ON POLE 37830296B21182 --- POWER RESTORED. VER/PDP IDC XXXX
2196 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2022-01-17 09:47 | 2022-01-17 14:15 | 64 | 268 | 4369601 | 17152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | pri. loop @ 1145-71 bad connection on main line, crew reqd. send to e. bear to repair. Released by crew 078S07 crew on site going to open rec on pole1145-201 to make repairs not by truck fetr 15:30 LRM rec opened @ 13:23 all pwr restored 14:15 please close ticket LRM Released by crew 078H06
2197 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-05-29 22:45 | 2008-05-30 17:48 | 15 | 1143 | 52738-1 | 17145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3308503// 3 PHASE POLE BROKE AT PHONE //POLE 318-34== C PHASE RECLOSER OPEN, CONTRACTORS ARE IN THE PROCESS OF RUNNING NEW LINES NEED TO WAIT TILL SUNRISE TO SAFELY TRACE OUT LINES AND REPLACE POLE//COD 25//OPENED AB PHASES @ 0925 TO WORK SAFELY//THIS INTERRUPTED 49 MORE CUSTOMERS//RESTORED ALL CUSTOMERS 1748// VER/DBM IDC XXXX
2198 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2015-01-21 10:03 | 2015-01-21 12:09 | 136 | 126 | 4948931 | 17136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED LOOSE AT POLE38831121D30415 ,MIDDLE PHASE RECLOSER OPEN FROM BEGINNING OF OUTAGE//HOT LINE CLAMP BURNED LOOSE AT POLE 415 , A PHASE ( CENTER PHASE AT POLE 415 ) . OPENED 2 OUTSIDE PHASES AT 11:50 AND REENERGIZED ALL 3 PHASES AT 12:09 , ALL WORK COMPLETE // GXJ RELEASED BY CREW 074S03 VER/CRB // PER VOICE REC - TROUBLE @ CENTER PHASE RECL `A` PHASE PER SERVICER - COULD NOT VERIFY WITH BUS OBJ OR SCADA/// L3/HFP XXX AJB
2199 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-10-03 11:18 | 2009-10-03 12:30 | 238 | 72 | H66272-1 | 17136 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | LOW SIDE SURGE ARRESTOR TO 69-12KV TR IN STATION FAILED CAUSING HIGH SIDE FUSE TO 69-12KV TR TO BLOW. //VER/GAH IDCC DUP TO OPEN TRANFORMER, OTHER TWO PHASES XXXX
2200 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-02-28 13:47 | 2017-02-28 15:52 | 137 | 125 | 4428711 | 17125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STEPDOWN OPEN ON POLE38831007D40164// 2 BAD CUTOUTS ON HIGH SIDE OF STEP DOWN ON POLE 1007-D4-164, WILL HAVE TO OPEN 3 REC. ON POLE 1032-B1-148. OPENED @1500, CLOSED @1552. // VER/CRB // CALLED SERVICER ONLY B PHASE OUT ON ARRIVAL SEE 4428931 FOR ADD OUTAGE (256 CUST) = L3/HFP HFPC CNT235 AJB
2201 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-11-01 10:00 | 2014-11-01 14:50 | 59 | 290 | H4679871 | 17110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED 40/5 POLE POLE 268D21 NEED DUMP TRUCK TO SET POLE/OPEN TAG AND GROUND AT 268-27 TO TACKETT/268D27 OPEN AT 1000 HRS RELEASED BY CREW 078S03,,CREW ON SITE,,POLE REPLACED,,ALL POWER RESTORED, WORK ORDER HAS BEEN WRITTEN// CLOSED @ 14:50// COD 3+59 // DUP OF 4679871 WHEN SW WAS OPENED // VER/HFP L3/HFP AJB
2202 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-12-18 07:37 | 2016-12-18 09:07 | 190 | 90 | 4210931 | 17100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BROKE CUTOUT ON POLE 796-232//REPAIRS MADE////RESTORED 9:07//COMPLETE//EM SJG
2203 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-01-24 19:01 | 2010-01-24 20:16 | 245 | 75 | 58928-1 | 17083 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | RELATED TO 58887-1//AFTER PATROLLING, SERVICER TRIED REC 141-252 & STATION BREAKER LOCKED OPEN @ 1901//DA SCHEME OPENED DEVICES 164-275, 165-267, 141-423//DA SCHEME CLOSED 164-3641 @ 19:01 AND 116-45 @ 19:02// 245 CUST REMAIN OUT//AFTER ISOLATING REC 141-252, BREAKER CLOSED @ 19:59// N.C. SWS 164-275 CLOSED @ 20:05//N.O. SWS 164-3641 OPENED @ 20:05//N.C. SWS 165-267 CLOSED @ 20:15//REC 141-423CLOSED@ 20:16//N.O. SWS 116-45 OPENED @ 20:22//DA SCHEME BACK NORMAL CLOSING TRBL//VER/DBM IDC XXXX PLC CC RELAY
2204 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-09-03 22:38 | 2022-09-04 09:35 | 26 | 657 | 4834311 | 17082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Part of previous outage which was restored/attempted to contact customer but call disconnected/will check during ldaylight hours.. got cutout replaced and xmfr back on @ 09:35
2205 | Hazard | 3309302 | VICCO | JEFF | 2009-03-11 16:19 | 2009-03-11 18:45 | 117 | 146 | 57311-1 | 17082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 28888054 /// CREW HAD TO OPEN RECLOSER ON POLE 37830322B00302 TO ISOLATE POLE THAT IS BURNING OPENED @ 1619//COD 117// VER/DBM IDC XXXX
2206 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-29 12:25 | 2008-03-29 13:33 | 251 | 68 | 61895-1H | 17068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401/// 41 OUT @ 0930 - OPENED RECLOSER @ 1225 TAKING OUT ADDITIONAL 248 CUSOTMERS// BACK ON @1333 // THIS WAS ASSOCIATED WITH SWITCHING THAT TOOK PLACE - TYING BECKHAM/HINDMAN AND GARRETT/LACKEY// 41 CUSTOMER OUT FROM WHERE LOOP BURNT OPEN @ POLE 158-1 RFOM 0930 UNTIL REST @ 1333// OPENED REC ON 182-257 @1225 TO ISOLATE AND MAKE REPAIRS// // VER/TOM IDC XXXX
2207 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-01-07 10:28 | 2014-01-07 11:52 | 203 | 84 | H4245781 | 17052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE OUT ON POLE 402-418 CONDUCTORS DOWN ON POLE 378-1 WILL NEED TO DROP RECLOSERS ON POLE418 TO MAKE REPAIRS//COD 51 (SCADA ALSO INDICATES B PHASE FAULT) (CALLS BEFORE SERVICER`S ARRIVAL CAME IN ON ALL 3 PHASES)//B PHASE OUT ON POLE 402-418 CONDUCTORS DOWN ON POLE 378-1 WILL NEED TO DROP RECLOSERS ON POLE418 TO MAKE REPAIRS//// 0PENED RECLOSERS AT 1028 CLOSED THEM AT 1152 A&C PHASE OUTAGE /// VER/HFP L3/HFP IDC XXXX
2208 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-10-17 14:50 | 2015-10-17 20:00 | 55 | 310 | 4357231 | 17050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 HEDRIX BURNED APART AT SPACER, TRUCK ACCESS//COD 55 FROM START C PHASE //OPENED SOLID BLADES ON POLE 38831074D00062 @ 1901 //OPENED RECLOSER38831074D00032 @ 1859//CLOSED IN SOLID BLADES @ 1955 PICKING UP 22 COD//CLOSED RECLOSER PICKING UP REMAINING CUSTS @ 2000//1/0 HEDRIX BURNED APART AT SPACER, TRUCK ACCESS. ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/CRB AJB
2209 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-05-11 09:03 | 2018-05-11 11:26 | 119 | 143 | 4335901 | 17017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPAIR CUTOUT THATS BAD AND ARM restored @ 1126
2210 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-11-27 01:50 | 2022-11-27 09:43 | 61 | 453 | 4182641 | 16998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | step down blew the lid and is on fire on pole 56-A4-143 . opened reclosoure on pole 55-223 @ 03:39 isolated and placed tags for rick maggard. no grounds placed Released by crew 077H24.. replaced stepdown , closed recloser @ 09:09 opened @09:29 to replace insulator restored @ 09:43 LR- The 1st All Out call came in at 0150
2211 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-10-28 09:19 | 2009-10-28 11:48 | 114 | 149 | 61301-1 | 16986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW OPENED OUTSIDE PHASE RECLOSERS A&C PHASES 112 CUSTOMERS TO ALLOW THEM TO REPLACE POLE BURNT OFF IN ORDER 59561-1 L3/HFP IDC XXXX
2212 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-10-25 12:52 | 2010-10-25 14:20 | 193 | 88 | H62700-1 | 16984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ISO 38831125B00772 "A" PHASE COD-53.PHASE A ONLY WAS OUT.XARM BROKE @ 38831125B00187 HAVE CREWS ENROUTE OPENED OTHER 2 PHASES AT 1252 RESTORED 1420 VER/KEP L3/KEP IDC XXXX
2213 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2014-08-10 10:22 | 2014-08-10 16:31 | 46 | 369 | 4350011 | 16974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIMARY WIRE DOWN ONLY === NEED LINE CREW AND BIG BUCKET AT POLE 37830395000013 === ALSO LINE FUSE OUT GOING TO OIL WELL IN HEAD OF HOLLOW POLE 37830395000032 === RELEASED BY CREW 077S03//COD 46// VER/DBM AJB CUST CALL INFRONT OF PFL AND BEHIND OCR.
2214 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-02-12 18:25 | 2019-02-12 22:28 | 153 | 243 | 4782791 | 16969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire is burnt down between recloser pole 278-335 and regulators on pole 278-258, express phase to Steer Fork is the one down, will need crew and big bucket // restored @ 2115
2215 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-02-05 16:12 | 2019-02-05 23:39 | 105 | 432 | 4756571 | 16968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | closed line fuse at 18:09, //L/F 37830030000074 CAME BACK OUT//OPENED L/F 37830054000022 AND CLOSED L/F 37830030000074 @ 1920//OPENED SB ON POLE 37830054000026 AND CLOSED L/F 37830054000022 @ 2034//sb on pole 37830055000092 also open//LIFTED HT ON SOURCE SIDE OF POLE 37830055000088//LF 37830054000022 WENT BACK OUT @ 2153 CLOSED BACK @ 2207//closed line fuse at 18:09, patroled line couldnt find anything//L/F 37830030000074 CAME BACK OUT//OPENED L/F 37830054000022 AND CLOSED L/F 37830030000074 @/// 5 customers restored @ 2207, tried new fuse on pole 37830054000026 multiple times until fault found, restored final 35 customers @ 2239 ARN ¦¦ LOOKS LIKE 4756871 SHOULD BE RELATED TO THIS - HFP//// 4756871 had 3 cust out at 1843, then transferred to this outage.
2216 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-05-19 10:28 | 2017-05-19 13:45 | 86 | 197 | 4817141 | 16942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, SHOT RECLOSER, STAYED ABOUT A MINUTE AND CAME BACK OUT. FOUND BAD CUTOUT ON POLE 1064-2, TOOK CLAMP OFF, XFMR DOESNT FEED ANYTHING, ALL POWER 38831040000018 L3/HFP XXXHFP AJB
2217 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-07-08 21:04 | 2012-07-08 23:00 | 146 | 116 | 4626161 | 16936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE 3 SINGLE RECLOSERS ON POLE 143C-411. ONLY THE A-PHASE RECLOSER IS OPEN. I AM PATROLLING LINE NOW. "A" PHASE ONLY COD-145 A LINE FUSE CUTOUT BROKE INTO ON POLE 143-363. TOP HALF WAS LYING AGAINST METEL BRACKET. I CHANGED CUTOUT. I AM GOING TO CLOSE RECLOSER ON POLE 143C-411WE HAVE 3 SINGLE RECLOSERS ON POLE 143C-411. ONLY THE A-PHASE RECLOSER IS OPEN. I AM PATROLLING LINE NOW. A LINE IDC CHANGED COUNT FROM 366 XXXX
2218 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-09-20 23:44 | 2010-09-21 11:30 | 26 | 706 | 51727-1 | 16916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SERVICER ON SITE , UNDERGROUND TROUBLE , D/S CALLING OUT CREW TO TEST CABLE .CALLED P TOLLIVERS CREW . AT 0330 , CREW CLOSED RISER FUSE . HOT TO PM 20-442. CREW WILL CONT. CABLE TESTING. RELEASED BY CREW 078H03ALL POWER RESTORED AT 11:30 (AM) 9/21/10 VER/KEP L3/KEP IDCC CDC83 XXXX
2219 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-03-22 03:35 | 2017-03-22 12:58 | 30 | 563 | 4576631 | 16890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DDC TAGS AND GROUNDS AT POLE 473-28 WIRE DOWN AT POLE 38830473000048, TO 50 TWO SPANS #6A, IF BRING SMALL BUCKET, MAY BE ABLE TO USE IT, CREW REQUIRED//DKM/0915/ CRAIG CRAMPTON GIVEN PERMISSION TO REMOVE DDC TAGS AND REPLACE WITH HIS OWN,TAGGED TO CREW3658 09:22./ ISO 38830473000028/ COD 30/ VER/BOW AJB
2220 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-09-11 13:18 | 2019-09-11 18:25 | 55 | 307 | 4004171 | 16885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | got bad 333 stepdown need 500 to replace with Released by crew 077S05 lead burned into and burned hole in stepdown power restored at 18:25 L3/HFP
2221 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2017-03-28 22:45 | 2017-03-29 00:59 | 126 | 134 | 4593131 | 16884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2150105 CC=1398/ SCADA INDICATES CB LOCKED OUT/ BAD CUTOUT ON POLE 1017-B1-276/ CREATED PO ORDER # 4593351 FOR XFMR CUTOUTS/ RESTORED CB AT 0059 REST 1393 CUSTS/ VER/JMD AJB
2222 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-16 19:46 | 2008-06-17 05:49 | 28 | 603 | 66069-1 | 16884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OFF ON POLE 223-33, WILL HAVE TO OPEN LINE FUSE TO PUT LOOP BACK ON.MADE LOOP UP POWER RESTORED POLE 33 BETWEEN POLE 223-32 & 223-101 28 CUST OUT DUPLICATED THIS RECORD FOR LINE FUSE OUTAGE & CORRECTED CUSTOMER COUNTS. VER/HFP IDC XXXX
2223 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-01-01 20:19 | 2018-01-02 04:35 | 34 | 496 | 4693691 | 16864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad bushing on step down on pole 37830505000050.power restored at 4:35
2224 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-03-04 02:45 | 2012-03-04 03:16 | 544 | 31 | H4543151B | 16864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CENTER PHASE BURNT DOWN AT 1098-280 HOT ON THE GROUND OPENED CB AT 2333 .PERFORMED SWITCHING TO RESTORE PART ALL WORK COMPLETE / VER/KEP DKG IDC XXXX
2225 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2009-05-05 11:42 | 2009-05-05 14:45 | 102 | 183 | 55204-1 | 16862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ON SITE, TWO RECLOSERS OUT ("A" &"C" PHASE OUT ONLY TILL 1315 OPENED GOAB POLE#868-205), PATROLLING LINE, XARM BROKE AT POLE# 868-D-74, CALLED R MARCUM FOR HELP CLOSED RECLOSER AT 1323ON SITE, TWO RECLOSERS OUT ( A & C PHASE OUT ONLY TILL 1315 OPENED GOAB POLE#868-205), PATROLLING LINE, XARM BROKE AT POLE# 868-D-74, CALLED R MARCUM FOR HELP CLOSED RECLOSER AT 1323. POWER ON AT 14:45 MADE DUP FOR "B" PHASE VER/KEP L3/KEP IDC XXXX
2226 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-06-04 20:25 | 2008-06-05 19:50 | 12 | 1405 | 58358-1 | 16860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRI RISER PULLED OUT OF BUSHING, WILL NEED TO OPEN LINE FUSE ON POLE 45-3518 VER/ARN
2227 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-09-02 14:26 | 2008-09-02 20:10 | 49 | 344 | 58615-1 | 16856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 077S08//3308401POLE 110-200 WE HAVE HIGH SIDE OF STEPDOWN OUT, OPEN REC. ARE READY TO TRY TO CLOSE HIGH SIDE FUSE//BAD 500KVA STEP-DOWNRELEASED BY CREW 077S08//3308401POLE 110-200 WE HAVE HIGH SIDE OF STEPDOWN OUT, OPEN REC. ARE READY TO TRY TO CLOSE HIGH SIDE FUSE. STEP-DOWN BURNT UP . JAMES SUMNER CREW TO CHANGE IT OUT. RELEASED BY CREW 077S08 - CLOSE IN STEPDOWN @ 2010 VER/TOM IDCC PN163, CDC92 XXXX
2228 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-12-31 18:35 | 2014-12-31 20:52 | 123 | 137 | 4895521 | 16851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A PHASE RECLOSER OUT ORIGINALLY (122CUSTOMERS & 1A&C PHASE CUST)/ PRIMARY LINE IS DOWN AT THE RECLOSER POLE/ #2 ALUM DOWN @ RECLOSER/ NEED LINE CREW TO REPAIR/ TRUCK OK/ RECLOSER OPEN & ISO @ 254D-464 & TAG TO RON/ WIRE BROKE OFF AT THE BASKET/---OPENED C PH. OCR (155 CUSTOMERS & 1 A&C PHASE CUST) @ 20:35--REPAIRED #2AA PRIM AND STIRRUP--RESTORED BOTH A & C PH. ORCS @ 20:52----TBL TKT COMP/ DUPLICATE IN HOIS/ ISO 38830254D00464/ COD TOTAL 278 AJBC CNT278 INTL PH A OUT. SEE H4895521 FOR B PH OUTAGE.
2229 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-06-05 17:59 | 2019-06-06 01:11 | 39 | 432 | 4433641 | 16848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | rotted windstream pole 1098-581. tech, line crew, yard dog, NO TRKS. Released by crew 078S07/ Released by crew 078H07/ ISO 39831098C00531/ COD 39 L3/HFP
2230 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2014-02-02 09:30 | 2014-02-02 13:15 | 131 | 225 | 4336321 | 16833 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PHASE A REC OPEN ARRESTER BLEW UP ON CSP XFMR 930-25. ISOLATED XFMR 930-25 AND CLOSED RECLOSER ON 930-85 @ 11:37 RESTORING ALL BUT ONE CUSTOMER. ADDITIONAL PERSONNEL ENROUTE TO ASSIST. INSTALLED NEW CUTOUT AND ARRESTER ON XFMR 930-25 AND CLOSED IT AT 13:15 RESTORING REMAINING CUSTOMER. SH//COD 131// VER/DBM L3/HFP IDC XXXX
2231 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-09-14 00:24 | 2020-09-14 12:05 | 24 | 701 | 4459911 | 16824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Difficult location/holding for crew in AM-no tags or grounds/wire down @ pole 495-19. at least one span of primary. could not tell what took it down.. hold for crew for in the morningwire down @ pole 495-19. at least one span of primary. could not tell what took it down.. hold for crew for in the morning Released by crew 077S11
2232 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-04-24 10:23 | 2012-04-24 16:11 | 360 | 348 | 4702111 | 16820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CSX REMOVING OLD LINE, POLE WAS ROTTEN AT THE GROUND. FELL OVER, 1072-5507 IS A 502, ALSO FOUND POLE 1072-5523 TO BE ROTTEN AT THE GROUND IT IS A 454 THAT NEEDS CHANGED TOO, CREW REQ. RELEASED BY CREW 078S06/ TWO CREWS ON SITE/FETR 1630/VEM/NO AS BUILT/TECH TO WRITE JOB/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1611/PLEASE CLOSE TICKET//VEM RELEASED BY CREW 078H14 COD-41 ISO LF 39831072C45522 VER/HFP L3/HFP IDC APPEARS TIME OFF WAS WHEN WE OPENED SWITCH XXXX
2233 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-07-20 01:06 | 2011-07-20 15:05 | 20 | 839 | 4565611 | 16780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 SOLID COPPER DOWN FROM POLE 333-35 TO 333-37. CUT WIRE OUT OF CUST DRIVE WAY ON POLE 333-37. PLACED GROUNDS ON POLE 333-107. WIRE BROKE AT RUNAROUND ON POLE 333-35 , NO TRUCKS TO THIS POLE. NEED MAN TREE CREW TO CUT LINE CREW AWAY TO POLE 333-35. NEED TO DO THIS IN THE DAY TIME. RELEASED BY CREW 078S01//VER/CRB IDC XXXX
2234 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-06-04 07:24 | 2011-06-04 07:50 | 644 | 26 | H4230141 | 16744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 345 CUSTOMERS OUT // A PHASE LOOPS BURNT OPEN AT POLE 833-474 CREW ON SITE. WILL HAVE TO OPEN KENWOOD-HAGER HILL BREAKER TO MAKE REPAIRS (EST. 30 MINUTES). OPEN STA BREAKER @ 0724 INTERRUPTING ADDITIONAL 644 CUSTOMERS // CLOSED STA BREAKER AT 0750 //VER/GAH IDCC TOF0525 XXXX
2235 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-04-19 07:30 | 2012-04-19 08:40 | 239 | 70 | 4686331 | 16730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *** PART OF ORDER 4686271 ( RESTORED BY ACCIDENT) CUST CALLS IN THAT ORDER ARE STILL ACTIIVE ALL OUT CALLS.WILL DISPATCH TO DAY SHIFT SERV. OPENED OCRS AT POLE 38831098A00606 AT 07:30 , THREE PHASE RECLOSER POLE ///VER/CRB IDCC TOF0544 XXXX
2236 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-05-11 15:36 | 2014-05-11 16:29 | 315 | 53 | 4686031 | 16695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN ON POLE 454-6082, OPENED REC A PHASE AT 16:11 BACK ON AT 16:29. IDC PN IS FOR RECLOSER XXXX
2237 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-08-12 09:26 | 2013-08-12 15:21 | 47 | 355 | 4653021 | 16685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE NEED LINE CREW REPLACE POLE 40TRUCK OK,ISO ON POLE 182-6016 GROUNDS@182-6017 TAG TO DDC RELEASED BY CREW 078S05/CREW ON SITE/CHANGED TAGS/FETR 1530/VEM/TECH WROTE JOB NO AS BUILT/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1521/PLEASE CLOSE TICKET/THANKS/VEM//COD 47 VER/HFP L3/HFP XXXHFP
2238 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-06-19 11:00 | 2018-06-19 11:30 | 556 | 30 | 4620811 | 16680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | EMERGENCY OUTAGE TO REPLACE DEFECTIVE CROSSARM AT POLE 38830044B00128 // COD-556 ISO OCR 38830044A00116 OFF @ 1100 ON @ 1130
2239 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2022-09-12 08:23 | 2022-09-12 10:33 | 128 | 130 | 4868591 | 16640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Top of pole 48-D3-150 is on fire and burnt the crossarm in two, will have to open 3 switches @48-D3-147 to make repairs. Myles R. crew en route to help with repairs. Opened all 3 switches @48-D3-147 @0825.///restored at 1033
2240 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-05-20 03:05 | 2009-05-20 06:41 | 77 | 216 | 50920-1 | 16632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN POLE 1058-401,SAMMONS IS GETTING HELP.// COD-77 // OPENED RECL 1058-370 @ 06:08 // COD-57 //IN ORDER TO PUT WIRE UP.MADE REPAIRS AND RESTORED AT 06:41.HAD BURNED IN TWO AT CONNECTION OF SWITCHES LETTING 1 PHASE FALL TO GROUND// ALSO SEE OUTAGE #H50920-1 VER/LDA IDCC PN68 XXXX
2241 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-05-28 19:53 | 2018-05-29 09:44 | 20 | 831 | 4512131 | 16620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B phase l/f open @75-2, found no trouble, tried l/f and did not stay, line on side of the mountain, will have to wait and patrol in daylight. Released by crew 074S05/// found a piece of old ground wire that had fallen out of bottom of arm and had laid down on top of arrester @ pole # 522-9// removed wire and refused line fuse @ 09:44 and restored service
2242 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-09-10 10:35 | 2019-09-10 10:59 | 692 | 24 | 4999351 | 16608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 211-176 split out/692cc/ Open 1035 Close1059
2243 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-04-09 14:15 | 2009-04-09 16:02 | 155 | 107 | 50803-1 | 16585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTENING ARRESTER SHORTED OUT ON POLE 215-417, TAKING OUT RECLOSER ON POLE 239-307. I CLEARED ARRESTER AND IM GOING AROUND TO CLOSE RECLOSER.I CLOSED RECLOSER ON POLE 239-307 IN AT 16:02 AND IT STAYED IN.//COD 155// VER/DBM AJB
2244 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-01-06 14:26 | 2022-01-06 14:45 | 872 | 19 | 4312331 | 16568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1173992/ Hold Order/ Per John Blankenship neutral connection arcing where neutral deadends on steel structure for the Fleming-McRoberts 12kV Line/ Opened FLEMING - MCROBERTS 12KV - CB C @ 1426 closed @ 1445
2245 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-11-28 22:32 | 2015-11-29 02:07 | 77 | 215 | 4490401 | 16555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 43-12 BAD CO, BURNT OFF 8ARM//WILL HAVE TO OPEN B PHASE RECLOSER WHEN READY TO MAKE REPAIRS//TOMPOLE 43-12 BAD CO, BURNT OFF 8ARM RELEASED BY CREW 078S07.. CREW ON SITE TO CHANGE CROSSARM ETR 0300.. OPENED B PHASE RECLOSER ON 44-606 TO SAFELY CHANGE CROSSARM AT 01:37 (OUTAGED 110 CC) - CLOSED B&C PHASE RECLOSERS AT 0207 RESTORING ALL CUSTOMERS// - WILL NEED TO DUPLICATE OUTAGE IN HOIS TO ACCOUNT FOR SECOND OUTAGE//TOM VER/TOM L3/TOM
2246 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-01-14 14:08 | 2017-01-15 01:36 | 24 | 688 | 4297901 | 16512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830501000325 25T LAT BLOWN--38830501000464 BROKE 19,9 C/O--REPLACED C/O--LAT IN AT 01:36--ALLGOOD--DS011517//COD 24 L3/HFP AJB
2247 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-10-15 19:18 | 2019-10-16 00:23 | 123 | 305 | 4143221 | 16475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 37830247D00967 burn off at cutout,need 50c2 pole,19.9kv //
2248 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-04-23 11:49 | 2012-04-23 14:48 | 92 | 179 | 4697101 | 16468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN AT REC, POLE 91-6105 TO 91-A-19 6-A COPPER WELD NEED TREE CREW AND LINE CREW TO MAKE REPAIRS WAIT FOR TREE CREW AND LINE CREW HAVE BEEN DIS-PATCHED RELEASED BY CREW 078S09//PRT ON SITE FOUND BAD CONNECTION ON HOT TAPS FETR 15:30///,RECLOSER LEFT OFF LINE 91-6105 DEFECTIVE PLACE IN ABNORMAL POWER RESTORED AT 14:48 PRT// VER/KEP IDC XXXX
2249 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-04-26 07:20 | 2014-04-26 11:15 | 70 | 235 | 4636421 | 16450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED REC AT 0720 FOR POLE FIRE ON PO#4636391//COD 70// VER/DBM L3/HFP IDC XXXX
2250 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-11-24 02:30 | 2018-11-24 06:12 | 74 | 222 | 4471381 | 16428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /PH C only (cod-74) open on 784-513. Patrolling. Line fuse cutout broke on 808-109 - difficult location. Replaced line fuse cutout and restored 40T line fuse on 784-513 at 6:12. sh L3/HFP
2251 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-10-23 10:53 | 2017-10-23 11:40 | 349 | 47 | 4478801 | 16403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 38830115C00089.REC OPEN @ 115-633, BAS 19.9 C/O @ 115-89, REPAIRED, RESTORED @ 11:40 VER/AWD L3/HFP XXXHFP ACB
2252 | Hazard | 3303902 | LESLIE | WOOTON | 2017-10-09 09:21 | 2017-10-09 16:06 | 92 | 405 | 4433911 | 16398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER ON 37830366B00182 @ CLOSED @ 0940 OPENED RECLOSER ON 37830366B00182 TO ISOLATE POLE FIRE. ASSOCIATED WITH 4433001.RELEASED BY CREW 077S01 VER/AWD ACBC TOF 0817
2253 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-06-25 10:36 | 2010-06-25 15:55 | 58 | 319 | 57362-1 | 16382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARMS ROTTED AND BROKE ON POLE 120-148. WE HAD 1 RECLOSER OUT ON POLE 120-61. I OPENED OTHER 2 RECLOSERS LONG ENOUGH TO OPEN LINE SWITCHES ON POLE 120-243 AND CLOSED ALL 3 RECLOSERS BACK IN AT 11:30. CREW IS ON THE WAY. WE REPAIRED POLE AND CLOSED SWITCHES AT 120-423 AT 15:55. VER/KEP L3/KEP IDC XXXX
2254 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-02-03 00:18 | 2022-02-03 00:35 | 963 | 17 | 4425851 | 16371 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | DOL 1180514 // SCADA indicates station l/o @ 0017 // cod 963
2255 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-08-08 14:50 | 2016-08-08 20:38 | 47 | 348 | 4750231 | 16356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 1094404--RISER FUSE IS IN @ POLE# 37821082A40321, WILL B CHECKING.. CREW REQUIRED. URD PRIMARY OPEN BETWEEN XFMER # 37821082A40828 TO # 37821082A40830.. REPLACED TRANSFORMER AND ELBOWS POWER BACK ON //VER /RBP MLR AJB
2256 | Whitesburg | 3312901 | JENKINS | KONA | 2017-03-23 11:32 | 2017-03-23 15:10 | 75 | 218 | 4579981 | 16350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE 4580571***/ C PHASE LOOP BURNED INTO ON POLE 404-78 (75 CUST), WILL NEED BIG BUCKET, 556 WIRE(4) 556 CONNECTORS. / LOOP SLEEVE BURNT OFF OPEN UNDER SWITCHES PL 405A-474 AT 14:50 CLOSED AT 15:10 / ISO 37830404C00078/ COD 75/ VER/BOW AJB
2257 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-07-20 23:25 | 2019-07-21 02:15 | 96 | 170 | 4740121 | 16320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Opened recl on 37830374D00185 to isolate a pole fire on 37830374C00018bad insulator on pole 374-18, opened recloser on pole 374-185 to isolate..opened 2325bad insulator on pole 374-18, opened recloser on pole 374-185 to isolate..at 23:25.bad insulator on pole 374-18, opened recloser on pole 374-185 to isolate..at 23:25.made repairs restored power at 02:15.
2258 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-01-23 11:00 | 2009-01-23 12:20 | 204 | 80 | 59357-1 | 16320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001003//PATROLED LINE AND FOUND NO HAZARDS3001003// CONNECTION MELTED APART AT POLE 38830230000071, ARCING TRIPPED RECLOSURE OPEN. - SPOKE W/SERVICER FAULT POLE WAS NOT 23-71 POLE IS 230-176// VER/KEP L3/KEP MLR OK
2259 | Whitesburg | 3312901 | JENKINS | KONA | 2016-04-03 01:36 | 2016-04-03 02:22 | 354 | 46 | H4026721 | 16284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B-PHASE LOOP BURNT IN-TO ON POLE 405B-49 WHERE LOOP WAS MADE UP WITH SPLIT BOLT//B PHASE 211//. OPENED SWITCHES ON POLE 405-474 AT 1:36 AND CLOSED BACK IN AT 2:20//ORIGINALLY 135 B PHASE OUT/OPENED SWITCH OUTAGINING 354 CUSTOMERS// VER/ ADH AJB
2260 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-02-04 15:24 | 2012-02-04 20:00 | 59 | 276 | 4319951 | 16284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REC. OPEN ON POLE 279-251, CHECKING LINE/// CLOSED REC AT 17:10, STAYED IN 10 MINUTES AND WENT BACK OUT./// ARRESTOR BAD ON POLE 255-12, CUT IN CLEAR, POWER RESTORED. VER/KEP IDC XXXX
2261 | Hazard | 3310502 | HADDIX | CANOE | 2010-06-17 06:35 | 2010-06-17 07:30 | 296 | 55 | H1138560-1 | 16280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WR# 35603156 / POLE 51-42 HAS BROKEN CROSSARMS/ @1958 OPEN 52-108 / @2045 OPEN SW 121-A-152 / @2104 CLOSE SW 169-305 /RELEASED BY CREW 077S05///RELOCATED LINE OFF HILL SIDE PUT BESIDE ROAD, RESTORE POWER AT 5:57 AM @ 0635 OPEN N.O. 296 CC ALL CUST REST AT 0730 DUP ORDER CREATED TO SHOW OUTAGE TO REST CKTS NORMAL OUT OF PHASE SW. SEE ORDER 66562-1 VER/PDP
2262 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-07-14 20:12 | 2022-07-14 21:40 | 185 | 88 | 4491791 | 16280 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE HARDWARE | transmission crew on site needs 224-145 open to make repairs on structure // Opened recl at 2012 closed @ 2140
2263 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2010-05-17 05:18 | 2010-05-17 07:15 | 242 | 117 | 63584-1 | 16264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED BAD CUTOUT ON POLE 357-172 AND CLOSED STATION BREAKER BACK IN AT 0625 REPLACED CUTOUT ON POLE 357-172 AND PUT LAST CUST ON AT 0715 VER/HFP L3/HFP IDCC CNT243 FIELD RESTORED INSTEAD OF RELEASED XXXX
2264 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2021-06-13 11:52 | 2021-06-13 16:03 | 70 | 251 | 4728851 | 16262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | loop burnt at pole 37820010C00005 GOING TO OPEN SB AT POLE 37820011A00060 @ 1530 //COD 64 FROM BEGINNING OF OUTAGE
2265 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-04-11 02:00 | 2021-04-11 14:00 | 58 | 560 | 4440721 | 16240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Released by crew 078H03 restored first time at 1000/reopened at 1240 for repairs 427-111.Released by crew 078H0 open recloscure on 38830427000008 to replace a primary insualtor on 338830427000111Released by crew 078H0 open recloscure on 38830427000008 to replace a primary insualtor on 338830427000111,,opened reclosure at 12:40
2266 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2020-03-29 19:15 | 2020-03-29 19:56 | 396 | 41 | 4534791 | 16236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1004862/Emergency outage due to pole fire outside station/Fault pole 23-234/Opened sws at 37830023000239 to isolate after breaker opened @ 1915/Center pole top pin broke off @23-234 and let center phase fall against pole, pole is on fire will need to open Ivy Court circuit to make repairs. 30-45 minute outage. off 1915-1956/
2267 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-03-24 16:22 | 2018-03-25 17:46 | 29 | 1524 | 4050721 | 16234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | TAGGED TO KYDDC/ line fuse blown on pole 793-23///primary pulled out of sleeve at pole 793-41//down across road//need line crew and flaggers//i installed 300amp switch at pole 793-101& opened and tagged to KY DDC to isolate wire down//line fuse blown on pole 793-23////restored up to open switch at 20:35/rem tag 1611 AWD.
2268 | Paintsville | 3401101 | FALCON | FALC-OILS | 2013-07-07 13:58 | 2013-07-07 14:36 | 427 | 38 | 4480781 | 16226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | SCADA INDICATES FEEDER BREAKER LOCKOUT @ 1358 // RELATED TO ORDER 4478971//WHEN RESTORING RECLOSER 806-6, IT FAULTED INTERNALLY//CREWS WORKING TO ISOLATE RECLOSER IN ORDER TO GET FEEDER BREAKER BACK IN// TR NEVER OUT IN HOIS VER/PDP IDC XXXX
2269 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2010-03-11 16:16 | 2010-03-11 17:52 | 169 | 96 | 65173-1 | 16224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SCADA INDICATES FEEDER LOCKOUT @ 1616 //WE HAVE A LIGHTING ARRESTOR BAD ON POLE 37830048D20985 WHICH IS THE RECLOSER POLE CREW IS THERE REPLACING L/A NOW.// WE ALSO HAD SOME BAD LOOP INSULATORS BAD ON THE SAME POLE NOTHING ELSE WAS ON THE LINE... CLOSED IN AT 17:52 TIM MCCOY RELEASED BY CREW 074H10 VER/LDA IDCC TOF1619 XXXX
2270 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-01-03 06:54 | 2022-01-03 11:07 | 458 | 253 | 4265521 | 16220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Appears to be A phase only that is affected//broke sw on pole 1105-344// getting material to make repairs11 Released by crew 074H07 \\DOL 1173008
2271 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-07-05 05:30 | 2009-07-05 15:30 | 27 | 600 | 65251-1 | 16200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110903// HAVE A 454 POLE BURNTED OFF, ABOUT 3 FT OF THE TOP, THIS IS A 3 WAY PRIMARY DEADEND POLE, EVEYTHING SHOULD WORK BACK, WILL NEED TRACT MACHINE TO GET TO POLE, HAVE LINE FUSE OPEN ON POLE 1098-753, ALSO HAVE LINE GROUND BETWEEN POLE, 1098-3172 AND 1098-3153 RELEASED BY CREW 078S06 JIM LINKOUS CREW ENROU// VER/DBM// IDCC TOF0442 XXXX
2272 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-10-10 09:03 | 2009-10-10 21:21 | 35 | 738 | 54525-1 | 16171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR/ 32146582 POLE 1123-1101 65T UNDERGROUND OUT RELEASED BY CREW 078S08/BAD U/G CABLE/CREW IS WORKING TOWARDS A PARTIAL RESTORATION. 1327 RESTORED 1147 & 1148// 1447 RESTORED 1105// 1900 INTERRUPTED 1105// 2106 RESTORED 1105 & 1103// 2121 RESTORED 1104//VEM RELEASED BY CREW 078H14 //VER/GAH IDCC CDC83 XXXX
2273 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-02-27 09:36 | 2008-02-27 15:05 | 83 | 329 | 50850-1 | 16161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401/// C PHASE RECL OUT 83 CUST-HFP182-143 IS BURNT OFF, CAN ISOLATE ON POLE # 182-142//@ 1143 RECL CLOSED REST 41 CUST//@ 1206 SECTIONALIZER CLOSED REST 16 CUST/RELEASED BY CREW 077S02NEW FUSE ON POLE 182/142 25 T SEND TO GRAPHICS VER/HFP IDC XXXX
2274 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-03-25 15:15 | 2009-03-25 20:41 | 85 | 326 | 61443-1 | 16158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116101//@ APPROX 1515 OPENED RECLOSER IN ORDER TO ISOLATE POLE FIRE ON POLE 181-159//COD 85//... CUT LOOP ON POLE 181-61 AND CLOSED RECLOSER UP TO NEW ISO POLE @ 1537//REMAINING CUST OUT 47// INSTALLED LINE FUSE ON POLE 181-159 (30 T) ALL POWER RESTORED AT 20:41//VER/CRB IDC XXXX
2275 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-10-09 15:41 | 2015-10-09 18:05 | 292 | 144 | 4333271 | 16149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LEFT HAND PHASE BACK TO STATION (C PHASE 292 CUSTOMERS)/ BAD LIGTNING ARRESTER ON CSP TRANSFORMER @ 38830900000146/ ISO 38830876B00028/ COD 292 BAD LIGHTNING ARRESTER ON POLE 900-146 TOOK RECLOSER ON C PHASE OUT AND BURNED HOLE IN TANK OF XFMER ///GOT ARRESTER AND XFMER ISOLATED ON 900-146///CLOSED C PHASE RECLOSER ON POLE 876-28 @ 16:36///ALL CUST BACK ON EXCEPT 1 FEED OFF BAD XFMER ON POLE 900-146///XFMER 900-146 BACK ON AT 18:05///COMPLETE BR VER/CRB // C PHASE PER SCADA - L3/HFP XXXHFP AJB
2276 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2012-09-18 17:09 | 2012-09-18 18:03 | 299 | 54 | 4065691 | 16146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 2150502// CC-1002//TODD HELSEL REPORTED THAT HETRIED TO BYPASS A BAD RECLSOER AT POLE 893-A-277 AND CAUSED CB TO LOCK OUT....VER/DWH IDC XXXX
2277 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-02-01 16:52 | 2015-02-01 22:33 | 55 | 341 | 4979171 | 16139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRI. CONDUCTOR AT POLE 358-439 BURNED INTO UNDER TIE WIRE. IT OPENED RECLOSER AT POLE 359-113. I CUT A LOOP AT DOUBLE DEADEND POLE 359-34. I CLOSED RECLOSER AT 359-113 IN AT 18:55. HELP IS ON THE WAY. I OPENED RECLOSER AT 22:24 SO WE COULD PUT HOT TAP BACK ON LINE AT 359-34. WE CLOSED RECLOSER AT 22:33 / ISO 37830359A10113/ COD 55 AJBC CNT55 SEC REST STEP. SEE H4979171
2278 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2011-04-21 01:20 | 2011-04-21 15:29 | 19 | 849 | 61573-1 | 16131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39658008 // POLE 38830069C24745 HAS TOP BURNT OFF---INSTALLED TAG AND GROUND AT POLE 38830069C24741--BAD LOCATION--NO TRUCK--NEED TO WORK IN MORNING-NEED TECH FOR POLE REPLACEMENT--NEED MANUAL TREE CREW RELEASED BY CREW 078S07//P TOLLIVER ON SITE//POLE REPLACED AT 13:00 WAITING ON TREE CREWS SEND TO M PHELPS PRT// RELEASED BY CREW 078H03 RELEASED BY CREW 078H12 COD-19 ISO LF 38830069C24741 VER/HFP L3/HFP IDC NEEDED A LOT OF TREE TRIMMING AND YARD DOG XXXX
2279 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2015-07-19 13:56 | 2015-07-20 12:20 | 12 | 1344 | 4911141 | 16128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-7056 BAD 50KVA NEED 75KVA AND 25KVA OPEN DELTA BANK 2-CUTOUTS 1LA TRUCK TO POLE NEED LINE CREW NEED TRANSFORMER BAG RELEASED BY CREW 078S08 RELEASED BY CREW 078Q04.. CREW ON SITE ETR 11:30. NEW ETR 13:00.. TRANSFORMER BANK RESTORED AT 12:20 AND TICKET COMPLETE CAY VER/CRB L3/DKG
2280 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-12-30 11:06 | 2019-12-30 16:14 | 59 | 308 | 4195251 | 16118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 331-B-142. line fuse didnt blow.. went back to recloser pole 355-182. isolated trouble on pole 355-A-303 grounded and tagged. closed recloser back in on pole 355-182 @ 14:55 heating up to 355-A-303. repairs made powr restored @ 16:14 Released by crew 077H16
2281 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-01-09 11:04 | 2011-01-09 16:03 | 80 | 299 | 60117-1 | 16066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4 MEN 6AWIRE, SLEEVES, TRUCK ACCESSIBLE, WILL NEED SOMESONE TO FLAG , DOWN BETWEEN 29-46 600FT,ALSO NEUT DOWN BETWEEN 29-30 OPENED TRAN AT POLE 30,, LINE WILL NEED TO BE DEENERGIZED TO MAKE REPAIRS//29 CUST HAVE BEEN OFF SINCE 1104/FUSE ON 597-44 OPEN AT 1449/FETR1645/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1603/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
2282 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-07-21 13:36 | 2013-07-21 16:45 | 85 | 189 | 4569151 | 16065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | NO CREW REQUIRED PUT 206-2322 IN ABNORMAL AND SEND A COPY TO BRADSHAW FOR POLE 206-2393 665 STOVALL LN ABOUT TREES AND CLEAN UP PINES//MADE AED VER/CRB L/3 CRB IDC XXXX
2283 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-04-30 09:20 | 2022-04-30 11:42 | 113 | 142 | 4817331 | 16046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | power restored 11:42
2284 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-07-21 01:30 | 2010-07-21 02:18 | 334 | 48 | H54345-1 | 16032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN FROM RECLOSER POLE , WILL REQUIRE FLAGGING CREW TO PUT BACK UP C PHASE IS DOWN BURNT INTO AT POLE , WILL HAVE TO OPEN OTHER TWO PHASES WHEN WE PUT BACK UP . PUT WIRE BACK UP OPEN ED OTHER TWO PHASES AT 0130 , RESTORED POWER TWO ALL CUSTOMERS AT 0218 . 1/0 ACSR APEARED TO HAVE HAD A BAD PLACE AT A STIRRUP JKC//VER/CRB IDCC DUP TO OPEN 2 PHASES B AND C XXXX
2285 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-03-25 05:48 | 2013-03-25 10:34 | 56 | 286 | 4954031 | 16016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD TAG PLACED FOR KY DDC//NEED 40` 5 POLE & CREW & AWP CREW// FRALEY TO REMOVE KY DDC TAGS & REPLACE WITH HIS //OPENED RECL ON 1048-279 @ 0650 HAVE A POLE BURNTED OFF, POLE NUM 1072-F-47, 405, WILL NEED POLE AND CUTOUT AND ARRESTOR, CREW REQ AND AWP REQ, I HAV RECLOSER ISOLATED AND GROUNDED AND TAGGED FOR DDC AT POLE 1049-D-279.OPENED RECL ON 1048-279 @ 0650 COD-60 ISO OCR 39831048D20279 VER/HFP L3/HFP IDCC CNT60, PN279, CDC86 XXXX
2286 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2017-09-05 13:03 | 2017-09-05 19:20 | 78 | 377 | 4331191 | 16008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 305-10 B PHASE RECLOSER OPEN ,,PATROLLING /// B PHASE OCR OPEN 78 CUST //,,CREW REQUIRED,NO TRUCKS,ISOL,BAD XFR CUTOUT @ 305-78,,RECLOSER 305-10 BACK IN @ 16:26 LEAVING OFF 1 CUSTOMER RELEASED BY CREW 078S05 RELEASED BY CREW 078H07 38830305000010 77 AT 1626 38830305000078 1 1920 VER/AWD L3/CAS SJG
2287 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2018-02-16 12:36 | 2018-02-17 01:18 | 21 | 762 | 4850861 | 16002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400701 // ETA 1300/ Had to open line fuse fuse on pole 172-232 due to pole fire/ Pole 172-30 is burnt off may have to change pole/// Joey Reed enroute to look at maybe lowering/// This is no truck ,but can get yard dog to set pole if we have to change it out
2288 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-01-02 09:47 | 2021-01-02 21:52 | 22 | 725 | 4843601 | 15950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | top of 3 phaes pole burnt off bad c/o Released by crew 077H04/ ISO 37830227A10293/ COD 22
2289 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-01-04 14:36 | 2020-01-04 16:50 | 119 | 134 | 4211721 | 15946 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 38830428000234 rec load side riser hanging in clear--line side riser on, rec in--16:50-allgood-ds010420
2290 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-09-04 18:13 | 2011-09-04 18:58 | 354 | 45 | 4809931 | 15930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE PULLED LOOSE FROM SLEEVE//SEE ORDER 4808361//CREWS HAD TO OPEN RECLOSER IN ORDER TO MAKE REPAIRS//COD 354// VER/DBM IDC XXXX
2291 | Hazard | 3309003 | JEFF | VIPER | 2019-12-15 12:08 | 2019-12-15 15:00 | 145 | 172 | 4155691 | 15924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER 37830369B40408 OPEN //COD 145//CLOSED RECLOSER 37830369B40408 @ 1332 UP TO RECLOSER 37830393B00089 //COD 53//BAD CUTOUT ON POLE 37830393B00091Ocr 369B/408 is out patrolling fault 393B/91 wen thru ocr on 393B/89 bad cutout on 393B/91 power ok
2292 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-01-06 02:56 | 2014-01-06 09:15 | 42 | 379 | 4234211 | 15918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ** CREW TO BE DISPATCHED AT DAYLIGHT AS WEATHER & ROAD CONDITIONS ALLOW.CREW TO BE DISPATCHED AT DAYLIGHT AS WEATHER & ROAD CONDITIONS ALLOW. LINE FUSE IS BLOWN ON POLE 963-D-84. PATROLLING LINE.CREW TO BE DISPATCHED AT DAYLIGHT AS WEATHER & ROAD CONDITIONS ALLOW. LINE FUSE IS BLOWN ON POLE 963-D-84. PATROLLING LINE. REPLACED BAD CUTOUT ON POLE 987-C-101.//COD 42// VER/DBM IDC XXXX
2293 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-04-15 17:03 | 2020-04-17 13:15 | 6 | 2652 | 4701251 | 15912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *ASD*/top of 19.9 cutout broke will need to be changed can not access will need to be climb Released by crew 074M01--back in at 1315
2294 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2015-08-06 09:59 | 2015-08-06 10:54 | 289 | 55 | 4103531 | 15895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN ON POLE 38821065B00275. B PHASE FAULT, PATROLLING THE LINE. FOUND A BAD TRANSFORMER CUTOUT ON POLE 38821065A00331. ILL REPLACE IT. POWER RESTORED AT 10:54.// VER/ ADH L3/HFP XXXHFP AJB
2295 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-11-17 00:33 | 2010-11-17 05:07 | 58 | 274 | 57151-1 | 15892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUTON 447-38 BURNED POLE INTO..MADE REPAIRS RESTORED POWER AT 05:07 VER/KEP L3/KEP IDC XXXX
2296 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-13 09:13 | 2012-02-13 13:00 | 70 | 227 | 4344401 | 15890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE ON CENTER STEPDOWN TRANSFORMER ON POLE 97-346 IS OPEN. I AM GOING TO CLOSE FUSE BACK IN. 500 KVA STEPDOWN TRANSFORMER IS BAD. STEVIE RAY AND CREW ARE GOING TO BRING ONE AND CHANGE IT OUT.COD-44 ON "B"CENTER PHASE. WE OPENED THE OTHER 2 RECLOSERS ON POLE 97-346 AT 12:15 AND I ALSO HIGH SIDE FUSE ON CENTER STEPDOWN TRANSFORMER ON POLE 97-346 IS OPEN. I AM GOING TO CLOSE FUSE BACK IN. 500 KVA STEPDOWN TRANSFORMER IS BAD. STEVIE RAY AND CREW ARE GOING TO BRING ONE AND CHANGE IT OUT/ IDC XXXX
2297 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-10-15 19:56 | 2013-10-16 11:30 | 17 | 934 | 4938791 | 15878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE F OUT,WILL PTRL///////NOTHING EVIDENT,RE-FUSED.FUSE BLEW.T HALL WILL WORK IN THE AM WEDNESDAY/////WILL NEED CREW TO PATRL,POSSIBLY REPAIR PROBLEM RELEASED BY CREW 074S06  1000 FT SPAN OF WIRE DOWN FROM 38830958000037 TO POLE 958-5  ISOLATED BAD SPAN OF WIRE  FED FROM N.O. @ POLE 958-2 @ 11:30  PLACED TAG @ POLE 958-33 FOR DDC RELEASED BY CREW 074H18 //VER/GAH IDC REMOTE AREA COULD NOT FIND THAT NIGHT XXXX
2298 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-01-02 23:26 | 2014-01-03 15:05 | 21 | 939 | 4220931 | 15862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER DUTY SUPERVISOR FOR THIS AREA, HOLDING NON-EMERGENCY CALLS UNTIL THE A.M. DUE TO TERRIBLE ROAD CONDITIONS//CUTOUT FAILED ON POLE 103-130PER DUTY SUPERVISOR FOR THIS AREA, HOLDING NON-EMERGENCY CALLS UNTIL THE A.M. DUE TO TERRIBLE ROAD CONDITIONS// POLE BURNED OF @ POLE #103-130 , OPENED LOOP ON POLE 103-108 . NEED LINE CREW , 45 POLE , 25KVA 7200 . CLOSED LINE FUSE ON POLE 102-119 @ 11:42 , ALL CUST. ON BUT XFMR ON POLE 103-130.PER DUTY SUPERVISOR FOR THIS AREA, HOLDING NON-EMERGENCY CALLS IDC XXXX
2299 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-11-12 16:08 | 2012-11-12 23:08 | 38 | 420 | 4388741 | 15856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED WITH TECH 251-73/TRUCKS OK/45/4 POLE 3 PHASE 2 INLINE 1 DEADEND WITH RECLOSER // HEMLEPP & MORGAN & MCCANN & PRICHARD & MCCOY - TECH PARSONS/ FETR 23:45 JEH/ REPAIRS COMP./// REC. @ 251-34 ONLINE @ 23:00 (13 CUST) // RECLOSER @ 251-73 DEFECTIVE, ISOLATED & TAGGED TO DDC // BY-PASS FUSE (40T) CLOSED @ 23:08 (25 CUST) ALL REMAINING CUSTOMERS POWER RESTORED. ///////JEH COD-38 ISO OCR 38830251000034 VER/HFP L3/HFP IDC XXXX
2300 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-08-23 03:31 | 2020-08-23 09:23 | 45 | 352 | 4359761 | 15840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Ocr out on 319/34 patrolling 6A wire down at 319/42 looks like it pulled out of splice need 2 man and bucket took clamps off of ocr no grounds no tags Released by crew 077S03.power restored
2301 | Hazard | 3302704 | HAZARD | KENMONT | 2013-01-14 19:13 | 2013-01-14 20:24 | 223 | 71 | 4604041 | 15833 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUTS ON PRIMARY METERING ON POLE 37830321A40605, BYPASSED PRIMARY METERING. --- POWER RESTORED AT 20:24 ENTERED AED VER/HFP L3/HFP IDCC TOF1856 XXXX
2302 | Hazard | 3303902 | LESLIE | WOOTON | 2020-11-15 08:53 | 2020-11-15 14:09 | 50 | 316 | 4677761 | 15800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Fuse open on pole 37830365C00039. One span of primary down @ pole 37830365A40366 going to pole 37830365A30367. Need line crew, bucket row crew, and #2 acsr to make repairs. Repairs made and restored @ 1409
2303 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-05-08 12:13 | 2011-05-08 12:24 | 1435 | 11 | H1151971-1 | 15785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | POLE FIRE // PAINTSVILLE/CITY 12KV CKT LOCKED OUT // SERVICER ENROUTE TO STATION// WILL NEED LINE CREW AND FLAGGERS // APPEARS THAT TEMPORARY SAFETY COVERS CAUGHT FIRE DUE TO HEAVY RAINS. CREW ENROUTE TO ASSIST./ //VER/GAH MAF IDC XXXX
2304 | South Williamson | 3411401 | DEWEY | INEZ | 2008-11-01 05:33 | 2008-11-01 09:32 | 66 | 239 | 61328-1 | 15774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNT OFF. WILL HAVE TO OPEN OTHER LINE FUSE ON THIS POLE (INTERRUPTING CUSTOMERS OFF FOUR MORE XFMRS) TO MAKE REPAIRS. WILL NOTE TIMES IN COMMENTS. OPENED OTHER LINE FUSE AT 9:22, MADE REPAIRS, AND CLOSED BOTH FUSES AT 9:32. SH//MADE ANOTHER OUTAGE FOR OTHER FUSE//3411401//VER/CRB IDC XXXX
2305 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-12-03 12:39 | 2014-12-03 19:45 | 37 | 426 | 4830301 | 15762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830151000024 BURNT OFF AT CUTOUT, MANUAL, 40 CL 4 POLE RELEASED BY CREW 077S04POLE 37830151000024 BURNT OFF AT CUTOUT, MANUAL, 40 CL 4 POLE , REPAIRS MADE, POWER RESTORED AT 19:45 COD-37 ISO OCR 37830151000199 VER/HFP L3/HFP AJB
2306 | Hazard | 3309302 | VICCO | JEFF | 2015-07-04 10:49 | 2015-07-04 15:58 | 51 | 309 | 4719921 | 15759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE AT POLE 37830348B00086 === POLE 348B-317 BURNED OFF AT CUTOUT ===A GOT MAIN LIN E ON AT 12:57 === NEED LINE CREW AND ROW CREW === WILL CHANGE POLE OUT AT A LATER DATE === GOT LINE SAFE === ROW CUT CAN GET TR\UCK TO POLE MADE OPS ORDER 031006621 == NO CUST OUT RELEASED BY CREW 077S03 VER/CRB AJB
2307 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-04-24 18:33 | 2021-04-24 20:00 | 181 | 87 | 4476981 | 15747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Switch on pole 38831122000033 broke affecting C ph customers only (181 cc)/opened C ph NO sw on 38831121C00021 to make repairs @2000 back on
2308 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-07-07 06:42 | 2017-07-07 09:00 | 114 | 138 | 4086531 | 15732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | AT POLE 47-6 HOT TAP ON C PHASE LINE SIDE OF RECLOSER HAS BURNED OFF. HAVE CALLED FOR COVER UP & OBSERVER. VER/CRB SJG CNT68 (B-PH PER CUST CALLS)
2309 | South Williamson | 3200302 | BELFRY | TOLER | 2009-04-06 21:07 | 2009-04-06 23:30 | 110 | 143 | 50035-1 | 15730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29261900 //POLE TP BURN OFF. 38821039B00253WR # 29261900 //POLE TP BURN OFF.POLE 1039-A-253. L3/HFP AJB
2310 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-06-17 14:16 | 2014-06-17 17:05 | 93 | 169 | 4101771 | 15717 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ROTTEN POLE @ 185-84 LAYING IN TREE NEED LINE CREW TO REPAIR RELEASED BY CREW 078S05 VER/CRB AJB
2311 | Hazard | 3309301 | VICCO | REDFOX | 2011-08-02 23:52 | 2011-08-03 05:00 | 51 | 308 | 4657141 | 15708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | PRIM METERING ON POLE 324-257 HAS GONE BAD, 1 BY-PASS CUTOUT IS ALSO BAD, WILL NEED TO REPLACE BY-PASS CUTOUT BEFORE RESTO`G POWER, 2 FUSES ARE BLOWN ON POLE 323-430. REPLACED 2 BY-PASS CUTOUTS AND REMOVED CLAMPS FROM METERING VER/PDP STC, CNT53, CRT`D 2ND TT, PER PHONE CONF & CALLS - A&C PHSES OUT, CREW OP`D B PHSE @ 01:25(2ND TT W/2), ALL REST @ 05:00, 1 OF 2 TT`S
2312 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2008-11-30 17:26 | 2008-11-30 19:57 | 104 | 151 | 53288-1 | 15704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007905//WR#27467830//CREW ON SITE/POLE TOP BURNT OFF/RECLOSER ON 547-177 OPENED BY CREW AT 1726/FETR1930/VEM/RAN INTO XFMR COMPLICATIONS/NEW FETR2000/VEM/RECLOSER BACK IN AT 1957/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
2313 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2014-11-11 00:29 | 2014-11-11 04:55 | 59 | 266 | 4718421 | 15694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN @ POLE 271C-126 TO POLE 271C-128 NEED LINE CREW TO REPAIR,ISO,GROUND & TAG TO BILL FRALEY RELEASED BY CREW 078S05 VER/KEP // PER SERVICER THE CONDUCTOR JUST BROKE // L3/HFP AJB
2314 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-08-31 11:20 | 2015-08-31 13:48 | 106 | 148 | 4185251 | 15688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ORIGINAL COD 106//STIRRUP BURNT OPEN ON PHASE B RECLOSER.STIRRUP BURNT OPEN ON PHASE B RECLOSER. OPENED ALL THREE RECLOSERS ON 954-579 @ 13:26, REPLACED STIRRUP AND CLOSED ALL THREE REC @ 13:48. SH RELEASED BY CREW 076S02 VER/CRB L3/DKG THIS IS THE ORIGINAL OUTAGE SEE H4185251 FOR OPENING OTHER 2 PHASES AJB
2315 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2010-11-16 17:44 | 2010-11-16 20:55 | 82 | 191 | 56619-1 | 15662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TRANSFORMER ON POLE 39831148B42019 AT 20;16--LINE FUSE ARE IN--REPLACED BAD CONNECTORS ON SECONDARY//VER/CRB/ IDC LOOKS LIKE THIS SHOULD BE PART POWER FROM SECOND CALL. CHANGED START TIME FROM 2016 XXXX
2316 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-10-10 15:47 | 2011-10-10 17:03 | 206 | 76 | 4962641 | 15656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREWS OPEND RECLOSER IN ORDER TO MAKE REPAIRS FOR ORDER 4961781//COD 206// VER/DBM IDCC TON1547 XXXX
2317 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-06-09 15:41 | 2010-06-09 21:19 | 70 | 338 | 59380-1 | 15631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S01 VER/HFP L3/HFP IDC XXXX
2318 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-12-12 08:16 | 2016-12-12 13:00 | 55 | 284 | 4186401 | 15620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | /CENTER PHASE RECLOSER IS OUT PATROLLING COD 55/CENTER PHASE RECLOSER IS OUT PATROLLING..TIE WIRE BROKEN, CONDUCTOR OFF PIN AND LYING ON THE CROSS ARM.ON P-777-15..ALSO PRIMARY NEUTRAL DOWN ON POLE- 777-19..#2 ALUMN.ALL CLIMBERS. A&C OPENED AT 1220./CENTER PHASE RECLOSER IS OUT PATROLLING..TIE WIRE BROKEN, CONDUCTOR OFF PIN AND LYING ON THE CROSS ARM.ON P-777-15..ALSO PRIMARY NEUTRAL DOWN ON POLE- 777-19..#2 ALUMN.ALL CLIMBERS.OPENED THE OTHER 2 REC AT 12.20..ISOLATED GRD AND TAGGED FOR MYSELF VER/AWD L3/
2319 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-12-08 22:35 | 2010-12-09 00:15 | 156 | 100 | H64509-1 | 15600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PHASE C IS DOWN AT POLE 1041-B-201.....ON HILLSIDE....CALLED J REED...NEED 3 MAN CREW....WILL OPEN & ISOLATE RECLOSER ON 1065-B-275....WHEN THEY ARE CLOSE....//...OPENED RECLOSER @ 22:35....MADE LINE REPAIRS.....CLOSED RECLOSER @ 00:15....POWER RESTORED.....JRV....12/09/10 // CUSTOMERS ONLY INTERRUPTED ON C PHASE FROM POLE 1041-B-201. (75 CUSTOMERS) //VER/GAH IDC XXXX
2320 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-02-19 05:26 | 2008-02-19 15:11 | 59 | 585 | 65079-1 | 15591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001203//BROKEN POLE//MIKE MAY (DHE) IS ENROUTE AT 0700POLE BURNT OFF 45-3009POLE BURNT OFF 45-3009 RELEASED BY CREW 078S08//CREW RAN INTO SOME UNFORESEEN DIFICULTY UPPED THE ETR TO315 PM//VER/CRB IDC XXXX
2321 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-05-01 10:14 | 2022-05-01 12:25 | 119 | 131 | 4820341 | 15589 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 375B-34. Getting crew to come help.
2322 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-03-05 11:35 | 2014-03-05 14:19 | 95 | 164 | 4453951 | 15580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON SOURCE SIDE OF STEPDOWN, NEED BUCKET TRUCK 19.9 CUTOUT AND FLAGGERS. OPENED REC. ON POLE 37830246D00450 AT 13:35, MADE REPAIRS, CLOSED REC. AT 14:00 COD-95 ISO LF 37830246D00258 VER/HFP L3/HFP IDC XXXX
2323 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2018-06-22 04:32 | 2018-06-22 06:00 | 177 | 88 | 4640981 | 15576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Double dead end pole loop is not on a ridge pin and a bird has grounded out between the loop and a guy attachment. There is not enough slack to push the loop up away from the guy attachment. Send to Tim Hall to have a line crew install a ridge pin. Will need flaggers. Power restored.//cod 177
2324 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-04-18 02:31 | 2018-04-18 06:20 | 68 | 229 | 4248861 | 15572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | loop burnt between 427-33 and 427-34. repairs made power restored @ 06:20 // L3/HFP
2325 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-05-28 06:24 | 2008-05-28 09:25 | 86 | 181 | 52021-1 | 15566 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802// REPLACED CUTOUT ON POLE 786-110//VER/CRB IDCC MCCDIS XXXX
2326 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-06-10 18:42 | 2021-06-10 19:13 | 502 | 31 | 4709481 | 15562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened 1100D4-325 to allow crews to replace failed cutout at 38831076B40205 outage should last 30 mins or less Off at 1842 On at 1913 Note: Order # 4708481 had 81 CC (B phase) already out before this outage was started
2327 | South Williamson | 3411401 | DEWEY | INEZ | 2014-01-29 10:41 | 2014-01-29 11:29 | 324 | 48 | 4323631 | 15552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | CREW MAKING REPAIRS TO FAILED SWITCH VER/ARN IDC OPEN SWITCH FOR REPAIRS XXXX
2328 | Whitesburg | 3309302 | VICCO | JEFF | 2016-03-01 19:45 | 2016-03-02 05:42 | 26 | 597 | 4794551 | 15522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON POLE 396-89, BAD INSULATOR ON POLE 396-35, FOUND TREE ON LINE AT 396-43. MADE REPAIRS RESTORED POWER AT 05:42.. VER/KEP AJB
2329 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2010-03-28 11:10 | 2010-03-28 16:00 | 139 | 290 | 55158-1 | 15510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 3442330 //CONFIRMED FUSE OUT PATROLLING LINE// 7200 XFMR CUTOUT FAILED ON POLE 37830296B11175 ISOLATED AND TRYING FOR PARTIAL RESTORE//PARTIAL RESTORE COMPLTED AT 12:40 RELEASED BY CREW 077S04 RELEASED BY CREW 077H03STS WR # 3442330 //CONFIRMED FUSE OUT PATROLLING LINE// 7200 XFMR CUTOUT FAILED ON POLE 37830296B11175 ISOLATED AND TRYING FOR PARTIAL RESTORE//PARTIAL RESTORE COMPLTED AT 12:40 RELEASED BY CREW 077S04 //ON SITE CHANGING CUTOUT AND ARRESTER. VER/HFP L3/HFP IDC XXXX
2330 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2014-06-14 18:15 | 2014-06-14 20:05 | 141 | 110 | H4091811 | 15510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX CABLE BURNT DOWN (A PHASE INITALLY OUT 59 CUST// MILLER & MAYNARD & NEWSOME // OPENED SWS @ 1815 ON POLE (299 CUST) 785-D-3314/0 HENDRIX CABLE BURNT DOWN. CREW ENROUTE TO REPAIR. OPENED SWITCHES ON 785-331 @ 18:15 TO ISOLATE.4/0 HENDRIX CABLE BURNT DOWN. CREW ENROUTE TO REPAIR. OPENED SWITCHES ON 785-331 @ 18:15 TO ISOLATE.COMPLETED REPAIRS AND CLOSED SWITCHES ON 785-331 @ 20:05. SH VER/HFP L3/HFP AJB CNT299 PH A INLT OUT.
2331 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-12-20 14:17 | 2012-12-20 14:55 | 408 | 38 | 4488491 | 15504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | BYPASSED RECLOSER RESTORED SERVICE @14:55 PLACED TAGS 3RD OUTAGE ON REC TODAY IT WASN`T OPERATING VER/KEP
2332 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-07-02 09:58 | 2008-07-02 11:20 | 189 | 82 | 61277-1 | 15498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402801// B PHASE RECLOSER HAS LEAD BURNT OFF. OTHER TWO APPEAR TO BE IN. CREW ENROUTE TO FLAG TRAFFIC SO REPAIRS CAN BE MADE.//COD 162// REPAIRS COMPLETE. SH// VER/DBM IDCC CNT162 PH A NOT B XXXX
2333 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-01-18 14:17 | 2011-01-18 16:25 | 121 | 128 | 62294-1 | 15488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT, BACK YARD, HILLSIDE WORK, JUST OFF RT 644 @ POLE 478-294 // CREW CLOSED THIS ORDER IN SPECTRUM WHEN POWER WAS NOT RESTORED, NEED TO DELETE ALL STEPS OF RESTORATION EXCEPT FOR THE ONE @ 1625 VER/HFP L3/HFP IDC XXXX
2334 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-10-10 21:42 | 2017-10-10 23:11 | 174 | 89 | 4444781 | 15486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED 23 11// VER/ADH L3/HFP XXXHFP ACBC CNT169
2335 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-09-25 14:08 | 2014-09-25 16:51 | 95 | 163 | 4528431 | 15485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNING ON POLE 38830251000096// NEED LINE CREW AND FLAGGING CREW// TRUCK OK// WILL HAVE TO OPEN SWITCHES ON POLE 251-207 OPENED B PHASE SWITCH @ 14:08// ISO 38830251000207// COD 95//CREW ON SITE/FETR1730/VEM/OPENED SWITCHES @1627/REPAIRS COMPLETE CLOSED SWITCHES@1651/ALLCUST RESTORED PLEASE CLOSE TICKET/THANKS/VEM VER/CRB IDCC PN99, FP99 XXXX AJB
2336 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-06-07 02:41 | 2010-06-07 11:39 | 63 | 538 | 58130-1 | 15470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSURE OUT AT 29-47 PATROLING NOW--WIRE DOWN ON TAP LINE AT POLE 6-50 NEED CREW RELEASED BY CREW 077S10 RESTORED POWER TO REMAINING CUSTOMERS AT 1139 JKC VER/KEP L3/KEP IDC XXXX
2337 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-07-07 09:54 | 2016-07-07 16:30 | 39 | 396 | 4554951 | 15444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S01.CUTOUT BROKE ON POLE 50-57 WILL REPLACE..WILL HAVE TO OPEN NC SWITCH UP AT POLE 50-48 TO CHANGE CUTOUT SAFELY..OPENED SWITCH UP @ 15:30..MADE REPAIRS AND CLOSED BACK AT 16:30 VER/AWD AJB
2338 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-06-26 18:25 | 2022-06-26 19:48 | 186 | 83 | 4324351 | 15438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | cross arm broke at pole 1036C-175..wire is floating in the clear..no outage as of now..crew in route..im sitting at fault pole..everthing is safe..going to wait till crew gets here before we open anything.opened rec at pole 1012D-55 at 18:25 to make repairs and got it back in at 19:48 LR- The 1st calls show that there was full Power and the All Out calls came in after recloser was opened at 18:25.
2339 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-01-10 08:57 | 2016-01-11 01:24 | 31 | 987 | 4598841 | 15431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T OPEN@ 20-7512, POLE TOP @ 20-7661, TRK TO POLE, TECH FOR LOCATES RELEASED BY CREW 078S07 CUT LOOPS AT 20-D4-7638/1000 CALLED ASHLAND WATER FOR A UNDERGROUND LOCATE//1115 CONTACTED 811 FOR LOCATE ORDER # 1601100042, ID 26766//CREW ON SITE--TAGD & GNDD TO RMV--INSTALLED LF ON PL# 20D4-7638(25T)--ON AT 01:15---XFMR IN ON NEW PL.20-7661 AT 01:24--MAKE MAP DESC. FOR NEW LF---TBL TKT COMP AJB TON FIRST REST STP ADDED STP.
2340 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-03-24 20:32 | 2018-03-25 13:40 | 15 | 1028 | 4061601 | 15420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad dead end insulator on pole 38831124C00195. will need 19.9 dead end insulator & short ext link. restored at 13:40./ ISO 38831124C00141/ COD 15
2341 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-01-01 09:48 | 2011-01-01 14:45 | 57 | 297 | 57637-1 | 15408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 38258603 // LINE FUSE OUT ON POLE 37830247D00764 --- POLE #37830247000907 IS BURNT OFF AT GUY FOR PRIMARY EXTENSION. ---DUTY SUPERVISOR NOTIFIED- CREW ENROUTE. INSTALLED 300 AMP DISC. ON POLE 37830247D00905, POWER RESTORED TO POLE 247- 905 AT 12:48 === ALL POWER RESTORED AT 1445 COD-57 ISO LF 37830247D00764 VER/HFP L3/HFP IDC XXXX
2342 | Hazard | 3309301 | VICCO | REDFOX | 2022-10-11 09:38 | 2022-10-11 10:43 | 237 | 65 | 4014231 | 15405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Open switch on pole 37830325C00264 to isolate and repair 37830326A00005replaced bad conn. opened 325c-264 @09:38, closed @ 10:43 Released by crew 077H13
2343 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-12-16 17:10 | 2008-12-16 20:05 | 88 | 175 | 59126-1 | 15400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 27707764PATROLING LINEPATROLING LINE---#2 PRIMARY PULLED OUT OF SLEEVE--CALLED B FRALEYPATROLING LINE---#2 PRIMARY PULLED OUT OF SLEEVE--CALLED B FRALEY RELEASED BY CREW 078S07 VER/TOM L3/TOM IDC XXXX
2344 | Hazard | 3303902 | LESLIE | WOOTON | 2008-01-09 09:36 | 2008-01-09 11:56 | 110 | 140 | 55069-1 | 15400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902//POLE#366-51 IS ON FIRE//THIS IS RECLOSER POLE//ALSO OPENED REC 366-182 TOTAL OUT 110)//VER/CRB IDCC TOF742 NO OUTAGE CALLS UNTIL 936 XXXX
2345 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-10-23 12:43 | 2009-10-23 14:48 | 123 | 125 | 66323-1 | 15375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP BAD ARRESTER ON POLE 91B38. I CHANGED TWO 70AMP SECTIONALIZERS ON POLE 19B42. AND PUT 50T FUSES NEED TO SHOW THAT ON MAPPING. /// C PHASE OUT 119 CUSTOMERS. FALT WENT THROUGH SECTIONALIZERS ON POLE 19B42 AND OPENED C PHASE RECLOCER ON POLE 115-55. SEND COPY TO PERRY FARMER PIKEVILLE ///CCC -HFP L3/HFP IDC XXXX
2346 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-03-01 10:21 | 2019-03-01 16:50 | 76 | 389 | 4941741 | 15368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | p#38830258000049 burnt off map showing 40-5 straight line with tap and 12t cutout. crew required mo pads or yard dawg 55-60 yrds off roadway in fieldp#258-49 burnt off map showing 40-5 straight line with tap and 12t cutout. crew required mo pads or yard dawg 55-60 yrds off roadway in field RECLOSOR IN @ 1217 UP TO 38830258000047//CLOSED SB @ 1650//MD MADE/ ¦¦¦ LOOKS LIKE THIS WENT THRU 2 SETS OF 15T FUSES IF THEY ARE ACTUALLY IN THE FIELD POLES 38830258000033 & 38830258000026 L3/HFP
2347 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-08-29 13:03 | 2013-08-29 15:50 | 92 | 167 | 4719311 | 15364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE OUT COD 92 STIRRUP AND HOT LINE CLAMP BURNED UP ON HIGH SIDE OF THE STEPDOWN TRANSFORMER A PHASE. CREW ENROUTE. OPENED OTHER PHASES AT 15:32 (139) CUSTOMERS.STIRRUP AND HOT LINE CLAMP BURNED UP ON HIGH SIDE OF THE STEPDOWN TRANSFORMER A PHASE. CREW ENROUTE. RELEASED BY CREW 074S02 ALL POWER ON 15:50 MAKE DUPLICATE ORDER FOR B&C PHASES VER/SEF L3/HFP IDC XXXX
2348 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-01-06 11:40 | 2014-01-06 15:13 | 72 | 213 | 4236981 | 15336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO ON POLE 420-45, WILL HAVE TO OPEN RECLOSER ON POLE 420-20 TO ISOLATE SO CREW CAN MAKE LOOP UP//ISO//COD 72/ 0PNSO CREW CAN MAKE LOOP UP RELEASED BY CREW 077S11 OPENED RECLOSER AT 300 (SEE ORDER 4238441) CLOSED IT AT 313 //COD 72 IDC XXXX
2349 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-03-27 08:28 | 2012-03-27 14:52 | 44 | 384 | 4621141 | 15328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | PRIMARY U.G. IS OUT, THEIR A LINE CREW COMING,. RELEASED BY CREW 074S05 3 POSITION PRIMARY FEEDTHROUGH BURNT UP 203/12:40(COD 4) 204/12:47(COD 2) 205/12:59(COD 2) 206/13:09(COD 0) 207/13:18(COD 6) 208/13:24(COD 0) ALL THE REST AT 14:52(COD 30) D SAMMONS // COD TOTAL 44// VER/DBM IDCC CDC83 XXXX
2350 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-09-16 15:06 | 2009-09-16 16:57 | 138 | 111 | 62465-1 | 15318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLEW UP. ISOLATING. FUSE ON POLE 38830875C00321 BLOWN. PH B RECLOSER OPEN AT POLE 875-406. WILL HAVE TO CUT SOME LIMBS TO REACH FUSE. 50T FUSE ON POLE 875-321. RE-FUSED WITH REC OPEN AND THEN CLOSED PH B RECLOSER ON POLE 875-406 AT 16:57 RESTORING ALL CUSTOMERS. NEED TO TRIM TREE AND CLEAN UP LIMBS THAT I CUT AT POLE 875-321. SEND TO BRADSHAW. THANKS, SH//COD 61//MD FILED ON INCORRECT PHASING AT FUSE POLE// VER/DBM IDCC CNT61 XXXX
2351 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-01-30 08:34 | 2013-01-30 13:23 | 53 | 289 | 4754051 | 15317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0928 - KEVIN BROWN ENROUTE TO HELP DANNY,PATROLING LINES TRIED FUSE CAME BACK OUT IN15 SEC, CALL FOR HELP RELEASED BY CREW 078S09/CREW ON SITE/BAD XFMR CUTOUT 1148-724/NO TRUCKS /CREW TO CHANGE/FETR 1400/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1323/PLEASE CLOSE TICKET/THANKS/VEM//MADE MDC ///VER/CRB L/3 CRB IDC CUT A LOT OF TREES THEN CAME BACK OUT HAD TO FOOT PATROL TO FIND TROUBLE XXXX
2352 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-02-16 12:20 | 2020-02-16 15:10 | 90 | 170 | 4409881 | 15300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester on pole 1064-22//MADE DAE ON BLOWN L/A //blown arrester on pole 1064-22, closedrecloser on pole 1040-18 at 15:10 Released by crew 077S07//DAE 1000047374 L3/HFP
2353 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2012-11-04 23:52 | 2012-11-05 11:27 | 22 | 695 | 4359061 | 15290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINE FUSE IS OUT ,PATROLLING LINE. POLE TOP SPLIT OUT ONE POLE UP FROM 1013-B-136. ALREADY HAS POLE TOP EXT ON IT JUST NEED TO PUT TWO BOLTS THROUGH POLE TOP AND TIE PRIMARY BACK IN. RELEASED BY CREW 079H06-WILL MAKE REPAIRS TO POLE AND RE-SAG PRI@NEUT CONDUCTORS R RAY ///VER/CRB L/3 CRB IDC XXXX
2354 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-02-01 09:16 | 2013-02-01 12:20 | 83 | 184 | 4780911 | 15272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RECLOSER ON 379-229 IS STILL IN BUT RISER IS BURN OFF LINE SIDE NEED TO OPEN RECLOSER REPAIR LEAD AN MAKE REC. BACK HOT. MADE HOT AT 12:20 ///VER/CRB L/3 CRB IDC CHANGED COUNT FROM 154 PH B ONLY XXXX
2355 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-02-26 06:16 | 2021-02-26 09:54 | 70 | 218 | 4253541 | 15260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINEF IS OUT,WILL PTRL///////NOTHING EVIDENT,WILL RE-FUSE/////////RE-FUSED&RESTORED.FUSE APPEARED TO HAVE MELTED OUT.TOOK IT UP 1 SIZE TO A 40T,WAS A 30T/ ISO 38821037A00130/ COD 70
2356 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-05-20 18:22 | 2020-05-20 23:50 | 47 | 328 | 4871771 | 15256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | line fuse open at 37830029000043. clamp has burnt primary into at pole 37830006000007. opened solid blade at pole 37830029000047 to isolate and closed line fuse at pole 29-43 in at 21:10. need line crew and row crew Released by crew 077S10 power restore at 11:50 Released by crew 077H02
2357 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2009-08-24 03:58 | 2009-08-24 14:00 | 28 | 602 | 61625-1 | 15256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP WR 31368305 // RELEASED BY CREW 078S08 ** RISER FUSE OUT POLED/S NOTIFIED THAT URD CREW WILL BE NEEDED.//@ 1256 ALL BUT 3 CUSTOMERS RESTORED 25 CUST RESTORED // ALL CUSTOMERS RESTORED @ 1400 // RISER FUSE OUT POLED/S NOTIFIED THAT URD CREW WILL BE NEEDED. FOUND BAD CABLE BETWEEN20-423- TO20-426 NORMAL OPEN POINT IS ABNORMAL FEEDING 20-423 CHG, FRON 20-445 L3/HFP IDC XXXX
2358 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-11-01 09:00 | 2013-11-01 11:28 | 103 | 148 | H4990031 | 15244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVE 2 PHASES OF #2 HENDRIX BROKE . CB NEVER OUT.. 2 PHASE OUT HAVE A LINE CREW FROM PIKEVILLE IN ROUTE TO REPAIR ** OPNED PHASE OTHER PHASE AT 0900 CLOSED ALL AT 1128** AT 1101 STEVE RAY HAS PERM TO CLOSE GOAB AT 954-100 // BASED ON CALLS & B.O. 148 CUST INITALLY OUT ON A & C PHASES & 103 OUTAGE WHEN SW OPENED DUPLICATING FOR SW OUTAGE VER/HFP L3/HFP IDC XXXX
2359 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-06-27 10:13 | 2015-06-27 16:24 | 41 | 371 | 4676061 | 15211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | C PHASE SWITCH BROKE ON 38830777000006 (41 CUTOMERS)/ OPENED RECLOSER 38830777000020 (115 CUSTOMERS) @ 1554 AND CLOSED @ 162438830777000006/ ISO 38830777000020/ COD 156/ DUPLICATE IN HOIS/ VER/BOW
2360 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2014-08-20 07:53 | 2014-08-20 11:40 | 67 | 227 | 4387791 | 15209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSERS SHOW TO BE IN. GOING TO THE UPPER JOHNS CREEK SIDE OF MOUNTAIN TO CHECK FOR PROBLEM. LOOKS LIKE ONLY THE C PHASE IS OUT. PATROLLING THE LINE. C PHASE RECLOSER ON POLE 37820007C30123 IS BAD, BYPASSED RECLOSER WITH A 100 T FUSE.// NEEDS PUT IN ABNORMAL BEFORE BEING CLOSED DKG ENTERED ABNORMAL AJB
2361 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-01-07 06:54 | 2014-01-07 11:52 | 51 | 298 | 4245781 | 15198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE OUT ON POLE 402-418 CONDUCTORS DOWN ON POLE 378-1 WILL NEED TO DROP RECLOSERS ON POLE418 TO MAKE REPAIRS//COD 51 (SCADA ALSO INDICATES B PHASE FAULT) (CALLS BEFORE SERVICER`S ARRIVAL CAME IN ON ALL 3 PHASES)//B PHASE OUT ON POLE 402-418CONDUCTORS DOWN ON POLE 378-1 WILL NEED TO DROP RECLOSERS ON POLE418 TO MAKE REPAIRS//// 0PENED RECLOSERS AT 1028 CLOSED THEM AT 1152 SEE H4245781 FOR A&C PHASE OUTAGE VER/HFP L3/HFP IDC XXXX
2362 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2018-10-02 08:56 | 2018-10-02 12:30 | 71 | 214 | 4188591 | 15194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Set bad transformer cutout offline at pole 38821089A00087. This transformer is not in use anymore. Power restored at 12:30
2363 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-23 18:38 | 2011-06-24 01:40 | 36 | 422 | 4403331 | 15192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 140-130 WIRE BURNT OPEN 116-708 80T BLOWN CALL DANNY FOR INFO. RELEASED BY CREW 078S08//PHASE "A" LOOPS OPEN ON 140-130 //COD 39//PHASE C STEPDOWN OPEN ON 116-708//COD 73(TOTAL 112)//@ 1230 OPENED OTHER TWO STEPDOWNS (COD +36)//MADE REPAIRS AND RESTORED ALL CUSTOMERS @ 0140// SJG CHANGED CNT148, CREATED H4403331 IDC XXXX
2364 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2009-12-26 14:45 | 2009-12-26 15:47 | 245 | 62 | 50802-1 | 15190 | TRANSMISSION LINE | EQUIPMENT FAILURE | STATIC WIRE | OPENED FEEDED BREAKER IN ORDER FOR TRANSMISSION CREW TO REPAIR STATIC WIRE. / COD-331 / MLR WV AND KY
2365 | Hazard | 3309003 | JEFF | VIPER | 2017-05-12 23:19 | 2017-05-13 09:03 | 26 | 584 | 4792511 | 15184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 416-32 FELL . LINE FUSE OUT ON POLE 416-3 . NEED LINE CREW & ROW CREW . RELEASED BY CREW 075H04 WIRE DOWN ON UP THE CREEK WILL LENTHEN THE FETR REPAIRS MADE AND POLE REPLACED POWER RESTORED AT 0903 37830416000003 37830416000032 VER/AWD AJBC CCO FEC57
2366 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-02-03 04:10 | 2017-02-03 09:40 | 46 | 330 | 4355861 | 15180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | KYDDC HOLD TAG & GROUNDS AT 136-76/RECLOSER OPEN 136-76 PATROLLING/ WIRE DOWN 136-19 TO 136-25/ISOLATED G&T TO KY DDC @ 136-76,#2 ACSR PULLED OUT OF SLEEVE,PICKUP OR 6 WHEELER ONLY TO POLE,NO TREE CREW RELEASED BY CREW 078S05,,CREW ON SITE,,ALL REPAIRS COMPLTED,,,ALL POWER RESTORED/ ISO 38830136000076/ COD 46/ VER/BOW L3/HFP XXXHFP AJB
2367 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-01-07 11:01 | 2020-01-07 11:44 | 353 | 43 | 4219291 | 15179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830030000209 has burn marks on middle phase need two de insulators and one arm pin and insulator for 19.9 will have to walk up driveway to pole ¦¦ No truck access ¦¦ OPENED RECL ON POLE 37830030000035 COD-352 OFF@ 1101 ON@ 1144 L3/HFP
2368 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-03-19 18:47 | 2008-03-20 00:40 | 43 | 353 | 58870-1 | 15179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411801// PRIMARY CONDUCTOR HAS BROKEN AND IS ON GROUND. I AM GOING TO CALL WILLIE AND GET HELP. RELEASED BY CREW 074S01 WE PUT WIRE UP AND REFUSED LINE FUSE. IDC CHANGED FROM WEATHER UNKNOWN XXXX
2369 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-08-01 12:03 | 2021-08-01 19:04 | 82 | 421 | 4990331 | 15172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 38820818A00069/causing operations at reclosing device//cutout broke on 818-69//back on hill//will have to open recloser on pole 818-a-235 to make repairs//need line crew //opened recloser at 18:30//restored all at 19:04//complete//em Released by crew 079S01
2370 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-03-10 13:16 | 2008-03-10 18:12 | 89 | 296 | 55908-1 | 15168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE//3000801//1510 CONTACTED CREW SUPERVISER FOR SERVICER//ISOLATED 294-12 WILL STILL BE OFF CALLED REYNOLDS GOING TO RECLOSER/RECLOSER STILL DIDNT STAY/BACK ON AT1605 ALL BUT ONE RELEASED BY CREW 078S03//3000801//1510 CONTACTED CREW SUPERVISER FOR SERVICER//VER/CRB IDCC TON1616 XXXX
2371 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-12-22 18:45 | 2011-12-23 03:28 | 29 | 523 | 4195991 | 15167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THOUGHT TREE WAS ON LINE,BUT WASNT,WAS ONLY VERY CLOSE.DID FIND BROKEN CUTOUT ON POLE 8-95,WILL HAVE TO REPLACE IT.WILL WAIT ON HELP // HAD TO REPLACE STEPDOWN// VER/TOM L3/TOM IDCC FEC58, CNT58 XXXX
2372 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-03-18 18:41 | 2020-03-18 23:40 | 180 | 299 | 4489731 | 15156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WE had a Deadend bell bad on pole 191-A-238,Lifited Hot Tap at pole 191-A-86 to isolate trouble,Restored Recloser at 190-D-280 at 20:04,Will make repairs, Released by crew 074S08//all repairs made power restored at 23:40 Released by crew 074H07
2373 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-09-06 03:42 | 2011-09-06 15:30 | 26 | 708 | 4827481 | 15141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM 9-6-11 PER DUTY // SEND TO BILL FRALEY WHEN TRAVIS RELEASES ORDER//WILL WORK IN THE AM 9-6-11 PER DUTY (449-6 LIFTED HOTTAP, NO GROUNDS PLACED,) 449-93BURNED OFF,(NEED 36 RIDGEPIN, 10KVA 120/240 7.2KV TRANS AND CUTOUT, MAY BE ABLE TO WINCH BUCKET TO POLE?, OLD ROAD BY POLE ALSO BRING YARDOG, TOPOF POLE IS GONE, WILL NEED TREE CREW TO TRIM WALNUT OUT FOR WIREWILL WORK IN THE AM 9-6-11 PER DUTY (449-6 LIFTED HOTTAP, NO GROUNDS PLACED,) 449-93BURNED OFF, VER/HFP L3/HFP IDC XXXX
2374 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2015-01-02 13:17 | 2015-01-02 14:09 | 291 | 52 | 4898561 | 15132 | TRANSMISSION LINE | EQUIPMENT FAILURE | NONE | TRANSMISSION LINE OUTAGE/ OPEN 1317 CLOSED 1409 VER/KEP // NOTE: PER ROTDC LOG: DONNIE BARTLEY REPORTS TROUBLE LOCATED ON STR 2 OUTSIDE OF HENRY CLAY S.S.?CAUSED BY POLE GROUND WHICH FELL INTO OUTSIDE PHASE L3/HFP AJB
2375 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-10-28 18:19 | 2017-10-28 21:09 | 89 | 170 | 4506151 | 15130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN AT SWITCH POLE 38830308000004. BURNED OFF ON LOAD SIDE AT SQUEEZE ON.PRIMARY DN AT 308-4. TRUCKS OK, LINE CREW REQUIRED//CREW ON SITE/FETR 2200/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST AT 2109/PLEASE CLOSE TICKET/THANKS/VEM/// VER/DKM L3/HFP XXXHFP ACB
2376 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-06-23 01:10 | 2022-06-23 13:10 | 21 | 720 | 4294321 | 15120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap found burned off at 38830269B00083 toward pole 38830269B00087 (11 COD) --Open LF 38830269B00079 (10 COD) to make repairs at 1235///hot tap burnt open on pole38830269B00083//line fuse on pole 269-79 open 12:35 and power restored at 13:10 Released by crew 078S09
2377 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2021-03-18 02:10 | 2021-03-18 11:30 | 27 | 560 | 4345661 | 15120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , crew required Released by crew 077S12 replaced cutout POWER RESTORED @11:30
2378 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2009-05-16 15:27 | 2009-05-16 17:15 | 140 | 108 | 58726-1 | 15120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE THREE MAIN LINE FUSES ON POLE 48-147. THE C PHASE FUSE IS BLOWN. THIS WOULD BE THE LEFT HAND PHASE WITH MY BACK TO THE STATION. I AM PATROLLING LINE NOW. CUTOUT IS BROKEN INTO ON POLE 25-138. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT AND CLOSED LINE FUSE AT POLE 48-147 IN AT 17:15//VER/CRB IDCC CCO XXXX
2379 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-04-28 08:58 | 2008-04-28 14:02 | 631 | 304 | 54856-1 | 15119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400301//RELATED TO ORDER 54809-1//HAD TO OPEN RECLOSER TO ALLOW FOR SAFE REPAIRS TO FUSES AND BURNT CROSSARMS//COD 631//RESTORED UP TO 1100-266 @ 0907//DEH - CREW ON SITE, CUT LOOPS ON 1100-24 TO ISLOLATE FAULT. COMPLTED AT 14:02. // VER/DBM IDC XXXX DEB OK
2380 | Paintsville | 3410602 | E.PRESTON | LANCER | 2020-05-25 19:18 | 2020-05-26 09:56 | 35 | 878 | 4905561 | 15112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse blown will check// Bad 100kva xfmr cannot access with big truck. I have contacted Tommy Goble and he is getting crew to replace. This is going to be held till in the morning and DHE crew is going to bring yard dog and replace. Opened fuse @ 0900 closed @ 0956
2381 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-01-18 10:03 | 2010-01-18 20:18 | 103 | 615 | 55837-1 | 15099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 33478692 // PATROLLED LINE... FOUND NOTHING//OPENED RECLOSER 238-182 AND CLOSED IN UP TO THAT PT @ 12:25// POLE 238-135 BURNED OFF AT THE NEUTRAL 45 CLASS 4 POLE DAVE SAMMONS IS SENDING A CREW TO MAKE REPAIRS. TOMORROW// FRAMED DOWN ON POLE ON AT 20:18 VER/HFP L3/HFP IDC XXXX
2382 | Whitesburg | 3312902 | JENKINS | JENKINS | 2011-08-31 12:58 | 2011-08-31 14:55 | 129 | 117 | 4778171 | 15093 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN CREW ON THEIR WAY RELEASED BY CREW 077S12REPAIRED CONDUCTORS //VER/CRB IDC XXXX
2383 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-02-15 06:05 | 2013-02-15 07:00 | 274 | 55 | 4820801 | 15070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN RECLOSERS TO SAFELY MAKE REPAIRS WHERE WIRE BURNT DOWN// ASSOCIATED WITH OUTAGE 4820711// HAS OPENED AT 0605 - // CLOSED AT 0700 VER/ARN IDC XXXX
2384 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-06-08 06:33 | 2009-06-08 08:50 | 110 | 137 | 54060-1 | 15070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ,,FOUND A BURNT JUMPER ON POLE 547-179,,,I WILL OPEN RECLOSER ON POLE 547-177,,,,POWER RESTORED OPEN @ 0815 CLOSED IN @ 0850// VER/TOM L3/TOM IDCC TOF0815, CDC86, PN176 XXXX
2385 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2021-12-07 18:20 | 2021-12-07 22:58 | 184 | 278 | 4159921 | 15044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp failed on pole 37830370000001 towards pole 37830370000002 // cod 31 // opened RECL 37830394D00171 @ 2216 // cod +153 // off at 2216 and on at 2258
2386 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-24 05:28 | 2016-02-24 05:49 | 949 | 21 | 4753171 | 15043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED VIA SCADA @ 0528 CLOSED @ 0535 CLOSED SW 117-A2-6028 VIA FIELD @ 0549 VER/ARN /// FIRST STEP SHOWED 949 CUST REST --- L3/HFP HFPC CNT949 AJB
2387 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2013-04-24 16:29 | 2013-04-24 19:55 | 73 | 206 | 4044331 | 15038 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BRACES PULLED APART LETTING CROSSARM TILT UP CAUSING PHASE A TO CONTACT THE GUY WIRE.//COD 73// VER/DBM IDC XXXX
2388 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-08-28 02:18 | 2012-08-28 03:32 | 203 | 74 | H4978981 | 15022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | <<PHASE C RECLOSER ONLY>>OPEN ON 785-121.//410 CUSTOMERS//. #4 CU PRIMARY DOWN ON 785-45.. CREW ENROUTE TO REPAIR.< CLOSED RECLOSER ON 785-121 (PH C) @ 2:12 ENERGIZING UP TO OPEN SWITCHES ON 809-81. CLOSED SWITCHES @ 3:32 RESTORING REMAINING CUSTOMERS. SH RELEASED BY CREW 07 IDCC DUP TO OPEN SWITCHES XXXX
2389 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-09-10 01:27 | 2017-09-10 19:25 | 17 | 1078 | 4343941 | 15022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINE FUSE OPEN @37830071C30923, FAULT INDICATOR TRIPPED AT FIRST TRANS. AFTER L/F, WILL NEED A LINE CREW TO HELP LOCATE FAULT, 3 PADMOUNT TRANS. ARE AFFECTED. ISOLATED BAD SPAN OF CABLE BETWEEN TRANS. 71-165 AND 166, CLOSED L/F @71-C3-923 AND PICKED UP CUSTOMRS ON 165 @1232. OPENED THAT L/F BACK UP @1530 TO SPLICE CABLE, MADE ALL REPAIRS AND CLOSED L/F BACK IN @1925. RELEASED BY CREW 074S05 37830071000165 VER/AWD SJG
2390 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-03-04 13:30 | 2019-03-04 14:25 | 273 | 55 | 4950611 | 15015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | OPENED RECLOSER 37830472000183//COD 273//CONDUCTOR OFF INSULATER @ POLE 37830496000002 //OFF @ 1330 ON @ 1425 L3/HFP
2391 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-04-29 23:02 | 2017-04-30 08:39 | 26 | 577 | 4696491 | 15002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINEF IS OUT,NOTHING EVIDENT,WILL RE-FUSE//////FUSE BLEW,NEED HELP TO PTRL ACROSS MTN//////BAD LA POLE 1007-106,CLEARED&RESTOREDAT 08:39 RELEASED BY CREW 074S06/ ISO 38830983000044/ COD 26/ VER/BOW L3/HFP XXXHFP AJB
2392 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-09-09 20:09 | 2015-09-10 01:00 | 58 | 291 | 4219551 | 14997 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | A PHASE RECL ONLY 58 CUST/ BAD SWITCH 37830091A00065/ ALSO BAD TRANS CUTOUT 37830091A00289/ ISO 37830115000055/ COD 58/ WITCH POLE 91-65 HAVE REPAIRS MADE. CLOSED RECLOSER IN AT 00:27 AND TRANSFORMER BANK IN AT 01:00/ VER/BOW /// PER VOICE RECORDER A PHASE OUT (MIDDLE PHASE RECL) COULD NOT TELL PER B.O. & CALLS OR SCADA = L3/HFP XXXHFP AJB
2393 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-02-10 00:05 | 2020-02-10 00:42 | 405 | 37 | 4386241 | 14985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A phase conductor off of insultor, laying on cross arm and smoking on pole 255-45. Need big bucket and a 12KV angle pin and insulator. Reclosers on pole 231-291 opened from 00:05 to 00:42 L3/HFP
2394 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2015-02-20 18:13 | 2015-02-20 22:00 | 66 | 227 | 4058701 | 14982 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | EMERGENCY OUTAGE DUE TO GOAB SW FAILING // OPENED CB VIA SCADA @ 1914 - 567 CUST PHASE A AND C IS BURNED UP ON THE GOAB. THE GOAB WILL NEED TO BE BYPASSED. LINE CREW IS EN-ROUTE TO MAKE REPAIRS. POLE 37820008A00150 IS OPENED AND TAGGED TO KYDDC. RELEASED BY CREW 079S02// CLOSED CB VIA SVC @ 2200 VER/HFP L3/HFP AJB
2395 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-05-07 23:28 | 2008-05-08 02:59 | 71 | 211 | 57980-1 | 14981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3201001//,ON SITE, PATROLLING LINE, CALLED R MARCUM FOR HELP//FOUND BURNT RISER AND BUSTED CUTOUT ON POLE 1062-30//OPENING NC SWITCH @ 1062-40 TO MAKE REPAIRS AT FAULT POLE//3201001// RELEASED BY CREW 080S01//LEFT HAND PHASE WAS THE ONLY OUTAGE UNTIL SWITH WAS OPENED IDC XXXX
2396 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-11-27 12:39 | 2021-11-27 17:51 | 48 | 312 | 4128511 | 14976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Load side fuse open at step Down at 236-2,(ASSESSING CONDITION)Load side fuse open at step Down at 236-2,At pole 236-15 tie wire has broke letting Primary come off Insulator and is laying against Pole top Pin,Going to Climb pole and tie Conductor back in.Load side fuse open at step Down at 236-2,At pole 236-15 tie wire has broke letting Primary come off Insulator and is laying against Pole top Pin,Going to Climb pole and tie Conductor back in.Restored service at 17:51.
2397 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-01-30 08:51 | 2013-01-30 15:15 | 39 | 384 | 4754321 | 14976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER PHASE RECLOSER OUT (A PHASE 39 CUST) MIDDLE PHASE RECLOSER IS OPEN, BAD CUTOUT ON POLE 184-215, WILL NEED TO OPEN CAPACITOR BANK TO REPAIR ///VER/CRB L/3 CRB IDC COUNT SEEMS HIGH BUT NO WAY TO DISPROVE XXXX
2398 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-06-16 20:16 | 2019-06-17 01:28 | 48 | 312 | 4515801 | 14976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 38830068A00585 B PHASE 48cc RECLOSURE WENT BAD TAGGED TO THE DDC AND CLOSED THE 600 AMP DISCONNECT AT 1:28 Released by crew 078H01/ ISO 38830068A00585/ COD 48
2399 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-12-01 09:20 | 2008-12-01 11:30 | 115 | 130 | 53447-1 | 14950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-112 RELATED TO ORDER 53383-1 NOTE FROM THAT ORDER--- POLE FIRE, POLE 38830326000120 IS BURNT INTO AND FLOATING, NEED CREW, 45-4 POLE, TRUCK OK, MAY NEED FLAGGERS. ERIC B WITH DAVIS H ELLIOT WILL BE WORKING THIS TICKET OUTAGE FOR THIS IN ORDER 53447-13001002 - POLE FIRE, POLE 38830326000120 IS BURNT INTO AND FLOATING, NEED CREW, 45-4 POLE, TRUCK OK, ERIC B WITH DAVIS H ELLIOT WILL BE WORKING THIS TICKET, OPENED SOLID BLADE ON POLE 326-11 AT 09:20 L3/KEP IDC XXXX
2400 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-04-08 12:39 | 2019-04-08 15:45 | 123 | 186 | 4069671 | 14948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | recloser open @ 374-D-119. failed arrester on pole 375-B-402.. lift clamp on pole 37830375B00402 isolating 1 pole tap to be able to make repairs. tagged to myself 077H21. recloser 374-119 CLOSED @ 14:40// ALL RESTORED @ 1545recloser open @ 374-D-119. failed arrester on pole 375-B-402.. lift clamp on pole 375-B-42 isolating 1 pole tap to be able to make repairs. tagged to myself 077H21. recloser 374-119 CLOSED @ 14:40.. last customer on 375-402 restored @ 15:45 Released by crew 077H21 L3/HFP sjg
2401 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2009-02-07 15:32 | 2009-02-07 18:00 | 101 | 148 | 56563-1 | 14948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3003703// POLR TOP BUSTED OUT @ 187-9// LYKINS DHE CREW HERE - WR # 28410939 // TOP OF POLE BROKE OUT. INSTALLED POLE TOP EXT. TO MAKE REPAIRS.// VER/TOM L3/TOM IDC XXXX
2402 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-02-27 03:41 | 2021-02-27 12:12 | 32 | 511 | 4259571 | 14926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse open on 263-A-4,(ASSESSING CONDITION)..Found a broke cutout on pole 239-6,Climbed pole and changed it tried fuse and it went back out,Found another one on 239-295 isolated it going to get cutout..Got Line fuse back in at 11:26..Restored Trans on 239-295 at 12:12.. Released by crew 074S01
2403 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-08-11 04:33 | 2012-08-11 21:15 | 18 | 1002 | 4927181 | 14925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD. OUT // CHECKING//LINE FUSE OUT ON POLE 24-1506 DUE TO TREES// WILL CUTFUSE CAME BACK OUT ON POLE1152-211 //NEED CREW /// D HAMILTON, & CAMPBELL, BILL & RICK RAY// CABLE BAD FROM PAD 1152-212 TO 1152-213 RELEASED BY CREW 074S05//ALSO BAD CABLE BTWN 1152-1232 & 1233. ALL ON AT 21:15. RELEASED BY CREW 074H03 IDC XXXX
2404 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-09-25 04:58 | 2009-09-25 11:01 | 45 | 363 | 61896-1 | 14887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN AT POLE469-235, TOP OF POLE 493-46 IS BURNED OFF BAD CUTOUT, ISOLATED ON POLE 493-11... MADE REPAIRS RESTORED POWER AT 11:01 VER/KEP L3/KEP IDC XXXX
2405 | Hazard | 3303902 | LESLIE | WOOTON | 2018-03-02 10:59 | 2018-03-02 18:30 | 33 | 451 | 4928561 | 14883 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout brokedown and burnt of 3 ft of a 35c5 pole,need 40c4 pole cutout complete 25kv transformer,clevis,ridge pin all 7200 kv,need r/w crew and line crew truck accessible Released by crew 077S04replaced pole and restored power at 1830
2406 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-01-02 14:30 | 2012-01-02 16:30 | 124 | 120 | H4225441 | 14880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4225441//OPENED OTHER 2 PHASES @ APPROX 1430 PER SERVICER//COD +112 // VER/DBM IDC XXXX
2407 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-07-18 07:00 | 2015-07-18 10:45 | 66 | 225 | 4905391 | 14850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 182-128, POWER RESTORED VER/KEP AJB
2408 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-03-10 11:21 | 2015-03-10 12:53 | 161 | 92 | 4176131 | 14812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RELEASED BY CREW 078S08/CPHASE OFF OF PIN @ 93-B-25/WILL NEED OUTAGE FOR REPAIRS/VEM/RECLOSERS @117-159 OPEN/FETR1415/VEM/ALL THREE RECLOSERS OPEN@1121/VEM/REPAIRS MADE AND ALL CUST RESTORED 1253/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830117A00159/ COD 161 IDCC PN41 XXXX
2409 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-07-30 09:18 | 2012-07-30 10:50 | 161 | 92 | 4864191 | 14812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/ARN IDC XXXX
2410 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2010-01-19 02:06 | 2010-01-19 07:46 | 47 | 340 | 56277-1 | 14812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER OPEN AT 469-235.. CLOSED RECLOSER AT05:20 MADE HOT UP TO POLE 493-11....CUT ARRESTER IN CLEAR RESTORED POWER AT 07:46 //COD 47 IDC XXXX
2411 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-06-14 04:24 | 2019-06-14 09:53 | 45 | 329 | 4504181 | 14805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | held PO till it rolled up to RecloserRECLR NOT OUT,WIRE DOWN@1081-52,HANGING IN THE CLEAR.NEED CREW,#4COPPER,MAY HAVE PULLED OUT OF A SLEEVE THERE@POLE 52RECLR NOT OUT,WIRE DOWN@1081-52,HANGING IN THE CLEAR.NEED CREW,#4COPPER,MAY HAVE PULLED OUT OF A SLEEVE THERE@POLE 52/////RELEASED FOR RICK RAY Released by crew 074S06. Restored at 09:53 L3/HFP
2412 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-02-01 02:15 | 2013-02-01 10:25 | 32 | 490 | 4779031 | 14800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL WORK IN THE AM DUE TO HAZARDOUS ROAD CONDITIONS. WIRE DOWN OPEN @ POLE 9 & CLOSED @ POLE 8 AT 09:45 ///VER/CRB L/3 CRB IDC XXXX
2413 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2011-08-21 11:10 | 2011-08-21 22:20 | 32 | 670 | 4735211 | 14790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 65T RISER FUSE OUT ON PL#1123-1101///UNKNOWN REASON///POSSIBLE UG BAD///CREW REQUIRED TO LOCATE/TROUBLE SHOOT RELEASED BY CREW 078H16--- XFORMER 1123-1147 & 1123-1148 STILL OUT ALL RESTORED @16:30 RELEASED BY CREW 078H01//PT ON SITE//REPAIRED UG ALL POWER RESTORED AT 22:20 CLOSE TKT. RELEASED BY CREW 078H03 COD-32 ISO DF 39831123A31101 IDC XXXX
2414 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-06-20 16:55 | 2019-06-20 19:51 | 84 | 176 | 4556931 | 14784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | pole on fire at 38830428000050 switch on pole38830404000198 opened at 16:55 need 36in ridge pin crew req tagged to bobby tacket no grounds Released by crew 078H09,repairs made all cust restored @ 1951 please close ticket thanks.bt
2415 | Hazard | 3309301 | VICCO | REDFOX | 2008-04-03 13:16 | 2008-04-03 21:45 | 29 | 509 | 63407-1 | 14761 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 37830325B00064, PATROLLING, FOUND TOP OF POLE BURNT OFF, POLE # 325-73 VER/HFP IDC XXXX
2416 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2012-08-14 17:47 | 2012-08-14 23:01 | 47 | 314 | 4937291 | 14758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SERVICER STEVE HALL FOUND BROKE CROSSARMS ON POLE 1047-104//OPENED RECLOSERS TO ISOLATE//COD 47//NEED 3 MAN LINE CREW W/BIG BUCKET//CREW ON SITE STARTING REPAIRS TCM// ARMS REMOVED//MD FILED//COD 47// VER/DBM IDC XXXX
2417 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-06-17 04:47 | 2009-06-17 12:28 | 32 | 461 | 52742-1 | 14752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WE HAVE RISER BURNT OFF AT CLAMP THAT SERVES STEPDOWN ON TRACE AND PRIMARY TAP AND XFMR THATS ON POLE 37830207C00009. JEFF COMBS, JEFF BAKER AND R/W CREW ENROUTE.////POWER RESTORED 1215//COD 32//ISO//UNABLE TO CLOSE ORDER//
2418 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-12-20 20:18 | 2012-12-21 03:45 | 33 | 447 | 4490441 | 14751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE AT 20:18 === POLE FIRE == POLE 37830466000067=== NEED LINE CREW NEED 3-4 LINE CREW. CHANGE POLE BURNED OFF.OPEN LINE AT 20:18 === POLE FIRE == POLE 37830466000067=== NEED LINE CREW === NEED 45 4 POLE 2 CUTOUTS POLE TOP PIN 2 T BRACKETS A 25 KVA TRANSF 72 KVA ==\OPEN LINE AT 20:18 === POLE FIRE == POLE 37830466000067=== NEED LINE CREW === NEED 45 4 POLE 2 CUTOUTS POLE TOP PIN 2 T BRACKETS A 25 KVA TRANSF 72 HUNDERD\OPEN LINE AT 20:18 === POLE FIRE == POLE 37830466000067=== NEED VER/PDP
2419 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-10-09 07:48 | 2022-10-09 13:31 | 43 | 343 | 4008311 | 14749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | primary slacked down to neutral between 962-21 & 20 // changed 19.9 dead end insulator // RESTORED @ 13:31
2420 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-11-07 02:32 | 2015-11-07 11:59 | 26 | 567 | 4416711 | 14742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MAYBE BAD TRANSFORMER , READING AT TRANSFORMER BUSHING 80VOLTS X1 TO X2 AND 80 VOLTS X3 TO X2 AND 160 FROM X1 TO X3,,,,GOING TO DO OTHERCKS///FOUND 2LINE FUSESOUT ON POLE 37830248A00407//BAD CUT OUT ON POLE 37830247C00143, BORN CROSSARM INTO ,NEED 2 8FT ARMS AND BRACES ,3 ARM PINS AND INSLULTORS,6 DEAD END INSULATORS AND SHOES,3 CUTOUTS AND ARM BRACKETS,3 LIGHTING ARRESTERS AND ARM BRACKETS.THISNIS ON A 30FT POLE, AND RESTORED POWER AT 1159 VER /CRB L3/HFP HFPC FP37830248A00143 AJB
2421 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-11-01 02:10 | 2013-11-01 18:30 | 15 | 980 | 4983341 | 14700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 078S08 - AT ISO POLE # 140/529 FOUND RISER PULLED OUT OF HOT LINE CLAMP GOING TO CUT-OUT. LINE DEPT. MADE REPAIRS. FOUND NO OTHER PROBLEMS. COD-15 ISO LF 38830140A20529 VER/HFP L3/HFP IDCC FEC48 XXXX
2422 | Hazard | 3309302 | VICCO | JEFF | 2015-11-04 14:20 | 2015-11-04 16:40 | 105 | 140 | 4409531 | 14700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPEN LINE RECLOSER AT 14:20 === END OF CROSS ARM BURNED OFF === NEED LINE CREW AND 8 CROSS ARM ARM PINS === REPLACED CROSS ARM === LINE FUSE ON POLE 322B - 21 NEEDS TO BE PUT ON MAPS 15 T IN FUSE ===/ MD DONE/ ISO 37830322B00302/ COD 105/ VER/BOW // VER TIME PER VOICE RECORDER - L3/HFP XXXHFP AJB
2423 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-12-10 22:06 | 2013-12-11 02:38 | 54 | 272 | 4150391 | 14688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEPDOWN FUSE OUT ON POLE 38830116D00708--BOTH ARRESTORS BLOW OFF TRANSFORMER-- RELEASED BY CREW 078S07/FETR/03:30/JEH/ REPAIRS COMP. POWER RESTORED @ 02:38//JEH A PHASE OUT PER B.O. AND CALLS IN TROUBLE ORDER TOTAL OF 54 CUST VER/HFP L3/HFP IDC XXXX
2424 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2012-09-18 09:12 | 2012-09-18 16:51 | 32 | 459 | 4058921 | 14688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830467000009 LINE FUSES OPEN AT 09:12 === INSULATOR WENT BAD LETTING PHASE LAY ON ARM === SETTING POLE FIRE === NEED LINE CREW AND ROW CREW === RELEASED BY CREW 077S03 WORKED POLE ,LOWERING ON IT , RIGHT OF WAY CREWS DOWN IN PROCESS OF RESTORING POWER COD-32 ISO LF 37830467000009 VER/HFP L3/HFP IDCC TOF0750 XXXX
2425 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-08-17 06:00 | 2018-08-17 12:48 | 36 | 408 | 4962961 | 14688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Dispatched in accordance with KYPCo Late Night Callout Guidelines //38830235000068 30t line fuse blown--38830259000022 pri off ridge pin nbt-crew req-ds081718 Released by crew 078S01 L3/HFP
2426 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-10-29 02:45 | 2014-10-29 11:10 | 29 | 505 | 4669731 | 14645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN MORNING RELEASED BY CREW 077S12 BAD CUTOUT TOOK CUTOUT OF LINE INACTIVE TRANSFORMER VER/CRB VER/HFP FAULT POLE IS INCORRECT AJB
2427 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-09-11 19:47 | 2022-09-11 21:53 | 116 | 126 | 4867461 | 14616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop burned open on pole 1012-52//will have to open reclosers on pole 1012-a-229 to make repairs//COD 93 FROM BEGINNING //loop burned open on pole 1012-52//will have to open reclosers on pole 1012-a-229 to make repairs//repairs made//opened at 21:15//restored at 21:53//complete//em Released by crew 079S01
2428 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-11-17 12:24 | 2014-11-17 17:24 | 66 | 300 | 4736021 | 14592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNED OF @ POLE 178B-331 , OPENED LOOP ON POLE 178B-330 . NEED BIG BUCKET & POLE TOP , INSULATOR , CUTOUT & T BRACKET . CLOSED RECLOSER ON POLE 178B-166 @ 16:00 . RELEASED BY CREW 075H04 ON SITE WORKING CLOSED LOOP ON POLE 330 MADE REPAIRS ALL POWER RESTORED AT 17:24 RELEASED BY CREW 077H02// COD 62+4 VER/HFP L3/HFP AJB
2429 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-07-10 17:34 | 2011-07-10 18:55 | 180 | 81 | 4500681 | 14580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 44-363 BAD LA ALSO INSTALLED LINE FUSE 30T ON POLE 44-159 ALSO TRANS ON POLE 44-518 ON SAME LINE FUSE SEND NOTE TO TREE PEOPLE TREES AND VINES NEED CUT OFF REC. POLE AND NEXT POLE COVERED IN VINES 44-665 AND 44-149 ENTERED MD.. SENT EMAIL COD-180 ISO OCR 38830044A00665 VER/HFP L3/HFP IDC XXXX
2430 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-04-28 00:30 | 2013-04-28 08:36 | 30 | 486 | 4052581 | 14580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN LOOP ON POLE 37830225D00276, MANUAL, WILL HAVE TO DEENERGIZE 3 PHASE TO REPAIR. FOUMD B HASE DOWN AT POLE 37830225D00274 RELEASED BY CREW 077S04// 30 CC OUT ORIGINALLY// OPENED OCR + 179CC// CLOSED OCR @ 0710 RESTORING 117 CC, LEAVING 92 (30 ORIGINAL +62 OUTAGED TO MAKE REPAIRS) RESTORED AT 0836 IDCC CNT209 XXXX
2431 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-02-29 00:22 | 2008-03-01 03:21 | 9 | 1619 | 51621-1 | 14571 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409002/ FAULT POLE 760-D-109 --- SERVICER OPENED LINE FUSE AT POLE 760-D-24 TO ISOLATE POLE FIREPOLE FIRE ON 760-109 OPENED ON POLE 760-24 TIM MIILER ON HIS WAY REWORKED POLE EVERY THING BACK TO NORMAL VER/PDP IDCC PN109, FEC49, CDC96 XXXX
2432 | Hazard | 3310502 | HADDIX | CANOE | 2018-11-10 04:39 | 2018-11-10 12:29 | 31 | 470 | 4385071 | 14570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN @ POLE 37830050000053// ///// QUESTIONS ABOUT THE EQUIPMENT FAILURE = L3/HFP
2433 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-07-25 16:10 | 2015-07-25 16:29 | 766 | 19 | 4941431 | 14554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | //BAD INSULATER ON POLE 39831123D37174//B PHASE LOOP INSULATOR BLOWN APART @ 1123-D3-7174.B PHASE LOOP INSULATOR POWER OFF @ 1610//BLOWN APART @ 1123-D3-7174. RELEASED BY CREW 078S07/POWER OFF AT 16:10 BACK ON @16:29 PLEASE CLOSE TIC RM//NO OUTAGE TILL RECLOSER OPENED VER/CRB
2434 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2017-07-07 12:01 | 2017-07-07 13:48 | 136 | 107 | 4088251 | 14552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP AND STIRRUP BURNED UP, I REPLACED THEM VER/CRB SJG
2435 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-05-22 11:14 | 2010-05-22 12:27 | 199 | 73 | 66297-1 | 14527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35235975 // LINE C/O BROKEN//// REPLACED BROKEN C/O ON POLE 247-764, CLOSED REC. ON POLE 247-616, POWER RESTORED. COD-199 VER/HFP L3/HFP IDC XXXX
2436 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-12-24 12:30 | 2016-12-24 18:33 | 40 | 363 | 4234721 | 14520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN 674-B-251 PATROLLING LINE... CUT OUT FAILED BURNING TOP OF POLE 674-B-97 WE CAN LOWER ATTACHMENTS DOWN AND REUSE POLE NEED 4 MAN LINE CREW I WILL CONTACT FOREMAN WITH MATERIAL LIST////TAGGED OPEN SWITCH ON POLE 251 TO MYSELF AND PLACED GROUNDS AT POLES 674 B 251 AND 674-98.POWER RESTORED 18:33/ ISO 38820674B00251/ COD 40/ VER/BOW AJB
2437 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-06-20 18:25 | 2018-06-21 00:25 | 60 | 360 | 4630941 | 14516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE L/F ON POLE 37830088000054 OPEN//COD 37 . opened A and C phases at 23:33 (cod +23), All customers restored at 00:25, ALL WORK COMPLETE / GXJ Released by crew 074S03
2438 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-09-12 21:45 | 2017-09-12 22:30 | 322 | 45 | 4355501 | 14490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED XFMR CUTOUT BURNT 8FT CROSSARM OFF IN DIFFICULT LOCATION. PHASE IS STILL HOT UNTIL WE OPEN ALL THREE TO MAKE REPAIRS. OPENED 2145-2230 38830833D00521 38830857000078FAILED XFMR CUTOUT BURNT 8FT CROSSARM OFF IN DIFFICULT LOCATION. PHASE IS STILL HOT UNTIL WE OPEN ALL THREE TO MAKE REPAIRS. REPLACED ARM, CUTOUT AND ARRESTER. RESTORED @ 22:30. SH VER/AWD L3/HFP XXXHFP SJG
2439 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2009-03-02 19:47 | 2009-03-02 21:29 | 142 | 102 | 54308-1 | 14484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 2150105// 1947 CB LOCKED OUT CC1577 //SERVICER DISP// AT 2020 TIM REPORTS AT RECLOSER POLE 1017-A-518 3 PHASE RECLOSER FAILED. GAVE TIM PERMISSION TO CLEAR RECLOSERS AND PUT THE BYPASSES IN. TIM BELIEVES THIS TOOK THE CB OUT. AT 2110 TIM REPORTS RECLOSERS IN CLEAR AND SOLID BLADE BYPASSES IN. CLOSED CB AT 2129 RESTORING 1577 CUSTOMERS. VER/JRJ IDC XXXX
2440 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-04-02 21:38 | 2016-04-03 10:20 | 19 | 762 | 4029921 | 14478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER LOOSE ON LOAD SIDE OF STEP DOWN TRANSFORMER PHASE A, OPENED B & C PHASES AT 10:05 FOR REPAIRS , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 RESTORED 1020 VER/KEP L3/HFP XXXHFP
2441 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-01-19 15:29 | 2022-01-19 19:00 | 211 | 211 | 4386471 | 14475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire is down between 151-230 and 151-54, crew on the way cutout failed on pole 54 causing wire to burn down Released by crew 077S02 // opened recloser on 151-252 to put wire up / off@1830 on@1900
2442 | Hazard | 3303902 | LESLIE | WOOTON | 2008-06-03 15:49 | 2008-06-03 17:57 | 113 | 128 | 55097-1 | 14464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3303902// LOOP BURNT OPEN ON A PHASE ONLY AT POLE 342-85//RELEASED BY CREW 077H03 FAULT POLE 37830342000085 RELATED TO ORDER 55250-1 RECLOSER OUTAGE TO MAKE REPAIRS TO LOOP IN THIS ORDER/3303902// LOOP BURNT OPEN ON A PHASE ONLY AT POLE 342-85//RELEASED BY CREW 077H03 OPENED RECLOSER ON POLE 365-175 AT 17;42 CLOSED AT 17:57
2443 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2012-06-21 22:33 | 2012-06-22 15:46 | 14 | 1033 | 4943251 | 14462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND RELEASED BY CREW 074S05 REPAIRS MADE ON AT 15:46 D SAMMONS COD-14 ISO DF 38831127B00234 VER/HFP L3/HFP AJB
2444 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-11-22 02:47 | 2008-11-22 06:44 | 61 | 237 | 50888-1 | 14457 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3116101//COD-61 //CREW REQUIRED 6A COPPER/WR NO.27405448/TRUCKS OK VER/LDA MLR OK IDC XXXX
2445 | South Williamson | 3411401 | DEWEY | INEZ | 2011-11-19 15:02 | 2011-11-19 17:21 | 104 | 139 | 4093331 | 14456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | FOUND OCR OPEN PATROLLING NOW TCM// CLOSED OCR IN AT 1721 STAYED IN THINKING ABOUT BYPASSING TCM/ BYPASSED OCR ON POLE 790-113 WITH 50T REMOVED LEADS HUNG TAG, PLEASE PLACE IN ABNORMAL SEND COPY TO CLIFF FREEMAN, THANKS TCM//MADE AED /// VER/CRB IDC XXXX
2446 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-01-22 11:26 | 2010-01-22 18:40 | 50 | 434 | 58006-1 | 14450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER BOYD CO 911, LINES DOWN @ MITCHELL STBAD CUTOUT BURNT TOP OF POLE OFF/ CALLED FOR CREW//LIFTED HOT TAP ON POLE 38830094A31070 AN INSTALLED GROUNDS AN TAGSBAD CUTOUT BURNT TOP OF POLE OFF/ CALLED FOR CREW//LIFTED HOT TAP ON POLE 38830094A31070 AN INSTALLED GROUNDS AN TAGS // INSTALLED GROUND ONPOLE 38830094A31073 //ADVISED JOE TO CHECK PRIMARY LOOP ON POLE 38830094A31070 --CLOSED LINE FUSE IN ON POLE 38830094A30255AT 13:50BAD CUTOUT BURNT TOP OF POL ON P VER/HFP L3/HFP IDC TOTAL COUNT IS 50 XXXX
2447 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-04-24 19:43 | 2013-04-25 05:45 | 24 | 602 | 4045691 | 14448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED FUSES ON POLE 37830248A00284 AT 20:10-- POLE # 37830248A00363, ROTTED OFF AT GROUND, ARMS BROKEN ON POLE 37830248A00344 AND 37830248A00342 RELEASED BY CREW 077S04 REPLACED POLE AND REPAIRS MADE POWER RESTORE TO ALL BUT ONE , REPAIRS WILL HAVE TO BE MADE ON THEIR SIDE AND CALL IN . POWER RESTORED AT 545 IDCC CNT48 XXXX
2448 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-04-08 19:42 | 2010-04-09 04:18 | 28 | 516 | 61303-1 | 14448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF ON POLE 380-359 ( 40/4, NEED 45/4 ) TRUCKS TO POLE. RELEASED BY CREW 078S01 VER/PDP IDC TOF1936 XXXX
2449 | Hazard | 3309302 | VICCO | JEFF | 2019-11-26 13:53 | 2019-11-26 16:45 | 84 | 172 | 4069601 | 14448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | top of cutout on high side C phase burnt off will need 2 19.9 cutouts, 2 7.2 cutouts t-brackets and arresters, big bucket , opened A&B phase at 15:45,restored at 16:45 Released by crew 077H14
2450 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-03-01 14:34 | 2018-03-02 17:57 | 29 | 1127 | 4893831 | 14441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 807388//bad 19.9 cutout on 139-6067, pole & arm burnt bad. on 3ph stepdown 2 pole structure//repairs completed and custoemrs restored//abnormal feed to be switched by local crews after start time //Made adjustments per DOL
2451 | South Williamson | 3411401 | DEWEY | INEZ | 2011-02-28 12:13 | 2011-02-28 19:05 | 35 | 412 | 64539-1 | 14420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF ON POLE 768-22// CREW ON SITE//REPAIRS MADE//RESTORED AT 19:05//COMPLETE//EM//VER/CRB IDC XXXX
2452 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-07-16 22:05 | 2011-07-16 23:45 | 144 | 100 | H4554441 | 14400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE REC. OPEN ON 38831125B00772// PATROLING// WIRE DOWN ON 1124-11 AT 2205- SERVICER OPENED A-C RECL TO MAKE REPAIRS. CLOSED AT.//23:45// REPAIRS MADE// POWER RESTORE DUP FOR HOIS. 4554441 VER/PDP IDC XXXX
2453 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-07-16 07:00 | 2017-07-16 12:13 | 46 | 313 | 4130151 | 14398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURNT INTO ON C PHASE @24-B4-511, WILL NEED A LINE CREW TO MAKE REPAIRS. WILL HAVE TO OPEN 3 SOLID BLADES @24-B4-352 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED SWITCH AT 24-352 ON ORDER 4131281. OPENED ALL 3 S/BS @1124, MADE REPAIRS AND CLOSED BACK IN @1213. VER/AWD L3/HFP HFPC CNT84 MLR
2454 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-01-30 09:47 | 2013-01-30 11:50 | 117 | 123 | 4755871 | 14391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. ///VER/CRB L/3 CRB IDC LOOKS LIKE PH A AND B ONLY OUT CHANGED COUNT FROM 236 XXXX
2455 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-11-19 12:32 | 2015-11-19 20:30 | 159 | 478 | 4471411 | 14382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON POLE 37830191D00328 BROKE DOWN AND BURNT POLE OFF RIGHT ABOVE XFM...LIFTED HOT TAP ON POLE 191D-49 TO MAKE REPAIRS.MIGHT BE ABLE TO FRAME DOWN. RELEASED BY CREW 074H21//CLOSED OPENED PT @ 2030// VER/CRB
2456 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-09-11 06:52 | 2010-09-11 19:35 | 35 | 763 | 65404-1 | 14380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | FOUND 1 6IN DISK BAD-NOT SURE IF THIS CAUSED OUTAGE--WILL REPLACE AND TRY--PHILLIP,RANDY,JIMFOUND 1 6IN DISK BAD-ALSO 140AMP RV BAD ON POLE 272-1318-ON AT 1230 TO POLE272-390 THIS ON AT 1245-UG STILL OPEN ON POLE272-1319--BAD 150 KVA--1356-----FETR FOR THIS1930--COMBS REPLACINGFOUND 1 6IN DISK BAD-ALSO 140AMP RV BAD ON POLE 272-1318-ON AT 1230 TO POLE272-390 THIS ON AT 1245-UG STILL OPEN ON POLE272-1319--BAD 150 KVA--1356-----FETR FOR THIS1930--COMBS REPLACING VER/HFP L3/HFP AJB TON12:45 1ST RST.
2457 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-09-18 01:56 | 2012-09-18 11:55 | 24 | 599 | 4056581 | 14376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 167 KVA STEPDOWN APPEARS TO BE BAD. WILL NEED FOREMAN 2 LINEMAN 167 KVA 19.9 /7200 LINE TRUCK & MATERIAL HANDLER.THIS WILL BE HEALD TILL MORNING TO REPLACE XFMR. RELEASED BY CREW 074S04 COD-24 ISO LF 38831101C40609 VER/HFP L3/HFP IDC XXXX
2458 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-03-13 11:37 | 2022-03-13 13:21 | 318 | 104 | 4619391 | 14366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Clamp burned up on A phase. Opened all reclosers on 37830153A00233 to make repairs. Opened: 13:11. Closed 13:21
2459 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-05-31 21:09 | 2010-06-01 01:45 | 52 | 276 | 54525-1 | 14352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | PATROLLING LINE, RECLOSER WENT BAD TAKING OUT HIGH SIDE STEPDOWN FUSE, BY-PASSED RECLOSER, POWER RESTORED IDC XXXX
2460 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-04-10 12:25 | 2014-04-10 18:15 | 41 | 350 | 4592361 | 14350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | TRIED FUSE IN ON 478C20203 FUSE BLOWED. LINECREW WITH FAULT LOCATING EQUIPMENT IN ROUT TO SITE, TESTING FOR FAULT LOCATION.//FAULTED ELBOW IN JUNCTION BOX 478-328 THAT FEEDS TO 478-325 GROUNDED AT TRANS 478-325 RELEASED BY CREW 078S11.CREW ON SITE,, ELBOW AND JUNCTION BOX REPAIRED, ALL POWER RESTORED VER/CRB IDC XXXX
2461 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-08-08 21:10 | 2019-08-08 21:22 | 1194 | 12 | 4861861 | 14328 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | station outage to safely bypass regulator ¦¦ VERIFIED TIMES PER SCADA = L3/HFP
2462 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-11-01 02:56 | 2013-11-01 15:30 | 19 | 754 | 4985951 | 14326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 076H06.WIRE DOWN ON POLE 760-96 TO 760-61 CREW MAKING REPAIRS.REPAIRS MADE COD-19 ISO LF 38830760B00057 VER/HFP L3/HFP IDC CHANGED FROM WEATHER UNKNOWN XXXX
2463 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-07-12 04:45 | 2015-07-12 09:15 | 53 | 270 | 4779731 | 14310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE STIRRUP BURNT OFF AT STEPDOWN. COD 53 // OPENED A& B PHASES ADDITIONAL 129 CUSTOMERS AT 0850 CLOSED ALL 3 PHASES AT 0915.//C PHASE STIRRUP BURNT OFF AT STEPDOWN. COD 53 //. WE OPENED RECLOSERS AT 287-286 AT 08:50, MADE REPAIRS AND CLOSED THEM BACK IN AT 09:15. RELEASED BY CREW 074S01 VER/SEF AJB
2464 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-12-29 07:52 | 2013-12-29 08:30 | 376 | 38 | 4209041 | 14288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | POLE 247-5 B PHASE 600 DISCONNECT SWITCH CREW REQUIRED GOING TO ISOLATE/247-12 ISOLATED B PHASE AT 0441 HRS (100 CC) // B. FRALEY, T. EVANS, K. GRIFFITH, C. YOUNGMAN TO ASSIST // STOREROOM - C.STONE TO ASSIST //AT - 0752 A-C PHASE RECL CC CLOSED AT 0830 MADE ANOTHER OUTAGE. 4209041 CC 376 VER/PDP IDC XXXX
2465 | South Williamson | 3411401 | DEWEY | INEZ | 2022-02-22 12:18 | 2022-02-22 12:35 | 969 | 16 | 4528361 | 14282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1185382 // SCADA indicates DA RECL 744-D2-578 operated to l/o // see DOL log for details//another cutout faile don pole 744-398 //
2466 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-11-07 02:36 | 2013-11-07 06:15 | 89 | 219 | 4017191 | 14271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER PATROLLING.CREW REQUIRED ISOLATING ON 150- 68 TRUCKS OKCREW REQUIRED ISOLATING ON 150- 68 TRUCKS OK/#4 COPPER PRIMARY ONLYCREW REQUIRED ISOLATING ON 150- 68 TRUCKS OK/#4 COPPER PRIMARY ONLY/174-163 BACK IN AT 0515 HRSCREW REQUIRED ISOLATING ON 150- 68 TRUCKS OK/#4 COPPER PRIMARY ONLY/174-163 BACK IN AT 0515 HRS, REPAIRS MADE, ALL POWER RESTORED VER/HFP L3/HFP IDC XXXX
2467 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-09-02 23:37 | 2013-09-03 12:38 | 36 | 781 | 4814871 | 14256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /A LINE CUTOUT HAS GONE BAD AND THE PRIMARY IS BURNED DOWN HANGING BY THE RISER ON THE CUTOUT. I CAN ISOLATE THIS ON POLE 331-145 AND GET MOST OF THE CUSTOMERS BACK ON. TO REPAIR EVERYTHING I NEED TWO MEN THIS WILL BE A MANUAL JOB.A LINE CUTOUT HAS GONE BAD AND THE PRIMARY IS BURNED DOWN HANGING BY THE RISER ON THE CUTOUT. I CAN ISOLATE THIS ON POLE 331-145 AND GET MOST OF THE CUSTOMERS BACK ON. I CLOSED THE FUSE IN AT 12:38 COD-36// VER/DBM L3/HFP IDC XXXX
2468 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-08-08 04:35 | 2008-08-08 11:00 | 37 | 385 | 50127-1 | 14245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | GOT SPAN OF WIRE DOWN ON POLE 1038-7 AND ALSO ON POLE 1038-44 GOT INSULATOR TRACKING AND GOT POLE BURNED. SEND TO GREG SHOUSE CREW COMMING TO PUT WIRE UP RELEASED BY CREW 077S05//COD 37// VER/DBM IDC CHANGED EQUIPMENT FROM CONDUCTOR PER CALL XXXX
2469 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-11-01 07:56 | 2014-11-01 12:15 | 55 | 259 | 4680281 | 14245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY CONDUCTOR BURNED DOWN UNDERNEATH A HOT TAP AT POLE 37820121000229. SOURCE SIDE IS IN THE CLEAR. I WILL CALL FOR HELP. I WILL LEAVE RECLOSER AT 97-134 ON UNTIL CREW GETS HERE, WE WILL HAVE TO OPEN IT TO PUT WIRE UP. OPENED RECLOSER ON POLE 97-134 AT 11:35. WE GOT WIRE PUT UP AND I CLOSED REC BACK IN AT 12:15// COD 73// RECLOSER IN ORGINALLY, DEENERGIZED FROM 229 DOWN, OPENED REC TO MAKE SAFE AND GROUNDED AT 229. CLOSED IN REC// AJB VER/DKG L3/DKGXXXC CNT THIS IS THE ORIGINAL OUTAGE FROM WIRE IN CLR
2470 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-02-02 20:03 | 2009-02-02 22:05 | 169 | 122 | 54906-1 | 14241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000102//BAD CUTOUT ON POLE 46-2152//ONLY PHASE A OUT//COD 167//ISO`D @ POLE 46-2156 AND CLOSED `-2152 @ 21:20 WHICH RESTORED 32 CUST//INSTALLED FUSE ON POLE 46-2208 (FILED MD) AND RESTORED UP TO NEW FUSE @ 2128 WHICH RESTORED 131 CUST//CLOSED IN NEW FUSE @ 2205 WHICH PUT LAST 4 CUST ON// IDC XXXX
2471 | Hazard | 3303901 | LESLIE | HYDEN | 2021-08-02 20:14 | 2021-08-02 20:46 | 445 | 32 | 4994871 | 14240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | DOL 1136530 // 37830364B00101 primary have broke loose and are popping and cracking/ laying against crossarm. adjacent pole is very rotten as well both poles have been flagged// bad 19.9 insulator on pole 37830388A00074, called for crew and flaggers//
2472 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-08-12 22:57 | 2009-08-13 00:10 | 195 | 73 | 52122-1 | 14235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR VER/PDP IDC XXXX
2473 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2016-05-13 10:25 | 2016-05-13 14:25 | 76 | 240 | 4212801 | 14221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 45-5813 PRI. LAYING ON GUY WIRE NEED GREW ASAP RELEASED BY CREW 078S08/CREW ON SITE/WILL NEED TO OPEN SWITCHES ON 45-5820/APROX ONE HOUR OUTAGE/VEM/FETR1430/VEM/OPEN SWITCHES AT 1325/HENDRIX REPAIRED AND SWITCHES CLOSE AT 1337/THREE PHASE TAP ON 45-5813 STILL OFF/FETR 1430/VEM/REPAIRS MADE AND FUSES RESTORED 1419/PLEASE CLOSE TICKET/THANKS/VEM AJB
2474 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2020-05-25 19:21 | 2020-05-25 23:18 | 60 | 237 | 4905581 | 14220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 2OF3 RECLRS OUT@963-213,WILL PTRL//////////COND OFF INSULATOR@963-19,HANGING BY HOTTAP.PTRLD REST OF LINE,FOUND NOTHING ELSE///////////MADE REPAIRS&RESTORED,ALL OK FAR AS WE CAN TELL//cod 60//ph A & B only //
2475 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-04-15 15:50 | 2011-04-15 17:06 | 187 | 76 | 57094-1 | 14212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY BURNT IN TWO ON 785-350 <<PHASE A ONLY>>. OPENED A PHASE REC ON 785-640 TO ISOLATE @ 16:15. CREW ENROUTE. OPENED PH B & C REC @ 16:42 TO MAKE REPAIRS. REPAIRS COMPLETE. CLOSED ALL THREE REC ON 785-640 @ 17:06 RESTORING ALL CUSTOMERS. SH RELEASED BY CREW 076S02 IDC XXXX
2476 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-07-23 20:54 | 2016-07-23 22:08 | 192 | 74 | 4672091 | 14208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3202203ARRESTOR FAILED INSIDE STATION AND LAYING ON NEUTRAL BUSHING OF REGULATOR//GOING TO CLEAR UP RELEASED BY CREW 079S01 VER/ARN MLR
2477 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-05-04 06:13 | 2009-05-04 14:45 | 35 | 512 | 65052-1 | 14200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ISOLATED ARRESTOR ON 245-69 TRYING LINE FUSE FAULT INDICATORS NOT TRIPPED/TACKETT WITH ME PATROLING LINE/FRALEYS CREW HERE ALSO RELEASED BY CREW 078S03 OPENED LOOPS AT POLE 245-149 TOWARDS 245-175 CLOSED FUSE AT 1245 // RESTORED LAST 4 @ 1445 VER/KEP L3/KEP IDC XXXX
2478 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-02-12 07:42 | 2009-02-15 14:35 | 3 | 4733 | 66218-1 | 14199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XMER CUTOUT BROKE. CAN DRIVE. TAKE JOE HUGHES RD OFF BUCK BRANCH RD. JOE HUGHES IS THE DIRT/GRAVEL RD, NOT THE PAVED ROAD. RELEASED BY CREW 074E06//REPAIRED AS OF 1435 PER PIKEVILLE OFFICE IDC XXXX
2479 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-05-08 09:50 | 2012-05-08 10:05 | 946 | 15 | H4757951 | 14190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED IN TWO ON LOAD SIDE OF RECLOSER ON POLE #38831077D00001. WILL HAVE TO OPEN BREAKER IN STATION TO ISOLATE.WILL GET LINE CREW TO REPAIR. THESE RECLOSURES NEED TO BE RELOCATED THEY ARE NOT TRUCK ACCESSABLE. PLEASE SEND A COPY OF THIS TO BOB SHURTLEFF & SEE IF HE CAN GET THEM RELOCATED. //PHASE A ONLY (9 CC) // OPENED STA BREAKER TO REPLACE HOT TAP AT POLE 1077-D-1 AT 0950 (946 CC)HOT TAP BURNED IN TWO ON LOAD SIDE OF RECLOSER ON POLE #38831077D00001. //VER/GAH IDCC CDC XXXX
2480 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-03-31 00:55 | 2011-03-31 09:33 | 35 | 518 | 60689-1 | 14186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS FAILED AND BURNT TOP OF 3 PHASE POLE OFF, ONLY C PHASE OUT (35 CUST) AT THIS TIME. CALLING FOR HELP // OPENED A & B PHASE REC (69 CUST) @ 0530, REMOVED CLAMPS AT POLE 229-150, THEN CLOSED RECLS AT POLE 204-80 @ 0541 RESTORING 60 CUST // SEE 60789-1 FOR SECOND RECL OUTAGE TO MAKE UP LOOPS VER/HFP L3/HFP IDC XXXX
2481 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-11-20 20:27 | 2011-11-21 02:50 | 37 | 383 | 4095461 | 14171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLING NOW..FOUND NOTHING, REFUSED LINE FUSE, AND IT BLEW, STILL TRYING TO FIND PROBLEM..CHANGING BAD EPOXILATOR INSULATOR..ALL POWER RESTORED @ 0250HRS..P.HICKS VER/ARN IDC XXXX
2482 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2009-04-01 10:55 | 2009-04-01 12:00 | 218 | 65 | 63732-1 | 14170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP WR # 29184265 // CREW HAD TO OPEN SWITCHES ON POLE 38830045A41599 TO ALLOW THEM TO MAKE EMERGENCY REPAIRS TO OVERHEAD CONDUCTOR THAT HAS FAILED...COD 218 L3/HFP IDC XXXX
2483 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-08-21 01:24 | 2012-08-21 11:40 | 23 | 616 | 4956981 | 14168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED PATROLING LINE WIRE DOWN PRIMARY ONLY TRUCKS OK TO 227-10#4 COPPER RELEASED BY CREW 078S03 VER/KEP IDC XXXX
2484 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2008-12-22 13:58 | 2008-12-22 18:30 | 94 | 272 | 62664-1 | 14129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3403202//ALL ON BUT 1 COUSTOMER ON POLE 139-294 RELEASED BY CREW 074S04 REPLACED BAD DEADEND INS. AND CUTOUT. REENERGIZED LINE AT 1830 RBW//COD 94//ISO 37830139A10045// VER/DBM L3/KEP IDC XXXX
2485 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-03-05 21:20 | 2011-03-05 22:32 | 196 | 72 | 50223-1 | 14112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN 3 RECLOSERS DUE TO THREE PHASE POLE BEING ON FIRE ON HALL RIDGE// ASSOCIATED WITH POWER ON ORDER 50219-1 // CALLING FOR CREW// STS WR# 39052012 BAD CUTOUT POLE 91-194 REPAIRED POLE FIRE TEP . REPAIR SEND TO TEC POLE NEEDS CHGED OPENED REC. ON POLE 91-74 9;20 BACK ON 1015 // 194 CUSTOMERS MAP DISC TO SHOW OCR ON MAP CORRECTLY COMPLETED// IDCC TOF2055 XXXX
2486 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-02-28 12:04 | 2010-02-28 14:10 | 112 | 126 | 61672-1 | 14112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | STS WR # 34050814 // RECLOSER HAS GONE BAD ON POLE 157-298, BY-PASSED RECLOSER ENTERED AED...HFP COD-112 VER/HFP L3/HFP IDC XXXX
2487 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-11-19 01:54 | 2008-11-19 09:29 | 31 | 455 | 66411-1 | 14105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WR 27354496 ** SERVICE FOUND WIRE DOWN WILL ISOLATE- CREW CALLED OUT TO MAKE REPAIRS.WIRE PULLED OUT OF SLEEVE AT 38830351000103, SLID THROUGH NEXT POLE, 2 SPANS PRIMARY DOWN, REC STILL CLOSED, PRI HANGING IN CLEAR AT FAULT POLE. . TRUCK OK RECLS NOT OUT .. WR 27354496 COD-31 AT POLE 103 A PHASE VER/KEP MLRC PN 388303510000075 IDC XXXX
2488 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-07-12 18:25 | 2021-07-12 21:09 | 86 | 164 | 4901691 | 14104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | URD riser open @24-B3-1135, checking. Top of URD riser broke off @24-B3-1135, Paul Layne coming to help change out. Got cutout replaced and riser restored @2109.
2489 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-02-11 21:37 | 2018-02-12 12:18 | 16 | 881 | 4832061 | 14096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire down at pole 38830874000012//appears wire pulled out of sleeve// Released by crew 076S02//no tags or grounds placed//wire down is way back on a hillside and fuse 38830874000009 confirmed open // ISO 38830874000009/ COD 16
2490 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-10-08 08:17 | 2015-10-08 12:08 | 61 | 231 | 4327381 | 14091 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP ON POLE# 151-22 BURNT INTO DUE TO CLOSE SPACEING ALSO BURNT NEUTRAL DOWN , WILLNEED TO OPEN OTHER RECLOSERS ON POLE# 151-252 IN ODER TO MAKE REPAIRS WILL KEEP TIMES // B PHASE INITALLY OUT 61 CUST // OPENED A & C RECL @ 1110 = 150 CUST // CLOSED AT 12:08 SEE H4327381 FOR A & C OUTAGE // VER/HFP L3/HFP AJB
2491 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-04-02 15:18 | 2016-04-02 22:00 | 35 | 402 | 4018871 | 14070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 25T OPEN ON 19A79, WINDSTREAM POLE 19A88 ROTTED. RELEASED BY CREW 078S07,,CREW ON SITE,,WAITING ON WINDSTREAM,,POLE SET ,,TRANSFERRING WIRE,, ALL REPAIRS MADE,,ALL POWER RESTORED VER/HFP L3/HFP AJB
2492 | Hazard | 3303901 | LESLIE | HYDEN | 2022-05-23 19:45 | 2022-05-24 12:30 | 14 | 1005 | 4936241 | 14070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | open primary fuse @ Bobby Munceys Cabin. pole 242-94 to isolate. will take boat to cabin in morn. Released by crew 077H09//NO OUTAGE TILL L/F OPENED AT 1945
2493 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-04-30 15:17 | 2013-04-30 16:48 | 159 | 91 | 4060251 | 14066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE A RECLSOER ONLY//COD 159 //A PHASE RECL OPEN AT 1035-254,WILL PATRLA PHASE RECL OPEN AT 1035-254,WILL PATRL/////OPEND 1011-100,CLOSED TO THERE,STAYED,THEN CLOSED IN AT 1648 AT POLE 1011-100,IT ALSO STAYED IN RELEASED BY CREW 074S06 COD-159 ISO OCR 38821035B40254 OUTAGE EXTENDED IN ORDER 4060601 VER/HFP L3/HFP IDC XXXX
2494 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-04-15 05:53 | 2014-04-15 07:30 | 145 | 97 | 4605201 | 14065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | FOUND HOT TAP ON SOURCE SIDE OF RECLOSER WAS BAD, REPLACED AND ALL CUST RESTORED AT THIS TIME OF 0730 AT THIS LOC VER/KEP IDC CHANGED END TIME FROM 0730 PER LOAD PROFILE AND CHANGED COUNT FROM 196 AND ADDED ORDER FOR OPENING PHASE A XXXX
2495 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-06-28 20:34 | 2008-06-29 06:45 | 23 | 611 | 58261-1 | 14053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED TREE CREW..TREES NEED TO BE CUT BEFORE I CAN GET FUSE TO STAY IN..BB RELEASED BY CREW 076S01RISER PULLED OUT OF HOT TAP... IDC XXXX
2496 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-04-29 12:40 | 2013-04-29 16:19 | 86 | 219 | 4056431 | 14034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN CREW ON THE WAY--OPEN LOOP ON 147-68---MAIN LINE BACK ON AT 15:15 RELEASED BY CREW 077S10//COD 86// VER/DBM IDC XXXX
2497 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2017-05-10 19:56 | 2017-05-11 13:55 | 13 | 1079 | 4778431 | 14027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 37830272B30377 ROTTEN AND GAVE OVER,BUCK ARM POLE / /HELD PER DUTY SUPERVISOR//NO TAGS OR GROUNDS IN PLACE//MADE MD TO SHOW TRANS ON LOAD SIDE OF L/F//COD 13//MAP SHOWS ONLY C PHASE HAS CUSTS/ THERE IS A PRIMARY METERING ON THIS ORDER SO OUTAGE STARTED FROM BEGINNING//SENT TO TECH TO GET PHASING CORRECT//POLE 37830272B30377 ROTTEN AND GAVE OVER,BUCK ARM POLE NEED 40C4 POLE,4 8FT ARMS,4 DEAD ENDS COMPLETE,2 ARM PINS COMPLET,2 CLEVIS,2 GUYS.5 MAN LINE CREW, R/W CREW//VER/CRB
2498 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-05-29 05:10 | 2010-05-29 09:25 | 110 | 255 | 53056-1 | 14010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" PHASE RECLOSER OUT ON POLE 1077-D-652 CC 109 COD-110 //-- WILL PATROL CLOSE RECLOSER AT 0715 REMOVE OPEN POINT 0925 VER/KEP L3/KEP IDC XXXX
2499 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-06-21 10:02 | 2015-06-21 11:30 | 159 | 88 | 4627631 | 13992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING OTHER LINE FUSE ON POLE 45-3638 TO SAFELY REPAIR CUTOUT/ORDER 4627631/CLOSED 1130// VER/ ADH AJB
2500 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2013-06-18 11:26 | 2013-06-18 12:32 | 212 | 66 | 4363531 | 13992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPACER CABLE DOWN AT POLE 272-B4-5, MAIN LINE STILL ENERGIZED, ONLY CUSTOMERS OUT IS AT POLE 272-B4-926 MWL RELEASED BY CREW 077M01 - OPENED AT POLE 272-B4-2 AT 1126 TO SAFELY WORK ON CABLE MWL , HENDIX CABLE BURN DOWN - CAN CLOSE TICKET POWER HAS BEEN RECLOSER MWL //VER/GAH IDCC PN3300602 XXXX
2501 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-01-17 03:17 | 2013-01-17 16:14 | 18 | 777 | 4616071 | 13986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RESTORED AT 1614// WAS OPENED TO ALLOW LOOPS TO BE MADE UP SAFELY// VER/TOM L3/TOM IDCC OPEN WHEN BREAKER OPENED TOF0457 XXXX
2502 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-03-24 19:48 | 2018-03-25 13:42 | 13 | 1074 | 4058761 | 13962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | patroling now. could not find anthing, fuse stayed in for a minute and blew again.send servicer at daylight. Released by crew 077H09 found bad insulator on pole 418-286, power restored // can close mwl / ISO 37830418000068/ COD 13
2503 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-09-26 23:18 | 2015-09-27 00:33 | 186 | 75 | H4276041 | 13950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1148-B3-709 HENDRIX BURNT INTO ON "C" PHASE COD-83POLE 1148-709 HENDRICK BURNT INTO TRUCK TO POLE LOOKS LIKE 4/0 PRI. CAN ON LINES ON 1148-326POLE 1148-709 HENDRICK BURNT INTO TRUCK TO POLE LOOKS LIKE 4/0 PRI. CAN ON LINES ON 1148-326 VER/KEP L3/DKG THIS OUTAGE OPENING OTHER 2 PHASES AJB
2504 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-04-21 07:18 | 2010-04-21 08:51 | 150 | 93 | 65822-1 | 13950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF 3 PHASE POLE BURN OFF == NEED LINE CREW & FLAGGERS == OPEN RECLOSER ON POLE 151-89 AT 7:18 AM == RELEASED BY CREW 077S03 IDC XXXX
2505 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-07-05 21:42 | 2015-07-06 01:13 | 89 | 211 | 4726581 | 13939 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON 834-389, ISOLATED , PATROLLED BACK SOLID ALL THE WAY BACK TO OCRS, HAVE RIGHT HAND OCR LOCKED OUT, CLOSING NOW TCM//"A" PHASE COD-51/FOUND BAD CUTOUT ON 834-73, ISOLATED , PATROLLED BACK SOLID ALL THE WAY BACK TO OCRS, HAVE RIGHT HAND OCR LOCKED OUT, CLOSING NOW TCM//FOUND BAD CUTOUT ON 834-73, ISOLATED , PATROLLED BACK SOLID ALL THE WAY BACK TO OCRS, HAVE RIGHT HAND OCR LOCKED OUT, CLOSING NOW TCM// CLOSED A OCR IN AT 00:18, NEED CUTOUT AND A BUCKET TO REPLACE CUTOUT ON 83 VER/KEP
2506 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2012-12-09 05:42 | 2012-12-09 10:45 | 46 | 303 | 4453001 | 13938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 1301 INSULATOR BROKEN ON 1145-33 NEED LINE CREW TR. TO POLE LINE FUSE OPEN ON 1146-07 //LINKOUS, PHELPS, YOUNGMAN //1301 INSULATOR BROKEN ON 1145-33 NEED LINE CREW TR. TO POLE LINE FUSE OPEN ON 1146-07 POWER RESTORED 10:45 //VER/GAH IDC XXXX
2507 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2016-07-08 18:43 | 2016-07-08 19:10 | 516 | 27 | 4584181 | 13932 | TRANSMISSION STATION | EQUIPMENT FAILURE | ARRESTER | T-LINE OUTAGE RESTORED 1910/// VER/DKM AJBC MCCST
2508 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-12-09 21:49 | 2017-12-09 23:45 | 120 | 116 | 4636931 | 13920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | c phase only,load side hot tap burned off on c phase rec.changing
2509 | Hazard | 3310502 | HADDIX | CANOE | 2015-03-10 09:44 | 2015-03-10 15:07 | 43 | 323 | 4176271 | 13889 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER OPEN ON POLE 37830169C00027. PATROLLED LINE DIDNT SEE ANYTHING ON LINE . CREW COMMING TO HELP FIND FAULT . FOUND BAD ARRESTER ON POLE 37830169D00295 VER/CRB AJB
2510 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-10-27 07:10 | 2018-10-27 10:00 | 172 | 170 | 4331631 | 13865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened recl 5120 at 0710 to clear up a pole fire at pole 1147-5505/ Open point on 39831147C45501, Busted fuse open on 39831147C45555. Feeds towards 1147-5505 (not on maps) Need line crew, and technician, windstream pole. In line 45-4, with a transformer and a tap. Grounded and tagged to rick morgan. Can lower everything on pole. Line fuse back in at 10:00, all power restored Released by crew 078H04//MD MADE//NO OUTAGE TILL OCR OPENED//
2511 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-04-10 23:11 | 2009-04-11 04:35 | 68 | 324 | 51294-1 | 13862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE--BAD CUTOUT BURNT TOP OF POLE OFF--CALLED V MULLINS--CUT LOOP AN INSTALLED TAG AN GROUND ON POLE 39831123A41542--CLOSED FUSE IN AT 01:25 RELEASED BY CREW 078S07/CREW ON SITE/FETR0530/VEM/REPAIRS MADE AND ALL CUST RESTORED 0435/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/LDA IDC XXXX
2512 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-02-02 18:20 | 2019-02-02 18:32 | 1155 | 12 | 4749451 | 13860 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | short outage for mobile installation at Coalton station ¦¦ VERIFIED TIMES PER SCADA & DOL
2513 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-10-13 16:41 | 2011-10-13 17:26 | 308 | 45 | 4975471 | 13860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DAMAGED INSULATOR FOUND - OPENED SW TO DE-ENERGIZE TO SAFELY MAKE REPAIRS// OPENED AT 1641 AND CLOSED AT 1726 - VER/TOM L3/TOM IDC XXXX
2514 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-01-26 11:35 | 2015-01-26 12:15 | 346 | 40 | 4964801 | 13840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENEING RECLOSER 174-A-220 TO REPLACE CROSSARM BRACE ON 198-52/ ISO 37830174A00220/ COD 346/ 1135-1215 /// VERIFIED TIMES WITH VOICE RECORDER // VER/HFP L3/HFP AJB
2515 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-06-27 17:30 | 2008-06-28 01:27 | 29 | 477 | 56614-1 | 13833 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3201001 RELEASED BY CREW 079H07HOT-TAP LOOP BURNED INTO AT POLE 1062-82,NEED 1 MAN TO OPEN LINE SO OUTAGE TIME/REPAIR TIME CAN BE MINIMIZEDTOOK OFF TO REPAIR AT 00:47,BACK ON AT 01:27.HOT-TAP HAD BURNED OFF AJB
2516 | Paintsville | 3401101 | FALCON | FALC-OILS | 2020-05-12 19:35 | 2020-05-12 20:13 | 364 | 38 | 4829061 | 13832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | BAD SWITCH AT POLE 38830806000202 CAUSING LIGHTS TO FLICKER ¦¦ FLAGGING CREW & CREW CALLED OUT TO MAKE REPAIRS. NO OUTAGE AT THIS TIME ¦¦ WILL TAKE APPROX 30 MINUTE OUTAGE TO REPAIR SW ¦¦ COINS CALL PLACED ¦¦ OPENED SWS @ 1935 ¦¦ CLOSED @ 2013Replaced failed 300 amp sw on 806-202. sh
2517 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-09-25 19:09 | 2012-09-26 02:50 | 30 | 461 | 4087431 | 13830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED B PHASE @ 1909//COD 30//OPENED OTHER 2 PHASES @ APPROX 1920//COD +116// POLE BURNT OFF 66-155 SEND TO BOB //COD 146 TOTAL//OPENED B PHASE @ 1909//COD 30//OPENED OTHER 2 PHASES @ APPROX 1920//COD +116// POLE BURNT OFF 66-155 SEND TO BOB RELEASED BY CREW 078S08 VER/ARN IDC XXXX
2518 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-12-29 04:25 | 2012-12-29 18:49 | 16 | 864 | 4547901 | 13824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED--TRUCK TO POLE--PRIMARY DOWN T POLE 38830089000015--INSTALLED TAG AND GROUND AT POLE 38830089000007 RELEASED BY CREW 078S07/CREW ON SITE/FETR 2000/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDC XXXX
2519 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-04-01 07:55 | 2008-04-01 09:33 | 141 | 98 | 62636-1 | 13818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202//SERVICER OPENED RECLOSER IN ORDER TO CHANGE A BROKEN CUTOUT (WAS CAUSING DEVICE OPERATIONS ON THE LINE)//COD 141//CREW TO ASSIST SERVICER, POLE IS IN A BAD CURVE, NEEDS FLAGGERS//VER/CRB IDC XXXX
2520 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-12-23 07:08 | 2009-12-26 11:54 | 3 | 4606 | 65035-1 | 13818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THERE IS A BAD 25KVA, 19.9 - THERE ARE 3-200 AMPS SRVCS HERE// 12-23 2100 - COINS INDICATED POWER STILL OFF. MAW POSSIBLE TRUCK APPROACH
2521 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-02-24 13:22 | 2016-02-24 17:45 | 143 | 263 | 4759001 | 13809 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C PHADE RECLOSER OPENED COD 143//CSP XFMR BURNED UP//CLOSED REC @ 1455//CSP XFMR BURNED UP RELEASED BY CREW 077S12 REPLACED TRANSFORMER POWER RESTORED AT 17:45 RELEASED BY CREW 075H03 VER/CRB AJB
2522 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-08-07 08:08 | 2013-08-07 11:58 | 60 | 230 | 4630831 | 13800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED OFF LINE COD-60 ISO PO @ 38831040000022 VER/HFP L3/HFP IDC XXXX
2523 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-04-03 14:10 | 2015-04-03 14:50 | 345 | 40 | H4263741 | 13800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRICKS BURNED DOWN BETWEEN P-785-263 AND 785-264..OPENED 785-D-331 /..OPENED SWITCHES AT 14.10 BACK ON AT 14.50.. RELEASED BY CREW 076S01 VER/KEP L3/HFP XXX AJB
2524 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-06-01 14:06 | 2022-06-01 15:58 | 123 | 112 | 4993481 | 13776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required 269-331 bad cutout on capbank Released by crew 078S03,repairs made all cust restored @ 1558 please close ticket thanks.bt
2525 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-06-10 16:23 | 2021-06-10 19:13 | 81 | 170 | 4708481 | 13770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase / Load side of the ground based Step down @1076-B4-205 has a busted cutout, Released by crew 074S05
2526 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-01-17 06:57 | 2009-01-17 09:50 | 90 | 173 | 56915-1 | 13745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000303//NEED CREWNEED CREW-PRIMARY DOWNNEED CREW-PRIMARY DOWN--COLD LOAD PROBLEMSNEED CREW-PRIMARY DOWN--COLD LOAD PROBLEMS--RECLOSER BACK ON AT 09:25--CLOSED LINE FUSE ON POLE 44-227 AT 09:50--REPLACED 15T FUSE ON POLE 44-227 WITH 20 T VER/KEP MD FILED L3/KEP AJB
2527 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-03-01 21:44 | 2018-03-01 23:45 | 126 | 121 | 4903191 | 13738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Wire burnt off on the stirup 38820818B00041/ open 2242 closed 2345/ Stepdwon stirrup burnt off 38820818B00041 (100 cust)/ opened recloser @ 2242 to repair/ closed recloser @ 2345 all power restored
2528 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-04-23 10:35 | 2015-04-23 11:15 | 342 | 40 | 4358281 | 13680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON RECLOSER BYPASS CREW OPENED RECL TO MAKE REPAIRS NRO ISSUED VER/KEP L3/HFP XXX AJB
2529 | Hazard | 3303902 | LESLIE | WOOTON | 2019-06-20 11:37 | 2019-06-20 16:00 | 52 | 263 | 4555891 | 13676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT
2530 | Pikeville | 3402002 | KEYSER | STONECOAL | 2013-09-12 18:36 | 2013-09-12 19:07 | 441 | 31 | 4844211 | 13671 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | BAD SWITCH ON POLE 1129A4-311.OPENED RECLOSERS ON POLE 1129A4-271 AT 18:36 SO WE COULD ISOLATE AND JUMPER SWITCH.CLOSED RECLOSERS ON POLE 1129A4-271 AT 19:07..MIDDLE SWITCH ON POLE 1129-311 IS JUMPERED. COD-441 ISO OCR 38831152000271 VER/HFP L3/HFP IDC XXXX
2531 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-04-10 11:16 | 2012-04-10 14:53 | 63 | 217 | 4660721 | 13671 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 CU PRIMARY AND NEUTRAL DOWN CREW ENROUTE. ///VER/CRB IDC CHANGED FROM WEATHER UNKNOWN XXXX
2532 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-03-05 19:35 | 2011-03-05 22:55 | 70 | 200 | 50172-1 | 13659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39051948 // @ 2057 SERVICER PATROLLING CKT //STS WR # 39051948 // BAD CO POLE 285-64 RESTORED 22:55 M.PHELPS RELEASED BY CREW 078H12 IDC XXXX
2533 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-07-24 15:41 | 2018-07-24 19:55 | 67 | 254 | 4849231 | 13658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary broke at basket on pole 38830019B00019, wire still in air. Need line crew, big bucket to pole Released by crew 078H04--crew on site--T&G to RMV @ 19B155-repaired basket--closed in 19B155@ 18:55--found more wire down at 19D148--Open G&T 19B19 to RMV--repairs to 1 span #2AA--30T in on 19B19 @ 19:55--tbl tkt comp---RMV Released by crew 078H16 L3/HFP
2534 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-09-28 10:25 | 2010-09-28 13:20 | 78 | 175 | 54706-1 | 13650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BROKEN 7200 PIN INSULATOR.ON POLE 450-122 //COD 78// VER/DBM IDC XXXX
2535 | South Williamson | 3411401 | DEWEY | INEZ | 2021-08-15 03:21 | 2021-08-15 10:55 | 77 | 434 | 4068871 | 13641 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 1139938/HOLD ORDER REQ/POLE BROKEN AT 672-189/DOL 1139938/POLE BROKEN AT 672-189/crew enroute//Dig # 2108150003DOL 1139938/POLE BROKEN AT 672-189/crew enroute//Dig # 2108150003 Released by crew 079S01 Released by crew 076H06
2536 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-12-27 12:58 | 2009-12-27 16:10 | 71 | 192 | 55748-1 | 13632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NEED NEW GUY ANCHOR INSTALLED ON POLE 285-49, NEEDS HAND DIG, NO TRUCKS TO POLR. RELEASED BY CREW 078S01 IDC XXXX
2537 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-04-14 00:52 | 2022-04-14 07:00 | 37 | 368 | 4760871 | 13616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | Have a Stirup burned into on A Phase at Recloser,Will have to Open Recloser to make repairs,will keep up with Time..Opened Recloser at 05:39 made repairs restored at 07:00.. LR- The 1st all out call came in at 00:52 on 4-14-22.
2538 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-06-25 13:58 | 2009-06-25 15:30 | 148 | 92 | 59252-1 | 13616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP BURNT OFF RISER ON REPAIRING/NO CREW REQUIRED L3/HFP IDC I THINK COUNT IS INCORRECT CALLS CLEARLY INDICATE A AND C NOT JUST A IDC CHECK COUNT VOICE RECORDER
2539 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-01-05 06:25 | 2010-01-05 08:56 | 90 | 151 | 60729-1 | 13590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED OPEN ON SWITCH POLE 43-40 WR 33313543 SEND TO CREWS RELEASED BY CREW 078S08 RELEASED BY CREW 078H0 RELEASED BY CREW 078S08 POLE-44-2004 TIME OFF 08:37 TIME ON 08:56// VER/DBM IDC XXXX
2540 | Hazard | 3309003 | JEFF | VIPER | 2015-09-10 10:39 | 2015-09-10 12:12 | 146 | 93 | 4222221 | 13578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C PHASE ONLY OUT THE A & B STILL IN ===COD 89//C PHASE ONLY 1 OUT THEA B STILL IN ===COD 89// CROSSARM BROKE === NEED LINE CREW RELEASED BY CREW 077S03C PHASE ONLY 1 OUT THE A @ B STILL IN ===COD 89//C PHASE ONLY 1 OUT THEA B STILL IN ===COD 89// CROSSARM BROKE === NEED LINE CREW RELEASED BY CREW 077S03 OPENED OTHER PHASES TO REPLACE ARM , 1039C PHASE ONLY 1 OUT THE A @ B STILL IN ===COD 89//C PHASE ONLY 1 OUT THEA B STILL IN ===COD 89// CROSSARM BROKE === VER/CRB L3/HFP XXXHFP AJ
2541 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-04-06 12:09 | 2010-04-06 13:40 | 149 | 91 | 59556-1 | 13559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | STS WR # 34544985 //REPLACED SOLID BLADE/NO CREW REQUIRED // COD-160 VER/HFP L3/HFP AJB IDC CHANGED COUNT FROM 160, ONLY CALLS ON PH C XXXX
2542 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-06-03 16:43 | 2010-06-04 12:02 | 21 | 1159 | 56032-1 | 13554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SEVICERS PATROLLING CKT. COMPLTED FOLLOWING STEP REST . STILL LOOKING FOR TROUBLE. AT POLE 369-19 LOOP OPEN CLOSED L.F 345-26 AT 2015.LINE FUSE OUT == LOOKED AT LINE COULDNT FINED ANY == REFUSED LINE UP POLE 37830346B00008 STILL HAVE 4 CUST == = WILL RETURN FRIDAY DAYLIGNT. FOUND BAD ARR VER/HFP L3/HFP IDCC XXXX
2543 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-09-29 19:57 | 2012-09-30 01:05 | 44 | 308 | 4099521 | 13552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEAD END INSULATOR BROKE AT POLE 397-37, ONE SPAN OF PRIMARY DOWN TO POLE 38. WILL NEED 2 MEN, DEAD END INSULATOR 15KV AND SHOE AND 50 FT. 6ACW WIRE. RECLOSER IS IN BUT WILL HAVE TO OPEN TO MAKE REPAIRS. WILL ALSO NEED A MANUAL TREE CREW. //C.SEXTON & J.BAKER TO ASSIST// J. COMBS GETTING R/W CREW // OPENED REC 421-130 @ 2345 (22 CUST), CLOSED REC @ 0105 //VER/GAH IDC XXXX
2544 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-11-02 08:29 | 2013-11-02 11:48 | 68 | 199 | 4002901 | 13532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNDT INTO ON POLE 426-258, WILL CHECK REST OF LINE FOR FAULT. PATROLLED LINE FOUND NO TROUBLE. CHANGED STIRRUP OUT AND CLOSED BACK IN AT 11:48. VER/CRB IDC XXXX
2545 | South Williamson | 3411401 | DEWEY | INEZ | 2014-01-07 13:20 | 2014-01-07 14:30 | 193 | 70 | 4249501 | 13510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DHE CONTRACTOR PAUL MUNCY FOUND LEAD BURNT OFF ON THIS REGULATOR//THIS HAS BEEN CAUSING THE OPERATIONS AND FLICKERING IN THE AREA//HE HAS OPENED STEPDOWN 768-41B IN ORDER TO MAKE REPAIRS//COD 193//ALL POWER RESTORE 1430// VER/DBM L3/HFP IDC XXXX
2546 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-07-31 07:00 | 2009-07-31 12:55 | 38 | 355 | 60968-1 | 13490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 623-29 CREW WILL REPLACE,,,BACK ON POWER RESTORED IDC XXXX
2547 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2019-03-23 14:33 | 2019-03-23 18:54 | 99 | 261 | 4018651 | 13485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SCADA Indicated outage @ 1433 99cc/ Hot tap on pole 38830021B43550 crossed phases/ Closed 3002106 @ 1520 99cc.......600 amp C phase switch on pole 38830021B43679 Fired Up and will need replaced./ Opened 3002106 @ 1521 99cc/ Crew required. Working on switching/ Closed N.O. 12kV SWS 38830021B30052 @ 1600 71cc/Released by crew 078H04--crew on site--replaced 3 600A Underslung Switches-- Released by crew 078H16/ Closed 3002106 @ 1854 28cc ¦¦ VERIFIED TIMES PER SCADA & DOL = L3/HFP
2548 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-04-14 14:10 | 2015-04-14 16:35 | 93 | 145 | H4316881 | 13485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | B PHASE OUT/PARTROLLING NOW//COD 49//XARMS BURNT ON POLE 954-C-683, LOAD BUSTING SWITCHES ON POLE 954-A4-908//INTERRUPTED 28 ADDTL CUSTOMERS//OPENED SWITCHES 954 908 AT.13.50..CLOSED REC OFF AT 14.10.TOOK REC OFF AT 16.21 BACK ON AT 16..35./OPENED AGAIN DUE TO SWITCH FAILURE/ RELEASED BY CREW 076S01/ FIX IT IN HOIS// VER/ ADH L3/DKGXXX AJB
2549 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-02-13 16:36 | 2008-02-13 21:00 | 51 | 264 | 62809-1 | 13464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302// ONLY A & B PHASES OPEN INTITALLY//OPENED C PHASE @ 1735 TO ISOLATE POLE//STARTING CUST COUNT 41//INTERUPTED 50 MORE WHEN OPENED C PHASE//TOTAL 91//POLE TOP BURNT OFF//CREW REQUIRED// C PHASE CUSTOMERS OUTAGED ON OTHER ORDER// - // VER/TOM IDC LOOKS LIKE C AND B INITIAL XXXX
2550 | Hazard | 3303901 | LESLIE | HYDEN | 2014-11-22 18:59 | 2014-11-23 00:12 | 43 | 313 | 4754531 | 13459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT GATE OF AN OLDER TYPE, MUST REPLACE CUTOUT. NEED 1 MAN AND AN 19.9 CUTOUT. VER/KEP AJB
2551 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-09-09 10:59 | 2021-09-09 12:56 | 115 | 117 | 4226021 | 13455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired loop on 198-41,,, closed solid blade in @ 12:56 all customers restored complete
2552 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-09-25 19:18 | 2009-09-25 22:10 | 78 | 172 | H62202-1 | 13416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE C FUSE BLOWN ONLY // COD 72//WR#31898687 // POLE-TOP BURNT OFF AT POLE#117-76 // 117-76 BURNT OFF// RELEASED BY CREW 078H07// VER/CRB IDCC DUP TO OPEN PH A AND B XXXX
2553 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-10-15 15:13 | 2009-10-15 17:22 | 104 | 129 | 66141-1 | 13416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 077S10 // SAME AS 65963 RELEASED BY CREW 077S10 POLE 220-207 INSULATOR BROKE REPLACED INSULATOR RESSAGED WIRE RESTORED POWER AT 1722 CREW 077H01 RELEASED BY CREW 077H01 // 104 COD IDCC TOF1410, TON1538 XXXX
2554 | Hazard | 3303901 | LESLIE | HYDEN | 2019-11-30 21:30 | 2019-12-01 09:55 | 18 | 745 | 4108331 | 13410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire burnt into at sleeve
2555 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-05-23 14:55 | 2011-05-23 19:08 | 53 | 253 | H4139961 | 13409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASE RECLOSERS OPEN ON 963-C-213....BAD CUTOUT ON PHASE A ON POLE 963-C2-29....ALSO TREE LIMBS ON LINE BETWEEN 963C18 & 963C20...WILL NEED CUT...NEED TREE CREW & LINE CREW....WILL HAVE TO OPEN 3RD RECLOSER TO CUT ROW....// RELEASED BY CREW 080S01.OPENED OTHER RECLOSER AT 14:55 IDCC DUP TO OPEN PHASE B XXXX
2556 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-06-18 06:50 | 2016-06-18 12:09 | 42 | 319 | 4383801 | 13398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE 4383891*** LOOP BURNT OPEN @ 37820025D00023LOOP OPEN@25-23,NEED FOREMAN,1 A LINEMAN,IS ON HILL ON CHLOE MTN//////WILL OPEN@25-63,OPND@11:35,GRNDD THERE,ALSO GRNDD@25-391/ WORK COMPLTD12:00,WILL RESTORE WHEN OKD TO DO SO.REMD GRNDS,RESTORED@12:09/ ISO 37820025D00023/ COD 42/ VER/BOW AJB
2557 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2020-02-23 09:50 | 2020-02-23 16:51 | 40 | 421 | 4425611 | 13387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | URD riser open @37830048C21254, checking. Bad feed through bushing @48-C4-1573, got changed out and picked up everything from 1573 @1651. Released by crew 074S05
2558 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2018-09-07 21:41 | 2018-09-08 01:40 | 56 | 239 | 4056141 | 13384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap burnt off basket, repairs made. All power restored at 1:40
2559 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-04-29 20:16 | 2021-04-30 00:15 | 56 | 239 | 4498221 | 13384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke line fuse cutout at 269-27. need one man and big bucket to make repaires. restored 00:15
2560 | Hazard | 3310502 | HADDIX | CANOE | 2014-05-22 22:47 | 2014-05-23 09:55 | 20 | 668 | 4743711 | 13360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 37830097000079 COD-20 ISO LF 37830073000003 AJB
2561 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-07-12 00:25 | 2015-07-12 02:31 | 106 | 126 | 4779291 | 13356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ORIGINAL ORDER# 4778981, RECREATED HERE FOR CREW WORK//PER JOHN SODIE, TWO POLES BACK TOWARDS RT 180 FROM THIS POLE, THERE IS A BROKE XARM AND A PHASE OFF THE INSULATOR// POLE 164-122 A PHASE ARM PIN INSOLATER BROKE OUT OF THE ARM NEED LINE CREW AND 6 WHEELER.//ARM CHANGED/// COD 106//SEE OUTAGE LOG FOR SWITCHING DETAILS// VER/DBM
2562 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-07-04 09:21 | 2017-07-04 11:16 | 116 | 115 | 4071301 | 13340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OOPHASE B ONLYOO SOURCE SIDE HOTLINE CLAMP BURNT OFF ON PH B RECLOSER.//COD 116 FROM BEGINNING//OOPHASE B ONLYOO SOURCE SIDE HOTLINE CLAMP BURNT OFF ON PH B RECLOSER. REPLACED HOTLINE CLAMP AND CLOSED REC @ 11:16. CALLED CUSTOMER JENNY LESTER TO CONFIRM REC PICKED UP. SH RELEASED BY CREW 076S02//DID NOT OPEN OTHER 2 PHASES// VER/CRB SJG
2563 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-12 14:30 | 2014-01-12 17:50 | 68 | 200 | 4274681 | 13340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | HAD THIS TROUBLE TWO TIMES BEFORE AND TROUBLE HAS TO BE ON TRANSFORMER AND POLE IS ROTTEN , GOING TO CHANGE POLE OUT BEFORE WE CAN FIX TROUBLE, GOT CREW COMMING TO CHANGE POLE OPEN LINE FUSE ON POLE 30-74 AT 1430 AND CLOSED AT 1746 AND TRANSFORMER AT 1750 RELEASED BY CREW 077S05//COD 68// VER/DBM L3/HFP IDC XXXX
2564 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-10-07 11:12 | 2016-10-07 14:45 | 86 | 213 | 4966991 | 13338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | C PHASE REC. OPEN ON POLE 73-644//COD 86..WILL PATROL..FOUND C PHASE LAYING AND BURNT INTO ARM ON POLE 121-223 WILL NEED LINE CREW AND WILL HAVE TO OPEN THE OTHER TWO REC. ON POLE 73-644 TO MAKE REPAIRS..OPENED UNDERSLUNG SWITCHES ON POLE 121-284 @ 13:25 TO MAKE REPAIRS AND CLOSED BACK IN @ 14:45.. VER/CRB // SEE DUP H4966991 = L3/HFP HFPC LCD37820121000284 DUP STP FEC44 AJB
2565 | Whitesburg | 3309302 | VICCO | JEFF | 2016-08-19 14:40 | 2016-08-19 16:25 | 127 | 105 | 4815701 | 13335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830323D00243 === BAD CUTOUT ON TRANSF MANUAL 19.9 === NEED LINE CREW === GOT MAIN LINE 37830323D00649 ON 16:25 (351 CUST)=== 37830323D00243 @ 1845 (2 CUST)/ VER/BOW L3/HFP XXXHFP AJB
2566 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-07-27 12:38 | 2021-07-27 16:00 | 66 | 202 | 4967271 | 13332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STIRUP BURNT UP ON STEPDOWN MADE REPAIRS @ 1600
2567 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-08-15 09:58 | 2015-08-15 13:20 | 66 | 202 | 4137101 | 13332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING LINE, WIRE HAS COME OFF INSULATOR ON POLE37830182D00114, CALLED FOR HELP// VER/CRB L3/HFP XXXHFP AJB
2568 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-08-20 14:57 | 2017-08-20 18:32 | 62 | 215 | H4280451 | 13330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED SWS AT 1065-D2-287 AT 1457PHASE A LAYING ON THE GROUND BURNING, I OPENED SWITCHES ON POLE 38821065D20287 AT 14:57. NEED COIL OF 1/0 PRIMARY. VER/AWD SJGC CNT256
2569 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-02-21 03:09 | 2020-02-21 05:09 | 111 | 120 | 4421811 | 13320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3411802/gaj/0316/all out disp 3542 T Fields --- Fields reports Solid Blade burnt up & open at 38821130000040///////austin hall enroute to help replace solid blade cutout all restored L3/HFP
2570 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-02-28 15:00 | 2017-02-28 15:52 | 256 | 52 | 4428931 | 13312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER 38831032B10148 TO MAKE REPAIRS ON PO ORDER 4428711//OPENED 1500 CLOSED 1552 VER/CRB /// SEE 4428711 ALSO FOR INITAL OUTAGE OF ONLY B PHASE (137 CUST) PER SERVICER = L3/HFP HFPC CNT158 AJB
2571 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-03-18 05:47 | 2012-03-18 10:24 | 48 | 277 | 4591361 | 13296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT TO STEPDOWN ON POLE 33-D-25 - NEED 1 MAN & BIG BUCKET - ED MATNEY TO ASSIST //BAD CUTOUT AT STEPDOWN AT POLE 33D25 NEED BIG BUCKET AND ONE MAN CANNOT REACH WITH SRV TRUCK. /// COD-48 ISO LF 37820033D00099 VER/HFP L3/HFP IDC XXXX
2572 | Hazard | 3308002 | JACKSON | PANBOWL | 2020-12-02 14:40 | 2020-12-02 14:53 | 1022 | 13 | 4739521 | 13286 | TRANSMISSION STATION | EQUIPMENT FAILURE | REGULATOR | Outage to allow Station crews to safely close TR fused discs after replacing failed Regulator in Station de-energized. Outage should last less than 30 mins from start. FETR 1515 1022 CC Off at 1440 On at 1453
2573 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-09-18 02:46 | 2012-09-18 09:41 | 32 | 415 | 4056861 | 13280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FUSE IS OPEN ON 526-49 PATROLLING LINE. WAITING ON LINECREW TO ASSIST. REPLACED BAD DEADEND BELL, APR CLOSE TICKET. DWEST COD-32 ISO LF 38830526000049 VER/HFP L3/HFP IDC XXXX
2574 | Hazard | 3303902 | LESLIE | WOOTON | 2008-05-19 16:12 | 2008-05-19 17:30 | 170 | 78 | 66028-1 | 13260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3303902// OPENED RECLOSER TO ISOLATE BURNING GOAB - COD 459// 289 RESTORED WHEN RECLOSER RESTORED CLOSED @ 1619// REMAINING CUSTOMERS RESTORED WHEN GOAB REPAIRED AND CLOSED @ 1730// VER/TOM IDCC REMOVED 4 MIN STEP FROM THIS OUTAGE XXXX
2575 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-06-23 20:00 | 2008-06-23 23:24 | 65 | 204 | 53229-1 | 13260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200204 // BAD CUTOUT NEED BIG BUCKET SEND TO TODD HELSEL RELEASED BY CREW 080S03 LF 38821065D20318 CC/65// OFF AT 10:00 ON AT 11:24// VER/SLK AJB
2576 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-10-29 10:49 | 2012-10-29 14:16 | 64 | 207 | 4181961 | 13248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF, LINE CREW ENROUTE. POWER RESTORED AT 14:16 COD-64 ISO LF 38820966A10128 VER/HFP L3/HFP IDC XXXX
2577 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-12-24 00:34 | 2009-12-28 14:56 | 2 | 6622 | 55025-1 | 13244 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUSTOMER WOULD LIKE TREES TRIMMED. HAS PART POWER. 12/27. MDH NEUTRAL IN SECONDARY BROKE. RESPLICED NEUTRAL IN SECONDARY
2578 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-02-14 20:35 | 2011-02-14 22:20 | 126 | 105 | 57425-1 | 13230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 177D-51, CREW ENROUTE. --- SDB / SWS AT POLE 201B/33 OPENED TO ISOLATE INSULATOR.BAD INSULATOR ON POLE 177D-51, CREW ENROUTE. OPENED SWITCHES ON POLE 37830201B00033 AT 2035----POWER RESTORED AT 22:20 VER/KEP IDC XXXX
2579 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-08-08 20:40 | 2017-08-08 22:25 | 126 | 105 | 4241691 | 13230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD 126//RELATED TO 4241671//OPENED RECLOSER TO ISOLATE DOWNED LINE//CONDUCTOR BURNED DOWN AT STURRIP AT POLE #38831078000022 BETWEEN 22 & POLE 8 HAVE CREW ON SITECONDUCTOR BURNED DOWN AT STURRIP AT POLE #38831078000022 BETWEEN 22 & POLE 8 HAVE CREW ON SITE/ ISO 38831077D10727/ COD 126/ OPENED @ 2040 VER/BOW SJG (RELATED TO 4241671)
2580 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2009-12-26 11:31 | 2009-12-28 18:38 | 4 | 3307 | 65818-1 | 13228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL IS BROKE IN S/DROP OUT FROM POLE. NEED A BIG BUCKET. DAVE SAMMONS SAID TO SEND THIS TO HIM. POLE# 237-49. ITS THE HOUSE ON MAIN ROAD { LITTLE BLUE HOUSE ON RIGHT } JUST BEFORE YOU TURN UP CHIMNEY ROAD, BUT YOU HAVE TO TURN UP CHIMNEY RD TO GET TO TRANS. POLE WHERE NEUTRAL IS BROKE. RELEASED BY CREW 074S01REPAIRED SERVICE NEUTRAL THIS TICKET COMPLETE CAN BE CLOSED 12/28 D SAMMONS RELEASED BY CREW 074H02
2581 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-05-30 16:12 | 2017-05-30 17:20 | 194 | 68 | 4883181 | 13192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | .CREW REQ, BAD B PHASE RECLOSER ON POLE 18-11, SOURCE SIDE BUSHING IS BURSTED, AND HOT LEAD BURNTED OFF LOAD SIDE OF THIS RECLOSER, HAVE ISOLATED AND TAGGED TO DDC, RECLOSER IS 100A V4H DOL 745947 AED: KY053017-0542-9006. VER/AWD AJB
2582 | Hazard | 3302704 | HAZARD | KENMONT | 2009-12-27 20:55 | 2009-12-27 23:53 | 74 | 178 | 58898-1 | 13172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 21:08 12-27, CALLED DUTY SUPERVISOR TO FIND SERVICER FOR THIS TROUBLE//....LOW SIDE STEPDOWN FUSE OUT, PATROLING NOW. P.HICKS.296D4-216...SPAN ON 296D3-271 NEEDS RESAGED TOMAROW MORN, REQUIRES BIG BUCKET, REFUSED LOW SIDE OF STEPDOWN, ALL POWER RESTORED @23:53//SENT NOTE TO B LINDON
2583 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-12-31 17:20 | 2018-12-31 17:50 | 439 | 30 | 4616261 | 13170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Doug Hall reports crossarm broken and cutout for transformer hanging off in the air at pole 41-54--CAUTION---do not pull off road at transformer. crossarm burnt into due to line fuse cutout bad. crew on the way. i will be open switches on pole 41-B-104 when the crew gets here and gets in position//OPENED GOAB @ 1720 CLOSED 1750
2584 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-01-26 19:28 | 2011-01-27 02:38 | 36 | 430 | 65720-1 | 13168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF...DUE TO CUTOUT BREAKING DOWN..CALLED ROGER MAYNARD HES BRINGING A CREW TO REPLACE POLE.. IDCC CNT38, TON230 STEP 1 XXXX
2585 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-09-29 06:50 | 2009-09-29 19:30 | 35 | 760 | 53340-1 | 13160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 65 FUSE OUT ON PRI RISER POLE, , HAVE CHECK ALL TRANSFORMER, DID NOT FIND ANYTHING DID NOT HAVE ANY PARKING STANDS IN THE SWITCHING CABINET OR IN THE TRANSFORMER, WAITING TILL SOMEONE BRINGS US SOME PARKING STANDS HAVE CHECK TO TRANSFORMER, 1123-1105, WELL BE HOT TO THIS TRANSFORMER RELEASED BY CREW 078S0665 IDCC CDC83 XXXX
2586 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2018-09-20 10:55 | 2018-09-20 13:04 | 102 | 129 | 4134091 | 13158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 2100102// lh (b?) phase low at 612c1-117 broke xarm//opening lf at 612c1-112 10:55 to make safe//End of crossarm rotted off and lefthand phase is about 4ft. off the ground,Will need 8ft. crossarm and braces. Released by crew 081S03..Making repairs BAcord
2587 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-12-29 02:18 | 2012-12-29 11:50 | 23 | 572 | 4547461 | 13156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PATROLING LINE/CREW REQUIRED #4 COPPER PRIMARY ONLY/TRUCK TO ONE POLE BESIDE ROAD /3 MAN CREW /180-51 RELEASED BY CREW 078S03// FETR 12:30 JEH/ REPAIRED NEUT.@181-66/ PRI. @180-52/ POWER REST. @ 11:50 // JEH// COD 23// VER/DBM IDC XXXX
2588 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2010-05-31 02:55 | 2010-05-31 09:46 | 32 | 411 | 53953-1 | 13152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 1122-97, HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC IDC XXXX
2589 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-02-08 13:06 | 2010-02-08 16:12 | 145 | 186 | H52894-1 | 13152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33777642 // HIGH SIDE FUSE BLOWN// "B PHASE ONLY" STEPDOWN TR BAD. CREW WILL REPLACE TR AND TRANSFER LOAD OFF B PHASE TO BALANCE.HIGH SIDE FUSE BLOWN// // OPENED UP OTHER 2 PHASES AT 1306 , CC 138 , CLOSED AT 1450 COLD LOAD P.U TOOK OUT RECL OPENED NO. SW AT POLE 265-406 . CLOSED ALL RECL AT 1510 228CC 162 CC OUT UNTIL N.O. IS CLOSED. ALL CUST REST AT 1612.STS WR # 3377764 VER/PDP IDC XXXX
2590 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-09-29 21:12 | 2015-09-29 21:54 | 313 | 42 | 4292071 | 13146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 38820966A30695 LETTINGSOUCE SIDE RISER CONTACT CROSSARM REPLACED CUTOUT RESTORED POWER AT21:54 MAKE ADDITIONAL OUTAGE FROM ORIGINAL CUSTOMER OUT FROM 2059 TILL 2154 L3/DKG VERIFIED WITH ALARM HISTORY AND SWITCHING ORDER VER/SEF L3/DKG VERIFIED WITH ALARM HISTORY AND SWITCHING ORDER
2591 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-05-19 12:00 | 2008-05-19 15:32 | 62 | 212 | 65886-1 | 13144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE...BAD TFRMER CUTOUT...POLE 1037A42...RECLOSER LOCKED OUT ON POLE 1037A130.....WILL CALL FOR CREW...CAN SAVE POLE AND USE A POLE TOP EXTENSION PIN FOR PRIMARY CLEARANCE....,JRVENTURINO...05/19/08 ...//...CREW MADE REPAIRS...RENERGIZED LINE....J R VENTURINO...05/19/08 // VER/TOM IDC XXXX
2592 | Hazard | 3420001 | SOFT SHELL | VEST | 2014-05-28 06:30 | 2014-05-28 09:35 | 71 | 185 | 4941681 | 13135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO AT 107-77 COD-71/ OPENED RECL 108-116 AT 0911 TO REPAIR COD-19/ VER/KEP IDC XXXX
2593 | Paintsville | 3401101 | FALCON | FALC-OILS | 2010-08-18 23:15 | 2010-08-19 12:55 | 29 | 820 | 57944-1 | 13115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING. LOOKING AT ONE MORE SPOT WHERE HOUSES ARE AND WILL TRY REC. CREW ENROUTE TO ASSIST. CREW ONSITE - WORKING TO DETERMINE CAUSE. REMOVED HOT-LINE-CLAMP ON 829-126 TO ISOLATE FAULT AND CLOSED REC @ 6:20 RESTORING UP TO AND INCLUDING TAP ON 829-126. POLE TOP BURNT OFF. CREW ENROUTE TO REPAIR. //COD 29// VER/DBM IDC XXXX
2594 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-03-06 14:26 | 2017-03-06 20:50 | 62 | 384 | 4526481 | 13114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED RECLOSERS ON 37830355B00182 TO SAFELY ISOLATE WIRE DOWN. BROKEN POLE AT 37830331B00143. NO OUTAGE PRIOR TO OPENING.BROKEN POLE IT PROBLEY WILL BE MANUAL , CREW REQUIRED . BROKE POLE 331-143 - ISOLATED AT 331-145 / 37830355B00182 ON @ 1708 (47 CUST) 37830331B00145 ON @ 2030 (13 CUST)/ 37830331B00143 ON @ 2050 (2 CUST)/ VER/BOW AJB
2595 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-03-08 02:43 | 2008-03-08 12:13 | 23 | 570 | 54815-1 | 13110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308001// COD-23 // RELEASED BY CREW 077S05// DUE TO ICING CONDITIONS WILL HAVE TO WAIT UNTIL 0900 TO PATROL LINE WITH A 4 WHEELER, UNABLE TO GET TRUCK ACROSS HILL //COD 23//SERVICERS PATROLLING LINES// POLE BURNT CAN FIX TEMPORARILY COUTOUT BAD ON OLD LINE NOT IN USE RECLOSURE WOULD NOT CLOSE IN USED BYPASS FUSE TO RESTORE POWER ON AT 1213 P HICKMAN//ENTERED ABNORMAL DATABASE ENTRY DBM// VER/DBM IDC XXXX
2596 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-03-10 16:28 | 2017-03-10 18:24 | 113 | 116 | 4546881 | 13108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | B PHASE LOAD SIDE LEAD OFF STIRRUP.LOAD SIDE PRIMARY RISER ON B PHASE RECLOSER ON 287-286 FELL OFF OF STIRRUP I REPLACED HOT TAP AND RESTORED POWER AT 18:24/ ISO 37830287000286/ COD 113/ VER.BOW AJB
2597 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-08-15 04:10 | 2011-08-15 08:43 | 48 | 273 | 4711631 | 13104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL DIPATCH AT REG WORK TIME.//// STIRRUP BURNT INTO LETTING CLAMP FALL OPENING LINE.//// REPLACE HOT LINE CLAMP AND STIRRUP, POWER RESTORED. COD-48 ISO SEC 37830227B00057 VER/HFP L3/HFP IDC XXXX
2598 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-09 13:45 | 2010-12-09 16:35 | 77 | 170 | H64774-1 | 13090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 500 KVA STEPDOWN TRANSFORMER. A PHASE// COD 118 // === OPENED B PHASE AT 13:45 //COD 118 + 77 //== POWER RESTORED UP TO POLE 246-439 AT 16:35.//VER/CRB IDCC DCMT, CDC92 XXXX
2599 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-02-07 08:08 | 2018-02-07 10:15 | 103 | 127 | 4810951 | 13081 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE OCR OPEN ON POLE 38830117A00159//COD 103//0850 TRIED RECLOSER AND IT CAME BACK OUT//PATROLLING//BAD CUTOUT ON POLE 38830117A00110//bad cut out on pole 117-110
2600 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-08-17 18:14 | 2018-08-17 21:05 | 79 | 171 | 4966061 | 13056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 6a cu boke in clear @ 43-45. primary hot to there. main line and tap are off, can open solid blade @ 43-40 to make repairs. trks to pole Released by crew 078S07 /// VERIFIED TIMES PER VOICE RECORDER L3/HFP
2601 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-06-03 21:00 | 2014-06-03 23:45 | 79 | 165 | 4968131 | 13035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD DEADEND ON 195-83 ISOLATED ON 195-33/PATROLING REST OF LINE/RECLOSER BACK IN AT 1145 HRS ONE CUSTOMER STILL OFF A BARN CUSTOMER OK TO FIX TOMORROW // NO TAGS PLACED--TIME ON 10:55 RELEASED BY CREW 078H01 VER/CRB AJB PH A.
2602 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-05-11 13:01 | 2011-05-11 14:42 | 129 | 101 | 4060131 | 13029 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | "C" PHASE COD-129C PHASE OPEN ON POLE # 231 / 292 , LOOKS TO BE RIGHT OF WAY PROBLEMS .C PHASE OPEN ON POLE # 231 / 292 , LOOKS TO BE RIGHT OF WAY PROBLEMS . REGULATOR BAD ON P#231 / 290 , OPENED REGULATOR AND TAGGED . RESTORED POWER AT 1442 JKC COD-129 ISO RECL 37830231B40291 VER/HFP L3/HFP
2603 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-06-05 10:19 | 2020-06-06 11:30 | 32 | 1511 | 4962231 | 13024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser open @37830024B30548, checking. Crews on site making repairs. Bad cable between 24-B3-548 and trans. 24-B3-1158, had to open L/F @24-B3-754 to make repairs, opend up @2230, made repairs and closed back in @2309. Cable still testing bad between trans. 24-B3-1158 and 1162, crew coming in the a.m. to make rest of repairs. Released by crew 074S05.ON AT 11:30
2604 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-02-28 11:11 | 2011-02-28 21:40 | 58 | 629 | 64433-1 | 13022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SEE ORDER 63939POLE 68-934 AEP POLE BROKE 30 CLASS 6 SEC. POLE NO TRUCK MAYBE YARD DOG OPENED TRANS. ON POLE 68-905 UNDERGROUND ON POLE ONE CUST TRYED TO CALL NO ANSWERPOLE 68-934 AEP POLE BROKE 30 CLASS 6 SEC. POLE NO TRUCK MAYBE YARD DOG OPENED TRANS. ON POLE 68-905 UNDERGROUND ON POLE ONE CUST TRYED TO CALL NO ANSWER RELEASED BY CREW 078S08---- POWER ON @ 21:40//VER/CRB IDCC FEC60 TON2020 STEP1 XXXX
2605 | Hazard | 3309002 | JEFF | JEFF | 2015-07-28 07:27 | 2015-07-28 10:42 | 124 | 195 | 4950491 | 12994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 37830321D00215 / OPENED SWITCHES AND TAGGED TO G.SHOUSE AT POLE 37830321D00416// VER/ ADH // VER TIMES PER SCADA & DISPATCH LOG L3/HFP HFPC TOF739
2606 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-03-13 11:46 | 2010-03-13 13:43 | 111 | 117 | 66394-1 | 12987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34241217BAD CUT-OUT REPLACED TICKET COMP//VER/CRB IDC THIS APPEARS TO BE PH C ONLY CHANGED COUNT FROM 161 XXX
2607 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-10-14 09:50 | 2010-10-14 13:16 | 63 | 206 | 59562-1 | 12978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37323750 //POLE TOP BURNT OFF ON POLE 212-172 45/4, OPENED STEPDOWN ON POLE 212-171 AT 09:50. NEED LINE CREW TO REPLACE POLE, TRUCKS TO POLE OK. D WHEELER IN ROUTE. LMRPOLE TOP BURNT OFF ON POLE 212-172 45/4, OPENED STEPDOWN ON POLE 212-171 AT 09:50. NEED LINE CREW TO REPLACE POLE, TRUCKS TO POLE OK. RELEASED BY CREW 078S01 COD-63 VER/HFP L3/HFP IDCC PN99 XXXX
2608 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-06-27 01:58 | 2009-06-27 13:59 | 18 | 721 | 64194-1 | 12978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/ARN
2609 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-05-22 10:43 | 2020-05-22 11:38 | 558 | 55 | 4886301 | 12962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout//WILL HAVE TO OPEN RECLOSER 37830254C00025//COD 559//OPENED @ 1115 //COD 4 FROM BEGIININGbad cutout Released by crew 077S02
2610 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-03-27 01:02 | 2009-03-27 01:50 | 270 | 48 | 61980-1 | 12960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RUSSELL/KENWOOD SW ORDER TO ALLOW CREWS TO REPAIR PTP ON POLE 1148-A-244 ON HOUR OUTAGE OUTAGE FROM 0102 TO 0150 OF 270 CUSTOMERS SW OPEN AT POLE 1148-A-187 TO POLE 1148-A-208 VER/PDP IDCC CDC90 XXXX
2611 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-09-28 21:20 | 2009-09-28 23:20 | 108 | 120 | 52747-1 | 12960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 108 COD // 1 PHASE OUT //RIGHT HAND REC OUT...PATROLLED LINE FOUND NOTHING...BBRIGHT HAND REC OUT...PATROLLED LINE FOUND NOTHING... BY PASSED RECLOSER ON POLE 900-104...BB //CREATED AED AND LOG ENTRY IDCC CNT392 XXXX
2612 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-04-17 17:01 | 2021-04-17 17:20 | 682 | 19 | 4458571 | 12958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO OUTAGE TILL GOAB OPENED ON POLE 37830179D00185//COD 682//INSULATER FAILURE ON POLE 37830179B00030//CREW IS ENROUTE TO DO WORK//OFF @ 17:01 ON @ 17:20
2613 | Hazard | 3309901 | SLEMP | DEFEATED CREEK | 2017-12-24 16:39 | 2017-12-25 12:25 | 33 | 1186 | 4672541 | 12948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Hold OrderReq/remote location/transferring load to alternate source/some customers to remain out till 12/25 line crosses mtn crew to check at daylight /DOL 792761/
2614 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2022-01-16 23:33 | 2022-01-17 08:06 | 45 | 513 | 4356331 | 12945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LF open @ 118-2, 4A Neutral down from 117-71 to 117-91, 4A primary down from 117-91 to 117-92. Crew required, trucks okay Released by crew 078S02 crew on site FETR 08:00 LRM///At 0800 when tried to restore LF 118-2 the LF at 94-B-42 blew (20 addtl COD)--all restored at 0806
2615 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-12-21 04:23 | 2012-12-21 10:03 | 38 | 340 | 4496851 | 12920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER TO BE DISPATCHED AT DAYLIGHT/HOT TAP LEAD BROKEN ON LINE FUSE AT POLE#69-4129/SERVICER TO MAKE REPAIRS/FETR1030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1003/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB
2616 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-04-07 13:15 | 2018-04-07 16:45 | 90 | 210 | 4199281 | 12911 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F ON POLE 38830250000116 IS OPEN//COD 120//no crew required 50t looks like load//CLOSED L/F IN @ 1452 THIS OPENED OCR 38830250000117//grounds at 250-161 isolated also tagged to virgin/back on 1645 Released by crew 078S03//FAILED CUTOUT ON POLE 38830274000022
2617 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-12-18 22:12 | 2008-12-19 05:35 | 35 | 443 | 60041-1 | 12905 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3007904//,,,,,WIRE BURNT OUT OF A COPPER COMPRESSION ON A SQUIRP,, BETWEEN POLES 669-9 TO POLE 669-11 JUST ONE SPAN MAY BE ABLE TO GET 4 WHEEL DRIVE TRUCK TO IT WIRE IS COPPER, I HAVE ISOLATED ON POLE 669-8 RELEASED BY CREW 078S02 // CLOSED RECLOSER @ 1210 LFOUND BAD DEAD END BELL/POLE#669-10/NEW FETR0615//NEW FETR0615/VEM/RECLOSER BACK IN AT 0535/ALL CUST RESTORED/PLEASE CLOSE TICKET/TANKS/VEM RELEASED BY CREW 078H14 VER/LDA L3/KEP IDC XXXX
2618 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-11-30 02:50 | 2016-11-30 04:00 | 184 | 70 | 4147101 | 12880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DKM/SOURCE TRANSFORMER AT POLE 320-A-48 THAT FEEDS RECLOSER ON POLE 320-A-49 IS DEFECTIVE. CONTROL SW ON RECL IS TAGGED AND THE BYPASS SWS ARE CLOSED RESTORING ALL CUSTOMERS. THE BLOWN FUSE ON TRANSFORMER HAS BEEN LEFT AND THE POLE HAS BEEN TAGGED DUE TO THE FACT THAT THEY COULD NOT TAG THE FUSE HANDLE VER/HFP L3/HFP AJB
2619 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-05-05 15:11 | 2013-05-05 15:34 | 560 | 23 | 4073751 | 12880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW OPENED RECLOSER IN ORDER TO MAKE REPAIRS RELATED TO ORDER 4072951//COD 560//B PHASE CONDUCTOR BURNT DOWN ON POLE 38830527009005// OPENED ON 478-90 AT 1511 CLOSED AT 1534 APR // VER/DBM IDC XXXX
2620 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2008-07-15 16:54 | 2008-07-15 20:36 | 58 | 222 | 53035-1 | 12876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3417601//OPENED DISCONNECTS IN ORDER TO REPAIR BURNT UP LOOPS ON THE MIDDLE PHASE ON POLE 966-618//SEE ORDER 53031-1//ISO 966-607//MAP DISCREPANCY REPORT SENT EARLIER TODAY FOR SAME MISSING DISCONNECTS//COD 40// VER/DBM IDC XXXX
2621 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-01-12 20:46 | 2015-01-13 04:10 | 29 | 444 | 4931531 | 12876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CREW REQUIRED POLE 293-70 TRUCKS OK PRIMARY ONLY /#2 ALUM. SMALL PIECE MAY B NEEDED/TAGGED TO DDC NO GROUNDS RELEASED BY CREW 078S03,,CREW ON SITE..ALL REPAIRS MADE,,ALL POWER RESTORED//COD 29// VER/DBM // PER VOICE RECORDER WIRE PULLED OUT OF SLEEVE // L3/HFP HFPC FEC46 AJB
2622 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-12-29 11:05 | 2013-12-29 13:40 | 83 | 155 | 4209451 | 12865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ERIC MCKINNEY COMING TO HELP REPAIR POLE - GOING TO LOWER EVERYTHING DOWN.TOP OF POLE BURNT OFF POLE#103-58. NEED 1 MAN BIG BUCKET CAN LOWER OPENED RECLOSER ON POLE 103-27 @ 11:05TOP OF POLE BURNT OFF POLE#103-58. NEED 1 MAN BIG BUCKET CAN LOWER OPENED RECLOSER ON POLE 103-27 @ 11:05 . REPAIRS MADE ON POLE#103-58 CLOSED RECLOSER BACK IN ON POLE #103-27 @ 13:40 COD-83 ISO OCR 37820103B00027 VER/HFP L3/HFP IDC XXXX
2623 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-08-04 03:20 | 2011-08-04 08:58 | 38 | 338 | 4662071 | 12844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS OUT ON POLE 97-28. I AM PATROLLING LINE NOW. TRANSFORMER CUTOUT ON POLE 97-37 BROKE DOWN AND CAUGHT POLE ON FIRE. TOP OF POLE HAS BURNED OFF. DAVE IS SENDING HELP TO PUT POLE FIRE OUT. WE PUT EXTENSION ON POLE AND REPULLED WIRES. WE CLOSED LINE FUSE IN AT 08:58 COD-38 ISO LF 37820097000028 VER/HFP L3/HFP STC PER PHONE CONF
2624 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2018-05-20 02:14 | 2018-05-20 16:51 | 43 | 877 | 4380831 | 12835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830403000146 40' Cl 5 pole top burnt off at c/o 4247 jerry riffe rd--crew req--cut breaker in at 38830403000144 toward 145 over rd rec 83-379/48 in at 05:20---36 of 43 cust restored-ds05191838830403000146 pole top burnt off at c/o 4247 jerry riffe rd--crew req--cut breaker in at 38830403000144 toward 145 over rd rec 83-379/48 in at 05:20---36 of 43 cust restored //38830403000146 40 Cl 5 pole top burnt off at c/o 4247 jerry riffe rd--
2625 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-09-10 08:15 | 2018-09-10 13:05 | 199 | 290 | 4073411 | 12825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE///////NEED BIG BUCKET,HAZARDOUS SITUATION TO REPLACE.HOTTAP ON OVER TOP OF CONDUCTOR,REMAINDER OF CUTOUT VERY CLOSE TO A GRNDED BRACKET//opened ocr 37820008D00093 to safely replace cutout//OPENED 1210 CLOSED 1305//COD 8 FROM BEGINNING
2626 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2019-10-22 06:28 | 2019-10-22 08:30 | 105 | 122 | 4179941 | 12810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 357-241 I isolated it Released by crew 077S12changed cutout and restored power at 1130//NO CUSTOMERS ON POLE 37830357D00241//CUSTS RESTORED 0830 L3/HFP
2627 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-06-23 19:37 | 2011-06-23 22:40 | 70 | 183 | 4403741 | 12810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 116-436 BAD 12KV D.E. INSULATOR.. RESTORED 22:40 VER/ARN IDC XXXX
2628 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-07-01 12:58 | 2019-07-01 13:31 | 387 | 33 | 4627201 | 12771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crew opened switch to safely repair broken crossarm at pole 37820076000132 REC OFF 1258 ON 1300 ¦¦ SWS CLOSED @ 1331crew opened switch to safely repair broken crossarm at pole 37820076000132////OPENED RECLR 52-211@12:58,OPENED 52-226,CLOSED@13:00/////////REPAIRS COMPLETED////////CLOSED 52-226@13:31 Released by crew 074S06
2629 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-05-25 14:29 | 2012-05-25 16:05 | 133 | 96 | 4831041 | 12768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY RISER BURNT OPEN AT HOT-LINE-CLAMP CONNECTION. CREW ONSITE. REPAIRED AND CLOSED RECLOSER 784-200 @ 16:05. SH//OPEN POINT WAS NEXT TO RECLOSER NO CHANGE IN CUST COUNT ///VER/CRB L/3 CRB IDC XXXX
2630 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-10-26 20:50 | 2013-10-26 23:15 | 88 | 145 | 4966181 | 12760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 139-52 ROTTED AT GROUND LINE AND LAYED OVER NEED 45-5 POLE 8 FOOT ARM BRACES 2 STEEL PINS 2 INSULATORS RELEASED BY CREW 074S11 // OPENED C PHASE RECL AT 2050 CLOSED AT 2315 VER/HFP L3/HFP IDC XXXX
2631 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-04-20 13:04 | 2015-04-20 18:23 | 40 | 319 | 4341461 | 12760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE OUT 619-126 PATROL,PRI &NEU #4 SOLID COPPER DOWN 642-11 TO12&13LINE CREW NO TR,POWER RESTORED 18;23/ ISO 38830619000126/ COD 40 VER/HFP L3/HFP AJB
2632 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-02-28 09:37 | 2011-02-28 16:57 | 29 | 440 | 64136-1 | 12760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | STS WR # 38966933 // WIRE LOOSE FROM HOT TAP NEED LINE CREW & BIG BUCKET TREE CREW ALSO TREE FELL ON SERVICE DROP ON POLE 1137D450 MAY ALSO NEED FLAGGERSWIRE LOOSE FROM HOT TAP NEED LINE CREW & BIG BUCKET TREE CREW ALSO TREE FELL ON SERVICE DROP ON POLE 1137D450 MAY ALSO NEED FLAGGERS RELEASED BY CREW 079H03 // 1648 OPENED RECL CLOSED @ 1657 IDC DCMT IDC XXXX
2633 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-03-16 09:31 | 2011-03-16 14:50 | 40 | 319 | 54738-1 | 12760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE CREW REQUIRED 40/5 BURNT OFF NEED 45/4/LINE FUSE ON 292-77 ABOUT 12 TO 20 CUSTOMERS OFF/TRUCKS OK/THIS IS A DEAD END POLE WITH 2 1/0 SECONDARYS OFF IT AND TRANSFORMER COD-21 CUST FROM 54765-1 MD FILEDPOLE FIRE CREW REQUIRED 40/5 BURNT OFF NEED 45/4/LINE FUSE ON 292-77 ABOUT 12 TO 20 CUSTOMERS OFF/TRUCKS OK/THIS IS A DEAD END POLE WITH 2 1/0 SECONDARYS OFF IT AND TRANSFORMER RELEASED BY CREW 078S03 VER/KEP IDC CHANGED COUNT FROM 21 XXXX
2634 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-08-11 13:44 | 2019-08-11 16:52 | 127 | 176 | 4871751 | 12754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 945545//175-107 bad pin insulator #2 alum down need roll trucks ok 175-126 off at 1435 hrs tagged to ramey ground at that location//cod 127 ¦¦¦¦ VERIFIED TIMES PER DOL - L3/HFP
2635 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2019-10-18 15:23 | 2019-10-19 17:55 | 10 | 1592 | 4166761 | 12749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DOL 963691///KYDDC Tags///Line fuse open @38831151D00469, checking. Tree fell on overhead line going from pole 1151-D-666 to 667, can isolate this section and create an order to remove this. removed inactive section of line and closed L/F back in @0018. Released by crew 074S05 opened 1151d469 17:52 closed at 17:55 all customers restored bad cable between PAD1151D 419 & 421 Released by crew 074S10
2636 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-12-26 08:59 | 2012-12-26 17:00 | 63 | 481 | 4520311 | 12747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RAYBURN GETTING CREW AN HAS MATERIAL LIST///CUT LOOP AND INSTALLED TAG AN GROUND AT POLE 38830069C45528/// CLOSED LINE FUSE IN ON POLE 38830069C35092 AT10:02 RELEASED BY CREW 078S07 ///VER/CRB L/3 CRB IDC XXXX
2637 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-07-19 09:35 | 2014-07-19 15:45 | 51 | 370 | 4262501 | 12745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 115-21 BURNT OFF AT TOP NEED BIG BUCKET AND WOODEN POLE TOP EXTENSION.. AND PRIMARY DOWN FROM POLE 115-14 TO 115-13.. ALL TRUCK ACCESSABLE EXCEPT POSSIBLE THE BURNT POLE.. #4 COPPER RELEASED BY CREW 078H22,,CREW ON SITE, WIRE AT 115-14 REPAIRED AND REC CLOSED AT 13:40//COD 51// VER/DBM AJB
2638 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-04-04 17:18 | 2014-04-04 22:55 | 184 | 337 | H4574831 | 12728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHECKED LINE BACK UP TO REC. ON POLE 204-264, WE HAVE ONE REC. LOCKED OUT BELIEVE ITS B PHASE//COD 276// PRIMARY IS OFF INSULATOR, UP IN TREES WILL OPEN GOAB ON POLE 178-297 WILL GO BACK TO REC POLE179-194 ONE REC IS OPEN AND WILL CLOSE CLOSE IT THEN GO TO REC. POLE 204-264 AND ENERGIZE DOWN TO GOAB OPEN POINT. OPENED GOAB AT 17:48.///CLOSED REC ON POLE 37830204000264 // THIS IS FOR THE C PHASE OUTAGE ON REC 179-194 VER/HFP L3/HFP
2639 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-12-24 09:53 | 2008-12-24 10:30 | 344 | 37 | 63327-1 | 12728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP STS WR # 27800250 // C PHASE OUT 366 (TOTAL) CUSTOMERS L3/HFP IDC LOOKS LIKE SEVERAL MISMAPPED CUSTOMERS XXXX
2640 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-02-17 17:31 | 2019-02-17 20:30 | 71 | 179 | 4801831 | 12709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dead-end insulator failed on 875-372. Making repairs. Replaced insulator and transformer cutout. Restored @ 20:30. sh
2641 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-12-07 08:59 | 2015-12-07 13:29 | 47 | 270 | 4514991 | 12690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT OPEN ON POLE 311-01..THIS IS WHERE THE BURDINE,LIVSA CIRCUIT DEAD-ENDS.WILL HAVE TO OPEN UP LINE FUSE ON POLE 287-170 WHICH IS ON THE ELWOOD,DORTON CIRCUIT.AND REC. POLE 311-151 THAT FEEDS TO POLE 311-01 TO MAKE REPAIRS. // SEE 4515821 & 4515861 ALL ON @ 1329 VER/HFP L3/HFP AJB
2642 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-09-03 19:15 | 2018-09-04 14:26 | 11 | 1151 | 4039451 | 12661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | sos 1060 rev 34 37830048C10800 normal @ 1446 // Bad 100 kva 7200 trans. on pole 25-A-341, gonna hold this till the a.m. transformer is 1200 lbs., will require a line crew with big bucket and line truck, it is truck accessible. Please send a copy of this to Dennis Massey and P.R. to get assigned in the morning. Released by crew 074S05
2643 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-05-02 04:14 | 2017-05-02 07:20 | 68 | 186 | 4726251 | 12648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE FUSE//COD 68//POLE 45-3638 BAD HOT TAP REPAIRED VER/CRB AJB
2644 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-07-23 16:52 | 2011-07-23 18:25 | 136 | 93 | 4601581 | 12648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE ON POLE 37830296B31287 IS OPEN, PATROLING LINE. FOUND BROKEN CUTOUT ON POLE 296-1255 VER/KEP
2645 | Hazard | 3309003 | JEFF | VIPER | 2016-08-17 19:34 | 2016-08-18 00:15 | 45 | 281 | 4806831 | 12645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BAD AT SOURCE SIDE OF SOLID BLADE RELEASED BY CREW 077S01 REPLACED INSULATOR ON POLE 392-84..RESAGGED CONDUCTOR..077H18 VER/CRB L3/HFP XXXHFP AJB
2646 | Cannonsburg | 3001401 | LOUISA | CITY | 2021-08-19 11:06 | 2021-08-19 13:15 | 98 | 129 | 4118381 | 12642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A phase fuse open on pole 454-A4-1677 (59 COD) A phase fuse blown on 454-1677, On pole 454-1604 a&c cutouts bad. crew in route.C phase fuse blown on 454-1677, On pole 454-1604 a&c cutouts bad. crew in route. C phase fuse in at 1315 close ticket.t. All power restored exept bank pole 454-1604, Bad txm on A phase.C phase fuse blown on 454-1677, On pole 454-1604 a&c cutouts bad. cre
2647 | South Williamson | 3411401 | DEWEY | INEZ | 2011-02-02 13:00 | 2011-02-02 13:27 | 468 | 27 | H53296-1 | 12636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DUPLICATE ORDER * ASSOCIATED WITH ORDER 53296-1 SINGLE PHASE OUT 235 CC.RECLOSER ON POLE 311 SHOWING VOLTAGE ON B AND C PHASE,, HAVE CUSTOMERS WITH PART POWER BEFORE THIS RECLOSER, PATROLING NOW//RECLOSER ON POLE 311 SHOWING VOLTAGE ON B AND C PHASE,, HAVE CUSTOMERS WITH PART POWER BEFORE THIS RECLOSER, PATROLING NOW//FOUND LOOP BURNT OPEN ON POLE 744-38// @ 1257 OPENED SWS AT 744-34 ALL PHS NOW OPEN. SEE DOL ENTRY 02/02/11 VER/PDP IDCC CNT925 CDC90 XXXX
2648 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-05-04 12:31 | 2015-05-04 14:03 | 743 | 92 | 4388351 | 12628 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | ARRESTOR FAILED ON THE 69-34KV TR AT PRINCESS // STATION DEPT ON SITE REPLACING ARRESTOR - TIMES PER LOG & SCADA VER/HFP L3/HFP AJB
2649 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-10-04 08:22 | 2018-10-04 13:41 | 81 | 319 | 4195451 | 12621 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B phase reclosure is out . will be patrolling line//COD 40 FROM THE BEGINNING OF OUTAGE//B phase reclosure is out . will be patrolling line.epoxalator broke on pole 37830020000013 eill need line crew insulator & 3 men//1136 COD DOWN TO 33 COD //WILL HAVE TO OPEN OTHER 2 SWITCHES/ OPENED OTHER 2 1320// Released by crew 074S04//CLOSED 3 SW @ 1341 // 40 cust initally out - note: 8 cust rest @ 1136 when B Phase recl closed //
2650 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-01-25 23:03 | 2021-01-26 07:27 | 25 | 504 | 4892451 | 12600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse on 1125-A-253 is blown// patroling// no hazards found will try line fuse// fuse kicked back out// will be looking// cut a bad arrestor in the clear at pole 1125-A-753 and found a melted dead end insulator at pole 1125-A-351, will be grounding line to change dead end insulator// restored at 0727
2651 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-11-30 04:08 | 2018-11-30 09:58 | 36 | 350 | 4492411 | 12600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found cutout broken on pole 145-35.will make repairs. L3/HFP
2652 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-12-24 02:14 | 2016-12-24 05:55 | 57 | 221 | 4231761 | 12597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED ON 881-24 AND BLEW LINE FUSE. REPLACED CUTOUT AND CLOSED LINE FUSE @ 5:55. SH VER/TOM L3/TOM AJB
2653 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-07-11 01:48 | 2020-07-11 08:14 | 62 | 386 | 4149741 | 12590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rec open @ 91-589, fault pole 115-490, big bucket can cut loop @ 115-490 Released by crew 078S07 crew on site only 9 cust out FETR 8:30 all pwr restored @ 8:14 please close ticket LRM//cod 62
2654 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2015-12-01 06:03 | 2015-12-01 10:41 | 63 | 278 | 4497581 | 12586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ 0705 PATROLLING LINE // B PHASE RECL LOCKED OUT (63 CUST)XFMR CUTOUT FAILED ON 738-294.XFMR CUTOUT FAILED ON 738-294. ISOLATED LINE FUSE ON 738-294 AND TAGGED TO S. HALL.XFMR CUTOUT FAILED ON 738-294. ISOLATED LINE FUSE ON 738-294 AND TAGGED TO S. HALL. CORRECT ISOLATING POLE IS 738-72..CLOSED REC @ 9:13 RESTORING ALL BUT LATTERAL ON 738-72 ALL REST @ 1041 COD-63 ISO OCR 38830738A00276 VER/HFP L3/HFP AJB
2655 | South Williamson | 3411401 | DEWEY | INEZ | 2012-02-29 16:36 | 2012-02-29 17:38 | 203 | 62 | 4521211 | 12586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND CUTOUT BAD ON POLE 766-26//CREW CHANGING CUTOUT NOW//REPAIRS MADE//CLOSED RECLOSER AT 17:38//COMPLETE/EM // COD 203 // VER/DBM AJB
2656 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-04-08 09:54 | 2009-04-08 15:25 | 38 | 331 | 50429-1 | 12578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308601// STEP DOWN ON POLE 353-328 IS BAD RELEASED BY CREW 074S073308601// STEP DOWN ON POLE 353-328 IS BAD //PUT POWER ON AT 1525//COD 38// VER/DBM IDCC CDC92 XXXX
2657 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2022-01-10 13:36 | 2022-01-10 17:02 | 61 | 206 | 4333131 | 12566 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | opened isolated grounded & tagged recloser to Bobby Tackett 38830214000052 @ 1406, pole 38830189000003 rotted off at the ground and fell over. land owner said you can back a truck in to set the pole if you want. no tags or grounds placed by servicer Released by crew 078S12,repairs made all cust restored @ 1702 please close ticket thanks.bt Lr- The 1st all out call came in at 13:36
2658 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-11-16 06:51 | 2011-11-16 11:50 | 42 | 299 | 4080621 | 12558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 6 DISC INSULATOR // CENTER PHASE - B PHASE OUT 42 CUSTOMERS VER/KEP IDC XXXX
2659 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2012-05-29 00:35 | 2012-05-29 09:41 | 23 | 546 | 4838601 | 12558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LINE FUSE DID NOT BLOW, HAD TO OPEN LINE. WIRE DOWN, JUST ABOVE FUSE ON POLE # 1088-A- 38. RELEASED BY CREW 079H06 MD FILED VER/KEP IDC XXXX
2660 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-11-03 02:20 | 2010-11-03 07:12 | 43 | 292 | 51164-1 | 12556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37603959 // SERVICER PATROLLING LINE// ... HOT LINE CLAMP AND STIRRUP BURNED APAERT AT RECLOSERSERVICER PATROLLING LINE// ... HOT LINE CLAMP AND STIRRUP BURNED APAERT AT RECLOSER ... REPLACED STIERRUP AND HOT LINE CLAMP, ALL WORK COMPLETE / GXJ VER/HFP L3/HFP IDC DCMT XXXX
2661 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2017-06-22 15:33 | 2017-06-22 16:16 | 292 | 43 | 4015391 | 12556 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | REGULATOR FAILED AT STATION. VER/ARN SJG
2662 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2009-08-04 17:55 | 2009-08-04 20:10 | 93 | 135 | 58904-1 | 12555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP C PHASE REC ONLY OPEN, PATROLED LINE AND FOUND NO HAZARDS, TRIED RECLOSURE AND IT DID NOT HOLDC PHASE REC ONLY OPEN, CLEARED BAD ARRESTER AT POLE 38830230000259 C PHASE 43 CUST ISO 38830254D36070 L3/HFP IDC CHANGED COUNT FROM 43 LOOKS LIKE MISSMAPPED TAPS XXXX
2663 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-07-07 09:01 | 2013-07-07 12:45 | 56 | 224 | 4478901 | 12544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S09 SERVICER FOUND LOOP OPEN NEAR RECLOSER ** OPENED RECL TO MAKE REPAIRS.RELEASED BY CREW 078S09 POLE 44-5521 LOOP BURNT OPEN REPAIRED OPEN REC. 12;25 ON 12;45//COD 56 + 3 // IDC XXXX
2664 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-05-07 18:04 | 2014-05-07 19:39 | 132 | 95 | 4672281 | 12540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP & STIRRUP BURNED OF. ( A PHASE ) ONLY A PHASE OUT FROM POLE 249C-18 . SEND TO DOUG C. POLE NEEDS CHANGED OUT ASAP ROTTEN AT GROUND.//COD 132//EMAILED TO D CHRISTIAN// VER/DBM L3/HFP HFPC CDC86 IDC XXXX
2665 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-06-06 11:51 | 2022-06-06 14:03 | 95 | 132 | 4025741 | 12540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | line out at pole 1086A-417 due to riser on line fuse cutout burned into.i made repairs and got line fuse on pole 1086A-417 back in at 14:03
2666 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-12-25 08:28 | 2012-12-25 10:24 | 108 | 116 | 4515501 | 12528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, CUT POLE TOP OFF AND REPLACED POLE TOP PIN AND INSULATOR. ///VER/CRB L/3 CRB IDC XXXX
2667 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-11-10 01:31 | 2015-11-10 05:23 | 54 | 232 | 4423191 | 12528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 447-83, BAD CUTOUT ON 447-179 BURNT POLE OFF WILL ISOLATE ON 447-22..COULDNT ISOLATE . MADE REPAIRS RESTORED POWER AT 05:23. VER/KEP L3/HFP XXXHFP AJB
2668 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-11-24 19:27 | 2014-11-24 20:39 | 174 | 72 | 4777431 | 12528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | RELATED TO ORDER 4766311//CLOSED N.O. SWS 875-A-252 AND TIED FALCON-BURNING AND FALCON-SALYERSVILLE @ 1845//OPENED N.C. SWS 852-193 @ 1858//NO CUSTOMERS OUTAGED AT THIS TIME//@ 1927 OPENED FALCON-BURNING FORK CB G IN ORDER TO DEENERGIZE LINE FROM THE BREAKER TO OPEN SWS 852-193 SO THAT SWS ON POLE 852-A3-387 CAN BE REMOVED//COD 174//ISO 3401103//BROKEN SWS 852-A3-387 REMOVED AND FEEDER RESTORED AT BREAKER @ 2039//CLOSED 852-193 @ 2045 TYING CKTS AGAIN//OP N.O. 875-A-252 @ 2100, CKTS NORMAL// VER/DBM AJB
2669 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-07-13 21:42 | 2010-07-13 23:40 | 106 | 118 | 66547-1 | 12508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY LOOP OPENED ON POLE 212-31. LINE CREW TO MAKE REPAIRS. VER/KEP L3/KEP IDCC PN180 XXXX
2670 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-08 17:10 | 2011-01-08 20:35 | 61 | 205 | 59915-1 | 12505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 CU PRIMARY BURNED DOWN UNDERNEATH A STIRRUP CREW ENROUTE//VER/CRB IDC XXXX
2671 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-10-19 03:46 | 2018-10-19 09:15 | 38 | 329 | 4268851 | 12502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | load side cutout failed..made repairs..
2672 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-11-07 02:50 | 2018-11-07 06:33 | 126 | 223 | 4375001 | 12484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C phase only cod-52/c phase loop burnt @ 1147-5031/school out/c phase loop burnt @ 1147-5031, road side phase. trk to pole Released by crew 078S07--crew on site--replacing burnt loop--open on 1147C3-5030 to safely make repairs(06:21)---repairs made---closed 1147C3-5030 @ 06:33---pwr restored--tbl tkt comp---RMV Released by crew 078H16 L3/HFP
2673 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-08-17 07:57 | 2016-08-17 10:35 | 79 | 158 | 4799521 | 12482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | JUMPER ARCED AND BURNED IN CLEAR AT SWITCH POLE 187-66.---REPAIRED--ALLGOOD--DS081716 VER/AWD L3/HFP XXXHFP AJB
2674 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-10-06 11:24 | 2010-10-06 12:43 | 158 | 79 | 57368-1 | 12482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE ONLY IS OUT//COD 116// 6A COPPERWELD NEUTRAL CONDUCTOR ALREADY HAD TWO STRANDS BROKEN. I CUT IN THE CLEAR.....DKG/PRIMARY NEUTRAL DOWN AT POLE 151-297/NOT BY TRUCK IDCC CNT254 ASSUMING APPROXIMATELY 40 CUSTOMERS MISSMAPPED XXXX
2675 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-05-03 14:07 | 2014-05-03 17:25 | 63 | 198 | 4659731 | 12474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 078S07 RELEASED BY CREW 078S08//COD 63C PHASE OUT//RELEASED BY CREW 078S07 RELEASED BY CREW 078S08/ PL# 116-D-708 STEP DOWN/ LOAD SIDE FUSE OPEN// PRI LOOP @ 140-489 ON ARM/ CLEARED / S.D. FUSE @116-D-708 CLOSED @17:25 JEH VER/SEF L3/HFP HFPC FP38830140000489 IDCC XXXX
2676 | Hazard | 3303902 | LESLIE | WOOTON | 2015-07-15 01:45 | 2015-07-15 20:38 | 11 | 1133 | 4869101 | 12463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POWER RESTORED, REFUSED TAP ON POLE341-28
2677 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-12-11 21:03 | 2008-12-12 00:09 | 67 | 186 | 57020-1 | 12462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR 27656846 C PHASE CUTOUT BROKEN DOWN,WILL ISOLATE PROVIDED POWER IS OFF ON THIS PHASE L3/HFP IDC CHANGED COUNT FROM 35 XXXX
2678 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-03-28 12:06 | 2010-03-28 15:27 | 117 | 201 | 55195-1 | 12459 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 34423102; B PHASE OUT 181 CUSTRECLOSER OPEN ON 428/234; PATROLLING LINES; TAP LINE FUSE CUTOUT FAILED ON POLE 428/93;CREW REQUIRED; NEED 7200 CUTOUT AND BRACKET; NOT TRUCK ACCESSABLE; ATTEMPTING TO CLEAN UP TAP POLE; RECLOSER BACK IN AT 1350HRS; PARTIAL PWR RESTOREDSTS WR# 34423102; RECLOSER OPEN ON 428/234; PATROLLING LINES; TAP LINE FUSE CUTOUT FAILED ON POLE 428/93;CREW REQUI CCC VER/HFP L3/HFP IDCC FP234, CNT181, PN306 XXXX
2679 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-04-21 19:20 | 2012-04-21 22:13 | 72 | 173 | 4693231 | 12456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLR BURNT OFF674-273 GOINGBTO LIFT HOT TAP ON CUTOUT OPEN @698-41 AT19:20 PLACED A TAG.NEED TO SEND TO TEC NEED POLE REPLACED IDCC TOF1753 XXXX
2680 | South Williamson | 3200302 | BELFRY | TOLER | 2019-03-19 13:55 | 2019-03-19 14:48 | 235 | 53 | 4000361 | 12455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | EMERGENCY OUTAGE TO REPAIR CONDUCTOR THAT IS BROKEN ¦¦ NOTE FIRST OUTAGE ONLY TO PLACE COINS CALL ¦¦ COD-235 SW 38821015A00020 OFF @ 1355 ON@1448 L3/HFP
2681 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-06-15 18:30 | 2022-06-16 01:25 | 30 | 415 | 4130261 | 12450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | step down 250 34/12kva on 38830453000274 has taken its top off. needs changed. by truck. no grounds or tags placed by servicer Released by crew 078S12 Repairs made. Closed at 01:25 Ticket complete.
2682 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-04-27 16:48 | 2009-04-27 18:55 | 98 | 127 | 51160-1 | 12446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 782-148 GREEN POLE CAUGHT ON FIRE FROM FOREST FIRE/OPENED RECLOSER AT 1648 OPENED SWITCH AT 783-118 CLOSED RECLOSER AT 1652/CREW IN ROUTE NOW TO STUB POLE TCM// PLEASE SEND COPY TO RON RYE POLE NEEDS CHANGED , DOZER TO MAKE ROAD, 45-2 POLE, CLOSED SWITCHES AT 18:55 ALL SHOULD BE BACK ON. TCM// VER/KEP L3/KEP IDC CHANGED FROM CAUSE OTHER XXXX
2683 | Pikeville | 3413401 | GARRETT | GARRETT | 2015-04-09 02:32 | 2015-04-09 07:25 | 80 | 293 | 4293401 | 12417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOTH TAPS ISOLATED AT POLE 37830016C00090, POLE 16-64 ON AT 04:54 . POLE 227 BURNED APART, LOWERED CONDUCTORS AND REPLACED CUTOUT AND ARRESTER , POLE 16-90 RESTORED AT 07:25, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03/ ISO 37830016C00064/ COD 80/ VER/BOW L3/DKGXXX AJB
2684 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-12-12 23:17 | 2020-12-13 03:25 | 50 | 248 | 4764051 | 12400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 38830380000193. repairs made power restored at 0325
2685 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-06-22 15:33 | 2017-06-22 16:17 | 1462 | 44 | 4015401 | 12382 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | REGULATOR FAILED AT STATION. OFF @ 1533 ON @ 1617 VER/ARN SJG
2686 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-11-01 04:01 | 2018-11-01 13:20 | 42 | 559 | 4348681 | 12378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | Bad 100 kva 7200 padmount trans.-37830024B31137-, tried the secondery fuse on the padmount and came back out, primary is still energized feeding through to padmount 24-B3-1138, crew required, difficult location and crew will have to open l/f on pole 24-B3-1135 to change out. Released by crew 074S05//COD 17 FROM BEGINNING// opened fuse @ 1125 closed@ 1320
2687 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-01-27 06:15 | 2016-01-27 16:04 | 21 | 589 | 4653261 | 12369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON POLE 37820147A00119 BURNED THE TOP OF THE POLE OFF. #4 CU WIRE STILL INTACT. CREW ENROUTE TO MAKE REPAIRS. RELEASED BY CREW 074S02. AWAITING NEW CREW TYPE./ ISO 37820147A20500/ COD 21/ VER/BOW AJB
2688 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-04-05 16:33 | 2021-04-05 19:02 | 83 | 149 | 4420941 | 12367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | sturrip burned off recloser
2689 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-07-28 16:53 | 2014-07-28 20:19 | 60 | 206 | 4303121 | 12360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S03 BAD CUTOUT === REPLACED CUTOUT === REFUSED LINE POWER OK//COD 60// VER/DBM AJB
2690 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-11-23 06:57 | 2010-11-23 08:08 | 174 | 71 | 58869-1 | 12354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LEFT HAND RECLOSER OPEN , PATROLLING NOW TCM// FOUND BAD CUTOUT ON 857-362 HANGING CLOSE TO GROUND BRACKET , CLEARED UP GOING TO SHOOT//C PHASE 173FOUND LEFT HAND RECLOSER OPEN ON POLE 833-400 , PATROLLING NOW TCM// FOUND BAD CUTOUT ON 857-362 HANGING CLOSE TO GROUND BRACKET , CLEARED UP GOING TO SHOOT .STAYED IN BACK ON AT 8:08 TCM//,//VER/CRB IDC XXXX
2691 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-08-06 12:49 | 2021-08-06 15:03 | 97 | 134 | 4012281 | 12338 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 1036C-259.i opened up recloser on pole 1036C-334 at 14:39.went back to pole 1036C-259 and changed cutout.i put 100T fuse in that cutout.i went back to recloser on pole 1036C-334 and picked all the cust back up at a time of 15:03 Released by crew 079S03
2692 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2013-07-23 19:03 | 2013-07-24 04:25 | 38 | 562 | 4584451 | 12326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY CONDUCTOR IS BAD IN THIS SPAN AND BROKE, 15 AMP FUSE IS BLOWN ON THIS POLE ALSO. TURN RIGHT DOWN DRIVE JUST PAST MAILBOX 1601, POLE IS BEHIND HOUSE. CLOSED STEPDOWN IN ON POLE 796B210 AT 21:15. OPENED AND TAGGED POLE 820A325 FOR KY DDC. RELEASED BY CREW 079S02 //VER/GAH IDC XXXX
2693 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-03-11 09:30 | 2009-03-11 12:51 | 181 | 201 | 57164-1 | 12309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 28880563 //FAULT POLE 44-637, LIFT HOT TAP 44-151, REC. CLOSED @10:35.FAULT POLE 44-637, LIFT HOT TAP 44-151, REC. CLOSED @10:35. POWER RESTORED @12:51 M.PHELPS RELEASED BY CREW 078H12 L3/HFP IDC XXXX
2694 | Hazard | 3310502 | HADDIX | CANOE | 2013-08-13 17:01 | 2013-08-13 21:47 | 43 | 286 | 4662241 | 12298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLEARING POSSIBLE RW SPOTS WILL TRY AT 2030---TRIED-FIRED UP ON HILL--MAYBE INSULATON-REPLACING INSULATOR ON POLE 125-DONT KNOW CUSTOMER COUNT VER/SEF L3/HFP XXXHFP
2695 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-04-25 07:33 | 2010-04-25 14:50 | 39 | 437 | 50605-1 | 12293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34818554 //BAD CUTOUT ON POLE 794-88. GOING TO TRY AND CLEAR CUTOUT.MAIN LINE BACK ON AT 12:45. ONE CUSTOMER STILL OUT.LAST CUSTOMER BACK ON AT 14:50 VER/HFP L3/HFP IDC XXXX
2696 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-11-11 13:35 | 2013-11-11 14:40 | 189 | 65 | 4028241 | 12285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DONNIE JENT FOUND BURNT OFF POLE, GOING TO OPEN RECLOSER TO REPLACE POLE. GOING TO CHECK POLE,LOOKS TO BE FLASH BURNT,WILL SEND UPDATES LATER..1335 TIME OFF 1440 TIME ON .CHANGED 3 POXYS,1 CUTOUT,1 ARRESTER,RESAG ALL PRIMARYS AND 1 NEUTRAL,,, VER/SEF L3/HFP IDC XXXX
2697 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2010-02-03 19:00 | 2010-02-04 12:54 | 12 | 1074 | 62809-1 | 12265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 33727293 // CREW PATROLLED LINE AND TRIED FUSE MULTIPLE TIMES WITH NO LUCK. AS PER TIM HALL , PIIKEVILLE D/S CREW WILL BE DISPATCHED AT DAYLIGHT TO PATROL LINE AND MAKE REPAIRS.//STS WR# 33727293// 6A WIRE UNTWISTED CONTACTED NEUTRAL IN SPAN BETWEEN 51-9 & 51-10 REPAIRS MADE ON AT 12:54 D SAMMONS VER/HFP L3/HFP IDC XXXX
2698 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-08-08 14:07 | 2017-08-08 14:48 | 299 | 41 | 4240441 | 12259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW OPENING SWITCH TO CHANGE BAD CROSSARM ON POLE 37830335C00097. ROTTEN CROSSARM, DE-ENERGIZED LINE AT 14:07 SHOULD BE LESS THAN 30 MIN./ ISO 37830335C00289/ COD 299/ RESTORED 1448/ VER/BOW SJG
2699 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-12-24 05:23 | 2019-12-24 23:00 | 29 | 1057 | 4179261 | 12258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | Riser fuse open @71-162, checking. Tried riser fuse and it came back out, no fault indicators tripped, will need a line crew with thumper to help with repairs. Isolated URD 71-206 and closed URD riser @1448. Trans. 207 and 208 still out. Energized trans. 207 @2118, and will have to change out padmount 208, it has a busted bushing. Got trans. changed and energized last customers @2300//cust counts are not verified correct, URD maps are not correct for this area//
2700 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-06-26 13:01 | 2015-06-26 15:00 | 145 | 119 | 4663091 | 12250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | // POLE 116-707 80T LINE FUSE OUT/ POLE 116-707 80T LINE FUSE OUT/ BACK ON 14:25/ NEED LARGE BUCKET TRUCK/ RESTORED MP/ ISO 38830116D00707/ COD 145/ VER/BOW AJB
2701 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-07-31 17:10 | 2015-07-31 19:45 | 79 | 155 | 4964901 | 12245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PIN ON DEAD-END INSULATOR FAILED//SERVICER GROUNDED AT FUSE POLE AND TAGGED TO HIMSELF IN ORDER TO MAKE REPAIRS SAFELY//COD 79 //HAVE REPAIRS MADE AND GRD AND TAG REMOVED, CLOSED IN LINE FUSE ON POLE 1122-66 AT 1945// VER/DBM AJB
2702 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-04-15 05:33 | 2014-04-15 08:12 | 77 | 159 | 4605301 | 12243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER @ POLE 350-27,RECLOSER IN @ 0812 ALL CUST RESTORED PLEASECLOSE TICKET THANKS.BT VER/KEP IDC XXXX
2703 | Hazard | 3309302 | VICCO | JEFF | 2012-04-23 16:51 | 2012-04-23 20:15 | 60 | 204 | 4699931 | 12240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WE HAVE HIGH SIDE OF STEPDOWN BLOWN ON ONE OF THE STEPDOWNS. WE ALSO HAVE NEUTRAL DOWN AT LOCATION. C PHASE IS OUT ///VER/CRB IDCC CDC92 XXXX
2704 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2016-02-19 14:04 | 2016-02-19 18:42 | 356 | 278 | 4736341 | 12238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CALLED 911 WITH ETA: 1310. OPENED SW ON 785-331 @ 14:04 TO CUT LOOPS. PRIMARY LOOPS CUT ON 38830785B40313 TO ISOLATE FAULT POLE. CLOSED SWITCHES ON 785-331 @ 14:37. RELEASED BY CREW 076S02// REPAIRS COMPLETED CLOSED IN AT 18:42 TCM// RELEASED BY CREW 076H01// VER/ ADH // VER TIME PER SCADA & VOICE REC L3/HFP HFPC TOF1256 CODO FEC57 AJB
2705 | Hazard | 3307301 | BULAN | ARY-HEINE | 2016-09-25 10:11 | 2016-09-25 13:30 | 69 | 199 | 4924131 | 12226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NEED LINE CREW & ROW CREW . OPENED GOAB ON POLE 128_23 @ 12:40 . CLOSED RECLOSERS ON POLE 128-17 @ 12:47 , SEE DOL CASE 690456 FOR ADDITIONAL SWITCHING AND TIMES//TOM - 189CC ON 128-17 (PART OF CKT FEEDING HADDIX/QUICKSAND) RESTORED TO 128-23 @ 1247 35CC - RESTORED 142 FROM ALTERNATE SOURCE AT 1330 TOTAL RESTORED 177(34 ON THIS RECORD AND 108 ON HADDIX RECORD)// 12 CC TO REMAIN OUT UNTIL REPARIS COMPLETED// VER/TOM L3/TOM AJB CCTOR FEC57
2706 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-11-18 06:44 | 2017-11-18 09:52 | 65 | 188 | 4564111 | 12220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | conductor is broke at fuse pole , hanging by lead on arrester 37830473000106/A phase out cod 59/opened blade on 37830473000103 addl cod 6.conductor is broke at fuse pole , hanging by lead on arrester. we will have to open reclosers at pole 449-854 to make repairs
2707 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-12-24 18:58 | 2022-12-24 23:50 | 56 | 292 | 4351501 | 12218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OCR 487-162 OPEN/WIRE DOWN 464-12/CUT LOOPS AT 464-11/CLOSED OCR AT#4 acsr down on 37830464000012. Cut loops and PLACED TAG AND GROUNDS FOR CALVIN WILLIAMS on 37830464000011 to isolate trouble. Closed recloser @ 22:04 Released by crew 077S06..comp23:50 Released by crew 077H13
2708 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-05-25 16:00 | 2009-05-25 21:20 | 165 | 320 | 64198-1 | 12194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE ONLY//COD 165//PRIMARY DOWN AT 38830185000151, ISOLATED AT SAME POLE, CUTOUT DOOR STUCK CLOSED AND ALLOWED RECLOSURE TO OPERATE,PRIMARY DOWN AT 38830185000151, ISOLATED AT SAME POLE, CUTOUT DOOR // ALL ON @ STUCK CLOSED AND ALLOWED RECLOSURE TO OPERATE, RECLOSURE CLOSED AT 17:03, TREE CREW CUTTING LINE. //RELEASED BY CREW 078S05/ ALL ON @ 21:20//VER/CRB IDC CHANGED FROM TREE IN R/W BECAUSE MAJORITY OF OUTAGE WAS CUTOUT ISSUE XXXX
2709 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-11-20 05:11 | 2015-11-20 11:57 | 30 | 406 | 4473221 | 12180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ****SEE 4473221*** PRIMARY PULLED OUT OF SLEEVE AT POLE 936-12 (30 CUST)//LAYING ON GROUND BURNING//OPENED SWITCH AT 936-8 TO ISOLATE///LINE CREW ENROUTE///REPAIRS MADE//RESTORED AT 11:57//COMPLETE//EM/ OPENED SWITCH AT 0840 38830936C00008 (3 CUST)/ ISO 38830936C00008/ COD 33/ DUPLICATE IN HOIS
2710 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2008-12-10 06:26 | 2008-12-10 14:32 | 33 | 486 | 55997-1 | 12177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000601 -/RECLOSER OUT ON 250-117 PATROLING LINE/ISOLATE ON 250-161/BURNT OFF POLE 40/5 TRUCKS OK/CREW REQUIRED/RECLOSER BACK ON AT 0841TO 250-161 RELEASED BY CREW 078S03//VER/CRB L3/WHV IDC XXXX
2711 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2016-04-07 03:31 | 2016-04-07 06:55 | 76 | 204 | 4061781 | 12171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 454-6509, POLE454-6531 BURNT OFF, TRUCK OK/// CUT LOOP AT FUSE FUSE FED BOTH DIRECTIONS TIME ON 0514/// T&G TO BRENT T AT 454-6509 RELEASED BY CREW 078S11,,CREW ON SITE,,REPAIRS MADE,,OPENED FUSE 454-6509 TO REPLACE JUMPER @0645,,,FINAL RESTORATION AT 0655 SEE H4061781 FOR OUTAGE TO MAKE UP LOOP VER/HFP L3/HFP AJB
2712 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-09-05 10:08 | 2016-09-05 16:28 | 32 | 380 | 4869101 | 12160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ***SEE 4869471*** POLE 116 D 709 BAD 500 KVA 34.5 TO 12 KV STEPDOWN. TRKS OK. REC OPEN @ 116-156/ ,,CRE ON SITE,,ALL REPAIRS MADE,,ALL POWER RESTORED 1628/ ISO 38830116D00709/ COD 32/ VER/BOW L3/HFP XXXHFP AJB
2713 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-08-08 20:07 | 2017-08-08 22:25 | 88 | 138 | 4241671 | 12144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE DOWN ON GROUND ARCING//ISO & FAULT POEL 38831078000022//COD 88//LINE DOWN ON GROUND ARCING/ LINE BROKE A STIRUP/ ISO 38831078000022/ VER/BOW SJG (RELATED TO 4241691)
2714 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-10-22 10:39 | 2008-10-22 13:30 | 71 | 171 | 57881-1 | 12141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3117601/PATROLING LINE// E MAIL TO RAYBURN--CSP NEEDS CUTOUT INSTALLED AN ARRESTOR REPLACED--ANIMAL GUARD CAN BE INSTALLED AT THAT TIME// CALLED CREW FOR HELP--REPLACED 12KV CUTOUT ON STEPDOWN ON POLE 92-124 AN REPAIRED BAD CONNECTION ON PRIMARY RISER VER/TOM IDC XXXX
2715 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-05-03 15:45 | 2021-05-03 18:46 | 67 | 181 | 4517281 | 12127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | wire has come ff the insolater on pole 38830260000056. isolated recloser and tagged to ramey Released by crew 078H03///back in at 18:46///complete BR
2716 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-02-01 14:01 | 2021-02-01 16:30 | 82 | 149 | 4926291 | 12124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary down from 170-4 to 170-5 wire broke in the clear had to open NC switch on pole 170-1 to make repairs, opened @1535, Kenny Little is coming to help with repairs
2717 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-03-19 11:15 | 2015-03-20 12:30 | 8 | 1515 | 4208991 | 12120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | TRANSFORMER OPENED AT 473-138 TO REPLACE POE AT 473-160 MWL // OPENED @ 1115 CLOSED @ 1230 COD-8 ISO TF 37830473000138 VER/HFP L3/HFP AJB ?SCH?
2718 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-02-08 13:06 | 2010-02-08 15:10 | 145 | 124 | H52894-1 | 12115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33777642 // HIGH SIDE FUSE BLOWN// "B PHASE ONLY" STEPDOWN TR BAD. CREW WILL REPLACE TR AND TRANSFER LOAD OFF B PHASE TO BALANCE.HIGH SIDE FUSE BLOWN//// OPENED UP OTHER 2 PHASES AT 1306 , CC 138 , CLOSED AT 1450 COLD LOAD P.U TOOK OUT RECL OPENED NO. SW AT POLE 265-406 . CLOSED ALL RECL AT 1510 228CC 162 CC OUT UNTIL N.O. IS CLOSED. ALL CUST REST AT 1612.STS WR # 3377764 VER/PDP IDC XXXX
2719 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-02-15 17:33 | 2016-02-15 23:40 | 33 | 367 | 4698321 | 12111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PR KEESEE IS ON SITE//SERVICER ETA 1900//POLE 74-26 POLE TOP BURNED OFF AND HANGING UPSIDE DOWN AGAINST POLE BURNING JUST ABOVE TRANS NTA BEHIND HOUSES UP ON HILLSIDE A LITTLE WAYS MAY B ABLE TO PATCH IT IF NOT TOO DAMAGED BY FIRE CREW IS ENROUTE SEND TO CLIFF FREEMAN//COD 33//EMAILED TO CLIFF FREEMAN VER/CRB L/3 CRB AJB
2720 | Hazard | 3310502 | HADDIX | CANOE | 2015-11-09 11:54 | 2015-11-09 16:49 | 41 | 295 | 4421391 | 12095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR NEED BAD ON POLE 37830169C00122 AND BURNED POLE OFF, GOT JEFF COMBS CREW COMMING TO CHANGE POLE OR LOWER IT DOWN/ ISO 37830169C00027/ COD 41 VER/HFP L3/HFP AJB
2721 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-07-05 19:05 | 2011-07-05 22:08 | 66 | 183 | 4471551 | 12078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1074-350 FAULT POLE//RECLOSER NEVER OPENED//COD 96//SWITCH AT 1074-339 OPENED AT 2001//PRIMARY CAME LOOSE FROM SLEEVE RESAGE PRIMARY WIRE THAT WAS DOWN RELEASED BY CREW 074S05//VER/CRB IDCC CDC83, CNT 98 ONLY PHASE B INITIALLY CREATED OUTAGE FOR OTHER 2 PHASES XXXX
2722 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-12-02 14:40 | 2020-12-02 14:53 | 929 | 13 | 4739511 | 12077 | TRANSMISSION STATION | EQUIPMENT FAILURE | REGULATOR | Outage to allow Station crews to safely close TR fused discs after replacing failed Regulator in Station de-energized. Outage should last less than 30 mins from start. FETR 1515 929 CC Off at 1440 On at 1453
2723 | Hazard | 3310502 | HADDIX | CANOE | 2019-02-11 11:50 | 2019-02-11 19:18 | 40 | 448 | 4777801 | 12040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | found broke insulator on pole 37840120000031 no burn marks on pole not sure if thats it or not Released by crew 077S05//CLOSED OCR IN @ 1730 UPTO HT LIFTED ON POLE 37840120000016//OPENED OCR BACK UP @ 1812 AND CLOSED @ 1918 // never lifted hot tap found another issue on first fault pole
2724 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-12-19 15:25 | 2008-12-19 17:45 | 86 | 140 | 60639-1 | 12040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 27756923 // LOOP BURN OFF AT POLE #1013-B-13. BURN OFF AT CONNECTION. RELEASED BY CREW 079H02 VER/HFP L3/KEP IDC XXXX
2725 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-01-26 07:42 | 2011-01-26 09:05 | 281 | 83 | H64341-1 | 12028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38577749 // ONLY CENTER PHASE OUT B PHASE 8 CUSTOMERS. OPEN RECLOSER ON POLE 48-24 AT 07:42 CLOSER IN AT 08:20 (251 CUSTOMERS ))RELEASED BY CREW 074S05//REPLACED C/O AND REPAIRED GUY AND CLOSED IN ALL 3 C/OS AT 9:05 DUPLICATE FROM 64341-1 VER/HFP L3/HFP IDC XXXX
2726 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-06-08 22:52 | 2013-06-09 09:25 | 19 | 633 | 4240771 | 12027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 500 SPAN OF PRIMARY DOWN === NEED 3 MAN LINE CREW AND ROW CREW === MAY NEED TO WAIT TILL DAYLIGHT //B.BETTINAZI REPORTED OK TO WORK AFTER DAYLIGHT // C.BOWEN GETTING RW CREW // REPAIRED LINE REFUSED == POWER OK VER/KEP IDC CHANGED FROM UNKNOWN XXXX
2727 | Hazard | 3310502 | HADDIX | CANOE | 2020-02-10 12:14 | 2020-02-10 14:54 | 96 | 160 | 4388061 | 12016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | recloser open on pole 49-141 closed it at 14:10. bad insulator on pole 25-120 blew line fuse on pole 25-118. cleared insulator and restored power at 14:54 Released by crew 077S10 ¦¦¦ SERIOUS CORDINATION ISSUE ???
2728 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-09-21 06:08 | 2017-09-21 12:12 | 33 | 364 | 4378081 | 12012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DISPATCHED IN ACCORDANCE WITH KYPCO LATE NIGHT CALLOUT GUIDELINES.C PHASE LINE FUSE BLOWN ON POLE 794-246//FOUND BROKE CUTOUT ON POLE 794-50//R MAYNARD ASSISTING.////REPAIRS MADE// 38820794C00246 VER/AWD L3/HFP XXXHFP SJG
2729 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-06-17 20:38 | 2009-06-18 06:10 | 21 | 572 | 50907-1 | 12012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | XFMR POLE 809-319 IS BROKE AND LAYING ACCROSS STREET. OPENED PH C REC ON POLE 809-148 AT 21:15 TO ISOLATE, REMOVED HOT LINE CLAMP ON POLE 809-293 AND CLOSED REC BACK AT 21:30. CREW ENROUTE. CREW ONSITE - REPAIR UNDERWAY. REPAIRS COMPLETE. RESTORED AT 06:10. SH//VER/CRB IDCC CNT53 XXXX
2730 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-05-09 18:20 | 2015-05-10 12:25 | 18 | 1085 | 4406851 | 12006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TAGGGED TO KYDDC/POLE BROKE 288D-24 , CUT LOOP ON POLOE 288D-17 AND GROUNDED AND TAGGED TO KYDDC/ . WILL NEED LINE CREW AND FLAGGERS TRUCK ACCESIBLE/ 40 POLE , POLE TOP PIN & INSULATOR , CLEVICE . WILL WORK IN THE AM 5-10-15 DUE TO REMOTE LOCATION/RESTORED 9 CUSTOMERS AT 2229/ POWER RESTORED TO LAST 9 CUSTOMERS AT 12:25 POLE REPLACED// VER/ ADH L3/DKGXXX
2731 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2018-05-23 23:00 | 2018-05-24 13:18 | 30 | 858 | 4405311 | 11988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | patroilling// riser fuse also blown on pole that feeds junction box 785-889// closed in fuse on pole 785-693 at 03:35 only thing out is junction box 889 and 789-986 will work in morning Released by crew 076H04//maps incorrect, send to technicians to field check//Repairs made back on @ 13:18 Released by crew 076H06//MAP DESC IS BEING MADE BY TECH TO SHOW RISER FUSE AND POLE ON 38830785D10889
2732 | Hazard | 3309302 | VICCO | JEFF | 2009-08-05 17:05 | 2009-08-05 17:56 | 235 | 51 | 65382-1 | 11985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED RECLOSER TO SAFELY MAKE REPAIRS ON LINE VER/KEP L3/KEP IDC XXXX
2733 | Pikeville | 3421001 | BREAKS | CITY | 2009-03-02 11:51 | 2009-03-02 12:50 | 203 | 59 | 53927-1 | 11977 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3400901//CREWS OPENED RECLOSER TO REPAIR WIRE THAT HAD COME OFF OF INSULATOR AND IS LAYING NEAR OTHER PHASE ONTOP OF A CROSSARM//COD 203// VER/DBM IDC XXXX
2734 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-23 16:13 | 2011-05-23 16:51 | 315 | 38 | H1152871-1 | 11970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 LINE CUTOUT ( B PHASE ) NO TRUCKS TO POLE. NEED LINE CREW. RELEASED BY CREW 078S01//REPLACED 19.9 KV CUTOUT S&C BRAND CUSTOMERS RESTORED PRTOLLIVER AT 16:50 (OPENED LINE VIA SCADA TO SAFELY CLIMB POLE)// RELEASED BY CREW 078H03 //VER/GAH
2735 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-10-28 01:38 | 2014-10-28 04:34 | 68 | 176 | 4666021 | 11968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 37830235000175 HOT LINE CLAMP BURNED OPEN ON A PHASE, OPENED 3 PHASE SECTIONALIZER AT POLE 175 AT 04:20 INTERRUPTING B & C PHASES TO REPAIR . ALL REPAIRS COMPLETE / ALL CUSTOMERS ON AT 04:34 // GXJ // SEE H4666021 FOR B & C PHASE OUTAGE - 75 CUST // VER/HFP L3/HFP AJB
2736 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-06-26 20:52 | 2010-06-27 04:15 | 27 | 443 | 57928-1 | 11961 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR# 35746038 /80T LINE FUSE OUT ON POLE 39831148B20865-- RELEASED BY CREW 078S07---- CABLE BAD 20-423 TO 20-426 VER/LDA IDCC CDC83 XXXX
2737 | South Williamson | 3200302 | BELFRY | TOLER | 2010-04-02 13:49 | 2010-04-02 16:53 | 65 | 184 | 57440-1 | 11960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER NOT OUT, BAD CUTOUT IN MAIN LINE BROKEN AT POLE#1040-A-3, CALLED R MARCUM FOR HELP "C" PHASE ONLYRECLOSER NOT OUT, BAD CUTOUT IN MAIN LINE BROKEN AT POLE#1040-A-3, CALLED R MARCUM FOR HELP, OPENED RECLOSERS AT POLE#1015-D-81 AT 1629, BACK ON AT 1653 AJB IDC XXXX
2738 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-11-24 02:27 | 2014-11-24 13:31 | 18 | 664 | 4759311 | 11952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 1147-436 30T UNDERGROUND FUSE OUT NEED LINE CREW AND DAYLIGHT---BAD PRIMARY CABLE BETWEEN XFMR 705 & 708---PARKED IN 705---OPENETD BLADE IN LIVE FRONT 708--TAGD IN BOTH XFMRS---OPENED RISER ON 691 @ 13:05 BACK IN @ 13:31---TBL TKT COMPLETED // COD-18 ISO @ 39831147A00436 N.O. HAD BEEN MOVED TO TR 1147-A3-697 - SEE DUP H4759311 FOR 2ND OUTAGE VER/HFP L3/HFP
2739 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-04-06 23:36 | 2016-04-07 03:35 | 50 | 239 | 4061211 | 11950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20-3040 CROSSARM BURNT OFF SEND CREW NEED ARM AND CUTOUT POLE 20-3031 65T BLOWN "A" PHASE COD-50 OPENED OTHER "C" PHASE COD-12 11:50 PM R,,CREW ON SITE VER/KEP L3/HFP HFPC FP38830020D13040 AJB
2740 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-11-04 16:28 | 2021-11-04 20:05 | 55 | 217 | 4058171 | 11935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Released by crew 078S05 crew on site LRMall pwr restored 20:05 please close ticket
2741 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-05-15 17:00 | 2009-05-15 17:40 | 298 | 40 | 57532-1 | 11920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW IS RPLACING INSULATORS AT STATION FETR 1900//VER/CRB IDCC TOF1616 XXXX
2742 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-05-18 15:51 | 2008-05-18 21:13 | 37 | 322 | 65541-1 | 11914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN ON POLE #1038-6 WILL NEED 2 MEN ISOLATING POLE #1038-4 WIRE PULLED OUT OF SLEEVE VER/JHM IDC XXXX
2743 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-10-03 06:26 | 2015-10-03 13:47 | 27 | 441 | 4307511 | 11907 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PATROLLING LINE TO DETERMINE CAUSE. APPEARS THAT A BAD SPOT IN PRIMARY BROKE AND BURNED NEUTRAL DOWN WHEN IT FELL AT 1073-34. (#4 CU) CAN TRUCK WITH FLAGGERS TO BLOCK ONE LANE RD. REPAIRS COMPLETE. RESTORED @ 13:47. SH// VER/ ADH L3/HFP XXXHFP AJB
2744 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-10-29 01:06 | 2014-10-29 13:30 | 16 | 744 | 4669691 | 11904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HOLD TILL DAYLIGHT RELEASED BY CREW 077S12 BAD CUTOUT POWER RESTORED VER/CRB L3/HFP
2745 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-02-02 09:43 | 2014-02-02 12:38 | 68 | 175 | 4336351 | 11900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 075H04 LINE FUSE OUT ON POLE 30-74 . FOUND BAD ARRESTER ON POLE 78-28 , CLEARED ARRESTER. CLOSED LINE FUSE ON POLE 30-74 @ 12:38.//COD 68 // AED ENTRY CREATED// VER/DBM L3/HFP IDC XXXX
2746 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-02-20 02:35 | 2015-02-20 11:15 | 27 | 520 | 4046911 | 11895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRIED FUSE @ 0713 02/20 AND IT CAME BACK OUT //PATROLLED LINE, GIVE FUSE A TRY, IT CAME BACK OUT.PATROLLED LINE, GIVE FUSE A TRY, IT CAME BACK OUT. WIRE DOWN AT 207-22, MANUEL JOB, WILL NEED CREWPATROLLED LINE, GIVE FUSE A TRY, IT CAME BACK. OUT. WIRE DOWN AT 207-22, MANUEL JOB, WILL NEED CREW. ISLOATED TROUBLE ON POLE 183-91, RESTORED POWER TO THERE AT 08:00PATROLLED LINE, GIVE FUSE A TRY, IT CAME BACK. OUT. WIRE DOWN AT 207-22, MANUEL JOB, WILL NEED CREW. ISLOATED TROUBLE ON POLE 183-91 VER/HFP L3/HFP
2747 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2021-01-30 10:28 | 2021-01-30 16:55 | 49 | 387 | 4920201 | 11883 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C Fuse is open,Line goes Through woods,(Patrolling)..We have broke croossarm on pole 54-128,Its Manual,Spoke with Paul Layne and he is getting Material and headed this way..Opened other 2 Switches at 14:24 made repairs and restored at 16:55.
2748 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-10-19 07:08 | 2018-10-19 09:20 | 90 | 132 | 4269031 | 11880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required load took out chg cutout also COD-119 ISO LF 38830250000116
2749 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-08-30 04:42 | 2022-08-30 10:03 | 37 | 321 | 4812831 | 11877 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on arm @ 139-92, Send to luke mccoy Released by crew 078S02///opened A and C phases at 0910 to make repairs-- 1003 fuse closed restoring all customers
2750 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-01-02 10:17 | 2008-01-02 13:49 | 56 | 212 | 52671-1 | 11872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED OFF ON POLE 196D-49 NEED 1 MAN ==//3312202== REPAIRED HOT LINE CLAMP = RESTORED POWER.//VER/CRB IDC XXXX
2751 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-08-11 16:46 | 2010-08-11 19:38 | 69 | 172 | 52702-1 | 11868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN CREW ENROUTE RELEASED BY CREW 074S02......CREW ONSITE, LINE FUSE OPEN ON POLE 37820148000050 ,ONE PRIMARY CONDUCTOR DOWN #4AA ON POLE 148-57....POWER RESTORED @ 19:38 VER/KEP L3/KEP IDC I BELIEVE THE RECLOSER WAS OUT AS WELL CHANGED COUNT FROM 20 AND CLEARING DEVICE FROM FUSE XXXX
2752 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-09-27 03:31 | 2010-09-27 10:20 | 29 | 409 | 53954-1 | 11861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON 1061-B-14....POLE 1085-A-522 TOP OF POLE BURNT OFF...BAD CUTOUT....CREW REQUIRED....TRUCK ACCESSABLE....WILL RAISE UP & EXTINGUISH FIRE....//...FIRE OUT...PLEASE SEND TICKET TO JOEY REED....THANKS... JRV...09/27/10 RELEASED BY CREW 080S01// COD 29// VER/DBM IDC XXXX
2753 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-05-03 20:49 | 2016-05-04 00:10 | 59 | 201 | 4171781 | 11859 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE ORDER 4171971 FOR RECL OUTAGE TO REPLACE CUTOUTBAD CUTOUT ON POLE 427-9, I CHANGED IT OUT , WE OPENED RECLOSER ON POLE426-685 AT 23:40 AND CLOSED BACK AT 00:10 5-4-16 RELEASED BY CREW 077S12// 63 COD ENTIRE OUTAGE// ASSCPIATED WITH 4171971 VER/TOM L3/TOM AJB
2754 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-12-08 08:50 | 2012-12-08 10:45 | 103 | 115 | 4451101 | 11845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT-LINE CLAMP BURNT OFF LOAD SIDE OF RECLOSER. REPLACING. REPAIRS COMPLETE. CLOSED RECLOSER @ 10:45. <<ONLY ONE OF THE TWO RECLOSERS ON 784-511 WAS OPEN>> (PH A) SH//COD 103// VER/DBM IDC XXXX
2755 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-10-28 15:35 | 2017-10-28 21:45 | 32 | 370 | 4505651 | 11840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FLICKERING LIGHT ISSUE. SERVICER PATROLLING LINES. MULTIPLE OCR AND CB OPERATIONS. NO OUTAGE AT THIS TIME. OPENED AT 1535/// VER/DKM L3/HFP XXXHFP ACB
2756 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2013-08-31 12:10 | 2013-08-31 14:38 | 80 | 148 | 4804421 | 11840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE B REC ONLY HOT-LINE CLAMP RISER BURNT OFF ON RECLOSER. CREW ENROUTE TO ASSIST. MADE REPAIRS AND CLOSED PH B REC @ 14:38. SH RELEASED BY CREW 076S02 COD 80. VER/CRB L/3 CRB
2757 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-11-30 13:07 | 2010-11-30 14:36 | 133 | 89 | 61109-1 | 11837 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//COD 133// VER/DBM IDC XXXX
2758 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2014-06-09 19:50 | 2014-06-09 20:19 | 408 | 29 | 4000291 | 11832 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | EMERGENCY STATION OUTAGE TO MAKE REPAIRS -AT DRAFIIN STATION // TOM OUTAGE APPROX 30 MIN FROM OUTAGE START TIME// VER/KEP AJB
2759 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-07-13 09:33 | 2012-07-13 12:57 | 58 | 204 | 4708501 | 11832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE -ONLY B PHASE RECLOSER OUT/COD-58/PATROLING LINE -ONLY B PHASE RECLOSER OUT--B FRALEYS CREWW ASSISTING--BAD CUTOUT N POLE 38830092A00884 ON PRISION PROPERTYPATROLING LINE -ONLY B PHASE RECLOSER OUT--B FRALEYS CREWW ASSISTING--BAD CUTOUT N POLE 38830092A00884 ON PRISION PROPERTY RELEASED BY CREW 078S07 IDC XXXX
2760 | Hazard | 3303902 | LESLIE | WOOTON | 2013-04-17 09:31 | 2013-04-17 14:45 | 43 | 314 | 4017921 | 11825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H04BAD CUTOUT ON POLE 37830415000075 == CUTOUT NOT IN US == REM FROM LINE === REFUSED LINE FUSE ON POLE 37830415000049 AT 14:02 AND FUSE ON POLE 37830415000063 14:45 == POWER OK VER/KEP IDC XXXX
2761 | Hazard | 3303901 | LESLIE | HYDEN | 2018-02-14 14:09 | 2018-02-14 18:15 | 48 | 246 | 4840721 | 11808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad dead-end insultaor on pole 388-340,
2762 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-05-29 06:23 | 2009-05-29 07:45 | 144 | 82 | 63962-1 | 11808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECL ON POLE 38830453000331 MAY BE OUT,,,,BAD RECLOSER,,,PLACED BYPASSES IN POWER RESTORED AND RECLOSER IS IN ABNORMAL VER/KEP L3/KEP IDC XXXX
2763 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-05-17 10:04 | 2021-05-17 14:00 | 50 | 236 | 4591721 | 11800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | primary came untied on pole hangin against pole top pin repairs made power restored at 14:00
2764 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-07-08 14:10 | 2013-07-08 14:40 | 393 | 30 | 4487841 | 11790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | TELATED TO 4485131 BROKEN CROSS ARM BRACES // COD-393 ISO OCR 37830356A00036 VER/HFP L3/HFP IDC XXXX
2765 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-11-11 09:55 | 2013-11-11 11:35 | 148 | 100 | H4027491 | 11776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX BURNT IN TWO AT SPACER. CREWS WORKING TO REPAIR DOWNED CONDUCTOR AND TWO DAMAGED CONDUCTORS.// OPENED GOAB AT POLE 954D2-100 @09:55. CLOSED GOAB @ 11:08, FUSES STILL OPEN @978-168//HENDRIX BURNT IN TWO AT SPACER. CREWS WORKING TO REPAIR DOWNED CONDUCTOR AND TWO DAMAGED CONDUCTORS. REPAIRS COMPLETE. CLOSED GOAB ON 954-100 @ 11:08 RESTORING ALL BUT OPEN LATTERAL ON 978-168. CLOSED THREE 40TS ON 978-168 @ 11:35 RESTORING REMAINING OUTAGED CUSTOMERS. SH VER/SEF IDCC DUP TO OPEN SW XXXX
2766 | Hazard | 3309301 | VICCO | REDFOX | 2008-07-08 18:03 | 2008-07-08 19:53 | 107 | 110 | H64554-1 | 11770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 1 PHASE OUT 0N POLE 323-430, CORRECTION, WIRE IS BURNT OFF IN STATION... 162 CUST OUT ORIGINALLY / OPENED BRK AT 1803 107 CUST OUT / TOTAL 269 CUST RISER ON LINE SIDE DISCONNECT BURNT INTO/ REPAIRED AT 1953 VER/KEP IDC XXXX
2767 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-01-10 19:00 | 2009-01-10 23:47 | 41 | 287 | 54047-1 | 11767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302//OPENED RECLOSER37830151000199 @ APPROX 1900 DUE TO POLE FIRE//COD 41//ISO// POLE 37830151000029 IS ON FIRE CUTOUT WENT BAD CALLING FOR CREW AND FLAGGERS/ LOWERED ARM ON POLE AND REMOVED XFMR CLEARENCE OK JEFF COMBS VER/KEP L3/KEP IDC XXXX
2768 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2016-02-26 15:58 | 2016-02-26 16:10 | 980 | 12 | 4780461 | 11760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, HAVE BAD CUTOUT ON A PHASE, AT THE CORNER OF OSMAN AND JAMES HANNAH DR.L BESIDE OLD GAS STATION, WELL NEED AWP AS WELL POLE NUMBER IS 901-4617 RELEASED BY CREW 078S06.. CREW ON SITE NO INTERRUPTION AT THIS TIME. OPENED SILOAM BREAKER @ 1558 CLOSED 1610.. OPENED BREAKER TO CHANGE BAD CUTOUT.. COMPLETE RELEASED BY CREW 078H22// VER/ ADH L3/HFP XXXHFP AJB
2769 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-05-11 15:46 | 2019-05-11 17:30 | 113 | 104 | 4253721 | 11752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout bad on pole 205-263, 2 line fuses blown on pole 205-80 Released by crew 077S02
2770 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-05-19 19:24 | 2011-05-19 23:20 | 101 | 236 | 4115391 | 11752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 40039878 //POLE 1051-47 BURNED OFF,WILL LOWER.ISOLATED AT 1051-16,RESTORED TO THAT POINT////////MADE REPAIRS AND RESTORED TO ALL AT 23:18 RELEASED BY CREW 074S06 RESTORED 76 @ 2041 & @ 2320 RESTORED 25 VER/HFP L3/HFP IDC XXXX
2771 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-02-19 20:29 | 2013-02-19 22:00 | 129 | 91 | 4832671 | 11739 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SEVICER OPENED GOAB SWITCHES IN ORDER TO MAKE SAFE REPAIRS RELATED TO ORDER 4832451//COD 140// VER/DBM IDC XXXX
2772 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-05-02 17:32 | 2011-05-02 19:03 | 129 | 91 | 53780-1 | 11739 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STS WR # 39791217 // PATROLLING LINE. MORE THAN TWO CUSTOMERS ARE OUT OF POWER. MAY HAVE A LOOP BURNT IN-TWO. FOUND LOOP BURNT IN-TWO ON POLE 401-13. GOING TO ISOLATE RECLOSERS ON POLE 401-17 IN ORDER TO REPAIR LOOP. TROUBLE IS MANUAL. // CREATED ORDER 53808-1 WHEN RECLOSER OPENED @ ????STS WR # 39791217 // P GOING TO ISOLATE RECLOSERS ON POLE 401-17 IN ORDER TO//VER/CRB IDC DCMTXXXX
2773 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-01-09 22:14 | 2016-01-09 22:48 | 345 | 34 | 4597991 | 11730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | TRIED RECLOSER ON POLE 262-177 VER/ARN AJB
2774 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-11-18 10:50 | 2010-11-18 13:40 | 69 | 170 | 57864-1 | 11730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED GOAB IN ORDER TO MAKE SAFE REPAIRS TO DOWNED LINES//SEE ORDER 57789-1 //COD 69// VER/DBM IDC XXXX
2775 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-08-07 19:03 | 2018-08-08 11:20 | 12 | 977 | 4921751 | 11724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1099-151 covered in vines, need cleared/ cleared vines/ man tree crew , Bad 50 kva 7200 transformer. Service truck to pole. Need pads to get truck in to pole. Access from 820 daniels drive. Bad 50kva 7200, Need line crew. Bring transformer sack, and mopads for truck. Service truck to pole in back yard.repairs made all cust restored @ 1120 please close ticket thanks.bt
2776 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-03 09:20 | 2010-12-03 10:56 | 122 | 96 | H62625-1 | 11712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PART OF 62625-1// OPENED OTHER PHASE AT0920 (122 CUST) AND CLOSED AT 1056 RELEASED BY CREW 077S05// VER/DBM IDC XXXX
2777 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-02-21 17:08 | 2011-02-21 18:25 | 152 | 77 | 59843-1 | 11704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | STS WR # 38886754 // CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE A BAD CROSSARMSTS WR # 3885 REPLACED BAD CROSSARM. POWER OFF 17:08 BACK ON 18:25. EVERYTHING OK VER/HFP L3/HFP IDC XXXX
2778 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-09-23 03:43 | 2011-09-23 13:00 | 21 | 557 | 4907271 | 11697 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 378-62, POLE 379-182 BURNT OFF AT XFMR, ISOLATED & GROUNDED AT POLE 378-62 RELEASED BY CREW 077S11 REPLACED POLE//COD 21// VER/DBM IDC XXXX
2779 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2009-04-25 13:13 | 2009-04-25 16:10 | 66 | 177 | 60203-1 | 11682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE BURNT OFF OUTSIDE STATION TRANSFERED CUSTOMERS TO BONNYMAN HAZARD VER/ARN IDCC TON1606 XXXX
2780 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-07-12 03:29 | 2011-07-13 11:55 | 6 | 1946 | 4522911 | 11676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OUT. ONLY ONE CUSTOMER HAVE NO POWER. RELEASED BY CREW 074F13 OLD TYPE 27KV C/O WITH LONG BARRELL BURNT UP. NEED NEW C/O & FBG BKT FOR LINE FUSE AT POLE 37830166000120. ALL OUT ON TAP OFF POLE 120 & XFRM ON 120. BJ RELEASED BY CREW 074E04 IDC XXXX
2781 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-11-01 10:48 | 2014-11-01 13:30 | 72 | 162 | 4683791 | 11664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | // B PHASE OUT COD 72// PATROLLED LINE AND DIDNT SEE ANY PROBLEMS. FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 13:30. SH VER/SEF L3/HFP AJB
2782 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-24 07:56 | 2018-11-24 09:45 | 107 | 109 | 4472151 | 11663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout L3/HFP
2783 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-02-14 09:00 | 2010-02-14 13:25 | 44 | 265 | 57531-1 | 11660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO ON POLE 1125-409. OPENED LINE FUSE ON POLE 1126A585.EVERYONE SHOULD BE BACK ON. //VER/CRB IDC XXXX
2784 | Hazard | 3420001 | SOFT SHELL | VEST | 2018-05-12 14:04 | 2018-05-12 15:35 | 128 | 91 | 4340411 | 11648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester/ cut it in the clear/ restored 1535/ ISO 37830157B20298/ COD 128Released by crew 077H02
2785 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-05-21 10:45 | 2017-05-21 11:45 | 194 | 60 | 4830031 | 11640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 68-909 CROSS ARM BURNT OFF NEEDS LOOKED AT ASAP TRUCK TO POLE POWER ON RELEASED BY CREW 078S08/ ALL POWER ON SAFE TO HOLD FOR CREW UNTIL IN THE MORNING/ OPENED L/F 38830068C00198 @ 1045//COD 194//CLOSED 1145// MD FILED// VER/DBM AJB
2786 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-11-17 22:40 | 2021-11-18 14:50 | 12 | 970 | 4103061 | 11640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | servicer was unable to locate the problem here//per duty supervisor, Rick Ray, hold until URD crew can work in the daylight // CREW ON SITE. ISOLATED AT X-FMR 72-C-480, FOUND BURNED BUSHING ON 72-C-483 WILL BE CHANGING PADMOUNT. BAD URD CABLE BETWEEN 72-C-43 AND 72-C-486 WILL BE THUMPING FOR LOCATION. REPAIRS COMPLETE ON AT 14:50
2787 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-03-18 16:16 | 2017-03-18 18:09 | 103 | 113 | 4568581 | 11639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLR IS OUT,WILL PTRL/////////1130-250,XFR LA AND XFR ITSELF BROKE DOWN,I ISOLATED THIS XFR AS IT DOESNT SERVE ANYTHING////////CLOSED&RESTORED/ ISO 38821130000301/ COD 103/ VER/BOW AJB
2788 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-11-27 13:55 | 2019-11-28 11:28 | 9 | 1293 | 4085031 | 11637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NC CREW REQ/ on site RM rec 166A259 ,A& Brec open also stepdown on A phaese open/ Bad 500kVa step-down xfmr on A phase/ crew required/ svc truck ideal because of proximity of 69kv.also according to BJ HUNT who ever fixes this will need TWIC CARD to get in because of holiday Released by crew 078H20,open step downs @ 1004,repairs made all cust restored @ 1128 please close ticket thanks.bt
2789 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-05-10 12:02 | 2017-05-10 19:30 | 95 | 448 | 4776471 | 11634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | KYDDC HOLD TAG//CREW REQUIRED BAD DEAD END INSULATOR ON 174-131 NO TRUCKS ISOLATED ON 174-21/RECL 38830174000163 BACK IN AT 1401 HRS (94 CUST)/ 1 CUSTOMER STILL OFF TAGGED TO DDC NO GROUNDS/CREW ON SITE/FETR 1930/VEM//1801 GAVE V MULLINS PERMISSION TO REMOVE KYDDC TAGS AND REPLACE WITH HIS OWN/ HOT TAP 38830174000021 ON @ 1930 RESTORING LAST CUSTOMER ALTHOUGH CUSTOMER WAS NOT READY TO BE HOOKED UP AND WILL CALL FOR RECONNECT/ VER/BOW AJB
2790 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-02-16 11:25 | 2013-02-16 13:24 | 263 | 119 | 4823511 | 11626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38831121C00092 WILL NEED 8 ARM AND BRACES 3 CUTOUS AND ARRESTERS, POLE 38831121D00065 LOOPS MADE SOLID, WILL NEED TO CUT LOOPS AND ADD 3 CUTOUTS ( 40T ) AND ARM MOUNT BRACKETS FOR 9 ARM, POLE 38831121C00093 WILL NEED TO REPLACE 40T WITH 25T . ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 MD FILED VER/KEP IDC XXXX
2791 | Hazard | 3303902 | LESLIE | WOOTON | 2016-09-28 23:21 | 2016-09-29 03:45 | 44 | 264 | 4940231 | 11616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING LINE, FOUND BAD INSULATOR ON STEPDOWN POLE, POWER RESTORED AT 03:45 RELEASED BY CREW 077S02//COD 44// VER/DBM L3/HFP XXXHFP AJB
2792 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-01-13 00:25 | 2012-01-13 02:05 | 116 | 100 | 4255071 | 11600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECL OPEN ON 576-140 PATROLLING LINE, 600-120 BURNT OFF, ISOLATED BY CUTTING PRIMARY AND NEUTRAL FROM 600-115. LINE CREW ATEMPTED TO GET INTO POLE BUT BOTTUM WAS A SWAMP. CUSTOMER STATED BOTTUM IS ALWAYS SOFT. WILL NEED DALE HAMILTON TO DO JOB. CUSTOMER ALSO SAID SERVICE WAS CAMPSITE AND NOT IMPORTANT, METER # 534086952 IS ONLY METER OFF. CREATED OPS ORDER TO SHOW STATUS OF METER. PER OPS #033781382 CREW 078S11//COD 138//EMAILED TO TECH AND CREWS// VER/DBM IDC APPEARS PH A ONLY CHANGED COUNT FROM 138 XXXX
2793 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-10-07 17:27 | 2011-10-07 19:52 | 80 | 145 | 4956541 | 11600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CENTER PHASE (B) LOOP BURNT OPEN ON POLE 37830048C10291//ISO//COD 80// AT 1930 , SERV OPENED A-C PHASE REC AT POLE 48-C21165 , < THAN 30 MIN OUTAGE TO MAKE REPAIRS .CENTER PHASE (B) LOOP BURNT OPEN ON POLE 37830048C10291.OPENED RECLOSERS ON POLE 48-1165 @ 19:33.(SEE 4956831) RESTORED ALL CUSTOMERS @ 19:52.ALL REPAIRS COMPLETE // COD 80//ISO// VER/DBM IDC XXXX
2794 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-02-24 04:18 | 2022-02-24 07:22 | 63 | 184 | 4538451 | 11592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop burned in 2 on 1146-81// will be making repairs.//Repairs made and restored @ 7:22
2795 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-04-20 09:45 | 2013-04-20 11:20 | 122 | 95 | 4032171 | 11590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF AT POLE 38830182B43567 - B PHASE 122 CUST //B PHASE BYPASS CLOSED, RECL ISOLATED & TAGS PLACED FOR KY DDC // NEED CREW TO REPLACE STYRUP & HOT TAP /// HOT TAP BURNT INTO ON B PHASE RECLOSER,LINE CREW NEED TO PLACE BASKET AND HOT TAP,BYPASS IN @1120 ALL CUST RESTORED,TAG TO DDC COD-122 ISO OCR 38830182B43567 VER/HFP L3/HFP IDCC FP NULL XXXX
2796 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-01-27 22:05 | 2019-01-27 22:17 | 965 | 12 | 4726731 | 11580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | CB outage to safely bypass defective recloser//cod 965 L3/HFP
2797 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-10-29 02:07 | 2020-10-29 09:50 | 25 | 463 | 4593821 | 11575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF is open on 962-21// checking// tried line fuse// kicked back out// check in daylight Released by crew 074S09/// C/O on pole 961-8 broke// all repairs made power restored at 09:50
2798 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-08-25 12:37 | 2014-08-25 14:35 | 98 | 118 | 4422041 | 11564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIMARY CAME OUT SPLICE BETWEEN POLES 428-59 AND 428-60//COD 98// VER/DBM AJB
2799 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2010-07-05 18:03 | 2010-07-06 01:45 | 25 | 462 | 62407-1 | 11550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3402204// POLE 38831121D00337 ARRESTER BAD, ADD TO ABNORMAL DATA BASE//AED CREATED// ARRESTER BAD ON POLE 1122-10, ADD TO ABNORMAL DATA BASE, 50 KVA CSP TRANSFORMER BAD AT POLE 210... REPLACED TRANSFORMER / ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/JHM IDCC CNT60 PN295 XXXX AJBC CNT30 PER PO.
2800 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-08-28 17:32 | 2017-08-28 23:57 | 30 | 385 | 4305801 | 11550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BLOWN LINE FUSE ON 984-15 PATROLLED LINE FOUND FAILED LINE FUSE AT 937-9 NTA CREW IS IN ROUTE CREW ARRIVED MADE REPAIRS RESTORED POWER AT 23:57 VER/KEP L3/HFP XXXHFP SJG
2801 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2021-11-26 10:20 | 2021-11-26 13:15 | 66 | 175 | 4125611 | 11550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout on pole 966A1-481 has broke down and tracked threw metal bracket causing pole fire..i got transformer fuse open at 09:45.i have crew in route.i opened the line fuse on pole 966A1-128 @ 10:20.crew made repairs and i got the line fuse on pole 966A1-128 back in at 13:15
2802 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2019-10-07 03:58 | 2019-10-07 13:35 | 20 | 577 | 4104951 | 11540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Released by crew 078S03---38830450000016 12t lat blown--vines and cracked insulator--lat in at 13:35-allgood-ds100719
2803 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-09-13 12:55 | 2020-09-13 13:23 | 568 | 28 | 4457001 | 11535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | dol 1053160 off @ 1255 on @ 1256 21 customers on @ 1306 257 customers on @ 1323 311 customers
2804 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-03-01 03:26 | 2018-03-01 11:45 | 36 | 499 | 4891441 | 11529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ 0748 patrolling line // I have broke cutout on pole 37830004D00302 going to take clamp off and i got line fuse in at 0830 (33 cust) // replaced cutout and arrester power restored to last customers at 11:45 // COD-36 ISO LF 37830004D00035
2805 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-11-12 10:41 | 2013-11-12 18:17 | 62 | 456 | 4031441 | 11528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RAYBUNS GETTING CREW//LIFTED HOT TAP ON POLE 38830069C45531-TAGED TO DDC// CLOSED FUSE IN ON POLE 38830069C35092 AT 12:55 RELEASED BY CREW 078S07WORK COMPLETE DW CLOSE TICKET PLEASE DW RELEASED BY CREW 078Q06 VER/CRB L3/HFP IDC XXXX
2806 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-04-16 16:11 | 2016-04-16 16:19 | 1441 | 8 | 4096091 | 11528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREWS REPLACING BROKE CROSSARM BRACES//EMERGENCY OUTAGE FROM 1610 UNTIL 1625 TO MAKE REPAIRS//SEE DOL CASE 650233//COD 1441//ISO 3010601//BOTH NCROSS ARM BRACES BROKEN,,,, RELEASED BY CREW 078H07 /// PER DOL & ALR OUTAGE FROM 1611 TO 1619 VER/HFP L3/HFP AJB
2807 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2015-05-15 19:27 | 2015-05-15 22:19 | 67 | 172 | 4433881 | 11524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE( 48 CUST) BYPASS BURNT UP // NEED 19.9 CUTOUT - 3 DEAD END BELL INSULATORS & BIG BUCKET & A LINE MECH // R THOMAS COMING TO HELP SERVICER MAKE REPAIRSCUTOUT ON A PHASE BURNT UP AND DESTROYED 3 BELL INSULATORS ON A PHASE TRUCK APPROACH NEED 1A LINEMAN AND BIG BUCKETCUTOUT ON A PHASE BURNT UP AND DESTROYED 3 BELL INSULATORS ON A PHASE COD-48 SEE 4434181 - NEEDS TO BE A STEP IN THIS ORDER - ALL CUST NOT RESTORED AJB
2808 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-06-12 19:54 | 2010-06-13 09:25 | 26 | 811 | 61807-1 | 11516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 076S02 BLOWN ARRESTER ON 786-148 DAMAGED CUTOUT. CREW WORKING TO REPLACE BOTH. FOUND ANOTHER PROBLEM WHEN WE CLOSED IN AND HAD TO OPEN. CLOSED FUSE ON 786-14 @ 2:10. XFMR OPEN ON 786-140. RELEASED BY CREW 076S02//CHANGED TRANSFORMER ON 786-140 AND RESTORED LAST CUSTOMERS @ 09:25//COD 26// VER/DBM
2809 | Hazard | 3302703 | HAZARD | HAZARD | 2009-07-25 23:55 | 2009-07-26 09:03 | 21 | 548 | 61286-1 | 11508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA 7200 120/240 XFMR BAD NEED TWO MEN AND MATERIAL BUCKET TO REPLACE RELEASED BY CREW 077S04 VER/KEP L3/KEP IDC XXXX
2810 | Hazard | 3303901 | LESLIE | HYDEN | 2013-01-30 08:39 | 2013-01-30 13:50 | 37 | 311 | 4754141 | 11507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT THIS THE LINE FUSE WILL NEED CREW WITH BIG BUCKET RELEASED BY CREW 077S01 AT 1120 * CONTACTED BRUCE LINDON , HE WILL SEND CREW WHEN AVAIL. COD-37 ISO LF 37830388D00403 VER/HFP L3/HFP IDC XXXX
2811 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2021-02-20 17:57 | 2021-02-22 17:52 | 4 | 2875 | 4198031 | 11500 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt up on pole, repaired per G Hicks
2812 | Whitesburg | 3409503 | BURDINE | JENKINS | 2019-02-12 02:38 | 2019-02-12 11:00 | 143 | 502 | 4779681 | 11488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO AT POLE 37830382C10187//COD 100//// //found loop burnt into on pole 382-187, will need to open reclosers on pole 382-306, outage time is approx 30 minutes//COD 100 FROM THE BEGINNING OF OUTAGE//OPENED OCR 37830358D00306 @ 1052 //// //found loop burnt into on pole 382-187, will need to open reclosers on pole 382-306, outage time is approx 30 minutes Released by crew 077S02//CLOSED OCR @ 1100//3 CUSTS REMAIN OUT ON OUTAGE 4779531/// C Phase at start of outage
2813 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-04-27 12:38 | 2010-04-27 17:33 | 42 | 295 | 52015-1 | 11488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WIRE DOWN @ 510 LITTLE HACKNEYS CR PER BOBBY TACKETT //I HAVE A POLE BURNT OFF AT POLE 37820150000024 WE CAN FRAME DOWN ON THE POLE TO MAKE REPAIRS,// I HAVE THE MAIN LINE FUSE ON POLE 151-69 CLOSED AT 17:11 LAST CUSTOMER ON AT 17:33 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC XXXX
2814 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2012-09-17 20:56 | 2012-09-18 02:15 | 36 | 319 | 4055461 | 11484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T LINE FUSE ,COULD NOT FINDE WHAT IS TAKING OUT LINE FUSE. FUSE CAME BACK OUT AT 23:44./BAD XFMR CUTOUT ON 282-3/CREW TO CHANGE/FETR 0300/VEM REPLACED BAD CUTOUT AND POWER BACK ON AT 02:15. VER/KEP IDCC TOF2019 XXXX
2815 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2009-10-19 13:28 | 2009-10-19 14:02 | 337 | 34 | 58047-1 | 11458 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | STATION CREW ON SITE// TARGET LOSS OF COOLING// OPEN @ 1328 - CLOSED @ 1402 // VER/TOM L3/TOM IDC XXXX
2816 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-02-25 01:04 | 2011-02-25 03:50 | 69 | 166 | 60971-1 | 11454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER LOCKED OUT ON POLE 37830272C21571, PATROLLING LINE. == CUTOUT BROKEN ON POLE 37830272C40847 REMOVED FROM LINE, NO LONGER IN USE.-- POWER RESTORED AT 3:50 A.M. VER/SDB IDC XXXX
2817 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2019-07-19 11:00 | 2019-07-19 13:49 | 116 | 169 | 4733671 | 11453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Solid blade switch broke on pole 1038-237 will have to open reclosers on pole 1062-279 to make repairs// Opened reclosers @ 13:23 // cod 59 on sw 38821038B00237 closed @ 1349 L3/HFP
2818 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-10-18 11:44 | 2012-10-18 16:10 | 76 | 266 | 4152481 | 11453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ISOLATED ON 350-76 GOING TO RECLOSER TO MAKE HOT EVERYTHING FROM 76 OVER STILL OFF/RECLOSER BACK ON 1403 HRS/CREW REQUIRED RELEASED BY CREW 078S03///POWER RESTORED AT 16:10 CLOSE TKT PRT RELEASED BY CREW 078H03 VER/KEP IDC XXXX
2819 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-06-03 18:20 | 2009-06-03 19:40 | 143 | 80 | 53949-1 | 11440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED UP BAD ARRESTER. CLOSED IN RECLOSER EVERYTHING OK. SEND COPY TO JASON BRADSHAW ROW PIKEVILLE. ROW NEEDS CUT BAD FROM RECLOSERS TO END OF LINE. WE WILL CONTINUE TO HAVE TROUBLE WITH TREES UNTIL THIS SECTION IS CUT VER/KEP L3/KEP IDC XXXX
2820 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2008-09-14 15:04 | 2008-09-15 17:45 | 9 | 1601 | 62535-1 | 11439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FOUND A 405 POLE THAT HAD ROTTEN OFF AT THE GROUND AND WIND BLOWED IT OVER, I HAVE HOT TAP LIFTED ON POLE 901-4588, AND LINE IS GROUNDED, WELL NEED CREW TO REPLACE THIS POLE, LOOKS LIKE THEY CAN USE EVERYTHING BACK JUST NEED A POLE RELEASED BY CREW 078S06// VER/DBM VER/DKG WAS ON RELIABILITY REPORT
2821 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-02-16 11:55 | 2017-02-16 13:21 | 133 | 86 | 4402261 | 11438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPLACED HOTTAP AND BASKET @ RECLOSER 38830205000017 VER/CRB L3/HFP XXXHFP AJB
2822 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-10-01 08:48 | 2015-10-01 15:36 | 28 | 408 | 4298121 | 11424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 250 STEPDOWN XFMR ON C PHASE AT POLE 376-18. WILL NEED FLAGGERS//OPENING OTHER PHASES @ 1415//COD 6 VER/CRB // PER VOICE RECORDER B PHASE STEPDOWN BAD & BUSINESS OBJECTS ALSO INDICATES B PHASE (66%) SCADA NO HELP = L3/HFP HFPC CDC92 AJB
2823 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-04-08 11:00 | 2019-04-08 13:24 | 131 | 144 | 4069401 | 11422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE RECL OUT 70 CUST ¦¦ BROKEN CUTOUTSOLID BLADE CUTOUT BROKE@1108-222,WILL HAVE TO OPEN RECLR@1108-22 IN ORDER TO REPLACE CUTOUT.OPENED@ 13:02, CLOSED @13:24. sjg
2824 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-09-12 16:42 | 2013-09-12 20:14 | 57 | 212 | 4845221 | 11412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 6A WIRE DOWN ON POLE 1146-73 APPEARS TO BURNT DOWN UNDER STIRRUP. CREW IN ROUTE SHORTLY 17:52 A PHASE OUT ONLY FROM RECLOSER POLE 1146-137. I HAVE APHASE RECLOSER IN NOW ON POLE 1146-137 TO TO OPEN POINT AT POLE 1146-74 SOLID BLAD GROUNDED AND TAGED FOR MYSELF. MADE RECLOSER HOT ON POLE 1146-73 AT 19:50 DOWN TO POLE 1122-12 CLOSED IN AT POLE 1122-12 AT 20:14 RELEASED BY CREW 074S11 VER/CRB L/3 CRB IDCC PN74 PROBABLY SOME SMALLER STEPS BUT CAN NOT VERIFY XXXX
2825 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-04-13 12:07 | 2009-04-13 16:46 | 87 | 279 | 51856-1 | 11408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401703// B PHASE RECLOSER OPEN - 85 COD// GOING TO ISOLATE @ POLE 265D-52// THEN WILL GET MAIN LINE ENERGIZED// CLOSED RECLOSER AT 1411/WR# 29329954/ CREW HAS ARRIVED AT SIGHT AND IS BEGINNING WORK RESTORED POWER AT 16:36// VER/DBM IDCC TOF0958 XXXX
2826 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2015-05-30 14:37 | 2015-05-30 15:14 | 308 | 37 | 4485561 | 11396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER RISER BURNT BASKET INTO PATROLLING LINE, REPLACED HOTTAP AND STIRRUP APR AT 1514 CLOSE TICKET AJB
2827 | Cannonsburg | 3001401 | LOUISA | CITY | 2017-01-14 17:20 | 2017-01-15 04:30 | 17 | 670 | 4298441 | 11390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE ONLY IS OPEN//COD 17//----38830454C24511 BROKE C/O--REPLACED--38830454A41611 40T LAT BLOWN--ON AT 04:30 ALLGOOD--DS011517 // L3/HFP
2828 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-08-31 11:55 | 2014-08-31 14:45 | 67 | 170 | 4440861 | 11390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 172C-206 . CLOSED RECLOSER ON POLE 172C-435 @ 14:25 , CAME BAK OUT , SAW FLASH . FOUND BAD CUTOUT ON POLE 172C-206 , REPLACED CUTOUT , CLOSED RECLOSER BACK @ 14:45 ALL POWER BACK ON .//COD 67// VER/DBM AJB
2829 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-12-10 04:56 | 2012-12-10 16:06 | 17 | 670 | 4455311 | 11390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE HAS BURNT OFF, WILL NEED TO REPLACE. 40 POLE, 2 8 ARMS, 2 SMALL BRACES, 4 DEAD-END UNITS, CUTOUT AND ARRESTOR, T-BRACKET, 2 CLEVIS AND SPOOLS, 2 ARM PINS AND INSULATORS. 7.2 KV. 25 KVA XFMR RELEASED BY CREW 077S02 // CLOSED STEPDOWN @ 1414 TAP TO POLE DAMAGE IS NOT ON MAP IN POWERON /// ISO LF @ 37830204000071 VER/HFP L3/HFP
2830 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-12-11 22:12 | 2008-12-12 15:45 | 19 | 1053 | 57048-1 | 11367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE IS OUT ON POLE 398-8. I AM PATROLLING LINE. I GAVE LINE A SHOT AND IT CAME BACK OUT. I AM BACK TO LOOKING FOR TROUBLE. FOUND A STRING OF INSULATORS BAD AT POLE 398-248. BRUCE LINDON HAS MATERIAL LIST AND WILL BE SENDING CREW //OPENED MAIN FUSE BACK @ 1535 & RESTORED ALL REMAINING CUSTOMERS @ 1545// VER/KEP L3/KEP IDCC FEC40 XXXX
2831 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-06-04 07:22 | 2015-06-04 11:14 | 50 | 232 | 4509261 | 11366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE IS NOT BLOWN ON POLE 38820989A00139, THE A PHASE IS OUT BACK TOWARDS THE RECLOSER ON POLE 38820964B00153, PATROLLING THE LINE. BAD PIN INSULATOR ON POLE 38820989A00131. I WILL NEED TO OPEN THE OTHER TWO PHASES TO REPLACE IT. SWITCHES OPENED ON POLE 38820964C00099 AND TAGGED FOR MATNEY. RECLOSER ON POLE 38820964B00153 OPENED AT 09:49 AND CLOSED BACK IN AT 09:56.RESTORED FINAL CUSTOMERS AT 1114/ L3/DKG SEE H4509261 FOR OPENING AT0949 AND CLOSE AT 0956 AJB
2832 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-01-24 05:06 | 2014-01-24 05:25 | 598 | 19 | H4305521 | 11362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE LOAD SIDE LEAD BURNT OFF TO RECL AT POLE 272-B4-477 (494 CUST)// OPENED RECL POLE 272-B4-477 TO REPAIR LEAD @ 0506 (598 CUST) // ON 0525 // LAST CUST ON @ 0700== RECLOSER STILL CLOSED === OPEN RECLOSER TO MAKER REPAIRS === BOPEN AT 5:05 CLOSED AT 5:25 === POWER OK === ALSO GOT BAD TRANSF ON POLE 37830272A40421 === NEED 1MAN BIG BUCKET AND 50 KVA 7200 === GOT POWER TO TRANSF AT 7:00 ==LOAD SIDE LEAD BURN OFF RECLOSER VER/HFP L3/HFP IDC XXXX
2833 | Pikeville | 3407101 | TOPMOST | DEMA | 2015-11-18 03:06 | 2015-11-18 12:34 | 20 | 568 | 4456211 | 11360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 25T FUSE OUT DUE TO POLE 210-16 BEING BURNT OFF. SOMEONE HAS BEEN DOING SOME DOZER WORK AND CUTING TREES ONE MAY HAVE GOT AGINST POLE. 3 MAN CREW REQUIRED NEED 40-5 POLE 2 CROSS ARMS BRACES 2 PIN INSULATORS ALSO NEED MANUEL ROW CREW TREES WILL NEED TO BE CLEARED AROUND POLE. I HAVE FUSE DOOR TAPED AROUND FUSE POLE 210-12 CREW WILL NEED TO ISO TEST AND PLACE GROUNDS. THIS IS 6A WIRE// VER/ ADH AJB
2834 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-08-18 13:43 | 2012-08-18 14:23 | 284 | 40 | 4949631 | 11360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUESTED OUTAGE TO MAKE UP LOOPS ON ORDER 4948801 BROKE POLE. TR NOT OUT PER HOIS. IDC USED RECLOSER POLE NUMBER AS LOCATION DEVICE XXXX
2835 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2022-09-05 09:23 | 2022-09-05 11:35 | 86 | 132 | 4839121 | 11352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required bad hot tap and basket
2836 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-05-18 18:16 | 2019-05-18 22:21 | 48 | 245 | 4295571 | 11352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | recloser open on pole 196B-190 opened solid blade on pole 196B-274 . closed recloser back at 22:04 hot to pole 274 , closed solid blade on pole 196B-274 @ 22:21. power back on . bad regulator on pole 196B-192, isolated & placed tags for DDC .//AED created//cod 48 L3/HFP
2837 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-04-05 10:45 | 2018-04-05 14:51 | 64 | 246 | 4181481 | 11324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Released by crew 074S11lights at xfmr 44-27 and 26 are flickering ,cust on 26 said refrig. not working correct -both xfmr on ctr phase -looking line over cpr 15:20send to ser truck or crew to check /connection and line volt,reg ? - lights at xfmr 44-27 and 26 are flickering ,cust on 26 said refrig. not working correct -both xfmr on ctr phase -looking line over cpr 16:00 4 4 18 Released by crew 074E05. Need side by side ATV to check.Bad reg. switch will open other 2 reclo. Restored at 14:51 /// PER VOICE RECORDER OPENED RECL ON CENTER PHASE @ 1045 (B PHASE 30 CUST) 04/05 & OTHER 2 PHASES (A&C 34 CUST) @ 1255
2838 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-03-26 13:08 | 2009-03-26 14:15 | 169 | 67 | 61766-1 | 11323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3301402// RECLOSER OPENED UP WHEN BYPASS LEAD BURNT IN TWO DURING MAINTENANCE//COD 169//REPAIRED BYPASS LEAD AFTER RECLOSER HAD BEEN TAKEN DOWN , HOTLINE CLAMP ON POLE WAS BROKEN AND WHEN LOAD WAS APPLIED IT FAILED AND A FLASH OCCUR , RESTORED POWER AT 1415 JEFF COMBS// VER/DBM IDC XXXX
2839 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-06-13 14:21 | 2012-06-13 15:45 | 178 | 84 | 4912111 | 11302 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONN/CLAMP | 2 CC & LOUISA STA REST AT1505....... 460 CC REST AT 1511.....139 CC REST AT 1545 ------------------------ VER/SDB IDC XXXX
2840 | Pikeville | 3408101 | SALISBURY | PRINTER | 2015-04-20 11:32 | 2015-04-20 17:25 | 32 | 353 | 4340651 | 11296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 65T LINE FUSE OUT POLE 1146-D-9 DUE TO BAD CUTOUT AND POLE 1146-D-23 BEING BURNT OFF. CALL ROBIE BLAIRS CREW WILL BE ON THE WAY TO MAKE REPAIRS. CLOSED LINE FUSE IN ON POLE 1146-D-9 AT 17:25 EVERYTHING OK/ ISO 38831146D00009/ COD 32 VER/HFP L3/HFP AJB
2841 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-09-21 16:44 | 2013-09-22 00:55 | 23 | 491 | 4874931 | 11293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 358-211 BROKE AND LOCKED RECLOSURE OUT ON POLE 382-118. WILL NEED 4 MAN LINE CREW, `1 ROW CREW, 40 POLE, POLE TOP PIN AND INSULATOR. REPLACED POLE AND RESTORED POWER AT 0055 IDCC CCU XXXX
2842 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-05-22 21:19 | 2013-05-23 14:25 | 11 | 1026 | 4167001 | 11286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE PATROLING,, FOUND BAD CUTOUT ON POLE 158 171 MANUAL WILL NEED LINE CREW TO CHANGE ,, AND GROUND LINE FOR TREE CREW LARGE PINE ON TELEPHONE PULLING PRIMARY DOWN IN TREES RELEASED BY CREW 077H02ON SITE PATROLING,, FOUND BAD CUTOUT ON POLE 158 171 MANUAL WILL NEED LINE CREW TO CHANGE ,, AND GROUND LINE FOR TREE CREW LARGE PINE ON TELEPHONE PULLING PRIMARY DOWN IN TREES ON SITE WORKING - CAN CLOSE POWER HAD BEEN RESTORED MWL IDC XXXX
2843 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-08-24 17:15 | 2011-08-24 20:20 | 61 | 185 | 4752851 | 11285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSLATOR//COD 61// VER/DBM IDC XXXX
2844 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-02-13 03:14 | 2008-02-13 11:04 | 74 | 470 | 62010-1 | 11274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201///CREW NEEDED POLE TOP BURNT OFF 40/5 12 KV CUTOUT -ARESTER SLACK SPAN DEADEND TRUCKS OK RELEASED BY CREW 078H04 **** CREW WILL BE NEEDED TO REPLACE POLE AT 379-100 *** THIS AM. ** L. RAYBURN WILL HANDLE THIS JOB TODAY.//LAST CUST ON @ 1104// VER/DBM IDC LOOKS LIKE THIS SHOULD BE PH C ONLY CHANGED COUNT FROM 159 XXXX
2845 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-04-21 08:04 | 2011-04-21 10:45 | 70 | 161 | 61589-1 | 11270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 39658426 / LOOP BURNED INTO ON POLE 147-40 AT 10:15 OPENED RECLOSER AT POLE 147-54--ALL BACK ON AT 10:45 VER/KEP IDC XXXX
2846 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-03-26 20:20 | 2010-03-26 22:05 | 199 | 105 | 54809-1 | 11262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34419690 /// OPENED RECLOSER AT 2020 NO OUTAGE TILL THEN. WAITING ON CREW. FAILED CUTOUT VER/KEP L3/KEP IDC XXXX
2847 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-07-22 17:25 | 2011-07-22 19:20 | 304 | 115 | 4582431 | 11260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PER EDDIE MATTNEY POLE 1064-C-6 HAS A BLOWN ARRESTOR - 911 ADDRESS 7630 HWY 1056 @ MCCAR POLE IN BACK YARD // EDDIES CELL 606-371-0766 . HE IS LOOKING OVER THINGS WHILE YOU ARE ENROUTE///RE-FUSED AND RESTORED RELEASED BY CREW 074S06 VER/HFP L3/HFP IDC XXXX
2848 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-02-23 10:20 | 2015-02-23 17:50 | 217 | 450 | 4074761 | 11250 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | CLOSED RECLOSER IN AT 1110//ISO AT PRIM POLE 39831124A20578//CSX PRI METER 1124 A2 578 REMOVED HOT TAPS OPENED COS AND GROUNDED CSX SIDE FOR XMISSION. PLACED TAGS TO KYDDCCSX PRI METER 1124 A2 578 REMOVED HOT TAPS OPENED COS AND GROUNDED CSX SIDE FOR XMISSION. PLACED TAGS TO KYDDC RELEASED BY CREW 078S07//TRANSMISSION POLE FELL BECAUSE OF INSULATER FAILURE //CLOSED OPEN PT AT 1750 VER/CRB L3/HFP XXX AJB
2849 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-12-03 14:57 | 2020-12-03 16:33 | 117 | 96 | 4742991 | 11232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | POLE 1089-86,RECLR RISER HAS COME OF STIRRUP.STIRRUP ALSO HAS BURNED INTO WHERE HOTTAP SITS ON IT.
2850 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-03-21 08:33 | 2018-03-21 13:24 | 43 | 291 | 4034691 | 11229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole burnt off on pole 38830851D20685 // isolated on pole 851-215 an tagged to tim thomas// closed 851-360 at 0950 //pole burnt off on pole 851-685 //isolated on pole 851-215 an tagged to tim thomas// closed 851-360 at 0950 // Released by crew 076H04. replaced tim thomas tag to Tommy Goble. placed a cutout on pole 851-655 with a 25T so we can pick load up /// SEE 4036521 CUST NOT RESTORED IN THIS ORDER DUE TO HOT LINE TAP BURNT IN CLEAR // ALL RESTORED @ 1324 // 6 CUSTOMERS INTERRUPTED IN ORDER 4036521 FROM 1250 TO 1324
2851 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-05-20 00:20 | 2017-05-20 06:00 | 33 | 340 | 4824601 | 11220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON POLE 263-04////WILL PATROL.BAD 19.9 DEADEND INSULATOR ON POLE 263-04 WILL MAKE REPAIRS.REPAIRS MADE.RESTORED. AJB
2852 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2014-07-27 03:09 | 2014-07-27 05:05 | 102 | 116 | 4291501 | 11212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE ONLY OPEN//COD 102//50T LINE FUSE POLE 69 A3 1003 RESTORED @ 04:45, HOT TAP FIXED POLE 69 C1 4001 RESTORED @ 05:05 MP RELEASED BY CREW 078H12// VER/DBM AJB
2853 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-03-25 12:34 | 2010-03-25 14:32 | 95 | 118 | 54353-1 | 11210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS BAD CUTOUT ON TRANSFORMER DOES NOT SERV ANYTHING. GOING TO TAKE OUT LINE/VER/CRB IDC XXXX
2854 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-05-06 19:16 | 2010-05-06 19:24 | 1401 | 8 | H56709-1 | 11208 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | SWITCHING TO RESTORE STINNETT STATION NORMAL SOS 1617 REV91 .. OPENED AT 1916. CLOSED AT 1924 VER/PDP IDC XXXX
2855 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-12-06 01:09 | 2018-12-06 08:20 | 26 | 431 | 4511291 | 11206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | low ambient temperatures// line burned down at pole 401-35 . will need two or three linemen to put wire back up Released by crew 077S12 power restored at 08:20
2856 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-02-09 14:14 | 2021-02-09 16:54 | 70 | 160 | 4952311 | 11200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | insulator bad on pole 381-A-2.. wire burnt down from 381-A-2 to pole 381-A-3.. #4 copper. Line crew and flaggers needed.. power restored @ 16:54
2857 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-06-25 00:11 | 2019-06-25 11:51 | 16 | 700 | 4588321 | 11200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Line fuse out on 1084A/244 wire down at 1084A/99 NO GROUNDS NO TAGS NEED LINE CREW ROW CREW #2 acsr//Unknown cause at this time, could not find fallen tree... may have burnt in two, ROW is grown up pretty bad// restored 1151
2858 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2020-12-26 08:46 | 2020-12-26 09:23 | 302 | 37 | 4822981 | 11164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | DA Scheme // DOL1078654 // continuation of 4822211 // DA RECL 296-D1-1616 locked back out at 0846 // servicer saw flash at primary metering //will isolate and try again // cod 495 // Released by crew 077H20
2859 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2017-02-28 15:58 | 2017-02-28 19:00 | 102 | 182 | 4429271 | 11164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED REC IN @ 1746//POLE FIRE @ 38820967A00148 ISO @ POLE 38820967A00147CUTOUT FAILED ON 967A148 TAKING OUT RECLOSER ON 991D266 I ISOLATED TROUBLE AT 967A147 AND RESTORED RECLOSER AT 17:46MADE REPAIRS ON 967A148 RESTORED POWER AT 967A147 AT 19;00 POLE NEEDS TO BE REPLACED/SEND TO TECH./SENT AWD VER/AWD AJB
2860 | Hazard | 3303901 | LESLIE | HYDEN | 2020-08-18 21:55 | 2020-08-19 10:36 | 43 | 761 | 4344881 | 11163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | isolated broke cutout on pole 388d-485 restored main line at 12:20,talked to Rick Maggard will hold till daylight , 19.9 cutout, will need row crew to cutout around pole// 34 cust restored @ 0020 // 1 cust remains on pole 388-D-485 // MD filed //OPENED LINE FUSE ON POLE 37830388D10485 TO MAKE REPAIRES OFF@1015 ON@1036isolated broke cutout on pole 388d-485 restored main line at 12:20,talked to Rick Maggard will hold till daylight , 19.9 cutout, will need row crew to cutout around pole// 34 c
2861 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-10-01 00:02 | 2016-10-01 02:30 | 76 | 148 | 4951671 | 11158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A CUTOUT WITH A SOLID BLADE BURNED UP ,I BYPASSED IT ON POLE 427-239///TOP CLAMP BURNED OFF SOLID BLADE AT POLE 37830427A00239-WAS TEMPORARILY REPAIRED AT 0215 AND RECLOSER AT 37830427A00030 WAS CLOSED AT 0230--CREATED AED TO HAVE SWITCH REPAIRED/// VER/DKM // VER REPAIRS PER VOICE RECORDER & TIMES = L3/HFP HFPC CNT81 AJB
2862 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-11-15 11:52 | 2020-11-15 18:07 | 97 | 375 | 4680611 | 11144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | POLE6-102,BPHASE RECLR IS OUT//////ALSO LINEF@3-19 IS OUT.////3PHASE LOOKS CLEAR,WILL TRY RECLR//////RECLR OPENED//////POLE3-31,COND LAYING ON THE ARM.AZ ENROUTE TO HELP. Opened reclosers @ 17:12 to unwrap phases//Unwraped phases on pole30-69 ///Closed reclosers in @ 17:37 up to 30-19///Closed 25Tline fuse in @ 17:50 on pole 30-19 on the 3 phase///Removed vine from pole 30-153 up in cane branch///Refused line fuse @ 18:07 on 30-19 and restored customers up in Cane Branc Released by crew 074S02
2863 | Whitesburg | 3309302 | VICCO | JEFF | 2014-04-15 10:05 | 2014-04-16 15:36 | 25 | 1771 | 4606171 | 11136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSER OUT ON POLE 396-89,OPENED FUSE ON POLE 395-84 TO ISOLATE , CLOSED RECLOSER IN AT 13:55 RESTORING UP TO POLE 395-84.CUT DEADENDS ON POLE 419-216 TO ISOLATE CLOSED LINE FUSE IN AT 18:11 .WILL NEED CREW & R/WAY CREW WITH 6 WHEELER TO PATROLL LINE TOMORROW . // FOUND CONDUCTOR THAT WAS FRAYED // COD-25 ISO OCR 37830396000089 VER/HFP L3/HFP IDC XXXX
2864 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2013-09-21 09:37 | 2013-09-21 15:25 | 32 | 348 | 4872481 | 11136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE OUT ON STEPDOWN, CHECKING XMF, BAD 250KV STEPDOWN XMF. BESIDE ROAD. LINECREW REQUIRED. TAGGED TO DDC. RELEASED BY CREW 078S11 VER/CRB L/3 CRB IDC XXXX
2865 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-03-08 09:06 | 2008-03-08 14:24 | 35 | 318 | 54913-1 | 11130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311401//RECLOSER IS LOCKED OUT. PATROLLING LINE. BROKEN CUTOUT HAS BURNED TOP OF POLE OFF AT POLE 328-11. I HAVE A FLAGGING CREW ON THE WAY AND I HAVE CALLED FOR ONE LINEMAN WITH BIG BUCKET//COD 35/// VER/DBM IDC XXXX
2866 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-08-04 09:36 | 2017-08-04 10:28 | 214 | 52 | H4222851 | 11128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID BLADE 300 AMP C/O BAD ON C PHASE @72-A-78, WILL HAVE TO OPEN ALL 3 REC. @72-A-80 TO MAKE REPAIRS, ALSO NEED A MANUAL R.O.W. CREW TO CUT UP TO POLE, NO TRUCK ACCESS. OPENED ALL 3 REC. @0936, MADE REPAIRS AND CLOSED BACK IN @1028. C COD 75/AB COD 214 37830072A00080 VER/AWD SJG
2867 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-04-28 14:33 | 2011-04-28 16:20 | 104 | 107 | 51703-1 | 11128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | "A " REG FAILED. SERVICER OPENED RECL AT1555 TO ISOLATE REGS.// RELEASED BY CREW 074S02 COD-104 TILL 1555 WHEN RECLOSER WAS OPENED COD-290 CLOSED AT 1620 RESTORED ALL CUSTOMERS/ REGS ARE TAGGED AND BYPASSED VER/KEP IDC XXXX
2868 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2017-06-22 13:41 | 2017-06-22 16:00 | 80 | 139 | 4015081 | 11120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE TOP INSULATOR BAD 37830371000002 === NEED LINE CREW ==== REPLACED INSULATER AND BAD CUTOUT === CLOSED RECLOSER POWER OK VER/CRB SJG
2869 | Hazard | 3309901 | SLEMP | DEFEATED CREEK | 2014-10-14 16:30 | 2014-10-16 14:49 | 4 | 2779 | 4624611 | 11116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SERVICER CHECKED CB STATUS //LOCKED OUT// ISOLATED CB// RESIDENTIAL CUSTOMERS WERE PREVIOUSLY TRANSFERRED WHILE WORKING SOS 2805 REV 11// AED UPDATED// NO OPERATING ORDER ISSUED//ALL NOTIFIED HOLD ORDER REQUIRED PRIOR TO BEGINNING WORK//TOM // FOUND BROKEN CROSS ARM// WILL REPAIR ON 10/16/2014// OPENED LOOPS ON P#539/98 WILL CHANGE STRUCTURE LATER RELEASED BY CREW 077H03// VER/TOM L3/TOM L3/HFP AJB
2870 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2022-07-26 12:02 | 2022-07-26 12:52 | 222 | 50 | 4584111 | 11100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | HOLD ORDER // DOL 1225409 // opened CB via SCADA at 1202 due to SW on fire at pole 38820771B30856 // crews on site to replace switch // cod 222 // (unplanned outage)//closed@ 1252
2871 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2018-04-23 18:01 | 2018-04-24 12:30 | 10 | 1109 | 4268301 | 11090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | KYDDC TAGS recloser open on pole 400-331,pole 400-104 rotted off at ground level wind blew it over..isolated recloser on pole 400-331 & placed tag for DDC..hold for crew tomorrow. //0744 gave g whitaker permission to to take control of tags & grnds// Released by crew 077S11
2872 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-11-29 17:08 | 2011-11-30 00:50 | 24 | 462 | 4127951 | 11088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PRC CREW REQUIRED--NEED TECH--333 KVA STEPDOWN IS BAD ,TRUCK TO POLE--GROUNDS CAUGHT FIRE AND BURNED POLE--POLE 38830116B00737 NEEDS REPLACED RELEASED BY CREW 078S07. --- SDB / 0050 / ALL CUST RESTORED. CC 24. VER/SDB IDC XXXX
2873 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-03-02 20:13 | 2010-03-02 23:59 | 49 | 226 | 62389-1 | 11074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAVE A TOP OF POLE BURNT OFF ON POLE 38831125D00760 IT HAS THE LINE FUSE OPENED AT POLE 38831125D00063 50T IN PROCESS OF GROUNDING LINE./// RESTORED POWER AT 11:59. TIM MCCOY RELEASED BY CREW 074H10 VER/PDP IDCC TON0000 XXXX
2874 | Hazard | 3308001 | JACKSON | S.JACKSON | 2020-03-24 20:24 | 2020-03-24 21:13 | 226 | 49 | 4507041 | 11074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ACTUAL CTR PH OUT ON 38831108B00029 A/143;C/200/C/183/AC 10/BC 21/3PH 5
2875 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2022-01-16 13:59 | 2022-01-16 17:30 | 63 | 211 | 4351411 | 11043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | POLE 27-86 ABT 4FT BURNED OFF,NEED CREW,POLE TOP PIN OR XARM TO EXTEND IT UPWARDS A LITTLE.ACCESS TIGHT BUT CAN BE DONE///////fuse in @1600 /MADE REPAIRS&RESTORED@17:30
2876 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-08-14 15:47 | 2013-08-14 18:00 | 83 | 133 | 4665791 | 11039 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REC. OPEN AT POLE 380-53, FOUND BAD LIGHTNING ARRESTOR AT POLE 357-39, WILL BE CHANGING. CLOSED REC. BACK IN AT 1800. VER/SEF L3/HFP XXX
2877 | South Williamson | 3411401 | DEWEY | INEZ | 2018-07-21 19:03 | 2018-07-21 19:46 | 306 | 43 | 4830401 | 11037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cut 38820745D00003 lifted hot tap closed DA Recl at 1940/xfmer closed at 1946cutout broke on 745-3///repairs made// Released by crew 079S01 L3/HFP
2878 | Hazard | 3302703 | HAZARD | HAZARD | 2015-03-16 14:05 | 2015-03-16 17:08 | 125 | 183 | 4198351 | 11017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SEC. POLE IN SLIDE , TRANSFORMER POLE ROTTEN E.PRATT WILL BE WORKING ON THIS RELEASED BY CREW 077S04// @ 1414// OPENED REC. ON 37830296A30746 @ 14:05, CLOSED REC. AT 15:30 RESTORED ALL BUT 37830296C10591/RESTORED FINAL CUSTOMERS 1708/COD125(121+4)// VER/ ADH L3/DKGXXXX AJB INLT CAUSE WAS FLOOD BUT THEN TOOK OUTAGE TO REPLACE CALL.
2879 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-07-21 16:11 | 2015-07-21 18:34 | 77 | 143 | 4927781 | 11011 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER IS OPEN ON 235-90 PATROLLING, FOUND & REPLACED BAD ARRESTER ON 258-91 VER/CRB AJB
2880 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-11-18 18:40 | 2008-11-18 21:32 | 64 | 172 | 66346-1 | 11008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3002105// FOUND SPAN OF HENDRIX DOWN AND WILL HAVE OPEN SWITCHES @ POLE 38830045C45784 @ 2059// THIS INTERRUPTED 24 ADDITIONAL CUSTOMERS// CLOSED SWITCHES BACK IN @ 2132 ALL POWER RESTORED// INITIAL OUTAGE WAS B PHASE TOTAL 86// RELEASED BY CREW 078S07 MLRC CDC 92 IDC XXXX
2881 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-04-14 12:12 | 2015-04-14 16:35 | 49 | 263 | 4316881 | 11002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE OUT/PARTROLLING NOW//COD 49//XARMS BURNT ON POLE 954-C-683, LOAD BUSTING SWITCHES ON POLE 954-A4-908//INTERRUPTED 28 ADDTL CUSTOMERS//OPENED SWITCHES 954 908 AT.13.50..CLOSED REC OFF AT 14.10.TOOK REC OFF AT 16.21 BACK ON AT 16..35. RELEASED BY CREW 076S01/ FIX IT IN HOIS// VER/ ADH AJB
2882 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-04-03 11:57 | 2015-04-03 15:51 | 47 | 234 | 4264301 | 10998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT POLE 117 D1 19..CREW REGD ,BIG BUCKET. RELEASED BY CREW 078S07/CREW ON SITE/FETR1630/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1551/PLEASE CLOSE TICKET/THANKS/VEM//COD 47 L3/DKGXXXX AJB
2883 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-05-20 14:10 | 2008-05-20 15:43 | 118 | 93 | 66481-1 | 10974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801/// CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE POLE ON US 60 NEAR TRUMBO ROAD/ VER/TOM IDC XXXX
2884 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2011-04-12 15:27 | 2011-04-12 18:50 | 54 | 203 | 55937-1 | 10962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 39541783 // RECLOSER ON POLE 197-98 IS OPENED. WITH BACK TO STATION THE LEFT HAND RECLOSER IS OUT. THE OTHER 2 IS IN. INSULATOR ON POLE 197-17 LOOKS LIKE IT HAS BROKEN DOWN AND POLE AND CROSSARM IS SMOKING AT TIMES. DENNIS IS BRINGING HELP TO CHANGE INSULATORS. WE WILL HAVE TO OPEN RECLOSERS AT POLE 197-98 WHEN CREW ARRIVES FOR ABOUT 45 MINUTES. I OPENED THE OTHER 2 RECLOSERS AT 18:25 SO WORK COULD BE DONE. WE FIXED PROBLEM AND CLOSED ALL 3 RECLOSERS IN AT 1850 ******_(&*_)(&*_)(*
2885 | Hazard | 3310502 | HADDIX | CANOE | 2021-12-22 17:12 | 2021-12-22 19:05 | 97 | 113 | 4221071 | 10961 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | hot line clamp and sturrip burnt off on low side stepdown
2886 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-07-08 16:44 | 2012-07-09 11:00 | 10 | 1096 | 4609251 | 10960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CREW REQ. PRIMARY DOWN AT 38830161000008, TRUCK OK RELEASED BY CREW 078S05//PER STEVI COBURN, BOB REYNOLDS STATES THIS HAS BEEN COMPLETED//COD 10
2887 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-10-16 07:34 | 2021-10-16 12:29 | 41 | 295 | 4354871 | 10934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | We have Line fuse open at 1035-191(ASSESSING CONDITION)Restored fuse on 1035-191 at 10:20,Fuse on 1059-17 Open..Restored fuse on 1035-191 at 10:20,Fuse on 1059-17 Open..,Rick Ray is with me to help make repairs.Restored Line fuse on 1059-17 at 12:29. Released by crew 074S01
2888 | Hazard | 3420001 | SOFT SHELL | VEST | 2013-01-07 05:18 | 2013-01-07 10:25 | 91 | 307 | 4573751 | 10927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, MAIN LINE BACK ON AT 07:16 AM BUT FOUND BROKE CUTOUT ON POLE 107-4 STILL HAVING 1 CUST OUT RESTORED 1025 VER/KEP IDCC CDC83 XXXX
2889 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2019-12-26 01:16 | 2019-12-26 02:12 | 195 | 56 | 4181871 | 10920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 425-50 , we isolated at pole425-47we closed switches back in at 02:12on pole 425-47 Released by crew 077S12 Outage to isolate failed equipment CB C open @ 0116 CB C closed @ 0118
2890 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-02-19 20:53 | 2015-02-20 02:54 | 1464 | 361 | 4044861 | 10914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED SHELBY 34KV CB A VIA SVC AT FIELD REQUEST DUE TO 3 PHASE POLE FIRE// ARCOS`D SERVICER// OPENED CB @ 2053 RESTORED @ 2059 VER/TOM L3/TOM L3/HFP HFPC FP AJB
2891 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-08-29 12:09 | 2008-08-29 16:17 | 44 | 248 | 57310-1 | 10912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP 3400301// UNKNOWN ONLY A PHASE OUT COD- 44 CUSTOMERS.3400301// UNKNOWN, CSP TRANSFORMER ARRESTOR, RECLOSER POLE 93-283 IDCC PN282 XXXX
2892 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-04-04 10:47 | 2014-04-04 14:34 | 48 | 227 | 4572911 | 10896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HI -SIDE CUTOUT BROKE HER @ 1102-702 WILL CHANGE. CLOSED STEP-DOWN IN ON POLE#1102-702 @14:28. CLOSED RECLOSER IN ON POLE#1101-D-182 @14:34 AND IT STAYED RELEASED BY CREW 074H17//COD 48// VER/DBM IDC XXXX
2893 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-12-02 14:50 | 2012-12-02 20:20 | 33 | 330 | 4436731 | 10890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF JUST ABOVE TRANSFORMER, NEED 3 MEN AND 25 KVA TRANSFORMER CUTOUT AND ARRESTOR AND TEE BRACKET, 45 CL. 4 POLE, TRUCK ACCESS. ///VER/CRB L/3 CRB IDC XXXX
2894 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-02-23 17:11 | 2014-02-23 18:08 | 191 | 57 | 4428901 | 10887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE SOLID BLADE IS OPEN//COD 191//BAD CUT OUT ON B PHASE ON POLE 204-1BAD CUT OUT ON B PHASE ON POLE 204-1 CLOSED SOLIDBLADE ON POLE 204-1 @ 18:08//COD 191// VER/DBM IDCC TOF1037, CDC86 XXXX
2895 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-02-16 00:08 | 2018-02-16 01:05 | 191 | 57 | 4846901 | 10887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 804388// related to 4845981//opened SWS 37830171000272 (all 3 ph) in order to repair failed B ph insulator on cap bank pole 37830171000188//cod 191//
2896 | South Williamson | 3411401 | DEWEY | INEZ | 2018-10-30 11:00 | 2018-10-30 12:20 | 136 | 80 | 4342281 | 10880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE POLE /// COD-136 ISO PO@ 38830696C00020 OFF@ ON@//opened at 11:00//closed at12:20//complete//em
2897 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2010-07-25 20:44 | 2010-07-25 23:00 | 80 | 136 | 57078-1 | 10880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 079H08 A & B PHASES ONLY 73 CUSTOMERS VER/ARN IDCC CNT73 XXXX
2898 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-02-01 23:41 | 2018-02-02 12:43 | 57 | 782 | 4791781 | 10878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 57 customers///DDC HOLD TAG/// pole 1072-5744, 355 pole, top of pole burnted off, well need l/c to make rep, have breaker cut in pri at pole 1072-5607, tagged and grd at this point to DDC, Material all should work back, new c/o and l/a, and new pole, , had B PHASE rec open when i arrived, after cut breaker in pri, i restored rec, at 1355, all cus t back on but 5, where pole is burnted off, @ 1011 gave v mullins perm to rem kyddc tags/
2899 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-09-03 14:38 | 2010-09-03 16:40 | 89 | 122 | 63283-1 | 10858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | MOVED ARRESTOR LEAD, 454-6528 RELEASED BY CREW 078H12//COD 89// VER/DBM IDC XXXX
2900 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2020-05-24 16:34 | 2020-05-24 18:48 | 81 | 134 | 4897271 | 10854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrester on CSP Xfm broke down on pole 37830212A00245. cut in clear and restored @ 18:48
2901 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-12-16 09:44 | 2014-12-16 13:30 | 48 | 226 | 4863931 | 10848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRIED REC. CAME BACK OUT PAT. AGAIN B. FRALEY IN ROUTE FINALLY FOUND BAD ARRESTER ON P 219 PWR RESTORED AT 13:30 PLEASE CLOSE TICKET COD-48 ISO OCR 38830165A00228 VER/HFP L3/HFP AJB
2902 | Hazard | 3302703 | HAZARD | HAZARD | 2022-03-15 17:49 | 2022-03-16 10:15 | 11 | 986 | 4629371 | 10846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer, in transformer bank that serves old Fualkner building on main st. bad 100 kva 7200 xfmr 120/240v additive pol. 2 bushing. no stock in Hazard. Aaron from Ashland storeroom will have one in Hazard Wed. morn at 7:00 am Released by crew 077H09.replaced xfmr.CCW// RESTORED @1015
2903 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2022-06-26 18:49 | 2022-06-26 22:50 | 45 | 241 | 4326401 | 10845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrestor on 38830331000028, repairs made, power restored at 2250
2904 | Hazard | 3310502 | HADDIX | CANOE | 2013-06-09 16:27 | 2013-06-10 10:30 | 10 | 1083 | 4243101 | 10830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE LOTS OF VINES FUSE OUT ,, BAD CUTOUT ,,CREW REQUIRED BUCKET POSSIBLE ,,COVER UP REQUIRED ,,IF NOT WILL REQUIRE OUTAGE ON LINE FUSE RELEASED BY CREW 077H02 REPLACED CUTOUT AND REMOVED VINES, RESTORING POWER AT 1030//COD 10//ISO 37830074000001// VER/DBM IDCC PN1 XXXX
2905 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-05-02 21:12 | 2009-05-02 23:11 | 91 | 119 | 63560-1 | 10829 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1064-112, TAP DONT SERVICE ANYBODY GOING TO CUT PRIMARY IN CLEAR AND PUT RECLOSER ON VER/ARN IDC XXXX
2906 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-05-02 18:42 | 2016-05-03 00:10 | 96 | 328 | 4164091 | 10808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RECLOSER OPEN ON POLE 424-51, BAD CSP XFMR ON POLE 424-239 ISOLATED XFMR.. NEEDS: NE, 2 A, 1 B-D.CLOSED RECLOSER IN AT 20:30 ON POLE 37830424B42204 (94 CUST)..POWER RESTORED AT 00:10 37830424000239 (2 CUST)/ VER/BOW AJB
2907 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-06-26 04:04 | 2009-06-26 05:19 | 144 | 75 | 61415-1 | 10800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER WILL CHANGE WHEN LIGHTING LETS UP POWER RESTORED VER/ARN
2908 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2018-10-11 13:25 | 2018-10-11 15:41 | 597 | 136 | 4221401 | 10798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole Fire at pole 38830045A31099/ Opened Station Breaker so fire dept can spray pole/ ISO 3002103/ COD 597 send to r.virgin Released by crew 078S07--crew on site--G&T to RMV @ 45-1099--fetr 15:41--replaced arms and cutouts---tbl tkt comp---rmv // TIMES PER SCADA & DOL Case #: 866857 L3/HFP
2909 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-03-31 15:28 | 2015-03-31 18:25 | 61 | 177 | 4249511 | 10797 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BACK TO STATION C & B RECLOSERS ARE OPEN ( 61 CUSTOMERS)///WIRE DOWN BETWEEN POLE 852-48 AND 852-49///OPENED A PHASE REC @ 17:30 AND OPENED ALL 3 LOAD SIDE DISCONNECTS SWITCHES AND PLACED TAG FOR ROBIE BLAIR///CLOSED RECLOSURES ON 852-409 @ 18:25///COMPLETE BR COD-96 SEE DUP H4249511 FOR A PHASE OUTAGE 35 CUST VER/HFP L3/HFP AJB CCTOR PER TROUBLEMAN
2910 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2013-10-06 14:05 | 2013-10-06 20:50 | 27 | 405 | 4914991 | 10795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SLEEVE PULLED OUT AND FAULT CURRENT BURNED DOWN ANOTHER SPAN OF WIRE ON 1116-1. OPENED SW ON 1140-3 TO ISOLATE DOWNED WIRE AND CLOSED RECLOSER ON 1140-71 @ 18:30. COMPLETED REPAIRS AND CLOSED SW ON 1140-3 @ 20:50 RESTORING REMAINING OUTAGED CUSTOMERS. SH COD-27 ISO OCR 38831140C40071 NOTE: RECL CONSIDERED FEEDER BREAKER ON THIS CKT VER/HFP L3/HFP IDC XXXX
2911 | Hazard | 3302703 | HAZARD | HAZARD | 2013-01-17 14:34 | 2013-01-17 15:16 | 257 | 42 | 4615991 | 10794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TO REPLACE FAILED SQUEEZE ON CONNECTION.. VER/TOM L3/TOM IDC XXXX
2912 | Pikeville | 3402003 | KEYSER | MULLINS | 2021-10-14 23:41 | 2021-10-15 02:03 | 76 | 142 | 4351481 | 10792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B phase loop burned in 2 at pole 1127-B-324, will have to open up 3 phase at pole 1127-B-222 and ground line to safely make repairs// opened 3 phase at 1127-B-222@01:04// closed@ 02:03
2913 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2015-03-04 06:23 | 2015-03-04 07:50 | 210 | 87 | 4096441 | 10782 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED THE MT. STERLING 34KV CB R LOCKED OUT // INTEERUPTING 232 CC// BROKEN CUTOUT FOUND @ POLE 771-D-313// SHOULD BE ABLE TO CLEAR AND WILL CLOSE BY CB // CLOSED STATION CB @ 0714 // 2 CC REMAIN OUT WHILE REPAIRS ARE MADE//CUTOUT CHANGED RESTORED REMAINING CUST. AT 7:50// TIMES PER SCADA & DISPATCH LOG VER/HFP L3/HFP AJB
2914 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-07-22 15:50 | 2014-07-22 19:30 | 49 | 220 | 4273471 | 10780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED RECLOSER ON POLE 38830141D00393 @ 1550 TO ISOLATE STEPDOWN // TACKETT & SIMMONS & GRIFFITH & HOWARDOPENED RECLOSER ON POLE 38830141D00393 @ 1550 TO ISOLATE STEPDOWN // RELEASED BY CREW 078S01,,CREW ON SITEOPENED RECLOSER ON POLE 38830141D00393 @ 1550 TO ISOLATE STEPDOWN // RELEASED BY CREW 078S01,,CREW ON SITE,, XFMR CHANGED,, REC CLOSED AT 19:30,,ALL POWER RESTORED RELEASED BY CREW 078H03. VER/CRB IDCC PN391 XXXX AJB
2915 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-06-14 04:05 | 2018-06-14 13:50 | 27 | 585 | 4599891 | 10770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.///line fuse blown on pole 168-6////will patrol...broke cutout on pole 168-26.will make repairs..closed fuse in and came back out..trees into pri. between poles 168-146 to pole 168-147.lifted hot tap on pole 168-21 to isolate.grounded and tagged to myself..will need row crew with small bucket to cut in clear./ 37830168000006 in @ 1029 (25cc)/ 37830168000021 in @ 1350 (2cc)
2916 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-01-08 03:14 | 2015-01-08 06:49 | 50 | 215 | 4917031 | 10750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | /ONE SPAN OF PRIMARY AND NEUTRAL IS DOWN. CAN USE BUCKET.ONE SPAN OF #4 COPPER PRIMARY AND NEUTRAL IS DOWN. CAN USE BUCKET.ONE SPAN OF #4 COPPER PRIMARY AND NEUTRAL IS DOWN. CAN USE BUCKET. POWER IS BACK ON. VER/TOM L3/TOM AJB
2917 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-05-12 02:26 | 2016-05-12 14:22 | 15 | 716 | 4204011 | 10740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ 472-27 LIFTED HOT TAP NEED LINE CREW TO REPLACE NO TRUCK,TREES IN LINE NEED 2 MANUAL TREE CREWS TO CUT FROM 471-24 TO 471-8 & POLE 471-3 RELEASED BY CREW 078S05 , WIRE DOWN BETWEEN 471-7 & 471-6. POWER RESTORED AT 14:22./ ISO 38830472000010/ COD 15/ VER/BOW
2918 | Pikeville | 3421002 | BREAKS | GRASSY | 2008-05-11 16:42 | 2008-05-11 19:44 | 59 | 182 | 61590-1 | 10738 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 642 ** ELKHORN CITY 69-12 KV TR 1 STATION OUTAGE. LITTLE GRASSY AND CITY 12K FEEDERS OUT.STATION SERVICER AND DENNIS MASSEY ENROUTE. VER/ARN MAFC CNT297, CCWL, CHANGED OUT SUBSTATION TRANS CUTOUT.
2919 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-04-02 15:45 | 2018-04-02 19:09 | 57 | 204 | 4165951 | 10728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on pole 37830215A00394 and burnt pole off @ bottom of cutout////lifted hot tap on pole 215-305 to isolate trouble...should be able to frame down will need 7200 cutout and bracket and fiber glass pole top extension to make repairs...//CLOSED STEP-DOWN @ 1639//cutout failed on pole 215-394 and burnt pole off @ bottom of cutout////lifted hot tap on pole 37830215A00305 to isolate trouble...should be able to frame down will need 7200 cutout and bracket and fiber glass pole top extension
2920 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-08-22 21:24 | 2012-08-23 02:30 | 35 | 306 | 4963811 | 10710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LOW SIDE STEPDOWN FUSE OUT ON POLE 37830215D00122 R/W IS GROWN UP @ POLE 37830239000265 ALL I COULD SEE WRONG IS BAD R/W IN A COUPLE OF LOCATIONS GOING TO TRY FUSE FUSE CAME BACK OUT @ 22:35 ISOLATED BAD ARRESTOR ON CSP XFMR, GOING TO REFUSE ALL POWER RESTORED @ 02:30 CC 35 IDC XXXX
2921 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-11-24 22:08 | 2008-11-25 11:37 | 203 | 809 | 51891-1 | 10707 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002001//RELATED TO ORDER 51836-1//SERVICER OPENED LINE IN ORDER TO ISOLATE POLE THAT HAS BURNT OFF//COD 203//FOUND A 405 POLE ALMOST BURNTED INTO, I HAD TO OPEN 300 AMP SOLID BLADE ON POLE 926-34, AT 2200, IN ORDER TO PUT OUT FIRE ON POLE 925-7, WAS CAUSED BY BAD CUTOUT OUT, THIS POLE IS LOC AT THE MOUTH OF ANDERSON CEMENTRY ROAD, THIRD PLACE ON RIGHT AFT, SINGLE POLE TAP COMING FROM POLE 926-7 IS STILL OUT//REST WAS BACK ON AT 2257//CREW REQUIRED////VER/CRB MLR OK IDCC CDC83 XXXX
2922 | South Williamson | 3200302 | BELFRY | TOLER | 2011-08-07 22:25 | 2011-08-08 00:05 | 107 | 100 | 4676881 | 10700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PREDICTED DEVICE NOT OUT..RECLOSER IS OPEN ON PHASE A (112 CUSTOMERS ON RECLOSER ) ON 1039A17.BURNT UP DOOR ON XFMR CUTOUT ON 1039A21 WHERE HAZRD CALL WAS..REST OF LINE LOOKS OK..//.CLOSED RECLOSER ON 1039A17 @ 00:05..JRV.08/08/11 VER/KEP IDC CHANGED START TIME FROM 2138 APPEARS ONLY ONE TRANSFOMRE OUT INITIALLY XXXX
2923 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-04-21 06:44 | 2010-04-21 09:55 | 56 | 191 | 65831-1 | 10696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T LINE FUSE OUT AND 6T TRANSFORMER FUSE OUT DUE TO BAD CUTOUT. ROW NEEDS CUT BAD SEND COPY TO COREY FARMER ROW PIKEVILLE. FROM FUSE POLE TO THE END OF LINE.//VER/CRB IDCC PH B ONLY CNT97 XXXX
2924 | Hazard | 3310502 | HADDIX | CANOE | 2013-02-12 15:00 | 2013-02-12 15:09 | 1188 | 9 | 4814321 | 10692 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TO MAKE ADJUSTMENTS ON MOBILE TRANSFORMER OFF @ 1500 ON @ 1509 VER/ARN IDCC CCSCO XXXX
2925 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-02-03 12:20 | 2008-02-03 13:32 | 223 | 72 | 65883-1 | 10680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201// LOAD BUSTED RECLOSER @ 428-296 TRIED PICKING UP HOT TAP AND THEN CLOSING IN RECLOSER// ENDED UP TAKING THE RECLOSER UPSTREAM POLE 306 OUT// PUT BYPASS IN RECLOSER A PHASE ON POLE 306 - PICKED UP TO RECLOSER POLE ON 296// PUT RECLOSER ON 306 IN ABNORMAL// WHEN CLOSE IN SERVICER FOUND BAD CUTOUT AND LA ON POLE 428-170// WILL CHANGE ALL BACK ON @ 1332 IDC XXXX
2926 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-11-14 16:02 | 2008-11-14 16:09 | 1523 | 7 | 64916-1 | 10661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP EMERGENCY OUTAGE TO REPLACE BROKEN CROSSARM RESTORED @ 1609 IDC XXXX
2927 | Hazard | 3310502 | HADDIX | CANOE | 2014-09-17 18:52 | 2014-09-17 19:57 | 164 | 65 | H4507001 | 10660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 1821 OPENED DA SW ON POLE 121-152 TO ALLOW CREW TO SAFELY REPLACE BROKEN CROSS ARM // 1822 SW 169-D-305 CLOSED REST ALL 277 CUST // 1852 OPENED SW 97-11 INTERRUPTING 164 CUST// 1957 @ 97-11 CLOSED SW REST 164 CUST// DUPLICATE OF RECORD 4507001 FOR WHEN SW OPENED @ 97-11 VER/HFP L3/HFP AJB
2928 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2015-11-12 13:06 | 2015-11-12 14:59 | 94 | 113 | 4435201 | 10622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFOMER CUTOUT BROKEN ON POLE 796-B-212. DOESNT FEED ANYTHING.. ISOLATED CUTOUT.. RESTORED AT 14:59 VER/CRB L3/HFP HFPC PN38820796B40236A AJB
2929 | Whitesburg | 3309302 | VICCO | JEFF | 2017-08-15 06:16 | 2017-08-15 07:43 | 122 | 87 | 4260611 | 10614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830348B00074 TOOK MAIN LINE OUT GOT MAIN LINE ON AT 7:43 === NEED CREW TO CHANGE CUTOUT MANUAL === RELEASED BY CREW 077S03 REPAIRS MADE AND POWER RESTORED AT 1027 VER/KEP SJG
2930 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-03-23 17:00 | 2011-03-23 20:20 | 53 | 200 | 57235-1 | 10600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT ON POLE 262-34, NEEDS LINE CREW, NO TRUCKS.//VER/CRB IDC XXXX
2931 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-01-17 13:51 | 2011-01-17 14:05 | 756 | 14 | 61909-1 | 10584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON CREW AND FELL INTO CUTOUT BRACKET COD-756 ISO RECL 37830387C40721 IDC XXXX
2932 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2010-01-06 19:29 | 2010-01-06 21:35 | 84 | 126 | 64198-1 | 10584 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE OPEN @ 1929 // DROPPED REMAINING CUSTOMER @ 2053 - THEN CLOSED IN THE 46KV CB "A" AT ELKHORN CITY AND PICKED UP DRAFFIN STATION @ 2135 // IDC NO CUSTOMERS OUT TILL 1929 PH A THEN REMAINING OUT WHEN TRANSMISSION OPENED AT 2054 XXXX
2933 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-01-17 02:35 | 2013-01-17 16:09 | 13 | 814 | 4613361 | 10582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 1148-78 BURNT OFF 50/2 POLE SEND TO BOB R. RELEASED BY CREW 078S08// RESTORED WHEN NEW SWS CLOSED AT 1609 IDCC TOF219 XXXX
2934 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-08-10 19:06 | 2011-08-10 19:13 | 1511 | 7 | 4694521 | 10577 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - NON LTC | SDB / 1906 / EMERGENCY DROP AND PICK TO REPAIR TR BUSHING AT STATON. CC = 1511. --- SDB / 1913 / 1511 CC RESTORED VIA LINE TIE TO W PAINTSVILLE/PAINTSVILLE 12KV CKT // SEE 4694801 FOR RETURNING EQUIPMENT & CKT TO NORMAL VER/HFP L3/HFP IDC XXXX
2935 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-02-07 15:12 | 2019-02-07 18:57 | 47 | 225 | 4764351 | 10575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required 182a102 can cut off and lower trucks ok/tagged 182a207 to b tackett also grounds placed Released by crew 078S03.repairs made all cust restored @ 1857 please close ticket thanks.bt
2936 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-06-06 14:16 | 2008-06-06 16:15 | 98 | 119 | 59175-1 | 10567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | THERE ARE 3 SINGLE RECLOSERS ON POLE 239-293. WITH BACK TO STATION RIGHT HAND PHASE IS OUT. THE OTHER 2 RECLOSERS ARE STILL CLOSED. DEB/DOWNLINE IS A 3 PHASE REC WHICH IS OPEN THERE ARE 3 SINGLE RECLOSERS ON POLE 239-293. WITH BACK TO STATION RIGHT HAND PHASE IS OUT. THE OTHER 2 RECLOSERS ARE STILL CLOSED. REGULATOR ON POLE 239-261 SHORTED OUT. I OPENED BYPASS ON REGULATOR AND CLOSED RECLOSER BACK IN ON POLE 239-293. VER/HFP IDC 3PH RECLOSER NOT PART OF TROUBLE
2937 | South Williamson | 3411401 | DEWEY | INEZ | 2013-07-12 04:18 | 2013-07-12 11:57 | 23 | 459 | 4511281 | 10557 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CAN SEE WIRE DOWN AT POLE 671-20//BROKE IN CLEAR AT INSULATOR/LOOKS LIKE IT PULLED OUT OF SLEEVE//I OPENED CUTOUT ON 672-218 TO ISOLATE AND TAGGED TO DDC//THIS SHOWS TO BE A 15T ON MAP BUT IS ACTUALLY SOLID,MAY WANT TO PUT FUSE IN AFTER REPAIRS ARE MADE//WILL NEED PAINTSVILLE LINE CREW///CAN ONLY GET PICK-UP OVER TOTHIS SIDE OF THE CREEK///#4COPPER RELEASED BY CREW 079S01// CREW ON SITE TCM/ COD-23 ISO PO VER/HFP L3/HFP IDC XXXX
2938 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-09-05 16:46 | 2012-09-06 03:45 | 16 | 659 | 4019471 | 10544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DIP FUSE BLOWN ON POLE 37830024B20666// NEED 3 MEN // HI POT EQUIP. RELEASED BY CREW 074S05 CREW ON SITE WORKING HEAVY RAIN WITH LIGHTING IN THE AREA WILL NEED TO WAIT A LITTLE UNTIL STORM MOVES OUT FOUND CABLE SPLICING IT CABLE 5 FEET DEEP //VER/GAH IDCC CDC83 XXXX
2939 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-06-05 05:41 | 2009-06-05 10:18 | 51 | 277 | 62943-1 | 10531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP ONLY B PHASE RECL OUT 49 CUST CUTOUT BROKE DOWN AND BURNED TOP OF POLE 37830120B00054 OFF. IT TOOK A SINGLE RECLOSER OUT ON POLE 120-61. I ISOLATED TROUBLE BY OPENING LINE FUSE ON POLE 120-28. I CLOSED RECLOSER AT POLE 120-61 BACK IN AT 08:14. STEVIE RAY AND HIS CREW ARE ON THE WAY TO FIX POLE. L3/HFP IDC XXXX
2940 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-11-30 19:00 | 2010-11-30 19:32 | 329 | 32 | 61337-1 | 10528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO 61210-1 COD-329 VER/HFP L3/HFP IDC XXXX
2941 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2013-12-16 20:32 | 2013-12-16 22:06 | 112 | 94 | 4166911 | 10528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | C PHASE LOOP OPEN ON SWITCH 703-79 COD 112LEAD BURNED OUT OF HOT TAP .C PHASE.LEAD BURNED OUT OF HOT TAP .C PHASE.CHG HOT TAP CLOSED SWITCH AT 22.06 VER/SEF L3/HFP IDC XXXX
2942 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2019-08-08 21:10 | 2019-08-08 21:21 | 957 | 11 | 4861851 | 10527 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | station outage to safely bypass regulator ¦¦ VERIFIED TIMES PER SCADA = L3/HFP
2943 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-12-01 00:51 | 2009-12-01 06:10 | 33 | 319 | 52506-1 | 10527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, POLE #518-47 BURNT OFF AT CUTOUT ... WILL ISOLATE ON POLE 518-35 & GROUND, MADE REPAIRS RESTORED POWER AT 06:10 IDC XXXX
2944 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-07-09 03:28 | 2008-07-09 12:45 | 82 | 557 | 65396-1 | 10519 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904//,,,FOUND PRIMARY WIRE SAGED DOWN BELOW NEUTRAL COULD NOT FIND OUT WHY, ,,FOUND BURNT POLE TOP AT POLE 619-143,, I HAVE ISOLATED ON POLE 619-5 BY REMOVING HOT TAP,,POLE IS TRUCK ACCESIBLE RECLOSER,, POLE IS BESIDE ROBERTA PAY LAKE TRAILER ON LEFT FOR//TOTAL COD 82// VER/DBM IDC XXXX
2945 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-02-09 19:12 | 2010-02-10 02:30 | 24 | 438 | H54569-1 | 10512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C PHASE ONLY OUT WHEN ARRIVED, CROSSARM BROKE AT POLE 38830278000015 AND 38830278000016, 1 PHASE OFF OF INSULATOR AT POLE 38830278000017, NO TRUCK TO ANY., WIRE ON GROUND HOT, NEED TO OPEN OTHER 2 PHASES. OPENED AND TAGGED AT 19:12// THIS OUTAGE FOR A & B PHASES - 24 CUSTOMERS VER/TOM L3/TOM IDC XXXX
2946 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-12-29 04:09 | 2012-12-29 16:35 | 36 | 746 | 4547661 | 10511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE TRIED FUSE ONCE/ISOLATED ON 227-27 NEEDS NEW CUTOUT AND ARRESTOR ONE CUSTOMER WILL BE OFF/CREW REQUIRED NO TRUCK RELEASED BY CREW 078S03/ FETR 16:30 REPAIRS COMP. POWER REST. @ 16:35 JEH RELEASED BY CREW 078H05//COD 36// VER/DBM IDC XXXX
2947 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-11-19 00:10 | 2017-11-19 16:05 | 11 | 955 | 4577031 | 10505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout failed on 1125-41. Replaced cutout and bracket. Restored @ 16:05. sh
2948 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-03-23 05:07 | 2010-03-23 08:37 | 50 | 210 | 53093-1 | 10500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT AT STEPDOWN-CALLING CREW-SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE /FETR0845/VEM/REPAIRS MADE AND POWER RESTORED 0837/PLEASE CLOSE TICKET/THANKS/VEM COD-50 VER/HFP L3/HFP IDC XXXX
2949 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-08-24 14:00 | 2017-08-24 23:12 | 37 | 552 | 4296321 | 10496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830282000063 35/7 CO OWNED POLE BROKE--38830282000055 CUT LOOP --38830235000068 30T LINE FUSE IN AT 18:20--CREW REQ NBT?-DS082417----CREW ON SITE--FETR 01:51--CHANGED G&T TO J. RAMEY DHE-- RELEASED BY CREW 078H16. BROKE POLE CHANGED OUT BUT TELEPHONE STILL NEEDS TRANSFERRED. LINE REENERGIZED 38830282000055 AT 23:12/ VER/BOW SJG
2950 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-03-13 03:31 | 2009-03-13 03:40 | 1166 | 9 | 57742-1 | 10494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED FEEDER TO MAKER REPAIRS ON LATERAL LINE ./ HOT LINE CLAMP BURNING ON RECLOSER (ORDER 57673) VER/LDA IDC XXXX
2951 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-09-07 08:14 | 2020-09-07 12:40 | 45 | 266 | 4438461 | 10493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RECL IS STILL IN // PRIMARY PULLED OUT OF SLEEVE @ POLE 319-A-42 // LINE IS HOT UP TO THIS POINT // OPENED RECL @ 1145 TO MAKE REPAIRS // CLOSED RECL @ 1240 RESTORING ALL CUSTOMERS
2952 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-06-03 11:38 | 2017-06-03 15:42 | 43 | 244 | 4901521 | 10492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | (B) PHASE RECLOSER OPEN ON 38831125B00772. 43 CREW REQUIRED: 3 MAN LINE CREW, 30 FT #4 CU, TRUCK ACCESS. WIRE DOWN 38831124D00012. OPENED A&C RECLOSERS ON 1125-772 @ 14:57 (ADDITIONAL 179 CUSTOMERS). CLOSED ALL PHASES AT POLE 772 @ 15:42, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/AWD AJB
2953 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-07-17 20:33 | 2009-07-17 22:05 | 114 | 92 | 57880-1 | 10488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308503//CONFIRMED RECLOSER OPEN PATROLLING LINE//RISER BURNED OFF AT HIGHSIDE CUTOUTON STEPDOWN//COD 114// VER/DBM IDC XXXX
2954 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-10-12 01:14 | 2011-10-12 06:05 | 36 | 291 | 4967441 | 10476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 122-39 16 COP VER/ARN IDC XXXX
2955 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-12-18 13:50 | 2012-12-18 16:06 | 77 | 136 | 4480481 | 10472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPENED RECLOSERS ON POLE 1090C158 AT 15:00. MAKING REPAIRS . LOOP BURNED OPEN AT POLE 1091-66. ///VER/CRB L/3 CRB IDC XXXX
2956 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-02-19 23:11 | 2015-02-20 05:00 | 30 | 349 | 4045751 | 10470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE IS OPEN ON38830595000080 THIS IS A STEP-DOWN PATROLLING LINE, ONE SPAN OF #2 ALUM PRIMARY ONLY DOWN LOOKS LIKE MAY HAVE BURNT INTO , POSSIBLY TRUCK OK. LINE DOWN FROM 38830595000031 TO 38830595000032. ISOLATED G&T TO DDC AT 595-80,LINECREW ONLY RELEASED BY CREW 078S11 VER/CRB L3/HFP XXX AJB
2957 | Pikeville | 3402003 | KEYSER | MULLINS | 2021-01-01 17:05 | 2021-01-01 19:11 | 83 | 126 | 4841451 | 10458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 1103-60 is broke, 45-4, 4 dead end bells and #2 shoes, 1 PTP and ins, 1, 7200 XCO and arrestor, 2 guy att// will have to open recloser on pole 1103-117 when crews arrive to safely make repairs//opened at 17:05 on at 19:11 Released by crew 074S09
2958 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-02-21 13:50 | 2019-02-21 19:14 | 37 | 324 | 4837431 | 10458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED RECLOSER 38821057C00240 TO TAKE LOAD OFF , THEN OPENING L/F 38821057C00037//TO REPLACE TRANSFORMER 38821057C00062//OPEN LF @ 1425 OPEN OCR @ 1418 //CLOSED L/F 1819//closed rec 1849//closed TR at 1914
2959 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-05-03 10:30 | 2009-05-03 13:55 | 51 | 205 | 63889-1 | 10455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29636924 POLE ON FIRE, CALLING FOR CREW OPENED LINE FUSE ON POLE 37830227B00065 @ 1030 51 CUSTOMERSWR # 29636924 POLE ON FIRE, CALLING FOR CREW, POLE # 227-78 , LINE FUSE OPEN ON 227-65 COD-51 ISO POLE 37830227B00065 L3/HFP IDCC PN75 XXXX
2960 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-07-28 20:15 | 2009-07-28 21:10 | 190 | 55 | 57347-1 | 10450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002002//HAD TO OPEN THIS RECLOSER TO REPAIR CROSSARM SAFELY//RELATED TO 55785-1//COD 190// VER/DBM IDC XXXX
2961 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-09-06 13:07 | 2008-09-06 15:25 | 80 | 138 | 59949-1 | 10448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3411902//C PHASE OUT ON REC 143-411 COD-80// RELEASED BY CREW 074H12//VER/CRB IDC XXXX
2962 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-03-24 15:10 | 2021-03-24 21:10 | 29 | 360 | 4370311 | 10440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | Pole 38830140B43519, 404 Ky Power pole broke at telephone, wire holding it up. Primary angle pole, with 15kva 7200, and service drop, Crew required, yard dog required. One pole away from 30T line fuse on 140-188. Released by crew 078S02////no outage till opened line fuse 140-B-188//Off at XXXX - On at XXXXPole 38830140B43519, 404 Ky Power pole broke at telephone, wire holding it up. Primary angle pole, with 15kva 7200, and service drop, Crew required, yard dog required. One pole away from
2963 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-07-02 21:00 | 2012-07-03 16:20 | 9 | 1160 | 4243801 | 10440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANS REPAIRED
2964 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-11-02 10:02 | 2020-11-02 11:13 | 147 | 71 | 4632611 | 10437 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B phase, load side clamp on recloser pole 153A-233 burnt off in the clear, made repairs to the rise and power restored at 11:13.
2965 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-10-10 11:34 | 2022-10-10 13:08 | 111 | 94 | 4011691 | 10434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Primary off insulator, broken tie wire @ 89-d4-108. Tagged to GH @ 9-221. Wire tied in, reclosure on 9-221 restored @ 13:08
2966 | Pikeville | 3408401 | KIMPER | LONGFORK | 2011-07-12 23:48 | 2011-07-13 00:20 | 326 | 32 | 4538731 | 10432 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | SDB / 2348 / FEEDER OPENED DUE TO ARCING LINE DISC. CC= 327. --- SDB / 0020 / ALL CUST RESTORED VIA TRANSFER BUS. TRANSFERRED TO GRAPEVINE CB IDC XXXX
2967 | Hazard | 3309302 | VICCO | JEFF | 2012-08-27 14:01 | 2012-08-27 17:07 | 56 | 186 | 4976741 | 10416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE IS OUT ON STEPDOWN 37830347A00300 === RECLOSER STILL IN ON NEXT POLE OUT === 333 KV STEPDOWN TRANSF BAD === NEED LINE CREW === A- PHASE INITALLY OUT 56 CUSTOMERSF USE IS OUT ON STEPDOWN 37830347A00300 OPENED OTHER PHASE @ 1620 = 59 CUSTOMERS /// COD-115 ISO LF 37830347A00300 SEE H4976741 FOR C PHASE VER/HFP L3/HFP IDCC CDC92 XXXX
2968 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2012-09-28 04:00 | 2012-09-28 13:08 | 19 | 548 | 4094751 | 10412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / WILL CHECK AT REGULAR TIME FAILED CUTOUT CREW ENROUTE. MD FILED SWITCH OUTAGE ON SEPERATE ORDER CUTOUT FAILED OPENED SWITCH 196-104 TO ISOLATE ALL POWER RESTOREDAT 1308 VER/KEP IDCC LOOKS LIKE PROBABLY PH C ONLY INITIALLY CNT86, PN98 XXXX
2969 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-02-10 18:46 | 2019-02-10 20:27 | 103 | 101 | 4775471 | 10403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke 1017-a1-127 /// iso 38820992D33063Replaced bad transformer cutout at pole 38821017A10127. Power restored at 20:27
2970 | Hazard | 3302703 | HAZARD | HAZARD | 2011-06-02 18:06 | 2011-06-02 18:33 | 385 | 27 | 4225341 | 10395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 40223386 // OPENED SWITCHES ON POLE 37830296A30149 @ 1806 CLOSED @ 1833 COD-385 ISO PO 37830296A30149 VER/HFP L3/HFP IDC XXXX
2971 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-05-14 17:05 | 2010-05-14 18:15 | 184 | 70 | 62119-1 | 10390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 35130605 // POLE 44-377 BAD LA POLE 44-665 REC. OUT COD-184 VER/HFP L3/HFP IDC XXXX
2972 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-12-22 00:47 | 2012-12-22 03:43 | 59 | 176 | 4504451 | 10384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | SERVICER DISPATCHED TO PATROL LINE. ** SERVICER FOUND BAD RECLOSER (BUSHINGS) WORKING TO ISOLATE AND BYPASS RECLOSER AT THIS TIME.SERVICER DISPATCHED TO PATROL LINE. LINE RECLOSER WENT BAD ON POLE 37830513D00102 === TOOK OFF LINE PLACED TAG FOR DDC === PUT BYPASSE FUSE === POWER OK VER/PDP
2973 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-06-05 08:42 | 2019-06-05 12:18 | 70 | 216 | 4429061 | 10362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad ptp on 1047-47, also open s/b switch on 1047-43, when to try rec, came back out, found bad c/o on 1047-132, lifted htsp on 1047-91, can be replaced later date, just feeds temp serv, need cust to open gate closed in rec at 1100 hot to pole 1047-43 Released by crew 078S06 ¦¦ L3/HFP
2974 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-12-25 15:14 | 2009-12-27 10:24 | 4 | 2590 | 56374-1 | 10360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BAD, NON TRUCK ACCESSIBLE --- REPLACED XFRM & RESTORED POWER TO 4 CUSTOMERS AT 10:00 ON 12-27-09 RELEASED BY CREW 074M02 //// PLEASE CLOSE THIS ORDER//IT FORCE CLOSED IDC XXXX
2975 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2019-11-22 16:40 | 2019-11-22 16:57 | 609 | 17 | 4057251 | 10353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SWITCH ON POLE 38830655B00106 ARCING //GOING TO OPEN GOAB ON POLE 38830654B00456//COD 832//OUTAGE WILL LAST APPROX 1 HOUR//300 amp solid switch is bad on p-655-106.opening switches on p-654-456 to chg OPENED @ 1640 CLOSED 1657//THE OPEN POINT BETWEEN INDEX-WEST AND FALCON - SALYERSVILLE CHANGES DAILEY THAT IS THE REASON FOR THE DUPLICATION ON THE ORDER 4057251
2976 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-02-22 12:27 | 2015-02-22 16:25 | 50 | 238 | 4071761 | 10346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | AFTER GETTING RECLOSER IN ON ORDER 4069991 THIS FUSE CAME OUT PROBABLY DUE TO LOAD/ FUSE IN @ 1322// LEFT 1053-A-168 &170 OFF/ TRIED FUSE SEVERAL TIMES HELD FOR FEW MINUTES CAME BACK OUT/ FUSE ON AND OFF SEVERAL TIMESPUT TRANSFORMER BACK ON AND FUSE CAME CUTOUT CAME BACK OUT./ GOING TO CHANGE CUTOUT TO 65T/ CUTOUT BACK IN @ 15:48 AND LEFT 38831053A00170 OFF TO ALLOW LOAD TO PICK UP ON FUSE/ SPRING WAS BAD ON CUOUT/ ISO 38831053A00164/ COD 50/ LAST TRANSFORMER BACK ON AT 16:25/ VER/BOW AJB
2977 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-05-08 16:04 | 2012-05-08 19:35 | 49 | 211 | 4761461 | 10339 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND LINE FUSE OUT CALLED CREW RELEASED BY CREW 078S08 VER/TOM L3/TOM IDC XXXX
2978 | Hazard | 3310502 | HADDIX | CANOE | 2017-01-09 10:51 | 2017-01-09 12:47 | 89 | 116 | 4280461 | 10324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE HOT CLAMP BURNT OFF ON POLE 169-185 (7 CUSTOMERS)/ ISO 37830169C00185/ COD 7/ CLAMP BURNED OF @ POLE 169C-185 , C PHASE RECLOSER OUT DO TO CLAMP BAD .CLOSED RECLOSER BACK ON POLE 37830169C00338 @ 12:47/ BUSINESS OBJECTS & POR INDICATES AN `A` PHASE OUTAGE 89 CUST = L3/HFP AJB
2979 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-09-15 08:19 | 2008-09-15 14:03 | 30 | 344 | 63699-1 | 10320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501// STS BAD CUTOUT ON POLE 1037-57 BURNED POLE OFF, GOT CREW COMING TO CHANGE OUT RELEASED BY CREW 077S05//ERIC PRATT DHE 3680 TO CHANGE OUT POLE//COD 30// VER/DBM MLRC FP NONE GIVEN IDCC FP, TOF0752 XXXX
2980 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-06-28 00:56 | 2019-06-28 06:40 | 30 | 344 | 4610191 | 10320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse had broke inside of gate.. this caused fuse to fall open. power restored @ 06:40/ ISO 37830450C00040/ COD 30
2981 | South Williamson | 3200302 | BELFRY | TOLER | 2008-10-19 07:41 | 2008-10-19 08:58 | 134 | 77 | 56987-1 | 10318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | 3200302 ON SITE, CHECKING TROUBLE, SECTIONALIZER NOT WORKING, BYPASSED WITH SOLID BLADES **AED CREATED. IDC XXXX
2982 | Hazard | 3309302 | VICCO | JEFF | 2008-01-25 08:48 | 2008-01-25 12:10 | 51 | 202 | 59724-1 | 10302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3309302//ROTTED WIRE//VER/CRB PLCC CDC 89 10 CALLS . . .DIFFERENT TRFRS PN IS NOT CORRECT 37830323C00129 PROBABLY PRIM OPEN
2983 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-11-13 05:19 | 2008-11-13 08:24 | 68 | 185 | 64322-1 | 10302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314402// IT IS FOGGY AND I CANNOT SEE LINE I HAVE HELP ON THE WAY CUTOUT BAD ON POLE 402-216 CLOSED MAIN LINE IN AT 0750 AM AND I HAVE 1 CUST STILL OFF REPLACED CUTOUTAND POWER ON AT 0824//VER/CRB IDC XXXX
2984 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2019-02-27 15:06 | 2019-02-28 00:38 | 18 | 572 | 4934111 | 10296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | URD riser open @47-B-155, .//DIP FUSE CAME BACK BACK OUT//BAD ELBOW ON ON UG TRANSFORMER 37830047B30159// Made repairs and closed L/F @0038.
2985 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-02-13 20:51 | 2014-02-14 12:27 | 11 | 936 | 4385751 | 10296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE 217-132 TOP BURNED OFF DUE TO A FAILED CUTOUT. WILL NEED A CUTOUT AND T BRACKET. WE MAY BE ABLE TO USE A POLE TOP EXTENSION. IF NOT, WE WILL NEED A RIDGE PIN. THE POLE IS ABOUT 35 FEET FROM THE ROAD, WE PROBABLY CANNOT USE A BUCKET TRUCK. WILL NEED AT LEAST A 3 MAN CREW. THIS IS 7.2 KV. RELEASED BY CREW 074S02 VER/SEF
2986 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2017-03-02 06:59 | 2017-03-04 16:10 | 3 | 3431 | 4495431 | 10293 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40` 4 BURNED OFF. 1/0 DE TAP DS115. 25KVA XFMER. 7.2 KV PL #941-C3-8540 4 BURNED OFF. 1/0 DE TAP DS115. 25KVA XFMER. 7.2 KV PL #941-C3-85 REPLACED POLE AND TRANSFORMER BACK ON AT 16:06 RELEASED BY CREW 074M01 VER/HFP L3/HFP
2987 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-22 17:58 | 2011-05-23 07:55 | 23 | 837 | 4124041 | 10291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR# 40059199 // POLE 117-223 AND 117-222 BAD LA POLE 117-148 30T RELEASED BY CREW 078H14 VER/HFP L3/HFP IDCC CNT32 XXXX
2988 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2020-03-03 19:17 | 2020-03-03 22:47 | 49 | 210 | 4449091 | 10290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 997582 // connection failed burning A phase conductor down at 1065-B-263. opened switches on 1065-D2-287 to make repairs//after completing repairs when attempting to restore, the CB at the station is unresponsive// have called station servicer to investigate// will attempt to pick up this ckt from another feed //
2989 | Hazard | 3303901 | LESLIE | HYDEN | 2019-12-10 08:17 | 2019-12-10 10:18 | 85 | 121 | 4140601 | 10285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | arm brace came loose will try to secure to restore power , a phase restored at 10:18 Released by crew 077H14 A phase only COD 85
2990 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2009-04-08 10:22 | 2009-04-08 13:29 | 55 | 187 | 50442-1 | 10285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 080S01 POLE TOP BURNED OFF @ POLE # 10-C-31RELEASED BY CREW 080S01 POLE TOP BURNED OFF @ POLE # 10-D-31//COD 55// VER/DBM AJB
2991 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-10-07 18:33 | 2010-10-07 20:19 | 97 | 106 | 57906-1 | 10282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP ON LOAD SIDE OF B PHASE RECLOSER BAD ,REPLACED HOT TAP POWER BACK ON POLE 379-167. ///VER/CRB IDC XXXX
2992 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-09-01 20:07 | 2014-09-01 23:41 | 48 | 214 | 4446211 | 10272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS BLOWN AT POLE 38821109C00006, PATROLLING THE LINE. BAD CUTOUT ON THE ISO POLE. CALLED FOR NE AND AN LMA TO HELP REPLACE THE CUTOUT. MIGHT HAVE TO DEENERGIZE LINE TO SAFELY CHANGE THE CUTOUT. I OPENED RECLOSER ON POLE 38821086A00417 AT 23:07. CLOSED RECLOSER BACK IN AT 23:41. ALL CUSTOMERS SHOULD BE ON NOW. VER/SEF // SEE 4446531 FOR RECL OUTAGE /// L3/HFP AJB
2993 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-01-21 03:19 | 2008-01-21 06:02 | 63 | 163 | 58187-1 | 10269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3409401////SERVICER FOUND RISER COME LOOSE FROM FUSE ON POLE 104-23//COD 63//SENT REPORT TO MAPPING ON MISSING FUSE ON POLE 23// VER/DBM IDC XXXX
2994 | Paintsville | 3401802 | INDEX | HOSPITAL | 2011-08-01 05:27 | 2011-08-01 11:21 | 29 | 354 | 4649661 | 10266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | APPEARS TO BE BAD U/G CABLE BETWEEN 654-463 AND 654-464.CALLED ROER MAYNARD ..HE IS ENROUTE..LINE FUSE BLOWN ON 654-436..BACK ON AT 11.21//MADE MDC//VER/CRB STC, CDC83, PER PHONE CONF
2995 | Hazard | 3309302 | VICCO | JEFF | 2020-04-26 01:33 | 2020-04-26 03:00 | 118 | 87 | 4751151 | 10266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3309302/0118/crews opened reclosers at 299C-254 to safely tie in b phase at 37830275000066 outage should last 2 Hrs from Start FETR 0330 --- gaj/0300/all cust restored
2996 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-11-19 01:57 | 2008-11-19 06:20 | 39 | 263 | 66412-1 | 10257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WR 27354499WIRE DOWQN ON POLE 90-50--WILL OPEN SOLID BLADE ON POLE 90-357 VER/KEP MLRC PN 38830090000010 IDC XXXX
2997 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-06-26 10:48 | 2018-06-26 15:16 | 39 | 268 | 4669621 | 10254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 223-106, fuse on 247-265 is blown, will open 247-29 and close 247-265..repairs made all power restored @ 15:16 hrs p.hicks
2998 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-10-29 00:52 | 2014-10-29 05:25 | 38 | 273 | 4669661 | 10254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | HIGH SIDE FUSE ON STEPDOWN TRANSFORMER AT POLE 37820098C00557 IS BLOWN. I AM GOING TO PATROLL LINE. WE ALSO HAVE A LINE FUSE ON POLE 98C-278. I FOUND A CUTOUT BREAKING ON POLE 99-1. THIS IS DIFFERENT PHASE THAN WHERE LINE FUSE IS BLOWN. I OPENED CUTOUT ON POLE 99-1 AT 02:25. WE ALSO HAVE AN INSULATOR BREAKING DOWN ON 99-2. I WILL WAIT ON LINEMAN AND WE WILL OPEN OTHER CUTOUT ON 98C-278 LONG ENOUGH TO CHANGE CUTOUT AND INSULATOR. I OPENED CUTOUT AT 04:25. I CLOSED STEPDO RELEASED BY CREW 074S01 VER/ARN AJB
2999 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-09-13 12:55 | 2020-09-13 13:20 | 410 | 25 | 4457201 | 10250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | dol 1053160 off @ 1255 on @ 1320 410 customrs
3000 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-10-28 17:07 | 2012-10-28 17:25 | 569 | 18 | 4178951 | 10242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE//FUSE POLE 37830248C00052 IS ON FIRE, BAD CUTOUT ON THIS POLE, DEENERGIZED RECLOSERS ON POLE 37830248A41086 AT 1707 REPLACED CUTOUT ON POLE 37830248C00052, REENERGIZED ON POLE 37830248A41086 AT 1725. FIRE OUT AND ALL POWER RESTORED. RELEASED BY CREW 077S04//COD 569// VER/DBM IDC XXXX
3001 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-08-04 04:43 | 2015-08-04 06:12 | 115 | 89 | H4972901 | 10235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE C RECLOSER ONLY OPEN ON 810-782.//COD 178 @ THIIS TIME//PHASE C RECLOSER ONLY OPEN ON 810-782. XFMR CUTOUT BROKE DOWN AND BURNED CROSSARM OFF. CREW ENROUTE TO ASSIST.//COD 178// OPENED UP SWITCHES AT POLE 834-A-15 INTERRUPTING 117 MORE CUSTOMERS AT 0433. // DUP OF 4972901 FOR 117 CUST - VER TIMES PER VOICE REC VER/HFP L3/HFP AJB
3002 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-09-14 13:12 | 2015-09-14 14:45 | 110 | 93 | 4236761 | 10230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ROTTEN CROSSARM 38830165A00004/ C PHASE FLOATING @ 38830165A00003 VER/ARN // VER TIMES PER ADX = L3/HFP XXXHFP AJB
3003 | Hazard | 3309901 | SLEMP | DEFEATED CREEK | 2020-08-31 18:13 | 2020-08-31 23:23 | 33 | 310 | 4409181 | 10230 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 1050048 // T-Line outage // Station source is out // investigating load xfers // xferred all load to Daisy_Leatherwood as of 2323 8/31/20 // lsr- The DOL shows this as 1 step of the circuit took out 33 Customers at 18:13 on 8-31-20 and restored at 23:23
3004 | Whitesburg | 3314401 | MAYKING | ERMINE | 2012-12-22 16:05 | 2012-12-22 16:35 | 341 | 30 | 4508941 | 10230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE BROKE AT POLE 449-164, IT WAS LAYING ON OUTSIDE PHASE HOT, I OPENED UNDERSLUNG SWITCHES AT POLE 449-175 AT 16:05, CLEARED GUY WIRE AND CLOSED BACK IN AT 16:35. ///VER/CRB L/3 CRB
3005 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-07-17 15:35 | 2019-07-17 20:15 | 119 | 280 | 4723151 | 10225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 alum dn from 38830428C40466 to 428-132. Pole 428-466 is broke but can change at later date. Lifted HT on 428-45. Recloser on 428-234 in @ 1700. Linecrew required Released by crew 078S11 crew on site FETR 20:00 LRM 20:15 all pwr restored LRM Released by crew 078H06 L3/HFP
3006 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-09-06 16:26 | 2012-09-06 17:37 | 144 | 71 | 4024941 | 10224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO ORDER 4022981//OPENED LINE IN ORDER TO MAKE REPAIRS TO FAILED CONDUCTORS//COD 144// VER/DBM IDC XXXX
3007 | South Williamson | 3411401 | DEWEY | INEZ | 2012-01-25 22:51 | 2012-01-26 04:15 | 65 | 324 | 4293441 | 10224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER LOCKED OUT//SHOWS C PHASE FAULT//PATROLING NOW//HAVE SWITCHES OPEN ON 767-28//BACK AT RECLOSER//CLOSED AT 23:57//GOING TO PATROL REST OF LINE// VER/KEP IDC XXXX
3008 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-02-28 19:34 | 2019-03-01 03:20 | 83 | 466 | 4939671 | 10216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 329-1 burnt off @ top,CREW REQUIRED Released by crew 078S05,repairs made all cust restored @ 0320 please close ticket thanks.bt
3009 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-03-03 00:43 | 2020-03-03 02:15 | 111 | 92 | 4445911 | 10212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRBL ¦¦ bad csp xfmr on pole 876-50..rec back in at 2.15.need 15 kva xfmr cutout and arrestor,,, brkt. truck accessible.//iso 38830876D00102//note: fused tap on recloser pole not protected by recloser, MD file//cod 111//
3010 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-10-09 03:02 | 2012-10-09 12:12 | 56 | 550 | 4124861 | 10208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SERVICER FOUND POLE 80-14 BURNT OFF.- TAP LIFTED AND TAGGED FOR DDC AT POLE 80-6 CLOSED RECLOSER AT 104-26 AT 0503 40-4 POLE SINGLE PHASE. POLE HAS SIDE TAP WITH GUY, AND TRANSFORMER. NEED RIDGE PIN AND 2 CLEVICES AND GUY ASSEMBLY1/4 A CUTOUT AND T-BRACKET. CAN USE TRUCK. NEED 3 OR 4 MEN.¦¦¦¦¦¦¦ REQUESTED PAUL LAYNE TO REMOVE DDC HOLD TAG AND REPLACE WITH HIS OWN HOLD TAGS // SEE 4125841 FOR OUTAGE ON RECL TO MAKE UP LOOPS COD-56 ISO OCR 37820104000026 VER/HFP L3/HFP IDC XXXX
3011 | Hazard | 3310502 | HADDIX | CANOE | 2021-06-26 11:27 | 2021-06-26 14:20 | 59 | 173 | 4809151 | 10207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulator on pole 99-14. repaired and restored power at 14:20
3012 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-01-04 07:43 | 2008-01-04 09:25 | 100 | 102 | 53558-1 | 10200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000301// CALLED CREW// B REYNOLDS/ JUST B PHASE OUT-IS CUSTOMER COUNT CORRECT RELEASED BY CREW 078S07// VER/TOM IDC XXXX
3013 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2020-12-26 14:21 | 2020-12-26 18:16 | 44 | 235 | 4825051 | 10186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN @ POLE 37830067C00164 COD 42//OPEN SWITCH ON POLE 37830067C00340 THIS OUTED 2 MORE CUSTS//A phase down @ 67C-164. Opened A phase switch @ 37830067C00340 @ 15:38A phase down @ 67C-164. Opened A phase switch @ 37830067C00340 @ 15:38. Repairs made and restored @ 18:16 Released by crew 074S11
3014 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-10-14 12:39 | 2010-10-14 13:03 | 424 | 24 | 59683-1 | 10176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 59661-1 - CREW OPENED RECLOSER TO ISOLATE TROUBLE IN THAT ORDER/ POLE TOP BURNT OFF CLOSED RECLOSER 1303 VER/KEP L3/KEP IDC XXXX
3015 | South Williamson | 3200301 | BELFRY | BELFRY | 2009-12-24 20:50 | 2009-12-24 21:27 | 275 | 37 | 60903-1 | 10175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW HAD TO OPEN SOLID BLADE SWITCH ON POLE 990-C1-25 TO REPAIR PHASE THAT HAS BURNT DOWN MLR
3016 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-06-12 21:55 | 2016-06-13 02:45 | 35 | 290 | 4340491 | 10150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER @ 21:55// DUE TO POLE FIRE ON POLE 851-210 - WILL REQUIRE CREW TO MAKE REPAIRS ONCE FIRE IS OUT//TOM////NEED 1 MAN AND FORMAN CLOSED @ 0245 VER/TOM L3/TOM AJB
3017 | Whitesburg | 3312901 | JENKINS | KONA | 2011-08-09 00:37 | 2011-08-09 01:35 | 175 | 58 | 4684611 | 10150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 0037 / RECLOSERS AT POLE 403-D-77 OPENED TO REPAIR BROKEN CUT OUT ON BYPASS SW (MIDDLE PHASE) CC = 175. --- SDB / 0135 / ALL CUSTOMERS RESTORED. VER/SDB IDC XXXX
3018 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-07-04 15:16 | 2011-07-04 17:35 | 73 | 139 | 4457171 | 10147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLEW @ POLE 698-41///PATROLLING NOW///THE FUSE CUTOUT WAS BAD ON POLE 698-41///CHANGED IT OUT AND CLOSED IT IN @ 5:35///COMPLETE BR //VER/GAH IDC XXXX
3019 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-11-12 22:35 | 2013-11-13 13:26 | 26 | 891 | 4033801 | 10138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DIP FUSE BLOWN ON 38831152B20211// WIIL REFUSE// FUSE CAME BACK OUT// ONE PAD STILL OUT 24-1587 (NOT ON MAP) CLOSED N.O. 1151-673 - ENERGIZED TO PARKED ELBOW (TAGGED TO KY DDC) AT JCT BOX ON PAD SIDE OF 1152-1625// WILL NEED UG CREW TO MAKE REPAIRS// BAD CABLE BETWEEN 1152-200 AND 24-1587 REPAIRS MADE ON AT 13:26 D SAMMONS // CLOSED THIS ORDER AND CREATED PO SWITCHING ORDER TO REFLECT FIELD CONDITIONS// CURRENT POWERON MAP WRONG DUE TO OPEN POINTS// VER/TOM L3/TOM IDC XXXX
3020 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-29 09:26 | 2008-03-29 13:33 | 41 | 247 | 61895-1 | 10127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401/// 41 OUT @ 0930 - OPENED RECLOSER @ 1225 TAKING OUT ADDITIONAL 248 CUSOTMERS// BACK ON @1333 // THIS WAS ASSOCIATED WITH SWITCHING THAT TOOK PLACE - TYING BECKHAM/HINDMAN AND GARRETT/LACKEY// 41 CUSTOMER OUT FROM WHERE LOOP BURNT OPEN @ POLE 158-1 RFOM 0930 UNTIL REST @ 1333// OPENED REC ON 182-257 @1225 TO ISOLATE AND MAKE REPAIRS// VER/TOM IDC XXXX
3021 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2014-12-01 23:05 | 2014-12-02 03:18 | 40 | 253 | 4824071 | 10120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT APPEARS BAD ON 37830048C21254//NO TRUCK// PARKED/ TAGGED TO DDC @ PAD 37830048C21427 FROM POLE 48-1254// CLOSED IN @ N.O. 37830048C41801// POWER RESTORED @ 3:18 VER/ARN L3/HFP AJB
3022 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-12-24 05:43 | 2022-12-24 07:33 | 92 | 110 | 4338961 | 10120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse on pole 1086A-417 melted out ..rec is off line and tagged out.fuse in bypass cutout is whats out...i got 80T line fuse on pole 1086A-417 back in at 07:33
3023 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-07-03 16:28 | 2012-07-04 09:20 | 10 | 1012 | 4281031 | 10120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER LEAKING OIL REPLACED TRANSFORMER 25KVA TIME ON 09:20 IDC XXXX
3024 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-08-12 11:04 | 2009-08-12 15:45 | 36 | 281 | 63662-1 | 10116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT REFUSED CAME BACK OUT--WIRE OFF INSL //COD 36// VER/DBM IDC XXXX
3025 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-12-15 10:49 | 2010-12-15 13:00 | 77 | 131 | H50404-1A | 10087 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE OUT ON STEPDOWN TRANS--FLAGERS AND HELP ON WAY //C PHASE STEP DOWN OUT 143 CUSTOMERS - CREW INSTALLING NEW STEPDOWN TR // ISO LF 37830149B00116 // OPENED OTHER STEPDOWN @ A PHASE 1049 & C AT 1158 ALL RESTORED @ 1300 THIS IS THE A PHASE OUTAGE 75 CUST VER/HFP L3/HFP IDC XXXX
3026 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-11-10 15:14 | 2014-11-10 15:23 | 1120 | 9 | 4717621 | 10080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER 204-264 TO SAFELY MAKE REPAIRS ON TICKET 4717551//COD1120 VER/CRB L3/HFP HFPC FP204-187 AJB
3027 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-07-03 17:59 | 2012-07-04 14:55 | 8 | 1256 | 4286571 | 10048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. I HAVE CUTOUT REPLACED CLOSED IN EVERYTHING OK. TICKET COMPLTED IDC XXXX
3028 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-02-13 17:35 | 2008-02-13 21:00 | 49 | 205 | 62809-1H | 10045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302// ONLY A & B PHASES OPEN INTITALLY//OPENED C PHASE @ 1735 TO ISOLATE POLE//STARTING CUST COUNT 41//INTERUPTED 50 MORE WHEN OPENED C PHASE//TOTAL 91//POLE TOP BURNT OFF//CREW REQUIRED// C PHASE CUSTOMERS OUTAGED ON THIS ORDER// - // VER/TOM IDC CHANGED TO PHA A XXXX
3029 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-07-26 11:40 | 2009-07-26 13:59 | 72 | 139 | H64110-1 | 10008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNED UP CROSSARMS OPENED "C" PHASE RECLOSER AT 1140 TO MAKE REPAIRS VER/KEP L3/KEP IDC DUP TO OPEN PHASE A XXXX
3030 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-06-18 00:40 | 2008-06-18 04:00 | 50 | 200 | 50185-1 | 10000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3003701/// BASKETT BURNT OFF ON LOAD SIDE OF RECLOSER NEED CREW. VER/JHM IDC XXXX
3031 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2016-06-11 15:25 | 2016-06-11 23:45 | 20 | 500 | 4336051 | 10000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 1127-3067 1 PHASE OPEN WIRE BURNT DOWN, CREW REQD. TRK OK. IN ALLEY. XFMER OPEN @ 16:54 // CREW REPLACING BROKEN POLE WILL WORK NEXT,,,CREW ON SITE,,REPAIRED WIRE AND BALANCED SME LOAD ON RISERS AJB
3032 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-01-08 22:18 | 2017-01-09 00:45 | 68 | 147 | 4278831 | 9996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN POLE 912-D-10/PRIMARY DOWN BETWEEN 912-10 AND 912-11///LOOKS LIKE IT BURNT INTO DUE TO BAD PLACE IN WIRE/////REPAIRS MADE//RESTORED AT 00:45//COMPLETE//EM VER/KEP L3/HFP HFPC FP38830912000010 AJB
3033 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-01-17 23:50 | 2013-01-18 06:00 | 27 | 370 | 4659371 | 9990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN A PHASE RECLOSER OPEN AT START OF OUTAGE 2 CUST *** SERVICER OPENED B-C AT 0130 . 27 CC *AT 0155 CREW CALLOUT.OLD WIRE FULL OF SPLICES FELL DOWN. WE PUT THE WIRE BACK UP AND CLOSED THE RECLOSERS VER/PDP IDCC CNT2 LOOKS LIKE PH B NOT A XXXX
3034 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2008-07-08 18:26 | 2008-07-08 18:58 | 330 | 32 | 65040-1 | 9988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3002104 CLOSED SWITCH ON POLE 1122 AT 1901 HOURS/ CLOSED SWITCH ON POLE 4495 AT 1858 ALL CUSTOMERS ON IDC CHANGED TIME OFF FROM 1835, HAD PHIL TOLLIVER WORKING ON BAD 600 AMP DISC THAT WAS FOUND XXXX
3035 | Hazard | 3310502 | HADDIX | CANOE | 2016-08-04 18:53 | 2016-08-05 00:15 | 31 | 322 | 4735611 | 9982 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S03BAD CUTOUT ON TRANSF AND ARRESTER =REPLACED == REFUSED LINE POWER OK VER/AWD AJB
3036 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-06-25 15:21 | 2008-06-25 16:20 | 169 | 59 | 53941-1 | 9971 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008001// POLE 70-656 BAD CUTOUT 65T // VER/TOM AJB PHASE B.
3037 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-04-17 17:02 | 2018-04-17 20:34 | 47 | 212 | 4247161 | 9964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire down between 378-C-15 and 378-C-273. recloser on pole 15 is in.. the wire thats burnt down is feeding the recloser pole. repairs made.. power restored @ 20:34. opened B & C @ 19:15 (21cc additional) closed 20:34/ A Phase 37830378C00015 (26cc) Out Originally/ L3/HFP/// trouble tickets show all out from start
3038 | Whitesburg | 3314401 | MAYKING | ERMINE | 2022-12-07 09:31 | 2022-12-07 14:25 | 115 | 294 | 4237611 | 9960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A Phase LF blown at 37830473000106 (Overall COD 65) and LF at 37830473000127 (COD 7) is also blown. Cutout at 37830473000202 (COD 2) is burnt up and will need to be replaced.A phase fuse opened on pole 473-106. Also A phase fuse opened off pole 473-127. Cutout gate burnt up on pole 473-127 causing it to blow fuse on pole 473-106. Bad cutout on pole 473-202.A phase fuse opened on pole 473-106. Also A phase fuse opened off pole 473-127. Cutout gate burnt up on pole 473-127 causing it to blow fu
3039 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-01-05 13:03 | 2013-01-05 17:00 | 42 | 237 | 4571561 | 9954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOK LIKE WIRE BROKE ON INS. CALLED CREW RELEASED BY CREW 078S08 LOOP OPEN POLE 163-6//REPAIRED LOOP ON POLE 6 POWER RESTORED AT 17:00 CLOSE TKT COD-42 ISO PO @ 38830163D30006 VER/HFP L3/HFP IDC XXXX
3040 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-03-22 01:51 | 2017-03-22 09:45 | 21 | 474 | 4576561 | 9954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | .BAD LINE CUTOUT ON POLE 37830170000022 === NEED BIG BUCKET AND 1 MAN ORLINE CREW WILL WAIT TILL START TIME/MADE MD TO SHOW LINE FUSE ON POLE 170-22 FEDING DIFF/ADH/ VER/AWD AJB
3041 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-02-10 23:02 | 2009-02-11 06:15 | 24 | 433 | 57562-1 | 9952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CALLED K BROWN TO HELP--AT 05:35 CLOSED IN AT 20-445 PICKING UP TO TRANSFORMER 20-371--AT 06:15 CLOSED IN AT 20-1069 TO TRANSFORMER 20 -368----UG PRIMARY CABLE BAD BETWEEN 20-368 A 20- 371-ISOLATED AN TAGED //VER/GAH MLR STEPS OF RESTORATION
3042 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-09-25 18:36 | 2018-09-26 11:45 | 41 | 1029 | 4156911 | 9948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need tree crew to clear poison ivy/ not sure if can is bad or connection bad/ opened transformer, Crew required. Bad 50kva 7200 transformer in back yard. yard dog access. Bring transformer sack. Access from 2638 Virginia ave. GH Released by crew 078H04,open line fuse 38830045B22521 @ 1045 line fuse in @ 1137,xfmr fuse in @ 1145 all cust restored please close ticket thanks.bt Released by crew 078H02
3043 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-03-14 11:00 | 2015-03-14 14:41 | 45 | 221 | 4193151 | 9945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE @ 496-13 NEED LINE CREW TO REPAIR 3 WAY DEADEND, OPEN RECLOSER ON POLE 472-29 @ 1030 & TAG TO V MULLINS/CREW ON SITE/FETR1500/VEM/UNSURE OF CAUSE/POLYMER CUTOUT ON FIBERGLASS BRACKET/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1441/PLASE CLOSE TICKET/THANKS/VEM/ ISO 38830472000029/ COD 45/ VER/BOW IDCC TOF0856 XXXX AJB
3044 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-02-15 13:00 | 2014-02-15 17:15 | 39 | 255 | 4390001 | 9945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE ON POLE 37830213000030 @ 1300 // MASSEY, LEWIS & MCCOWN //RMD DDC TAG PLACED TAG FOR DRM AT 14:26 CAN USE POLE EXTENSION/ POLE 213-175//1 36IN FIBER EXT./2 C/O,2L/A,1 1301IN,2 18IN CUT BRACKETS,2 LA,1 #2PDE,1 7.2INS COD-39 ISO LF 37830213000030 VER/HFP L3/HFP
3045 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2022-02-12 08:00 | 2022-02-12 09:55 | 132 | 115 | 4476341 | 9942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 35 customers on A phase line fuse blown on pole 48-147 will patrolA phase line fuse blown on pole 48-147 will patrol//6A primary burnt down in between poles 25-2 and 25-171////opened b & c phases up @08:54 to make repirsA phase line fuse blown on pole 48-147 will patrol//6A primary burnt down in between poles 25-2 and 25-171////opened b & c phases up @08:54 to make repairs///Repairs made closed in @ 09:55 and restored service
3046 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-03-18 09:35 | 2008-03-18 11:57 | 70 | 142 | 58114-1H | 9940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3407401// 1 PHASE ON GROUND AND GUY WIRE BURNED APART, OPEN AT POLE 1098-273 AT 09:35, #4 AA PULLED APART IN MID-SPAN...ALL WORK COMPLETE / GXJ IDC DUP TO OPEN RECLOSER XXXX
3047 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-02-02 18:20 | 2019-02-02 18:32 | 828 | 12 | 4749461 | 9936 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | short outage for mobile installation at Coalton station ¦¦¦ VERIFIED TIMES PER SCADA & DOL & SOS 19-070906 REV1
3048 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2021-03-28 02:24 | 2021-03-28 08:45 | 41 | 381 | 4388251 | 9921 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | sectionalizes @ pole 37830048D11252 is in/ will be patrolling/ closed 0n pole 37830048C21254 @ 0615 all on but 1 coustomer on 37830048C21431/ 37830048C21431 on @ 0845/ elbow still open on 37830048C21430/ no customers left out/ will call to log on circuit to make repairs on 3/28/21/ can close order 4388251
3049 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-05-18 18:39 | 2019-05-19 01:00 | 26 | 381 | 4295691 | 9906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED LINE CREW, FLAGGING CREW/ 167 KVA STEPDOWN I need a 167 kva xfmr, line crew with line truck and bucket, and flagging crew//cod 26 L3/HFP
3050 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-01-03 08:39 | 2014-01-03 16:00 | 23 | 441 | 4223361 | 9903 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 3 FUSES OPEN ON POLE 37830223D41125 POSSIBLE PRIMARY FAULT. PADMOUNT 37830223D41132 BAD, RELEASED BY CREW 077S043 FUSES OPEN ON POLE 37830223D41125 POSSIBLE PRIMARY FAULT. PADMOUNT 37830223D41132 BAD, 37830223D411132 ENERGIZED AT 15:40 --- 37830223D41126 ENERGIZED AT 15:45 --- 37830223D41133 ENERGIZED AT 15:55 --- 37830223D41183 ENERGIZED AT 16:00 POWER RESTORED.///? IDCC STP MISSING, CDC83 XXXX
3051 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-12-30 04:54 | 2019-12-30 09:00 | 47 | 246 | 4192691 | 9882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | recl,305-55 in @ 07:00 line fuse 330-45 open ,patrolling,,found bad arrester @ 329-39.line fuse 330-45 restored @ 09:00
3052 | Hazard | 3303902 | LESLIE | WOOTON | 2013-07-05 10:28 | 2013-07-05 14:35 | 40 | 247 | 4470941 | 9880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT GATE//COD 40// VER/DBM IDC XXXX
3053 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-04-02 19:28 | 2016-04-02 22:00 | 65 | 152 | 4024131 | 9880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-5092 BAD CUTOUT CHGED BACK ON// VER/ ADH AJB
3054 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-05-08 09:08 | 2022-05-08 11:25 | 72 | 137 | 4865341 | 9864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | pole39830975000023 loop open ( COD 72)pole 975-23 loop open
3055 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2015-10-31 20:40 | 2015-11-02 13:45 | 4 | 2465 | 4400181 | 9860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SPOKE WITH CUSTOMER AND THIS IS O/L ONLY - WILL HAVE CHECKED AT REGUALR SHIFT//TOM (TIME MODIFIED BY DST CHANGE)NEED XFMR 25 KVA 7200, CREW TO CHANGE , THIS IS ALSO TWO SERVICES SEWER PUMP AND GARAGE RELEASED BY CREW 077S12 REPLACED 25 KVA POWER RESTORED AJB
3056 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-06-22 13:24 | 2008-06-22 23:57 | 30 | 633 | 51827-1 | 9850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308002// FOUND BAD ARRESTER AND BAD 100 KVA TRANSFORMER ON POLE 1083..782 ..,,JEFF COMBS WILL BRING WITH HIM// ADJUST TIME IN HOIS - 10 COD STILL OUT ON POLE 1083-782 // OUT UNTIL TRANSFORMER REPLACED// BACK ON AT 2357 // AFTER BEING RESTORED, FOUND 2ND TRANSFORMER BAD WITH COD-15 // SEE #52573-1 // VER/LDA IDC XXXX
3057 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-21 10:26 | 2008-07-21 14:15 | 43 | 229 | 55683-1 | 9847 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF 140-14 OPENED REC. ON 140-136 10;00 BACK ON 2;15//3008701 MLR OK
3058 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-07-05 16:06 | 2022-07-06 10:20 | 9 | 1094 | 4384661 | 9846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 7.2 kv cutout on stepdown.. pole 37830179B00015.. Released by crew 077H18 replaced 2 cutouts power restored at10:20
3059 | Hazard | 3303902 | LESLIE | WOOTON | 2009-03-08 23:13 | 2009-03-09 01:42 | 66 | 149 | 56390-1 | 9834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | VER/HFP COD-66 WR # 28836853 FOUND BROKEN GUY WIRE ON POLE 535-35 WRAPPED AROUND NEUTRAL...REMOVED GUY CLOSED RECLOSER AT 01:42 RESTORING POWER L3/HFP IDC XXXX
3060 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-03-26 03:58 | 2014-03-26 12:15 | 71 | 497 | 4525691 | 9815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT POLE 227-59 ISOLATED POLE 227-57 RESTORED REC AT 0537 FAILED CUTOUT. WILL NEED 45 POLE RELEASED BY CREW 077S02 VER/SEF IDCC CNT101 PH C ONLY XXXX
3061 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-11-15 07:10 | 2016-11-15 10:15 | 53 | 185 | 4101441 | 9805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 38830020D37082 6A PRI. DOWN TRUCK TO POLE BEWARE OF DOGS RELEASED BY CREW 078S08 CREW ON SITE FETR 11:15 PWR RESTORED @ 10:15 PLEASE CLOSE TICKET LRM VER/CRB L3/HFP XXXHFP AJB
3062 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-05-05 19:48 | 2011-05-05 23:08 | 49 | 200 | 4013011 | 9800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED BAD ARRESTOR ON POLE 38830045B12082//WR#39851996TRIED FUSE CAME BACK OUT--R VIRGIN T BURTON ASSISTING- REPLACED -BAD ARRESTOR ON POLE 38830045B12088//VER/CRB IDC XXXX
3063 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-04-06 00:19 | 2009-04-06 03:35 | 50 | 196 | 65921-1 | 9800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONFIRMED 1 PHASE OUT AT RECLOSERS PATROLLING LINE// 7200 VOLT XFMR CUTOUT FAILED AT POLE 37830201B00374 INACTIVE XFMR REMOVED CLAMP ON POLE 37830201B00029 ATTEMPTING RESTORE//ONLY B PHASE WAS OUT RESTORED COMPLETE AT 03:35 IDCC CNT216 XXXX
3064 | Hazard | 3309302 | VICCO | JEFF | 2014-09-04 16:15 | 2014-09-04 17:25 | 140 | 70 | 4463611 | 9800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 37830348A00135, WE HAVE DEADEND INSULATOR BURNED UP AND CONDUCTOR SAGED BACK, NO POWER OFF RIGHT NOW BUT WHEN CREW GETS HERE WE WILL HAVE TO KILL LINE. NEED LINE CREW, 6 DEADEND INSULATORS FOR 19.9.//SERVICER OPENING RECLOSER 323-D-649, TO ISOLATE TROUBLE TO SWITCH 348-A-52. RECLOSER OFF @ 16:15 ON @16:19/ SWITCH 348-A-52 OPENPOLE 37830348A00135, SIWTCH CLOSED IN @ 17:25// COD 322// VER/ ADH L3/HFP HFPC CNT258 AJB REMOVED MOME REST STEP OF 4 MIN WITH 64 CUST. OMS CROSSER.
3065 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-11-15 13:58 | 2013-11-15 14:11 | 753 | 13 | 4041561 | 9789 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RE-OPENED RECLOSER AT POLE 190-D-313 AT 1358 TO REMOVE 2 LEADS TO SWS AT POLE 190-5 AND RESQUEEZE // 15 MINUTE OUTAGE // RESTORED AT 1411 //VER/GAH L3/HFP IDC XXXX
3066 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-03-15 11:24 | 2011-03-15 12:31 | 146 | 67 | H54446-1 | 9782 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 54446-1//@ 11:24, CREWS OPENED RECLOSERS ON POLE 1065-275 (INTERRUPTING 156 CUST, SEE H54446-1)// CREWS OPENED SWITCHES ON 1065-D2-287 TO ISOLATE HAZARD @ 11:38 (SEE 54477-1)//REPAIRED DOWN CONDUCTOR// CLOSED UNDER ARM BLADES ON POLE # 1065-D2-287 @12:24........CLOSED RECLOSER ON POLE# 1065-B-275 @12:31, THIS SHOULD RESTORE ALL CUST.// VER/DBM IDC XXXX
3067 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-05-13 00:54 | 2016-05-13 03:01 | 77 | 127 | 4210751 | 9779 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WHILE RESTORING CUSTOMERS ONE PHASE CAME OFF THE INSULATOR AT POLE 483-B-42// THIS IS MANUAL - WILL PROVIDE FETR AS SOON AS POSSIBLE//TOM VER/TOM L3/TOM AJB
3068 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-07-28 05:57 | 2010-07-28 13:50 | 24 | 473 | 58277-1 | 9777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 36180181 // UG LOOP OUT--- BAD CABLE -NOT POSSIBLE TO BACKFEED -// CABLE TESTING BAD BETWEEN PADMOUNT TR`S 20-A1-438 TO 20-A1-434STS WR # 36180181 // UG LOOP OUT--- BAD CABLE -NOT POSSIBLE TO BACKFEED - RELEASED BY CREW 078S07 VER/HFP L3/HFP IDCC CNT20 XXXX
3069 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-01-29 14:38 | 2014-01-29 15:00 | 444 | 22 | 4324211 | 9768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE CUTOUT - LEFT HAND PHASE ///A PHASE CUTOUT SMOKED UP// T. HALL SENDING CREW TO HAVE A CLOSER LOOK RELEASED BY CREW 074S05 // CREW OPENED RECLOSER TO ALLOW THEM TO REPLACE SWITCH THAT FAILED.A PHASE SWITCH - LEFT HAND PHASE /// OPENED ALL 3 RECLS @ 1438 CLOSED @ 1500 ISO OCR 38831152000271 VER/HFP L3/HFP IDC XXXX
3070 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-05-22 11:14 | 2010-05-22 11:30 | 610 | 16 | 66293-1 | 9760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECLOSER TO ALLOW THEM TO CLEAR A CUTOUT THAT HAS FAILED // RELATED TO ORDER 66281-1 /// COD-610 // OPENED RECL @ 1114 CLOSED @ 1130 // VER/HFP L3/HFP IDC XXXX
3071 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2011-03-27 08:09 | 2011-03-27 11:28 | 49 | 199 | 59637-1 | 9751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39319366 //LINE FUSE OUT ON 81-C-502.....POLE FIRE & BAD CUTOUT ON 81-C-504....NEED CREW...LINE FUSE OUT ON 81-C-502.....POLE FIRE & BAD CUTOUT ON 81-C-504....NEED CREW...//....EXTINGUISHED FIRE...BAYONETTED POLE....LEFT XFMR DE-ENERGIZED....NO LONGER SERVES ANY CUSTOMERS....RE-FUSED LINE CUTOUT ON 82-C-502.....POWER RESTORED...JRV, JOEY REED, ED MATNEY....03/27/11 COD-49 ISO LF 37820081C00502 VER/HFP L3/HFP IDC DCMT XXXX
3072 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2011-03-27 08:09 | 2011-03-27 11:28 | 49 | 199 | 59637-1 | 9751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39319366 //LINE FUSE OUT ON 81-C-502.....POLE FIRE & BAD CUTOUT ON 81-C-504....NEED CREW...LINE FUSE OUT ON 81-C-502.....POLE FIRE & BAD CUTOUT ON 81-C-504....NEED CREW...//....EXTINGUISHED FIRE...BAYONETTED POLE....LEFT XFMR DE-ENERGIZED....NO LONGER SERVES ANY CUSTOMERS....RE-FUSED LINE CUTOUT ON 82-C-502.....POWER RESTORED...JRV, JOEY REED, ED MATNEY....03/27/11 COD-49 ISO LF 37820081C00502 IDC XXXX
3073 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2018-03-30 09:21 | 2018-03-30 17:54 | 19 | 513 | 4154641 | 9747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNED OFF,NEED CREW.50FT POLE,XARM&BRACES,PINS&INSULATORS/ Fuse 38820992C00183 open/ lifting hot clamp @ 38820992C00214/ ISO 38820992C00183/ COD 19
3074 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-12-23 08:54 | 2022-12-23 11:45 | 57 | 171 | 4307471 | 9747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | One span #2 primary down from 92-366 to 92-367. Lf open on 92-142. Crew required. Trucks okay. No row. Could use flaggers to hold traffic. Released by crew 078S02 crew on site FETR 12:00LRMPWR rstored11:45please close
3075 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-16 13:49 | 2013-01-16 14:37 | 203 | 48 | 4611931 | 9744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ASSOCIATED WITH POWERON ORDER 4609341 - OPENED RECLOSER TO RESTORE CUSTOMERS TO NORMAL FEED// OPENED AT 1349 CLOSED IN AT 1437 // VER/TOM L3/TOM IDC XXXX
3076 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-06-08 07:24 | 2017-06-08 10:09 | 59 | 165 | 4922231 | 9735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONDUCTOR PULLED OUT OF SLEEVE AT POLE 38830160000065 //,,CREW ON SITE ,NEW FETR,10:15,ALL CUSTOMERS RESTORED,,SOLID BLADE 160-65 BACK IN @ 10:09 COMPLETE VER/AWD SJG
3077 | Hazard | 3303902 | LESLIE | WOOTON | 2009-12-08 21:41 | 2009-12-09 10:09 | 13 | 748 | 58550-1 | 9724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD PULLED OUT HOT LINE CLAMP RELEASED BY CREW 077S01... LINE NEEDS TO BE RESAGGED PER SERVICER/NEEDS CREW RESTORED AT 1009 AM VER/HFP L3/HFP IDC XXXX
3078 | Hazard | 3303902 | LESLIE | WOOTON | 2010-07-19 09:10 | 2010-07-19 09:50 | 243 | 40 | 52997-1 | 9720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 1309 INSULATOR ON A PHASE, POLE ON FIRE @ TELEPHONE ATTACHMENT BELOW NUETRAL. WILL HAVE TO OPEN 3 PHASE RECLOSER ON POLE 387-159 TO REPAIR.....OPEN RECLOSER 387-159 @ 09:10 & CLOSED BACK IN @09:50 HRS...P.HICKS ALL POWER RESTORED IDC XXXX
3079 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2009-02-18 06:20 | 2009-02-18 07:46 | 113 | 86 | 63712-1 | 9718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409402//ONLY C PHASE IS OUT ON POLE 149-248 (NEW POLE NOT ON MAP YET... IS JUST ABOVE POLE 149-68)//COD 113//FAILED CUTOUT ON PRI METER POLE 149-87//LIFTED HOTTAP TO ISOLATE ON SAME POLE... FEEDS NOTHING ACTIVE PER SERVICER//MD FILED//RESTORED ALL CUST @ 0746//WILL NOT CLOSE VER/KEP L3/KEP IDCC PN190 XXXX
3080 | Pikeville | 3407103 | TOPMOST | KITE | 2017-05-26 13:50 | 2017-05-26 21:00 | 64 | 430 | H4866451-A | 9712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE OUT ONLY OPENED A AND B PHASE OPENED AT 13:50 DUE TO BURNT OFF POLE 209-207. CLOSED IN N/O SWITCHES ON POLE 234-24 AT 15:20 TO OPEN SWITCHES ON POLE 209-285. AT 21:00 CLOSED RECLOSER IN ON POLE 209-25 UP TP OPENSWITCHES ON POLE 209-D4-258 AT 21:34 OPENED SWITCHES ON POLE 234-24 AND AT 22:02 CLOSED SWITCHES IN ON POLE 209-D4-258 UP TO N/O POLE 234-24 RESTORING ALL CUST. RELEASED BY CREW 074S11///OUTAGE RECORD FOR OPENING A & B PHASES/// VER/DKM AJB
3081 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-06-02 07:51 | 2013-06-02 09:40 | 89 | 109 | 4207791 | 9701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RICK RAY & ERIC MCKINNEY COD-89 ISO OCR 38830984000147 VER/HFP L3/HFP IDC XXXX
3082 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-11-25 22:01 | 2010-11-26 04:45 | 24 | 404 | 59641-1 | 9696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | D/S TO CALLOUT SERVICER....NEED ONE MAN TO HELP,.. FOUND LOOP BURNT INTO ON 195-57...P.HICKS...ALL POWER RESTORED @ 04:45 HRS..P.HICKS//VER/CRB IDC XXXX
3083 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-06-13 14:31 | 2012-06-13 15:05 | 285 | 34 | H4912001 | 9690 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | REGULATOR | ONE PHASE ON BUSSEYVILLE - LOUISA CIRC OUT ..MANUALLY INTERRUPTED LOUISA STATION AT 1431 AND RESTORED AT 1505 IDC XXXX
3084 | South Williamson | 3411401 | DEWEY | INEZ | 2010-06-22 13:37 | 2010-06-22 15:05 | 110 | 88 | 54619-1 | 9680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | RELEASED BY CREW 076H04 // OUTAGED WHEN HANDLE BROKE ON OCR ON 649-202 // BYPASS PUT IN AND POWER RESTORED @ 1505 AJB TON15:10 PER COMM. IDC XXXX
3085 | Hazard | 3309302 | VICCO | JEFF | 2021-11-03 10:45 | 2021-11-03 12:07 | 118 | 82 | 4052441 | 9676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PHASE OFF ARM ON MANUAL POLE 37830275000063 // OPENED RECLOSER @ open @ 1045 closed @1207
3086 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-04-28 21:15 | 2012-04-29 01:00 | 43 | 225 | 4720711 | 9675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "B" PHASE RECL OUT ONLY (43 CUST) - CONNECTOR BROKE ON LOAD SIDE OF RECLOSER - NEED 1 MAN & CONNECTOR - CALVIN WILLIAMS TO ASSIST - CLOSED RECL AT 0100 //VER/GAH IDC XXXX
3087 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-10-01 03:48 | 2009-10-01 10:15 | 25 | 387 | 60540-1 | 9675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308502//FUSE OUT ON POLE 174-D-456 - LEAD ON SOURCE SIDE BURNT OFF AND RE-ATTACHED TO LOAD SIDE OF FUSE - SERVICER REPORTED DUE TO LOCATION WAIT TO MAKE REPAIRS AT REGULAR WORKTIME.3308502//WIRE BURNED OFF LINE CUTOUT AT 37830174D00456 REQUIRES BIG BUCKET AND FLAGGERS CALLING FOR ASSISTANCE//SEND TO JEFF COMBS RELEASED BY CREW 077S04 RESTORED AT 1015 JKC DALE CUSTOMER COUNT WRONG ON THIS ADDED SEVERAL CUST AROUND 174-463 FROM 174-382 JUST GUESSING VER/KEP L3/KEP IDC XXXX
3088 | Pikeville | 3421001 | BREAKS | CITY | 2017-08-03 13:25 | 2017-08-03 14:19 | 179 | 54 | 4220461 | 9666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CROSSARMS PER DENNIS MASSEY//DAVE SAMMONS TO WORK OPENED RECLOSERS @13:25 CRACKED CUTOUT BURNT ARM CLOSED IN @14:19 D SAMMONS/ ISO 37820244000046/ COD 179/ VER/BOW L3/HFP XXXHFP SJG
3089 | Whitesburg | 3409503 | BURDINE | JENKINS | 2017-02-12 01:06 | 2017-02-12 11:10 | 16 | 604 | 4387091 | 9664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 077S12//CREW HAS ARRIVED AND TRYING TO LOCATE PROBLEM//L/F OPENE ON POLE 37830358D00237 //LIFTED HT ON POLE 37830358D00131//TRIED FUSE AND IT CAME BACK OUT//PUT HT BACK ON @ 1019 THIS DID NOT PICK UP ANY CUSTS//RELEASED BY CREW 077S12. BAD ARRESTER ON POLE 358-166. REPLACED ARRESTER AND CUT-OUT. RESTORED POWER AT 11:10 VER/CRB L3/HFP XXXHFP
3090 | Hazard | 3309302 | VICCO | JEFF | 2014-01-01 19:00 | 2014-01-01 22:30 | 46 | 210 | H4217421 | 9660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PHASE B HAS FELL DOWN IN ROAD, IN BETWEEN POLES 276-74 AND 276-75, COD-79 PULLED OUT OF SLEEVE, WILL NEED BIG BUCKET, 2 MEN AND FLAGGING CREW. OPENED RECLOSERS ON POLE 299-254 AT 19:00 HRS, COD-46 CLOSED AT 22:30 VER/KEP IDC XXXX
3091 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-04-22 09:39 | 2017-04-22 11:30 | 87 | 111 | 4667031 | 9657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE SECTIONALIZER CUT-OUT HAS FAILED @ POLE 99-14, WILL BE PATROLLING TO MAKE SURE NO OTHER PROBLEMS. FOUND NO OTHER TROUBLE, HAD TO OPEN TRANS. ON POLE 99-14 TO CHANGE SEC., OPENED @1112, CLOSED @1121, AND PUT SEC. BACK IN @1130. OPENED TFO ON 4667611. VER/AWD L3/HFP XXXHFP AJB
3092 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2012-08-09 01:39 | 2012-08-09 03:30 | 87 | 111 | 4914001 | 9657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLLED LINE // BROKEN FUSE LINK AT POLE 901-5574 //VER/GAH IDC XXXX
3093 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-10-12 07:29 | 2014-10-12 11:50 | 37 | 261 | 4608111 | 9657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ 1006 PATROLLING LINE //CHANGED BAD CUTOUT COD-37 ISO LF 37830380C00066 VER/HFP L3/HFP L3/IDC XXXX AJB
3094 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-12-29 08:08 | 2011-12-29 11:10 | 53 | 182 | 4212391 | 9646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | /PATROLLING LINEPATROLLING LINE, LOOP BURNT INTO ON POLE 134-46, CALLING FOR BIG BUCKET/ VER/KEP IDC XXXX
3095 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-12-06 11:19 | 2021-12-06 14:21 | 53 | 182 | 4151941 | 9646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B phase laying on the ground energized, had to open 3 600 amp switches at pole 21-51 to make safe// Tagged to Rodney Owens of DHE// no grounds Released by crew 074S09
3096 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-07-24 14:51 | 2012-07-24 18:00 | 51 | 189 | 4810681 | 9639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ONLY A PHASE RECLOSER LOCKED OUT CREW REQUIRED--TRUCK TO POLE--NEED REGULAR CROSSARM --3 PINS AND INSULATORS--BRACES--CUTOUT AND ARRESTOR RELEASED BY CREW 078S07//OPENED B AND C PH RECLS AT 17:15. ALL POWER RESTORED AT 18:00.//COD 112 IDC CHANGED TIME OFF FROM 1442 AND CNT FROM 112 XXXX
3097 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-04-02 13:52 | 2018-04-02 14:47 | 175 | 55 | 4165411 | 9625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 175 ISO 38830882D00151Cutout failed and burnt crossarm in two. No interruption but will have to open three switches on 882-151 to isolate fault pole 38830882D00078 .//OPENED @ 1352 Made repairs and closed switches on 882-151 at 14:47. sh Released by crew 076S02 L3/HFP
3098 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-10-17 12:53 | 2019-10-17 15:48 | 55 | 175 | 4162711 | 9625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Sleeve pulled out on 6A copper primary. Supervisor notified and will be sending a crew to assist. Made repairs and restored @ 15:48. sh
3099 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-16 19:40 | 2008-07-16 23:43 | 135 | 243 | 53419-1 | 9623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308401//WIRE DOWN AT POLE #133-153..TROUBLE ISOLATED ON POLE # 133-153...RESTORED POWER AT 20:50 TO EVERYONE BUT THE COAL CO...OPENED RECLOSER AT 23:18 MADE LOOPS UP RESTORED POWER 23:43// VER/DBM IDCC TON2018 XXXX
3100 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-07-31 00:11 | 2009-07-31 03:25 | 68 | 194 | 59346-1 | 9622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ON SITE, PATROLLING LINE, BAD INSULATOR AT POLE#770-C-50, OPENED UP AT POLE#770-C-45, POWER ON UP TO POLE#770-C-45 AT 0215 IDCC CNT85 STP TON XXXX
3101 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2013-03-05 20:50 | 2013-03-06 05:25 | 28 | 515 | 4874101 | 9620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 19.9 CUTOUT ON 5524-168, LINECREW REQUIRED. RELEASED BY CREW 078S11// CREW ON SITE// FETR 01:00 JEH/ REVISED FETR 03:30/ WIRE DOWN @524-274/FUSEOPEN@524-225/CLOSED STEPDOWN IN @ 00:25/REST UP TO 524-225/ PL#524-274 SPLIT OUT UP MIDDLE/ WILL TEMP.WITH 2/10 FT CROSSARMS TONIGHT/SEND TO TECH. TO WRITE PL. CHANGE-OUT. RELEASED BY CREW 078S11// CREW ON SITE// FETR 01:00 JEH/ REVISED FETR 06:00/ IDCC TON151 STEP 1, FP168, CDC92 XXXX
3102 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2010-02-05 03:55 | 2010-02-05 08:15 | 37 | 260 | 63153-1 | 9620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLED LINE AND NO HAZARDS FOUND ATTEMPTING RESTORE//WILL NEED ASSISTANCE AT FUSE CALLING FOR BIGGER BUCKET//INSULATOR BAD ON POLE 37830175000108 WR#33753022 IDC XXXX
3103 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2008-11-08 07:27 | 2008-11-08 15:25 | 96 | 478 | 63206-1 | 9618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 571-104 BURNT DUE TO CUTOUT, HAS 25KVA TRANSFORMER RUNNING PRIMARY DEADEND ONE DOWN GUY AND 1/0 LASH, IS TRUCK ACCESIBLE WILL NEED NEW POLE, 40 CLASS 5 WILL BE FINE,,,RECLOSER BACK IN A 08:55 . JIM LINKOUS ENROUTE TO REPLACE POLE. ALL POWER RESTORED AT 15:25// THERE WERE ONLY 2 CUSTOMER OUT NOT 4 - PER JIM LINKOUSE// VER/TOM IDCC PN183, LOOKS LIKE 3 CUSTOMERS PLUS ONE MISMAPPED DID A MD XXXX
3104 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-01-11 06:43 | 2013-01-11 06:56 | 739 | 13 | 4594831 | 9607 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARCOSED STEVE BREWER TO ASSIST DUE TO BAD CUTOUT POLE 45-7154 //BAD CUTOUT AND LA POLE 45-7154 CHGED OPENED REC. POLE 69-5017 06:43 ON 06:56 VER/ARN IDCC MCCNI XXXX
3105 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-01-01 00:45 | 2008-01-01 10:10 | 17 | 565 | 52154-1 | 9605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310501 //POLE 991-1 WE HAVE LINE FUSE OUT, POLE 991-15 BROKE OFF AT THE GROUND. MANUEL SET ACROSS CREEK IN BOTTOM. PRIMARY WIRE BROKE. LINE FUSE SIZE 15T ON 991-1. POWER RESTORED// MAP DISC ISSUED//// VER/TOM IDCC PN53 XXXX
3106 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-06-11 06:55 | 2020-06-11 10:15 | 48 | 200 | 90110813 | 9600 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | fault @ 1099-90. open intelleropter @ 1099-6965 & tagged to ddc. open 3 600a disc @ 1099-68 & ddc tag. hold order to mphelps. Released by crew 078S07 sjg related to 90110811
3107 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-04-02 21:18 | 2015-04-03 00:30 | 50 | 192 | 4260861 | 9600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARM BURNT OFF AT POLE963C134 PHASE IS HANGING IN MIDAIR NEED CREW AND BIG BUCKET CUSTOMER SAID WE CAN GET IN THEIR YARD TO MAKE REPAIRS .// NO POWER OUT UNTIL 2118 WHEN B PHASE RECL OPENED DUE TO PHASE ON TELEPHONE CABLE (50 CUST) // OPENED A & C PHASE @ 2330 (83 CUST) /// ALL ON @ 0030 04/03 SEE H4260861 VER/HFP L3/HFP AJB
3108 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2012-11-09 08:00 | 2012-11-09 10:40 | 60 | 160 | 4376041 | 9600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY CONDUCTOR BROKE AT STIRRUP. WORKING TO ISOLATE - CREW ENROUTE TO MAKE REPAIRS. OPENED SWITCH ON 38830786A00110 @ 9:20 TO ISOLATE. REPAIRS COMPLETE. CLOSED SWITCH ON 786-110 @ 10:35. CLOSED RECLOSER ON 785-1266 @ 10:40 RESTORING REMAINING OUTAGED CUSTOMERS. SH ///VER/CRB L/3 CRB IDC XXXX
3109 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-02-21 14:16 | 2015-02-21 16:46 | 64 | 150 | 4064271 | 9600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | B PHASE RECLOSER OUT ON POLE 449-854 COD-64 RECL AT 473-334 IS ON "B" PHASE MD FILED /B PHASE OFF INSULATOR AT POLE 473-125 & BLOWING TOGETHER, OPEN SOLID BLADES ON POLE 473-120 TO ISOLATE/OPENED RECLOSERS AT 16:33, ISOLATED SOLID BLADES CLOSED RECLOSERS AT 16:46 ., CLOSED SWITCH AT 1824 TIE WIRE BROKE DUP CREATED VER/KEP AJB
3110 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-05-14 08:40 | 2017-05-14 10:00 | 120 | 80 | 4797041 | 9600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 231-45 CREW REQUIRED TRUCKS OK #4 COPPER/TAGGED TO TACKETT GROUND PLACE AT RECLOSER /TOOK RECLOSER OFF AT 0840HRS RELEASED BY CREW 078S03,,CREW ON SITE 38830207D22140 38830231000045 231-45 CREW REQUIRED TRUCKS OK #4 COPPER/TAGGED TO TACKETT GROUND PLACE AT RECLOSER /TOOK RECLOSER OFF AT 0840HRS RELEASED BY CREW 078S03,,CREW ON SITE,,WIRE PULLED OUT OF SLEEVE,,ALL REPAIRS COMPLTED, ALL POWER RESTORED VER/AWD AJB
3111 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-05-11 05:46 | 2010-05-11 09:40 | 41 | 234 | 59303-1 | 9594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000301// WILL BE DISPATCHED IN THE A,M, POLE 44-316 BAD CUTOUT POLE 44-4064 30T INSTALLED CUTOUT ON POLE 44-336 15T FOR MAPPING//COD 41//MD FILED // VER/DBM IDC XXXX
3112 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-12-16 10:29 | 2016-12-16 12:32 | 78 | 123 | 4200651 | 9594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELATED TO 4200341 // THIS ORDER CONTAINS TROULBE FROM THAT ORDER // STEPDOWN HAS RISER BURNT OFF AJB
3113 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2022-02-11 08:52 | 2022-02-11 12:30 | 44 | 218 | 4467481 | 9592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 38830308000018 solid blade riser broke at c/o line side --repaired-in at 12:30-allgood-ds021122
3114 | Hazard | 3310502 | HADDIX | CANOE | 2010-03-26 11:13 | 2010-03-26 15:39 | 36 | 266 | 54661-1 | 9576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34413659 //GOT POLE # 50-59 TOP BURNED OFF NEED CREW AND OTP AND INS. AND CUTOUT AND ARRESTOR 19.9KV COD-36 VER/HFP L3/HFP IDC XXXX
3115 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-07-14 17:13 | 2010-07-14 19:45 | 63 | 152 | H66666-1 | 9576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONFIRMED C PHASE RECLOSER OPEN PATROLLING LINE//ATTEMPTING RESTORE//LINE WONT STAY PATROLLING MORE//15:15 RESTORED TO OPEN SWITH AT POLE 200-368//C PHASE IS DOWN AT POLE 37830223C00152 OPENING ALL PHASE TO MAKE REPAIRS ALSO POLE 37830223C00466 IS BURNED OFF WILL HAVE TO LOWER XFMR AND PRIMARY IDCC DUP TO OPEN 2 RECLOSERS XXXX
3116 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-01-09 00:53 | 2015-01-09 02:20 | 110 | 87 | 4922511 | 9570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP IS BURNED OFF REC. RISER ON POLE 38831126A00077 // WILL REPAIR/// REPLACED RISER AND HOT TAP // POWER RESTORED @ 2:20 VER/HFP L3/HFP AJB
3117 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-04-30 04:56 | 2014-04-30 06:57 | 79 | 121 | 4649891 | 9559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE RECLOSER OPEN PATROLING LINE RELEASED BY CREW 078S07 // B PHASE - 89 COD// 79 RSTORED WITH THIS OUTAGE - 10 TRANSFERRED OUT TO OTHER OUTAGE.//CAPTURE TIMES ACORDINNGLY VER/TOM L3/TOM IDC XXXX
3118 | Hazard | 3310502 | HADDIX | CANOE | 2008-01-25 11:20 | 2008-01-25 11:59 | 245 | 39 | 59575-1HA | 9555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310502// COD-1235 // TOP OF POLE BROKE OFF // WILL LOWER LINE ON POLE & REPLACE CROSSARM//3310502 RELEASED BY CREW 077S05 VER/LDA DEBBIE/149 CUST OFF AGAIN ON ORDER 59575-1H...245 CUST OFF AGAIN ON ORDER 59575-1HA IDC XXXX
3119 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-01-17 16:17 | 2010-01-17 20:50 | 35 | 273 | 55579-1 | 9555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF == NEED 2 LINE MAN == MANUAL POLE == LOWER EVERYTHING DOWN ON POLE ==REFUSED POWEROK VER/TOM L3/TOM IDC XXXX
3120 | Whitesburg | 3312901 | JENKINS | KONA | 2012-07-31 17:21 | 2012-07-31 22:02 | 34 | 281 | 4872491 | 9554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LINE FUSE ON POLE 404-68 IS OPEN. PATROLLING LINE. REFUSE CUT-OUT ON POLE 404-68. HOWEVER, ON POLE 404-45, THE JUMPER THAT IS SUPPLYING POWER TO LATERAL IS BURNT IN-TO. APPROXIMATELY 4 FEET OF JUMPER IS HANGINNG DOWN HOT. NEED BIG BUCKET AND TWO MEN TO CLEAR JUMPER AND MAKE REPAIRS. SEND TO CECIL SEXTON RELEASED BY CREW 075H01 COD-34 ISO PO @ 37830404B00045 VER/HFP L3/HFP IDC XXXX
3121 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-07-11 05:14 | 2015-07-11 22:55 | 9 | 1061 | 4773951 | 9549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED-TRUCK OK- NEED AWP FOR TRAFFIC CONTROL ON US 23-NEED TECH- POLE- 39830902A00659 IS BURNT OFF AT CUT-OUT LINE FUSE ON POLE-39830902A00029 IS OUT IT FEEDS POLE 902-659 AND POLE 902-741 ( THIS FEEDS 4 APTS.) RELEASED BY CREW 078H18.. CREW ON SITE ETR 22:30.. NEW ETR 23:30.. LINE FUSE BACK IN AT 22:55.. COMPLETE//COD 9
3122 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2016-03-30 17:04 | 2016-03-30 23:17 | 34 | 373 | 4006531 | 9530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078S01/UNSURE OF CAUSE /PATROLLED LINE FOUND NO HAZARDS/FUSE CAME BACK OUT/CREW CHANGING HARDWARE ON POLE 334-17/VEM/INSTALLED TWO FUSES ON 334-126/FEEDING TOWARDS POLE334-82 BACK IN AT 2115/VEM/ISOLATED HOT TAP 344-102/FUSE ON 334-126 IN AND HOLDING AT 2157/VEM/FETR FOR TWO REMAINING CUST 2345/VEM/LAST TWO CUST RESTORED 2317/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 AJB
3123 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-10-09 05:01 | 2014-10-09 05:11 | 953 | 10 | 4577341 | 9530 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP L3/HFP AJB CCTIN FEC57 PER TRANS LOG AND DISP LOG.
3124 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-09-01 07:38 | 2019-09-01 09:45 | 75 | 127 | 4970421 | 9525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 37830446000204/19.9 solid blade power restored at 09:45 L3/HFP
3125 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-01-16 00:40 | 2012-01-16 01:00 | 476 | 20 | H4263241 | 9520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | <<C PHASE RECLOSER ONLY>> OPEN ON 38830785D40121 DUE TO PRIMARY CONDUCTOR BREAKING AT STIRRUP ON LINE SW POLE 809-81. OPENED SWITCHES ON 809-81 @ 00:40, COMPLTED REPAIRS AND CLOSED SW @ 1:00. CLOSED PH C REC ON 785-121 @ 1:05 RESTORING ORIGINAL OUTAGED CUSTOMERS. SH RELEASED BY CREW 076S02 IDC XXXX
3126 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-10-12 10:54 | 2011-10-12 11:50 | 170 | 56 | 4970131 | 9520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF AT 94-6510 "B" PHASE ONLY COD-30 OPENED RECLOSER AT 94-6503 TO ISOLATE AND REPAIRPOLE 94-6510 HOT TAP BURNT OFF OPENED REC. POLE 94-6503 11;32 TILL 11;50 SEND NOTE TO RAYBURN NUMBER 4 WIRE NEEDS TO BE UPGRADED NUMBER 2 RISER 2-OUTAGE IDCC CNT191, PH A NOT B XXXX
3127 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-04-28 09:17 | 2008-04-28 14:30 | 38 | 313 | 54873-1 | 9518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201// POLE TOP BURNT OFF ON POLE 403-59. OPENED SOLID BLADE ON POLE 403-52. BAD POLE IS 40 CLASS 5 WITH XFORMER AND PRIMARY TAP. MAY GET TRUCKS TO POLE. RELEASED BY CREW 078S01---CREW ON SITE 1230, , FETR 1500----ALL CUST BACK ON 1430//VER/CRB IDC XXXX DEB OK
3128 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-11-16 21:35 | 2010-11-16 22:24 | 194 | 49 | 56892-1 | 9506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE ON FIRE--OPEN RECLOSER ON POLE 38830070B12016 AT 21:35-INSTALLED TAG AN GROUNDS--MADE TEMPOARY REPAIRS-E MAIL TO MARTIN AN TOLLIVER--POLE NEEDS REPLACED 11-17-10-REMOVED GROUNDS AN TAGS // COD-194 /// SENT EMAIL AS REQUESTED ... CREW TO REPLACE TOMORROW 11/17/10 VER/HFP L3/HFP IDC XXXX
3129 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-12-12 00:37 | 2008-12-12 10:31 | 16 | 594 | 57190-1 | 9504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE RECLOSER OUT ON POLE# 296-1477, CONDUCTOR DOWN 1 POLE FROM RECLOSER POLE,,FAULT POLE 296-612 RELEASED BY CREW 077E01//3300602//COD 16MIDDLE PHASE RECLOSER OUT ON POLE# 296-1477, CONDUCTOR DOWN 1 POLE FROM RECLOSER POLE,,FAULT POLE 296-612 RELEASED BY CREW 077E01//3300602//BROKE AT STIRRUP VER/KEP L3/KEP IDCC PN352 XXXX
3130 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2008-10-17 17:03 | 2008-10-17 20:14 | 50 | 191 | 56670-1 | 9494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP RELATED TO ORDER 56669-1 CHANGED THE TIME OFF OF THIS ORDER TO FIRST CALL TIME IN ORDER 56669-1...50 CUSTOMERS INTERRUPTED IN THE RUSSELL-KENWOOD NOT 27, DUE TO SWITHCING & MAPS NOT BEING CORRECT. 4 CUSTOMERS RESTORED @ 2000, REMAINING 46 CUSTOMERS RESTORED @ 2014 IDCC CNT4, TOF1705, STEP MISSING COUNT, CDC45 XXXX
3131 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2011-04-21 09:09 | 2011-04-21 15:00 | 27 | 351 | 61623-1 | 9477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONLY B PHASE - CENTER PHASE 27 CUSTOMERSTWO SPANS OF PRIMARY DOWN CREW ENROUTE./// OPENED OTHER 2 RECLS @ 1324 ALL RESTORED @ 1500 (A & C PHASE TOTAL 27 CUST) ISO RECL 37820197000098 SEE H61623-1 VER/HFP L3/HFP IDC XXXX
3132 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-07-10 11:57 | 2020-07-10 16:00 | 39 | 243 | 4141091 | 9477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required bad cutout/big bucket Released by crew 078S03
3133 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-06-18 17:26 | 2022-06-19 19:45 | 6 | 1579 | 4242691 | 9474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | lifted tap to isolate trouble/// MADE REPAIRS AND RESTORED @19:45
3134 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-05-11 13:42 | 2013-05-11 15:45 | 77 | 123 | 4104401 | 9471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE OUT 77 CUST //B PHASE REC. OPEN ON 38820794D00029// PATROLING// FOUND BROKEN LINE CUTOUT BACK ON MTN. ON 38820819A00023// ISOLATED CUTOUT// ALL IT FED WAS AN INA. XFMR ON SIDE TAP, LEFT NO ONE OFF// CLOSED REC. // POWER IS RESTORED COD-77 ISO OCR 38820794D00029 VER/HFP L3/HFP IDC XXXX
3135 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2011-02-05 16:15 | 2011-02-05 19:55 | 43 | 220 | 54526-1 | 9460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DUPED DUE TO AREA CROSSOVER// "A" PHASE ONLY COD-33/PHASE A RECLOSER OPEN ON POLE 966-A3-619.....PATROLLING NOW.....BAD CUTOUT ON PHASE A ON POLE 966-C2-607...HAVE ISLOATED CUTOUT....HAVE PATROLLED WHAT I CAN SEE OF LINE, WHICH IS NOT MUCH....MOST OF LINE IS WAY UP ON HILL...IF NO HZRDS, WOULD LIKE TO CLOSE RECLOSER ON 966-A3-619// IDC PHASE C NOT A XXXX
3136 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-04 17:15 | 2013-01-04 17:59 | 215 | 44 | 4569401 | 9460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | SWITCHING TO TRANSFER LOAD AND ISSUE HOLD ORDER TO CREW TO REPAIR FLOATING PHASE AT POLE 164-C-25. --- SDB / 1715 / SW 275 & SW 250 OPENED. 317 CC OUTAGED --- SDB / 1718 / SW 267 CLOSED. REST 102 CC @ 1756 OPEN 165-267 CLOSED 164-250 @ 1759 CLOSED 215 ALL CC REST. VER/PDP IDCC PN100, REMOVED 102 CUSTOMER 3 MIN STEP ON AT 17:18, CDC98 XXXX
3137 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-12-03 02:42 | 2009-12-03 05:25 | 58 | 163 | 61884-1 | 9454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY AND NEUTRAL DOWN BETWEEN POLES 621-42 TO POLE 621-41, I WILL PUT WIRE UP MYSELF ,,,POWER RESTORED VER/KEP L3/KEP IDC XXXX
3138 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-01-14 01:54 | 2012-01-14 03:03 | 137 | 69 | H4260051 | 9453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED 4 MAN CREW PLUS FLAGGERS--OPENEN AN -TAGED C PHASE RECLOSER PRIMARY DOWN BETWEEN POLES 38830068A00096 AND 38830068A00095 RELEASED BY CREW 078S07 144 CUSTOMERS AT THIS TIME/ HAD C PHASE DOWN BACK ON AT 3:03 VER/ARN IDCC DUP TO OPEN PH B AND A XXXX
3139 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-07-12 13:51 | 2011-07-12 14:08 | 556 | 17 | H4528171 | 9452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ONLY B PHASE OUT (MIDDLE PHASE)---POSSIBLE BAD POST TOP ---WILL HAVE TO DROP 3 DV AT POLE 270-183-1 HOUR--NOT SURE IF THIS IS FAULT TIL WE LOOK AT CLOSER-FETR -1400--JEFF COMBS CREW--B PHASE OUT 0730-1405--A&C 1315 TIL 1405-- RELEASED BY CREW 077S06 IDC XXXX
3140 | Hazard | 3303902 | LESLIE | WOOTON | 2009-05-01 06:32 | 2009-05-01 08:55 | 66 | 143 | 61585-1 | 9438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902 -BAD 27KV CUTOUT//VER/CRB IDC XXXX
3141 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-31 14:15 | 2009-02-02 18:32 | 3 | 3137 | 53503-1 | 9411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1/0 SEC DOWN. 25 KVA TRANSFORMER (7.2 KVA) IS BAD//THIS HAS BEEN REPAIRED PER TIM HALL
3142 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-08-22 07:04 | 2019-08-22 11:59 | 33 | 295 | 4925491 | 9399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 597-4 LF off @ 0828Opened LF on 597-4 @ 0828 taking additional 4 customers out. Bad 333 step dn on 597-5 crew required.Opened LF on 597-4 @ 0828 taking additional 4 customers out. Bad 333 step dn on 597-5 crew required. Released by crew 078S11
3143 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2021-01-23 15:35 | 2021-01-23 18:13 | 68 | 158 | 4887251 | 9384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ETA 1640//OPENED SOLID BLADES 37830018D00007//COD 68//Wire down from 37830018D00008 to 37830018D00009. Opened 300 amp switches @ 18D-7 @ 17:00 to make repairsWire down from 37830018D00008 to 37830018D00009. Opened 300 amp switches @ 18D-7 @ 17:00 to make repairs. Repairs made and restored @ 18:13
3144 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-11-11 19:50 | 2022-11-11 22:10 | 67 | 140 | 4130071 | 9380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OCRs at 166-B1-364 Off 1950 due to broken crossarm ready to fall/38830166B10364 rec open at 19:50 taging to mr t lewis---38830165A00110 45/4 dbl arm burnt off just above braces.crew in route--ds11112238830166B10364 rec open at 19:50 taging to mr t lewis---38830165A00110 45/4 dbl arm .. pole burnt off just above braces.crew in route--ds111122 Released by crew 078S01
3145 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-01-04 16:40 | 2016-01-04 23:19 | 32 | 399 | 4584961 | 9380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DIP FUSE BLOWN ON POLE# 24-548 WILL RE-FUSE/// FUSE CAME BACK OUT/// NEED CREW TO CHECK UNDERGROUND PRIMARY AND XFMS///PARTIAL RESTO FROM 1917 TO 2012 REPAIRED UG CONDUCTOR AND CLOSED DIP FUSE IN @ 23:19 AND RESTORED SERVICE RELEASED BY CREW 074H17 VER/KEP AJB AJB
3146 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-05-05 22:50 | 2018-05-06 03:43 | 32 | 293 | 4313171 | 9376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Step down transformer on pole 38830092B00269 failed, 250 kva, Trucks to pole. Released by crew 078H04 L3/HFP
3147 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-12-21 12:35 | 2017-12-21 14:06 | 103 | 91 | 4662551 | 9373 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | outage to safely replace pole 118-89 PO#4661381/ COINS call placed/ OPENED RECL @ 1235 closed back in @ 14:06 please close tic RM
3148 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2012-07-25 13:04 | 2012-07-25 13:25 | 446 | 21 | 4825381 | 9366 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | ARRESTER | 2153502 446 CUSTOMERS LOVELY WOLF CREEK 34KV LINE THAT FEEDS THE MIDDLE BURNING CREEK STATION OUT FROM KY SIDE.
3149 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-06-11 18:19 | 2011-06-12 11:39 | 9 | 1040 | 4297411 | 9360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 MAN CREW NEEDED TO REPLACE BROKEN CUTOUT ON ARM BKT, NOT TRUCK ACCESSIBLE, BRING C/O & ARR AND 12 BKT TO POSSIBLY MOUNT ON POLE; POLE HARD TOO SEE FOR TREES...M HATFIELD --- SDB / 1139 / RESTORED. VER/SDB IDC XXXX
3150 | Hazard | 3310502 | HADDIX | CANOE | 2014-09-14 00:24 | 2014-09-14 05:27 | 73 | 303 | 4497481 | 9354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN ON POLE 37830099000042, NEED TWO MEN AND BIG BUCKET LOOK LIKE #4 AL IS ROTTED AND BURNED DOWN ON POLE 99=26 TOOK CLAMP OFF AND GONG TO RECLOSER CLOSED CLAMP AT0222 VER/SEF /// SEE 4497531 FOR OUTAGE TO MAKE UP LOOPS /// L3/HFP AJB
3151 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2020-06-09 00:39 | 2020-06-09 03:05 | 64 | 146 | 4982131 | 9344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser open on 241-284 will patrol/// Loop burnt into on pole 241-3///will make repairs/// Repairs made closed recloser in @ 03:05 and restored service // cod 64 //
3152 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2011-04-20 14:36 | 2011-04-20 17:02 | 64 | 146 | 61325-1 | 9344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39649800 //RECLOSER ON POLE 454-3516; FAULT POLE 478-1053 BAD CUTOUT; ALL POWER RESTORED AT 1702 CLOSE TICKET COD-64 ISO RECL 38830478A31007 VER/HFP L3/HFP IDCC PN1007 XXXX
3153 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2015-05-26 18:54 | 2015-05-27 00:40 | 27 | 346 | 4467511 | 9342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OPEN ON #1122C-78 TREES ON PRI. AT #1122C-235, WILL NEED MANUAL TREE CREW,/JPS RELEASED BY CREW 078E09,,CREW ON SITE..TREES NOT THE PROBLEM,,BAD ARRESTER ON POLE 39831122C00097,,REPAIRS MADE, ALL POWER RESTORED VER/KEP AJB
3154 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-09-27 17:03 | 2011-09-27 17:14 | 848 | 11 | H4925121 | 9328 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | 69-12KV TR 1 TRIPPED DURING MOBILE TRANSFORMER INSTALLATION - SDB / 1647 / ALL CUST RESTORED. 848CC// SCADA INDICATED BREAKER TRIPPED BACK OUT @ 1703 ARRESTORS BLEW ON POLE 37830225B00427 WHICH COULD HAVE BE DUE TO EARLIER OUTAGE ON ORDER 4925121 -- RESTORED @ 1714 --- COD-848 ISO FB VER/HFP L3/HFP IDC XXXX
3155 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-06-20 07:25 | 2014-06-20 10:03 | 59 | 158 | 4119991 | 9322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | BAD REC. LIGHTING RELEASED BY CREW 078S08BAD REC. LIGHTING RELEASED BY CREW ISOLATED RECLOSURE ON PN 92-93 REFUSED STEPDOWN PN 92-964 POWER RESTORED AT 10:33 PLEASE CLOSE TICKET THANKS DWW AJB CNT110
3156 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-02-02 19:50 | 2014-02-03 11:48 | 77 | 958 | 4338731 | 9318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE BURNTED OFF, POLE 1024-286, LIFTED HTSP ON POLE 1024-175, GROUNDED AND TAGGED TO DDC, CREW REQ, BUT NOT TILL TOMMORROW, JUST FEEDS A BILL BOARD SIGN, 354 POLE. CAN NOT GET TRUCK TO POLE RESTORED ALL OTHER CUST AT 2140 AT THIS LOC HOLD TAG PLACED FOR DDC - CONTACT DDC UPON ARRIVAL//HOLD TAG PUT IN LLOYD RAYBURN NAME AT 1145 ON 02-03-2014 VER/CRB L3/HFP IDC XXXX
3157 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-09-22 07:55 | 2017-09-22 14:40 | 23 | 405 | 4381291 | 9315 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | GOT FUSE OUT ON POLE 38830785D20210..LOOKING IT OVER NOW. FUSE CAME BACK OUT.. GOING TO BE LOOKING OVER MORE..OPENED OTHER TWO RISER CUTOUTS ON POLE 785-210.. MADE UP SECONDARY LOOPS UP ON POLE 785-208. TWO FEED CUSTOMERS FROM POLE 785-207.. OPEN TRANSFORMER ON 207. AT 14;10 AND CLOSED BACK IN AT 14:40. TO RESTORE POWER.. CREATED 4382851 TO REFLECT 785-207 OUT. VER/AWD VER/ALB L3/HFP HFPC DUP MCCDL CDC83
3158 | Hazard | 3302704 | HAZARD | KENMONT | 2017-03-17 13:57 | 2017-03-17 16:12 | 69 | 135 | 4565031 | 9315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON LOAD SIDE OF SET DOWN CALLED FOR LINE CREW === REPLACED CUTOUT === POWER OK 1612/ ISO 37830296D40216/ COD 69/ VER/BOW AJB
3159 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2018-12-21 21:50 | 2018-12-22 01:00 | 49 | 190 | 4588971 | 9310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | line fuse blown on 1060C22. patrolled line found #4 cu primary down at 1060-B-119. looks like it burnt down under a stirrup. crew is en route. crew arrived ,made repairs, restored power at 01:00 L3/HFP
3160 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2019-06-05 13:37 | 2019-06-05 15:24 | 87 | 107 | 4431611 | 9309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Found bad cutout on 571-61, was able to clear up. Apr at 1524 close ticket
3161 | Pikeville | 3401001 | ELWOOD | DORTON | 2020-11-30 10:29 | 2020-11-30 15:51 | 35 | 322 | 4730761 | 9307 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Have 2 broke crossarms on pole 287-103 and 287-99,Have contacted Paul Layne and he is getting material together and headed my way,Will have to open other 2 fuses and ground at 287-18 to make repairs will keep up with time.//B PHASE OPEN ONLY// OPENED OTHER TWO PHASES @ CLOSED@Have 2 broke crossarms on pole 287-103 and 287-99,Have contacted Paul Layne and he is getting material together and headed my way,Will have to open other 2 fuses and ground at 287-18 to make repairs will keep up with ti
3162 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-03-23 15:31 | 2022-03-23 18:18 | 81 | 167 | 4663291 | 9301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | sleeve failed,
3163 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2009-06-02 20:57 | 2009-06-03 09:52 | 12 | 775 | 62821-1 | 9300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED, R MARCUM KNOWS WHAT HE NEEDS, WILL WORK TOMORROW RELEASED BY CREW 080S01. A&B PHASE IS OPEN. WE WILL OPEN C PHASE TO MAKE REPAIRS IDC XXXX
3164 | Hazard | 3310502 | HADDIX | CANOE | 2009-01-29 18:52 | 2009-01-29 23:25 | 34 | 273 | 51647-1 | 9282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502//--LAST LINE FUSE IN JOE LITTLE-BAD 19,9 CUTOUT-BURNT LINE DOWN 6A 26-6 30T FUSE--NEED TO CORRECT COUNT AJBC CNT24
3165 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-08-18 11:25 | 2009-08-18 13:50 | 64 | 145 | 64360-1 | 9280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 50 T FUSE OUT DUE TO BAD ARRESTER ON POLE 188D195. I WILL BE CHANGING. ARRESTER CLEARED UP AND CHANGED FUSED UP EVERRTHING OK. VER/KEP L3/KEP IDC XXXX
3166 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-03-03 19:49 | 2017-03-04 12:58 | 9 | 1029 | 4517341 | 9261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE ON HILL BEHIND DOUBLE WIDE TURN DOWN TURNIP LN RELEASED BY CREW 077H14 BAD TRANSFORMER NEED 25 KVA 7200 RELEASED BY CREW 077H04/ ISO 37830124000055/ COD 9/ MD DONE/ VER/BOW
3167 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-09-05 20:38 | 2015-09-05 20:53 | 617 | 15 | 4208391 | 9255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED ERMINE 12KV CB A VIA SVC AT SERVICER REQUEST DUE TO POLE FIRE ON ANGLE POLE// UNSAFE TO APPROACH WHILE ENERGIZED// ALL CUSTOMERS WILL BE RESTORED AS QUICKLY AS POSSIBLE//TOM APPROX OUTAGE TIME 20MIN.. - SEE 4208311 FOR ORIGINAL OUTAGE DETAILS VER/TOM L3/TOM AJB
3168 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-04-29 12:23 | 2020-04-29 14:37 | 69 | 134 | 4767681 | 9246 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DOL1014258///CB was on NRO and went out ands found bad relay on CB after it tripped - transferred customers to Pounding Mill cktvulcan breaker malfunctioned,isolated vulcan breaker and fed vulcan circuit customers from Freeburn breaker. Released by crew 079S03
3169 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-12-30 04:52 | 2010-12-30 11:34 | 23 | 402 | 56911-1 | 9246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 911 CALL ONLY INDICATING POWER OUT STS BAD PT INSULATOR ON POLE 5-91 CALL DOUG CHRISTIAN AND HE IS WAITING FOR STARTING TIME TO SEND HELP //VER/GAH IDC CHANGED ALL INSULATORS IN AREA WHILE POWER WAS OUT THIS LENGTHEND THE OUTAGE XXXX
3170 | Whitesburg | 3312901 | JENKINS | KONA | 2009-12-28 07:38 | 2009-12-28 11:35 | 39 | 237 | 59716-1 | 9243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CONDUCTOR PULLED OUT OF A SPLICE IDC XXXX
3171 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-11-18 03:52 | 2014-11-18 11:34 | 20 | 462 | 4739951 | 9240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONFIRMED FUSE OUT//SERVICER PATROLLING//LINE FUSE IS BLOWN ON POLE 37830215B00388. I AM PATROLLING LINE NOW3-MAN LINE CREW NEEDED. NEED SMALL PIECE OF #4 SOL COPPER.. THIS IS TRUCK ACCESSIBLE.. LINE FUSE IS BLOWN ON POLE 37830215B00388. COD-20 ISO LF 37830215B00388 VER/HFP L3/HFP AJB
3172 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-01-20 11:15 | 2008-01-20 13:15 | 77 | 120 | 157891-1HB | 9240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NO. 4 COPPER WIRE DOWN ONE SPAN 1 PHASE ONLY/C PHASE COD-114/0845 RESTORED 20 CUST UP TO POLE 49 OPENED SWITCH AT POLE 49 366 CUST ALL 3 PHASES SO CREW COULD MAKE REPAIRS SAFELY ON PLE 71-197/MADE REPAIRS TRIED TO ENERGIZE SWITCH AT 1115 CUTOUT BURNT UP ON C PHASE AND OPENED RECLOSER POLE 72-383 ON B&C PHASE COD-311 REPAIRED CUTOUT TRIED RECLOSER AT 1210 IT CAME OUT OPENED RCLOSER POLE 70-151 AND 47-6 TO SECTIONALIZE,B PHASE RECLOSER POLE 383 WILL NOT STAY IN BYPASSED RECLOSER RESTORED AT 1 IDC XXXX
3173 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-01-10 16:08 | 2020-01-10 17:55 | 114 | 107 | 4231501 | 9234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A and B phase open on 21-b4-3615, opened C phase at 17:05/ Opened switches on pole 45-1191, tagged and grounded to Bobby reynolds. Hendrix broke at pole 45-A3-1182. Fuses on 21-3615 closed back in at 17:55 Released by crew 078H04 Released by crew 078H07
3174 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-10-05 20:02 | 2011-10-06 00:05 | 38 | 243 | 4950781 | 9234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE IS DOWN BETWEEN POLE 286-77 AND 286-78. IT BLEW LOW SIDE FUSE ON STEPDOWN TRANS. AT POLE 286-202. I AM GOING BACK IN HILLS TO SEE WHAT TOOK LINE DOWN. I WILL CALL FOR HELP. IT LOOKS LIKE PRI. CONDUCTOR MAY HAVE HAD A BAD PLACE IN MIDSPAN AND BURNED DOWN UNDER LOAD. HELP IS ON THE WAY.WE PUT WIRE UP AND CLOSED LOW SIDE FUSE IN AT 00:05. CC = 38 VER/SDB IDC XXXX
3175 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2011-05-30 12:03 | 2011-05-30 19:47 | 32 | 464 | 4209341 | 9232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR#40161266//WR#40161266 PRI .RUN BAD FROM 1123-1102 TO 1123-1147 SEND TO VERNONWR#40161266 PRI .RUN BAD FROM 1123-1102 TO 1123-1147 SEND TO VERNON RELEASED BY CREW 078S08/THUMPED CABLE AND LOCATED FAULT //BACK HOE IS ENROUTE/CONTACTED STORES FOR MATERIAL/FETR2200/VEM/REPAIRS MADE AND POWER RESTORED TO REMAINING CUST 1947/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC DCMT XXXX
3176 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-07-23 12:39 | 2008-07-23 17:30 | 37 | 291 | 58802-1 | 9227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401702//FOUND BROKEN CUTOUT ON POLE 75-176. I AM GOING TO ISOLATE AT POLE 75-175 . THE HIGH SIDE FUSE IS BLOWN AT POLE 98-557 AT THE STEP DOWN ON PHASE A , I AM GOING TO RE-FUSE AND CLOSE. RBW. IDCC FP NULL, CNT49 XXXX
3177 | Hazard | 3303901 | LESLIE | HYDEN | 2021-07-12 06:35 | 2021-07-12 10:00 | 45 | 205 | 4896161 | 9225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 388-451
3178 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2008-08-07 16:14 | 2008-08-07 17:12 | 159 | 58 | 66615-1 | 9222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 66579-1 CREW HAD TO OPEN SWITCH DUE TO CROSS ARM BURNING AND CONDUCTORS ABOUT TO FALL// OPENED GOAB @ 1614 // BAD CUT OUT - CLOSED GOAB IN @ 1712 // VER/TOM IDCC PN1650 XXXX
3179 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-12 11:08 | 2008-03-12 11:30 | 419 | 22 | 56483-1H | 9218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// SERVICER FOUND HOT LINE CLAMP BURNT ON RECLOSER POLE (FAULT/ISO) 37830181B00385- WILL HAVE TO OPEN OTHER TWO PHASES TO MAKE REPAIRS/// /CLOSED @ 1132/ HOT LINE CLAMP BURNT OFF MIDDLE PHASE, OPENED RECLOSER TO REPAIR// B PHASE OPEN FROM ENTIRE TIME CLOSED // COD ON B -190// 323 ON A/C - MAP DISC ISSUED FOR WRONG PHASE CUSTOMERS THAT CALLED IN// IDC TO OPEN RECLOSER PH A IS MIDDLE NOT B XXXX
3180 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2015-02-18 03:16 | 2015-02-18 07:47 | 34 | 271 | 4037831 | 9214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD AND BURNED TOP OF POLE OFF , I NEED TWO MEN,A NINE FOOT ARM, NEW CUTOUT AND BRACKET//COD 34// VER/DBM L3/HFP XXX AJB
3181 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-12-22 19:19 | 2012-12-23 01:00 | 27 | 341 | 4509701 | 9207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE OUT ON POLE #345-45 WIRE DOWN ON POLE # 345C-255 NEED 2 MEN & ROW CREW VER/PDP
3182 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-05-29 13:17 | 2012-05-29 17:40 | 35 | 263 | 4841321 | 9205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OUT ON POLE 37830102000149, CHECKING LINE.//// CHANGED C/O CUT TREES POWER RESTORED COD-35 ISO OCR 37830102000149 VER/HFP L3/HFP IDC XXXX
3183 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-05-20 13:47 | 2008-05-20 17:37 | 40 | 230 | 66465-1 | 9200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001204//WIRE DOWN ON POLE#68-177. LOCATED ACROSS FROM 4327 SHANNON DR. FUS OPEN ON POLE#68-152 RELEASED BY CREW 078S04// WILL NEED FUSE SIZE PRIMARY DOWN 68-177// MIKE MAY DHETO WORK//SENT MAP REPORT ON MISSING 30T FUSE ON POLE 68-152// VER/DBM IDC XXXX
3184 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2010-11-16 16:35 | 2010-11-16 17:27 | 177 | 52 | 56541-1 | 9198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2970603// RELATED TO 56230-1 // OPENED REC 83-167 & REC 83-18 CC=177 VER/GDK IDC XXXX
3185 | Hazard | 3302703 | HAZARD | HAZARD | 2013-02-23 05:56 | 2013-02-23 10:20 | 73 | 264 | 4841391 | 9192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | A PHASE REC OPEN ON POLE 37830296A30746, BAD CSP TRANSFORMER ON POLE 37830272D20431, OPENED TRANSFORMER, CLOSED REC. AT 08:00--- XFMR RESTORED AT 10:20 ///VER/CRB L/3 CRB IDCC CNT24 XXXX
3186 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-03-18 10:54 | 2008-03-18 12:15 | 326 | 81 | 58165-1 | 9191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601// 19.9 CUTOUTS BROKE APART ON POLE 92-161//SERVICER CLEARED HAZARD AND RESTORED ALL BUT TAP COMING OFF FAULT POLE @ 1120//ORIGINAL COD 326//NOW ONLY 13 CUST REMAIN OUT// VER/DBM IDC XXXX
3187 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-08-31 13:18 | 2018-08-31 21:02 | 76 | 464 | 4023111 | 9189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Hold Order Req/CREW REQUIRED///DOL CASE 855856///,2 broke poles 351-82 40-5 ,351-84 30-6 ,,,,351-83 25kva xfr off bolts,,,,recloser 351-76 isolated grounded and tagged to kyddc,,,loop open @ 352-7 grounded and tagged to kyddc ,,back fed from normally open solid blade @ 377-123 ,,restoring 35 customers,crew on site--replaced 2 poles---and xfmr---pwr restored 21:02---tbl tkt comp---rmv
3188 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-07-23 09:05 | 2009-07-23 11:49 | 56 | 164 | H64048-1 | 9184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP MIDDLE PHASE LINE DOWN ON HILL - 3RD AND 4TH SPAN FROM RECLOSER BEHIND 289 FRASURE BR // COD-46 //OPENED OTHER 2 PHASES AT 0905 - 56 CUSTOMERS L3/HFP IDC XXXX
3189 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-12-23 13:18 | 2017-12-23 17:48 | 34 | 270 | 4668281 | 9180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT OFF POLE 39831123D37217//L/F OPEN ON POLE 39831123D37126//25t lf open @ 1123-7126, burnt pole 1123-7217, line crew, tech, no trks25t lf open @ 1123-7126, burnt pole 1123-7217, line crew, tech, no trks/onsite RM25t lf open @ 1123-7126, burnt pole 1123-7217, line crew, tech, no trks/onsite RM fuse in at 17:48 please close tic RM
3190 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-07-08 11:10 | 2018-07-08 16:50 | 27 | 340 | 4750611 | 9180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Called out lne crew and Tech to replace pole 39831073B12160 // no outage until switches 39831073B20122 were opened @ 1110 restored @ 1650
3191 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-12-15 19:26 | 2009-12-15 21:43 | 67 | 137 | 63677-1 | 9179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO, MAKING REPAIRS, 4 TO 4 COPPER CRIMPET BURNT UP, OPENING LOOP FROM BOTTOM OF CUTOUT TO LINE//COD 67// VER/DBM MLR
3192 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-02-11 03:25 | 2020-02-11 10:04 | 23 | 399 | 4390801 | 9177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3411801/gaj/0337/all out disp G Ratliff 3545 -- gaj/0614/patrolled line found no cause, attempting line fuse --- gaj/0630/fuse blew crews foot patrolling for cause3411801/gaj/0337/all out disp. fuse out on pole 1008-23 will be patroling line. wire down between pole 1008-33 and 1008-34.3411801/gaj/0337/all out disp. fuse out on pole 1008-23 will be patroling line. wire down between pole 1008-33 and 1008-34. will need a manual right of way crew and a line crew #4 copper.3411801/gaj/0337/all ou
3193 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-01-21 14:45 | 2009-01-21 15:18 | 278 | 33 | 58854-1 | 9174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP WR # 28157417 // EMERGENCY REPAIRS - CREW FOUND 556 CONDUCTOR LAYING ON CROSS ARM. CREW NEEDED TO OPEN SWITCHES SO THEY COULD SAFELY REPLACE BROKEN INSULATOR AND TIE PHASE BACK IN. STS OPEN AT 1445 AND CLOSED BACK IN 1518 RELEASED BY CREW 077S05 L3/HFP MLR OK
3194 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-01-23 06:08 | 2017-01-23 10:30 | 35 | 262 | 4320041 | 9170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | I FOUND A TREE IN THE LINE AT POLE 423-136 , I HAVE A ROW CREW COMMING TO CUT IT OUT. LOW SIDE FUSE OUT/STEPDOWN ON.I FOUND A TREE IN THE LINE AT POLE 423-136 , I HAVE A ROW CREW COMMING TO CUT IT OUT. I FOUND A BAD LIGHTNING ARESSTER ON POLE 423-229 I CUT IT IN THE CLEAR/RESTORED 1030. 37830423C00201 VER/AWD L3/HFP XXXHFP AJB
3195 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-11-14 11:57 | 2019-11-14 12:50 | 173 | 53 | 4033131 | 9169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | PER DOUG BEVERLY AT POLE 37830520000009 CROSS ARM IS BURNT INTO & SWITCH IS HANGING ON BY A TREAD¦¦ OUTAGE NECESSARY TO ALLOW CREW TO MAKE EMERGENCY REPAIRS ¦¦ COD-173 ISO SW 37830496000024 OFF@1157 ON@1250
3196 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-06-25 00:51 | 2020-06-25 06:30 | 32 | 339 | 4071551 | 9168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | URD riser fuse open @37830024B30548, checking. Isolated cable going from padmount 24-B3-1158 to padmount 1162 and closed riser back in @0430. Paul Layne bringing hi-pot sticks to check cable. Cable checked good, found bad bushing on padmount 24-B3-1162, will be changing. Got trans. replaced @0630. Released by crew 074S05
3197 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-02-27 23:03 | 2008-02-28 01:57 | 667 | 174 | 51110-1 | 9154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000102 / COD-667/ CKT OUTAGED DUE TO HENDRIX CABLE BURNING IN TWO / WILL TAKE COUPLE OF HOURS TO MAKE REPAIRS / 2303 OPENED STATION CB OUTAGED 667 CUSTOMERS/ 2311 CLOSED TIE SW AND RESTORED 644 CUSTOMERS / 2/28/08 0157 CLOSED CB RESTORED 23 CUST / VER/LDA IDCC CCSCO XXXX
3198 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-03-29 11:36 | 2008-03-29 17:28 | 26 | 352 | 61940-1 | 9152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR FAILED ON POLE 37830272B40351//SAWED TOP OFF POLE FIRE EXTINGUISHED VIRGILS CREW WILL REPLACE INSULATORS WHEN COMPLETING OTHER TROUBLE RELEASED BY CREW 077S04 RELEASED BY CREW 077H04// // VER/TOM IDC XXXX
3199 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-07-11 12:03 | 2018-07-11 15:06 | 50 | 183 | 4761921 | 9150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | rec. pole 141-393 basket & hot tap burnt off, trk to pole. Released by crew 078S07
3200 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2011-12-21 17:30 | 2011-12-21 19:32 | 75 | 122 | 4193801 | 9150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSERS @ 1727 IN ORDER TO ISOLATE POLE FIRE//CREW REQUIRED // OPENED RECLOSERS ON POLE 796-764AT 17:30//POLE 820-342 BURNT///CREW ENROUTEOPENED RECLOSERS ON POLE 796-764AT 17:30//POLE 820-342 BURNT///CREW ENROUTE RELEASED BY CREW 079S01 ///VER/CRB IDC XXXX
3201 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2021-07-16 20:00 | 2021-07-17 11:15 | 10 | 915 | 4922711 | 9150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Csp xfm bad on pole 37830067C00275.// Difficult location behind houses and on a steep hillside.// Released by crew 074S11//opened LF 0n pole 275 at 10:10 cl at 11:15 Released by crew 074H07
3202 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2008-07-28 07:12 | 2008-07-28 10:55 | 41 | 223 | 60983-1 | 9143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3404301//LINE DOWN ACROSS CREEK WAITING ON CREW.LINE DOWN ACROSS CREEK WAITING ON CREW.LINE BURNT DOWN UNDER CONNECTIONS ON STRIPUP VER/TOM IDC XXXX
3203 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2012-12-13 01:13 | 2012-12-13 05:20 | 37 | 247 | 4465731 | 9139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER PATROLLING CKT.LOOP BURNT OPEN ON POLE 97-7 * E. MCKINNEY COMING OUT HELP. CREW ON SITE MAKING REPAIRS.LOOP BURNT OPEN ON POLE 97-7 REPAIRES MADE RESTORED SAERVICE @ 05:20 ///VER/CRB L/3 CRB
3204 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-12-26 10:16 | 2020-12-26 14:40 | 39 | 264 | 4823661 | 9136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester on pole 55-142. made hot to 55-92 at 14:00. all power restored at 14:40 Released by crew 077S10
3205 | Hazard | 3310502 | HADDIX | CANOE | 2020-11-15 06:30 | 2020-11-15 16:39 | 15 | 609 | 4676651 | 9135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | confirmed line fuse out , 3 spans wire down #2 acsr need line crew row crew and flaggers, fuse is open not grounded Released by crew 077S07 Released by crew 077H04//CLOSED 1639
3206 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-07-04 08:41 | 2017-07-04 10:51 | 71 | 130 | 4071221 | 9122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REC ON 1071-126 WAS CLOSED, PATROLLED BACK FOUND LOOP BURNTED OPEN ON POLE1071-28, OPEN 300 AMP SOLID BLADE ON POLE 1071-24, GRD AND TAGGED TO MYSELF, MADED REPAIRS ON LOOP, REMOVED GRDS AND TAG, CLOSED IN SOLID BLADE AT 1071-24 AT 1042, TO OPEN REC, CLOSED IN REC ON 1071-126 AT 1051 RESTORING POWER TO CUST AT THIS LOC BY AMG RELEASED BY CREW 078S06 VER/CRB SJG
3207 | Hazard | 3309302 | VICCO | JEFF | 2010-09-15 19:39 | 2010-09-15 23:27 | 40 | 228 | 50208-1 | 9120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE LOOP BURNED INTO AT POLE 37830322C00055 CALLING FOR BIG BUCKET//COD 15//ISO //OPNEED RECLOSER 322-302 @ 2315 IN ORDER TO MAKE REPAIRS TO LOOP (SEE ORDER 50235-1)//RESTORED 2327// IDC APPEARS THIS MAY ACTUALLY BE PH C WITH A MISSMAPPED TAP CHANGED COUNT FROM 54 XXXX
3208 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-07-26 19:21 | 2011-07-26 22:53 | 43 | 212 | 4626501 | 9116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PRIMARY CAME OFF RIDGE PIN ON POLE 185-102, NO TRUCKS TO POLE , NEED LINE CREWAND NEW RIDGE PIN. RELEASED BY CREW 078S01 / WIRE DOWN ON ROCK CLIFF//VER/CRB IDC XXXX
3209 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2015-07-27 22:40 | 2015-07-27 23:15 | 260 | 35 | H4949171 | 9100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIDDLE PHASE CUTOUT CRACKED SETTING POLE1089A507 ON FIRE BETWEEN ARM BRACES AND SPAN GUY ATTACHMENT POLE MOSTLY BURNT INTO BEST TO REPLACE IT NOW 45 4 POLE WILL SEND MATERIAL LIST TO FOREMAN// HAD TO OPEN @ 1089-A-3 @ 2240 TO MAKE SAFE (260 CUST)////TOMMIDDLE PHASE CUTOUT CRACKED SETTING POLE1089A507 ON FIRE BETWEEN ARM BRACES AND SPAN GUY ATTACHMENT POLE MOSTLY BURNT INTO BEST TO REPLACE IT NOW 45 4 POLE OPENED @ 2240 CLOSED @ 2315/ DUPLICATE IN HOIS/ VER/BOW
3210 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-02-12 11:05 | 2013-02-12 14:00 | 52 | 175 | 4813261 | 9100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "B" PHASE REC. OPEN ON 38820989D00018/ COD-52 /L/A BLOWN ON POLE 38820990A00052 WILL REPLACE //B PHASE REC. OPEN ON 38820989D00018/ COD-52 /L/A BLOWN ON POLE 38820990A00052 WILL REPLACE //CUT LA IN CLEAR WILL NEED OBSERVER TO CHANGE// CLOSED REC.//POWER IS RESTORED VER/KEP IDC ASSUMING PH A FROM CALLS BUT MANY MISSMAPPED SO LEFT COUNT AS IS XXXX
3211 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-09-28 08:57 | 2016-09-28 14:00 | 30 | 303 | 4934391 | 9090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT LINE CLAMP HAD LOOP OPENED VER/AWD L3/HFP HFPC CDC83 AJB
3212 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-07-10 06:36 | 2008-07-10 18:15 | 13 | 699 | 50481-1 | 9087 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FOUND BROKE NEUTRAL LYING ACROSS ROAD,, FOUND BROKE POLE POLE # 523-73 POLE IS NOT TRUCK ACCESIBLE RELEASED BY CREW 078S02----REPAIRED SPAN OF 6A NEUTREL ON POLE 523-64 IDC CHANGED FROM TREE OUT PER CONF CALL XXXX
3213 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-08-18 12:27 | 2010-08-18 15:25 | 51 | 178 | 57632-1 | 9078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON STEPDOWN, WILL NEED FLAGGING CREW ... REPLACED CUTOUT RESTORED POWER AT 15:25//VER/CRB IDCC CDC92 XXXX
3214 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-10-17 03:32 | 2008-10-17 12:01 | 37 | 509 | 56406-1 | 9077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201//POLE TOP BURNT AT POLE 425-161 TRUCK ACCESSABLE/(45/4) NEEDS LINE CREW ,TRUCKS OK. KEEP GATE CLOSED..LIFTED HOT TAP ON POLE 425-52/ CLOSED RECLOSER AT 0730////VER/CRB IDC XXXX
3215 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-03-17 22:56 | 2020-03-18 04:09 | 29 | 313 | 4486781 | 9077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIM&N BURNED DOWN BETWEEN 8-161&8-152,NEED CREW,#2,MATERIAL BUCKET///////HIGH SIDE FUSE OUT@STEPDOWN////opened & isolated RECL 37820008B00160 and closed step down to check if good /////MADE REPAIRS&RESTORED//cod 29//
3216 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-03-15 04:37 | 2008-03-15 14:57 | 44 | 620 | 57371-1 | 9076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001002// POLE FIRE ON POLE 38830496000080, ISOLATED AT POLE 38830496000013, NEED CREW AND 45 CLASS 4 POLE, TRUCK OK, NARROW PART OF 201, WILL NEED TO BLOCK ROAD WHILE WORKING, RESTORED REC AT 06:45 @ 1108 CREW REQUESTED FETR UPDATED TO 1500//3001002// POLE VER/HFP IDC XXXX
3217 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2013-02-01 08:54 | 2013-02-01 10:55 | 75 | 121 | 4780721 | 9075 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT-LINE CLAMP BURNT OFF ON LINE SIDE RECLOSER RISER. <<PHASE C ONLY>> WORKING TO REPAIR. REPLACED STIRRUP AND HOT-LINE CLAMP AND RESTORED @ 10:55. SH ///VER/CRB L/3 CRB IDCC CNT109 XXXX
3218 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-12-11 18:37 | 2009-12-11 22:03 | 46 | 206 | 57259-1 | 9073 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SUSPECT OVERLOAD SINCE FUSE APPEARS TO HAVE MELTED OUT, PER DALE HAMILTON//COD 46// VER/DBM MLR OK
3219 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-07 20:57 | 2010-01-08 00:33 | 42 | 216 | 66003-1 | 9072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN RECLOSER TO REPLACE BURNT BASKET @ POLE 425-198// IDC XXXX
3220 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-09-27 14:27 | 2010-09-27 20:56 | 44 | 389 | 54278-1 | 9066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER POLE 429/364 OPEN; PATROLLING LINES; BURNT TOP OUT OF POLE 405/53; CREW REQUIRED; ISOLATED BETWEEN POLES 405/51 AND 405/49; PARTCIAL PWR RESTORED AT 1706 HRS; OPENED RECLOSER AT 2046HRS TO MAKE UP LOOPS; FULL RESTORATION AT 2056HRS; CLOSE TICKET//VER/CRB IDCC TON2055 XXXX
3221 | Pikeville | 3408103 | SALISBURY | MARTIN | 2018-08-08 01:51 | 2018-08-08 15:35 | 11 | 824 | 4923381 | 9064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines.netural down at pole#38831074B00487will need 6a & sleeves ,& material handler Released by crew 074S04Dispatched in accordance with KYPCo Late Night Callout Guidelines.netural down at pole#38831074B00487will need 6a & sleeves ,& material handler Released by crew ..TREE ON LINE AT 1074-354.NEED 4 OR 5 MAN MANUAL ROW CREW..
3222 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-11-18 20:43 | 2017-11-19 00:09 | 44 | 206 | 4571221 | 9064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 284-91///will patrol.found broken xfm. cutout on pole 284-39.will make repairs////restored
3223 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2015-05-11 02:51 | 2015-05-11 03:43 | 174 | 52 | H4407921 | 9048 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | SCADA INDICATED 69-12KV TR 1 @ SOUTH PIKEVILLE DE-ENERGIZED. THIS HAS STATION INTERRUPTED AND APPROX 1786 PIKEVILLE AREA CUSTOMERS// STATION SERVICER AND D-LINE SERVICER CALLED IN//TOM WILL UPDATE AS INFORMATION BECOMES AVAILABLE//TOM - ***UPDATE @ 1135 DETERMINED STATION TRANSFOMER LTC HAS FAILED - LOOKING AT LOAD TRANSFER OPPORTUNITIES AND WILL NEED A MOBILE TRANSFOMER INSTALLED - ALL NECESSARY PARTIES NOTIFIED//TOM VER/KEP AJB
3224 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2018-07-18 05:01 | 2018-07-18 12:57 | 19 | 476 | 4792401 | 9044 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | will dispatch at start time per late night guidelines High side fuses blown on station transformer due to arrester failure. Crews working to repair. Released by crew 076S02 L3/HFP
3225 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2022-07-26 14:54 | 2022-07-27 19:45 | 17 | 1731 | 4586861 | 9037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | NO DDC TAGS//URD riser open @1152-B2-211, checking. Isolated cable @junction box 1152-214 going toward padmount 1152-B2-218. Closed URD riser back in @1705, this will take a line crew with hi-pot sticks. Released by crew 074S05 Released by crew 074H07
3226 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-08-15 02:48 | 2017-08-15 10:43 | 19 | 475 | 4260331 | 9025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DISPATCHED IN ACCORDANCE WITH KYPCO LATE NIGHT CALLOUT GUIDELINES. B PHASE COD-19/ L/F OPEN @25-A-328, PATROLLING. BAD POLE TOP INSULATOR ON POLE 25-A-29, TIM HALL GETTING A BIG BUCKET TO COME HELP, WILL HAVE TO OPEN A AND C PHASE TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED A AND C PHASE @1013, CLOSED ALL BACK IN @1043. VER/KEP SJG
3227 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2010-01-06 20:54 | 2010-01-06 21:35 | 220 | 41 | H64198-1 | 9020 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 46KV TRANSMISSION LINE OPERATING // A PHASE OPEN @ 1929 // DROPPED REMAINING CUSTOMER @ 2053 - THEN CLOSED IN THE 46KV CB "A" AT ELKHORN CITY AND PICKED UP DRAFFIN STATION @ 2135 // IDC NEED SEPARATE OUTAGE FOR REMAINING CUSTOMERS IDC NO CUSTOMERS OUT TILL 1929 PH A THEN REMAINING OUT WHEN TRANSMISSION OPENED AT 2054 XXXX
3228 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-08-28 12:57 | 2010-08-28 15:20 | 63 | 143 | 61497-1 | 9009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR PL, 1072-182 RE-PLACED 40-T LINE FUSE ON POLE 1048-6 COMP VER/KEP L3/KEP IDC XXXX
3229 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-03-21 09:31 | 2013-03-21 11:25 | 79 | 114 | 4944681 | 9006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD BURNED OFF AT STEP DOWN--BIG BUCKET ON THE WAY/"A" PHASE ONLY COD-79 VER/KEP IDC XXXX
3230 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-03-13 17:46 | 2009-03-13 19:40 | 79 | 114 | 58267-1 | 9006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURN OPEN AT POLE #1013-63//COD 62//LOOP BURN OPEN AT POLE #1013-63//RELEASED BY CREW 079H02//ISO//COD 62// VER/DBM IDC XXXX
3231 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-06-04 18:51 | 2008-06-04 20:06 | 120 | 75 | 57017-1 | 9000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3402001//BAD ARRESTER......DAH//COD 120// VER/DBM IDC XXXX
3232 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-08-18 15:30 | 2010-08-18 19:00 | 62 | 210 | 57753-1 | 8994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OUT ON POLE 37830255D00200,CHECKING LINE//// FOUND XFMR C/O BROKEN UPON HILL ON POLE 37830255C00086 , TRYING TO GET UP WITH ERIC PRATT TO FIX.REC. OUT ON POLE 37830255D00200,CHECKING LINE//// FOUND XFMR C/O BROKEN UPON HILL ON POLE 37830255C00141 , TRYING TO GET UP WITH ERIC PRATT TO FIX. ISOLATED C/O FROM LINE, TOOK CLAMP OFF. GOING BACK TO REC. TO MAKE HOT. IF IT STAYS WELL JUST HAVE ONE CUST OFF. VER/KEP L3/KEP IDCC DCMT, CNT63 XXXX
3233 | Paintsville | 3401101 | FALCON | FALC-OILS | 2010-12-04 20:53 | 2010-12-04 21:55 | 145 | 62 | 63074-1 | 8990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON 830-16...CALLED ROGER MAYNARD WE WILL HAVE TO DROP RECLOSERS TO CHANGE.. OPENED RECLOSER AT 2053 AND CLOSED AT 2055 STILL OUT FROM POLE 830-10OPEN SWITCHES ON 830-1- AT 20.55.. RELEASED BY CREW 076S01 VER/ARN IDC REMOVED 2 MIN STEP FOR 88 CUSTOMERS XXXX
3234 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-10-08 21:05 | 2017-10-08 22:52 | 84 | 107 | 4424871 | 8988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PH ONLY//COD 84B PHASE RECLOSER IS OPEN, PATROLLING THE LINE.B PHASE RECLOSER IS OPEN, PATROLLING THE LINE. I REPLACED BAD LINE CUTOUT AT POLE 38821016D00250, POWER RESTORED, SEND A COPY TO CLIFF FREEMAN TO HAVE POLE 38821016D00250 REPLACED, ITS A GREEN POLE AND IS BURNT AT THE TOP SET OF CROSS ARMS.//COD 84//EMAILED TO TECH// VER/DBM L3/HFP XXXHFP ACBC CNT95
3235 | Hazard | 3302703 | HAZARD | HAZARD | 2012-08-01 22:48 | 2012-08-01 23:01 | 691 | 13 | 4882261 | 8983 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CIRCUIT BREAKER OPENED TO ALLOW CREW TO SAFELY REPLACE CUT OUT THAT WAS HIT BY LIGHTENING // RESTORED @ 2301 COD-688 ISO FB VER/HFP L3/HFP IDCC TOF2104 XXXX
3236 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-03-28 20:31 | 2009-03-29 00:10 | 41 | 219 | 62515-1 | 8979 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | WR 29127679-1 BAD STEPDOWN TR CUTOUT & RECL BUSHING. ** CALLING D/S FOR HELP..BAD RECLOSER, AND CUTOUT. VER/PDP IDCC CDC92, TOF2005 XXXX
3237 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-01-01 17:58 | 2022-01-02 15:20 | 7 | 1282 | 4252281 | 8974 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | C phase trans. open @ bank pole 1127-B-513, checking. Bad 15 kva 7200 trans., this will take a line crew with a material handler big bucket. Trans. also needs to be cut over for 120/ 208 bank. Released by crew 074S05// repairs made // restored @ 15:20
3238 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-10-29 08:30 | 2012-10-29 13:29 | 30 | 299 | H4180681 | 8970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE 1121-309, TO HAVE TOP BURNTED OFF, I OPEN UP SOLID BLADE ON POLE 1121-102 AT 0830, WELL NEED A CREW TO MAKE REPAIRS, 405 POLE, BUT MAY BE ABLE TO USE A POLE EXTEND ON THIS, WELL NEED NEW CUTOUT AND POLE TOP PIN, EVERYTHING ELSE WILL WORK BACK, IS IN FIELD MAY BE ABLE TO GET TRUCKS TO POLE. CREW REQ, HAVE LINE GROUNDED AND TAGGED AT POLE 1121-102 RELEASED BY CREW 078S06 TOTAL COD 31 ISO PO @ 39831121B00102 DUP FOR 30 CUST IN RECORD # 4180681 VER/HFP L3/HFP IDCC TOF712 XXXX
3239 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-07-11 06:01 | 2010-07-11 08:44 | 55 | 163 | 64966-1 | 8965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3309103// SERVICER OPENED A SET OF RECL`S TO ISOLATE A ENERGIZED CONDUCTOR.CONDUCTOR BURNED DOWN AT RECLOSER ON POLE 520-9, OPENED RECLOSER ON 448-365 AT 07:15 TO ISOLATE, OPENED SWITCHES ON 472-200 TO ISOLATE TROUBLE CLOSED RECLOSER AT 448-365 AT 07:36 ENERGIZING UP TO POLE 472-200. MAD IDC XXXX
3240 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2019-08-08 21:09 | 2019-08-08 21:21 | 745 | 12 | 4861871 | 8940 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | station outage to safely bypass regulator ¦¦¦ VERIFIED TIMES PER SCADA = L3/HFP
3241 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2020-05-14 18:27 | 2020-05-14 19:49 | 109 | 82 | 4836511 | 8938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A phase REC. only out will patrol// Found and replaced blown arrester on pole 859-A-29. Closed A phase REC. and restored customers @ 19:49
3242 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-10-28 14:13 | 2008-10-28 17:19 | 48 | 186 | 60134-1 | 8928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001102// HOT TAP BURNT OFF 66-11 POLE 66-28 OPENED REC. 15;40 RELEASED BY CREW 078S08 COMP WORK DONE BY CREW 3324//COD 48// VER/DBM IDC XXXX
3243 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-07-26 09:36 | 2009-07-26 11:08 | 97 | 92 | 64905-1 | 8924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 296A-1033.....OPEN GOAB ON POLE 296A-1042 AND MADE BRKR HOT AT 09:46 HRS FOR A PARTIAL RESTORE......CONTRACT CREW ON SIGHT WORKING TO CHANGE INSULATOR. MANUAL CANNOT GET BUCKET TO. REPLACED INSUALTOR & CLOSED GOAB POLE 296-A-1042 AT 1108 RESTORING 97 CUSTOMERS IDC XXXX
3244 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-02-09 16:58 | 2010-02-09 19:18 | 98 | 140 | 54556-1 | 8920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IN AT 18:18 HRS, STILL HAVE LINE FUSE OUT ON POLE # 134-55, PATROLLING LINE, BAD CUTOUT ON POLE # 135-206, REPLACED CUTOUT, ALL POWER RESTORED//COD 98// VER/DBM IDC XXXX
3245 | Hazard | 3420001 | SOFT SHELL | VEST | 2012-01-11 11:30 | 2012-01-11 17:30 | 37 | 360 | 4247441 | 8920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 131-17 IS ON FIRE, BAD INSULATOR OR CUTOUT, //VER/GAH IDC XXXX
3246 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-06-30 12:09 | 2008-06-30 14:24 | 66 | 135 | 60145-1 | 8910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLED LINE AND DID NOT FIND ANY HAZARDS, LINE FUSE CUTOUT HAS BAD CONNECTIONS, WE ARE GOING TO CHANGE IT OUT. CUTOUT CHANGED POWER RESTORED COD-66 VER/HFP IDC XXXX
3247 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-01-15 10:04 | 2021-01-15 12:15 | 68 | 131 | 4870791 | 8908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | C phase fuse open on step-down TR (68 COD) servicer found tap burnt off at 37820005000025 due to failed sleeve crew enroute to make repairs FETR 1400///restored 1215
3248 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-09-07 10:24 | 2009-09-07 11:20 | 159 | 56 | 52290-1 | 8904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 31595528 // ISO 38830045D26672 // MD FILED FOR MISSING LINE FUSE // COD 159 POLE 45-6637 CHANCE CUTOUT FELL APART REPAIRED POLE 45-6672 65T// VER/DBM IDC XXXX
3249 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2020-06-30 01:21 | 2020-06-30 08:46 | 20 | 445 | 4091891 | 8900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Held in accordance with KPCO late-night callout guidelines. . A phase stirrup burnt in 2. line crew required for repairs. COD 20
3250 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2017-07-02 11:09 | 2017-07-02 15:47 | 32 | 278 | 4067121 | 8896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | //ISO 38830045C45687/ COD 32//POLE 45-5904 BAD ARM NEED 3-CUTOUT LA 8FT. ARM//POLE 45-5904 BAD ARM NEED 3-CUTOUT LA 8FT. ARM/CREW ON SITE/FETR 1630/VEM/TRIED FUSE AT 1323/DID NOT HOLD /BAD LA ON 45-C4-5697/VEM/REPAIRS MADE AND ALL CUST RESTORED 1547/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830045C45687/ COD 32/ VER/BOW /// DKM SJG
3251 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-10-09 22:38 | 2015-10-09 22:50 | 741 | 12 | 4335411 | 8892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LA REPLACED VER/SEF L3/HFP XXXHFP AJB
3252 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-11-05 13:10 | 2018-11-05 19:38 | 55 | 388 | 4363751 | 8880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire//OPENED L/F 38830123000002 @ 1310//NO OUTAGE TILL THEN//pened `123-2 at 1310 hrs/123-20 burnt off tagged to him no groundspole fire/send to jason ramey tagged to him no grounds/Opened recl on 38830147000078 at to safely replace cutout on 38830123000002/opened recl 1906-1938pole fire//OPENED L/F 38830123000002 @ 1310//NO OUTAGE TILL THEN//pole fire/opened `123-2 at 1310 hrs/123-20 burnt off crew required trucks ok send to jason ramey tagged to him no groundspole fire/opened `123-2 at 1 // L3/HFP
3253 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-11-24 07:16 | 2018-11-24 11:35 | 64 | 259 | 4471881 | 8876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | burnt off pole @ 38830118C24544. truck ok, will need pole top extension. grounded & tagged to R. Morgan @ pole 38830118C24545. Line fuse back in @ 09:15. All cust restored up to pole 118c4545 Released by crew 078H17/arrived RM/ Hot tap on 118-4545 on @ 1135/ all power restored Released by crew 078H08 L3/HFP
3254 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-04-28 01:15 | 2013-04-28 06:21 | 29 | 306 | 4052631 | 8874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..SOLID BLADE CUTOUT ON C PHASE POLE 964C99.CUTOUT BROKE IN HALF.HOT SIDE HANGING IN CLEAR.CAN REPLACE SAFELY..//.MIDDLE PHASE CUTOUT ALSO GOING BAD.NEED THREE 300A CUTOUTS..2 MEN.BIG BUCKET.WILL HAVE TO DROP LINE OUT..//..OPENED RECLOSERS ON 964B153 @ 05:50..REPAIRS MADE..CLOSED RECLOSERS @ 06:21 ALL CUSTOMERS RESTORED..JRV.J REED & R THOMAS.04/28/13 VER/ARN IDC XXXX
3255 | Hazard | 3303902 | LESLIE | WOOTON | 2014-10-10 08:26 | 2014-10-10 11:20 | 51 | 174 | 4601221 | 8874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLEARED BAD 7200 CUTOUT COD-51 ISO OCR 37830437000113 VER/HFP L3/HFP AJB
3256 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-08-07 16:58 | 2018-08-07 17:36 | 539 | 38 | 4920331 | 8866 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Recloser 38831125C20619 Locked Out while On Hot Line Tag. Closing Hot Line Clamp 38831149000191 up to open line fuses 38831149000282 and Failed Lightning Arrestor on pole 38831149000282 took it out./ RECL 38831125C20619 on @ 1714/ fuses 38831149000282 on @ 1736 L3/HFP
3257 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-08-27 10:48 | 2014-08-27 14:25 | 70 | 217 | 4428111 | 8865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON 464-12 OPENED LINE ON 464-11 CLOSED OCR @ 1230 RELEASED BY CREW 077S01 RELEASED BY CREW 077H04 VER/KEP AJB
3258 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-10-28 07:05 | 2009-10-28 12:17 | 38 | 312 | 60400-1 | 8864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUT-OUT FAILED , BURNING POLE BEHIND 620 PIN OAKS DR,68-1263 FAULT POLE, LIFTED HOT TAP ON POLE68-578 NXT ST OVER,PINES HILLS DR POWER IS PARTIAL RESTORED UP TO OPEN POINT ON POLE 68-578AT 0921 A.M KWB ES HILLS DR POWER IS PARTIAL RESTORED UP TO OPEN POINT ON POLE 68-578AT 0921 A.M KWB //STS WR# 32421049 ORDER 62624-1 FOR OUTAGE TO MAKE UP LOOPS L3/HFP IDCC TON0910 XXXX
3259 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-06-14 16:21 | 2016-06-14 19:57 | 41 | 216 | 4347391 | 8856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN CREW ENROUTE VER/CRB AJB
3260 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-09-05 09:20 | 2014-09-05 10:15 | 161 | 55 | 4467611 | 8855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPAIRING CROSSARM ON POLE 38820722D00024// ISO 38820746C00241// COD 161// OPENED AT 9:20/// CLOSED 10:15 VER/HFP L3/HFP AJB
3261 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2010-11-30 05:38 | 2010-11-30 07:50 | 67 | 132 | 60917-1 | 8844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//COD 67// VER/DBM IDC XXXX
3262 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-09-28 19:04 | 2009-09-28 23:03 | 37 | 239 | 52268-1 | 8843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | PATROLLING LINE, POLE # 131-25 HAS ROTTED OFF AT GROUND LEVEL, TIED OFF WITH ROPE, WILL TRY TO GET REPLACED TOMORROW. POWER RESTORED IDCC CNT377 XXXX
3263 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-08-12 06:38 | 2010-08-12 06:58 | 442 | 20 | 53327-1 | 8840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER LOCKED OUT// TAKING CLAMP OFF BAD CUTOUT LOCK RECLOSER //VER/GAH
3264 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2020-07-29 17:18 | 2020-07-29 19:25 | 89 | 127 | 4251871 | 8835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | TRIED FUSE ON POLE 38830118D10634 AND IT BLEW THE FUSE BACK ON POLE 38830118D16173//PATROLING AGAIN//THID TOOK OUT ALL 3 PHASES//OPENED SWITCH ON POLE 38830118D10103 TRYING 38830118D16173 AGAIN//SB OPEN ON POLE 38830118D10103 //COD 30//fault @ 118-4573, restored sb @ 118-103 @ 19-25 Released by crew 078S07//GUY WIRE FLIPPED ONTO TRANS 38830118C24546
3265 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-07-29 13:20 | 2013-07-29 19:38 | 30 | 378 | 4604181 | 8830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | "A" PHASE OUT CKING NOW , LIFTED EBLOW AT 784-322 GOING TO PAD 784-325 REFUSING NOW TCM//.HOT UP TO PAD 322, HI POTTING CABLE NOW TO FIND FAULTED SPAN , RELATED TO 4604131 HOT TO 325 18:19 GOING TO PAD 784-325 REFUSING NOW TCM//. ,FOUND BAD SPAN BETWEEN 784-336 & 784-340 ISOLATED AND TAGGED ,BACK FEED FROM 784-500 TO 784-340 , CUTOUT BETWEEN PHASES, MIDDLE PHASE AND OUTSIDE PHASE SAME PHASE ON POLE 7 IDC NEED MORE INFO
3266 | South Williamson | 3200302 | BELFRY | TOLER | 2016-05-02 14:43 | 2016-05-02 15:29 | 232 | 46 | 4159971 | 8824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 300 AMP SWITCH ON POLE 1015-20. RELEASED BY CREW 079H07 OPENED RECLOSER ON 38821015A00052 TO DECREASE LOAD. SWITCH CLOSED 1515. RECLOSER RESTORED 1521. VER/AWD AJB
3267 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-10-15 15:04 | 2019-10-15 18:50 | 39 | 226 | 4142501 | 8814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DRY BR TAP-OFF CUTOUT HAS BROKEN,NEED 1 MAN.WILL HAVE TO REPLACE CUTOUT,IS UP ON HILL ABT 200FT//////////REPLACED CUTOUT&RESTORED POWER 18:50
3268 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2020-06-10 19:46 | 2020-06-11 15:15 | 13 | 1169 | 4994021 | 8813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 39830901C45586 got a bad cutout burnt arm into needs linecrew to change arm need 2 8ft arms, everything is energized except transformer on 901c45586 Released by crew 078H09//LIFTED HT @ 1330
3269 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-08-01 07:48 | 2008-08-01 14:00 | 47 | 372 | 63249-1 | 8804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 165-224 NEEDS 40-4 POLE AND NEW CUTOUT. NEEDS LINE CREW, CUT LOOP ON POLE 165 - 206 AND PLACED GROUNDS . ORDER 63452-1 CREATED FOR OUTAGE WHEN CREW OPENED RECL TO MAKE UP LOOPS//BAD CUTOUT ON POLE 165-224 NEEDS 40-4 POLE AND NEW CUTOUT. NEEDS LINE CREW, CUT LOOP ON POLE 165 - 206 AND PLACED GROUNDS . POWER RESTORED @ 14:00 M.PHELPS RELEASED BY CREW 078H12 VER/HFP IDCC PN169 CHANGED START TIME FROM 0705 XXXX
3270 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-06-24 03:50 | 2010-06-24 15:07 | 13 | 677 | 56254-1 | 8801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE DOWN FROM POLE 185-66 TO 185-137, POLE 185-200 REPLACED ARRESTER ON CSP TRANSFORMER, 30T FUSE POLE 185-176 OPEN RELEASED BY CREW 074S03/// WHEN CREW ARRIVES WILL HAVE TO TAKE THE OTHER 2 PHASES OUT TO PULL DOWNED WIRE. TIM MCCOY//ONLY B PHASE OPEN//COD 12//OPENED OTHER TWO PHASES INTERRUPTING 5 MORE CUST @ 1145//RESTORED ALL CUST AS OF 1222// IDCC CNT17 PH B 13, ECTENDED TO COVER SECOND OUTAGE XXXX
3271 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-03-02 02:43 | 2015-03-02 09:42 | 21 | 419 | 4089741 | 8799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER LATENIGHT GUIDELINES WILL LOOK AT IN A.M. 10T FUSE MELTED OUT,THE CUTOUT DOOR DID NOT DROP OUT, BURNING UP THE DOOR./ COD 21// VER/ ADH L3/HFP XXX AJB
3272 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-09-08 16:19 | 2018-09-08 18:55 | 92 | 156 | 4059161 | 8797 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on p-850-22.A PHASE //COD 37 FROM BEGINNING//WILL BE OPENING OTHER 2 PHASES//bad cutout on p-850-22.opened the other 2 phases at 18.00.chging cutout//CLOSED 1855
3273 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-02-20 11:49 | 2015-02-21 12:15 | 6 | 1466 | 4055381 | 8796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT POLE 38831101D30264,WILL RE-FUSE//////////BAD XFR NEED 50KVA,POSSIBLY APPROACHABLE,19.9 IN XFR BANK BEH PAUL LAYNES DADS ///////////NEED CREW RELEASED BY CREW 074S06//////////REPLACED BAD XFR,RESTORED POWER,ALLOK AFTERWARDS//COD 6// VER/DBM
3274 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-07-10 13:59 | 2015-07-10 22:41 | 17 | 522 | 4764401 | 8794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING FOR OUTAGE TREE GROWN UP INTO LINES AT PL.38830269D00173, WAITING ON TREE CREW, KWB CREW ARRIVED RELEASED BY CREW 078S09 OPENED UP CSP 38830269D00061 AND CLOSED IN @ 2236 CLOSED CSP @ 2241 VER/CRB
3275 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-04-23 11:02 | 2022-04-23 14:27 | 72 | 205 | 4792631 | 8784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN C/O @ POLE 1088-A-161///OPEND REC @ POLE 1088-A4-417 @ 13:48//CLOSED & RESTORED @ 14:27 Released by crew 074S06// A PHASE ONLY
3276 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-05-01 23:26 | 2010-05-02 03:52 | 33 | 266 | 53586-1 | 8778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNT OFF TOP OF 40/5 POLE NEED LINE CREW , TRUCKS TO POLE OK . RELEASED BY CREW 078S01// WILL PUT WOOD POLE TOP EXT / CANT GET ANY CUSTOMERS BACK ON MOST CUSTOMERS APAST BURNED OFF POLE //VER/GAH IDC XXXX
3277 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-01-09 05:25 | 2008-01-09 15:10 | 15 | 585 | 55004-1 | 8775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//**DUPED DUE TO AREA CROSSOVER**//ON SITE, PATROLLING LINE//POLE TOP BURNT ON 1185-36//OPENED SOLID BLADES ON POLE # 1139-109 AT 0727//ON SITE, PATROLLING LINE RELEASED BY CREW 080S01 CREW ON SITE// ISOLATING SWITCH CLOSED UP TO THE TWO SETS OF RECLOSERS ON 11-536 @ 1505//@ 1510, RECLOSER FEEDING HURRICANE CRK CLOSED//@ 1510 OTHER REC ON POLE 11-536 CLOSED ON A & B PHASES BUT C PHASE MUST BE BYPASSED//C PHASE NOT RESTORED UNTIL 1518 IDC 3/24 SHIFTED 12 CUSTOMERS FROM KY TO VA XXXX
3278 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2008-06-04 19:24 | 2008-06-05 04:00 | 17 | 516 | 57092-1 | 8772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 100 AMP CUT OUT BLOWN UP NEEDS REPLACED ASAP 20-1069 RELEASED BY CREW 078M01//3010601//IDC DIP FUSE IS OUT, REPLACED CUTOUT IDCC CNT34, PN 382 XXXX
3279 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-02-01 16:31 | 2011-02-01 21:05 | 32 | 274 | 52861-1 | 8768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | B & C PHASE OUT 8 CUSTOMERS OPENED OTHER RECLOSER @ 1800 29 CUSTOMERS /// CROSSARM ON POLE 166-20 BROKE AND LET PHASE WIRE FALL. IT OPENED ONE OF THE RECLOSERS ON POLE 166-230. I OPENED THE OTHER RECLOSERS AT 18:00. CREW IS ON SITE TO CHANGE ARM COD-37 ISO RECL 37830166000230 SEE H52861-1 FOR 29 CUST OUTAGE VER/HFP L3/HFP IDC LOOKS LIKE A AND C OUT ORIGINALLY CHANGED COUNT FROM 8 XXXX
3280 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-04-07 00:49 | 2009-04-07 08:50 | 21 | 481 | 50078-1 | 8761 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000202 - 40/5 XFORMER POLE TOP BURNT OFF. NEED LINE CREW , TRUCKS TO POLE OK. NEED 45/5 POLE TO REPLACE OLD POLE. MIGHT BE ABLE TO PUT WOODEN EXT. ON OLD POLE. LINE FUSE OPEN ON POLE 356-164./FETR0830 -*** RON VIRGIN AND JOHN HALL STILL ON SITE. VERNON HAS MEETING IN PAINTSVILLE . WILL RELEASE TICKET TO DDC TO WORK . CREW WILL HAVE NOT COMPUTER.3000202 - 40/5 XFORMER POLE TOP BURNT OFF. NEED LINE CREW , TRUCKS TO POLE OK. NEED 45/5 POLE TO REPLACE OLD POLE. MIGHT BE ABLE TO PUT WOODEN EXT. ON//VER/CRB IDC
3281 | Hazard | 3420001 | SOFT SHELL | VEST | 2013-03-24 23:27 | 2013-03-25 03:06 | 40 | 219 | 4953241 | 8760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE ON GROUND POLE 108-36 // OPENED RECL POLE 108-116 @ 0025 //RELEASED BY CREW 077S08 // //VER/GAH IDCC TOF0025, CNT54, PN116, CDC86 XXXX
3282 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-01-01 02:47 | 2018-01-01 04:56 | 78 | 129 | 4691161 | 8749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | loop open on pole 38830278000052 //repaired loop and closed line fuse 278-41 Released by crew 078S05//cod 65 (+13) //
3283 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-06-01 14:38 | 2011-06-01 16:10 | 95 | 92 | 4219571 | 8740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A PHASE RECLOSER OUT ON POLE 37830249B10346, PATROLING LINE. COD-95 VER/KEP IDC XXXX
3284 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-12-23 21:05 | 2012-12-24 00:15 | 46 | 190 | 4512251 | 8740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRI BROKE @POLE334-48,NEED LINE CREW NO TRUCK 2105 * SERVICER OPENED RECL AT POLE 334-A-141 TO MAKE REPAIRS.PRI BROKE @POLE334-48,NEED LINE CREW NO TRUCK,OPENED RECLOSER ON POLE 334-141@2105&PLACED GROUNDPRI BROKE @POLE334-48,NEED LINE CREW NO TRUCK,OPENED RECLOSER ON POLE 334-141@2105&PLACED GROUND RELEASED BY CREW 078H04PRI BROKE @POLE334-48,NEED LINE CREW NO TRUCK 2105 SERVICER OPENED RECL AT POLE 334-A-141 TO MAKE REPAIRS.PRI BROKE @POLE334-48,NEED LINE CREW NO TRUCK,OPENED RECLOSER ON VER/PDP
3285 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-05-31 12:10 | 2011-05-31 12:19 | 971 | 9 | H4212971 | 8739 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | NO LOAD ON C PHASE OUT OF THE STATION//LOOP BURNT OPEN ON REGULATOR IN STATION WAITING ON STATION MECH. TO CHECK REGULATOR PR TOLLIVER//BYPASSED REGULATOR POWER RESTORED AT 12:17 PR TOLLIVER RELEASED BY CREW 078H03//VER/CRB IDCC DUP TO OPEN BREAKER XXXX
3286 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-01-06 15:52 | 2022-01-07 12:40 | 7 | 1248 | 4313361 | 8736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 4wd pickup neededLINE FUSE OUT ON 247-A -497. ROAD GOES STRAIGHT UP MOUNTAIN, MAY NOT BE ABLE TO PATROL. CANNOT ACCESS TONIGHT. P.HICKS Released by crew 077H09. P.HICKS Released by crew 077H09 /// broken cutout on pole 246A-613
3287 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-03-31 12:36 | 2015-03-31 18:25 | 25 | 349 | H4247321 | 8725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RIGHT HAND PHASE FUSE BLOWN (A PHASE 14 CUST) ON POLE 794-246///AT POLE 794 -98 PHASE OUT OF SAG DOWN BELOW NEUTRAL BEEN BLOWING INTO NEUTRAL WHEN WIND BLOWS//CREW ENROUTE//NO TRUCK//WILL HAVE TO OPEN OTHER TWO PHASES WHEN CREW ARRIVES TO REPAIR//OPENED OTHER 2 PHASES AT 17:15//REPAIRS MADE//RESTORED AT 18:25//COMPLETE//EM COD-37 TOTAL DUP OF 4247321 FOR B & C PHASE OUTAGE 25 CUST VER/HFP L3/HFP AJB
3288 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2021-03-28 18:40 | 2021-03-29 03:45 | 39 | 545 | 4394971 | 8715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | bad 7200, 75kva padmount xfmr, not by truck, in a back yard of 120 camelot ct, will need yard dog or mini excavator. need inviromental to clean up oil that has leaked out Released by crew 078H03,open line fuse @0100 in @0345 all cust restored please close ticket thanks,bt Released by crew 078H02
3289 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-12-22 05:02 | 2008-12-22 05:46 | 198 | 44 | H62145-1 | 8712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE HAS BURNED DOWN ON POLE 356-89 WILL NEED 3 MEN AND A HAND COIL OF # 4 COPPER "B" PHASE ONLY COD-207 OPENED "A"&"C" @ 0502 COD-198/ ALL POWER RESTORED @ 0546 PUT WIRE BACK AND CLOSED RECLOSERS BACK IN AT 0546 VER/KEP L3/KEP IDC XXXX
3290 | South Williamson | 3200302 | BELFRY | TOLER | 2015-06-27 02:34 | 2015-06-27 03:00 | 335 | 26 | H4669351 | 8710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 079H03 LEAD BURN OFF A PHASE ON THREE PHASE RECLOSER WILL OPEN TO MAKE REPAIRS R THOMAS//OPENED OTHER PHASES @ 0234//THIS OUTAGED YHE OTHER 335 CUSTS //ORGINALLY 200// VER/CRB L3/DKG SEE 4669351 FOR ORIGIAL 200 CUST AJB
3291 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-12-28 10:09 | 2008-12-28 15:20 | 28 | 311 | 64608-1 | 8708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ,,,,TOP OF POLE 454-1645 BURNT OFF ABOUT A FOOT AND 9 INCHES OF POLE GONE I STOPPED FIRE BY REMOVING BURNT OFF PIECES AND CUTTING OUT THE REST I DO NOT BELIEVE YOU CAN FRAME DOWN A POLE TOP OR POLE CHANGE OUT WILL HAVE TO BE DONE. IT IS TRUCK ACCESSIBLE//3001401 INSTALLED FIBERGLASS POLE TOP NO OTHER FIELD WORK REQUIRED//VER/CRB L3/KEP IDC XXXX
3292 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-10-08 11:10 | 2015-10-08 12:08 | 150 | 58 | H4327381 | 8700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP ON POLE# 151-22 BURNT INTO DUE TO CLOSE SPACEING ALSO BURNT NEUTRAL DOWN , WILLNEED TO OPEN OTHER RECLOSERS ON POLE# 151-252 IN ODER TO MAKE REPAIRS WILL KEEP TIMES // B PHASE INITALLY OUT 61 CUST // OPENED A & C RECL @ 1110 = 150 CUST // CLOSED AT 12:08 DUP OF 4327381 VER/HFP L3/HFP AJB
3293 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-02-20 17:52 | 2015-02-20 20:10 | 63 | 138 | H4053801 | 8694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 25KV CSP XFMR BURNT UP, NEEDS CHANGED/ MANUAL, 12KV. // OPENED RECL 63 CUST @ _1752___ TO FIX BROKEN INSULATOR // CLOSED @ __2010______ XFMR 3 CUST BACK ON @ 2028 // DUP OF 4053801 FOR RECL OUTAGE VER/HFP L3/HFP AJB
3294 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-03-12 12:00 | 2008-03-12 15:01 | 48 | 181 | 56519-1 | 8688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001203/POLE FIRE OR DEFECTIVE POLE ****** ERIC BAIER CUT OPEN POINT 69-255 TO SAFELY ISOLATE POLE 45-2783 TO REPLACE POLE OTHER LINES ISOLATED ON POLE 69-254 SHOWN ON ORDERS 56464 & 56472 ALSO NO POINT 45-2782 . VER/PDP IDC XXXX
3295 | Hazard | 3303902 | LESLIE | WOOTON | 2015-08-04 23:21 | 2015-08-05 12:30 | 11 | 789 | 4979111 | 8679 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 6DISC ON FUSE POLE WILL NEED LINE CREW IN THE AM TO MAKE REPAIRS RELEASED BY CREW 077S01 OPENED STEPDOWN AT 11:18 CLOSED AT 12:30// VER/ ADH /// VER TIMES PER VOICE REC - SEE DUP H4979111 FOR STEPDOWN OUTAGE OF 24 CUST L3/HFP HFPC DUP
3296 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-11-14 22:19 | 2014-11-15 10:30 | 30 | 731 | 4728891 | 8673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY WIRE DOWN FROM POLE 99 TO POLE 62 BUCKET TRUCK ACESS. TOOK CLAMP OFF ON POLE 16 TRIED 15T FUSE ON POLE 3, NEED 3 MAN CREW , CAN USE ONE D OR RELEASED BY CREW 077H02 PUT WIRE UP AND RESTORED POWER TO REST OF CUSTOMERS AT 1030 RELEASED BY CREW 077H03 VER/SEF // BAD SPOT IN CONDUCTOR L3/HFP AJB
3297 | Hazard | 3303902 | LESLIE | WOOTON | 2019-03-26 12:53 | 2019-03-26 15:20 | 59 | 147 | 4025051 | 8673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 365A/116 loop ins. went bad no fire now brunt end arm off need crew and 4 8 foot arms 6 deadend ins.3 arm pins and ins. 7200 ¦¦ no outage until recl opened - first step for coins call - delete in DOVS ¦¦365A/116 loop ins. went bad no fire now brunt end arm off need crew and 4 8 foot arms 6 deadend ins.3 arm pins and ins. 7200 Released by crew 077S03 opened on pole 365-c 209 at 12:53 to make repairs closed back at 1520
3298 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-07-27 17:50 | 2017-07-27 21:07 | 44 | 197 | 4189741 | 8668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 842B27 FOUND AND REPLACED BROKEN CUTOUT ON 866-7 RESTORED POWER AT 21:07 38820842B00027 38820866A00007 VER/AWD SJG
3299 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-01-02 13:09 | 2012-01-02 16:30 | 43 | 201 | 4225441 | 8643 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIDDLE PHASE RECLOSER LOCKED OUT, PATROLLING LINE. MIDDLE PHASE HAS BURNT DOWN BECAUSE OF BAD CUTOUT ON POLE. MAIN LINE NEUTRAL IS DOWN ALSO. POLE # 183-124//COD 32//OPENED OTHER 2 PHASES @ APPROX 1430 PER SERVICER//COD +112 SEE H4225441// TOTAL OUT 156// VER/DBM IDCC CNT32 PH A IS MIDDLE XXXX
3300 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-08-22 18:56 | 2011-08-22 19:16 | 432 | 20 | 4743641B | 8640 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE | SYDNEY STATION INTERRUPTED DUE TO TRANSMISSION.. TDC WORKING TO RESTORE STATION AS SOON AS POSSIBLE. VERIFIED BY DKG/TRANSMISSION POLE SPLIT ALLOWING STATIC WIRE TO FALL ON CONDUCTOR ..DROPPED 432 CUST TO GO BACK TO NORMAL IDC XXXX
3301 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-01-18 01:30 | 2013-01-18 06:00 | 32 | 270 | H4659371 | 8640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE DOWN A PHASE RECLOSER OPEN AT START OF OUTAGE 2 CUST *** SERVICER OPENED B-C AT 0130 . 27 CC *AT 0155 CREW CALLOUT.OLD WIRE FULL OF SPLICES FELL DOWN. WE PUT THE WIRE BACK UP AND CLOSED THE RECLOSERS 4659371 VER/PDP IDC CHANGED COUNT FROM 27 XXXX
3302 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-09-25 23:45 | 2015-09-26 03:45 | 36 | 240 | 4272281 | 8640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 233-65 VER/KEP L3/HFP HFPC FP 38830233000065 AJB
3303 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-04-19 14:34 | 2008-04-19 16:18 | 83 | 104 | 52383-1 | 8632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | ,,, FOUND BURNT UP PRIMARY JUMPER ,,,, REPAIRED JUMPER MYSELF RECLOSER BACK IN AT 16:17//3000202//VER/CRB AJB
3304 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2015-07-06 10:22 | 2015-07-06 13:08 | 52 | 166 | 4730341 | 8632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED LOAD SIDE HOT TAP AND STIRRUP, ALL WORK COMPLETE / GXJ// VER/ ADH AJB
3305 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-10-03 14:10 | 2018-10-03 19:54 | 162 | 344 | 4193811 | 8628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 man crew required 204-31 bad location/ had to open recl 38830205000017 (150cc) 1924-1954/ 38830204000031 (12cc) 1954 L3/HFP
3306 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2011-02-10 16:06 | 2011-02-10 19:22 | 44 | 196 | 55973-1 | 8624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | MIDDLE PHASE OUT. RECLOSER SHOWING CLOSED ON POLE 892C253. PATROLLING NOW . MAY BE LOOP OPEN//FOUND BROKE FUSE ON POLE 38820869A29003//MIDDLE PHASE FUSE ONLY IS BROKE//COD 44// //VER/GAH IDC XXXX
3307 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-04-16 02:16 | 2011-04-16 04:14 | 73 | 118 | 57557-1 | 8614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 429-67 BROKE 19.9 CUTOUT ALSO WHILE CHANGING HIGH SIDE NOTICED LOW SIDE WAS STARTING TO FELL CHANGED LOW SIDE CUTOUT AS WELL ALL POWER RESTORED AT 0414 CLOSE TICKET VER/PDP IDC XXXX
3308 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-05-26 17:32 | 2020-05-26 22:06 | 90 | 274 | 4910581 | 8602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | C phase down between poles 38831074A00349 & 38831074A00350 pulled out of sleeve. Need crew and flagging crew busy road. Can work with bucket. Opened C phase 300 amp swich on 38831074A00339 & tagged to DDC @ 19:20 will have to open A&B phase to make repairs when crew arrives. Opened A&B switches @ 21:09//closed 2206//cod 16(+72)
3309 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2014-01-27 21:15 | 2014-01-27 21:35 | 430 | 20 | 4318171 | 8600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CEW OPENING RECLOSERS TO MAKE REPAIRS, SOLID BLADE SWITCH BREAKING DOWN. CREW ON THE WAY OPENED RECLOSER ON POLE 67-A-261 AT 21:15 CLOSED RECLOSERS BACK IN AT 21:35 VER/KEP L3/HFP IDC XXXX
3310 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-08-30 11:48 | 2021-08-31 11:39 | 6 | 1431 | 4176141 | 8586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 079S03 xfmr fuse out be refusing bad co complete order
3311 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-08-19 17:40 | 2009-08-19 19:54 | 64 | 134 | 52748-1 | 8576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, POLE TOP BURNT OFF, POLE#1113-D-113, CALLED R MARCUM FOR HELP//COD 64// VER/DBM IDC XXXX
3312 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-06-28 15:07 | 2008-06-28 18:13 | 46 | 186 | 57556-1 | 8556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT ARRESTOR IN THE CLEAR AND REFUSED LINE VER/KEP IDC XXXX
3313 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-10-29 05:04 | 2017-10-29 11:00 | 24 | 356 | 4507641 | 8544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | UNIT 3112 REPORTS RECLOSER IS OPENBAD CUTOUT BURNT TOP OF POLE OFFBAD CUTOUT BURNT TOP OF POLE OFF RECLOSER ISOLATED AND TAGED TO VIRGIL HURT GROUND PLACED AT POLE #459-360 VER/AWD L3/HFP XXXHFP ACB
3314 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-09-16 15:55 | 2010-09-16 19:29 | 44 | 214 | 50718-1 | 8544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 36918089 // ONE SPAN # 4 SOLID COPPER DOWN FROM POLE 378-52 TO 378-54, NO TRUCKS TO POLES. OPENED SOLID BLADE ON POLE 378-50 AND PLACED GROUNDS. NEED LINE CREW. RELEASED BY CREW 078S01/CREW ON SITE/FETR2030/VEM/REPAIRS MADE AND REMAINING CUST RESTORED AT 1929/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14//COD 44// VER/DBM IDC XXXX
3315 | Hazard | 3303901 | LESLIE | HYDEN | 2012-05-05 17:03 | 2012-05-07 16:30 | 3 | 2847 | 4751081 | 8541 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S01//WILL WORK MONDAY MORNING//NON-RESIDENCE IS ACROSS LAKE COD-3 ISO LF 37830242000144 VER/HFP L3/HFP IDC XXXX
3316 | Whitesburg | 3312901 | JENKINS | KONA | 2010-01-12 15:40 | 2010-01-12 19:51 | 34 | 251 | 53251-1 | 8534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED BIG BUCKET TO REPLACE... MADE REPAIRS RESTORED POWER AT 19:51//COD 34 IDC XXXX
3317 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2019-05-30 15:42 | 2019-05-30 18:09 | 58 | 147 | 4389751 | 8526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | found l/f out patrolled line found bursted pri deadend ins and bad arm pin ins on 879-215, have rep maded all power restored at this loc at 1809 by amg
3318 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-09-26 14:54 | 2015-09-26 23:50 | 35 | 536 | 4275231 | 8525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | LOOPS CUT AT POLE 38830282000030 NO GROUNDS PLACED // POLE 282-31 BURNT OFF 40/5 POLE CUT POLE LINE FUSE IN POLE 282-30 REC. BACK ON 16:25,ALL CUST RESTORED @ 2350 PLEASE CLOSE TICKET THANKS.BT RELEASED BY CREW 078H19 VER/KEP L3/DKG MAP DOES NOT SHOW REC ON POLE 30/OPEN POINT MADE IN POWERON TO REFLECT CORRECT SEQUENCE AJB
3319 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-06-12 15:01 | 2008-06-12 15:52 | 167 | 51 | 63181-1 | 8517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 24759139// 143 CUST COD-HFP HOT LINE CLAMP BURNT-UP ON RECLOSER POLE. REPAIR IN PROGRESS. REPLACED HOTLINE CLAMP AND STIRRUP - RE-ENERGIZED RECLOSER AT 15:52. SH CCC -HFP VER/HFP MLR CNT 143 IDCC XXXX
3320 | Hazard | 3303902 | LESLIE | WOOTON | 2020-08-20 10:18 | 2020-08-20 12:29 | 65 | 131 | 4350031 | 8515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | undoing conductor from insulator on pole 37830413B00094 and conductor broke // repaired and restored @1229
3321 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-02-22 06:55 | 2017-02-22 09:06 | 65 | 131 | 4413301 | 8515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOAD SIDE FUSE OF STEPDOWN XFM. BLOWN ON POLE 286-235...WILL PATROL..FOUND BAD CUTOUT ON POLE 286-36.WILL MAKE REPAIRS...REPAIRS MADE CLOSED BACK IN @ 09:06... L3/HFP XXXHFP AJB
3322 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-08-27 07:33 | 2008-08-27 14:00 | 22 | 387 | 55778-1 | 8514 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3202202// CONDUCTOR OFF INSOLATOR ON POLE 818-D-157. LINE FUSE OUT ON POLE 819-1//COD 76// UPDATED FETR DUE TO CREW BEING USED AT BREAKER OUTAGE//DHE PAUL MUNCY 3677 TO REPAIR THIS//3202202// CONDUCTOR OFF INSOLATOR ON POLE 818-D-157. LINE FUSE OUT ON POLE 819-1//COD 76// UPDATED FETR DUE TO CREW BEING USED AT BREAKER OUTAGE RELEASED BY CREW 079H02// VER/DBM IDC CHANGED COUNT FROM 76 AND PN FROM 38820794D00029 XXXX
3323 | Hazard | 3420001 | SOFT SHELL | VEST | 2018-11-09 10:03 | 2018-11-09 11:10 | 127 | 67 | 4382321 | 8509 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 156-239, can remove hot tap and restore power. power restored//SENT TO TECH
3324 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2018-11-26 03:10 | 2018-11-26 08:37 | 26 | 327 | 4476251 | 8502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | will work in the AM 11/26/18 per late night guidelines.line fuse out on 211-423. will be patrolling line.netural is down @ 37830211C000266. appears to be broke at pole .map showes 8a . will need wire & sleves. COD-26 ISO LF 37830211C00423
3325 | Hazard | 3303902 | LESLIE | WOOTON | 2014-09-01 01:56 | 2014-09-01 14:55 | 12 | 779 | 4442811 | 8493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD 7200 CUTOUT ON POLE 37830511000014/// AFTER REPAIRING CUTOUT FOUND TREE ON LINE AT POLE 37830511B40130// OPENED UP LINE FUSE ON 37830511B40130 SO TREE CREW CAN REMOVE TREEWILL WORK IN THE AM 9-1-14 BAD 7200 CUTOUT POWER RESTORE TO 511-130 @ 1320 MADE HOT @ 1455 RESTORING POWER TO EVERYONE RELEASED BY CREW 077S01// ISO 37830511000014/// COD 12// VER/BOW VER/DKG L3/DKG
3326 | Whitesburg | 3312902 | JENKINS | JENKINS | 2020-07-25 18:29 | 2020-07-25 20:10 | 84 | 101 | 4232551 | 8484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp on a nc switch burned off on pole 381-698 . I replaced it Released by crew 077S12/ A Phase (84 customers) Hot Clamp burnt off on the switch 37830381D40698 repaired and restored at 2010/ ISO 37830381D40698/ COD 84
3327 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2010-06-14 08:44 | 2010-06-14 14:15 | 26 | 331 | 63299-1 | 8481 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON POLE 139B366. A PHASE CUTOUT BROKE INTO. DALE HAS CREW HEADED THIS WAY. B AND C PHASE OFF AT 13:40 ON AT 14:15. CUTOUTS REPLACED EVERYTHING OK//VER/CRB
3328 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-12-01 11:37 | 2014-12-01 15:20 | 45 | 223 | 4821101 | 8481 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN AT POLE 1125-822, #4 CU PRIMARY NEUTRAL DOWN FROM POLE 564 TO POLE 1125-216, NO TRUCK ACCESS . REPAIRED PRIMARY NEUTRAL AND CLOSED 1125-564 AT 14:43 . REPLACED CUTOUT POLE 822 AND CLOSED AT 15:20 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/CRB L3/HFP AJB
3329 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-07-17 03:30 | 2008-07-17 04:24 | 157 | 54 | 53484-1 | 8478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3308002/// PART OF OUTAGE 53473 ,, PUTTING UP WIRE,, ONE OF THREE RECLS FOUND OPEN.. OPENED THE OTHER TWO TO MAKE REPAIRS. POWER RESTORED AT 0400HRS DKG/FIX IN HOIS/CANNOT CLOSE ORDER MLR THIS OUTAGE FOR ONE PHASE
3330 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-08-20 18:11 | 2014-08-20 19:00 | 173 | 49 | 4391531 | 8477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED A&B PHASES ON SWITCH @ 38821139B00109/// COD 159 +16/// 2 BAD CUTOUTS ON POLE 38821139B00037/// NEEDS MAP DISCREPANCY ENTERED BEFORE CLOSING THIS ORDER///// B PHASE-15T FUSE AND A PHASE 20T FUSE IS NOT SHOWN ON THE MAP ON POLE 38821139B00037 BUT SHOULD BE SHOWN//THIS IS RELATED TO ORDER 4388291// MADE MAP DESCREPANCY ADH// VER/ ADH AJB COUNT MINUS 2 ON OTHER ORDER.
3331 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-01-14 14:45 | 2014-01-14 19:40 | 93 | 295 | 4281751 | 8475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF @ 304-58 NEED LINE CREW TRUCK OK,CUT LOOP @ 303-76 TAG TO DDC,RECLOSER IN @ 1543 // GAVE RON VIRGIN PERMISSION TO REMOVE DDC HOLD TAGS & REPLACE WITH HIS OWN///REPLACED PL W/45CL5///ALSO INSTALLED 40T LF ON POLE 303-76 WHERE LOOPS WERE CUT THAT LOOKS TO THE END OF THE LINE//PWRR RESTORED @ 19:40///LIGHTS CAME ON RELEASED BY CREW 078H16//MADE MDC VER/CRB L3/HFP IDC XXXX
3332 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-12-23 06:12 | 2013-12-23 08:33 | 60 | 141 | 4194961 | 8460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECL OPEN,WILL PTRL COD 60C PHASE RECL OPEN,WILL PTRL//////BROKEN CUTOUT AT CAP BANK 1056-282,CLEARED THIS FAULT.WILL CLOSE RECL//////CLOSED RECL AND RESTORED VER/SEF L3/HFP IDC XXXX
3333 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-07-14 08:30 | 2012-07-15 08:00 | 6 | 1410 | 4721011 | 8460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELEASED BY CREW 074S03 BAD RUN BAD UG FEEDING PAPA JOHNS PIZZA NEED TO REPLACE REWWIRE FOR THIS TX. RELEASED BY CREW 079H01CALL BILL JOHNSON FOR CABLE LOCATE RELEASED BY CREW 074S10//CREW ON SITE, WILL DE-ENERGIZE @ THUMB CABLE. BAD UNDER ROAD. PULLED OLD OUT AND NEW CABLE IN. LIKE TERMINATING NOW. OPENED XFMR 22:45, CLOSED @ 08:00. //VER/GAH IDCC CDC83 CCU XXXX
3334 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-06-15 10:36 | 2016-06-15 15:50 | 27 | 314 | 4348081 | 8454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 269-79 WINDSTREAM 40/5 NEED 45/2 TOP BUSTED OUT SEND TO TECH /TRUCKS OK//PAT THOVSON WAS GOING TO CONTACT WINDSTREAM// OPENED FUSE ON TUNNEL CUT LOOP AT 10:36 AND ON SINGLE TAP OPEN RECLOSER AT 13:47 CLOSED RECLOSER ON 269-D-74 AT 14:20 TUNNEL CUT LOOP WILL REMAIN OUT FOR ANOTHER 2 HOURS AND THE SINGLE TAP, TAP FEEDING TOWARDS 269-80 RESTORED AT 15:49 SINGLE TAP ON AT 15:50 SEE 4349661 FOR RECL OUTAGE (WINDSTREAM POLE) VER/HFP L3/HFP AJB BOTH LF OR ONE?
3335 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2009-10-21 09:31 | 2009-10-21 11:39 | 66 | 128 | 62701-1 | 8448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, CHECKING FOR TROUBLE, BAD TRANS CUTOUT ON FUSE POLE, WHEN TRANS CUTOUT FAILED, IT BLEW LATERAL FUSE//COD 66// VER/DBM IDC XXXX
3336 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-03-06 11:34 | 2015-03-06 13:02 | 96 | 88 | 4144761 | 8448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 1302 03/06 TRYING LINE FUSE AFTER PATROLLINGPOLE 69-1557 BAD LA TRUCK TO POLE 69-1554 80T LINE FUSE L3/DKGXXXX AJB
3337 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2019-10-07 22:09 | 2019-10-08 07:45 | 29 | 576 | 4115961 | 8439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Fault on UG blew 20T riser fuse 785-1725 and line fuse 785-1733. Closed LF 785-1733 @ 00:30 restoring all but xfmrs 785-893 & 898. Testing to determine fault. Repairing fault in ug conductor. Repaired and restored remaining cust @ 7:45. sh Released by crew 076S02
3338 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-08-20 04:48 | 2014-08-20 10:00 | 27 | 312 | 4387061 | 8424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL WORK IN THE AM 8-20-14 WILL WORK IN THE AM 8-20-14WILL WORK IN THE AM 8-20-14 WILL WORK IN THE AM 8-20-14,, RECLOSER IS OPEN ON 549-135 PATROLLING LINEWILL WORK IN THE AM 8-20-14 WILL WORK IN THE AM 8-20-14,, RECLOSER IS OPEN ON 549-135 PATROLLING LINE,,, CLEARED TWO ARRESTERS ON 549-106 RECLOSER CLOSED AND HOLDING AT 10:00WILL WORK IN THE AM 8-20-14 WILL WORK IN THE AM 8-20-14,, RECLOSER IS OPEN ON 549-135 PATROLLING LINE,,, CLEARED TWO ARRESTERS ON 549-106 RECLOSER CLOSED AND HOLDING AJB
3339 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2015-10-11 00:41 | 2015-10-11 06:05 | 26 | 324 | 4337631 | 8424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CHECKING NOW.UNDER GROUND BAD CALLING CREW OUT!! VER/KEP L3/HFP HFPC CDC83 AJB
3340 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-06-14 21:27 | 2009-06-14 23:45 | 61 | 138 | 63920-1 | 8418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 65T FUSE OUT ON POLE 1147-101. LOOKING OVER LINE AT THIS TIME. BAD CSP TRANSFORMER ON POLE 1147-98. SERVES NOTHING AT THIS TIME. NEEDS REMOVED. NEED TO SEND COPY TO RON RYE ENG PIKEVILLE. POLE 1147-101 PRIMARY LAT NEEDS TO BE BELOW THE THREE PHASE. ROOM ON POLE TO LOWER DOWN THIS IS VERY HARD TO WORK WITH AND IT ABOVE THE THREE PHASE. SEND COPY TO ROW JASON BRADSHAW PIKEVILLE LINE NEEDS CUT BAD FROM POLE 1147-101 TO END OF LINE.//COD 61// VER/DBM MLR OK
3341 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-11-01 03:16 | 2013-11-01 07:31 | 33 | 255 | 4986951 | 8415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON RIGHT HAND PHASE RECLOSR LEAD HAS COME OFF THE HOT LINE CLAMP "C" PHASE ONLY COD-26 VER/KEP L3/HFP IDCC CNT26 XXXX
3342 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-07-10 03:36 | 2009-07-10 05:28 | 75 | 112 | 52787-1 | 8400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FETR 0530 EMERGENCY . SWITCHING ORDER TO TRANSFER CUSTOMERS FROM THE HITCHINS/GRAYSON 12KV CKT TO THE GRAYSON/DIXIE PARK 12KV CKT. TO ALLOW VERNON MULLINS TO REPAIR PHASE OFF INSULATOR ON POLE 207-56 . 75 CC OUTAGE FROM 0336 TO ? CORRECT IN HOIS. TO SHOW ONLY 75 CC . RELEASED BY CREW 078H14 VER/ARN MLRC CDC 90
3343 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-10-15 17:57 | 2018-10-15 19:18 | 154 | 81 | 4256391 | 8382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPEN RECLOSERS ON POLE 426-43 AT 18:30 CLOSED AT 19;18 BAD INSULATOR ON POLE 450-162 Released by crew 075H03 // CALLED MIKE EMBERTON & HE SAID CENTER PHASE RECLOSER WAS ALREADY OPEN - PER CALLS & MAP 'B' PHASE 30 CUST L3/HFP
3344 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2019-06-16 15:57 | 2019-06-16 17:00 | 133 | 63 | 4513641 | 8379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | right hand phase fuse broken//map calls this phase C but most cust calls are on B phase and some on A&C//cod 133??//100 amp fuse broke at pole 38820942B41484 on the B phase. Power restored at 17:00.//
3345 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-06-25 23:11 | 2015-06-26 01:09 | 71 | 118 | 4658291 | 8378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | MADE AED ON ARRESTER//REPLACED CUTOUT VER/CRB
3346 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-02-09 20:01 | 2020-02-09 22:50 | 96 | 169 | 4386221 | 8374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Phase C line fuse cutout failed (46cc). Opened PH A & B Line fuses @ 22:38 to replace (50cc). Replaced cutout and closed all three fuses on 38830737000221 @ 22:50. sh Released by crew 076S02 L3/HFP
3347 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-09-27 11:57 | 2018-09-28 15:51 | 5 | 1674 | 4166631 | 8370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on line fuse glen combs is going to get crew to replace Released by crew 077S05..pole to be worked is across creek that is flooded waist deep and running fast, will have to leave till water gos down, probily friday..p.hicks /// CREW TO RETURN LATER FRIDAY ALLOWING TIME FOR WATER TO GO DOWN repairs made power restored at 1551
3348 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-05-11 12:04 | 2019-05-11 16:10 | 34 | 246 | 4252901 | 8364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 37830311000001.this is open point that separates Burdine/Levisa and Elwood/Dorton.will need line crew with 7200 cutout to make repairs..nontruck access.//cutout broke on pole 311-01.this is open point that separates Burdine/Levisa and Elwood/Dorton.will need line crew with 7200 cutout to make repairs..nontruck access. ¦¦¦ PER THE RELIABILITY CALL... THIS COULD HAVE POSSIBLY BEEN THE CAUSE OF OUTAGE 4251411 L3/HFP
3349 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-10-16 02:22 | 2020-10-16 09:20 | 20 | 418 | 4560611 | 8360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | send to Shane Tackett after shift starts per Dennis MasseyLine fuse blown on 335-C-138, ( Patroling Line ).Line fuse blown on 335-C-138, ( Patroling Line ).Cutout had cracks in it on 335-C-138,Went ahead and changed it and restored service at 09:20..
3350 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-04-04 12:19 | 2016-04-04 14:20 | 69 | 121 | 4049301 | 8349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED RECLOSER ON 865-20 TO REPLACE BROKEN POLES 865-28 & 865-20 . ISO 38820865A00020 COD 69 VER/AWD AJB TOF04/03
3351 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-09-14 23:30 | 2012-09-15 07:40 | 24 | 490 | 4049551 | 8340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINE FUSE IS BLOWN ON POLE 23-201. I AM PATROLLING LINE NOW. POLE#-37830023D40103 HAS ROTTED AT GROUND LEVEL AND FELL OVER. TREE IS HOLDING IT UP. //D. MASSEY, R. RAY & B. CAMPBELL TO ASSIST // I OPENED A SOLID BLADE CUTOUT ON POLE 23-78 TO ISOLATE FAULT. I CLOSED LINE FUSE AT 23-201 IN AT 01:20. THIS GOT 3 OR 4 TRANSFORMERS BACK ON. TRANS. ON 78 IS ELINE FUSE IS BLOWN ON POLE 23-201. I AM PATROLLING LINE NOW. POLE#-37830023D40103 HAS VER/KEP IDC XXXX
3352 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-05-02 05:42 | 2021-05-02 09:05 | 41 | 203 | 4511871 | 8323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | suspect Ph A only is open 41 customers//hot tap burned out of stirrup..bad location,, road washed out. only 1 recloser is out..901-240
3353 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-07-28 14:13 | 2012-07-28 17:52 | 39 | 219 | 4857601 | 8320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 182-144 HAS BURNT OFF, BAD CUTOUT. --- SDB / 1600 / OPEN AT POLE 182-D-142. CLOSED FUSE AT POLE 182-C-132. 13 CC REST. VER/KEP IDC XXXX
3354 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2014-06-09 19:51 | 2014-06-09 20:19 | 297 | 28 | 4000281 | 8316 | DISTRIBUTION STATION | EQUIPMENT FAILURE | CUTOUT | OUTAGE TO MAKE EMERGENCY REPAIRS IN STATION/ ISOLATED 12KV BUS/ VER/KEP AJB
3355 | Hazard | 3303902 | LESLIE | WOOTON | 2009-12-02 11:48 | 2009-12-02 16:00 | 33 | 252 | 55344-1 | 8316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD BURNING POLE CAN LOWER ARM CREW HAS BEEN CALLED OPEN REC ON POLE 366-51 AT 1148 // VER/DBM IDC XXXX
3356 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-04-25 20:42 | 2011-04-26 12:06 | 9 | 924 | 64904-1 | 8316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE CKING TROUBLE///PRIMARY DOWN ACROSS HWY 421 WAITING FOR AWP TO FLAG TO GET HERE TO FLAG ROAD// REPLACE 19.9 CUTOUT AND 10 FT #4 SOLID COPPER ON POLE #37830387B00475//COD 9// VER/DBM IDC XXXX
3357 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-02-28 01:20 | 2010-02-28 01:50 | 277 | 30 | 61623-1 | 8310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308502// STS 34050489 == INSULATOR GOING BAD ON CENTER PHASE == CALLED FOR LINE CREW == OPEN RECLOSER AT 01:20 == ON AT 01:50 == POWEROK IDCC TOF2242 XXXX
3358 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-08-06 03:59 | 2010-08-06 16:34 | 11 | 755 | 66648-1 | 8305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE OPEN ON POLE #38830331000042, POLE #331-43-TOP OF POLE BURNT OFF,WILL NEED 40-4, COPPER PRI. DEADENDS, 25 KVA NEW BRACKT. AND CUSTOUT, POLE HAS BURNT DOWN TO TRANSFORMER. RELEASED BY CREW 078E09 VER/HFP L3/HFP
3359 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-03-19 16:08 | 2008-03-19 17:48 | 87 | 100 | 58723-1 | 8297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601// BUSTED CUTOUT ON POLE CUTOUT BAD116-250 ALSO INSTALLED 40T LINE FUSE POLE 116-726 50T HIGH SIDE 80T LOW SIDE// WILL ISSUE MAP DISC FOR FUSE// VER/TOM IDC XXXX
3360 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-03-10 14:37 | 2021-03-10 16:39 | 68 | 122 | 4323401 | 8296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser is open on 97-134,We have Primary down at pole 121-229,Rick Ray is on his way to help make repairs.Restored at 16:39.
3361 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-07-19 21:25 | 2008-07-20 17:10 | 7 | 1185 | 54268-1 | 8295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3301402 - //FUSE WOULDNT STAY GOING TO RETURN IN THE MORNING TO CHECK UG PRIMARY I ADVISED CUSTOMER AND THEY AGREED TO WAIT // 08:30 RESTORED TO PADMOUNT AT POLE 37830248B00759 RELEASED BY CREW 077S043301402 - / // REPLACED WITH OVERHEAD AND COMPLETED RESTORE IDCC CDC83 XXXX
3362 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-06-08 18:27 | 2015-06-09 09:40 | 11 | 913 | 4534521 | 8291 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | \\IDC ONE OF THREE FUSES OUT 40TCREW REQUIRED TRUCK OK- BROKEN CUT-OUT ON POLE 38830118C14060 NEAR CATLETTSBURG YOUTH CENTER FUSE OUT ON POLE 38830118C14027 NEAR NEW JUSTICE CENTER RELEASED BY CREW 078H18/CLOSED LINE FUSE IN @ 1156/ RELEASED BY CREW 078Q04 /// NEED MORE INFORMATION ON WHICH FUSE WAS OUT??? VER/HFP IDCC TON0042, CNT40 XXXX AJB
3363 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-05-01 06:57 | 2009-05-01 09:46 | 49 | 169 | 61608-1 | 8281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR#29620607//3008701// POSSIBLE BAD STEPDOWN TRANSFORMER CREW ON SITE CHECKING NOW // COD-49 ENTERED MD --HFP L3/HFP IDC PER CONF CALL FOUND BAD CUTOUT XXXX
3364 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-06-24 16:16 | 2011-06-24 17:50 | 88 | 94 | 4411051 | 8272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | ISOLATED CKT DUE TO CONDUCTOR PULLED LOOSE FROM INSULATOR ON POLE 1149-50 //VER/GAH IDC XXXX
3365 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-05-23 13:22 | 2011-05-23 16:30 | 44 | 188 | 4143971 | 8272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 30074286 // BAD CUT-OUT ON POLE 43-276 GIVE TO JOE HEMLEPP RELEASED BY CREW 078S09/CREW ON SITE MAKING REPAIRS///REPAIRS COMPLETE XFMER OUT OF SERVICE FROM 16:15 TO 16:30 POWER REST.@16:30 J. HEMLEPP& CREW 078H05 RELEASED BY CREW 078H05 COD- 44 ISO RECL 38830043000189 VER/HFP L3/HFP
3366 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-04-10 13:59 | 2013-04-10 16:55 | 47 | 176 | 4995351 | 8272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LOW SIDE STEPDOWN FUSE BLOWN, CHECKING LINE//// ARRESTOR BLOWED OFF POLE, TREES IN LINE GOT ASPLUNDH TO CUT TREES THAT ARE IN LINE WHILE POWER IS OFF/// TREES CUT, ARRESTOR TOOK CARE OF, POWER RESTORED.. ///VER/CRB L/3 CRB IDC XXXX
3367 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-07-01 00:01 | 2014-07-01 11:30 | 12 | 689 | 4177121 | 8268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | # 4 ACSR PRIMARY DOWN FROM POLE 618-9 TO 618-1, TRUCKS TO POLE 618-9. NEED LINE CREW. WORK IN DAY TIME. RELEASED BY CREW 078S01.. FETR 12:00 CREW ONSIGHT. 15T FUSE BACK IN AT 11:30 VER/HFP L3/HFP IDC CHANGED FROM UNKNOWN XXXX AJB
3368 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-10-08 00:54 | 2018-10-08 10:05 | 15 | 551 | 4206901 | 8265 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | , have 556 basket burnted into, and hot tap has come off, this is on C phase, can use truck, pole 1098-3107//cod 3// L3/HFP/// trouble tickets show B phase
3369 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2013-02-01 09:15 | 2013-02-01 15:48 | 21 | 393 | 4780901 | 8253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY TAP CUTOUT FAILED AND BURNED POLE OFF. RELEASED BY CREW 079H06 RECL ISOLATED 868-74 AND TAGGED FOR DDC - 1027 - PERM TO JOEY REED TO R/R TAGS .. ON ARRV. ///VER/CRB L/3 CRB IDC XXXX
3370 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-03-15 22:23 | 2012-03-16 12:07 | 10 | 824 | 4586671 | 8240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKEN,WILL REQUIRE OUTAGE ON 3 PHASE TO CHANGE, ABOVE PHASES ON MANUAL POLE. SEE 4587551 FOR RECL OUTAGE TO REPLACE CUTOUTLINE FUSE CUTOUT BROKEN,WILL REQUIRE OUTAGE ON 3 PHASE TO CHANGE, ABOVE PHASES ON MANUAL POLE. RELEASED BY CREW 077S04 COD-10 ISO PO @ 37830153D00009 VER/HFP L3/HFP IDC XXXX
3371 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-05-26 07:57 | 2020-05-26 10:28 | 64 | 151 | 4907041 | 8236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C phase open on pole 38830021B43615/patrolling. #2hendrix primary burnt in two at pole 38830045A31181. Crew required, trucks to pole ¦¦ send to B Ramey per VernonC phase open on pole 38830021B43615/patrolling. #2hendrix primary burnt in two at pole 38830045A31181. Crew required, trucks to pole. Opening Switches on 38830045A31191C phase open on pole 38830021B43615/patrolling. #2hendrix primary burnt in two at pole 38830045A31181. Crew required, trucks to pole. Opening Switches on 38830045A31191
3372 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-02-20 21:40 | 2015-02-21 17:15 | 7 | 1175 | 4059611 | 8225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP APPEARS TO BE OPEN // WILL CHECK// BAD 25 CSP // NEED CUTOUT // CUTOUT BRACKET// MAY NEED TO UPGRADE XFMR// TRUCK IS QUESTIONABLE// THIS IS BEHIND A CARPORT // CREW REQUIRED RELEASED BY CREW 074S05//COD 7// VER/DBM
3373 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-09-20 14:01 | 2013-09-20 14:55 | 152 | 54 | 4870911 | 8208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PHASE OFF BROKEN INSULATOR//RECLOSER GROUNDED, TAGGED AND ISOLATED BY VIRGIL HURT// VER/CRB L/3 CRB IDC NOT SURE IF ALL THREE RECLOSERS WERE OUT XXXX
3374 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-05-18 23:39 | 2020-05-19 02:30 | 48 | 171 | 4851871 | 8208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored @ 02:30.. found nothing on line. fuse had just broke loose
3375 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-03-28 15:16 | 2018-03-28 17:40 | 57 | 144 | 4140161 | 8208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Wire down between 37830182B00160 and 37830182B00110.patrolling line, span of primary is down
3376 | Hazard | 3309302 | VICCO | JEFF | 2012-08-27 17:34 | 2012-08-28 06:25 | 11 | 771 | 4977981 | 8205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 37830347D00117, MAY NEED TO SHOW CUST. OUT./// REFUSED LINE BLEW BACK OUT. RECHECKING LINE. NEED R/W CREW, TERRIBLE ON HILL!//// CUT DEADENDS AND INSTALLED SOLID BLADE SWITCH ON POLE 37830371000037. PAUL GOING BACK TO LINE FUSE AND TRY IT UP TO 371-37.//// GOT POWER RESTORED UP TO POLE 371-37 AT 05:39 (6 CUST).. STILL HAVE FAULT ABOVE POLE 371-37. ALL ON 6:25 (5 CUST) //VER/GAH IDC DIFFICULT TO FIND XXXX
3377 | Whitesburg | 3309302 | VICCO | JEFF | 2014-09-04 16:15 | 2014-09-04 17:25 | 117 | 70 | 4463611 | 8190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 37830348A00135, WE HAVE DEADEND INSULATOR BURNED UP AND CONDUCTOR SAGED BACK, NO POWER OFF RIGHT NOW BUT WHEN CREW GETS HERE WE WILL HAVE TO KILL LINE. NEED LINE CREW, 6 DEADEND INSULATORS FOR 19.9.//SERVICER OPENING RECLOSER 323-D-649, TO ISOLATE TROUBLE TO SWITCH 348-A-52. RECLOSER OFF @ 16:15 ON @16:19/ SWITCH 348-A-52 OPENPOLE 37830348A00135, SIWTCH CLOSED IN @ 17:25// COD 322// VER/ ADH L3/HFP HFPC STP AJB OMS CROSSER.
3378 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-06-16 05:03 | 2012-06-16 07:00 | 70 | 117 | 4919781 | 8190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 37830248A00017, PATROLING LINE.-- BAD GAP ARRESTOR ON POLE 37830248A00439, REPLACED CUTOUT AND ARRESTOR ON POLE 37830248A00439, ALL POWER RESTORED AT 0700. //VER/GAH IDC XXXX
3379 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-04-28 13:40 | 2009-04-28 15:10 | 91 | 90 | 55164-1 | 8190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP EMERGENCY OUTAGE... CREW MAKING REPAIRS TO POLE HAD TO OPEN UP RECLOSER TO COMPLETE THERE WORK SAFELY..... COD-91 ISO POLE 3883104000018 DEAD END CAME LOOSE WHEN CREW WAS WORKING TO REPAIR POLE & CREW HAD TO OPEN RECLOSER. L3/HFP IDC XXXX
3380 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-07-26 13:10 | 2021-07-26 14:44 | 87 | 94 | 4957641 | 8178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Rec 453-91 is open patrolling line/// Replaced broken cutout on 38830429B00027, apr at 1444 close ticket
3381 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-04-22 17:20 | 2017-04-23 00:30 | 19 | 430 | 4669181 | 8170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-253 OPENED 25T LINE FUSE 17:20 POLE 68-967 BURNT OFF 45/4 POLE NO TRUCKS MIT USE BACKYARD TOOL RELEASED BY CREW 078S08//COD 19//REPAIRS COMPLETE // REPLACES 4669011 // AJB INLT CALL IS TO REPORT TROUBLE ONLY.
3382 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-04-20 07:36 | 2019-04-20 11:31 | 45 | 235 | 4139651 | 8167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout has went bad , pole fire, opened line at 08:32/COD 2 FROM BEGINNING OF OUTAGE//cutout has went bad , pole fire, opened line at 08:32, line fuse on pole 227-65 , line fuse back in at 11:31 L3/HFP
3383 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-07-27 16:05 | 2017-07-27 17:13 | 120 | 68 | 4186951 | 8160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830199D00144 HAS ARM ABOUT BURNT INTO,NEED LINE CREW WITH BIG BUCKET AND 1 8FT ARM ,2 ANGLE PINS AND INSULATORS,1 SET OF BRACES RELEASED BY CREW 077S04 REPLACED BAD CUTOUT AND ARM OPENED SOLID BLADES ON POLE 200:368 AT 16:05 RESTORED POWER AT 17:13 VER/AWD SJGC CDC83
3384 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-06-28 02:27 | 2008-06-28 11:34 | 44 | 547 | 57128-1 | 8158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND TOP OF A 454 POLE BURNTED OFF, AT THE END OF DREAM WAY LANE, POLE NUMBER IS 901-400, HAVE LINE ISOLATED AT POLE 901-347, AND GROUNDED AT THIS POLE ALSO, WELL NEED CREW, AND NEW POLE, AND NEW CUTOUT AND ARRESTOR RELEASED BY CREW 078S06---------- POWER ON @ 11:34 VER/ARN AJB
3385 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2010-04-26 23:28 | 2010-04-26 23:46 | 453 | 18 | H51659-1 | 8154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BAD BURNED TOP OF BUCK POLE OUT/ CUT LOOPS ON POLE 401-189 TO ISOLATE/ FEEDER CB CLOSED AT 2008 RESTORING 453 CUSTOMERS // 2328 OPENED FEEDER TO CLOSE LOOPS/2346 CLOSED FEEDER - RESTORED ALL. SEE ALSO 51659-1 VER/LDA IDC XXXX
3386 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-04-25 10:01 | 2014-04-25 17:34 | 18 | 453 | 4632701 | 8154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED POLE 269-170 PHONE COMPANY POLE/NEED 40/5 POLE HAS ALLEY ARM/WITH OPEN WIRE SECONDARY/ON EAGLE HALL CEM RD/LINE FUSE OPEN ON 269-169 RELEASED BY CREW 078S03//CREW ON SEEN MAKING XFERS//REPAIRS MADE///PWR BACK ON @ 17:34///TBL TKT COMPLETED///COD 18// VER/DBM AJB
3387 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-02-23 18:43 | 2021-02-25 16:00 | 3 | 2717 | 4236241 | 8151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 182-b2-2569 bad 25 kva xfr,replaced xfr customers restored complete
3388 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-11-14 08:24 | 2010-11-14 09:38 | 110 | 74 | 55501-1 | 8140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | <<<<PHASE A REC ONLY>>>> LIGHTNING ARRESTER FAILED ON XFMR POLE. CLEARED FAULT AND CLOSED RECLOSER @ 9:38 RESTORING ALL CUSTOMERS. SH//COD 110// VER/DBM IDC XXXX
3389 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-02-23 06:37 | 2014-02-23 10:13 | 49 | 216 | 4427561 | 8136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SERVICER PATROLLING LINE. A PHASE HAS BURNED DOWN AT A SPLICE MID SPAN. NEED TWO MEN AND BUCKET TRUCK. OPENED DISC AT POLE 38821041B00010 TO ISOLATE TROUBLE. CLOSED RECLOSER BACK IN AT 07:49. CLOSED IN AT POLE 1041-B-10 AT 10:13. RELEASED BY CREW 079S02//COD 49// VER/DBM
3390 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-02-08 00:25 | 2009-02-08 08:25 | 20 | 480 | 56616-1 | 8136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3000902 SEND NOTE TO RAYBURN BAD LA ON POLE 1123-1575 ALSO POLE 1123-1578 VER/JHM IDC COMBINED WITH 56623-1 AND 56630-1 WENT BACK OUT AFTER CLOSEING, ALSO BAD INSULATOR AND CUTOUT XXXX L3/DKG
3391 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-02-28 08:34 | 2011-02-28 16:36 | 39 | 482 | 63788-1 | 8136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE # 978-191 BROKEN// ISOLATED AND GROUNDED ON POLE978-307//CLOSED FUSE ON 978-343 AT 11:40, REPORTING ALL EXCEPT ISOLATED CUSTOMERS// PAUL MUNCY WILL BE CHANGING POLE// RELEASED BY CREW 076H02 /// UPDATED FET @ 1547 DUE TO CREW REQUEST ////VER/CRB IDC CHANGED CAUSE FROM WIND XXXX
3392 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-03-31 16:30 | 2015-03-31 20:04 | 38 | 214 | 4248761 | 8132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECL @ 1630 BAD C/O BURNT POLE INTO WILL HAVE TO BE CHANGED OUT 40/4 POLE, C/O, ARRESTOR, BRKT, RUNNING CORNER AND BELL, CLEVIS AND SPOOL, JEFF STANDING BYBAD C/O BURNT POLE INTO WILL HAVE TO BE CHANGED OUT 40/4 AJBPOLE, C/O, ARRESTOR, BRKT, RUNNING CORNER AND BELL, CLEVIS AND SPOOL, JEFF STANDING BY. OPENED REC. AT 16:33 COD-38 ISO OCR 37830505000003 VER/HFP L3/HFP AJB
3393 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-05-05 19:38 | 2019-05-05 21:45 | 64 | 127 | 4228491 | 8128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | high side cutouts broken on step-down pole 194-336.. repairs made..restored @ 21:45/ 37820194C00264 L3/HFP
3394 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2017-12-24 04:37 | 2017-12-24 08:50 | 33 | 253 | 4671521 | 8125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A phase has burned down at pole 38820966D00662. Need two men with bucket truck and AWP to flag traffic. Opened line fuses at pole 38820966D00662 at 08:30, and closed back in at 08:50.
3395 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-06-13 13:14 | 2019-06-13 15:39 | 56 | 145 | 4495231 | 8120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DDC TAGS // DOL 930110 // loop burnt open on pole 162c36. opening line fuse on pole 38830162C00035 to make loop back up safely. will be hot up to pole 162c35 but will only be picking up wire once line fuse is open. tagged to ky ddc at pole 162c35. truck ok/arrived RM fuse in @15:39 please close tic RM Released by crew 078H20
3396 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2017-10-07 15:07 | 2017-10-07 21:00 | 23 | 353 | 4417711 | 8119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4418611/ RISER BURNT OFF AT BOTTOM OF LINE FUSE CUTOUT. WILL NEED TO OPEN TWO SWITCHES ON 38830954A40908 WHEN CREW GETS HERE. DIFFICULT LOCATION - CREW ENROUTE TO ASSIST. REPLACED CUTOUT AND RESTORED @ 21:00. SH/ ISO 38830954C20683/ COD 23/ VER/BOW ACB
3397 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-03-07 05:59 | 2022-03-07 17:59 | 59 | 720 | 4573171 | 8109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | got pole 124 71 burned off took clamp off to 70 and transformer , made recloser hot at 0756. talked to glen combs and he getting crew and material Released by crew 077S05
3398 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-12-26 18:40 | 2009-12-27 08:10 | 10 | 810 | 52632-1 | 8100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF BAD. JUMPERED TO ANOTHER TRANSF. POWER IS ON
3399 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-06-08 06:01 | 2019-06-08 09:05 | 44 | 184 | 4453661 | 8096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced bad transformer cutoutat pole 38820965A00245. Power restored at 09:05. L3/HFP
3400 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-11-13 06:33 | 2008-11-13 09:00 | 55 | 147 | 64340-1 | 8085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3410501 -WIRE DOWN IDC XXXX
3401 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-07-31 16:56 | 2022-08-03 12:15 | 2 | 4039 | 4644481 | 8078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout will need to climb Released by crew 078F03//replaced cut out kland
3402 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-04-04 15:43 | 2014-04-04 20:35 | 102 | 292 | 4574721 | 8069 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE 254-2001 BURNT OFF WITH TECH TRUCKS OK/BURNT 40/5 POLE END END WITH TRANSFORMER INSTALL/ISOLATED ON 254-338 /POLE 254C277 BACK IN AT 1700 HRS/POLE 254 338 TAGGED AND GROUNDED TO TACKETT RELEASED BY CREW 078S03,,,CREW ON SITE,, 1 CUSTOMER,,FINAL RESTORATION 20:35 /// NOTE: LAST CUST PRIMARY LINE (TAP) NOT ON MAP IN POWERON VER/HFP L3/HFP IDCC CNT101 XXXX
3403 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-02-01 11:43 | 2013-02-01 12:55 | 112 | 72 | H4778921 | 8064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WILL WORK IN THE AM DUE TO HAZARDOUS ROAD CONDITIONS. WE HAD TO OPEN RECLOSERS AT POLE 402-418 TO MAKE REPAIRS AT POLE 378-272 . OPEN AT 11:43 CLOSED AT 12:55 ///VER/CRB L/3 CRB IDCC CHANGED OFF TIME FROM 1143 FOR PH C ONLY CREATED H ORDER FOR OPENING PH A AND B XXXX
3404 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-03-29 00:26 | 2015-03-29 02:32 | 64 | 126 | 4240021 | 8064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GREG FUGATE REPORTS WIRE BROKE AT DEAD END ON POLE 37830273B00132, ROTTEN WIRE... POWER RESTORED. VER/SEF AJB
3405 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-03-01 18:15 | 2018-03-01 22:27 | 32 | 252 | 4895201 | 8064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Hot tap on line fuse burned off right again hendrix, Crew required. truck okay Released by crew 078H04/crew on site/FETR 2245/vem/repairs made and all cust restored 2227/please close ticket/thanks/vem //cod 32
3406 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-06-03 14:57 | 2017-06-03 15:42 | 179 | 45 | H4901521 | 8055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | (B) PHASE RECLOSER OPEN ON 38831125B00772. 43 CREW REQUIRED: 3 MAN LINE CREW, 30 FT #4 CU, TRUCK ACCESS. WIRE DOWN 38831124D00012. OPENED A&C RECLOSERS ON 1125-772 @ 14:57 (ADDITIONAL 179 CUSTOMERS). CLOSED ALL PHASES AT POLE 772 @ 15:42, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/AWD AJB
3407 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-02-26 13:16 | 2009-02-26 15:18 | 66 | 122 | 51749-1 | 8052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000801//REPLACED CUTOUT ON POLE 268-8. ALSO FOUND PRIMARY DOWN ON FUSE POLE 269-299 (THIS POLE SHOWS TO BE A SECONDARY POLE ON OUR MAPS, UNSURE IF POLE HAS WRONG TAG OR IF MAPS ARE WRONG... CLOSEST FUSE POLE IS -117) . PRIMARY IS HOT UP TO THIS POLE BE CAREFUL... THIS IS LOCATED AT 8820 US 60 WEST ABOUT ONE MILE BEFORE POPPY MTN. // LINE CREW NEEDED// COD 66//ISO 38830269A00117// VER/DBM IDC XXXX
3408 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-11-16 10:24 | 2008-11-16 16:00 | 27 | 336 | 65654-1 | 8042 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3116701// A PHASE UNDERGROUND PRI. OUT AGAIN POLE 1148-865 80T RELEASED BY CREW 078S08// CREW ON SITE LOOKING FOR WAY TO BACK FEED/ BAD CABLE FROM 20-442 TO 20 438 VER/KEP IDCC CDC83 XXXX
3409 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-04-05 13:43 | 2017-04-05 16:50 | 43 | 187 | 4617071 | 8041 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON POLE 674-251////FOUND BAD PIN INSULATOR ON POLE 674-349//REPAIRS MADE//RESTORED AT 16:50//COMPLETE//EM VER/CRB L3/HFP XXXHFP AJB
3410 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2015-10-30 10:03 | 2015-10-30 11:10 | 120 | 67 | 4396161 | 8040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | TIM HALL REPORTED BRACKET BROKEN ON REGULATOR BANK, WILL NEED TO OPEN RECL ON POLE 37820172000246 TO BYPASS REGULATORS AND SAFELY REPLACE/REPAIR BANK /// OPENED RECL @ 1003 CLOSED @ 1110 COD-120 WE EXPECT ABOUT A ONE HOUR OUTAGE./ ISO 37820172000246/ COD 120/ VER/BOW L3/HFP XXXHFP AJB
3411 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-08-13 17:38 | 2009-08-13 19:16 | 82 | 98 | 56626-1 | 8036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT ON POLE 355-21. VER/KEP L3/KEP IDC LOOKS LIKE PH B ONLY CHANGED COUNT FROM 156 XXXX
3412 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-07-07 05:16 | 2020-07-07 10:03 | 28 | 287 | 4120991 | 8036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | broken HT on 1123/6530---making repairs---made repairs on A Phase Hot tap--restored pwr on @ 10:03---checked meters all on--tbl tkt comp----rmv
3413 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-02-15 00:55 | 2015-02-15 05:42 | 28 | 287 | 4023741 | 8036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NOT RECEIVING ON SPECTRUM/POLE 518-38 FAILED CUTOUT BURNT OFF POLE/ NEED 2 MEN POLETOP EXT 7200 CUTOUT & BRACKETT/ VER/KEP L3/HFP XXX AJB
3414 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2019-09-26 08:12 | 2019-09-26 12:14 | 55 | 242 | 4059451 | 8030 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 PHASE OF HENDRIX CABLE BURNT IN CLEAR AT POLE 38820966B00600A ¦¦¦ WILL NEED CREW1 phase burnt in two at 966B600 at a splice.conductor is hanging in the clear.crew is en route.trk app.1 phase burnt in two at 966B600 at a splice.conductor is hanging in the clear.crew is en route.trk app. OPENED SW @ 1108 (30 CUST) CLOSED @ 1214
3415 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-02-13 08:36 | 2014-02-13 19:45 | 12 | 669 | 4379341 | 8028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 7.2 KV ARRESTOR BAD, CLEARED ARRESTOR, POWER RESTORED. - CAN CLOSE MWL VER/KEP
3416 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2013-08-28 22:02 | 2013-08-29 09:11 | 12 | 669 | 4717191 | 8028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 69/1244 BAD 50KVA TRUCK OK NEED CREW RELEASED BY CREW 078S08CHANGED BAD 7200 50KVA TRANSFORMER ALSO CHANGED CUTOUT VER/SEF IDC XXXX
3417 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2021-11-30 16:49 | 2021-11-30 20:45 | 34 | 236 | 4135841 | 8024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | on pole 1088A-6 the riser wire on B-phase line fuse has burned off at the hotline clamp. made repairs and got the line fuse on pole 1088A-6 back in 20:45
3418 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-05-06 06:30 | 2013-05-06 13:34 | 28 | 424 | 4075331 | 8022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O BURNT TOP POLE OFF HOT UP TO POLE 265/41 AT 1100AM LAST CUST. ON AT 1334 RELEASED BY CREW 077H04 COD-28 ISO LF 37830241000029 VER/HFP L3/HFP IDC XXXX
3419 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-01-11 18:08 | 2014-01-12 00:30 | 21 | 382 | 4273611 | 8022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON 38830979C00139// WILL REFUSE// BAD 100 KVA XFMR// WILL NEED CREW// XFMR CHANGED// POWER IS RESTORED VER/KEP L3/HFP IDC XXXX
3420 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-02-05 00:03 | 2010-02-05 11:11 | 12 | 668 | 63137-1 | 8016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | THIS IS A BAD LINE UP ON SIDE OF HILL, WAITING FOR DAYLIGHT TO PATROLL STS FOUND BAD INSULATOR ON POLE 1060-8 GOT CREW COMMING TO HELP CHANGE IT IDC XXXX
3421 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-01-11 09:50 | 2009-01-11 15:33 | 64 | 343 | 54213-1 | 8014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3420002//OPENED RECLOSER @ 0950 DUE TO POLE FIRE//COD 64// CAN GET MAIN LINE BACK ON AFTER WE CUT IN LINE DEAD-END. EST C HALL RD TO BE RESTORED AT 18:00 HRS// VER/DBM L3/KEP IDC XXXX
3422 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-04-25 05:41 | 2014-04-25 11:45 | 22 | 364 | 4631471 | 8008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED AT START TIME THIS AM. CUT ARRRESTER IN THE CLEAR ON POLE LOCATION_NUMBER 37830440000010 AND POLE 37830440000020 BOTH ARE MANUAL === BAD CUTOUT ON POLE 37830440000015 REPLACED CUTOUT === REFUSED LINE POWER OK//COD 22//AED ENTRY CREATED// VER/DBM AJB
3423 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2016-08-18 07:43 | 2016-08-18 13:31 | 23 | 348 | 4808941 | 8004 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T LF OPEN @ 66-112, GROUND PLACED TO R. VIRGIN@ 66-112 POLE TOP @ 66-147, BAD 12KV C/O, WINDSTREAM POLE RELEASED BY CREW 078S07---CREW ON SITE--ALL REPAIRS MADE--40T LF PL66-112 IN @ 13:31---TBL TKT COMP--RMV VER/AWD AJB
3424 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2018-08-07 14:41 | 2018-08-07 21:02 | 21 | 381 | 4919011 | 8001 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DOL 849482 //sdb / 1441 / Beaver Creek-Mckinney #1 46kV between Shepherd S.S. and Spring Fork locked out interrupting Spring Fork Station. 21 CC. Wire down at Shepherd sw. Crew enroute to make repairs. Released by crew 076S02//
3425 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2016-12-29 08:59 | 2016-12-29 17:52 | 15 | 533 | 4247881 | 7995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD RISER FUSE OPEN @152-B2-211, CHECKING. FAULT INDICATORS DETERMINED BAD SPAN OF URD PRIMARY BETWEEN JUNCTION BOX 24-A1-1292 AND TRANS. 24-A1-1296, I ISOLATED THIS SPAN AND CLOSED DIP FUSE BACK IN @ POLE 152-B2-211 @1204, 1 CUST. STILL WITH NO POWER, WILL HAVE TO HAVE A LINE CREW WITH FAULT FINDER. RELEASED BY CREW 074S05 VER/AWD
3426 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-07-17 15:46 | 2016-07-18 10:48 | 7 | 1142 | 4650321 | 7994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200. TRANSFORMER IS ACROSS THE CREEK AND IS POSSIBLY TRUCK APPROACH FROM THE ROAD. CUSTOMER WILL WAIT TILL DAYLIGHT FOR THE CREW TO REPLACE THE TRANSFORMER. SHE IS ELDERLY AND ASK TO WORK THIS ASAP. RELEASED BY CREW 079S02.. CHANGED TRANSFORMER AND CUT VINES OFF SECONDARIES..
3427 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-09-12 06:07 | 2022-09-12 19:26 | 10 | 799 | 4868231 | 7990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Wess Cupp enroute /pole 380-A-97 is burnt of right above the transformer.. cutout has broke down and caught pole on fire. top of pole is hanging on by wire and still smoking. dont know if pole top extension will work or if pole will need to be replaced. no truck access to pole Released by crew 077S11
3428 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-05-16 17:02 | 2020-05-17 01:54 | 15 | 532 | 4843161 | 7980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva pole 70-a2-612 going to make repairs FETR 2:30 LRM all pwr restored @ 1:54 please close ticket LRM/ ISO 38830070A20612/ COD 15
3429 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-06-04 10:15 | 2015-06-04 11:12 | 140 | 57 | H4509071 | 7980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE DOWN FROM POLE 37830091A00052 TO 51, OPENED B PHASE SWITCH AT 91A-56// CLOSE RECLOSER @ 0452 RESTORING 31CC// 37COD// 6 REMAIN OUTAGED UNTIL REPAIRS MADE//TOM . CREW REQUIRED: 2 MAN MANUAL ROW CREW, FLAGGERS, 3 MAN LINE CREW, 50 FT # 4 CU, TRUCK ACCESS . POLE 91-56 OPENED A AND C PHASES AT 10:15 . RESTORED ALL CUSTOMERS AT 11:12 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03// VER/ ADH L3/HFP HFPC CDC86 AJB
3430 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-10-08 16:45 | 2021-10-09 11:45 | 7 | 1140 | 4332351 | 7980 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | we have a phase out on the secondary that feeds customer, need A lineman with add a phase for a temp fix until tech can locate trouble// will have to open pad mount XFM 71-208 to safely install add a phase//opened pad mount 71-208@ 19:58 closed @ 20:42, add a phase did not work, Paul Layne will return in the morning to dig up ug Released by crew 074S09/UG sec replaced power restored at11:45
3431 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-04-22 20:54 | 2009-04-23 01:39 | 28 | 285 | 52227-1 | 7980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 29484366 //BAD 250 KVA STEPDOWN TRANSFORMER--SEND TO P TOLLIVERBAD 250 KVA STEPDOWN TRANSFORMER--SEND TO P TOLLIVER RELEASED BY CREW 078S07//REPLACED STEPDOWN POWER RESTORED AT 1:39 P R TOLLIVER/// VER/LDA IDCC CDC92 XXXX
3432 | Pikeville | 3403001 | PIKEVILLE | CITY | 2013-01-28 10:30 | 2013-01-28 14:00 | 38 | 210 | 4746301 | 7980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 25-B-419 // POLE HAS BURNT ALMOST IN TWO AT CUTOUT// OPENED-TAGGED RECS ON 25-391 TO MAKE SAFE//OPENED 10:30// TIM IS GETTING A CREW TO REPAIR ///VER/CRB L/3 CRB IDC XXXX
3433 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-02-07 19:14 | 2017-02-07 22:00 | 48 | 166 | 4369321 | 7968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | HIGH SIDE OF STEP DOWN @ POLE 37820073D00589, PATROLLING. FUSE PULLED INTO ON HIGH SIDE OF STEP DOWN, REFUSED @2200. 37820073D00589 COD 48 VER/AWD L3/HFP HFPC CCU CDC92 FEC57 FP AJB
3434 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2013-12-23 23:55 | 2013-12-24 00:39 | 181 | 44 | 4198121 | 7964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREATED ORDER TO MODEL OUTAGE NECESSARY TO ALLOW CREW TO CHANGE BAD C PHASE CUTOUT AT POLE 444-15, ON ORDER 4198041 C PHASE RECL AT POLE 419-D-72 OPEN AT 2355 181 CC CLOSED AT 1239 VER/PDP L3/HFP IDC XXXX BAD CUTOUT ON POLE 444-15, CREATED ORDER TO MODEL OUTAGE NECESSARY TO ALLOW CREW TO CHANGE BAD C PHASE CUTOUT AT POLE 444-15, ON ORDER 4198041 C PHASE RECL AT POLE 419-D-72 OPEN AT 2355 181 CC CLOSED AT 1239 BAD CUTOUT ON POLE 444-15, RELEASED BY CREW 077S11
3435 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-09-21 19:07 | 2020-09-21 20:56 | 73 | 109 | 4483971 | 7957 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | load side sturup burnt up--crew in route-ds092120 Released by crew 078S01 crewonsite FETR 21:15 LRM all pwr restored 20:56
3436 | Hazard | 3303901 | LESLIE | HYDEN | 2010-08-07 10:14 | 2010-08-07 10:55 | 194 | 41 | 50997-1 | 7954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREWS OPENED RECLOSER ON POLE 364-19 IN ORDER TO REPAIR BURNT LOOP ON POLE 364-12//COD 194// VER/DBM MLR
3437 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-07-01 11:15 | 2021-07-01 14:29 | 41 | 194 | 4834891 | 7954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed on 809-206. Crew enroute to assist. Found additional problem on fuse pole (Broken Insulator). Difficult location.//OPENED SW 38830784D00499 @ 1351Line fuse cutout failed on 809-206. Crew enroute to assist. Found additional problem on fuse pole (Broken Insulator). Difficult location. Closed sw 784-499 @ 14:29. sh Released by crew 076S02
3438 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-07-13 06:47 | 2012-07-13 18:50 | 11 | 723 | 4717141 | 7953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | POLE 525 - 85 LOOP OPEN, REPAIRED OFF @18:20 ON @ 18:50 IDC RESTORED SEVERAL TIMES IN PO AND MAYBE FIELD. I JUST SET TO THE EARLIEST CALL XXXX
3439 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-04-29 06:50 | 2008-04-29 11:15 | 30 | 265 | 55339-1 | 7950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403201//DEWEY AKERS WITH DHE FOUND A DOWNED LINE, POLE TOP BURNT OFF @ POLE 140-42//GREG JUSTICE ENROUTE//COD 30//CREW REQUIRED// REPAIRED POLE AND PUT UP CONDUCTOR. WILLIE ROBINSON// VER/DBM IDC XXXX
3440 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2022-07-21 11:14 | 2022-07-22 09:15 | 6 | 1321 | 4541991 | 7926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Ticket needs to be checked in daytime hours. Thick vegetation, inaccessible line, very difficult to see. GRF, BKR Released by crew 077E10
3441 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-08-18 17:59 | 2021-08-18 21:47 | 35 | 228 | 4112141 | 7922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolled line found nothing. ready to refuse and found the center phase cutout was burnt up because the gate hung in. will need to replace cutout before being made hot Released by crew 077S11
3442 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-10-08 08:52 | 2013-10-08 11:37 | 137 | 165 | H4920431 | 7911 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVENT FOUND PROBLEM YET, T. SMITH ON WAY TO ASSIST. FOUND WIRE DOWN AT POLE 183-45. WIRE IS STILL HOT IN TREES. WILL NEED TO OPEN RECLOSERS ON POLE 17. CAN OPEN LOOPS ON POLE 183-31 AND RE-ENERGIZE RECLOSERS RELEASED BY CREW 077S02 VER/CRB L/3 CRB IDCC DUP TO CUT LOOPS XXXX
3443 | Hazard | 3309301 | VICCO | REDFOX | 2021-01-12 15:35 | 2021-01-12 17:08 | 85 | 93 | 4864311 | 7905 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Randy Fields found broke crossarm brace arm is vertical with one phase off insulator // opening recloser on pole 37830301000019// OFF@15:35 , ON@17:08 p.hicks crew on site.
3444 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-09 09:58 | 2009-06-09 14:30 | 29 | 272 | 59463-1 | 7888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LOOKS LIKE BAD STEPDOWN XFORMER ON POLE 164-208. RELEASED BY CREW 078S01 VER/KEP L3/KEP MLR CDC 83
3445 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-08-24 03:44 | 2020-08-24 11:39 | 47 | 475 | 4362561 | 7881 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830165B00370 burnt off at c/o approx 16 above neu--d/e tran pole--isolated at 38830165B00242 --rec 38830165A00228 in at 06:25--crew req-ds082420/arrived RM power on @ 11:39 please close tic RM
3446 | South Williamson | 3411401 | DEWEY | INEZ | 2017-05-24 13:49 | 2017-05-25 01:45 | 11 | 716 | 4849181 | 7876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079S01//LINE FUSE BLOWN ON 744-165///FOUND BROKE CUTOUT ON POLE 721-51//REPLACED CUTOUT//RESTORED AT 01:45//COMPLETE//EM VER/ARN
3447 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-09-02 02:28 | 2012-09-02 12:15 | 66 | 587 | 4993591 | 7866 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC OPEN POLE 1098-88 CC 66, FAULT POLE 1098-813, LOOPS CUT POLE 1098-812, MP ---- SDB / 0357 / RECL AT POLE 88 CLOSED, REST 62 CC//NEED 3 MEN,TECH AND STOREROOM- 9-CUT OUTS POLETOP EXT , 8FT XARM AND BRACES AND 3 POSITION CUTOUT BRKT-3 ARM MT BRACKETS,3 ARRESTORS./INSTALLED 3-65T ON POLE 1098-812 POWER RESTORED AT 12:15 CLOSE TKT PRT// IDC XXXX
3448 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-03-08 20:51 | 2014-03-09 00:55 | 41 | 244 | 4462201 | 7863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GOT WIRE DOWN ON POLE38831109000058. I CANT FINE WHAT TOOK IT DOWN. GOT SOLID BLADE OPEN ON POLE38831109000021 AND GOING TO RECLOSER, CLOSED RECLOSER AT 2251 CLOSED FUSE ON POLE 1133-9 AT 0055 RELEASED BY CREW 077S05 VER/KEP IDC XXXX
3449 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-06-30 21:20 | 2015-07-01 01:42 | 30 | 262 | 4701061 | 7860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRIMARY CONDUCTOR OFF OF POLE TOP PIN ON POLE1085-12 NTA BUT I THINK I CAN REPAIR IT FUSE BLOWN BUT DIDNT DROP DOWN ON POLE 1061B14 - CLOSED @ 0140 AJB
3450 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2015-08-20 13:41 | 2015-08-20 15:30 | 115 | 109 | 4158281 | 7855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSSARM BURNT OFF DUE TO LINE FUSE CUTOUT FAILURE ON 954-492. OPENED 3 RECLOSERS ON 954-182 AT 14:07 TO ISOLATE. CLOSED RECLOSERS @ 14:30. CREW ENROUTE TO REPLACE CROSSARM AND 3 CUTOUTS. REPLACED ARM AND 3 CUTOUTS. RESTORED @ 15:30. SH RELEASED BY CREW 076S02 VER/HFP L3/HFP AJB
3451 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-07-25 12:45 | 2020-07-25 14:58 | 59 | 133 | 4231371 | 7847 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1098-343 open & tagged to B. Ramey/ #4sol primary down from 1098-304 to 1098-305/ GROUNDS also placed @ these locations/ crew enroute/ Released by crew 078H08///repairs made///LF closed at 14:58///complete BR
3452 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2019-04-03 11:28 | 2019-04-03 12:56 | 103 | 88 | 4053671 | 7832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Phase B fuse is open at pole 38820917C00383. Patrollng line.//COD 18 FROM BEGINNING OF OUTAGE//B PHASE L/F IS BAD//OPENING A & C PHASES// Replaced phase B cutout. I opened the A & C phase at 12:45. L3/HFP sjg
3453 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-11-01 06:28 | 2016-11-01 09:54 | 38 | 206 | 4066841 | 7828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP AND STIRRUP BURNED OFF, CREW IS COMMING TO REPLACE RELEASED BY CREW 077S12 VER/AWD /// PER VOICE REC RIGHT HAND PHASE OUT WITH BACK TO STATION = C PHASE PER POR = L3/HFP XXXHFP AJB
3454 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-02-27 15:53 | 2016-02-27 17:18 | 92 | 85 | 4782571 | 7820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NETUTRAL AND BUSTEDCUTOUT FAILED ON POLE 220-26/OPEN REC. AT 15:53 AND CLOSE AT 17:18// VER/ ADH AJB
3455 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2011-02-13 16:38 | 2011-02-13 19:44 | 42 | 186 | 56598-1 | 7812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CREW COD-42 "C" PHASE ONLY TILL SWITCHES ARE OPENED CALLED CREW--556 LOOP BURNT OPEN ON C PHASE ** UPDATE AT 1830 , CREWS ARE LOGGING ON CKT NOW AND WILL MAKE THE REPAIRS TO THE OPEN LOOP AS ENERGIZED //VER/GAH IDC XXXX
3456 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-06-26 17:18 | 2008-06-26 23:30 | 21 | 372 | 55039-1 | 7812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED CUTOUT REFUSED 25 AMP FUSE VER/HFP IDC XXXX
3457 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-12-29 09:15 | 2014-12-29 13:27 | 31 | 252 | 4889111 | 7812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING RECLOSER 207-C4-327, TO SAFELY MAKE REPAIRS TO POLE FIRE//I OPENED RECLOSER AT POLE NO. 207C4-327 AT 09:15. WE NEED A 45C4 POLE, CUTOUT AND ARRESTOR, 25 KVA7200V. XFMR, AND A LINE CREW WITH A BIG BUCKET RELEASED BY CREW 077S12// COD 31/ ON @ 1327// VER/ ADH AJB
3458 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2015-06-08 15:22 | 2015-06-08 19:26 | 32 | 244 | 4528321 | 7808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RISER BURNED OFF TRANSFORMER ON POLE 47C-221 5 CUSTS AFFECTED HAVE TO CLIMB POLE.C DESKINS RELEASED BY CREW 079F03/ WILL HAVE TO OPEN LINE FUE ON POLE 47-C-206 WILL CALL BACK BEFORE OUTAGING/ VER/CRB AJB
3459 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-10-17 18:59 | 2015-10-17 20:00 | 128 | 61 | HA4357231 | 7808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 HEDRIX BURNED APART AT SPACER, TRUCK ACCESS//COD 55 FROM START A PHASE //OPENED SOLID BLADES ON POLE 38831074D00062 @ 1901 //OPENED RECLOSER38831074D00032 @ 1859//CLOSED IN SOLID BLADES @ 1955 PICKING UP 22 COD//CLOSED RECLOSER PICKING UP REMAINING CUSTS @ 2000//1/0 HEDRIX BURNED APART AT SPACER, TRUCK ACCESS. ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/CRB AJB
3460 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-07-06 07:31 | 2012-07-06 11:40 | 55 | 249 | 4530321 | 7807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE HOT TO 247-914 @ 9:22 MODELED MWL MADE HOT TO FUSE ON POLE 271-571 @ 10:00 (NO FUSE ON MAP NEEDS MD --- 15T PLACED AT POLE 271-571) BAD CUTOUT AT 271-638 MWL ---- REPLACED 2 BAD CUTOUTS ON POLE 271-571, REPLACED 1 BAD CUTOUT ON POLE 271-638, ALL POWER RESTORED AT 11: 40 CAN CLOSE TICKET MWL IDC XXXX
3461 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-01-12 08:15 | 2016-01-12 11:58 | 35 | 223 | 4608661 | 7805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BURNT OFF ON POLE 235-38. NEED LINE CREW NO TRUCKS TO POLE RELEASED BY CREW 078S01---NO ACCESS TO POLE--HAVE TO WALK---NEED TO REPLACE HOTTAP---OPEN LF 235-68---FOR LOAD REMOVAL TO RE-INSTALL H.T.--REPAIRED H.T.---CLOSED LF @ 235-68 @ 11:58----TBL TKT COMP,,,RMV// VER/ ADH AJBC LCD
3462 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-07-19 20:20 | 2012-07-20 10:47 | 9 | 867 | 4778571 | 7803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 100 KVA IS BAD 7200 PRI/ 120/240 SECONDARY NEED XFMR, 2 MEN & MATERIAL HANDLER RELEASED BY CREW 074S04// CREW ON SITE STARTING REPAIRS TCM// COD-9 ISO TF 38830979D00030 VER/HFP L3/HFP IDC XXXX
3463 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-04-03 09:27 | 2009-04-03 12:00 | 51 | 153 | 64514-1 | 7803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401//SERVICER KENNY NAPIER OPNED FUSE DUE TO POLE FIRE (REPORTED IN ORDER 64481-1)//POLE NEEDS CREW TO REPLACE//CREW ENROUTE//COD 51// VER/DBM IDC XXXX
3464 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-04-22 16:27 | 2016-04-22 22:57 | 20 | 390 | 4116691 | 7800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079H03 FAILED CUTOUT ON 1137D307 I REPLACED CUTOUT AND STANDOFF BRACKET RESTORED POWER 22:57 VER/AWD AJB
3465 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-03-09 09:07 | 2011-03-09 14:07 | 26 | 300 | 52007-1 | 7800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE AT 09:07 INSTALLED GROUNDS ON POLE 90-40--DAVIS CREW TO REPLACE POLE-NEED TO GO BACK WITH 45CL4 POLE--NEED BUCKET TREE CREW--ALL BESIDE DEADEND RD RELEASED BY CREW 078S07 VER/KEP IDC XXXX
3466 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-05-26 15:59 | 2009-05-26 17:14 | 104 | 75 | 52302-1 | 7800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP STS WR# 29980737//ISO 39830902A00020//COD 97//RELEASED BY CREW 078S06 L3/HFP IDC XXXX
3467 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-01-29 16:45 | 2008-01-29 18:25 | 78 | 100 | 60749-1 | 7800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601// LOOKS LIKE STEPDOWN OUT @ POLE 38830092B00187 COD 86//B AN C PHASE LOAD SIDE FUSES BLOWN/PATROLING LINEB AN C PHASE LOAD SIDE FUSES BLOWN/PATROLING LINE/ B-PHASE CUTOUT BAD//CALLED DRT TO HELP/ OPENED A PHASE AT 18:06/PATROLING LINE//CALLED DRT TO HELP/ / REPLACED 2 CUTOUTS ON TRANSFORMER BANK/ A AN B PHASE IDC XXXX
3468 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-06-13 19:01 | 2012-06-13 22:50 | 34 | 229 | 4913331 | 7786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | PATROLLING//FOUND BAD RECLOSER TAGGED TO DDC AND REMOVED SOURCE AND LOAD SIDE LEADS INSTALLED 3-40T FUSES SEND TO ENG. TO REPLACE RECLOSER, PLEASE CLOSE TKT PRT //VER/GAH IDC XXXX
3469 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-03-30 04:47 | 2020-03-30 05:59 | 108 | 72 | 4541441 | 7776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Opened recloser at 38830292C20402 to safely make repairs to failed equipment.
3470 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-06-24 20:32 | 2016-06-25 03:44 | 18 | 432 | 4468001 | 7776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FUSE BLOWN AT POLE 560-30 #2 AL PRIMARY DOWN AT POLE 560 -19 BURNED INTO AT HOT LINE CLAMP NOT TRUCK ACCESSIBLE RELEASED BY CREW 077E02 VER/CRB
3471 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2021-12-06 16:26 | 2021-12-06 19:56 | 37 | 210 | 4155571 | 7770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Primary loop burnt into on pole 147-100 will need line crew
3472 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-04-02 17:13 | 2016-04-02 18:02 | 159 | 49 | 4017961 | 7764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE BYPASS HAS FAILED AND BURNED THROUGH THE CROSSARMS. WILL NEED TWO TEN FOOT ARMS WITH BRACES, THREE 19.9 CUTOUTS WITH ARM BRACKETS, SIX 19.9 DEADEND INSULATORS. THIS WILL REQUIRE AN OUTAGE TO MAKE REPAIRS. TWO BUCKET TRUCKS CAN WORK THIS TO SHORTEN THE OUTAGE TIME. //OPENED SWITCH @ 1713//CLOSED SWITCH @1759 UPTO SECT//1802 CLOSED SECT IN P/U ALL REMAINING CUSTA PHASE BYPASS HAS FAILED AND BURNED THROUGH THE CROSSARMS. WILL NEED TWO TEN FOOT ARMS WITH BRACES, // TIMES PER VOICE REC = VER/HFP L3/HFP
3473 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-04-25 13:24 | 2013-04-25 15:40 | 57 | 136 | 4047491 | 7752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | /C PHASE(COD-57) RECLOSER OUT DUE TO HOT LINE CLAMP BURNT THROUGH STIRRUP ON SOURCE SIDE OF RECLOSER. 1 MAN AND BUCKET ON THE WAY./C PHASE RECLOSER OUT DUE TO HOT LINE CLAMP BURNT THROUGH STIRRUP ON SOURCE SIDE OF RECLOSER. 1 MAN AND BUCKET ON THE WAY. REPAIRS MADE RECLOSER IN. AT 15:40 EVERYTHING OK VER/KEP IDC XXXX
3474 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2008-11-24 17:55 | 2008-11-25 01:17 | 47 | 442 | 51729-1 | 7750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000302//POLE BURNT OFFPOLE BURNT OFF 20-1049//@ 1925 CLOSED N.O. SWITCH 20-1028 AND BACK-FED UP TO ISOLATING PT 20-1041//THIS RESTORED 37 OF THE 47 CUSTOMERS//10 CUST REMAINING OUT//STS W/R 27426664// CALLED FOR TREE CREW PRIMARY LAYING IN TREES IN 3 OF 4 DEAD END SPANS/ @23:57 TRIMMERS STILL HAVE 1 SPAN TO CUT R/W VERY BAD SHAPE/ STARTING TO SWITCH LINE BACK @ 12:58 VER/JHM MLR STEPS OF RESTORAION IDC XXXX
3475 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-08-17 17:50 | 2011-08-17 18:15 | 310 | 25 | 4721611 | 7750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW REPAIRING BROKE CROSS ARM DKG... 165-A-267, 164-B-275 (OPENING THIS OUTAGED CUSTOMERS), 164-B4-3641 .... VER/DKG IDCC CDC98 XXXX
3476 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2010-09-18 11:39 | 2010-09-20 12:05 | 48 | 2906 | 51191-1 | 7747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#36940341//OPENED SWITCH 1148-504 ISOLATING FAULT POLE 1148-978 (POLE BURNT OFF DUE TO BAD CUTOUT) /THEN 1322 CLOSED SWITCH 20-1028 IN PICKING UP 47 CUST FROM THE BELLEFONTE/BELLEFONTE CIRCUIT RELEASED BY CREW 078S08 // ONLY CUSTOMERS OUT IS SOCCER FIELD //PUT FIRE OUT WILL WORK MONDAY 9/18 P R TOLLIVER//CREW ON SITE PR TOLLIVER 9/20/10// 1205 - CLOSED 1148-504 (RESTORE 1 CUST) //1230 - OPENED 20-1028 (48 CUST INTPT) 1245 - CLOSED 1148-2028 (RESTORE 48 CUST) //VER/GAH IDC XXXX
3477 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-09-25 02:47 | 2022-09-25 15:15 | 19 | 748 | 4918101 | 7746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG riser fuse open on 1127-B-232// checking// bad UG cable need line crew with high pot sticks to locate trouble// fault is in cable from pad mount 1127-B-359 to 360, isolated trouble and restored 1127-B-359 @ 11:09// 1127-B-360 res @ 15:15 Released by crew 074S09
3478 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2022-12-24 04:27 | 2022-12-24 05:55 | 88 | 88 | 4338751 | 7744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | center phase line fuse on pole 917C-383 is melted out .i got fuse back in at 05:55---Based on calls looks to be A phase fuse???
3479 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-05-15 22:57 | 2020-05-16 00:10 | 106 | 73 | 4840661 | 7738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | recl out on 697-C4-113.cutout failed on 697-C-24.replaced cutout restored power at 00:10/ ISO 38820697C40113/ COD 106
3480 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2008-12-08 08:14 | 2008-12-08 10:13 | 65 | 119 | 55358-1 | 7735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3200201// CONTROL CABLE 120 VOLT LEAD WAS BURNED INTO, MADE REPAIRS AND PUT RECLOSER BACK ON LINE.//COD 65// VER/DBM L3/KEP IDC XXXX
3481 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-03-29 12:09 | 2009-03-29 14:08 | 65 | 119 | 62674-1 | 7735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP COD-65 WR # 29128272 // FOUND LOOP BURNTED OPEN ON POLE 1071-28, HAVE REPAIRS MADE AND POWER SHOULD BE RESTORED TO THIS CUST L3/HFP IDCC PN285 XXXX
3482 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2019-02-20 11:08 | 2019-02-20 12:40 | 84 | 92 | 4814971 | 7728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | load transfer and outage to safely replace insulators at pole 3783-0272-B3-0491
3483 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-10-01 11:00 | 2014-10-01 12:15 | 103 | 75 | 4541481 | 7725 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | DE-ENERGIZED LINE DUE TO 46KV TRANSMISSION LINE CROSSING 12KV LINE . OPENED @ 1100 CLOSED @ 1215 VER/HFP L3/HFP AJB
3484 | Hazard | 3310502 | HADDIX | CANOE | 2013-08-07 10:51 | 2013-08-07 18:00 | 18 | 429 | 4631621 | 7722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLING LINE--BAD EPOLX INSL---HELP COMING--FETR 1830--REPLACED 4 INSULATORS CUT TREES---ON AT 1800 IDC XXXX
3485 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-06-14 14:59 | 2009-06-14 20:50 | 22 | 351 | 62988-1 | 7722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3402202 LINE DOWN BETWEEN POLE#18-54 AND 18-345 //PHASE A OUT ONLY//COD 22 //OPENED SWITCH 180-54 @ 1654, INTERRUPTING 11 MORE CUSTOMERS//WIRE BACK UP SOLID BLADE CLOSED IN, ALL CUST RESTORED @ 2050//NO TREES INVOLVED... CONDUCTOR APPEARS TO HAVE FAILED//ISO 37830018000054 MLR CREATED DUP FOR OPENING OF ADDITIONAL PHASES
3486 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-01-02 00:17 | 2018-01-02 07:07 | 33 | 410 | 4694131 | 7713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire is down at 37830129A00078, isolated trouble at 37830129A00037. closed recloser 37830129B00017 at 02:30 hrs. opened recloser 37830129B00017 back up at at 07:03 to put clamp back on, closed back in at 07:07. all power restored
3487 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-05-07 16:35 | 2012-05-07 18:30 | 67 | 115 | 4756391 | 7705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT 50T COD-67 ISO LF 39831123D47503 VER/HFP L3/HFP IDC XXXX
3488 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-11-10 15:40 | 2020-11-10 18:35 | 44 | 175 | 4658291 | 7700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout on pole 38830045C45732 failed and burnt an 8ft crossarm into // made repairs and restored @ 1835
3489 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-16 18:52 | 2008-06-17 13:10 | 7 | 1098 | 66150-1 | 7686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 174-429, BROKEN CUTOUT, NEED BIG BUCKET. BE CAREFUL GOING UP HILL , SOMEONE WILL HAVE VTO HOLD WIRES UP TO GET UNDER THEM RELEASED BY CREW 077S08 REPLACED CUTOUT AND ARRESTER JKC // VER/TOM IDC XXXX
3490 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-02-06 11:12 | 2013-02-06 11:24 | 640 | 12 | 4794611 | 7680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | SERVICER TO BE DISPATCHED AT REG WORK TIME 0730. STS TWO HOLE PAD ON GOAB SWITCH IS HEATING UP ON POLE 29-6 ON MIDDLE PHASE ON LOAD SIDE OF SWITCH, NEED TWO HOLE PAD FOR 4 / 0 PRIMARY AND TWO FOOT OF 4 / 0 ACSR WIRE RELEASED BY CREW 077S05//OPENED REC AT 1112SERVICER TO BE DISPATCHED AT REG WORK TIME 0730. STS TWO HOLE PAD ON GOAB SWITCH IS HEATING UP ON POLE 29-6 ON MIDDLE PHASE ON LOAD SIDE OF SWITCH, NEED TWO ///VER/CRB L/3 CRB IDC XXXX
3491 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-02-19 08:01 | 2013-02-19 13:50 | 22 | 349 | 4828831 | 7678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT OUT OF THE BOTTOM OF CUTOUT. A PHASE OUT ONLY. POLE 18-54. MADE REPAIRS EVERYTHING OK. IDC CHANGED TIME OFF FROM 0613 PER CALLS XXXX
3492 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-02-25 04:16 | 2018-02-25 09:00 | 27 | 284 | 4880501 | 7668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got cutout on pole 37830172D00169 bad need two man and 7200 cutout Released by crew 077S05//
3493 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-02-24 21:28 | 2022-02-25 02:25 | 35 | 297 | 4542061 | 7665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on 146-268 will patrol///Bad cutout on pole145-257 burnt top of pole off///Can lower///Cut in line deadend between poles 145-35 and 145-99 to isolate fault///will be making repairs///Lowered primary and changed bad cutout restored remaining customers @02:25 Released by crew 074S02
3494 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-05-17 06:57 | 2016-05-17 10:24 | 37 | 207 | 4224581 | 7659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOWSIDE STEPDOWN F IS OUT,WILL PTRL////////WIRE INTO AT 31-49,NEED SMALL CREW,#2,BUCKET ACCESSABLE////////REPAIRS COMPLETED,WILL RE-FUSE//////////RE-FUSED AND RESTORED VER/AWD /// VER PER VOICE RECORDER FAULT POLE REPORTED BY FIELD IS INCORRECT SHOULD BE 37830310000049 == L3/HFP HFPC FP37830031000049 AJB
3495 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2016-06-21 20:04 | 2016-06-21 22:40 | 49 | 156 | 4401871 | 7644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD BURNT OFF SOLID BLADE ON RECLOSER POLE 184-266, ALL POWER RESTORED VER/AWD AJB
3496 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-08-12 06:30 | 2009-08-12 06:58 | 273 | 28 | H60012-1 | 7644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE IS DOWN AND HAS BROKE IN THE CLEAR RECLOSERS ARE IN AT THIS TIME I HAVE HELP COMING WE WILL OPEN RECLOSERS WHEN WE PUT WIRE BACK UP AT 0630 CREW HAS OPEN B PHASE IS DOWN AND HAS BROKE IN THE CLEAR RECLOSERS ARE IN AT THIS TIME I HAVE HELP COMING WE WILL OPEN RECLOSERS WHEN WE PUT WIRE BACK UP WE OPENED RECLOSERS AT 0618 AND CLOSED BACK AT 0658// IDC XXXX
3497 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-12-01 18:16 | 2009-12-01 19:40 | 91 | 84 | 54601-1 | 7644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSERS FOR CREW TO SAFELY MAKE REPAIRS // SEE ORDER 54320-1 RELEASED BY CREW 077S02//COD 91// VER/DBMDC XXXX
3498 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-08-31 04:33 | 2021-08-31 16:42 | 15 | 729 | 4182691 | 7638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | pole 38831037000037 top has burned off , recloser 1037-71 got disc sw open and tag for greg shouse got recloser 1061-224 in at 0851 Released by crew 077S05 ETR 17:00. Power restored at 16:42.
3499 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-08-15 20:35 | 2016-08-15 20:58 | 332 | 23 | H4780561 | 7636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 45-3638 HOT TAP & BASKET BURN UP ON LINE FUSE ON HENDRIX ACROSS FROM 1917 BLACKBURN AVE ACROSS FROM HIGHLAWN AVE. FLAGGERS , LINE CREW NEEDED TR. OK RELEASED BY CREW 078S04, OPEN RECLOSER 45-2609 TO MAKE REPAIRS.DEENERGIZED AT 20:35. POWER RESTORED AT 20:58 DUP OF 4780561 FOR REC OUTAGE VER/HFP L3/HFP AJB
3500 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-11-22 20:06 | 2020-11-22 23:23 | 221 | 197 | 4715861 | 7633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | conn 38830018000015/opened recl on 38830018000011
3501 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2017-10-11 14:03 | 2017-10-11 14:20 | 721 | 17 | 4447091 | 7631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED CB VIA SCADA @ 1403 - 720 CUST // BASKET FAILED ON PRIMARY METERING AND NEEDED EMERGENCY OUTAGE TO REPAIR RELATED TO 4446841/ 3010602 CLOSED @ 1411 (RESORT 514)/ 39831124B38178 CLOSED @ 1420 (RESTOR 207)/ VER/BOW /// TIMES PER SCADA = L3/HFP XXXHFP ACB
3502 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-07-28 00:19 | 2014-07-28 03:25 | 41 | 186 | 4298111 | 7626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD LIGHTING ARRESTER ON POLE 1109-74 CUT IN CLEAR//COD 41//AED ENTRY CREATED FOR BLOWN ARRESTER// VER/DBM AJB
3503 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-03-27 03:59 | 2013-03-27 07:50 | 33 | 231 | 4960931 | 7623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND ONE PHASE HENDRIX BURNT IN CLEAR// CREW TO MAKE REPAIRS// 556 CONDUCTOR IS BURNED DOWN BEHIND SOUTH SIDE MALL. WHEN READY TO MAKE REPAIRS WE WILL NEED TO OPEN AT POLE 966-629. & TAG FOR EDDIE MATNEY556 CONDUCTOR IS BURNED DOWN BEHIND SOUTH SIDE MALL. WHEN READY TO MAKE REPAIRS WE WILL NEED TO OPEN AT POLE 966-629...OPENED LINE AT 06:55..NOT ON MAP ..CLOSED BACK IN AT 07:50. VER/PDP IDCC CNT63, TOF0655 XXXX
3504 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-07-06 06:58 | 2018-07-06 09:05 | 60 | 127 | 4735331 | 7620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 076S01// fuse out on pole 809-514 // changing bad arrester on 809-1081 // changing bad cutout on 809-518// repairs complete, restored at 09:05
3505 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-08-25 11:02 | 2016-08-25 12:10 | 112 | 68 | 4834811 | 7616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE BROKE ON CREW -- OPENED B PHASE RECL 122 CUST TO ISOLATE PHASE THAT IS DOWN OPENED @ 1106 CLOSED @ 1210 (112 CUST INTERRUPTED WHEN # 4 CU PHASE BROKE & 10 INTERUPTED WHEN RECL OPENED) DUP IN HOIS FOR 10 SEE H4834811 FOR RECL OUTAGE VER/HFP L3/HFP AJB
3506 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-08-20 12:03 | 2010-08-20 16:45 | 27 | 282 | 58674-1 | 7614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON 1110-D-37.....PATROLLED LINE....ALL LOOKS OK..RE-FUSED...CAME BACK OUT...PATROLLING AGAIN...BAD PIN INSULATOR ON POLE 1110-D-65....CALLED CREW....THEY ARE ENROUTE...//...FINALLY FOUND PROBLEM....BAD ARRESTER ON 1110-D-40....CUT IN CLEAR...RE-FUSED....POWER ON....JRV...08/20/10//VER/CRB IDC XXXX
3507 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-12-21 06:14 | 2012-12-21 12:00 | 22 | 346 | 4497301 | 7612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND HOT TAP BURNTED OFF BASKET, I REPLACED HOT WITH A LINE FUSE, INSTALLED A 40T FUSE ON POLE 1072-5504, NEED TO SEND TO MAPPING TO SHOW THIS FUSE INSTALLED ON THIS POLE//MADE MDC ////VER/CRB L/3 CRB
3508 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-02-05 09:12 | 2010-02-05 13:10 | 64 | 238 | 63289-1 | 7609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37820049000075 REC. OPEN ---- TOP OF POLE BURNED OFF ON POLE 37820050000096--I HAVE A HOT TAP LIFTED ON POLE 37820050000050 WILL NEED A CREW TO REPLACE WILL CONTACT T. HALL//VER/CRB IDC XXXX
3509 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-12-21 15:24 | 2008-12-22 00:48 | 50 | 564 | 61572-1 | 7608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27766703 /// FAULT POLE 38831032000065 - ISOLATED ON 38831032000040// NEED 40` 5 POLE & 25KVA 7.2KV TRANSFORMER & DEADEND POLE ASSEMBLY MATERIALS.. L3/HFP IDC XXXX
3510 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2013-01-28 06:25 | 2013-01-28 09:50 | 37 | 205 | 4745351 | 7585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOW SIDE FUSE ON STEP DOWN BLOWN//PATROLING//BROKE CUTOUT ON POLE796-113//JOEY BRINGING CREW AND BIG BUCKET TO CHANGE OUT//REPAIRS MADE RESTORED AT 09:50//COMPLETE//EM ///VER/CRB L/3 CRB IDC XXXX
3511 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-08-13 16:10 | 2011-08-13 19:15 | 41 | 185 | 4703451 | 7585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CONDUCTOR FELL OFF INSULATOR. OPEN OTHER 2 PHASES AT 19:00//COD 96// IDCC CNT96 XXXX
3512 | Hazard | 3303901 | LESLIE | HYDEN | 2014-09-22 12:15 | 2014-09-22 14:53 | 48 | 158 | 4519151 | 7584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW OPENED TO MAKE REPAIRS ON LINEMADE REPAIRS ON DAMAGED INSULATORS ON POLE 387-13 VER/KEP AJB
3513 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-02-18 17:31 | 2009-02-18 17:43 | 632 | 12 | 64555-1 | 7584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TIM MILLER OPENED RECLOSERS TO SAFELY MAKE REPAIRS ON LINE SEE ORDER 64213-1//COD 628// VER/DBM IDC XXXX
3514 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2020-11-01 18:04 | 2020-11-02 01:25 | 22 | 441 | 4621981 | 7583 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | DOL 1066051 // wire pulled loose from sleeve at pole 38831140A00019 // cod 22 //Released by crew 076S03/// Breaker open// Sleeve pulled out and has 1 span of #4cu primary down @ pole 1140-A-19. Opened switch on 1140-C-3 to isolate trbl and closed Breaker @20:36. Have extra servicer and ROW crew onsite to assist with repairs///Released by crew 076S03/// Breaker open// Sleeve pulled out and has 1 span of #4cu primary down @ pole 1140-A-19. Opened switch on 1140-C-3 to isolate trbl and closed Breaker//
3515 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-04-25 00:28 | 2010-04-25 16:23 | 54 | 955 | 50488-1 | 7580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34818413 //.. BURNED DEADEND POLE # 1072-209.. LIFTED HOT TAP ON 1072-58 WILL HAVE ONE CUSTOMER OFF WHEN CLOSING FUSE ON 1048-6... NEED LINE CREW MAYBE BETTER TO WAIT UNTIL MORNING CUST HAS AREA FENCED OFF CANT GET TRUCKS TO POLE .. NEED TECHNICIAN TO CHECK ABOUT RELOCATING POLE INTO FIELD .. 3000701//.. LIFTED HOT TAP ON POLE 1072-58 ONLY WILL HAVE ONE CUSTOMER OFF WHEN CLOSING FUSE ON POLE 10 //VER/GAH IDC XXXX
3516 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2018-09-27 16:13 | 2018-09-27 17:20 | 113 | 67 | 4167211 | 7571 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | open reclosure on poles 1047-142 and 1047 -141 @ 16:13 closed @ 1720
3517 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-04-20 09:29 | 2021-04-20 12:25 | 43 | 176 | 4463671 | 7568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LF open 67/20--6A Primary down at same location--sleeve failed--crossing rte 5---need Line & Flag crew--LF open on 67/112 needs re-installed--bad places in Primary where crosses serv drop to 1st. house--assign to B Ramey--NO T&Gs placed Released by crew 078H16///Complete BR
3518 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-04-17 04:58 | 2013-04-17 13:22 | 15 | 504 | 4016911 | 7560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD ON LINE FUSE POLE, THERE IS TWO CUTOUTS ON THIS POLE THAT NEEDS TO BE CHANGED , I WILL NEED HELP RELEASED BY CREW 077S12 PULLED 2ND TAP OFF AT 1300 BOTH ON AT1322 RELEASED BY CREW 075H01 VER/KEP IDC XXXX
3519 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-02-19 02:00 | 2013-02-19 09:00 | 18 | 420 | 4828451 | 7560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 38831133000047 POWER RESTORED AT 38831133000040 AT 0900 ///VER/CRB L/3 CRB IDC ORIGINAL CUSTOMER NOT OUT BUT NEXT TO FUSE THAT WAS BLOWN XXXX
3520 | Paintsville | 3401802 | INDEX | HOSPITAL | 2013-10-04 10:07 | 2013-10-04 11:55 | 70 | 108 | 4909881 | 7560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLING LINE. PORCELIN ARRESTER BLEW AND BOTTOM RISER CONTACTED XFMR CUTOUT ON 654-614. CLEARED FAULT AND RESTORED @ 11:55. SH VER/SEF L3/HFP IDC XXXX
3521 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-01-18 13:40 | 2011-01-18 13:50 | 756 | 10 | 62279-1 | 7560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 1350 HOT VER/HFP L3/HFP IDC XXXX
3522 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-02-23 21:48 | 2019-02-24 10:23 | 10 | 755 | 4851321 | 7550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | \\Broke cutout @ 573-80, 19.9 no trucks. crew required, Linecrew will need to take larger outage in order to isolate cutout. Released by crew 078S11Broke cutout @ 573-80, 19.9 no trucks. crew required, Linecrew will need to take larger outage in order to isolate cutout. Released by crew 078S11--crew on site---repaired bad cutout--restored pwr @ 10:23---tbl tkt comp---rmv
3523 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-09-28 10:37 | 2012-09-28 13:05 | 51 | 148 | 4095451 | 7548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 331-27. ///VER/CRB L/3 CRB IDC XXXX
3524 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-08-14 22:18 | 2021-08-14 23:40 | 92 | 82 | 4067491 | 7544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | copper sleeve pulled out at recloser. opened recloser at 2310, made repirs, closed recloser at 2340
3525 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2013-10-08 04:14 | 2013-10-08 11:37 | 17 | 443 | 4920431 | 7531 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVENT FOUND PROBLEM YET, T. SMITH ON WAY TO ASSIST. FOUND WIRE DOWN AT POLE 183-45. WIRE IS STILL HOT IN TREES. WILL NEED TO OPEN RECLOSERS ON POLE 17. CAN OPEN LOOPS ON POLE 183-31 AND RE-ENERGIZE RECLOSERS RELEASED BY CREW 077S02 VER/CRB L/3 CRB IDCC CNT152, CDC86 XXXX
3526 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2009-11-27 06:18 | 2009-11-27 10:23 | 198 | 245 | 66156-1 | 7526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002105// FP 45-5075 WR / 32848917 BAD CUTOUT POLE FIRE NEED CROSSARM 3- CUTOUTS AND 1-1301 INS. RELEASED BY CREW 078S08---CREW ON SITE,WILL CHANGE BAD CO AND REPAIR CONDUCTOR CB OPEN FROM 0618-0621 CC 567 SWS AT POLE 45-407 OPEN VER/PDP 0621 CB CL. 369 CC REST. SWS ON POLE 45-4057 & 5074- OPEN. N.O. SW ON POLE 45-5115 CL 198 CC REST. AT 1023 SWS 4057 & 4074 CL ALL CUST REST. VER/PDP IDC XXXX
3527 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-08-20 20:28 | 2018-08-21 02:10 | 22 | 342 | 4978851 | 7524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | One fuse out on pole. Bad 167kva transformer, 7200. Trucks to pole/Part out until 2135/ One fuse out on pole. Bad 167kva transformer, 7200. Trucks to pole Released by crew 078H04 L3/HFP
3528 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2013-06-09 18:44 | 2013-06-09 21:52 | 40 | 188 | 4244281 | 7520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 6 INCH DISK. HAVE T.HALL IN ROUT WITH INSULATOR.PLEASE SEND A NOTE TO R/W TO HAVE ALL OF TRIMBLE BR. CUT . IT IS IN BAD SHAPE. THANKS G.R. //VER/GAH IDC XXXX
3529 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-10-28 14:41 | 2012-10-29 01:15 | 90 | 634 | 4178751 | 7516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE FIRE POLE 174-163 40/5 DEAD END WITH TRANSFORMER/ISOLATED ON 150-68/TRUCKS OK 2 CUSTOMERS WILL BE OFF/RECLOSER POLE 174-163 BACK N AT 1552 HRS RELEASED BY CREW 078S03//COD 90MADE H.T. BACK UP AT 01:15//VOLT CK GOOD///JLL. VER/SDB IDC XXXX
3530 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-11-09 17:40 | 2021-11-09 18:25 | 167 | 45 | 4071391 | 7515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke solid blade cutout on pole 292-16. will have to open rec on pole 269-D-356 when help arrives to safely maker repaires. off @ 17:40. on @ 18:25 Released by crew 077S10
3531 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-12-23 13:26 | 2009-12-28 18:36 | 1 | 7510 | 58018-1 | 7510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | M#533605501...BAD 25 KVA XFMR..NEED CREW TO CHG...BB RELEASED BY CREW 076S01 XFMR CHANGED 12/28 ON AT 18:36 D SAMMONS DKG/122809/1900 HRS/CLOSED ORDER PER COMMENTS/FOUND IN WRONG STATUS CHECK TIME ON IN HOIS
3532 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-12-13 05:49 | 2022-12-13 08:08 | 54 | 139 | 4254671 | 7506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | Jumper broke on 598-18, making repaires, apr at 0808 close ticket
3533 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-06-22 11:57 | 2020-06-22 14:00 | 61 | 123 | 4059311 | 7503 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | customer at address 9520 dug into a miss marked secondary causing primary nuetrul to fall knocked recloser out got repairs made to nuetrul// crew required to fix underground coming off pole38830115C00285// recloser back in at 14:00
3534 | Hazard | 3309302 | VICCO | JEFF | 2010-06-08 00:01 | 2010-06-08 07:22 | 17 | 441 | 58577-1 | 7497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 37830345C00147 WIRE DOWN ON B PHASE AT THIS POLE CALLING FOR TREE CREW AND LINE CREW/WILL WORK FIRST THING IN THE MORNING DUE TO HAZARDOUS LOCATION OF FAULT POLE AND NUMBER OF CUSTOMERS OUT //COD 17//OPENED N.C. SWITCH ON 345-C-369 IN ORDER TO MAKE REPAIRS (SEE H58577-1) @ 07:12 INTERRUPTING 53 ADDITIONAL CUSTOMERS//CLOSED BACK AND RESTORE POWER TO ALL CUSTOMERS @ 0722// VER/DBM IDC XXXX
3535 | Hazard | 3303902 | LESLIE | WOOTON | 2012-02-23 00:21 | 2012-02-23 21:10 | 6 | 1249 | 4484241 | 7494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS WORKING ON THIS CIRCUIT PROJECTED TIME OF RESTORATION 23:59 2/23/12CREWS WORKING ON THIS CIRCUIT PROJECTED TIME OF RESTORATION 2/23/12 REPLACED CUTOUT POWER ON @2110 //VER/GAH IDC XXXX
3536 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-12-27 18:49 | 2020-12-27 20:25 | 78 | 96 | 4828801 | 7488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | hottap burnt off on fuse pole 37830196D00045 //related to order 4815241//opened GOAB 37830220000143 in order to make repairs//open @ 1851 // closed @ 2025//cod 74 //
3537 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-01-23 22:05 | 2019-01-24 00:41 | 48 | 156 | 4713571 | 7488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout pole 37830253000200/ bad cutout on pole 253-200, replaced cutout, all power restored/ ISO 37830253B40231/ COD 48 L3/HFP
3538 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-03-20 14:31 | 2008-03-20 18:25 | 32 | 234 | 59502-1 | 7488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #8CW & #6CW PRIMARY & NEUTRAL DOWN, CONTACTED TIM HALL FOR CREW, B PHASE OPEN ON POLE 16-64, C PHASE HOT FOR NOW......ALL WORK COMPLETE / GXJ THIS IS THE B PHASE OUTAGE ORDER 59508-1 CONTAINS OUTAGE FOR C PHASE VER/HFP IDCC PN6 XXXX
3539 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-03-23 15:07 | 2008-03-23 18:35 | 36 | 208 | 60092-1 | 7488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3402202// POWERON PREDICTING B PHASE FUSE OUT 40T ON POLE 37830067C00052 - 36 CUSTOMERS// POLE 68-42 A PHASE OFF INSULATOR, NO OTHER TROUBLE FOUND ......ALL WORK COMPLETE / GXJ VER/HFP IDC XXXX
3540 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-10-19 07:54 | 2011-10-19 10:03 | 58 | 129 | 4997221 | 7482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 447-83, BAD CUTOUTS ON POLE 447-9005 & POLE 447-197.. REPLACED CUTOUT ON 447-9005 & REMOVED CUTOUT ON 447-197 NOT SERVING ANYTHING, RESTORED POWER AT 10:03//COD 58// VER/DBM IDCC TOF83 FIRST CALL FLICKERING XXXX
3541 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2011-09-20 08:16 | 2011-09-20 16:48 | 31 | 512 | 4887241 | 7472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WITH BAD == NEED LINE CREW == OPEN LINE ON POLE 37830465000030 === MAIN LINE ON AT 09:48 == RELEASED BY CREW 077S03ON SITE WORKING MADE REPAIRS AND RESTORED POWER AT 1648 CREW 077H01//COD 31 IDC NEEDED R/W CREW THIS EXTENDED OUTAGE XXXX
3542 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2009-10-09 07:58 | 2009-10-09 12:07 | 30 | 249 | 66451-1 | 7470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ((WREQUEST 32130492 ))// BREWER EN ROUTE //WR/ 32130492 POLE 1148-78 HOT TAP BURNT OFF POLE 1148-78 //CREW ON /SITE/FETR1045/VEM/FOUND BAD CUTOUTS /NEED BREAKER OUTAGE/NEED 3 200 AMP CUTOUTS/VEM/NEW FETR FOR SHORT WHITE OAK 1300/VEM/REPAIRS MADE AND ALL CUST RESTORED 1207/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 // ONLY 30 OUT - BAD BASKET // VER/TOM IDC XXXX
3543 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2017-06-14 13:48 | 2017-06-14 20:21 | 19 | 393 | 4967821 | 7467 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESTORED ALL 2021FOUND A BAD CUTOUT @ 296-37 CLOSED LINE FUSE @ 20:21 COMPLETE 38830296000028 38830296000037 VER/AWD SJG (EAST FUSE)
3544 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-01-02 23:58 | 2014-01-03 13:15 | 12 | 797 | 4221111 | 7464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER DUTY SUPERVISOR FOR THIS AREA, HOLDING NON-EMERGENCY CALLS UNTIL THE A.M. DUE TO TERRIBLE ROAD CONDITIONS// STS GOT 25 KVA 7200 TRANSFORMER BAD NEED 50 KVA AND CUTOUT AND ARRESTOR AND MAT HANGER BUCKET LINE FUSE RESTORED AT 0815 POLE # IS 1083D40373 RELEASED BY CREW 077S05 TRANSFORMER REPLACED IDCC TON1305 STP1 XXXX
3545 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-06-19 10:50 | 2018-06-19 12:43 | 66 | 113 | 4620651 | 7458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew opening step down to replace bypass cutout and insulator on recl 37830263C00322B/ ISO 37830263C00322B/ COD 66/1050- 1243
3546 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-10-01 18:32 | 2011-10-01 21:20 | 47 | 168 | 4938641 | 7456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON 38831152000097// PATROLLING//TOP OF POLE BURNED OFF AT 1151-704// I LIFTED A HOT TAP ON POLE 1151-525//DAMAGES REPAIRED //POWER IS RESTORED //VER/GAH IDC XXXX
3547 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-10-03 18:40 | 2014-10-04 03:25 | 34 | 525 | 4549041 | 7455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE,ON POLE 188-299, LIFTED HOT TAPS ON POLE 188-296. PUT REC. BACK IN AT 21:00 TAGED POLE 188-296 TO BILL F RELEASED BY CREW 078S01--- 300 AMP SWITCH ON POLE188-299 VER/KEP L3/HFP AJB
3548 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-06-29 03:27 | 2014-06-29 14:12 | 31 | 645 | 4166691 | 7455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830151000204 === OPEN LINE ON POLE 3783015100037 === MADE MAIN LINE HOT AT 7:14 === POLE 37830151000100 IS FEED OFF POLE 204 NOT OFF 36 ==== CALLED FOR LINE CREW === TOP OF POLE BURNED OFF NEED TO REPLACE POLE 204 === REPLACE POLE GOT THE LAST CUST AT 14:12 === POWER ALL ON ==== VER/KEP AJB
3549 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-05-06 00:47 | 2013-05-06 09:35 | 53 | 528 | 4075001 | 7453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1060-247 BURNED OFF. OPEN SOLID BLADES ON POLE 1060-319 AND PUT RECLOSER BACK IN 0236 CLOSED SOLID BLADES ON POLE 1060-319 AT 0935 RELEASED BY CREW 077S05 COD-53 ISO OCR 38831083C40963 VER/HFP L3/HFP IDCC PN963 XXXX
3550 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-09-14 21:49 | 2022-09-14 23:21 | 81 | 92 | 4883671 | 7452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | 37830272A41201 spacer cable messenger has pulled loose from shoe//cod 81//iso 37830272A40605
3551 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-09-10 13:43 | 2011-09-10 15:21 | 76 | 98 | 4855001 | 7448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PULLED 6A WIRE UP MADE REPAIRS /// COD-76 ISO OCR 38830142C00019 VER/HFP L3/HFP IDC XXXX
3552 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-01-11 10:12 | 2014-01-11 12:25 | 56 | 133 | 4272001 | 7448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | ON SITE PATROLING LINE//TIE WIRE BROKE, CONDUCTOR CAME OFF INSULATOR//COD 48//ISO 38830478A40037//MD FILED//ON SITE PATROLING LINE/ ON POLE478-136 WIRE CAME OFF INSULATOR TIE WIRE BROKE/POWER BACK ON AT 12:25 PLEASE CLOSE TIC RM//COD 48// VER/DBM L3/HFP HFPC CC48 IDCC XXXX
3553 | Hazard | 3302703 | HAZARD | HAZARD | 2017-05-30 00:17 | 2017-05-30 00:28 | 677 | 11 | 4880051 | 7447 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - NON LTC | 0017 TO 0028 VER/ARN AJB
3554 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-06-13 14:31 | 2012-06-13 15:05 | 219 | 34 | H4911951 | 7446 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | REGULATOR | ONE PHASE ON BUSSEYVILLE - LOUISA CIRC OUT ..MANUALLY INTERRUPTED LOUISA STATION AT 1431 AND RESTORED AT 1505 IDC XXXX
3555 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-02-20 12:03 | 2015-02-21 12:52 | 5 | 1489 | 4055651 | 7445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT 37820025D00122 REFUSED TRANSFORMER BUT STILL NO POWER. ENERGY LIMIT FUSE BAD OR TRANSFORMER BAD NEED SERVICER OR CREW TO REPAIR RELEASED BY CREW 074M01///////NEED CREW,BAD25 19.9,CAN USE MAT HANDLER RELEASED BY CREW 074S06//COD 5// VER/DBM
3556 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-09-17 10:42 | 2008-09-17 11:25 | 173 | 43 | 64819-1 | 7439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3008003// FOUND LOOP BURNT OPEN @ POLE 94-6510 / OPENED C PHASE RECLOSER TO ISOLATE AND MAKE REPAIRS - OPENED @ 1113 AND CLOSED @ 1125// COD 69 REPLACED RISER AND HOT TAP// 41 CUSTOMER OFF ENTIRE TIME FROM LOOP THAT BURNT ON SOLID BLADE - THEN ADDITIONAL 28 OFF WHEN OPENED C PHASE RECLOASE IDCC CNT246 XXXX
3557 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2011-05-04 06:03 | 2011-05-04 12:55 | 18 | 412 | 4005721 | 7416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | SEND TO T CANTRELL RELEASED BY CREW 078S07...BAD UNDERGROUND PRIMARY CABLE BETWEEN 20 - 420 AND 20 - 400...NEW CABLE ALREADY IN PLACE..//COD 18// VER/DBM IDC XXXX
3558 | Hazard | 3308002 | JACKSON | PANBOWL | 2020-07-19 11:25 | 2020-07-19 13:50 | 51 | 145 | 4182441 | 7395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulator on pole 1083-1222. restored 13:50
3559 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-03-13 12:22 | 2009-03-13 16:30 | 44 | 248 | 58099-1 | 7392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 38831126A00767 BURNT OFF BELOW GUY ATT. ISO. ON POLE 629 RELEASED BY CREW 074H07 ALL REPAIRS MADE POWER BACK ON AT 16:30//COD 44// VER/DBM IDC CUSTOMER COUNT 44 XXXX
3560 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-01-23 23:53 | 2015-01-24 01:21 | 84 | 88 | 4955391 | 7392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4953571//OPENED BREAKER THEN OPENED SWS 69-623 TO ISOLATE TROUBLE AND CLOSED BREAKER IN UP TO SWS ON "-623 @ 2359//COD 91// SWS CLOSED BACK IN 0121// VER/DBM L3/HFP HFPC TOF2355 CNT91 AJB
3561 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-10-07 04:33 | 2009-10-07 12:30 | 37 | 477 | 57323-1 | 7389 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SAME AS 57301, POWER IS BACK ON RELEASED BY CREW 077S08 RELEASED BY CREW 077H02//VER/CRB IDC XXXX
3562 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-10-12 14:06 | 2011-10-12 17:10 | 61 | 184 | 4971261 | 7374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON 1014B4-124...TOP OF GREEN POLE BURNT OFF..BAD CUTOUT.POLE 1038A3-356..CREW ENROUTE...WILL LIFT HOT LINE CLAMP ON 1038C325 & PICK UP MOST OF CUSTOMERS ON PARTIAL RESTORE..///.PARTIAL RESTORE @ 16:00..//.CREW BAYONETTED POLE TOP, RESAGGED WIRE, & REPLACED BAD CUTOUT..LAST FEW CUSTOMERS RESTORED AT 1710 COD-61 ISO LF 38821014B40124 VER/HFP L3/HFP IDC XXXX
3563 | Pikeville | 3403001 | PIKEVILLE | CITY | 2013-07-10 16:49 | 2013-07-11 01:00 | 15 | 491 | 4499101 | 7365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | LINE FUSE SERVING UNDERGROUND PRI. AT POLE24-1503 IS BLOWN. I TRIED IT BUT IT CAME BACK OUT. I CALLED FOR HELP RELEASED BY CREW 074S01 VER/KEP IDCC CDC83 XXXX
3564 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-10-01 16:40 | 2014-10-01 18:25 | 70 | 105 | 4542641 | 7350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PORCELIN ARRESTER BLEW UP ON XFMR POLE 875-573. CLEARED ARRESTER AND RESTORED @ 18:25. SH COD-70 ISO LF 38830875C00321 VER/HFP L3/HFP AJB
3565 | Cannonsburg | 3001401 | LOUISA | CITY | 2020-07-23 08:43 | 2020-07-23 11:10 | 50 | 147 | 4213821 | 7350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Looks to be c phase fuse blown on 454-1677. Conductor broke in between basket and will need repaired before we can re energize. Crew required Released by crew 078S11,repairs made all cust restored @ 1110 please close ticket thanks.bt
3566 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-03-16 10:22 | 2012-03-16 12:07 | 70 | 105 | 4587551 | 7350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4587401 CREW HAD TO OPEN RECLOSERS SO THEY COULD SAFELY REPLACE A BROKEN CUTOUT ON A POLE THAT HAS NO TRUCK ACCESS. COD-70 ISO OCR 37830153A40273 VER/HFP L3/HFP IDC XXXX
3567 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-09-14 17:55 | 2010-09-14 18:01 | 1224 | 6 | 66535-1 | 7344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED SWITCH TO SAFELY ISOLATE CUTOUTS ON 1073-3518 SEE PO 66301-1 VER/KEP L3/KEP IDC XXXX
3568 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-02-27 08:02 | 2009-02-27 09:50 | 68 | 108 | 52002-1 | 7344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3202201// CUTOUT BAD COD-68 L3/HFP IDC XXXX
3569 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2014-06-12 16:52 | 2014-06-13 11:10 | 12 | 1098 | 4079531 | 7326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BURNED TOP OF POLE 941-189 OFF///BLEW FUSE ON POLE 941-301///CUTOUT ON POLE 941-102 OPEN TO ISOLATE ///WILL CLOSE UP TO POLE 102///NEED 3 MAN LINE CREW//MANUAL TREE CREW//MAY POSSIBLY USE BIG BUCKET///7200 CUTOUT AND BRKT//FIBERGLASS POLE TOP EXT//CLOSED IN UP TO OPEN CUTOUT AT 18:55///CREW ENROUTE//BIG BUCKET WAS SHORT OF REACHING POLE///WE HAVE FIRE OUT///NEED LINE CREW TOMORROW////NO TAGS OR GRDS PLACED// RELEASED BY CREW 079S01//COMPLETE 1110 6-13//
3570 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-12-02 08:10 | 2014-12-02 08:47 | 198 | 37 | 4824581 | 7326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TIL RECLOSER OPENED//OPENED REC 39830901C45559 @0810//NO OUTAGE TIL RECLOSER OPENED// OPENED UP RECLOSERS AT 0810, REPLACED BAD LINE FUSE CUTOUT ON POLE39830901C45574, RESTORED RECLOSERS ON POLE 901-5559 AT 0847, POWER RESTORED TO ALL CUST VER/CRB L3/HFP AJB
3571 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-02-05 19:12 | 2010-02-05 19:25 | 563 | 13 | 65092-1 | 7319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | PLANNED OUTAGE TO STRAIGHTEN POLE 161-5 ON P.O. TROUBLE ORDER 64627-1 //VER/GAH IDC XXXX
3572 | Hazard | 3301401 | COMBS | COMBS | 2014-12-31 16:16 | 2014-12-31 17:51 | 77 | 95 | 4895311 | 7315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED REC. ON POLE 37830271C11075 AT 16:16==== BAD INSULATORS ON POLE 37830271A00035//THIS RECLOSER DOESNT SHOW ON MAP//A MDC HAS ALREADY BEEN MADE//CUST COUNT IS THE SAME//OPENED REC. ON POLE 37830271C11075 AT ------16:16==== BAD INSULATORS ON POLE 37830271A00035, REPLACED INSULATORS AND REPAIRED SERVICE, POWER RESTORED AT 17:51 VER/CRB AJB
3573 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-09-20 13:26 | 2008-09-20 20:35 | 26 | 429 | 65817-1 | 7314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3116701//1148-865 80T OUT//TIME ON 2035//COD 26// VER/DBM IDCC CDC83 XXXX
3574 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-02-17 19:07 | 2015-02-18 17:51 | 7 | 1364 | 4037391 | 7313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OPEN ON POLE 37830247A00639, VERY STEEP, ICY ROAD, NOT SAFE TO PATROL AT THIS TIME,WILL HOLD UNTIL 02-18-15 PER B. LINDON. RELEASED BY CREW 077S04RESTORED POWER TO ALL BUT THREE CUSTOMERS AT 1024 . BAD 25 KVA ON P#247 / 537RESTORED POWER TO ALL BUT THREE CUSTOMERS AT 1024 . BAD 25 KVA ON P#247 / 537 CHANGED TRANSFORMER AND RESTORED POWER TO LAST CUSTOMER AT 1751 RELEASED BY CREW 077H03 VER/HFP L3/HFP
3575 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-08-16 19:31 | 2018-08-17 01:03 | 22 | 332 | 4962151 | 7304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Lifted hot tap on transformer on pole 37820169000079 restored at 0103//cod 22//bad csp which fed no one// L3/HFP
3576 | Pikeville | 3421001 | BREAKS | CITY | 2019-11-14 14:05 | 2019-11-14 14:13 | 913 | 8 | 4034591 | 7304 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | Short outage to safely bypass Regulator at Breaks Station/ DOL 971003 & 970950 off @ 1405 on @ 1413
3577 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-06-22 23:39 | 2018-06-23 09:00 | 14 | 561 | 4650761 | 7302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A phase L/F open @38831101D30263, checking. Also L/F open on 1101-D1-282. Found no trouble, closed l/f on 1101-D3-263 @0728, found a bad 19.9 dead end insulator on pole 1101-D3-429, will be changing. Got dead end changed out and closed l/f @1101-D1-282 @0900. Released by crew 074S05
3578 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-03-04 06:50 | 2016-03-05 13:15 | 4 | 1825 | 4813901 | 7300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | **SEE H4813901** #4 COPPER PRIMARY DOWN AT 574-10,,BROKE IN CLEAR AT FUSE POLE, FAULT POLE IS ENERGIZED,,NO TRUCK, COULD USE 6-WHEELER,,PULLED OUT OF SLEEVE,,ISOLATION POLE IS 574-10/ OPENED LINE FUSE 38830374A10082 @ 1150 TO REPAIR PRIMARY @ 38830374000010/,,OPENED FUSE 38830374A10082 AT 11:50/ ALL REPAIRS MADE & ALL POWER RESTORED/ FINAL RESTORATION 13:15/ DUPLICATE IN HOIS/ VER/BOW AJB
3579 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-04-16 19:07 | 2010-04-16 20:11 | 114 | 64 | 64071-1 | 7296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | POLE 20-7522 LOOP BURNT OPEN REPAIRED COD-114 VER/HFP L3/HFP IDC XXXX
3580 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2009-09-11 09:27 | 2009-09-11 13:15 | 32 | 228 | 66141-1 | 7296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGED CUTOUT == REFUSED POWER OK VER/KEP L3/KEP IDC XXXX
3581 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-06-28 17:10 | 2014-06-28 21:40 | 27 | 270 | 4165571 | 7290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F BLOWN ON 38831027D00172// WILL PATROL//L/F CUTOUT BROKE// NEED 1 MAN AND BUCKET/// POWER RESTORED @ 21:40 VER/ARN AJB
3582 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2020-01-03 01:26 | 2020-01-03 07:43 | 33 | 377 | 4206151 | 7286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 245-148 crew required with a tech broke cutout burnt pole off/tagged to ramey grounds at 245-147 isolated at that location/245-55 back on at 0312 hrs to 245-147 Released by crew 078S03//INSTALLED A 300 AMP SB ON POLE 38830245B00148//WILL BE ENERGIZING FROM HERE//245-148 crew required with a tech broke cutout burnt pole off/tagged to ramey grounds at 245-147 isolated at that location/245-55 back on at 0312 hrs to 245-147 Released by crew 078S03///Complete BR Released by crew 078H22 L3/HFP
3583 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-07-06 10:52 | 2009-07-06 16:33 | 29 | 341 | 52300-1 | 7279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP A PHASE FUSE OUT 29 CUST /// CROSSARMS ROTTED AND BROKE ON POLE 834-33 - DIFFICULT LOCATION. OPENED SW. ON POLE 834-28 TO ISOLATE TROUBLE. CLOSED FUSE ON POLE 11 AT 12:12 ENERGIZING UP TO AND INCL. XFMR ON POLE 28. CREW ENROUTE. RELEASED BY CREW 076S02/// REPAIRS COMPLTED AND POWER RESTORED AT 16:33 L3/HFP MLR OK
3584 | Whitesburg | 3312901 | JENKINS | KONA | 2022-03-12 12:34 | 2022-03-12 17:25 | 25 | 291 | 4610071 | 7275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad line fuse cutout on pole 404-b-68 - falls open, wont stay closed. power restored @ 17:25
3585 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2011-07-22 16:29 | 2011-07-22 21:39 | 24 | 310 | 4581221 | 7272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRYED 30T AT 17;05 CAME BACK OUT POLE 69-1620 NEED CREW /// TREE CREW IS CUTTING TREE FIRST POLE PAST THE FUSE REPLACING ARRESTORTRYED 30T AT 17;05 CAME BACK OUT POLE 69-1620 NEED CREW /// TREE CREW IS CUTTING TREE FIRST POLE PAST THE FUSE REPLACING ARRESTOR/FUSE BACK IN AT 2131/ALL CUST RESTORED/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP
3586 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-02-11 23:43 | 2018-02-12 00:33 | 200 | 50 | 4832001 | 7262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | at pole 91-590 ( which is a step-down platform) we have b phase cutout failing and tracking on arm will need to replace all three cutouts NO OUTAGE YET Released by crew 078H01//ISO//cod 200 // VER TIMES PER VOICE RECORDER = L3/HFP
3587 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2014-06-19 10:47 | 2014-06-19 12:05 | 93 | 78 | 4110821 | 7254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FAULT INDICATORS & CUSTOMER INFO LEADS TO A BAD 6 IN. DISC INSULATOR ON POLE 38831102000046. I HAVE ISOLATED THIS ON POLE 38831078000049.XFMR ON 49 IS NOT BEING USED. VER/KEP AJB
3588 | Hazard | 3310502 | HADDIX | CANOE | 2020-05-03 14:07 | 2020-05-03 15:45 | 74 | 98 | 4790711 | 7252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | lighting arrester went bad and csp transformer
3589 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-05-13 19:15 | 2020-05-13 22:35 | 38 | 200 | 4833011 | 7250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1905ishbad cutout on p-925-7..opened cutout at 19:15..need 2 man line crew and big bucket \\\ OPENED LEFT HAND PHASE @ 1915 (36 CUST) OPENED SINGLE SPAN TAP @ 2210 (2 CUST)
3590 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-04-28 15:55 | 2011-04-28 16:20 | 290 | 25 | H51703-1 | 7250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | "A " REG FAILED. SERVICER OPENED RECL AT1555 TO ISOLATE REGS.// RELEASED BY CREW 074S02 COD-104 TILL 1555 WHEN RECLOSER WAS OPENED COD-290 CLOSED AT 1620 RESTORED ALL CUSTOMERS/ REGS ARE TAGGED AND BYPASSED VER/KEP IDC XXXX
3591 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-08-14 09:47 | 2017-08-14 13:57 | 29 | 250 | 4257411 | 7250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE 45-6777 3-65T OUT POLE 45-6542 2-CROSS ARMS BROKE RELEASED BY CREW 078S08---CREW ON SITE--G&T TO RMV--REPLACED ARMS--REPAIRED 1 SERVICE DROP---TBLT TK COMP---RMV VER/HFP L3/HFP SJG
3592 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-01-10 08:49 | 2015-01-10 12:20 | 58 | 211 | 4925561 | 7243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | "B" PHASE ONLY COD-58/WIRE DOWN 1075-11/ LIFTED HOT TAP 1051-50/CLOSED FUSE AT 1005 RESTORED 37 CUST/ HAVE LINE ISOLOATED & MY TAG & GROUNDED AT POLE 1051-50/REPAIRS MADE POWER RESTORED AT 12:20 NO FAULTS DETECTED LOOKS LIKE LINE JUST MELTED INTO RELEASED BY CREW 074H07 VER/KEP L3/HFP AJB PH B.
3593 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-08-10 19:41 | 2009-08-11 07:45 | 10 | 724 | 60942-1 | 7240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR/31163864 BAD 50KVA TRUCK TO POLE RELEASED BY CREW 078S08 COD-10 ISO TF 39831123D26531 L3/HFP IDC XXXX
3594 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-07-31 19:14 | 2022-07-31 20:40 | 84 | 86 | 4645621 | 7224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RECL (not on map) open at 65-571//phase burnt down under a mac between poles 89-188 and 51// opened switch on 188 C phase// Restored recloser on pole 65-571 @ 20:40/// Crew required and flaggers/opened other 2 phase at 18:28/closed all3 phases at 19:25 on pole 89-188 Released by crew 074H07
3595 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-03-02 19:04 | 2015-03-03 05:15 | 13 | 611 | 4092911 | 7223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "B" PHASE OPEN COD-13/ POLE 199-197 "C" PHASE OFF AT 2035 COD-152/GROUNDED AND TAGGED TO DDC /FAILED CUTOUT BURNT POLE INTO POLE 198-93/45/2 POLE DOUBLE DEADEND 2 PHASE WITH SINGLE PHASE TAP ALSO HAS UNDERGROUND ON POLE WITH 15 KVA RELEASED BY CREW 078S03 RECLOSER CLOSED AT 0415 ALL RESTORED EXCEPT XFMER POLE#93/XFMER CLOSED 0515/H4092911 FOR "C" PHASE VER/KEP L3/HFP XXX
3596 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-01-01 04:55 | 2022-01-01 11:15 | 19 | 380 | 4242861 | 7220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LF open on 1149-41, no hazards found// fuse did not hold// bad dead end insulator and XCO on pole 1149-94, need big bucket to make repairs, water is getting over road in spots
3597 | Pikeville | 3401001 | ELWOOD | DORTON | 2019-07-17 21:58 | 2019-07-17 22:07 | 802 | 9 | 4725531 | 7218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | BREAKER | DOL 939402//opened CB for momentary outage to close xfer bus discs at ELWOOD station.//this is to restore customers from Virgie ckt due to failed CB//cod 802// ¦¦ VERIFIED TIMES PER SCADA & DOL - L3/HFP
3598 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-03-15 23:12 | 2008-03-15 23:21 | 802 | 9 | 57578-1 | 7218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008002/// 45-7514 BAD CUTOUT VER/JHM IDCC TOF2149, TON2330, PN 7514 XXXX
3599 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-10-09 05:01 | 2014-10-09 05:11 | 721 | 10 | 4577601 | 7210 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP L3/HFP AJB CCTIN FEC57 PER TRANS LOG AND DISP LOG
3600 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2010-02-09 23:51 | 2010-02-10 01:20 | 81 | 89 | 54711-1 | 7209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, POLE#1113-B-184, ONE CUST STILL OUT ON THIS POLE, WILL MAKE REPAIRS TOMORROW - CUSTOMER OK TO LEAVE OUT - CREATED IW, WILL NEED THREE CUTOUTS VER/TOM L3/TOM IDC XXXX
3601 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-06-01 13:54 | 2008-06-01 15:40 | 68 | 106 | 53736-1 | 7208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308402// FOUND BAD CUTOUT ON POLE 279..185 TOOK OFF LINE DID NOT SERVE ANYONE//COD 68// VER/DBM IDC XXXX
3602 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-01-02 21:17 | 2014-01-02 21:45 | 314 | 28 | H4219861 | 7208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE ONLY OUT AT RECL 459-166 DUE TO SLIDE ***326CC. *5 POLES HAS BROKE 8FT ARMS WILL NEED R/W CREW 3 LINECREWS AND A FLAGGING CREW LOOPS OPENED AT 576-85 & TAGS PLACED FOR DDC.* TAGS TO BE REPLACED BY FIELD LCS. AND WORKED CREW DISP AUTHORITY. DAVOX SAYS SLIDEC PHASE ONLY OUT AT RECL 459-166 DUE TO STIRUP FAILURE 326CC. 5 POLES HAS BROKE 8FT ARMS WILL NEED R/W CREW 3 LINECRWS AND A FLGGNG CREW LOOPS OPND AT 576-85 & TAG//?????? IDCC DUP TOP OPEN RECLOSERS XXXX
3603 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-07-04 10:07 | 2015-07-04 11:15 | 106 | 68 | H4719151 | 7208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | JOEY FOUND LEFT HAND PHASE WITH BACK TO STATION BURNT DOWN LOOKS LIKE BAD COPPER TP ALUM CONNECTION HES GOIN TO RECLOSER WILL CALLWITH POLE # A PHASE COD 13// OPENED OTHER PHASES @ 1007// COD 106//JOEY FOUND LEFT HAND PHASE WITH BACK TO STATION BURNT DOWN LOOKS LIKE BAD COPPER TP ALUM CONNECTION HES GOIN TO RECLOSER WILL CALLWITH POLE # REPAIRED CONDUCTOR ON POLE1038B141 VER/CRB L3/DKG THIS IS FOR OPENING OTHER 2 PHASES. ORIGINAL OUTAGE IS ALREADY IN APPROVED
3604 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-08-15 12:03 | 2022-08-15 14:14 | 55 | 131 | 4744701 | 7205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad pole top insulator on pole 397-42. replaced insulator. power restored
3605 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-06-28 20:46 | 2021-06-29 10:05 | 9 | 799 | 4819011 | 7191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF BLOWN,PROBABLY ALSO THE CURRENT LIMITER FUSE//////NEED 1 MAN,A OR B LINEMAN,DOESNT MATTER WHICH/////NEED CREW,XFR BUSHING IS BAD.NO ACCESS.WATCH SEPTIC@HSE.NEED TO WORK IN AM.CHANGE CUTOUT IF TAP HAS TO BE OPENED TO WORK Released by crew 074S06//opened L/F at 9:20 closed in at 10:05
3606 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-08-22 08:58 | 2019-08-22 18:55 | 27 | 597 | 4926101 | 7189 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | LEFT HAND FUSE "C" PHASE FUSE OUT ON POLE 39831123D26530 ¦¦¦50t lf open @ 1123-6530, cut a & c loops @ 1123-6541 isolating bad 12 c/o at 1123-658150t lf open @ 1123-6530, restored @ 11:05.cut a & c loops @ 1123-6541 isolating bad 12 c/o at 1123-6581.. no grounds placed./// trouble tickets show A phase
3607 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-03-19 07:59 | 2022-03-19 10:05 | 57 | 126 | 4644871 | 7182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Load side fuse open on Step Down at 286-235(ASSESSING CONDITION)Load side fuse open on Step Down at 286-235,Found a broke fuse on Load side,Replaced fuse and restored service at 10:05..
3608 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-03-18 23:18 | 2020-03-19 05:00 | 21 | 342 | 4490131 | 7182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Load side of step down open @38821108000061, patrolling. Bad angle insulator @1108-65, will be making repairs. Got insulator changed out, closed S/D back in @0500.
3609 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-08-14 21:46 | 2010-08-14 23:59 | 54 | 133 | 55006-1 | 7182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKEN DOWN AT 1126-318 AND OPENED RECLOSER ON POLE 1126-841. I AM GOING TO CHANGE CUTOUT AND CLOSE RECLOSER IN. VER/KEP L3/KEP
3610 | Hazard | 3309301 | VICCO | REDFOX | 2013-02-27 02:18 | 2013-02-27 06:54 | 26 | 276 | 4856971 | 7176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON POLE 37830326D00177, CHECKING LINE, REFUSE LINE STAYED IN ABOUT 1 MINUTE AND BLEW. PROBABLY NEED HELP //JOHNNY LAWSON TO ASSIST //POLE 37830326D00059 WE HAVE XFMR C/O BROKEN ///VER/CRB L/3 CRB IDC XXXX
3611 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2019-11-27 15:06 | 2019-11-27 22:08 | 17 | 422 | 4089301 | 7174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B phase stinger broke at cutout; B phase only out; released to line; truck ok Released by crew 078E02 restored @ 2208
3612 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-04-14 16:49 | 2009-04-14 23:51 | 17 | 422 | 52262-1 | 7174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW FOREIGN POLE /INLINE POLE /NEED TECH ALSO 40/5 POLE/SEND TO MULLINS RELEASED BY CREW 078S03/CREW ON SITE/FETR0130/VEM/REPAIRS MADE AND ALL CUST RESTORED 2351 4-14-09/PLEASE CLOSE TICKET/THANKS/VEM VER/PDP IDC XXXX
3613 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-04-10 11:03 | 2016-04-10 13:46 | 44 | 163 | 4077401 | 7172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OPEN ON 875-167. INSTALLED 40T LINE FUSE ON 875-167 AND CLOSED @ 13:46 RESTORING OUTAGED CUSTOMERS. MD ENTERED SH VER/AWD AJB
3614 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-11-23 11:27 | 2010-11-23 14:10 | 44 | 163 | 59011-1 | 7172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | WR#37866706 REMOVED REC. OF LINE CLOSED BYPASS//VER/CRB IDC XXXX
3615 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-05-04 11:39 | 2014-05-04 14:22 | 44 | 163 | 4661271 | 7172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 3 MAN PRC CREW RELEASED BY CREW 078S07/FETR 15:30 JEH/ REPAIRS COMPLETE/POWER RESTORED @ 14:22//JEH PLEASE CLOSE TICKET VER/SEF L3/HFP HFPC FP67 20 IDC XXXX
3616 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-03-25 12:30 | 2009-03-25 15:40 | 94 | 190 | 61402-1 | 7165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN BETWEEN POLE 1123-1063 AND POLE1123-1050 OPENED FUSE ON POLE 1123-1050 --100T//COD 94//REPAIRED LINE TRIED FUSE AND IT CAME BACK OUT/---POLE 1123 -1081 BURNT OFF, CREW WILL LOWER ALL HARDWARE ON POLE , LAST CUSTOMER ON @ 1540// VER/DBM IDCC TOF1251 XXXX
3617 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-08-29 23:53 | 2020-08-30 09:20 | 17 | 567 | 4402321 | 7164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | riser fuse is out on pole 37830071000162. line crew required defective UG between 37830071000203 & 37830071000204 . Removed & parked elbows at 37830071000203 towards 37830071000204 closed riser fuse at 37830071000162 @ 04:45 restoring 9 CC remaining 8 CC restored at 0920
3618 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-12-31 01:08 | 2009-12-31 07:46 | 18 | 398 | 51259-1 | 7164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, PATROLLING LINE//BAD CUTOUT ON TRANSFORMER 940-71//COD 15 IDC XXXX
3619 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2015-01-29 10:38 | 2015-01-29 12:13 | 106 | 95 | 4972441 | 7158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /BAD TRANSFORMER CUTOUT ON POLE 38820942B20016, PHASE C FUSE IS BLOWN ON POLE 38820942B20078. /COD-106/BAD TRANSFORMER CUTOUT ON POLE 38820942B20016, PHASE C FUSE IS BLOWN ON POLE 38820942B20078. PHASE C CLOSED BACK IN AT 11:45.BAD TRANSFORMER CUTOUT ON POLE 38820942B20016, PHASE C FUSE IS BLOWN ON POLE 38820942B20078. PHASE C CLOSED BACK IN AT 11:45. TRANSFORMER BANK ON POLE 38820942B20016 RESTORED AT 12:13. RELEASED BY CREW 079S02/COD 104+2// VER/ ADH L3/HFP XXX AJB
3620 | South Williamson | 3411401 | DEWEY | INEZ | 2012-10-02 04:15 | 2012-10-02 08:50 | 26 | 275 | 4105831 | 7150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE CHECKED AFTER REGULAR WORKTIME AS PER SET GUIDELINES //RECLOSER OPEN ON 792-156///PATROLLING//CUTOUT BROKE ON 792-72//CHANGING NOW//RESTORED AT 8:50//COMPLETE//EM//COD 26// VER/DBM IDC XXXX
3621 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-03-06 02:01 | 2011-03-06 12:02 | 16 | 601 | 50280-1 | 7150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINES.. LINE FUSE OUT 246-26. BAD CUTOUT BURNED TOP OF POLE #246-166. CREW REQUIRED TRUCKS OK CUST SAID COULD BACK IN YARD.. DEADEND PL XFMR 2 SERVICES.. TROUBL ISOLATED POLE 246-26 AND GROUNDED WILL CLOSE BACK IN FUSE ON POLE 246-26 AND RESTORE BOATHOUSE RD.. FUSE IN AT 5:11 RELEASED BY CREW 078H22PATROLLING LINES.. LINE FUSE OUT 246-26. BAD CUTOUT BURNED TOP OF POLE #246-166. CREW REQUIRED TRUCKS OK CUST SAID COULD BACK IN YARD.. DEADEND PL XFMR 2 SERVICES.. VER/HFP L3/HFP IDC XXXX
3622 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-05-04 11:07 | 2009-05-04 21:56 | 11 | 649 | 51701-1 | 7139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GAVE 911 ETA--40 CLASS 5 POLE BURNT OFF--BAD CUTOUT--POLE 38830070B22575-HAS BAD CUTOUT AN BURNT INTO ALSO--POLE NEEDS REPLACED RELEASED BY CREW 078S07/VER/CRB IDC XXXX
3623 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-04-17 18:52 | 2008-04-17 22:35 | 32 | 223 | 51939-1 | 7136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 300870REPLACED BAD ARRESTOR1// STEP DOWN ON POLE 140-1004 IS OUT//LINE SIDE FUSE ON STEP DOWN OUT// CALLING LLOYD N CREW TO HELP MLR OK, IDC XXXX AJB
3624 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-11-27 19:08 | 2018-11-28 00:18 | 23 | 310 | 4485441 | 7130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary dn beween pole 1008-33 and 34 we will be making repairs//cod 23 ALSO SEE 4485671
3625 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-08-16 16:48 | 2012-08-16 19:00 | 54 | 132 | 4944741 | 7128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | A PHASE RECLOSER OUT ON POLE 80-36. FOUND BAD REGULATOR ON POLE 104-118. CLOSED RECLOSER BACK IN ON POLE 80-36 AT 19:00//COD 52//AED CREATED IDCC CNT138 XXXX
3626 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-04-28 07:00 | 2013-04-28 08:36 | 179 | 96 | H4052581 | 7122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN LOOP ON POLE 37830225D00276, MANUAL, WILL HAVE TO DEENERGIZE 3 PHASE TO REPAIR. FOUMD B HASE DOWN AT POLE 37830225D00274 RELEASED BY CREW 077S04// 30 CC OUT ORIGINALLY// OPENED OCR + 179CC// CLOSED OCR @ 0710 RESTORING 117 CC, LEAVING 92 (30 ORIGINAL +62 OUTAGED TO MAKE REPAIRS) RESTORED AT 0836 IDCC CNT209 XXXX
3627 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-10-02 02:41 | 2011-10-02 08:14 | 58 | 333 | 4939351 | 7116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED,BURNING THE TOP OF THE POLE OFF. ISOLATED ON POLE 80-14 CLOSED RECLOSER AT 0440 RELEASED BY CREW 074S02 COD-58 ISO OCR 37820104000026 VER/HFP L3/HFP IDC XXXX
3628 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-08-15 10:44 | 2022-08-15 20:47 | 89 | 603 | 4743921 | 7115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 25 KVA Xfmr. Manual. Opened recloser on pole # 147-54 at 19:33, closed at 20:47. Customer has full power. Released by crew 077H07
3629 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-04-14 16:01 | 2009-04-14 22:15 | 19 | 374 | 52245-1 | 7106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE 40/5 WITH A 45/5 TRUCKS OK AT 341 PARKER LN THIS IS A FOREIGN POLE TECH NEEDED/SEND TO VERNON MULLINS RELEASED BY CREW 078S03/CREW ON SITE/VEM/REPAIRS MADE ALL CUST RESTORED2215/ RESTORATION IS CORRECT /CHANGED FETR TO COMPLETE TICKET/PLEASE CLOSE TICKET/THANKS/VEM// COD 19// VER/DBM IDC XXXX
3630 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-11-12 07:41 | 2012-11-12 13:04 | 22 | 323 | 4384081 | 7106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 HENDRIX BURNED DOWN. WILL WILL REQUIRE SLEEVES, 2 MEN & MATERIAL HANDLER RELEASED BY CREW 074S04// CREW ON SITE STARTING REPAIRS TCM//COD 22// VER/DBM IDC XXXX
3631 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-08-10 07:14 | 2009-08-10 10:35 | 50 | 201 | 52325-1 | 7105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 31148706 // TREES 1147-4185 BAD CUTOUT AND LA 1147-5157 INSTALLED TO 25T LINE FUSES ON 1147-4184 1123-6533 50T IN AT 9:00 AM POLE 1147-4184 25T ON 10:35 /// ENTERED MD...HFP COD-50 ISO LF 39831123D26533 L3/HFP IDCC TON XXXX
3632 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-03-23 06:11 | 2011-03-23 10:16 | 29 | 245 | 56906-1 | 7105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOPS BURNT OPEN ON C PHASE @ POLE 38830576A00065//COD 36//ISO//PATROLLING LINE. LOOP OPEN ON POLE 576-65 WAITING ON FLAGGERS AND LINE CREWPATROLLING LINE. LOOP OPEN ON POLE 576-65 WAITING ON FLAGGERS AND LINE CREW TO ARRIVE//OPENED RECLOSER 527-D3-18 (IN NEW ORDER) TO MAKE BACK LOOPS// VER/DBM IDC XXXX
3633 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-04-08 10:56 | 2019-04-08 14:45 | 31 | 229 | 4069191 | 7099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | @1215 PATROLLING LINEbad insulator on pole 450-32 manualbad insulator on pole 450-32 manual replaced insulator an cutout sjg
3634 | Pikeville | 3402002 | KEYSER | STONECOAL | 2016-07-25 17:24 | 2016-07-25 20:25 | 40 | 181 | 4678561 | 7099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM SPLIT OUT ON 1104-18 LETTING C PHASE COME INTO CONTACT WITH CROSSARM NEED CREW WITH BIG BUCKET RELEASED BY CREW 079H03//OPENED SWITCHES ON POLE38831128000024// CLOSED L/F @ 1938//P/U 3 CUST//CROSSARM SPLIT OUT ON 1104-18 LETTING C PHASE COME INTO CONTACT WITH CROSSARM NEED CREW WITH BIG BUCKET RELEASED BY CREW 079H03..OPENED THREE 600 AMP SWITCHES ON POLE 1128-24. CLOSED IN AT 1104-18 AT 19:38.HOT UP TO 1128-24..CLOSED 1128-24 AT 20:25 RELEASED BY CREW 079H07 VER/CRB AJB
3635 | Hazard | 3302704 | HAZARD | KENMONT | 2010-07-31 10:43 | 2010-07-31 14:00 | 36 | 197 | 59801-1 | 7092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 37830297000004 LINE FUSE BLOWN ON THIS POLE, PRIMARY WIRE DOWN ON POLE 297-76////WIRE BACK UP AND VINES CUT. POWER RESTORED.//VER/CRB IDC XXXX
3636 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-06 18:25 | 2008-07-06 18:43 | 394 | 18 | 63364-1 | 7092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RELATED TO ORDER 63232-1 OUTAGE NECESSARY TO RETURN CIRCUIT TO NORMAL AFTER CREW REPAIRED BROKEN CROSS ARM. VER/HFP IDC XXXX
3637 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-06-25 01:45 | 2015-06-25 13:34 | 10 | 709 | 4653301 | 7090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIL WORK IN THE AM 6-25-15///// OPENED FUSE ON 573-80&GROUNDED&TAGGED TO RON V AT 573-80, #4 SOLID COPPER DOWN AT 572-32 CREW REQUIRED RELEASED BY CREW 078S11///REPAIRS MADE///573-80 IN @ 13:34///TBL TKT COMP///RMV// VER/ ADH
3638 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-02-10 01:42 | 2010-02-10 01:59 | 417 | 17 | 54758-1 | 7089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HAD TO OPEN OCR ON POLE 1137A-331 TO PLACE JUMPER ON GOAB AT POLE 1137D-753// VER/TOM L3/TOM IDCC CNT160. THERE WERE NO ADDITIONAL CUSTOMERS OUTAGED XXXX
3639 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2012-07-02 20:16 | 2012-07-03 15:57 | 6 | 1181 | 4242171 | 7086 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTIONS BURNT UP AT TRANS REPLACED CONNECTIONS
3640 | Hazard | 3303902 | LESLIE | WOOTON | 2017-06-27 10:11 | 2017-06-27 14:17 | 40 | 246 | 4050311 | 7086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BAD 8FT CROSSARM PHASE HANGING IN AIR, OPENED SOLID BLADE @ 317-15 ISOLATED TAG AND GROUNDED CLOSED OCR 37830341000093 @ 1135 (17 CUST..CREW ON SITE.ALL 37830317000015 POWER RESTORED @ 14:17 (23 CUST)..P.HICKS/ VER/BOW SJG
3641 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-01-17 04:09 | 2008-01-17 08:05 | 30 | 236 | 57270-1 | 7080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311401// CLOSED IN @ 0805 - FOUND BAD CUTOUT // FAULT POLE 3783030400132 - ISO 37830328C10867 RECLOSER// 30 COD//// VER/TOM IDC XXXX
3642 | Whitesburg | 3314401 | MAYKING | ERMINE | 2012-09-09 22:59 | 2012-09-10 00:57 | 60 | 118 | 4034601 | 7080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER OPEN ON POLE 473-334, TIE WIRE BROKE ON POLE 473-56 ALLOWING PRIMARY TO MAKE CONTACT WITH POLE TOP PIN. MADE REPAIRS RESTORED POWER AT 00:57 VER/ARN IDC XXXX
3643 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-07-10 04:04 | 2014-07-10 06:00 | 61 | 116 | 4223921 | 7076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PER KEVIN BROWN FUSE BROKE VER/SEF AJB
3644 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-09-12 02:07 | 2014-09-12 03:40 | 76 | 93 | 4492271 | 7068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP ON LOAD SIDE OF RECLOSER HAS BURNED OFF BELL. I AM GOING TO REPLACE HOT TAP. I REPLACED HOT TAP AND CLOSED RECLOSER BACK IN AT 03:40 VER/HFP L3/HFP AJB
3645 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-08-24 00:30 | 2017-08-24 02:34 | 57 | 124 | 4294901 | 7068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE CONDUCTOR HAS BURNED INTO AT THE STIRUP ON POLE 38821038B00114. I WILL NEED TO OPEN A&B PHASE RECLOSER TO MAKE REPAIRS. OPENED A&B RECLOSERS AT 01:51. CLOSED AT 0234/ ORGIANNAL 57 ADDITONAL 59// VER/ADH SJG
3646 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-12-09 13:02 | 2020-12-09 17:56 | 24 | 294 | 4756531 | 7056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | ARRIVED RM replacing BAD padmount XFM @39831147C35196 .grounding & tagging@1147-5195 to RM all power on @ 17:56 please close tic RM
3647 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2014-10-04 17:30 | 2014-10-04 18:12 | 168 | 42 | 4553661 | 7056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//CUT-OUT FAILED AT POLE 449-1008, HAD TO OPEN 3 LINE FUSES AT POLE 449-47 TO PUT OUT ARM AND CHANGE CUT-OUT, OPENED AT 17:30 CLOSED BACK IN AT 18:12.//NO OUTAGE TIL FUSES OPENED VER/CRB L3/HFP AJB
3648 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-06-25 15:07 | 2009-06-25 22:02 | 17 | 415 | 59699-1 | 7055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE IS BLOWN ON POLE 163-108. I AM PATROLLING LINE NOW. LIGHTENING ARRESTER BLEW UP ON POLE 163-124 AND TOOK OUT LINE FUSE ON POLE 163-108. I CLEARED ARRESTER AND CLOSED LINE FUSE IN AT 22:02.//COD 17// VER/DBM
3649 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-12-08 03:19 | 2008-12-08 06:15 | 40 | 176 | 55311-1 | 7040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3308603/// WR # 27582660 ***** LOAD SIDE FUSE IS BLOWN ON STEPDOWN. I AM PATROLLING LINE. LOAD MAY HAVE TAKEN THIS FUSE OUT. EVEN IF THERE IS NO TROUBLE ON THIS LINE, I WILL NEED ANOTHER MAN AND TRUCK TO HELP PICK UP LOADLOAD SIDE FUSE IS BLOWN ON STEPDOWN. I AM PATROLLING LINE. LOAD MAY HAVE TAKEN THIS FUSE OUT. EVEN IF THERE IS NO TROUBLE ON THIS LINE, I WILL NEED ANOTHER MAN AND TRUCK TO HELP PICK UP LOAD. FOUND LTNG ARRESTOR BLOWN OFF ON POLE 423-137. I OPENED LINE FUSE VER/KEP L3/KEP IDC XXXX
3650 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-11-12 13:25 | 2013-11-12 16:21 | 40 | 176 | 4032281 | 7040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN BURNING TOP OF POLE OFF..TIM MILLER ON SITE.851 -161 BURNED OFF..ISOLATED AND GRD ON POLE 851-360. VER/SEF L3/HFP IDC XXXX
3651 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-12-01 04:13 | 2016-12-01 04:33 | 352 | 20 | H4155751 | 7040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS IN PLACE @ 37830262000034; REC. OPEN ON POLE 262-177/OPENED 262-177 AT 0405 TO CLOSE GOAB 262-C1-315 WHEN CLOSED BACK AT 0413 RECL 214-D-175 OPENED- OPENED SW AT 262-34 THEN CLOSED AT 0433 THEN CLOSED RECL 262-177 AT 0436/FOUND BAD CUTOUT ON POLE 262-C1-317.MADE REPAIRS..BUT STILL FEEDS THROUGH REC. 262-177 AND TAKING REC. OUT ON POLE 214D-175.ENERGIZED BACK TO SWITCH POLE 262-34.ISOLATED AND TAGGED TO DDC. NO GROUNDS PLACED.MAY HAVE BAD DEAD-END INSU DDC TAGS OFF 0853 VER/AWD AJB
3652 | Hazard | 3309003 | JEFF | VIPER | 2021-01-31 12:09 | 2021-01-31 19:03 | 17 | 414 | 4923421 | 7038 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse out on 418/34 patrolling 418/190 pole brunt off 40C4 double dead end need 4 man line crew 2 dead ends 7200V cutout and lighting arr. line fuse not isloted no grounds no tags send to G.Shouse Released by crew 077S03
3653 | Hazard | 3311103 | STINNETT | WENDOVER | 2014-07-14 21:16 | 2014-07-15 04:10 | 17 | 414 | 4245701 | 7038 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER NOT OPEN//ONLY FUSE ON 435-57//COD 17REPLACED BAD CUTOUT AND REMOVING TREES BURNING IN LINE VER/ARN AJB
3654 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-06-01 14:30 | 2012-06-01 19:55 | 123 | 325 | 4863711 | 7035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP TAGGED AND INSTALLED GROUND ON POLE 39831123A41539--RAYBURN GETTING CREW--CLOSED RECLOSER IN ON POLE 39831123A41513 AT 15:25--ONLY ONE CUSTOMER OUT--CAN WORK POLE FROM PARKING LOT OF CHURCH /RELEASED BY CREW 078S07.FETR 20:00 JEH/ REPAIRS COMP. POWER REST.@ 19:55//// 078H05 RELEASED BY CREW 078H05 COD-128 VER/HFP L3/HFP IDCC STP MISSING XXXX
3655 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-02-08 13:00 | 2008-02-08 13:12 | 586 | 12 | 52721-1 | 7032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3308502 THIS IS MAP MANIPULATION/THESE CUST ARE NOT OUT AT THIS TIME/USING MAP TO GET CUST LIST FOR NOTIFICATION. ..DKG/CUST INTERRUPTED AT 1300 HRS/RESTORED AT 1312 IDC XXXX
3656 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-03-01 05:04 | 2009-03-01 08:37 | 33 | 213 | 52680-1 | 7029 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400303- J . SHEPHERD CALL OUT TO HELP DAVE SAMMONS, BUT HIS TRUCK BROKE DOWN. POLE 1150-340 BURNT OFF AT CUTOUT. REMOVED TAP ON 1150-260 JUST 4 XFMRS OFF ALL OTHERS ON AT 7:25 LAST 4 XFMRS ON AT 8:37 DAVID SAMMONS 3/1/09 IDC XXXX
3657 | South Williamson | 3200302 | BELFRY | TOLER | 2012-07-13 23:52 | 2012-07-14 04:57 | 48 | 305 | 4719791 | 7026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT WENT BAD AND BURNED TOP OF POLE OFF REPAIRED AND EVERYONE BACK ON. IDC XXXX
3658 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-05-07 02:30 | 2022-05-07 13:05 | 20 | 635 | 4856391 | 7024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed - difficult location. Additional personnel enroute to assist.//Fuse toward 76-D-54 open on arrival lifted tap toward pole 76-D-53 and opened fuse toward 76-D-6 to safely change the cutout///Dispatched in accordance with KYPCo Late Night Callout Guidelines. Line fuse cutout failed - difficult location. Additional personnel enroute to assist. Crew onsite.Dispatched in accordance with KYPCo Late Night Callout Guidelines. Line fuse cutout failed - difficult location. Additio
3659 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-06-11 19:19 | 2011-06-11 23:59 | 40 | 280 | 4297911 | 7020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 40348583 //POLE TO BURNT OFF 40/5 POLE 333-103, TRUCKS TO POLE .FIRST PLACE ON THE LEFT UP NEBO, (621 ) NEED LINE CREW.POLE TO BURNT OFF 40/5 POLE 333-103, TRUCKS TO POLE .FIRST PLACE ON THE LEFT UP NEBO, (621 ) . OPENED SOLID BLADE ON POLE 333-73 AND PLACED GROUNDS.POLE TO BURNT OFF 40/5 POLE 333-103, TRUCKS TO POLE .FIRST PLACE ON THE LEFT UP NEBO, (621 DO NOT WORK POLE IF STILL SMOKING CALL FIRE DEPT TO PUT FIRE OUT PER LRM COD-40 ISO LF 38830309000101 VER/HFP L3/HFP IDC DCMT XXXX
3660 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-05-08 09:14 | 2008-05-08 12:40 | 53 | 206 | 58151-1 | 7018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//PAGED R MARCUM @ 0930// TAP POLE 10C28 55 CUSTOMERS BAVK ON AT 1122// VER/TOM IDCC CDC83, CNT58 XXXX
3661 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-09-04 12:19 | 2010-09-04 14:20 | 58 | 121 | 63581-1 | 7018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT OF HIGH SIDE OF SECTIONIZER MADE REPAIRES POWER ON @1420//COD 58// VER/DBM IDC XXXX
3662 | Hazard | 3310502 | HADDIX | CANOE | 2009-04-11 10:51 | 2009-04-11 17:05 | 84 | 374 | 51447-1 | 7016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502//POLE FIRE//VER/CRB IDC XXXX
3663 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-04-18 18:52 | 2009-04-18 20:05 | 96 | 73 | 58270-1 | 7008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONDUCTOR BURNT APART. REPAIRS COMPLETE. RESTORED AT 20:05. SH VER/KEP L3/KEP IDC XXXX
3664 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-11-03 02:15 | 2019-11-03 04:01 | 66 | 106 | 4286231 | 6996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DOL 967703 //B Ph stirrup burnt off on switch pole 38831121D00028//related to 4285781 //cod 66 //restored @ 0301 //
3665 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-03-13 04:04 | 2009-03-13 04:10 | 1166 | 6 | 57758-1 | 6996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN FEEDER BREAKER TO MAKE REPAIRS / 30 MINUTE OUTAGE / DIFFERENT CASE OF TROUBLE / VER/LDA IDCC 0405, CHANGED FROM SCHEDULED XXXX
3666 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-11-23 01:17 | 2013-11-23 08:08 | 17 | 411 | 4066591 | 6987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830386000059 BURNT OFF. BAD CUTOUT. VER/CRB L3/HFP IDC XXXX
3667 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-07-06 09:30 | 2015-07-06 11:37 | 55 | 127 | 4729811 | 6985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEF OUT POLE 963-71,WILL PTRL////////POLE 987-26,CUTOUT BROKEN,WILL REPLACE/MD MADE FOR SWTICH INSTEAD OF LINE FUSE ON 987-26/ADH// VER/ ADH AJB
3668 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2010-02-01 10:41 | 2010-02-01 19:38 | 13 | 537 | 61950-1 | 6981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | LINE FUSE POLE 52-9 IS OUT,WILL PATROL FOR FAULT AND RE-FUSE IF NOTHING IS FOUNDXARMS BROKE ON POLE 52-241,WILL NEED REPAIRED B4 POWER CAN BE RESTORED.HAVE TALKED TO PVILLE ABT THIS,WILL BE A WHILE PER T HALL.ELLIOT CREW IN AREA IS GOING TO MAKE REPAIRS//VER/CRB IDC XXXX
3669 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-10-29 10:29 | 2013-10-29 17:45 | 16 | 436 | 4971901 | 6976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 50-38 BURNED INTO,50C4,3PHASE LINE,SINGLE ARM.TRUCK FRIENDLY.BUCKET AND LINE TRUCK.NEED CREW RELEASED BY CREW 074S06 VER/CRB L/3 CRB IDCC TOF0931 PER VOICE RECORDER XXXX
3670 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-01-11 03:39 | 2017-01-11 07:24 | 31 | 225 | 4285661 | 6975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED AND BURNT POLE TOP OFF. FRAMED DOWN AND REPLACED CUTOUT. RESTORED @ 7:24. SH 38830875A30442 38830875C00196 VER/AWD L3/HFP XXXHFP AJB
3671 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-11-05 13:05 | 2010-11-05 19:55 | 17 | 410 | 53190-1 | 6970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD BURNED POLE OFF == CALLED FOR LINE CREW == OPEN ON POLE 37830272A40691 === OPEN LINE AT 1305 AND TRANSF IS ALSO == RELEASED BY CREW 077S03 COMPLTED JOB AT 1955//COD 17//ISO// VER/DBM IDC XXXX
3672 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2018-01-02 05:38 | 2018-01-02 10:25 | 26 | 287 | 4694971 | 6966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire down from pl 398-142 to 398-374 will open fuse on pl 399-16 pick up to that point from 374-93 dew to cold weather closed 37830374D00093 at 09:54 37830399000016 at 10:25 power restored
3673 | Hazard | 3302704 | HAZARD | KENMONT | 2013-04-14 12:19 | 2013-04-14 14:28 | 54 | 129 | 4008101 | 6966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURNED INTO ON POLE 37830321A00276 ==REPAIRED LOOP == OPEN STEP DOWN AT 14:05 TO 14:28 == POWER OK (SEE 4008311)//COD 54// VER/DBM IDC XXXX
3674 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-11-25 01:44 | 2017-11-25 05:15 | 33 | 211 | 4600691 | 6963 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire burned down in the stirrup
3675 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-07-27 18:22 | 2014-07-27 21:30 | 37 | 188 | 4295271 | 6956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD AND BURNED THE CROSSARM INTO ON THE LINE FUSE POLE 450-37, I WILL HAVE TO OPEN THE THREE RECLOSERS ON POLE 426-43 TO MAKE REPAIRS. I NEED A MAN TO HELP ME. // SEE 4296641 FOR REC OUTAGE TO MAKE REPAIRS /// CUTOUT WENT BAD AND BURNED THE CROSSARM INTO ON THE LINE FUSE POLE 450-37, I WILL HAVE TO OPEN THE THREE RECLOSERS ON POLE 426-43 TO MAKE REPAIRS. I NEED A MAN TO HELP ME.WE OPENED RECLOSERS ON POLE 426-43 AT 21:10 AND CLOSED AT 21:30 IN DIFFERENT ORDER//COD 37// VER/DBM AJB
3676 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2016-05-24 05:49 | 2016-05-24 11:55 | 19 | 366 | 4253431 | 6954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | *** SEE 4254351*** WILL WORK AT START TIME 5-24-16. WIRE DOWN @ 1151-102. NEED MANUAL TREE CREW ,LINE CREW,DEADEND HARDWARE FOR AUL & COPPER & INSULATORS FOR BOTH .POWER IS NOW RESTORED/ WIRE BROKE IN CLEAR @ 38831151D00102 SIDE TAP AND TO END OF LINE THE TRANSFORMER ON THAT POLE WAS STILL ON (19 CUST)/ ISO 38831151D00102/ COD 19/ 1155 RESTORED/ VER/BOW
3677 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-01-08 14:52 | 2019-01-08 17:55 | 38 | 183 | 4641131 | 6954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Bad recloser, bypassed and tagged for DDC
3678 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-12-08 15:17 | 2021-12-08 15:23 | 1158 | 6 | 4162741 | 6948 | TRANSMISSION LINE | EQUIPMENT FAILURE | CAPACITOR | DOL 1168245 Temporary Coalton Station Outage to Isolate failed 69kV CAP Bank AA at Coalton
3679 | South Williamson | 3411401 | DEWEY | INEZ | 2015-03-27 02:43 | 2015-03-27 17:42 | 33 | 899 | 4233541 | 6947 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 744-17//PATROLING//FOUND BROKE CUTOUT ON POLE 744-349 ON SIDE TAP THAT ISNT FUSED///I LIFTED HOT TAP ON POLE 744-157 TO ISOLATE TAGGED TO KYDDC///THIS SERVES A VACANT HOUSE THAT WAS BOUGHT BY STATE WHEN 4-LANE CAME THROUGH//IT DOES STILL HAVE ACTIVE METER ON IT///POLE BEHIND HOUSE WILL NEED LINE CREW//CLOSED LINE FUSE AT 5:52//ONLY ONE METER LEFT OUT //REMOVED METER //ACCOUNT FINALED OUT A YEAR AGO///REMOVED DDC TAG///COMPLETE/ TAP LEFT OFF/ LINE WILL BE REMOVED/ VER/BOW AJB
3680 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-10-13 04:42 | 2015-10-13 09:44 | 23 | 302 | 4343111 | 6946 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WITH SOLID BLADE BROKE @ POLE # 37830020000024 TIM HALL IS TO SEND CCONTRACTOR TO CHANGE ALL 3.//C PHASE COD 23// OPENED OCR ON OTHER TICKET 4343601 THIS OUTED THE OTHER 2 PHASES// VER/CRB //SEE 4343601 ALSO - COULD NOT VERIFY WITH SCADA OR BUSINESS OBJECTS, VER PER VOICE REC = L3/HFP AJB INLT PH C OUT.
3681 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-10-25 07:42 | 2008-10-25 15:25 | 15 | 463 | 58850-1 | 6945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3001002 - RELEASED BY CREW 078S05 @ 0956 REDIRECTED SERVICER TO A POLE FIRE.POLE FIRE AT 38830472000023, CREW HAS BEEN CALLED AND IS ON THE WAY. 40 CLASS 4 POLE, CUTOUT NEEDED. NO PLACE TO ISOLATE LINE.//CREW ON SITE @12:40//REPLACED 40/4 AND 10KVA ALSO TAP CROSSING ROAD P TOLLIVER COD-15 IDC XXXX
3682 | Hazard | 3309003 | JEFF | VIPER | 2018-09-27 10:57 | 2018-09-27 14:34 | 32 | 217 | 4166271 | 6944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | found failed insulator on manual pole 369-37, stepdown fuse out. repairs made, all power restored @ 14:34..p.hicks
3683 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-12-21 09:30 | 2019-12-21 11:41 | 53 | 131 | 4174421 | 6943 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Step down fuse blown on 191-209 will patrol// Fuse had pulled apart inside cutout door. I refused and restored power @ 11:41 Released by crew 076S03//MADE MD TO SHOW STEP-DOWN
3684 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-11-08 04:21 | 2019-11-08 11:20 | 41 | 419 | 4009791 | 6939 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DOL 969122///KYDDC TAGS//burnt off double deadend pole top 1146-144/ need pole top ext/ lifted hot tap on 1146-75/ Tagged & Grounded to DDC/ line fuse on 1146-686 restored @ 0600/ crew required/ 3329 bucket ideal b/c back yard location/ Released by crew 078H08,all cust restored @ 1120 please close ticket thanks.bt Released by crew 078H02 L3/HFP
3685 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-04-23 16:59 | 2019-04-23 18:41 | 68 | 102 | 4151231 | 6936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary broke while crew was installing new equipment/recl 487-162 on 1-shot/ 487-162 REC CLOSED @ 1841 ¦¦ I CHANGED THIS TO EQUIPMENT FAILURE BECAUSE PRIMARY BROKE AT ARMOR ROD WHILE CREW WAS INSTALLING A BASKET WHILE REPLACING A POLE = L3/HFP
3686 | Pikeville | 3407101 | TOPMOST | DEMA | 2013-05-23 16:35 | 2013-05-23 17:20 | 154 | 45 | 4173791 | 6930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREE BURNING LINE -- SERVICER OPENED RECLOSER TO MAKE SAFE UNTIL TREE COULD BE REMOVED / CUT I HAVE CUTOUT REPLACED EVERYTHING READY TO MAKE HOT. SEND COPY TO ENG PIKEVILLE CUTOUT BURNT ARM ABOUT HALF WAY INTO. EVERYTHING OK DOUBLE DEADEND. COD-154 VER/HFP L3/HFP IDC XXXX
3687 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-01-12 12:00 | 2012-01-12 13:30 | 77 | 90 | 4251301 | 6930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED LINE DUE TO POLE FIRE // COD 77 // OPENED FUSE ON POLE 155-51 FUSE NOT ON MAP BAD CUTOUT ON POLE 155 - 139 BURNED POLE WILL B ABLE 2 LOWER EVERYTHING .OPENED FUSE ON POLE 155-51 FUSE NOT ON MAP BAD CUTOUT ON POLE 155 - 139 BURNED POLE WILL B ABLE 2 LOWER EVERYTHING OFF AT 1200 RESTORED POWER AT 1330 CREW 077H01 .//COD 77// VER/DBM IDC XXXX
3688 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2013-05-15 21:01 | 2013-05-16 01:51 | 26 | 290 | 4119531 | 6913 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE BLOWN ON 801-23.PATROLLED LINE ALL CLEAR.RE FUSED CAME BACK OUT.TOOK 5 CSP XFMRS OFF LINE REFUSED CAME BACK OUT.CUT DEAD END 801-97 FUSE BACK IN 115.LIGHTNING ARRESTER BAD ON 116..REPLACED..RE CONNECTED DEAD END ON P 97 AT 145..FUSE BACK IN AT 151.. RELEASED BY CREW 076S01 VER ARN IDC XXXX
3689 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-05-12 02:13 | 2008-05-12 12:42 | 17 | 629 | 62336-1 | 6913 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE WORKED IN THE DAYLIGHT ON 5/12/08.POLE FIRE AT POLE 70-169 I ISOLATED ON POLE# 37830070000166 ALSO HAVE WIRE & POSSIBALLY POLE DOWN THIS IS ISOLATED AT POLE # 70-45 HAVE ALL ON BUT 3 COUSTOMERS. AT 08:12WILL GIVE INFO TO PIKEVILLE RELEASED BY CREW 074S04//3410502//VER/CRB IDCC CNT34 XXXX
3690 | Whitesburg | 3409503 | BURDINE | JENKINS | 2021-09-03 15:48 | 2021-09-03 16:36 | 144 | 48 | 4207561 | 6912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | crew found bad insulator on 382-A3-162 //opened RECL 358-D-306 // cod 144 // opened @ 16:02 // closed @ ____crew found bad insulator on 382-A3-162 //opened RECL 358-D-306 // cod 144 // opened @ 16:02 // closed @ 16:36 all power restored. p.hicks
3691 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2020-05-04 19:14 | 2020-05-04 19:35 | 329 | 21 | 4798481 | 6909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | crew replacing defective crossarmEnd of crossarm broke out and let a phase float. Also burnt neutral in two in a service. Made repairs. sh // opened GOAB at 1914 closed back at 1935
3692 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-05-03 16:55 | 2009-05-03 20:45 | 30 | 230 | H64345-1 | 6900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29637783 /// POLE 38831098B00692 OPENED SWITCHES AT 16:55, A & C PHASE OF RECLOSER OUT 267 CUST// WR # 29637783 /// POLE 38831098B00692 OPENED SWITCHES AT 16:55,CLOSED AT POLE 606 AT 17:05 ... ALL WORK COMPLETE / GXJ REST BACK ON @ 2045 L3/HFP IDC XXXX
3693 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-07-14 18:32 | 2022-07-15 12:30 | 16 | 1078 | 4491811 | 6898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 38821137B00376 waiting on tree crew to get out to transformer pole 38831137B00732 looks like broke cutout. got transformer cutout cut in the clear was taking line fuse out will need crew to come change it will have 3 customers off got line fuse back in at pole 38821137B00376 at 1:00.. Released by crew 079S02/// REPLACED CUTOUT AND RESTORED @12:30 Released by crew 074H06
3694 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-12-28 06:47 | 2009-12-28 12:50 | 19 | 363 | 59644-1 | 6897 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE LINE FUSE OUT--- BROKE CUTOUT AT LINE FUSE ALSO HAD TO CUT R/W IDC XXXX
3695 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-08-19 03:29 | 2011-08-19 10:40 | 16 | 431 | 4727971 | 6896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / WILL DISP TO DAY SERVICER PATROLLING. TREES GROWN UP INTO PRIMARY IN NEARLY EVERY SPAN BUT ALL WIRE APPEARS TO BE UP AND IN THE CLEAR NOW. HAVE TO WALK IN TO FUSE POLE. FOUND BAD LINE FUSE CUTOUT - DIFFICULT LOCATION. WORKING TO REPLACE. COMPLETE. RESTORED @ 10:40. SH COD-16 ISO LF 38830834A00043 VER/HFP L3/HFP IDC XXXX
3696 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-14 21:07 | 2015-02-15 03:30 | 18 | 383 | 4019471 | 6894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPEN LINE FUSE 254-B-4 FOR POLE BURNT INTO/, WILL HAVE TO REPLACE POLE VER/KEP // PER VOICE RECORDER FUSE OPENED @ 2107 - L3/HFP HFPC TOF1838 AJB
3697 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-09-18 14:23 | 2009-09-18 18:12 | 62 | 229 | 52304-1 | 6878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 31791620 // C PHASE OUT ONLY 58 CUSTOMERS // ENTERED MD FOR CUSTOMER WHO`S TRANSFORMER SHOWED CONNECTED TO `A` PHASE...HFPWR # 31791620 // C PHASE OUT ONLY 58 CUSTOMERS // ENTERED MD FOR CUSTOMER WHOS TRANSFORMER SHOWED CONNECTED TO A PHASE...HFP RESTORED LAST TWO CUST AT 18:12 RELEASED BY CREW 077H03 IDC XXXX
3698 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-02-11 12:58 | 2016-02-11 13:23 | 275 | 25 | 4689221 | 6875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | OPENING RECLOSER ON POLE 37830202C10208 TO SAFELY REPAIR CROSSARM BRACES.//ISO 37830202C10208 COD 275 VER/AWD /// VER TIMES PER VOICE RECORDER - NO DAVOX = L3/HFP XXXHFP AJB
3699 | Whitesburg | 3401301 | FLEMING | NEON | 2021-09-08 20:23 | 2021-09-09 10:40 | 8 | 857 | 4223481 | 6856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer fuse out on pole 355-D3-382. tried transformer and it came back out. looks like oi is coming out of it. bad 25 kva 7200. probably hold for crew until the morning Released by crew 077S11transformer fuse out on pole 355-D3-382. tried transformer and it came back out. looks like oi is coming out of it. bad 25 kva 7200. probably hold for crew until the morning. transformer replaced, power restored
3700 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-03-30 05:45 | 2014-03-30 08:14 | 46 | 149 | 4538961 | 6854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "A" PHASE COD-46 STIRRUP OFF AT POLE 1122-289 HOT LINE CLAMP MUST HAVE BEEN LOOSE BURNT STIRRUP SOME AND COME OFF OF THE STIRRUP. PLACED HOTLINE CLAMP BACK ON STIRRUP AND TIGHTENED UP EVERYTHING OK CLOSED SWITCH BACK IN AT 08:14 VER/KEP IDC XXXX
3701 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-08-19 07:49 | 2017-08-19 11:30 | 31 | 221 | 4278161 | 6851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 PHASE (A PHASE COD-31) OF HENDRIX BURNT DOWN AT POLE 785-273/ OPENED GOAB 785-D2-331 AT 1003/ MADE REPAIRS AND CLOSED 785-331 @ 11:30. SH RELEASED BY CREW 076S02 VER/KEP SJG
3702 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-03-11 10:43 | 2008-03-11 13:30 | 41 | 167 | 56181-1 | 6847 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116703// VERNON MULLINS AND CREW ENROUTE TO MAKE REPAIRS// LOUP BURNT OPEN AT POLE 19-C-137/ HOT TAP LOOP BURNT OPEN// SEND TO VERNON RELEASED BY CREW 078S07/CREW SECURING JOB SITE TO MAKE REPAIRS/FETR1400/VEM/RECLOSER 1147-187 OPEN AT 1252 BACK IN AT 1330/PLEASE CLOSE TICKET/THANKS/VEM RELATED TO ORDER 56218-1 (RECLOSER OUTAGE TO CLOSE LOOPS) VER/HFP XXXX
3703 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-04-23 09:10 | 2010-04-23 11:39 | 109 | 149 | 66573-1 | 6825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 34805387 //CREW REQUIRED TRUCKS OK ISOLATED ON 183-88/2 CUSTOMERS WILL STILL BE OFF #4 SOLID COPPER PRIMARY ON 182-320 BACK ON AT 1011 HRS/CREW ON SITE/VEM/LA FAILED /WIRE BACK UP/CHG C/O AND ARR/CUST RESYORED 1139/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP IDC XXXX
3704 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-03-28 13:46 | 2008-03-28 14:57 | 96 | 71 | 61619-1 | 6816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | 3401702// FOUND BAD CUTOUT ON SECTIONALIZER//3401702// I REPLACED A CUTOUT THAT HAD FAILED. //// VER/TOM IDC XXXX
3705 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-05-29 18:00 | 2015-05-29 20:25 | 47 | 145 | 4481941 | 6815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 205-448 REC. OUT. HAVE BAD LINE C/O ON POLE 229-48//// LINE C/O CHANGED REC. BACK ON. COMPLTED/ ISO 37830205D00448/ COD 47/ VER/BOW AJB
3706 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-04-06 18:45 | 2022-04-06 21:10 | 47 | 145 | 4732481 | 6815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT ON POLE 37830177D00001//COD 47//A manual loop is burnt in the clear on pole 177-D-1, I will be opening a solid blade one pole back on 177-D-58 to make repairs.COD STILL 47
3707 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-04-03 11:05 | 2015-04-03 11:35 | 227 | 30 | 4264001 | 6810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | RELATED TO 4262101/ OPEN 38830235000173 ALL 3 PHASES IN ORDER (227 CUSTOMERS MORE)// 173 BACK IN @ //CREW REQUIRED//WILL NEED 600A CUTOUT//TRUCK OK(BIG BUCKET, BUT WILL NEED EXTRA MEN TO FLAG TRAFFIC)// ALL 3 RECLOSERS CLOSED IN AT 1135 L3/DKGXXXX PER VOICE RECORDER AJB
3708 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-07-09 10:14 | 2014-07-09 14:30 | 105 | 256 | 4218661 | 6808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OUT ON POLE 184-438, PATROLLING LINE, FOUND BAD CUTOUT ON POLE 184-70, REMOVED HOT TAP, GOING BACK TO RECLOSER. CLOSED RECLOSER AT 11:17 HRS, WILL NEED BIG BUCKET, CUTOUT AND ARRESTOR, T-BRACKET TO RESTORE FINAL CUST RELEASED BY CREW 077S02 COD105// VER/ADH AJB
3709 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-12-23 13:18 | 2014-12-23 17:30 | 27 | 252 | 4877061 | 6804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 COD FROM BEGINNING//@ 1318 STEPDOWN OPENED COD 27// FUSE IS OPEN ON 524-168, POLE 524-221 BURNT OFF DUE TO BAD CUTOUT, LINECREW REQUIRED WILL NEED 4 MOEPADS TO REACH POLE WITH TRUCK RELEASED BY CREW 078S11 VER/CRB AJB SEE H4877061 FOR INLT XFR OUTAGE.
3710 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2012-06-19 20:01 | 2012-06-19 20:37 | 189 | 36 | H4932771 | 6804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE 327 CUST // RISER BURNT OFF OF TWO HOLE PAD CONNECTOR ON GOAB SWITCH ON 7-C-5..NEED CREW.WILL HAVE TO DROP STATION BREAKER TO REPAIR...//..JUSTICE, HOMER & MATNEY, EDWARD OPENED CB @ 2001 INTERUPTING AN ADDITIONAL 260 CUSTOMERS. // CLOSED CB @ 2037 RESTORING ALL CUSTOMERS. VER/HFP L3/HFP IDC XXXX
3711 | Pikeville | 3402002 | KEYSER | STONECOAL | 2021-06-10 00:59 | 2021-06-10 12:17 | 10 | 678 | 4700891 | 6780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | R.O.W. really bad @this location, line is all on hillside, will need a manual R.O.W. crew first thing in the a.m., rain and fog is too dangerous to attempt in the dark. Line fuse open @1128-68, checking. Released by crew 074S05R.O.W. really bad @this location, line is all on hillside, will need a manual R.O.W. crew first thing in the a.m., rain and fog is too dangerous to attempt in the dark. Line fuse open @1128-68, checking. Found a bad dead end insulator @38831128000146, will be making repa
3712 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-09-29 19:57 | 2012-09-30 01:05 | 22 | 308 | H4099521 | 6776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEAD END INSULATOR BROKE AT POLE 397-37, ONE SPAN OF PRIMARY DOWN TO POLE 38. WILL NEED 2 MEN, DEAD END INSULATOR 15KV AND SHOE AND 50 FT. 6ACW WIRE. RECLOSER IS IN BUT WILL HAVE TO OPEN TO MAKE REPAIRS. WILL ALSO NEED A MANUAL TREE CREW. //C.SEXTON & J.BAKER TO ASSIST// J. COMBS GETTING R/W CREW // OPENED REC 421-130 @ 2345 (22 CUST), CLOSED REC @ 0105 //VER/GAH IDC XXXX
3713 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-08-08 14:54 | 2022-08-08 16:45 | 61 | 111 | 4705191 | 6771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced hotline clamp power restored at 16:45
3714 | South Williamson | 3200302 | BELFRY | TOLER | 2019-12-10 18:14 | 2019-12-10 21:03 | 40 | 169 | 4143051 | 6760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse blown on989d39.i think primary is off of arm pin and laying on arm,NTA. i will tr too make repairs. repaired wire laying on arm. restored power at 21:03./cod 40
3715 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-04-05 09:30 | 2011-04-05 11:40 | 52 | 130 | H65052-1 | 6760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSERS ON 1036-B1-315 NOT OUT...BURNT OFF CROSSARM (BAD XFMR CUTOUT) BACK ON 1012-B-150...PHASE C OFF OF ARM...CROSSARM & CUTOUT NEED REPLACED....CREW REQUIRED...TRUCK APPROACH....C PHASE RECLOSER LOCKED OUT ON POLE 1012-A-229...OTHER 2 RECLOSERS STILL HOT....WILL HAVE TO BE DE-ENERGIZED TO REPLACE ARM...//..NEED 8 CROSS ARM, 2 BRACES, 3 ARM PINS, 3 INSULATORS, & CUTOUT...// RELEASED BY CREW 080S01 THIS TICKET NEEDS TO ROLL UP INTO 65052 WHERE WE HAVE C PHASE RECLOSER LOCKED OUT ON 1012A229 IDC XXXX
3716 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-11-15 17:29 | 2008-11-16 01:00 | 84 | 451 | 65473-1 | 6759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003// STS WR 27304867 POLE FIRE AT 183-385, B PHASE REC ON POLE 183-D-6091 OUT CC 84 ISOLATED AT 38830183D000103001003//POLE FIRE AT 183-385, ISOLATED AT 38830183D00010, REC, BACK ON AT 18:45 *** BRENT IS ON JOB SITE AND WILL HELP CREW. VER/PDP IDC XXXX
3717 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-06-24 16:04 | 2010-06-25 04:35 | 9 | 751 | 56933-1 | 6759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW ON SITE TCM// VER/LDA IDC XXXX
3718 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-11-17 08:53 | 2011-11-17 10:42 | 62 | 109 | 4086441 | 6758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE / // COD-62 ISO OCR 37830255D00200PATROLLING LINE, FOUND BAD CUTOUT ON POLE # 255-142, NOT SERVING ANYTHING, CUT IN CLEAR COD-62 ISO OCR 37830255D00200 VER/HFP L3/HFP IDC XXXX
3719 | Hazard | 3309301 | VICCO | REDFOX | 2016-03-25 15:44 | 2016-03-25 19:15 | 32 | 211 | 4882541 | 6752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON STEPDOWN 37830325A20345, NEED 1 MAN, 7200 & 19.9 CUTOUT AND 2 TEE BRACKETS AND BIG BUCKET./ ISO 37830325A20345/ COD 32/ VER/BOW L3/HFP XXXHFP AJB
3720 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-09-09 08:45 | 2018-09-10 12:53 | 4 | 1688 | 4062921 | 6752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need 50 kva 7200 tran and new risers, c/o and fiberglass t bracket --crew req nbt--per conversation with cust may try back yard bucket (go in from barn out back along fence) Released by crew 078S01/opened xfmr/wil work in daylight/spoke with cust/resend to mullins Released by crew 078H14need 50 kva 7200 tran and new risers, c/o and fiberglass t bracket --crew req nbt--per conversation with cust may try back yard bucket (go in from barn out back along fence) Released by crew 078S01/opened xfmr/w
3721 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2018-07-23 22:21 | 2018-07-23 22:36 | 450 | 15 | 4845131 | 6750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened recloser on 37830231A20329 to safely replace cutout on order 4841441.//cod 501
3722 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-08-02 07:37 | 2008-08-02 12:07 | 25 | 270 | 63751-1 | 6750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3001201//LINE FUSE OUT ON POLE 38830045B22549 STEVE PLEASE LET ME KNOW THE FUSE SIZE SO I CAN GET IT ON THE MAP..THANKS..HFP--BAD INSULATOR-CALLED CREW - RELEASED BY CREW 078S07//REPLACED 12KV PIN INSULATOR NO TRUCKS & TRIMNED TREES FROM ROW P R TOLLIVER BACK ON AT 12:00 ENTERED MD - HFP .... COD 25 VER/HFP IDCC PN2547 XXXX
3723 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-02-03 08:34 | 2014-02-03 13:57 | 45 | 323 | 4343151 | 6747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND TOP OF POLE BURNTED OFF AT THE END OF MEADE HOLLOW, TAKE RIGHT FORK TO THE END, I CUT LOOP ON POLE 1146-176, LINE IS NOT GROUNDED OR TAGGED, WELL BE CREW REQ, I RESTORED ALL CUST BUT ONE, CLOSED IN LINE FUSE AT 1100 ON POLE 1146-7 NO TRUCKS TO POLE EITHER ONE RELEASED BY CREW 078S06 LOWER EQUIPMENT UNTIL GOOD WEATHER TO REPLACE POLE VER/CRB L3/HFP IDC XXXX
3724 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2018-05-04 12:07 | 2018-05-04 15:00 | 39 | 173 | 4306141 | 6747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolled line found nothing wrong, returned to l/f, it was not blown, looking at it with bincolar, look like the top of the c/o is bad, CREW REQ, AND AWP, will have to sit up on rt.7 can use truck, at the mouth of shutlz rd and rt. 7 on 1500 L3/HFP
3725 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-10-14 18:20 | 2012-10-14 19:55 | 71 | 95 | H4139371 | 6745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY NEUTRAL AND 1 HOT OPEN WIRE SECONDARY HAS BURNT DOWN, CUTOUT ON XFMR HAS ALSO BURNT UP, CALLING FOR HELP // MULLINS & SHOUSE ****CREW OPENED SWS AT POLE 130-135 TO MAKE REPAIR..PRIMARY NEUTRAL AND 1 HOT OPEN WIRE SECONDARY HAS BURNT DOWN, CUTOUT ON XFMR HAS ALSO BURNT UP, CALLING FOR HELP, OPENED MAIN LINE TO MAKE REPAIRS. ALL POWER RESTORED VER/HFP L3/HFP IDCC DUP TO OPEN SWITCH XXXX
3726 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-01-18 10:12 | 2011-01-18 11:15 | 107 | 63 | 62186-1 | 6741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EMERGENCY OUTAGE TO ALLOW CREW TO REPLACE DEFECTIVE CUTOUT // COD-107 ISO LF 38820941B00071 VER/HFP L3/HFP IDC XXXX
3727 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-02-01 20:52 | 2013-02-02 00:10 | 34 | 198 | 4784061 | 6732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT, NEED 1 MAN AND BIG BUCKET AND 7200 CUTOUT. === POWER RESTORED. 00:10 VER/KEP IDC XXXX
3728 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-11-03 20:59 | 2010-11-03 22:05 | 102 | 66 | 51490-1 | 6732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD IN FRONT OF MIKE RAY ROBINSONS HOUSE PER WILLIE ROBINSON // CUTOUT BROKE DOWN ON POLE 167-293 AND OPENED RECLOSER AT POLE 167-598. I AM GOING TO REPLACE CUTOUT. I CHANGED CUTOUT AND CLOSED RECLOSER IN AT 22:05.//COD 102// VER/DBM IDC XXXX
3729 | South Williamson | 3200302 | BELFRY | TOLER | 2009-06-02 18:16 | 2009-06-02 20:13 | 112 | 117 | 61063-1 | 6732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, BAD CUTOUT AT POLE#1038-164, RECLOSER OUT ON POLE#1039-A-17, CLOSED AT1914, ALL BUT 2 OR 3 CUST VER/KEP L3/KEP IDC XXXX
3730 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-02-27 23:36 | 2011-02-28 03:00 | 33 | 204 | 63601-1 | 6732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIM AND NEUTRAL DOWN,IS 6A.HELP ENROUTE/////NOTE NEW FETR///////MADE REPAIRS AND RESTORED. CC= 33, BAD SLEAVE AT POLE 987-20 IDC XXXX
3731 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2012-08-11 02:13 | 2012-08-11 02:31 | 374 | 18 | 4927031 | 6732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 2206403--**KY SIDE CUSTS - 374 CUSTS TOTAL**--RELATED TO 4926571--RE-OPENED CB TO SAFELY CLOSE IN 600A SWS IN RELATED OUTAGE--CC410--OPENED AT 0213--CLOSED AT 0231 //VER ANM IDC XXXX
3732 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-03-25 13:23 | 2012-03-25 14:07 | 153 | 44 | 4615311 | 6732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP APPEARS TO HAVE BURNT OPEN ON DOUBLE DEADEND 955-35. ONLY FOUR CUSTOMERS AFFECTED. OPENED REC 955-508 @ 13:23. REPLACED INSULATOR AND LOOP. CLOSED BOTH RECLOSERS ON 955-508 @ 14:07 RESTORING ALL CUSTOMERS. SH //VER/CRB IDC XXXX
3733 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-02-07 11:38 | 2009-02-07 13:45 | 53 | 127 | 56424-1 | 6731 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW ON SIGHT REPAIR 6A COPPER// VER/TOM L3/TOM IDC XXXX
3734 | Hazard | 3302703 | HAZARD | HAZARD | 2017-07-24 13:32 | 2017-07-24 13:42 | 673 | 10 | 4173381 | 6730 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | DOL 759463// RELATED TO 4170481//OPENED N.O. SWS 37830296A30445 TO PERFORM OUT OF PHASE SWITCHING TO PUT CKTS BACK NORMAL // OPENED 1332// CLOSED CB C AT HAZARD @ 1342// VER/DBM L3/HFP XXXHFP SJG
3735 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-01-07 23:06 | 2014-01-08 05:00 | 19 | 354 | 4256581 | 6726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 149-24 WIRE DOWN CREW REQUIRED PRIMARY ONLY/NO. 4 COPPER/ISOLATED TAGGED AND GROUNDED AT POLE 149-9//REYNOLDS, HOWARD, & MORGANPOLE 149-24 WIRE DOWN CREW REQUIRED PRIMARY ONLY/NO. 4 COPPER/ISOLATED TAGGED AND GROUNDED AT POLE 149-9 RELEASED BY CREW 078S03 VER/SEF IDC XXXX
3736 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-09-24 23:44 | 2013-09-25 09:55 | 11 | 611 | 4885211 | 6721 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILLL BE DISPATCHED AT REG WORK TIME ON 9/25/13 PLEASE HAVE TECH CHECK EQUIPMENT ON SITE ,WE HAVE LINE FUSE OUT ON POLE 382-58. THE WIRE IS PULLED OUT ON POLE 382-58,WERE GOING TO ISOLATE ON POLE 382-57 VER/CRB L/3 CRB IDCC FEC49 XXXX
3737 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-10-17 12:12 | 2008-10-17 16:42 | 34 | 270 | 56568-1 | 6720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830249C00296 BURNED INTO, LIFTING CLAMP AT POLE 37830249C00045 FOR A PARTIAL RESTORE//WE ALSO FOUND PRIMARY AND NEUTRAL WIRE DOWN AT POLE 37830249C00041//PARTIAL RESTORE COMPLETE AT 15:20//3301402//VER/CRB IDCC CNT38 XXXX
3738 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2015-09-22 10:00 | 2015-09-22 11:00 | 112 | 60 | 4259521 | 6720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | EMERGENCY OUTAGE NECESSARY TO ALLOW CREW TO REPLACE DEFECTIVE SET OF CROSSARMS // COD-112 ISO OCR @ 38831053B00230.PULLED OFF @ 10:00 BACK ON @ 11:00 VER/HFP L3/HFP AJB
3739 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-03-30 06:40 | 2008-03-30 09:20 | 42 | 160 | 62073-1 | 6720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201//, ON SITE, CHECKING TROUBLE, BAD CUTOUT ON POLE#722-D-125, CALLED R MARCUM FOR HELP / COD-42 // VER/LDA IDC XXXX
3740 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-03-18 09:17 | 2008-03-18 11:57 | 42 | 160 | 58114-1 | 6720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3407401// 1 PHASE ON GROUND AND GUY WIRE BURNED APART, OPEN AT POLE 1098-273 AT 09:35, #4 AA PULLED APART IN MID-SPAN...ALL WORK COMPLETE / GXJ IDC CNT144 XXXX
3741 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2022-08-03 19:46 | 2022-08-04 11:45 | 7 | 959 | 4671711 | 6713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER NEEDS REPLACED PER SHANE TACKETTBAD CSP TRANSFORMER ,Will be Replacing..BAD CSP TRANSFORMER ,Will be Replacing..Restored 11:45.
3742 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-04-05 07:25 | 2011-04-05 23:24 | 7 | 959 | 65265-1 | 6713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOTTOM OF CUTOUT BROKE INTO & FELL DOWN OUT OF WAY --NEED CUTOUT & ARRESTER & BRACKETT CAN REACH WITH BUCKETT THIS IS AT THE GULF SERVICE STATION RELEASED BY CREW 074M02 COD-7 ISO TF 37830139A10060 VER/HFP L3/HFP IDC XXXX
3743 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-08-06 03:07 | 2019-08-06 08:00 | 27 | 293 | 4844761 | 6711 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | patrolling line/ load side lead burnt off at pole 223-B-30/line fuse blown on 223-101, connection burnt off line fuse on pole 223-30, will need 19.9 kv cutout, one man and big bucket truck. dont know yet what blew fuse on 101patrolling line, line fuse blown on 223-101, connection burnt off line fuse on pole 223-30, will need 19.9 kv cutout, one man and big bucket truck. dont know yet what blew fuse on 101. fuse back in on pole 30 at 07:00 hrspatrolling line, line fuse blown on 223-101, connecti
3744 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-02-02 18:21 | 2019-02-02 18:34 | 516 | 13 | 4749471 | 6708 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - NON LTC | short outage for mobile installation at Coalton station ¦¦¦ VERIFIED TIMES PER SCADA & DOL & SOS 19-070906 REV 1 = L3/HFP
3745 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-06-08 11:30 | 2010-06-09 03:28 | 7 | 958 | 58748-1 | 6706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3402001 ARRESTER BLEW, SEND THIS TICKET TO DAVE SAMMON CREW RELEASED BY CREW 074S05 ARE REPLACING PRIMARY U.G. CABLE AND PADMOUNT.SEND THIS TICKET TO DAVE SAMMON CREW RELEASED BY CREW 074S05 ARE REPLACING PRIMARY U.G. CABLE AND PADMOUNT. REPAIRS MADE ON AT 03:28 D SAMMONS IDCC CDC83 XXXX
3746 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-08-12 14:55 | 2013-08-12 17:24 | 45 | 149 | 4654811 | 6705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PER STEVE BREWER THIS IS THE CHARLES RUSSELL ELEMENTRY SCHOOL - RESOURCE CENTER - PHASE DOWN & HILL SIDE ON FIRE//1 SPAN OF PRI NEUTRAL DOWN ON POLE 70-675//SERVICER OPENED FUSE @ 1455 // COD 45/// BURNT DOWN IN MID SPAN NO TRUCK TO POLE HOLD FOR GREWS RELEASED BY CREW 078S08//COD 45// VER/DBM L3/HFP
3747 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-07-18 20:40 | 2014-07-18 21:30 | 134 | 50 | 4260511 | 6700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 1309 INSULATOR DAMAGED IN HOUSE FIRE--WILL DROP LINE ON POLE 1108-1 FOR ABOUT 1 HOUR TO REPLACE WHEN HELP ARRIVES ARM OK NOW OPENED AT 2040 CLOSE AT 2130 RELEASED BY CREW 077S06//COD 134// VER/DBM AJB
3748 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-02-17 11:21 | 2017-02-17 12:30 | 97 | 69 | 4404281 | 6693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OOPENED RECLOSER ON 38830852B30409 TO SAFELY REPLACE POLE 38830853000007.// OPENED AT 11:21// REPAIRING NOW// REPAIRS COMPLETE, CLOSEDPOLE 852-409 AT 12:30, RESTORNG AL CUSTOMERS VER/AWD L3/HFP XXXHFP AJB
3749 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-01-29 20:18 | 2009-02-03 11:45 | 1 | 6687 | 51704-1 | 6687 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST STILL OUT PER COINS CALL 1-31/RLL RELEASED BY CREW 078E04 ///// BAD 15 KVA 7.2 TRANSFORMER N.T.A. WILL NEED LINE CREW PER BUZZ BARKER TRUCK 2105 RELEASED BY CREW 081H03 CALLED CUSTOMER 2/2 @ 2054 THEY STILL DO NOT HAVE POWER, APO, BT
3750 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-24 18:55 | 2009-09-25 10:50 | 7 | 955 | 61691-1 | 6685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | LINE FUSE IS OUT,WILL PATROL.RE-FUSED,DID NOT STAY IN.TIM HALL SAID TO HOLD UNTIL MORNING AND WE CAN SEE LINE AND SNAKES THAT RAIN HAS BROUGHT OUT RELEASED BY CREW 074S06/TIRE WIRE BROKE ON POLE 934-9 AND CONDUCTOR LAYING ON POLETOP / RETIED CONDUCTOR AND CLOSED IN LINE FUSE VER/KEP L3/KEP IDC XXXX
3751 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-06-04 02:53 | 2015-06-04 11:12 | 37 | 499 | 4509071 | 6683 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE DOWN FROM POLE 37830091A00052 TO 51, OPENED B PHASE SWITCH AT 91A-56// CLOSE RECLOSER @ 0452 RESTORING 31CC// 37COD// 6 REMAIN OUTAGED UNTIL REPAIRS MADE//TOM . CREW REQUIRED: 2 MAN MANUAL ROW CREW, FLAGGERS, 3 MAN LINE CREW, 50 FT # 4 CU, TRUCK ACCESS . POLE 91-56 OPENED A AND C PHASES AT 10:15 . RESTORED ALL CUSTOMERS AT 11:12 , ALL WORK COMPLETE / GXJ // VER/ ADH L3/HFP HFP AJB
3752 | Hazard | 3309302 | VICCO | JEFF | 2012-08-07 16:07 | 2012-08-07 18:54 | 40 | 167 | 4908711 | 6680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELEASED BY CREW 077S03 == LOOP ON POLE 37830346A00215 LAYED DOWN ON TOP OF TRANSF == INSTALLED RIDGE PIN == REFUSED POWER OK ///VER/CRB L/3 CRB IDC XXXX
3753 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2015-03-10 10:09 | 2015-03-10 11:55 | 63 | 106 | 4176071 | 6678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ 1109 PATROLLING LINEL/F BLOWN ON 24-B4-227// BAD CUTOUT ON 24-483/WILL CHANGEL/F BLOWN ON 24-B4-227// BAD CUTOUT ON 24-483/WILL CHANGE// POWER RESTORED @ 11:55/ ISO 37830024B40227/ COD 63 AJB
3754 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2020-04-02 10:58 | 2020-04-02 13:04 | 53 | 126 | 4554501 | 6678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | found bad arrester on csp xfmr. will refuse on pole 18-d4-589.refused @ 13:04
3755 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-09-29 19:06 | 2017-09-29 19:27 | 318 | 21 | 4400571 | 6678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C PHASE CONDUCTOR HAS FALLEN OUT OF CROSSARM ON 5-99 DUE TO ARM BEING ROTTEN CREW REQUIRED 2 MEN AND FOREMAN TRK APP 7200 NEED 8 FT CROSSARM AND 2 ARM PINS AND INSULATORS 1906-1927 37820004C10345. RELATED TO 4400131. 37820005000099. VER/AWD ACB
3756 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-01-25 16:43 | 2010-01-25 22:54 | 18 | 371 | 59695-1 | 6678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT 47-318 "A" PHASE COD-66 VER/KEP L3/KEP IDC LOOKS LIKE PH C NOT A CHANGED COUNT FROM 66 XXXX
3757 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-11-03 22:29 | 2018-11-04 00:15 | 63 | 106 | 4361011 | 6678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfm fuse blown will refuse// Refused xfm @ 00:15 and restored service 1 customer
3758 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2015-07-27 07:11 | 2015-07-27 10:27 | 34 | 196 | 4945311 | 6664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B&C OPEN @45-C4-5687,BAD 12KV C/O @ 45C45793. , B PHASE XFMER OPEN @ 45C45793. CREW REQD. RELEASED BY CREW 078S07/CREW ON SITE/FETR1115/VEM/REPAIRS MADE AND ALL CUST RESTORED 1027/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH L3/HFP HFP FP38830045C45687 AJB
3759 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2020-01-10 17:23 | 2020-01-10 20:23 | 37 | 180 | 4231711 | 6660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole# 901-5007 rotten. opening up 3 40t lf on p# 901-5008 to transfer #6 sol cu pri. windsteam on site hand digging pole hole. FETR 20:30 LRM opened line @ 18:00LRM pwr restored @ 20:23 checking volatage on new xfmr please close ticket LRM/// transformer restored @2034
3760 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2019-06-27 14:30 | 2019-06-27 14:56 | 286 | 26 | 4606481 | 6660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DOL Case 934253///recl that was being put on line failed while CB was on non-reclose
3761 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-01-03 22:29 | 2009-01-04 01:00 | 44 | 151 | 51136-1 | 6644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CHANGED BAD INSULATOR ON POLE 496-83 L3/KEP IDC XXXX
3762 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-05-08 10:14 | 2018-05-08 13:16 | 38 | 182 | 4323341 | 6640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1057-149 NEARLY BURNED INTO.CREW ENROUTE TO MAKE REPAIRS.OPND RECLR 1057-240@10:14,OPEN FUSE@MOUTH@10:24(POLE 1057-37) closed line fuse @ 1303 // closed recl @ 1316
3763 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-01-26 12:37 | 2011-01-26 14:00 | 80 | 83 | 64594-1 | 6640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38581964PATROLLING LINEPATROLLING LINE, CUTOUT BAD ON INACTIVE XFMR COD-80 ISO RECL 37830230B00256 VER/HFP L3/HFP IDC XXXX
3764 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-04-04 06:13 | 2008-04-04 10:10 | 28 | 237 | 63706-1 | 6636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3000201// ONE SPAN #4 SOLID COPPER DOWN FROM POLE 331-41 TO 331-42. NEEDS LINE CREW.//COD 28// VER/DBM IDC XXXX
3765 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-01-17 02:00 | 2012-01-17 06:15 | 26 | 255 | 4266151 | 6630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LOOP LAYING AGAINST POLE 37830177B30488, NEED 1 MAN, BIG BUCKET, POLE TOP PIN AND INSULATOR. CALVIN WILLIAMS TO ASSIST // //VER/GAH IDCC PN318 XXXX
3766 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2011-04-20 09:39 | 2011-04-20 14:27 | 23 | 288 | 61087-1 | 6624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 2150502--WR#39644533 // B PHASE RECL 941C-277 // CC 12 (ACCORDING TO FIELD PERSONEL MAP SHOWS 20) // PRIMARY BELOW NEUTRAL AT 941C-217 DUE TO BROKEN POLE // WILL LOWER NEUTRAL UNTIL FINAL REPAIRS CAN BE MADE IDC XXXX
3767 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-03-23 17:39 | 2011-03-23 22:27 | 23 | 288 | 57314-1 | 6624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2- 65T A&B PH LINE FUSE OPEN ON POLE 38830069A10254. THE B PH C/O AND DOOR WILL NEED TO BE REPLACED ITS BEEN ON FIRE TONIGHT // RAN OUT THE TAPS ALL LOOKS OKAY///TRUCK TO POLE MAY NEED FLAGGING.......CPS RELEASED BY CREW 078E04//VER/CRB IDCC CNT34 XXXX
3768 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-04-22 09:23 | 2012-04-22 14:24 | 22 | 301 | 4693821 | 6622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE--NEED 3 MAN PRC CREW TO REPLACE BAD CUTOUT ON POLE 38830020C24507 RELEASED BY CREW 078S07// CHANGE CUTOUT BETWEEN PHASES CUTTING TREE OUT OF WAY COMPLETE @ 14:24//COD 22// VER/DBM IDC XXXX
3769 | Hazard | 3311103 | STINNETT | WENDOVER | 2017-10-08 16:19 | 2017-10-08 16:32 | 509 | 13 | 4422621 | 6617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OFF 1619 ON 1632 VER/ARN L3/HFP HFPC CDC98 ACB
3770 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-12-23 21:15 | 2022-12-23 22:18 | 105 | 63 | 4335061 | 6615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse melted out at 335-B-205,Up fuse to 65 and Restored service at 22:18..
3771 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2018-12-17 07:13 | 2018-12-17 08:40 | 76 | 87 | 4573081 | 6612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE RISER HOT CLAMP BURNT OFF @ RECLOSER // 76 CUST ON @ 0840
3772 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2009-09-25 08:06 | 2009-09-25 12:30 | 34 | 264 | 62023-1 | 6611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO ISOLATE BURNING POLE ON ORDER 61969 RESTORED AT 1230 ADDED 25T FUSE TOWARDS POLE#6119 FOR PARTIAL VER/KEP L3/KEP IDCC FP NULL XXXX
3773 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-03-04 18:15 | 2015-03-05 21:47 | 4 | 1652 | 4101681 | 6608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLDING TILL 3-5-15 DUE TO HIGH WATER BAD TRANSFORMER CUTOUT. I WILL TRY TO GET THE FIRE DEPT TO FLAG THE ROAD SO I CAN REPLACE THE CUTOUT, THE TRANSFORMER POLE IS IN VERY BAD SHAPE TO CLIMB. BAD 50 KVA 19.9, NEED TRANSFORMER, CUTOUT AND BRACKET, AWP, TWO MEN AND A BUCKET. RELEASED BY CREW 079S02HOLDING TILL 3-5-15 DUE TO HIGH WATER BAD TRANSFORMER CUTOUT. I WILL TRY TO GET THE FIRE DEPT TO FLAG THE ROAD SO I CAN REPLACE THE CUTOUT, THE TRANSFORMER POLE IS IN //COD 4//MD FILED//ISO// VER/DBM
3774 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2015-07-15 12:14 | 2015-07-16 10:15 | 5 | 1321 | 4877551 | 6605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED FLAGGERS CHANGE OUT BAD XFMR REPLACED XFMR RESTPRED POWER AT 10:15
3775 | Hazard | 3303902 | LESLIE | WOOTON | 2010-11-24 06:15 | 2010-11-24 10:50 | 24 | 275 | 59201-1 | 6600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | STS WR # 37877837 // PATROLED LINE COULDNT FIND FAULT, GOING TO REFUSE LINE,..367-03 IS NOT BLOWN, PATROLING BACK TO NEXT ISOLATING DEVICE, OPENED RECLOSER ON 366-51 @08:06 HRS, ALL CUSTOMERS RESTORED @ 1050 IDCC CNT18 XXXX
3776 | Hazard | 3309003 | JEFF | VIPER | 2018-07-25 19:04 | 2018-07-26 00:15 | 42 | 311 | 4857261 | 6597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 span primary down line still hot up to pole 37830392000071 cod 23 out/ opened stepdown outaging 19 addl from 2226-2304//l/f on 37830392000084 leaving 5 cc out unti l due to 2nd tree down// Released by crew 077H09//cod 42 L3/HFP
3777 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2022-06-02 20:50 | 2022-06-03 05:17 | 13 | 507 | 4009021 | 6591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire down between pole 307-124 and pole 307-70. 1 span of primary only. #2 wire needed for sleeving. 2 men and big bucket needed to make repairs. bad cutout on pole 307-76. wire burnt down from pole 307-63 to 307-69. primary only. when closed fuse wire burnt down because of bad cutout//cod 13
3778 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-06-20 10:00 | 2008-06-20 10:27 | 244 | 27 | 51056-1 | 6588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPENED RECLOSER SO CREW COULD SAFELY REPLACE CROSSARM/ SWITCHED TO KEEP MOST CUST ON VER/KEP IDC XXXX
3779 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-11-02 23:30 | 2009-11-03 00:06 | 183 | 36 | H56728-1B | 6588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP LEAD ON B PHASE-OPENED A AN C PHASE UP AT 2301 TO MAKE REPAIRS-CALLED CREW// CLOSED C AN B PHASE IN AT 2318-INSULATOR FAILED-B PHASE FUSE BLEW AT 2330-OPENED A PHASE AT 2338 // IDC XXXX
3780 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-09-08 15:31 | 2010-09-08 17:00 | 74 | 89 | 64658-1 | 6586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "B" PHASE ON RECLOSER OPEN PHASES ROLL ON OUT THE LINE CALLING IT COD-83/OPENED 2ND RECLOSER AT 1635 TO MAKE REPAIR ON CLAMPI REPLACED A HOT LINE CLAMP THAT HAD FAILED. VER/KEP L3/KEP IDC XXXX
3781 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-07-27 01:27 | 2012-07-27 12:25 | 10 | 658 | 4840271 | 6580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078S08. CO OPEN ON 38830116B00545. SMALL LIMB ON PRI. IN LAST SPAN. NO TRUCK. NEED BUCKET TO GROUND. CUTOUT HAS BEEN REFUSED AND IS READY TO CLOSE. SGM. RELEASED BY CREW 078E01,, FOUND BAD ARRESTER AT POLE 38830116B00567, REPLACED ARRESTER. ALL POWER RESTORED, BT VER/KEP
3782 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-10-26 17:55 | 2010-10-26 21:50 | 28 | 235 | 64832-1 | 6580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLED LINE , FOUND NO DAMAGE , RESET SECTIONALIZER & RESTORED POWER //VER/GAH IDC FOUND BAD CUTOUT LATER XXXX
3783 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2020-07-19 14:12 | 2020-07-19 18:40 | 75 | 268 | 4182861 | 6580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | A&B OCRS out @ 38831047C30142 will be patroling. Crossarm broke @ 38831047000006 wire still together. Need 8 ft arm and braces.// B phase out only // OPENED OTHER 2 PHASES ON RECLOSER @1740 RESTORED @1840
3784 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-12-13 01:36 | 2017-12-13 07:05 | 20 | 329 | 4643831 | 6580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | contacted customer, says entire road is without power// hot line clamp burnt off at pole 927-14 NBT 39830927000014
3785 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-09-09 07:55 | 2018-09-09 12:29 | 24 | 274 | 4062641 | 6576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 18-69/TE
3786 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-04-29 20:54 | 2021-04-29 22:40 | 62 | 106 | 4498341 | 6572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester on pole 487-92 cut in clear // restored 2240
3787 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-05-21 22:55 | 2014-05-23 11:24 | 3 | 2189 | 4733351 | 6567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARRIVED @ SITE..RP.. TOP OF XFMR C/O BROKEN.,COULD NOT RE-FUSE.,WILL NEED CREW, 34.5 KV C/O,,ARRESTOR,HLC.,& 18 FIB. BRKT. (MANUAL)..POLE LOCATED ON HILLSIDE NEAR ENTRANCE TO GAMBILL DR. ABOVE ONHWY 15.RGP. RELEASED BY CREW 077E09 ON SITE OPEN LINE FUSE ON 174-295 10:24 BACK ON 11:24
3788 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-08-07 12:47 | 2021-08-07 16:00 | 170 | 193 | 4015101 | 6567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONDUCTOR PULLED OUT OF SLEEVE AT POLE 37830379C00156//COD 9//WILL HAVE TO OPEN SWITCHES AT POLE 37830379C00164 TO MAKE REPAIRS Open @ 1530, closed switches at 16:00. power restored Released by crew 077H16
3789 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2016-09-30 05:39 | 2016-09-30 12:23 | 29 | 404 | 4946541 | 6562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE FUSE IS BLOWN AT POLE 38820941B00071/ PATROLLING THE LINE/ CLOSED C PHASE IN ON POLE 38820941B00071 AT 08:42 (RESTOR 6 CUST)/ LINE FUSE BLOWED ON POLE 38820941B00460. 40/5 POLE TOP BURNED OFF AT 38820941B00462/ HOT TAP SET OFF AT POLE 38820941B00146/ CLOSED FUSE IN ON POLE 38820941B00460 AT 09:29 (RESTORE 22 CUST)// WAITING ON CREW, IN ROUTE.MADE REPAIRS AND RESTORED 38820941B00146 AT 12:23 (1 CUST)/ VER/BOW AJB
3790 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-03-31 05:30 | 2011-03-31 09:33 | 69 | 243 | H60689-1 | 6559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS FAILED AND BURNT TOP OF 3 PHASE POLE OFF, ONLY C PHASE OUT (35 CUST) AT THIS TIME. CALLING FOR HELP // OPENED A & B PHASE REC (69 CUST) @ 0530, REMOVED CLAMPS AT POLE 229-150, THEN CLOSED RECLS AT POLE 204-80 @ 0541 RESTORING 60 CUST // SEE 60789-1 FOR SECOND RECL OUTAGE TO MAKE UP LOOPS DUP OF 60689-1 FOR A & B PHASE OUTAGE VER/HFP L3/HFP IDC XXXX
3791 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-07-22 18:13 | 2020-07-22 20:42 | 44 | 149 | 4206581 | 6556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse out on pole 674-251//found nothing//several times this has been out//cust. stopped me & said he saw a fire from his xfmr pole 674-318//found nothing other than a porcelin arrestor blown//i replaced cutout & arrestor on that pole///restored at 20:42//complete//em
3792 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-01-26 09:43 | 2011-01-26 17:06 | 16 | 443 | 64462-1 | 6555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38579347 CUTOUT BAD AND BURNED POLE # 1083-C4-431 OFF AT TRANSFORMER NEEDS POLE AND CREW TO CHANGE POLE OUT RELEASED BY CREW 077S05 REPLACED POLE AND CLOSED OCR AT 1625 , ONE XFMR STIL OFF TO 3 CUSTOMERS RESTORED LAST THREE CUSTOMERS AT 1706 JKC COD-16 ISO RECL 38831083D30268 // VER/HFP L3/HFP IDCC STP MISSING XXXX
3793 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-01-30 10:24 | 2013-01-30 12:30 | 52 | 126 | 4756691 | 6552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD DEADEND INSULATOR ON POLE 402-49, RICK MAGGARD IS BRINGING ME A INSULATOR AN GOING TO HELP ME CHANGE IT. ///VER/CRB L/3 CRB IDC XXXX
3794 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-10-08 10:00 | 2018-10-08 10:50 | 131 | 50 | 4207871 | 6550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SHAWN RENNER FOUND ONE 1 STRAND HOLDING CONDUCTOR//OPENED OCR 37820098D00149 UP TO MAKE REPAIRS OFF 1000 ON 1050 L3/HFP
3795 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-12-05 13:30 | 2019-12-05 15:29 | 55 | 119 | 4128621 | 6545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | arrived pole was smoking, 1071-33, either have a bad ptp or deadend ins. on this pole, open up rec on pole 1071-126 at 1330, isolated line side of rec and bypass, grd tagged to B Ramey, may be about to get small truck to pole Released by crew 078S06///repairs made///recloser closed in at 15:29///complete br
3796 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-01-19 13:44 | 2013-01-19 22:07 | 13 | 503 | 4694911 | 6539 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE IS OPEN ON 596-58 PATROLLING LINE. APR AT 2207 CLOSE TICKET. DWEST VER/PDP IDC NEEDED CREW TO HELP FIND TROUBLE XXXX
3797 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-07-26 11:56 | 2022-07-26 17:40 | 19 | 344 | 4584071 | 6536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PHASE OFF INSULATER AT 37830151000025 ( COD 19)
3798 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-09-27 19:51 | 2018-09-27 22:10 | 47 | 139 | 4169071 | 6533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | DOL 863195//dead-end pole, lead is almost touching guy wire causing it to spark, will need breaker outage to repair Released by crew 077S02//cod 47// Going off of DOL
3799 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-04-24 06:38 | 2015-04-24 09:00 | 46 | 142 | 4361401 | 6532 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF ON POLE#207/REPAIRED AND RESTORED POWER AT 0900/HOT TAP BURNT OFF NO CREW REQUIRED VER/KEP L3/HFP XXX AJB
3800 | Hazard | 3303902 | LESLIE | WOOTON | 2019-02-04 15:03 | 2019-02-04 18:15 | 34 | 192 | 4753441 | 6528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 7200 ON POLE 510-7
3801 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-04-06 15:10 | 2017-04-06 17:35 | 45 | 145 | 4621961 | 6525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 69-63 LOOP BURNT OPEN OPENED A PHASE REC. 15:10 SEND TO RON -- COD 45//POLE 69-63 LOOP BURNT OPEN OPENED A PHASE REC. 15:10 SEND TO RON // CREW ON SITE--MAKING REPAIRS TO BURNT OPEN LOOP--ALL WORK COMPLTED-OCR IN ON 69-310 AT 17:35--TBL TKT COMP--RMV 38830069A10310 VER/AWD L3/HFP HFPC LCD38830069000063 FP38830069000063 AJB
3802 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-01-23 19:08 | 2008-01-23 19:15 | 932 | 7 | 59307-1 | 6524 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 3308502// THIS WAS SWITCHING TO TRANSFER LOAD FROM BONNYMAN-HAZARD// OPEN BRKR @ 1908// OPEN SWITCH POLE 247A-639 @ 1912// CLOSE SWITCH 296-C2-1042 @ 1913 RESTORE 678 CUST- TIES BONNYMAN-HAZARD TO HAZARD/BLK GLD// CLOSE SWITCH 174-B-27 @ 1915 RESTORING 932 CUST// TIES BONNYMAN-HAZARD TO ENGLE/GRAPEVINE -LAST STEP CHAGNED FROM 935 TO 932 DUE TO CUSTOMER OUTAGE 3 CUST OUTAGED ON OTHER ORDER - VER/TOM IDC REMOVED 678 CUSTOMER STEP THAT WAS ONLY 5 MIN 7/31/08 CHANGED FROM DLINE OVERLOAD PER RELIAB MTG XXXX
3803 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-02-14 22:44 | 2018-02-15 02:21 | 30 | 217 | 4841671 | 6510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Found broken arrester at pole 38830454D26571. cleared up and power restored at 02:21//cod 30
3804 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2008-09-18 06:23 | 2008-09-18 11:37 | 24 | 314 | 65094-1 | 6508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP 3010601/// 100T FUSE ON 20-10693010601/// 100T PLOLE-20-1069 ON 09;45 TO 20-371 RELEASED BY CREW 078S08 1137 HRS PICKED UP TRANSFORMER ON 390 IDCC CDC83, FEC57 XXXX
3805 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-07-16 21:13 | 2010-07-17 01:14 | 27 | 241 | 51195-1 | 6507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3000303/ PRI UNDERGROUND BAD TRANS. 20-6052 AND 6053 IDCC CDC83 XXXX
3806 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-09-09 12:31 | 2011-09-09 15:02 | 43 | 151 | 4851581 | 6493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 477-240 COD--43 IS LF 38830477000260 VER/HFP L3/HFP IDC XXXX
3807 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-04-25 21:50 | 2015-04-26 01:20 | 35 | 210 | 4365811 | 6492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE OUT ONLY (35 CUSTOMERS)/ POLE 450C-40. ALSO, LINE FUSE OPEN ON POLE 450C-243. BAD CUT-OUT ON POLE 450C-246. CLOSED LINE FUSE ON POLE 450C-40 AT 00:47.C-PHASE LINE FUSE OPEN ON POLE 450C-40. ALSO, LINE FUSE OPEN ON POLE 450C-243. BAD CUT-OUT ON POLE 450C-246. CLOSED LINE FUSE ON POLE 450C-40 AT 00:47. CLOSED LINE FUSE ON POLE 450C-243 AT 0120//DID MD ON BOTH FUSES VER/SEF AJB
3808 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-02-27 14:15 | 2019-02-27 16:30 | 48 | 135 | 4933741 | 6480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Rec. open @1126-A4-841.Bad insulator on pole 1126-A-419, will be making repairs. Got insulator changed out, closed rec. @1630. L3/HFP
3809 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-10-23 23:57 | 2013-10-24 10:45 | 10 | 648 | 4958701 | 6480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES //ISO 37830172C00166// WIRE DOWN ON POLE 37830172D00167. I WILL BE OPEN FUSE ON POLE 37830172C00158 TO PUT WIRE UP. OPEN LINE FUSE AT 0935 AND CLOSED AT 1045 (SEE ORDER 4959241)RELEASED BY CREW 077S05//COD 10// VER/DBM L3/HFP IDC XXXX
3810 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-09-09 12:27 | 2009-09-09 14:15 | 66 | 108 | 59043-1 | 6468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER OPEN. CUTOUT BROKE ON POLE 737-157. CREW ENROUTE TO ASSIST. ISOLATED BAD CUTOUT AND CLOSED REC ON POLE 738-276 AT 14:00 LEAVING ONLY LATTERAL ON POLE 737-157 OFF. REPLACED CUTOUT AND RESTORED TAP AT 14:15. (RESTORING REMAINING CUST) ALSO HAD XFMR ON POLE 737-157 OFF FROM 13:50 TO 14:15. SH VER/KEP L3/KEP IDCC CNT134, ADDED 9 MISSMAPPED CUSTOMERS XXXX
3811 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2016-05-22 15:18 | 2016-05-22 17:30 | 49 | 132 | 4248071 | 6468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRI JUMP OFF PTP, I HAVE IT RETIED AND ALSO RETIE THE NEUTRAL AT THIS ON LOC, ON POLE 900-8037, ALL POWER RESTORED AT THIS LOC AT 1730 AMG REC 39830900000119 VER/AWD L3/HFP HFPC CCO FEC44 AJB
3812 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-04-24 11:45 | 2011-04-24 12:07 | 294 | 22 | 63562-1 | 6468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | IDC XXXX
3813 | South Williamson | 3200302 | BELFRY | TOLER | 2018-01-20 18:02 | 2018-01-20 22:56 | 22 | 294 | 4760231 | 6468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A phase recloser had opened when the power was restored on an earlier outage. /// RELATED TO 4759921 - EXTENDING THIS OUTAGE TO TIME OFF FOR THAT ORDER - L3/HFP
3814 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-09-30 21:25 | 2012-09-30 23:06 | 64 | 101 | H4101031 | 6464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SINGLE PHASE WIRE DOWN AT POLE 1147-282 PER JIM LINKOUS POLE 1147-282 PRI. AND NU. BURNT DOWN REC. OPEN ON 1147-237 A PHASE (147 CC) OPENED B PHASE 21;25 (64 CC) TO DO WORK RELEASED BY CREW 078S08/ FETR 23:15// JEH// REPAIRS COMP. ALL POWER RESTORED @ 23:06 ////JEH //VER/GAH IDC XXXX
3815 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2019-11-07 04:41 | 2019-11-07 11:50 | 29 | 429 | 4004871 | 6456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Closed line fuse 785-1733 @ 6:35. Bad ug between xfmr 785-883 and jct box 785-887.Closed line fuse 785-1733 @ 6:35. Bad ug past jct box 785-9001. Crew onsite locating fault to repair. Dig # 1911070205.Closed line fuse 785-1733 @ 6:35. Bad ug past jct box 785-9001. Crew onsite locating fault to repair. Dig # 1911070205. Repaired and restored @ 11:50. sh RELATED TO 4005551 L3/HFP
3816 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-07-26 05:27 | 2011-07-26 10:05 | 33 | 278 | 4622821 | 6444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3401703// WE HAVE 3 SINGLE RECLOSERS ON POLE 267-48. THE C-PHASE RECLOSER IS OPEN. THE OTHER 2 ARE STILL CLOSED IN. I AM PATROLLING LINE NOW. INSULATOR IS BAD ON POLE 243-9. I OPENED LINE FUSE ON POLE 243-9 TO ISOLATE DEADEND INSULATOR AND CLOSED RECLOSER AT POLE 267-48 IN AT 07:55. WE CLOSED CUTOUT ON 243-9 AT 10:05 AND IT STAYED. RELEASED BY CREW 074S01 IDCC CNT87 XXXX
3817 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-03-23 14:09 | 2019-03-23 15:36 | 74 | 87 | 4018591 | 6438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | rec. open on pole 103-27////will patrol. arrester bad on pole 103-116..blowed in clear POWER RESTORED @ 1536 L3/HFP
3818 | Hazard | 3301401 | COMBS | COMBS | 2021-04-01 07:09 | 2021-04-01 08:45 | 67 | 96 | 4409951 | 6432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp burnt off at pole 248-159 // opened line fuse to put clamp back on off@0835 on@0845
3819 | Pikeville | 3421002 | BREAKS | GRASSY | 2012-11-01 10:57 | 2012-11-01 17:15 | 17 | 378 | 4316231 | 6426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED OPEN POLE 221-129 IDC XXXX
3820 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-11-23 16:20 | 2022-11-23 18:05 | 97 | 105 | 4176491 | 6425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole 165-18 is rotten and has fell over against Garage,Myles Robinette is on the way to help make repairs..Will open GOAB at 165-195 and keep up with Time..//SW OFF @ 1620 ENERGIZED @ 1725 TRANS AN TAP STILL OFF AT POLE 37830165000018//NO OUTAGE TILL 1620 WHEN GOAB OPENED ON POLE 37830165000195//all repairs made// on @ 18:05 Released by crew 074H18
3821 | Pikeville | 3421001 | BREAKS | CITY | 2009-06-26 07:40 | 2009-06-26 09:08 | 73 | 88 | 61770-1 | 6424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | COD-73 // FOUND BAD ARRESTOR ON POLE 220-628 // RESTORED AT 0908 // VER/KEP L3/KEP
3822 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-05-21 19:48 | 2018-05-21 22:50 | 44 | 182 | 4389851 | 6417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase (1 cust) cutout failed on 24B754 opened 3 cutouts feeding 3 phase tap and 1 cutout feeding single phase tap (43) at 20:25//crew on site/ ISO 37830024B30754/ COD 44/ Restored @ 2250
3823 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-06-20 13:59 | 2009-06-20 20:40 | 16 | 401 | 64129-1 | 6416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED 35/7 BROKEN GOING BACK WITH 40/5 TRUCKS OK/CALLED TECH ALREADY WINDSTREAM POLE/INLINE POLE RELEASED BY CREW 078S03 //VER/GAH
3824 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-06-25 23:38 | 2009-06-26 06:03 | 24 | 385 | 61313-1 | 6410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE OUT ON POLE 879-2 PATROLING//@ 0120 RESTORED UP TO POLE 903-2// RELEASED BY CREW 078S09/CREW ON SITE/PATROLLING LINE ON FOOT/VERY ROUGH ROW/FETR0830/VEM/LA INTO XARM/CLEARED AND RESTORED 12T ON 879-2 AT 0603/ALL CUST RESTORED/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP L3/KEP
3825 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-08-19 17:14 | 2009-08-19 19:51 | 157 | 157 | 52789-1 | 6409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR # 31314040 //PHASE C RECLOSER OUT. LIGHTNING ARRESTER ON CSP XFMR EXPLODED AND CAUSED PRIMARY RISER TO FALL AGAINST TOP OF XFMR BURNING HOLE IN IT. ISOLATED XFMR (WILL HAVE TO CHANGE) AND RESTORED ALL OTHER CUSTOMERS AT 17:51 RESTORING 152 CUSTOMERS DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO REPLACE XFMR. 5 OUT NOW.//LAST CUSTS ON @ 1951//COD TOTAL 157// VER/DBM IDC PHASING APPEARS TO BE VERY BAD XXXX
3826 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-07-20 20:07 | 2008-07-21 13:55 | 6 | 1068 | 54690-1 | 6408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LI NE FUSE OUT TREES POSSIBLE//PATROLLING...BAD CUTOUT...30 T FUSE....BB VER/DKG IDC XXXX
3827 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-01-27 00:31 | 2012-01-27 02:00 | 72 | 89 | 4296321 | 6408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 116-436 BAD CUTOUT 40T FUSE POLE 92-124 80T LINE FUSERELEASED BY CREW 078S08 IDC XXXX
3828 | Pikeville | 3407103 | TOPMOST | KITE | 2017-05-26 11:34 | 2017-05-26 21:00 | 22 | 566 | 4866451 | 6404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE OUT ONLY OPENED A AND B PHASE OPENED AT 13:50 DUE TO BURNT OFF POLE 209-207. CLOSED IN N/O SWITCHES ON POLE 234-24 AT 15:20 TO OPEN SWITCHES ON POLE 209-285. AT 21:00 CLOSED RECLOSER IN ON POLE 209-25 UP TP OPENSWITCHES ON POLE 209-D4-258 AT 21:34 OPENED SWITCHES ON POLE 234-24 AND AT 22:02 CLOSED SWITCHES IN ON POLE 209-D4-258 UP TO N/O POLE 234-24 RESTORING ALL CUST. RELEASED BY CREW 074S11///ORIGINAL OUTAGE RECORD/// VER/DKM AJB
3829 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-09-12 18:14 | 2015-09-12 18:36 | 291 | 22 | H4230921 | 6402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE SMOKING REALLY BAD ABOUT TO CATCH FIRE AT 108 HONEY CUT, OPENED RECLOSERS ON POLE 231-291, 811 DIG # IS 1509120062, GAVE MATERIAL LIST TO T. SMITH, CAN CUT LOOPS WHEN CREW ARRIVES ON POLE 255-200/OPENED 1030/CLOSED 1215POLE SMOKING REALLY BAD ABOUT TO CATCH FIRE AT 108 HONEY CUT, OPENED RECLOSERS ON POLE 231-291, 811 DIG # IS 1509120062, GAVE MATERIAL LIST TO T. SMITH, CAN CUT LOOPS WHEN CREW ARRIVES ON POLE 255-200. OPENED RECLOSERS TO MAKE LOOPS UP AT 18:14/ON 1836// VER/ ADH L3/HFP XXXHFP AJB
3830 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-09-11 12:44 | 2011-09-11 14:21 | 66 | 97 | 4856871 | 6402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP COD-66 ISO PO 38830094A31024 VER/HFP L3/HFP IDC XXXX
3831 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-04-27 20:20 | 2008-04-27 23:40 | 32 | 200 | 54674-1 | 6400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301101// BAD CUTOUT == REPLACED== REFUSED POWER OK //COD-32// VER/LDA IDC XXXX
3832 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-06-24 14:20 | 2014-06-24 15:00 | 160 | 40 | 4147891 | 6400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD HOT TAP BURNTED OFF RECLOSER LEAD ON THE SOURCE SIDE HAVE REPLACED AND POWER IS RESTORED TO ALL CUST AT THIE LOC AT 1500//COD 160// VER/DBM AJB
3833 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2017-04-18 07:35 | 2017-04-18 08:55 | 80 | 80 | 4653571 | 6400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED OCR 37830223A10576. RISER BURNT OFF/OPENED TO REPAIR.HOT LINE CLAMP BURNED OFF HIGH SIDE OF RECLOSER == REPAIRED POWER OK 0855 VER/AWD L3/HFP XXXHFP AJB
3834 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2011-01-01 01:21 | 2011-01-01 13:12 | 9 | 711 | 57464-1 | 6399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38258341 //BAD CUTOUT ON POLE 110-94 MANUEL POLE WAIT UNTIL DAYLIGHT TO COMPLETE RELEASED BY CREW 077H04 == CHANGED CUTOUT == REFUSED LINE == POWER OK COD-9 ISO LF 37830110B40002 VER/HFP L3/HFP IDCC CDC92 XXXX
3835 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-08-19 07:56 | 2020-08-19 13:30 | 23 | 334 | 4345751 | 6398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | on pole 38831133000002 got bad insulator and arrestor , need 2 19,9 de insulators , cutout and arrester and pt pin and insulator for 19.9 and on pole38831133000002 got a ballon on cutout, got line fuse in on pole 38831132000159 at 0956 Released by crew 077S05, crew on site, all power restored @ 13:30 hrs p.hicks Released by crew 077H09
3836 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-09-16 16:20 | 2017-09-16 21:37 | 34 | 317 | 4367321 | 6394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830645D20297 REC OPEN--83-645/27 TO 83-645/127 PRI DOWN--ISOLATED AT 83-645/27 - CUT LOOPS. REC IN AT 19:20 -- RELEASED BY CREW 078S01--CREW ON SITE--REPAIRED 1 SPAN #2AA PRIMARY--PWR RESTORED AT 21:37---TBL TKT COMP---RMV/// VER/DKM SJG
3837 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-06-23 17:56 | 2015-06-23 19:30 | 68 | 94 | 4646341 | 6392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT- CHG OUT POWER RESTORED KWB VER/CRB AJB
3838 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2009-04-14 03:04 | 2009-04-14 09:20 | 17 | 376 | 52066-1 | 6392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 2 BAD DISC INSULATORS...NEED CREW...CANNOT GET TRUCK CLOSE TO THIS POLE..678-38..BB CALLED TIM MILLER...HE IS CALLING OUT CREW.. CHG 2 DEAD ENDS REFUSED 65 T...BB VER/KEP L3/KEP IDC XXXX
3839 | Hazard | 3302704 | HAZARD | KENMONT | 2021-11-27 07:45 | 2021-11-27 09:08 | 77 | 83 | 4127851 | 6391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | found bad arrester on step down transformer..replaced arrester.. A phase was out
3840 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-04-14 00:27 | 2022-04-14 06:00 | 638 | 333 | 4760591 | 6390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed. Additional personnel enroute.//opened feeder breaker at 0445 // closed at 0454 //this was to safely isolate failed cutout// Replaced cutout and restored line fuse 828-308 @ 6:00. sh //
3841 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-07-08 23:13 | 2012-07-08 23:19 | 1065 | 6 | 4607091 | 6390 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | STATION DE-ENERGIZED DUE TO FAILURE OF TRACE CREEK BREAKER AT COALTON STATION //VER/GAH IDC XXXX
3842 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-03-31 16:46 | 2019-04-01 16:32 | 15 | 1426 | 4045501 | 6388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed and burnt pole 152-4 off down to the xfm /// will need line crew , 40/4 pole, double deadend eqipment Released by crew 074S02.cut inline dead end at pole152-5..can restore all but two cust.will need yard machine tomorrow. closed line fuse on pole 151-88 at 21:18. two customers still out..hold for crew for tomorrow Released by crew 079H07 on @ 1632 pole 152-5
3843 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-05-26 13:12 | 2016-05-26 15:06 | 56 | 114 | 4261651 | 6384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | ASSOCIATED WITH POWERON ORDER 4258841// OPENED @_____/ CLOSED @ _____// 1312-1506 VER/AWD AJB
3844 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-01-07 00:50 | 2014-01-07 10:30 | 11 | 580 | 4243671 | 6380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED SMALL BUCKET TO GET TO XFMER .CONTRACTORS ARE GOING TO CHANGE XFMER OUT .NEED 50 KVA NO TRUCK DUE TO DRAIN TILE THEY CAN LOOK AT GETTING TRUCK ACROSS RELEASED BY CREW 076H06//COD 11// VER/DBM L3/HFP IDC XXXX
3845 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-06-23 07:35 | 2021-06-23 09:31 | 55 | 116 | 4797481 | 6380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | B phase load side fuse blown on step down pole 38831125C30024A// patroling// took a inactive CSP XFM off line at pole 1125-C3-22 will try stepdown fuse
3846 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-07-31 12:19 | 2020-07-31 14:09 | 58 | 110 | 4264121 | 6380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 1137-345.replaced.restored..
3847 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-07-22 11:29 | 2016-07-22 13:17 | 59 | 108 | 4666931 | 6372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP AND HOT LINE CLAMP BURNED UP , I REPLACED THEM//59 B PHASE CUSTOMERS// VER/ ADH AJB
3848 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-06-03 17:41 | 2012-06-03 18:51 | 91 | 70 | 4876941 | 6370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTTAP BURNT OFF PROBABLY WAS LOOSE, MADE REPAIRES APR CLOSE TICKET//COD 91//ISO// VER/DBM IDC XXXX
3849 | Hazard | 3302704 | HAZARD | KENMONT | 2016-09-10 21:19 | 2016-09-10 22:57 | 65 | 98 | 4884121 | 6370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT ON POLE37830296C40553,,REPLACE/ ISO 37830296C20537/ COD 65/ VER/BOW L3/HFP XXXHFP AJB
3850 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2021-12-09 15:21 | 2021-12-09 16:00 | 163 | 39 | 4164481 | 6357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Broken crossarm reported by ahspundh on pole 1089-a-327/ opening, tagging, grounding for contract crew at pole 38821089A00008/ switches on pole 38821089A00008 are not on poweron map/ opened @ 1521/ closed @ 1600
3851 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-12-04 13:46 | 2010-12-04 21:20 | 14 | 454 | 62998-1 | 6356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 COP PRIM DN AT STEPDOWN 6-136,NEED CREW/////WR#-37989706,,DALE H IS ENROUTE SHORTLY RELEASED BY CREW 074S06//CREW ON SITE. HAD COND UP BUT BROKE IN ANOTHER SPAN, WILL HAVE TO RE PULL. RESTORED AT 21:20 VER/ARN IDC XXXX
3852 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-12-09 12:54 | 2018-12-09 16:15 | 54 | 201 | 4527731 | 6354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | loop burnt into on pole 279-206, got loop in clear, recloser back in at 14:45, 1 xfmr still out. repaired loop, all power restored
3853 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-04-25 10:00 | 2018-04-25 10:50 | 127 | 50 | 4276921 | 6350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened @ 10patrolling line found broken 300 amp solid blade c/o on 1071-24, open rec on 1072-285 at 1000, tg and grd to self at work site, maded repairs. closed in rec on 1072-285 at 1050, all power is restored at this loc by amg/ ISO 39831072A10285/ COD 127
3854 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2022-11-20 07:18 | 2022-11-20 09:39 | 45 | 141 | 4164401 | 6345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | rec in.. on pole148-504 found copper broke out of top of solid blade.. opened rec at 9:12 to make repairs. rec back in at 9:39.. complete
3855 | Hazard | 3302703 | HAZARD | HAZARD | 2020-11-17 23:14 | 2020-11-18 02:45 | 65 | 211 | 4703691 | 6340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | A PH ONLY OUT (65CC) at 37830296A30746/wire down at 37830272D21563/iso at 37830272D20736/closed recl @ need line crew & manual ROW/a phase rec open on 296-746. wire down at 272-1563. lifted clamp at 272-736 and closed a phase rec at 00:40. need line crew and row crewa phase rec open on 296-746. wire down at 272-1563. lifted clamp at 272-736 and closed a phase rec at 00:40. need line crew and row crew. restored 02:45 Released by crew 077S10
3856 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-11-01 17:59 | 2013-11-01 18:23 | 264 | 24 | H4992291 | 6336 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | 2206403; ****HOIS CREATED DUPLICATE. ORDER HAS ALREADY BEEN VERIFIED****JEFF FERRY TO ASSESS 2257 304 633-3648 FOUND A PHASE OUT ON MAIN LINE -- PAD POLE IN STATION BREAKER. -- NOTIFIED DDC RELEASED BY CREW 068E04 //DC 12 WV PH A CUSTOMERS AND 117 KY PH A CUSTOMERS. WILL BE OPENING OTHER TWO PHASES AT 1700/ DEENERGIZED 2 PHASES AT 1759/ RESTORED FROM TRANSMISSION AT 1823// VER/RSL IDC XXXX
3857 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-02-29 20:45 | 2012-02-29 21:17 | 198 | 32 | 4523281 | 6336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RELATED TO 4521941 // SER SERVICER RANDY FIELDS, ANYTIME THE RECLOSER ON THE SOURCE SIDE OF THE ONE GOES OUT, THIS ONE OPENS UP AS WELL // NEED ENGINEERING TO CHECK THIS RECLOSER FOR ISSUES // COD 198//RECLOSER ON THIS POLE DONT PICK BACK UP WHEN WE LOSE POWER BEHIND IT, PLEASE SEND NOTE TO MIKE LEWIS ON THIS MATTER. POWER RESTORED AT 21:17 HRS RELEASED BY CREW 077S02//EMAILED TO MIKE LEWIS // VER/DBM AJB
3858 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-09-21 01:07 | 2020-09-21 09:55 | 12 | 528 | 4480841 | 6336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Transformer fuse restored @ 09:55
3859 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2018-05-10 13:46 | 2018-05-10 14:50 | 99 | 64 | 4331711 | 6336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE 38820991D40136 - CREW HAD TO OPEN RECLOSER TO SAFELY REPAIR BAD CONNECTION // COD-152 ISO OCR 38820991D40266 // Restored @ 1450 // crossover outage
3860 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-08-10 08:35 | 2018-08-10 23:40 | 7 | 905 | 4936551 | 6335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 50t primary ug riser open @ 1148-464, recent digging around riser pole for new water lines. line crew. need locating tools. Released by crew 078S07, repairs made all cust restored @ 2340 please close ticket thanks. bt//cod 7 L3/HFP
3861 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-04-13 05:38 | 2022-04-13 13:45 | 13 | 487 | 4755651 | 6321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50KVA 7200 on pole 176-54. I have help on the way to replace this XFMR. Released by crew 077S04
3862 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-11-15 09:57 | 2011-11-15 12:35 | 40 | 158 | 4078381 | 6320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 60 AMP CUTOUT//B PHASE ONLY COD 40 ///VER/CRB IDC XXXX
3863 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-10-11 05:54 | 2018-10-11 12:45 | 29 | 411 | 4218211 | 6319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAULT POLE 39831000A00285 // 28 CUST ON @ 0925 /found l/f out, on 1000-40, patrolled found at 22 meadows lane, a 404 pole burnted off, will be crew req, can use trucks, just pole and new c/o all other material should work back. grd and tag to ron virgin at pole 1000-89, lifted htsp at this pole. closed in l/f restoring power to all cust but one, at 0925
3864 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-06-25 19:04 | 2016-06-25 19:31 | 234 | 27 | 4475461 | 6318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | REGULATOR FAILED WHILE RESTORING OUTAGE MLR VER/ARN MAF AJB REMOVED STP CNT. ONLY 234 CUST PREV REST WERE OUT WITH THIS CB OUTAGE. CB LO WITH ATM TO REST 97 CUST AT 19:04. SEE INLT CB OUTAGE 4449821.
3865 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-11-18 22:18 | 2015-11-19 10:00 | 9 | 702 | 4467461 | 6318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRIED TO CLOSE FUSE - CAME BACK OUT HARD// LOOKED AT ALL OF LINE THAT COULD GET TO// PART OF ROAD IS BLOCKED// WILL HAVE TO WAIT UNTIL DAYLIGHT //TOM FOUND BAD CUTOUT ON POLE 458:158// VER/ ADH
3866 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-01-17 03:40 | 2022-01-17 11:11 | 14 | 451 | 4360931 | 6314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LF open on 117-114, primary down from 117-116 to 117-117. No trucks to pole, crew required Released by crew 078S02 crew on site FETR 10:30 LRM all pwr restored 11:11 Please clsoe tiket LRM
3867 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-05-03 05:08 | 2009-05-03 06:30 | 77 | 82 | 63766-1 | 6314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308603 RECLOSER IS OPEN ON POLE 448-204. FOUND BROKEN CUTOUT AT POLE 446-46 IDC XXXX
3868 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-01-19 01:24 | 2016-01-19 01:48 | 263 | 24 | 4630571 | 6312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO 4629811//OPENED FEEDER BREAKER TO REPAIR FAILED LOOP ON POLE 283-116//COD 263// VER/DBM AJB
3869 | South Williamson | 3202201 | LOVELY | LOVELY | 2015-04-14 00:57 | 2015-04-14 02:20 | 76 | 83 | 4314411 | 6308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BROKE CUTOUT UP IN CHAFFINS BR ON POLE 674-318//REPLACING NOW//REPAIRS MADE//RESTRED AT 2:20//COMPLETE//EM VER/SEF AJB
3870 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-04-19 22:45 | 2019-04-20 02:25 | 53 | 220 | 4138821 | 6305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed on pole 80-69 and burnt top of pole off/// lifted hot tap on pole 80-25 and isolated truoble /// Dennis Massey has crew enroute to make repairs/// Closed recloser back in @ 00:40 on pole #37820104000026 and restored all customer except for 2 off of pole# 80-69/// Repairs made restored hot tap @ 02:25 on pole 37820080000025 Released by crew 074S02 L3/HFP
3871 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-11-06 05:50 | 2017-11-06 09:20 | 30 | 210 | 4533201 | 6300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 077H16 B phase recloser out on pole 426-43 bad cutout on pole 426-53 power restored at 09:20 37830426D00043 37830426D00053
3872 | Hazard | 3302704 | HAZARD | KENMONT | 2009-01-16 09:16 | 2009-01-16 10:40 | 75 | 84 | 55764-1 | 6300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELATED TO ORDER 55515-1 CREW HAD TO OPEN OTHER STEPDOWN TO REPLACE BAD STEPDOWN TRANSFOMRER PLEAS CLOSE ORDER @ 1040 THANKS VER/KEP L3/KEP AJB PHASE C.
3873 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2021-07-07 18:36 | 2021-07-08 01:56 | 47 | 440 | 4868561 | 6295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Fuse still in @ 45-d1-6077, crew will have to open when they arrive, Primary down from 38830045D16089 to 38830045D16090. Crew required, can reach with big bucket Released by crew 078S02 Opened on 38830045D16077 at 01:27. Closed at 01:56. Ticket complete. Released by crew 078H11
3874 | Hazard | 3303901 | LESLIE | HYDEN | 2014-08-18 06:20 | 2014-08-18 11:06 | 22 | 286 | 4377371 | 6292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT RELEASED BY CREW 077S01 CHANGED CUTOUT AND RESTORED POWER AT 1106 VER/CRB AJB
3875 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-01-18 12:25 | 2011-01-18 16:47 | 24 | 262 | 62254-1 | 6288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38482678 //CREW REQUIRED POLE BURNT OFF CAN CUT OFF POLE 270-263 OPEN LINE FUSE ON 270-18 AT 1225 HRS/TRUCKS OK SIDE ROADCREW REQUIRED POLE BURNT OFF CAN CUT OFF POLE 270-263 OPEN LINE FUSE ON 270-18 AT 1225 HRS/TRUCKS OK SIDE ROAD/SEND TO MULLINSRELATED TO 62228-1/CREW ON SITE/NEED TO CHANGE POLE/FETR1800/VEM // ENTERED MD...HFP COD-24 ISO LF 38830270D00018 VER/HFP L3/HFP IDC DCMT XXXX
3876 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-06-03 18:24 | 2022-06-03 19:12 | 131 | 48 | 4015161 | 6288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C phase recloser was out due to stirrup burning off on load side of recloser on pole 356-B-8. replaced with new stirrup, power restored
3877 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-11-04 11:53 | 2008-11-04 14:30 | 40 | 157 | 62092-1 | 6280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PLEASE DON`T FORGET THE FETR...THANKS CONNECTION ON CUTOUT RISER BURNT UP.THANKS, LEAD FROM BOTTOM OF CUTOUT BURN-IN TWO IDC XXXX
3878 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-07-04 03:45 | 2008-07-04 18:42 | 7 | 897 | 61971-1 | 6279 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG PRIMARY LINE FUSE OUT-NO POLE#-MAP NOT IN FIELDVIEW/ TRIED FUSE CAME BACK OUT RELEASED BY CREW 078S07-----POWER RESTORED TO XFORMER PAD 45-6229 @ 08:15 UG PRIMARY BAD FROM 6229 TO 6230 --- RELEASED BY CREW 078H01 22 CUSTOMERS TOTAL ....U/G MAP NOT CORRECT ENGINEERING TO CORRECT. VER/HFP IDC CHECK MAPPING AND NUMBER OF CUSTOMERS WITH SAME AS OUTAGES, AND POSSIBLE GHOSTS LOOKS MORE LIKE 7 CUSTOMERS XXXX
3879 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2016-01-08 19:02 | 2016-01-08 21:28 | 43 | 146 | 4596301 | 6278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 81-D-109 REPLACED CUTOUT RESTORED POWER AT 21:28// VER/ ADH AJB
3880 | Hazard | 3302703 | HAZARD | HAZARD | 2015-02-21 00:47 | 2015-02-21 08:15 | 14 | 448 | 4060011 | 6272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE MELTED OUT, POWER RESTORED.//COD 14// VER/DBM L3/DKGXXXX
3881 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-06-22 11:30 | 2021-06-22 13:38 | 49 | 128 | 4791741 | 6272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATER BROKE ON POLE 38831101D40183//OPENED STEP DOWN AND RECLOSER ON POLES 38831101D40702 AND 38831101D40776 TO MAKE REPAIRS//OFF @ 1130 ON @ 1338
3882 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-07-19 15:21 | 2012-07-19 21:20 | 32 | 359 | 4770211 | 6268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ALL BUT ONE CUSTOMER RESTORED- POLE 287-7 AT 9300 RUNYAN ROAD BAD 25 KVA TRANSFORMER TRUCK TO POLE RELEASED BY CREW 078H18,XFMER CHANGED ON POLE287-7 ALL CUST RESTORED@2120 PLEASE CLOSE TICKET THANKS.BT VER/ARN IDC XXXX
3883 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-07-29 13:20 | 2013-07-29 17:21 | 26 | 241 | 4604131 | 6266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELATED TO ORDER 4604181 MAPPING ISSUE ON THIS - SENT CLIFF FREEMAN AN EMAIL TO HAVE TECH FIND OUT HOW THIS IS IN FIELD AND UPDATE MAPS /// COD-26 ISO LF 38830784C00286 VER/HFP L3/HFP IDC NEED MORE INFO ON MAPPING XXXX
3884 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-10-12 01:12 | 2010-10-12 03:00 | 58 | 108 | 58819-1 | 6264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | REPLACED SECTIONALIZER WITH FUSE LINK //VER/GAH IDC XXXX
3885 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-03-28 09:26 | 2021-03-28 13:47 | 24 | 261 | 4390191 | 6264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 12kv cutout on pole 295-A-14, manual and in the approach distance. Will need a manual ROW crew to remove a tree that is pulling down some secondary on this pole as well. The T-bracket for this cutout is mounted on the back side of the bottom bolt of the pole top pin. There is a single phase recloser one pole back from this outage. Crew required. Released by crew 077S04 // OPENED RECLOSER @1311 CLOSED @1347. LR- The 1st ALL OUT call came in at 9:26 3-28-21.
3886 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-11-02 12:57 | 2013-11-02 13:08 | 569 | 11 | H4003751 | 6259 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | CB B LINE DISC FAILED OUTAGE TO REPLACE VER/KEP L3/HFP
3887 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-01-30 09:26 | 2013-01-30 14:10 | 22 | 284 | 4755071 | 6248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE ON XFORM BANK 45-4303 OUT, REFUSE XFORM FUSE CAME OUT LIKE CANNON NEED LINE CREW BAD 167KVA 4 BUSHING XFORM IN BANK WYE-WY. SEND TO BILL FRALEY RELEASED BY CREW 078S04 COD-22 ISO TF 38830045C14303 VER/HFP L3/HFP IDC XXXX
3888 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2009-02-27 04:30 | 2009-02-27 13:12 | 56 | 522 | 51950-1 | 6248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 28711945 //CENTER REC OUT.. 56 CC .HOT TAPS OFF ON POLE 801-24- 801-76...ONLY 1 CUST OUT WHEN I CLOSE CENTER RECLOSER.. LOOPS OPENED ON P.O. AT POLE 24 . BOBBY WILL ARRANGE FOR CREW TO REPLACE POLE 801-77// COMPLTED AT 13:12// VER/DBM IDCC FP20 XXXX
3889 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-12-20 07:28 | 2010-12-20 09:50 | 44 | 142 | 54432-1 | 6248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD HAS BURNT OFF RECLOSER ON POLE 250-8, APPEARS ALL VXES ARE IN ON POLE 249-349//COD 44// VER/DBM IDCC PN349 XXXX
3890 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-01-26 09:13 | 2011-01-26 13:30 | 45 | 257 | 64421-1 | 6245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38578451 //247-1028 BURNT DUE TO FAILED CUTOUT OPENED LINE AT 247-1095 INSTALLED 40T RESTORED TO THERE AT 1110 EXTENEDED OUTAGE DUE TO HITTING ROCK---POWER RESTORED. COD-45 ISO LF 37830247D00449 // VER/HFP L3/HFP IDC XXXX
3891 | Hazard | 3310502 | HADDIX | CANOE | 2016-08-11 10:42 | 2016-08-11 11:34 | 120 | 52 | 4762181 | 6240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE DEFECTIVE RECLOSER (AED ENTRY TRACKING# KY022616-1111-8629) CLOSED AED // OFF @ 1044 ON @ 1134 IOS OCR 37830050000116 VER/HFP L3/HFP AJB
3892 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2013-05-20 18:55 | 2013-05-21 02:55 | 13 | 480 | 4140741 | 6240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GARRETT, JAMES G., WORRIX, ROBERT B. MASSEY, DENNIS R. BAD 50 KVA XMER, 7.2 KV, WILL NEED A 50 KVA AND 37.5 KVA TO SPLIT UP LOAD, MATERIAL HANDLER................SEF BAD 50KVA . NEED 2 MAN CREW MATERIEL HANDLER BUCKET TRUCK 50KVA TRANSFORMER 37.5 TRANSFORMER 7200, 2 CUTOUTS 2 ARRESTERS. WILL NEED TO CUT OPEN WIRE TO SPLIT LOAD NEED 2 INSULATORS FOR THATBAD 50KVA . NEED 2 MAN CREW MATERIEL HANDLER BUCKET TRUCK 50KVA TRANSFORMER 37.5 TRANSFORMER 7200, 2 CUTOUTS 2 ARRESTERS. VER/TOM L3/TOM IDC XXXX
3893 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-04-07 15:38 | 2009-04-07 17:59 | 68 | 141 | 50290-1 | 6238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303903//I MADE A MDC//BAD CUTOUT ON POLE 338-25,ISOLATED CUTOUT, CLOSED RECLOSER AT 17:09 RESTORING POWER TO ALL BUT 1 CUSTOMERS..... REPLACED CUTOUT RESTORED POWER TO XFMR ON POLE 338-25 AT 17:50//VER/CRB IDCC TON XXXX
3894 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-06-24 06:48 | 2015-06-24 07:15 | 231 | 27 | 4649141 | 6237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SOURCE SIDE RISER IS OFF OF BASKET,,BASKET APPEARS TO BE OK,,PATROLED LINE AND CLOSED BY-PASS AT 07:15,,TAGGED REC TO B TACKETT FOR REPAIRS TO RISER,,CREW EN-ROUTE,,ALL POWER RESTORED.// VER/ ADH AJB
3895 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-12 12:07 | 2010-05-12 15:10 | 34 | 183 | 60419-1 | 6222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 116-155 IDC XXXX
3896 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-02-06 04:34 | 2008-02-06 09:49 | 27 | 315 | 50359-1 | 6217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3002105 PRIMARY OPEN AT POLE 5095 SEVICER WILL BE ISOLATING TREE CABLE DOWN.// OPENED N TAGED SWITCHES ON POLE 45-5145 AT 07:15// OPENED AN TAGED SWITCHES ON POLE 45-4105 AT 07:45 // CLOSED SWITCHES ON POLE 45-4022 AT 08:05/ SEND TICKET TO PHIL TOLLIVER RELE VER/ARN IDC XXXX
3897 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-02-24 05:03 | 2012-02-24 08:45 | 28 | 222 | 4491141 | 6216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TX CUTOUT CAUSED LINE FUSE TO BLOW REPLACED CUTOUT EVERYONE BACK ON. AJB
3898 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2021-08-24 08:57 | 2021-08-24 11:15 | 45 | 138 | 4142711 | 6210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Solid blade fell open @ 39831148B40977, Changed to 65T and back in @ 11:15//MD MADE
3899 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-08-25 18:52 | 2008-08-25 19:09 | 365 | 17 | 54846-1 | 6205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW OPENED SWITCHES ON POLE 38830806000202 ( 364 CUST) TO ALLOW THEM TO SAFELY REPLACE A CROSSARM. CREW ESTIMATES 15 MINUTES TO MAKE REPAIRS. (RELATED TO ORDER 54825-1 THAT REPORTS BAD X-ARM).//3401101//VER/CRB IDC XXXX
3900 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2022-02-15 05:25 | 2022-02-15 14:02 | 12 | 517 | 4482611 | 6204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Bad 167 step down on pole 177-645. Truck accessible need flaggers Released by crew 077H05
3901 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-11-17 04:32 | 2012-11-17 11:55 | 14 | 443 | 4404171 | 6202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUSE OUT PATROLLING LINE NOW//COD 14// VER/DBM IDC XXXX
3902 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2013-10-13 15:56 | 2013-10-13 18:35 | 39 | 159 | 4933781 | 6201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED OFF ON 37830048A41148//TREE ON CSP XFMR ON 37830048A31147/// WILL OPEN LF FUSE ON 37830048A40043 TO MAKE REPAIRS/// REPAIRS MADE// POWER IS RESTORED VER/CRB L/3 CRB IDC XXXX
3903 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-04-06 17:59 | 2010-04-06 20:08 | 48 | 129 | 59903-1 | 6192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER OPEN ON POLE 328-158, PATROLLING LINE,,ARRESTER BLOWN ON POLE 328-98 FALLING ACROSS PHASE TAKING RECLOSER OUT.. MADE REPAIRS RESTOREED POWER AT 20:08//COD 48// VER/DBM AJB IDC XXXX
3904 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-07-17 03:15 | 2011-07-17 03:58 | 144 | 43 | H4554681 | 6192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED B PHASE REC ON 1125-772// WIRE DOWN @ 1125-190 0315 OPENED -A-C RELOSERS TO MAKE REPAIRS.OPENED B PHASE REC ON 1125-772// WIRE DOWN @ 1125-190//REPAIRED WIRE// POWER RESTORED 190 CC DUP FOR REST.4554681 VER/PDP IDC XXXX
3905 | Pikeville | 3421002 | BREAKS | GRASSY | 2016-04-11 12:01 | 2016-04-11 14:53 | 36 | 172 | 4079951 | 6192 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 69KV CONDUCTOR MELTED OUT BETWEEN ELKHORN CITY AND HASI//SEE DOL CASE 649133//COD 241// AJB
3906 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-06-24 01:44 | 2022-06-24 04:15 | 41 | 151 | 4305581 | 6191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 04:15
3907 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2020-01-04 12:55 | 2020-01-04 17:45 | 28 | 290 | 4211191 | 6185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OUTAGE STARTED AT 1255//38830380000110 20t open--38830356000021 pole top insulator failed--38830356000019 cut in breaker--38830380000110 20t lat open--38830356000021 pole top insulator failed, pole charred to neu-need pole top pin and insulator-nbt--38830356000019 cut in breaker--lat in to breaker at 83-356/19 at 14:10 // Released by crew 078H07 L3/HFP
3908 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-10-11 09:04 | 2009-10-11 13:45 | 22 | 281 | 56643-1 | 6182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | @ NOTIFIED V. MULLINS JOE MORELAND REQUESTS CREW.CREW REQUIRED BACK UPON HILLNO TRUCKS 4 WHEELER OK #4 COPPER SLEEVE WENT BADCREW REQUIRED /SEND TO FRALEYCREW REQUIRED BACK UPON HILLNO TRUCKS 4 WHEELER OK #4 COPPER SLEEVE WENT BAD/SEND TO FRALEY RELEASED BY CREW 078S03 VER/TOM IDC XXXX
3909 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-12-11 07:59 | 2009-12-11 10:46 | 37 | 167 | 60871-1 | 6179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP CREW REQUIRED; LOOP BURNT INTO ON POLE 477/239; NOT TRUCK ACCESSABLE; RELEASED TO LINE CREW RELEASED BY CREW 078S12/CREW ON SITE/WILL HAVE TO OPEN STEP DOWN ON 453-421/FETR1217/VEM //CREATED ORDER 63849-1 FOR STEPDOWN OUTAGE L3/HFP MLR
3910 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-06-12 10:10 | 2018-06-12 15:35 | 19 | 325 | 4589411 | 6175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole 989-B-292 will need replaced. Paul Muncy with DHE will be doing the work. Digs have been called in. Confirmation # 1806120807. Line fuse opened on pole 989-A-139 at 10:10 and tagged to me Joey Reed. Paul Muncy has permission to replace with his when he arrives. Released by crew 079H07 // power back on for now will need to finish tomorrow // Restored @ 1535
3911 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-09-03 09:28 | 2010-09-03 09:49 | 294 | 21 | 63127-1 | 6174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREW OPENED RECLOSER IN ORDER TO REPAIR BAD LOOP ON POLE 850-5//COD 486//RESTORED UP TO OPEN SWS 875-7 @ 0949 //RELATED TO ORDER 63091-1// IDC RECLOSER OPEN FOR 3 MIN TO OPEN SWITCH ON POLE 875A-7 XXXX
3912 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-09-06 13:09 | 2009-09-06 15:15 | 49 | 126 | 51065-1 | 6174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TIE WIRE BROKEN AND LAID ON CROSSARM VER/TOM L3/TOM IDC XXXX
3913 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-06-05 12:02 | 2020-06-05 15:09 | 33 | 187 | 4963371 | 6171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Recloser is open on 645-297 patrolling38830645D20297, One span of #2 alum dn from 645-126 to 645-142. Linecrew only required. Released by crew 078S11//RM on site isolating REC .rec in @15:09 please close tic RM
3914 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2012-08-03 14:04 | 2012-08-03 16:18 | 51 | 134 | 4889251 | 6162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE AND HAVE NOT FOUND ANYTHING. LINE FUSE BLEW WHILE I WAS DRIVING BY. LINE FUSES ON POLES 423-154 AND 423-115 ARE BLOWN. REFUSED CUT-OUT ON POLE 423-154 AT 15:54//ISO 37830423B00154//PATROLLING LINE AND HAVE NOT FOUND ANYTHING. LINE FUSE BLEW WHILE I WAS DRIVING BY. LINE FUSES ON POLES 423-154 AND 423-115 ARE BLOWN. REFUSED CUT-OUT ON POLE 423-154 AT 15:54. REFUSED CUT-OUT ON POLE 423-115 AT 16:18.PATROLLING LINE AND HAVE NOT FOUND ANYTHING. VER/HFP L3/HFP IDC XXXX
3915 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-07-09 22:22 | 2010-07-10 00:56 | 40 | 154 | H64526-1 | 6160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN NEXT TO XFMER CUTOUT ON ONE PHASE OF BANK ON 966-B-604...DONT THINK FUSE IS BLOWN....WILL RAISE UP ABOVE LIGHTS TO TAKE CLOSER LOOK...//...MIDDLE PHS FUSE BLOWN....ARRESTER ON LEFT PHASE BLOWN UP....ALL 3 ARRESTERS NEED REPLACED....NEED CREW....R MARCUM CALLED....GETTING CREW...//...OPENED BLADES ON 966-B-629 @ 00:12..REPLACED 3 ARRESTERS, & ONE CUTOUT ON POLE 966B604.....CLOSED BLADES ON 966B629 @ 00:56....ALL OK....JRV....07/10/10 IDC XXXX
3916 | Hazard | 3420001 | SOFT SHELL | VEST | 2010-02-15 11:57 | 2010-02-15 18:00 | 51 | 363 | 57892-1 | 6153 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER LOCKED OUT ON POLE # 110-151//COD 51// PATROLLING LINE. POLE # 109-17 HAS BURNT OFF AND WILL NEED REPLACED. CALLING FOR HELP//57890-1 IS ASSOCIATED WITH THIS ORDER//OPEN PTS WERE WRONG IN POWERON//MD FILED//OTHER ORDER RESTORED @ 1308 DUE TO SWITCHING WHICH RESULTED IN A PARTIAL RESTORATION (RESTORED 25 CUST)//CUT DEADEND ON POLE # 109-18, RESTORED TO THERE AT 1410// IDCC CNT25 XXXX
3917 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-01-16 23:57 | 2009-01-17 00:26 | 212 | 29 | H56429-1 | 6148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401101// HAVE A PHASE WIRE DOWN @ POLE 806-202// 150 COD - // CREW ENROUTE. SHOULD START RESTORING IN SECTIONS BY 01:00. OPENED PH B&C ON 202 AT 23:57. REPAIRS COMPLETE. CLOSED SWITCHES ON POLE 202 AT 00:26 PICKING UP ALL CUST ON PH B&C AND CUST ON PH A UP TO OPEN RECS ON POLES 806-6 AND 806-186(COLD LOAD PICKUP) CL REC ON 186 AT 00:38. CLOSED REC ON 806-6 AT 1:00 RESTORING REMAINING CUST. SH// 150 CUSTOMER ON SWITCH - 3 MISMAPPED// VER/KEP MADE DUP TO SHOW "B"&"C" PHASE AJB PHASES B AND C.
3918 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2008-05-22 16:37 | 2008-05-22 18:45 | 48 | 128 | 50548-1 | 6144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3301701// CREW OPENED LINE FUSE TO ALLOW THEM TO SAFELY REPLACE A BROKEN/ROTTEN POLE.//COD 48// VER/DBM IDC XXXX
3919 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-12-09 08:08 | 2017-12-09 13:15 | 20 | 307 | 4633011 | 6140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | rotton 4 acsr replaced span
3920 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-12-27 14:35 | 2011-12-27 15:08 | 186 | 33 | 4205721 | 6138 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW OPENED SWITCH TO SAFELY MAKE TEMP REPAIRS ON A ROTTEN POLE THAT WAS LEANING BADLY JOB TO BE WRITTEN FOR PERMENANT REPAIRS RELEASED BY CREW 077H01 ////VER/CRB IDC XXXX
3921 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-01-03 10:02 | 2011-01-03 12:00 | 52 | 118 | 58157-1 | 6136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE OUT ON STEPDOWN XFMR.....POLE 1112-B-149.....DONT SEE A BIRD OR ANIMAL....WILL PATROLL LATERAL, EVEN THO IT IS HIGH DIDE FUSE.....//....LINE OK.....NO HZRDS...WILL RE-FUSE...//...STEPDOWN BAD....WILL ISOLATE & TAG....AND PICK UP CUSTOMERS FROM A BYPASS LINE OFF OF POLE 1112-B-82 ON THE LOW SIDE OF NEARBY 3 PHASE STEPDOWN STATION.....ALL CUSTS RESTORED @ 1200....JRV....01/03/11 VER/KEP L3/KEP IDC XXXX
3922 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-02-21 16:33 | 2015-02-21 18:24 | 80 | 111 | H4064271 | 6136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | B PHASE RECLOSER OUT ON POLE 449-854 COD-64 RECL AT 473-334 IS ON "B" PHASE MD FILED /B PHASE OFF INSULATOR AT POLE 473-125 & BLOWING TOGETHER, OPEN SOLID BLADES ON POLE 473-120 TO ISOLATE/OPENED RECLOSERS AT 16:33, ISOLATED SOLID BLADES CLOSED RECLOSERS AT 16:46 .B PHASE RECLOSER OUT ON POLE 449-854, CLOSED SWITCH AT 1824 TIE WIRE BROKE VER/KEP AJB
3923 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-09-02 19:07 | 2010-09-03 03:00 | 21 | 473 | 63023-1 | 6133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 36729217 // POLE 19-86 25T BACK ON UP TO 1147-923 08;40 RELEASED BY CREW 078S08 AT 2345 , CREWED CLOSED FUSE & CAME BACK OUT. CREWS WILL CONTINUE TO PATROL LINE.STS WR # 36729217 // POLE 19-86 25T BACK ON UP TO 1147-923 08;40 RELEASED BY CREW 078S08 BAD LA ON 1147-843 ALL CUST BACK ON @ 03:05 VER/PDP IDC FAULT POLE IS INCORRECT XXXX
3924 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-09-03 16:50 | 2020-09-03 19:56 | 125 | 186 | 4427431 | 6130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | A phase recloser stirrup burnt off on line side.need crew and flaggers,trk app Released by crew 079S03 opened 19;30 closed 19;56
3925 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-08-10 14:38 | 2012-08-10 18:25 | 27 | 227 | 4924781 | 6129 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--BAD LINE FUSE CUTOUT O 3 PHASE POLE--CAN REACH WITH FROM ACROSS ROAD WITH LARGE BUCKET RELEASED BY CREW 078S07 ( FOUND WIRE DOWN AT POLE 39831123C24526) ;ALL POWER RESTORED AT 18:25 COD-27 ISO LF 39831123C24519 VER/HFP L3/HFP IDC XXXX
3926 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-02-21 13:15 | 2020-02-21 15:01 | 312 | 106 | 4422911 | 6122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened line fuse 38831038D20118 to transfer conductor COD 37 Off @ 1318 cutout failed and tripped recl 38831062000064 COD 275 also @ 1318 recl back in @ 1323 and line fuse in @ 1501 // First call was showing 1315 was given a time of 1318 L3/HFP
3927 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-12-11 22:19 | 2008-12-12 18:44 | 5 | 1225 | 57753-1 | 6121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3308602//SLEEVE PULLED OUTSLEEVE PULLED OUT CLOSED LINE FUSE AT 1842 XFMR FUSE AT 1844 L3/HFP IDCC TOF1242 12/12 XXXX
3928 | Pikeville | 3408103 | SALISBURY | MARTIN | 2008-12-24 15:49 | 2008-12-25 02:00 | 10 | 611 | 63549-1 | 6110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3408103// VER/ARN L3/KEP IDC XXXX
3929 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2013-05-07 03:35 | 2013-05-07 12:23 | 32 | 528 | 4080551 | 6108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF AT 1123-1175, OPENED HOT TAP AT 1123-1130 AND TAGGED TO KYDDCLINE FUSE OUT ON 1123-1118 , COD-32 ISO LF 39831123A31118 VER/HFP L3/HFP IDC XXXX
3930 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-04-12 06:36 | 2010-04-12 12:15 | 18 | 339 | 62168-1 | 6102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/KEP L3/KEP IDC XXXX
3931 | Hazard | 3308001 | JACKSON | S.JACKSON | 2019-07-21 10:19 | 2019-07-21 16:40 | 16 | 381 | 4741101 | 6096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 7200 transformer, needs 37.5 or 50kva about 15 meters on transformer Released by crew 077S05, changed out bad xfmr to 50kva, all power restored @16:40 hrs.p.hicks L3/HFP
3932 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-06-27 08:10 | 2010-06-27 10:05 | 53 | 115 | 58007-1 | 6095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A VER/KEP L3/KEP
3933 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2011-07-24 19:05 | 2011-07-24 23:30 | 23 | 265 | 4612231 | 6095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 078S09 CUST SAW FLASH IN SAME AREA DIFFERENT PL,226-178 BAD BELL TYPE INSLULATOR, TRANSFORMER ON POLE OFF LINE, ALREADY TALK TO VERNON SURGILL LN LEFT FORK RELEASED BY CREW 078S09,, CHANGED 2 INSULATORS, ALL POWER RESTORED//COD 23// VER/DBM IDC XXXX
3934 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-03-25 09:55 | 2018-03-25 12:16 | 45 | 141 | 4089331 | 6095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Primary wire down from reclosure pole 38830140B00136, to pole 38830140B00147. One span, Trucks to pole. #4 primary came out of sleeve. Can open step down on pole 38830140B02002 to do work de-energized. Released by crew 078H04/on site RM opening step down to make repairsopened step down 12:00 closed in 12:16 please close tic RM
3935 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-07-10 11:18 | 2018-07-10 13:54 | 39 | 156 | 4757581 | 6084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary wire has come loose from hot line clamp feeding Caney hollow at 941B-109 i can make repairs after patrolling line repaired broken hot line clamp at 941-B-109.restored power at 13:54.
3936 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-06-11 18:47 | 2010-06-12 04:00 | 11 | 553 | 60337-1 | 6083 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 076H06 LIGHTING ARRESTER BLOWN ON POLE771-420 CHANGING NOW.LINEFUSE OPEN ON 771-5.CHANGED ARRESTER VER/ARN IDC XXXX
3937 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-08-19 22:10 | 2015-08-19 23:53 | 59 | 103 | 4155241 | 6077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4 SOLID COPPER DOWN BETWEEN 44-C4-7680 & 44-D3-7008./ HOT TAP LIFTED @ POLE 38830044D37008/ ISO 38830044D37008/ COD 59 VER/KEP L3/HFP XXXHFP AJB
3938 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-07-10 23:05 | 2015-07-11 02:50 | 27 | 225 | 4771101 | 6075 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 141-96 AND PATROLLING.. FOUND BAD CUTOUT ON POLE 117-548 CREW ON SITE ETR 2:30..ALSO FOUND SPAN OF PRIMARY DOWN FROM POLE 117B-2504 TO 117B-2510 BY TREE.. NEW ETR 3:00//COD 27 AJB
3939 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-04-02 14:44 | 2015-04-02 16:16 | 66 | 92 | 4259471 | 6072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOAD SIDE RISER FELL OUT OF CUTOUT ON POLE 996-128 CAN REACH IT WITH MY TRUCK AND WILL REPAIR IT/COD 67// VER/ ADH L3/DKGXXX VERIFIED WITH VOICE RECORDER AJB
3940 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2016-04-17 00:58 | 2016-04-17 08:45 | 13 | 467 | 4097121 | 6071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT AT FUSEPOLE 214-207 LINE CREW REQUIRED, WILL WORK IN AM//COD 13 AJB
3941 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-06-27 17:41 | 2018-06-28 10:30 | 6 | 1009 | 4681511 | 6054 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830045D16132 sec pole has leg burnt into--hold for crew and tree crew daylight--ds062718 Released by crew 078S01 Waiting on asplundha FETR 12:15 all pwr restored @ 10:30 please close ticket LRM
3942 | Hazard | 3302703 | HAZARD | HAZARD | 2009-10-28 04:53 | 2009-10-28 10:40 | 63 | 347 | 60103-1 | 6051 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3302703// POLE BURNED OFF NEED TO REPLACE RELEASED BY CREW 077S03 POWER RESTORED @ 1040 // G FUGATE L3/HFP IDCC CNT16, FP721 XXXX
3943 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-06-13 16:08 | 2010-06-13 20:10 | 25 | 242 | 62946-1 | 6050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PHASE BROKE IN CLEAR ON POLE 241-8//ISO 37820241B00008 //COD 25 // VER/DBM
3944 | Hazard | 3303902 | LESLIE | WOOTON | 2008-12-21 21:35 | 2008-12-21 23:25 | 55 | 110 | 61926-1 | 6050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP HIGH SIDE CUTOUT ON STEPDOWN TRANSF BAD == REPLACED == POWER OK L3/HFP IDC XXXX
3945 | Pikeville | 3421001 | BREAKS | CITY | 2010-05-08 12:10 | 2010-05-08 15:54 | 27 | 224 | 57828-1 | 6048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIM COMING TO POLE 220-51 IS HOT BUT WHERE BRIDGE ST TAPS ON IS BURNED INTO IN THE CLEAR.DALE ENROUTE SHORTLY TO HELP.OPENED AT 220-61 TO REPAIR AT 15:46PM,CLOSED AND RESTORED TO ALL AT 15:55 IDCC CNT56 XXXX
3946 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-06-23 18:21 | 2015-06-24 05:32 | 18 | 671 | 4646601 | 6039 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | /POLE 1123-6630, 25 T RESTORED @ 20:23, BAD 7200, 75KVA DOUBLE BUSHING ISOLATED @1123-6635. NO TRK TO XFMER. RELEASED BY CREW 078S07///CHANGED BAD 75KVA XFMR///CUTOUT & LA///VOLT CK 123/123/246///TBL TKT COMP.RMV VER/KEP
3947 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2008-01-02 08:15 | 2008-01-02 09:40 | 71 | 85 | 52622-1 | 6035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3301701/ SERVICER OPENED B PHASE TAP AT POLE 394-D-170 TO MAKE REPAIRS.HOTLINE CLAMP BURNED OFF STUPE == REPLACED ==.//VER/CRB IDC XXXX
3948 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-07-17 11:09 | 2019-07-17 12:54 | 119 | 105 | 4720871 | 6035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 cu primary conductor broke in the clear on load side of 38830760D00011. Crew enroute to assist.//COD 34 FROM BEGINNING OF OUTAGE//#4 cu primary conductor broke in the clear on load side of 38830760D00011. Crew enroute to assist. Opened sw 38830784C00023 @ 12:25 to safely make repairs.#4 cu primary conductor broke in the clear on load side of 38830760D00011. Crew enroute to assist. Opened sw 784-23 @ 12:25 to safely make repairs. Made repairs and restored @ 12:54. sh Released by crew 076S02 ¦¦ L3/HFP
3949 | Hazard | 3303902 | LESLIE | WOOTON | 2018-07-07 09:20 | 2018-07-07 15:15 | 17 | 355 | 4747191 | 6035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | restored @ 1515
3950 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-10-25 21:34 | 2013-10-25 23:18 | 58 | 104 | 4963581 | 6032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ON AT 2318 // SPECTRUM DOWN - COMMENTS DID NOT COME BACK// PER VOICE RECORDER CONDUCTOR PULLED OUT OF SLEEVE VER/HFP L3/HFP IDC XXXX
3951 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-07-13 10:43 | 2012-07-13 13:10 | 41 | 147 | 4709731 | 6027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-4557 BAD CUT OUT REPLACED POLE 44-4527 40T LINE FUSE IDC XXXX
3952 | Pikeville | 3407101 | TOPMOST | DEMA | 2012-07-15 09:48 | 2012-07-15 14:35 | 21 | 287 | 4730391 | 6027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOWERED CONDUCTOR, REMOVED SLACK FROM PRIMARY, TRIMMED TREES, INSTALLED NEW CUTOUT AND ARRESTER, AND REFUSED LINE CUTOUT . ALL WORK COMPLETE / GXJ/COD 21 IDC XXXX
3953 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-23 20:13 | 2014-11-23 20:36 | 262 | 23 | H4756851 | 6026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND LAYING ON BRACKET ARCING / OPENED RECLOSER 767-110 @ 2013 TO CLEAR IT/CLOSED @ 2026 --262 CUST/CUTOUT BROKE ON POLE 767-11/// NEED ONE MAN TO ASSIST//REPAIRS MADE//RESTORED AT 00:30 RELEASED BY CREW 079S01 VER/KEP AJB
3954 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2019-12-24 04:34 | 2019-12-24 07:48 | 31 | 194 | 4179231 | 6014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 38830021B30057 B-phase cutout bad, truck ok, crew reqd for someone to observe Released by crew 078H17/ ISO 38830021B30057/ COD 31
3955 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-06-28 15:39 | 2015-06-28 16:10 | 194 | 31 | H4686131 | 6014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET FOR LATERAL BURNT OFF HENDRIX. CREW REQD. 39831124B33073/ ISO 39831124B33073/ COD 58/REPAIRS WILL REQ SWITCHING/FETR1630/VEM/NOTE TO MAPPING LINE FUSE IS NOW ON B PHASE/VEM RELEASED BY CREW 078H14 VER/KEP
3956 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-01-19 05:14 | 2011-01-19 12:17 | 15 | 423 | 62544-1 | 6009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF ON POLE 142-4003, NEED 45/4 ,AND LINE CREW. MAY GET TRUCKS TO POLE. RELEASED BY CREW 078S01/CREW TO CHANGE POLE/FETR1300/VEM/RECLOSER 142-6040 BACK IN AT 1149/XFMR AT 142-4003 STILL OPEN/FETR1300/VEM/XFMR RESTORED 1217/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 //COD 15// VER/DBM IDC XXXX
3957 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-05-19 00:25 | 2020-05-19 04:16 | 26 | 231 | 4852021 | 6006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patroling--38830092A00341 broke c/o --crew req-ds051920 Released by crew 078S01///Complete BR
3958 | Paintsville | 3401802 | INDEX | HOSPITAL | 2008-06-03 01:42 | 2008-06-03 01:50 | 750 | 8 | 54743-1H | 6000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | 3401802//SERVICER IS PATROLLING LINE//B PHASE OUT...UNKNOWN REASON AT THIS TIME..PAINSTVILLE CREWS ON THE WAY TO HELP WALK LINE THROUGH THE MTNS..BB LOOP OPEN ON MT B PHASE ONLY *** FEEDER NOT OUT. SERVICER CHANGE TAPS ON FOLLOWING POLES TO RESTORE CUST. 654-114 5 CC 5 AT 2334 - 654-118 CC 79 AT 2350 AT 0142 OPENED CB _BYPASSED B PHASE REG CLOSED CB AT 0150 ALL CUST RESTORED. DKG/OPEN REG HAD B PHASE OUT THIS IS FOR OPENING BRK TO BYPASS BAD REG VER/PDP
3959 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2019-11-22 13:30 | 2019-11-22 19:50 | 18 | 380 | 4056651 | 6000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE //OPENED TRANSFORMER FUSE @ 1330//NO OUTAGE TILL THEN//bad cut burnt over half of polebad cut burnt over half of pole Released by crew 077S04//LIFTED CLAMP ON THE SOURCE SIDE OF POLE 37830246D00344 THIS OUTED 10 MORE CUSTS @ 1454//1458-1950
3960 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-11-15 07:15 | 2020-11-15 19:45 | 8 | 750 | 4676741 | 6000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | span of wire down between poles 177-76 and 177-380, cannot isolate without re-working manuel pole. will need line crew and manuel r-o-w crew Released by crew 077S02
3961 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2009-01-06 13:33 | 2009-01-06 16:15 | 37 | 162 | 51947-1 | 5994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3001001//COD-37 MD FILED FOR TRANS ON POLE 45/SERVICER PATROLING/3001001// BAD CUTOUT. 38830329000039 L3/HFP IDCC CNT55 XXXX
3962 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2019-12-01 08:04 | 2019-12-01 15:12 | 14 | 428 | 4110341 | 5992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B ph out only cod 14//c o bad pole219 50 t out on 214 closed 1512
3963 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-11-02 23:38 | 2009-11-03 00:06 | 214 | 28 | H56728-1C | 5992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP LEAD ON B PHASE-OPENED A AN C PHASE UP AT 2301 TO MAKE REPAIRS-CALLED CREW// CLOSED C AN B PHASE IN AT 2318-INSULATOR FAILED-B PHASE FUSE BLEW AT 2330-OPENED A PHASE AT 2338 // IDC XXXX
3964 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-05-28 17:43 | 2022-05-28 19:50 | 115 | 127 | 4977851 | 5991 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser failed on c phase switch at pole 1127-B-85, Paul Laynes crew going to help with repairs( COD 42) FROM BEGINNING OF OUTAGE //OPENING A & B PHASES TO MAKE REPAIRS OFF @ 1941 CLOSED @19:50
3965 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2021-06-18 12:06 | 2021-06-18 13:09 | 95 | 63 | 4767101 | 5985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Bad recloser on pole 249-B1-346. A Phase Recloser was by passed and power restored at 13:09.
3966 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-09-28 08:45 | 2012-09-28 10:55 | 46 | 130 | 4094961 | 5980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON POLE 37830022A30353/// PATROLING// BAD CUTOUT ON 37830022000102// REPLACED //TREE ON LINE ON 37830022000111// CUT TREE OFF // POWER IS RESTORED ///VER/CRB L/3 CRB IDC XXXX
3967 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-05-12 14:46 | 2013-05-12 16:41 | 52 | 115 | 4107461 | 5980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOTTOM SIDE OF CUTOUT RISER BURNT OUT PL#39831099B10095////CHANGE CUTOUT AND RISERS///CANNOT REACH WITH SERV BUCKET///NEED LINE CREW AND BIG BUCKET///PAST JERDANS DAIRYBAR ON RIVERSIDE DR. TL AT CSX FOLLOW DOWN BESIDE RAILYARD/// RELEASED BY CREW 078H16/ FETR 17:15 JEH/ REPAIRS COMPLETE POWER REST. @ 16:41 JEH COD-52 ISO PO 39831099B10095 VER/HFP L3/HFP IDC XXXX
3968 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-02-28 14:29 | 2011-02-28 18:02 | 33 | 213 | 64767-1 | 5969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE 38830473000028 PATROLLING LINE FOUND LINE FUSE ON POLE473-34 OPEN PATROLED MAIN LINE FOUND NOTHING RECLOSER ON POLE 473-28 CLOSED BACK AT 1709 PAROLLING TAP 473-34 BAD CUTOUT ON POLE 473-34 CHANGED CUTOUT FUSE CLOSED AT 1802 ALL POWER RESTORED CLOSE TICKET RELEASED BY CREW 078S11//VER/CRB IDCC STP MISSING XXXX
3969 | South Williamson | 3200302 | BELFRY | TOLER | 2009-01-01 01:09 | 2009-01-01 04:50 | 27 | 221 | 50400-1 | 5967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200302ON SITE, BAD CUTOUT AT POLE#1040-A-6, CALLED R MARCUM FOR HELP// 27867361 VER/JHM ADDED CUST FROM TRANS POLE 6 L3/KEP IDC XXXX
3970 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-10-02 06:13 | 2012-10-02 09:54 | 27 | 221 | 4106131 | 5967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F S OUT,WILL PATRL//////BROKEN CUTOUT 983-93,WILL REPLACE///////REPLACED BAD CUTOUT AND RESTORED//COD 27// VER/DBM IDC XXXX
3971 | Whitesburg | 3312902 | JENKINS | JENKINS | 2009-05-02 10:54 | 2009-05-02 16:45 | 17 | 351 | 63078-1 | 5967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP // LOWELL LOOKS LIKE IT IS NOW A 65T FUSE OUT ON POLE 382-A1-102. LINE FUSE IS BLOWN, I AM PATROLLING LINE. I FOUND SOME RT OF WAY PROBLEMS AND CUT THE WORST OF IT BETWEEN POLE 357-114 AND 115. I AM GOING TO GIVE LINE A SHOT. FOUND ROTTEN CROSSARM WITH PRIMARY LAYING ON IT AT POLE 381-167. NEED 2 MEN AND POLE TOP PIN. THIS IS SINGLE PHASE AND I BELEIVE ARM CAN BE ELIMINATED COD-17 ISO POLE 37830382A10102 L3/HFP IDC XXXX
3972 | South Williamson | 3411401 | DEWEY | INEZ | 2011-06-05 02:27 | 2011-06-05 02:36 | 663 | 9 | 4233731 | 5967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | "A" PHASE SWITCH FAILED AT POLE 767-C-150 //VER/GAH IDC XXXX ..
3973 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-12-29 18:52 | 2019-12-30 00:23 | 18 | 331 | 4191071 | 5958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout and arrestor on pole 37830031000008 // cod 18
3974 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-04-04 00:29 | 2017-04-04 13:09 | 24 | 760 | 4610701 | 5958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED LINE FUSE ON 875-167 AT 2 AM (SEE 4610751)..GRD TAGGED..MYSELF.. CHANGED INS ON 875-53..BAD 10 KVA CSP XFMR ON P-874-35.LAST POLE IN THE RT FK OF SUGAR CAMP BR..NO TRUCK ACCESS..LINE FUSE 38830875A00053 BACK IN AT 4.15 (23 CUST).. RELEASED BY CREW 076S01//CREW REQ//COD 24// CREW ON SITE TCM/ CALLED FOR R/W CREW TO CUT PATH TO WINCH CAN UP TCM/ XFMR 38830874000035 @ 1309 (1 CUST)/ VER/BOW /// TIME PER VOICE REC = L3/HFP XXXHFP AJB
3975 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-08-23 12:00 | 2015-08-23 13:33 | 64 | 93 | H4164191 | 5952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 7200 CUTOUT WILL WORK IN THE DAYLIGHT RELEASED BY CREW 077S01ARRIVED AT JOB SIGHT WAITING ON RIGHT OF WAY CREW OPENED SWITCH ON POLE 130 /135 AT 1200 REPAIRS MADE AND CLOSED BACK RESTORING POWER AT 1333 RELEASED BY CREW 077H03// VER/ ADH L3/DKG AJB
3976 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2021-08-31 06:33 | 2021-08-31 10:41 | 24 | 248 | 4182671 | 5952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LF open on 1073/2059--1 span #4CU prim down 1073/16---failed splice--T&G to RMV--making repairs---make repairs---closed 25T LF 1073/2059 @ 10:41---tbl tkt comp---rmv
3977 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-03-12 23:20 | 2009-03-13 06:25 | 14 | 425 | 57673-1 | 5950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | COD-13... C PHASE DOWN AT POLE 344, #4CU, D. HAMILTON ENROUTE ... ALL WORK COMPLETE / GXJ P.O. ADMIN ALL CUST ON AT 0625 IDC XXXX
3978 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-03-14 15:54 | 2016-03-14 19:52 | 25 | 238 | 4844491 | 5950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | C PHASE HOT TAP RISER OPEN AT POLE 1074-15 AND LAYING ACROSS B PHASE, OPENED C PHASE LINE CUTOUT AT POLE 14 AT 17:10 (25 ORIGINAL CUST) . REPAIRS ON POLE 15 COMPLETE, ALL CUSTOMERS RESTORED @ 1952/ OPENED THE OTHER 2 LINE FUSES ON POLE 38831074D00014 @ 1920 (9 CUST) AND RESTORED THE LINE FUSES 38831074D00014 @ 1952/ ISO 38831074D00014/ COD 34/ DUPLICATE IN HOIS/ VER/BOW AJB
3979 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-01-28 12:15 | 2013-01-28 13:15 | 99 | 60 | 4747311 | 5940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER OR CONTROL CABLE IS BAD ON RECLOSER CAUSING IT TO OPEN. WE CLOSED RECLOSER BACK IN AND GOT CUSTOMERS BACK ON. CREW IS ON THE WAY TO CHANGE CONTROL CABLE. ///VER/CRB L/3 CRB IDC XXXX
3980 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-01-04 03:27 | 2012-01-04 06:12 | 36 | 165 | 4231411 | 5940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHG CUTOUT ON 784-261.BACK ON AT 6.12 VER/ARN IDC XXXX
3981 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-10-21 07:55 | 2013-10-21 10:40 | 36 | 165 | 4950461 | 5940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN LINE FUSE AT 9:00 ON 211-47 PRI DOWN AT 211-101 TO 211-102 NEED OF 6A PRI WIRE 100 FT. NO TR. LINE CREW 4 MEN RELEASED BY CREW 078S04 COD-36 ISO LF 38830211000047 VER/HFP L3/HFP IDC CHANGED FROM UNKNOWN XXXX
3982 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-12-12 12:54 | 2010-12-12 14:20 | 69 | 86 | 65596-1 | 5934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38077642 //----REMOVED HOT TAP ON POLE 285-66 ALL POWER ON EXCEPT FOR BARN --- POLE 285-82 IS BURNT OFF // SENT EMAIL AS REQUESTED...HFP COD-70 ISO REC 38830309000008 SEE 65631-1 TO REPLACE POLE 1 CUSTOMER // VER/HFP L3/HFP IDC XXXX
3983 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2016-10-11 07:04 | 2016-10-11 09:05 | 49 | 121 | 4984061 | 5929 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE 49 CUSTOMERS/. PRIMARY OPEN DUE TO HOT LINE CLAMP BURNT OFF REPLACED HOT LINE CLAMP CLOSED FUSE IN EVERYTHING OK VER/HFP L3/HFP AJB
3984 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-08-29 08:57 | 2009-08-29 16:33 | 13 | 456 | 55747-1 | 5928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP WR # 31473882 // LINE FUSE OPEN AT 38830351000105, POLE BROKE AT 38830351000117, LINE CREW REQUIRED, TRUCK OK. IN LINE POLE WITH TAP AND NEED NEW ANCHOR AND GUYWIRE. CLEARED WIRE OUT OF ROAD, 40 POLE. /CREW ON SITE/FETR1730/VEMLINE FUSE OPEN AT 38830351000105, POLE // POLE ROTTED OFF COD-13 ISO LF 38830351000105 L3/HFP IDC XXXX
3985 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-11-12 11:20 | 2011-11-12 14:00 | 37 | 160 | 4069641 | 5920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED OFF ON POLE 1059-93, GOT PHILIP HICKS COMMING TO HELP MAKE REPAIRS RESTORE AT 1400 RELEASED BY CREW 077S05 VER/KEP IDC XXXX
3986 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-02-15 07:40 | 2013-02-15 09:00 | 74 | 80 | 4820911 | 5920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BURNED DOWN AT POLE 333-85 WHEN WE PUT THE POWER ON THIS MORNING ON ANOTHER CASE OF TROUBLE VER/KEP IDC XXXX
3987 | South Williamson | 3411401 | DEWEY | INEZ | 2017-12-13 09:33 | 2017-12-14 19:37 | 21 | 2044 | 4645201 | 5917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | sectionalizer out on pole 38830861C20116///tried it and came back out//will start checking on u/g//CLOSED SECTIONALIZER 38830861C20116 @ 1540 UPTO L/F 38830861C20124 AND L/F 38830861C20137 CLOSED L/F 38830861C20124 @ 1555//OPENED SECTIONALIZER BACK UP @ 1843//CLOSED 38830861C20137 IN @ 2121 THIS DID NOT PICK UP CUSTS//closed sectionalizer @ 2310 upto junction box 38830861C10170 tagged to tommy goble/ power back on @19:37 Released by crew 076H06
3988 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-04-10 02:12 | 2020-04-10 10:00 | 27 | 468 | 4614791 | 5916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection broken at top of cut out.//OPENED L/F @ 0940 CLOSED 1000
3989 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-10-28 08:35 | 2011-10-28 13:44 | 34 | 309 | 4029281 | 5916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 226-25 HAS BURNT OFF AND WIL NEED REPLACED, CALLING FOR CREW. TOOK CLAMP OFF ON POLE 226-212 AND MADE HOT TO THERE, XFMR INCLUDED, MADE HOT TO 212 AT 09:29 RELEASED BY CREW 077S02 RESTORED POWER AT 13:44 RELEASED BY CREW 077H01 ///VER/CRB IDC XXXX
3990 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-03-09 15:06 | 2015-03-09 20:17 | 19 | 311 | 4173391 | 5909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078H16///CHANGED 2 L/AS PL#S38830066000036 & 38830066000059///59 LOOKED TO BE BAD///20T LF IN AT 20:17///NOTHING TO BE ENTERED IN ABNORMAL DB////TBL TKT COMP VER/CRB L3/IDC XXXX
3991 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-03-30 08:42 | 2018-03-30 16:55 | 42 | 493 | 4154461 | 5906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30t lf open @ 117-148, pole top 117-151, no trks, poe top extension, yard dog ?loops cut @ 117-152, 2taps & xfmer stay on. sb closed @ 118-29/ .all cust restored at 16:55/ ISO 38830117D00148/ COD 22/ SWITCHING DOL 814053
3992 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-05-26 00:11 | 2008-05-26 03:58 | 26 | 227 | 51249-1 | 5902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3008702 - PRIMARY & NEUTRAL DOWN AT POLE 188-201 INTERRUPTING 26 CUSTOMERS// AT 0253 OPENED RECLOSER ON POLE 188-180 TO MAKE REPAIRS INTERRUPTING 16 ADDITIONAL CUSTOMERS// AT 0358 MADE REPAIRS AND CLOSED RECLOSER BACK RESTORING ALL CUSTOMERS// (TREE CABLE) SEE ALSO H51249-1 VER/LDA IDC XXXX
3993 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-09-19 06:10 | 2009-09-19 11:12 | 57 | 302 | 53809-1 | 5902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3000202// BURNT OFF POLE TOP (262-6 ) LIFTED HOT TAP AND PLACED GROUNDS ON POLE 262-6, REC. BACK IN AT 07:50. NEEDS LINE CREW TO REPLACE POLE 40/5, TRUCKS TO POLE. RELEASED BY CREW 078S01 REPAIRED @ 11:12 L3/HFP IDC XXXX
3994 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-10-24 20:57 | 2012-10-25 15:00 | 20 | 1083 | 4169781 | 5900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED AT POLE 38831145000042, CLOSED AT POLE 38831144D30084 AT 10:35, TIM HALL INFORMED . JOB IN SYSTEM / GXJ RELEASED BY CREW 074S03,,,ALL POWER RESTORED AT 15:00 RELEASED BY CREW 074H07 VER/KEP IDC XXXX
3995 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2022-02-03 09:01 | 2022-02-03 11:12 | 45 | 131 | 4427491 | 5895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | two broke cutouts, one on pole 184-83 and 1 on 184-144. closed recloser on pole 184-266 back in at 11 :12 hrs, crew coming to replace cutouts Released by crew 077S02
3996 | Hazard | 3303902 | LESLIE | WOOTON | 2011-07-21 08:59 | 2011-07-21 18:48 | 10 | 589 | 4573641 | 5890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART OF SAME OUTAGE AS TICKET 4572391..LC RELEASED BY CREW 077E07 LEAD BURNED OF DEADEND CLAMP ON POLE 365-71 ACROSS CREEK AND CREEK IS RUNNING HIGH WILL HAVE TO WALK IN TO IT FROM JEFF CAUDILLS HSE..LC RELEASED BY CREW 077E07 COD-10 ISO LF 37830365D00072 VER/HFP L3/HFP
3997 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2008-05-01 17:46 | 2008-05-01 19:21 | 62 | 95 | 56127-1 | 5890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CENTER PHASE OUT.A PHASE 62 CUSTOMERS/ TREES ARE ALL IN THIS LINE. NEED TO SEND TO R/W TO BE CUT.......DAH VER/HFP IDCC CDC63 XXXX
3998 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-07-28 17:45 | 2009-07-28 18:16 | 190 | 31 | 55888-1 | 5890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3002002//SERVICER OPENED RECLOSER IN ORDER TO CLEAR UP BROKEN CUTOUT//SEE ORDER 55785-1//COD 190// VER/DBM IDCC TOF1612 XXXX
3999 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-01-08 07:18 | 2014-01-08 13:26 | 16 | 368 | 4257741 | 5888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUSE OPEN ON POLE 468-1, PRIMARY BURNT DOWN AT POLE 467-38, WILL NEEED LINE CREW & #2 ALL. WIRE. RELEASED BY CREW 077S11. GOT WIRE PUT BACK UP CLOSED L/F AT 13:26. //VER/GAH IDC XXXX
4000 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-02-01 15:57 | 2014-02-01 16:03 | 981 | 6 | 4335271 | 5886 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | OPENED CB TO SAFELY BYPASS STATION REGULATOR VER/KEP VER/HFP L3/HFP IDC XXXX
4001 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-02-27 10:08 | 2009-02-27 12:28 | 42 | 140 | 52085-1 | 5880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3308502// CONFIRMED LINE FUSE OPEN PATROLLING LINE// CLEARED A BAD ARRESTOR AT POLE 37830199C00325 ATTEMPTING RESTORE//7200 VOLT ARRESTOR BAD//COD 42// VER/DBM IDC XXXX
4002 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-23 15:24 | 2015-02-23 21:56 | 15 | 392 | 4075841 | 5880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE OUT ON STEPDOWN, POLE # 37830278B00195 BAD STEPDOWN, WILL NEED CREW AND 333 KVA STEPDOWN RELEASED BY CREW 077S02//COD 15// VER/ ADH VER/HFP XXX AJB
4003 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-02-25 20:33 | 2013-02-26 00:03 | 28 | 210 | 4845691 | 5878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | MULLINS & BURTON & STONE & MCCANN // BASKET BURNT OFF AT POLE 2 POLES BACK FROM RECL //POLE 67-85 HOT TAP BURNT OFF CALL CREW NO TRUCK TO POLEPOLE 67-85 HOT TAP BURNT OFF CALL CREW NO TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR0030/VEM/XFMR ON 67-107 BACK IN @0001/RECLOSER ON 67-6022 BACK IN@0003/ALL CUST RESTORED/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDCC PN170 XXXX
4004 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-03-09 15:38 | 2009-03-09 16:30 | 113 | 52 | 56654-1 | 5876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONDUCTOR BROKE WHILE CREW WAS DEADENDING WIRE ON POLE (OLD COPPER). WILL NEED TO OPEN RECLOSER TO MAKE REPAIRS. // A PHASE OUT// 115 COD //2 OUTAGED ON RECLOSER OUTAGE - 113 AFFECTED BY THIS OUTAGE// VER/TOM L3/TOM IDC XXXX
4005 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-11-13 14:19 | 2008-11-13 18:45 | 90 | 266 | 64604-1 | 5873 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3003701//POLE FIRE AT 38830160000143, ISOLATED AT 38830160000065, CREW REQUIRED, 1 CUST OUT AFTER CLOSING REC.POLE FIRE AT 38830160000143, ISOLATED AT 38830160000065, CREW REQUIRED, 1 CUST OUT AFTER CLOSING REC. REC ON AT 15:22.POLE FIRE AT 38830160000143, ISOLATED AT 38830160000065, CREW REQUIRED, 1 CUST OUT AFTER CLOSING REC. REC ON AT 15:22. RELEASED BY CREW 078S05 IDC XXXX
4006 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-03-29 01:36 | 2009-03-29 07:02 | 32 | 326 | 62553-1 | 5872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVR PATROLLING CKT. FOUND BAD TR CUTOUT ON POLE 410-D-192 CALLING D/S FOR BUCKET CREW TO REPLACE. VER/ARN IDC XXXX
4007 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-02-06 16:09 | 2013-02-07 14:15 | 20 | 1326 | 4796841 | 5863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DIP FUSE BLOWN ON 38831152B20211// ISLOATED ELBOW ON 1152- 212 //WILL REFUSE TO 1152-212//REFUSED TO 212 RELEASED BY CREW 074S05// REPAIRS MADE RESTORED AT 14:10 D SAMMONS RELEASED BY CREW 074H02 ///VER/CRB L/3 CRB IDC XXXX
4008 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-06-20 09:46 | 2021-06-20 12:55 | 31 | 189 | 4774481 | 5859 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrestor at pole 39830901C35058
4009 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-05-04 12:27 | 2022-05-04 12:58 | 189 | 31 | 4836621 | 5859 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | crews found Jumper burnt off at Switch pole 37830248C00559 affecting 189 A phase customers FETR 1300
4010 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-11-22 04:04 | 2013-11-22 07:39 | 29 | 215 | 4063891 | 5857 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE 110-7 BACK OUT *** SERVICER PATROLLING WAS OUT ON ORDER 4063871 EARILER.FUSE 110-7 BACK OUT SERVICER PATROLLING WAS OUT ON ORDER 4063871 EARILER. 15T LINE FUSE BROKE WENT BACK WITH 20 T VER/PDP IDC THIS IS PROBABLY OUT STILL FROM AN EARLIER OUTAGE BUT I CAN NOT PROVE XXXX
4011 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-01-10 22:48 | 2014-01-11 02:35 | 59 | 227 | 4270321 | 5853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR FAILED ON 738-31 AND CAUSED RECLOSER TO LOCK OUT. ISOLATED BAD XFMR AND CLOSED RECLOSER 738-404 @ 00:25 RESTORING ALL BUT ONE CUSTOMER. CREW ENROUTE TO CHANGE XFMR. CHANGED XFMR AND CLOSED @ 2:35 RESTORING LAST OUTAGED CUSTOMER. SH RELEASED BY CREW 076S02 VER/KEP L3/HFP IDC XXXX
4012 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-08-20 17:45 | 2022-08-22 18:30 | 2 | 2925 | 4779561 | 5850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Secondary pole 143-B-189 is rotten and leaning toward house,Shawn Goble is on the way to replace pole..DIG 2208221935,Open 17:45 Closed 18:30,Please send copy to Bill Johnson to create job on replacing pole 143-B-189.S Goble replaced secondary pole..
4013 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-03-25 04:01 | 2020-03-25 09:13 | 81 | 312 | 4507921 | 5850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | w new buckley/38830044B378041143 w new buckley.. windstream pole 44b256 burnt off. crew reqd.1143 w new buckley.. windstream pole 44b256 burnt off. crew reqd. Released by crew 078S07,,, OFF@ 0752 ON @ 0855 TRANSFORMER ON @ 0913
4014 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-02-27 19:48 | 2021-02-28 02:30 | 15 | 402 | 4264201 | 5850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | no hazards found, installed a line fuse on pole 38831126B00406, energized 1126-B-122 @ 01:10, will try new line fuse on pole 1126-B-406// found bad insulator on pole 38831150000116, made repairs @ 0215
4015 | Hazard | 3308002 | JACKSON | PANBOWL | 2021-06-29 01:54 | 2021-06-29 09:24 | 13 | 450 | 4819701 | 5850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Dispatched in accordance with KYPCo Late Night Callout Guidelines.// loop burnt up on pole 1059/53Dispatched in accordance with KYPCo Late Night Callout Guidelines. loop burned into at pole 137830050A20053
4016 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-12-22 15:19 | 2010-12-22 16:45 | 68 | 86 | 55106-1 | 5848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER 241-284 IS OUT //NON NETWORK//COD 68HIGH SIDE CUTOUT ON STEPDOWN TRANSFORMER HAS BROKEN IN TWO AT POLE 241-283. I AM GOING TO OPEN THE RECLOSER AT POLE 241-284 AND CHANGE CUTOUT AND THEN CLOSE RECLOSER BACK IN. I CHANGED CUTOUT AND CLOSED RECLOSER IN AT 16:45. IDC XXXX
4017 | Hazard | 3310502 | HADDIX | CANOE | 2016-04-03 19:08 | 2016-04-03 22:00 | 34 | 172 | 4046231 | 5848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 97-14 ROTTED OFF 1977? LINE HOT WILL HAVE TO KILL WHEN WE ARE READY-ENOUGH MEN ALREADY OUT--RONNIE TO BRING POLE-SEND TO TIM RELEASED BY CREW 077S06POLE 97-14 ROTTED OFF 1977? LINE HOT WILL HAVE TO KILL WHEN WE ARE READY-ENOUGH MEN ALREADY OUT--RONNIE TO BRING POLE-SEND TO TIM RELEASED BY CREW POLE REPLACED AND POWER RESTORED AT 10:00 RELEASED BY CREW 077H02 VER/ARN AJB
4018 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2018-12-10 13:07 | 2018-12-10 15:00 | 80 | 113 | 4545281 | 5847 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | lf @ 68-59 open. 12 kv c/o broken & not on maps, feeds towards 68-448. pole 68-858 damaged. tech. // OPENED XFMR FUSE ON POLE 38830068A00858 1410 - 1420 3 CC//lf @ 68-59 open. 12 kv c/o broken & not on maps, feeds towards 68-448. pole 68-858 damaged. tech. Released by crew 078S07lf @ 68-59 open. 12 kv c/o broken & not on maps, feeds towards 68-448. pole 68-858 damaged. tech. Released by crew 078S07,repairs made all cust restored @ 1500 please close ticket thanks.bt // line fuse on pole 38830068A36068 not on map cod 49
4019 | Hazard | 3309302 | VICCO | JEFF | 2014-08-06 17:21 | 2014-08-06 19:00 | 59 | 99 | 4337631 | 5841 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HIGHSIDE RISER OR HOT LINE CLAMP BURNED OFF ON RECLOSER // C PHASE ONLY OUT - 59 CUST (PER BUSSINESS OBJECTS) COD-59 ISO PO @ 37830347A00316 VER/HFP L3/HFP AJB PH C.
4020 | Hazard | 3309302 | VICCO | JEFF | 2014-08-11 13:54 | 2014-08-11 16:20 | 40 | 146 | 4354261 | 5840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HIGH AND LOW SIDE FUSES ARE BLOWN ON STEPDOWN XFMR, PATROLLING LINE. FOUND BAD CUTOUT ON POLE # 346-184, REPLACED CUTOUT AND POWER RESTORED /// COD-40 ISO LF 37830346A00511 VER/HFP L3/HFP AJB
4021 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-08-13 13:02 | 2019-08-13 18:45 | 17 | 343 | 4880081 | 5831 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830404000138 40t lat blown-38830404000123 30/6 burnt off at brace hardhead-crew req Released by crew 078S01 installed 36 in ext. L3/HFP
4022 | Pikeville | 3402003 | KEYSER | MULLINS | 2018-07-22 13:25 | 2018-07-22 15:11 | 55 | 106 | 4834561 | 5830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP FROM RECLOSER BURNT
4023 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-02-05 15:53 | 2008-02-06 04:58 | 71 | 785 | 66643-1 | 5825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3010602//POLE 20-C1-4052 BROKEN, CREW WORKING TO GET PARTIAL RESTORE OPENED SWITCH 1148-6546 @ 1633 CLOSED RECLOSER 1148-4003 @ 1640 RESTORING 35 CUST, OPENED SWITCH 1148-4048 @ 1642, CLOSED SWITCH 1148-5074 @ 1655 TIEING RUSSELL/BEAR RUN AND BELLEFONT/FLATWOODS CIRCUITS RESTORING 16 CUST,OPENED TAP POLE 1148-6537 @ 1706, CLOSED SWITCH ON POLE 6546 @ 1715 ESTORED 7 CUST, CUT LOOPS 20-4053 @ 1905,CLOSED LOOPS @ POLE 6547 @ 1930 REST 6 CUST REPAIRS COMPLETE AND POWER REST VER/KEP IDC XXXX
4024 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2012-07-07 21:11 | 2012-07-08 03:15 | 16 | 364 | 4587471 | 5824 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | ONE PHASE OF OPEN SECONDARY BURNED DOWN..NEED ONE MAN.. AND TREE CREW WITH BUCKET AND CHIPPER. RYAN NEWSOME TO ASSIST /BRYANT LEWIS GETTING TREE CREW //CUT TREES ENOUGH TO GET XFMR BACK IN..NEVER HEARD FR TREE CREW.. //VER/GAH
4025 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-12-29 01:44 | 2016-12-29 04:06 | 41 | 142 | 4247411 | 5822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON POLE 167B-9001.PATROLLED.FOUND BAD DEADEND INSULATOR ON POLE 167B-9001 WILL MAKE REPAIRS..RESTORED./// VER/DKM AJB
4026 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-07-06 14:27 | 2008-07-06 20:55 | 15 | 388 | 63212-1 | 5820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW COMING FROM PIKEVILLE WITH TRANSFORMER TO REPLACE 100KVA TRANSFORMER THAT FAILED. RELEASED BY CREW 076S01 RELEASED BY CREW 076H02 VER/ARN IDC XXXX
4027 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-01-14 09:15 | 2009-01-14 09:45 | 194 | 30 | 54861-1 | 5820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001003//RELATED TO TRBL ORDER 54831-1//CREWS OPENED RECLOSER IN ORDER TO REPAIR DOWNED CONDUCTOR//COD 194// VER/DBM L3/KEP MLR OK
4028 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-04-16 00:59 | 2015-04-16 10:40 | 10 | 581 | 4324411 | 5810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 38830044C24534// BAD 37.5 KVA CSP, 7200 XFMER. UPGRADE TO 50 KVA. RELEASED BY CREW 078S07// ***CHANGE ISO POLE TO 4534**** DID MD ON ALL CUSTOMERS VER/CRB L3/DKGXXX AJB
4029 | Hazard | 3309301 | VICCO | REDFOX | 2011-05-11 12:45 | 2011-05-11 15:00 | 43 | 135 | 4059841 | 5805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON POLE 37830300B00073. VER/HFP L3/HFP
4030 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-01-10 09:11 | 2016-01-10 11:07 | 50 | 116 | H4598231 | 5800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" & "C" PHASE OPEN COD-47/DID NOT SEE ANYTHING ON LINE, VERY FOGGY AND RAINING, TRIED REC. CAME BACK OUT, A LOT OF THIS IS ON HILLSIDE, HOLD TILL DAYLIGHT. ...2 BAD CUTUOTS ON POLE 37830318A00115./OPENED "B" PHASE AT 0911 COD-50/. ...2 BAD CUTUOTS ON POLE 37830318A00115.. 4 BAD CUTOUTS AND INSULATOR..POWER RESTORED @ 11:07 VER/KEP AJB
4031 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-02-16 00:10 | 2012-02-16 13:40 | 12 | 810 | 4351861 | 5800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BUD JOHNS TO ASSIST //FUSE OPEN ON 502-178 PATROLLING LINE //FRALEY, RUGGLES & PRICHARD TO ASSIST //FUSE OPEN ON 502-178 PATROLLING LINE,, POLE 502-118 BROKE OFF. INSTALLED SOLIDBLADE ON 502-110 IDC ESTIMATED TIMES XXXX
4032 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-01-21 13:53 | 2009-01-21 17:00 | 31 | 187 | 58869-1 | 5797 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP WR # 28158492 // AT POLE 37830224D00076 LOOP IN BURNED INTO CALLING FOR ASSISTANCE//SEND TO JEFF COMBS RELEASED BY CREW 077S04 REPAIRED LOOP AND RESTORED POWER AT 1700 JEFF COMBS L3/HFP AJB
4033 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-03-23 10:02 | 2011-03-23 10:16 | 414 | 14 | 56977-1 | 5796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED RECLOSER TO SAFELY MAKE REPAIRS AT POLE 576-A-65 WHERE "C" PHASE HAD BURNT IN TWO COD-542 VER/KEP IDC XXXX
4034 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-05-26 22:17 | 2015-05-27 10:21 | 8 | 724 | 4469101 | 5792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 269C-31 , WILL TAKE BIG BUCKET , WILL BE CLOSE IF BUCKET WORKS POLE , ALSO WILL NEED FLAGGERS . 19.9 CUTOUT . THIS FEEDS POMP HOLLOW . POLE MAY BE MANUEL . RELEASED BY CREW 075H04 COMP.CCW VER/CRB
4035 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-02-04 16:20 | 2020-02-04 19:21 | 32 | 181 | 4362121 | 5792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEF IS OUT,WILL PTRL////////NOTHING EVIDENT,WILL RE-FUSE WHEN HELP GETS TO ME // BAD CUTOUT ON POLE 1082-254 MADE REPAIRS AND RESTORED @ 1921 // Line fuse on pole 38821082000093 protects both taps // MD made
4036 | Pikeville | 3421002 | BREAKS | GRASSY | 2020-02-07 08:09 | 2020-02-07 17:56 | 57 | 257 | 4375881 | 5786 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | DOL 991068 // Grassy 12kV CB G Ph A Line Disc at Breaks burnt up//cod 113 //closed in N.O. GOAB on 220-C4-0993 at 1148 and OPENED Grassy CB G @ 1155//This restored 113 cust on ph A and transferred B & C cust to Breaks - City 12kV ckt //
4037 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-11-29 02:04 | 2015-11-29 08:00 | 24 | 356 | 4490611 | 5784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF -CLEARING TAP WILL RESTORE ALL BUT -840 AROUND 0600-RONNIE AND AUSTON TO HELP ME-ALL ON BUT 2 AT 0600 THE 2 ON AT 8 RELEASED BY CREW 077S06//COD 24// VER/DBM
4038 | Hazard | 3309003 | JEFF | VIPER | 2015-10-09 16:56 | 2015-10-09 22:17 | 18 | 321 | 4333751 | 5778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD ARRESTER ON POLE 37830418000216//MADE AED ON ARRESTER//BAD ARRESTER ON POLE 37830418000216, BAD CUTOUT ON POLE 37830418000150, REPLACED CUTOUT, POWER RESTORED @ 22:17 VER/CRB L3/HFP XXXHFP
4039 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-03-15 22:28 | 2012-03-16 10:30 | 8 | 722 | 4586691 | 5776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW TO CHANGE CUT OUT IN DAYLIGHT BUCKARM THAT HAS TO BE CLIMBED TO WORK WOULD BE SAFER TO DO IN MORNING.RST RELEASED BY CREW 079H01 COD-8 ISO LF 38821086D00235 VER/HFP L3/HFP IDC XXXX
4040 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-10-13 19:23 | 2010-10-14 05:00 | 10 | 577 | 59415-1 | 5770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLING FOR TREE CREW ONLY/TREE CREW BEING CALLED OUT/BAD CUTOUT ON AT 103-9 //VER/GAH IDC XXXX
4041 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2009-01-10 20:21 | 2009-01-10 21:17 | 103 | 56 | 54100-1 | 5768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202202//CUTOUT BAD ON POLE 793-45//COD 103// VER/DBM L3/KEP IDC XXXX
4042 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2009-03-20 17:06 | 2009-03-20 23:21 | 40 | 375 | 60453-1 | 5766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | VER/HPF WR # 29020427 // GUY BROKE AT POLE 37820147B00181 ALLOWING PRIMARY & NEUTRAL TO SAG INTO THE TOPS OF SOME TREES. CALLING FOR CREW TO REPAIR THE GUY & ANCHOR AND RESAG PRIMARY & NEUTRAL. L3/HFP IDC XXXX
4043 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-12-16 19:18 | 2008-12-16 23:40 | 22 | 262 | 59224-1 | 5764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3303903// PATROLING LINE // VER/TOM L3/TOM IDC XXXX
4044 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-05-30 18:43 | 2022-05-30 20:42 | 153 | 107 | 4984231 | 5760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Tie wire broke at pole 144-B-379 allowing conductor to burn into arm,Going to open Recloser on pole 144-B-380 to make repairs..Open@ 20:05.Closed 20:42..
4045 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-04-10 07:42 | 2015-04-10 17:18 | 10 | 576 | 4305541 | 5760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JIM OPENING LINE FUSE TO CHANGE C/O ON PO#4301531 RELEASED BY CREW 078F03// VER/DBM
4046 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-07-31 07:39 | 2008-07-31 08:39 | 96 | 60 | 62572-1 | 5760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001401 -,,,,TRIED FUSE HELD FOR ABOUT 10SECS WILL TAKE CLOSER LOOK,,,FOUND WIRE BARELY TOUCHING POLE,,, I CUT 2FOOT OF POLE OFF AND IT IS BACK ON//COD 96//CONDUCTOR SAGGED DOWN INTO POLE// VER/DBM IDC XXXX
4047 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-27 14:12 | 2008-08-27 20:12 | 16 | 360 | 56332-1 | 5760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308603// FUSE OUT ON POLE 495-21 REPORT OF WIRE DOWN WILL UPDATE WHEN ARRIVEGOT SPAN #2 DOWN ON POLE 496-182 RELEASED BY CREW 075H01//VER/CRB IDC XXXX
4048 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-05-06 01:50 | 2020-05-06 09:50 | 12 | 480 | 4804081 | 5760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DDC TAG/// DOL 1016098 Line fuse out on 200D/117 wire down in road at 200D/117 to 200D/136 primary only looks like hot line clamp brunt primary down line fuse on 200D/117 tagged to KY. DDC no grounds placed #2 alum. need line crew will have to block road Released by crew 077S03 power restored at 09:50
4049 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2020-03-03 22:29 | 2020-03-03 22:47 | 320 | 18 | 4450191 | 5760 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | DOL 997582//related to order 4449091 // Failed CB C at Barrenshe // short outage to close transfer bus at the station to pick up both ckts//cod 320
4050 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2019-01-21 05:42 | 2019-01-21 10:46 | 21 | 304 | 4698021 | 5754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3002105 // 1 phase hendrix down in alley @ 38830045C35095 // B PHASE INITALLY OUT // 0750 OPENED SWS @ 38830045C35145 // trk to pole. open switches on 45-5095 @ 07:50 tagged to r.morgan/RM on site
4051 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-08-27 03:16 | 2008-08-27 06:11 | 38 | 175 | 55589-1 | 5750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3002001 / COD-38 / FOUND BAD RIDGEPIN ON POLE 901C3-5044 / LIFTED HOT TAP ON POLE 901-5038 / WILL CLOSE RECLOSER TO RESTORE ALL BUT A COUPLE CUSTOMERS /FOUND BAD POLE TOP INSULATOR ON POLE 901-5044, HAVE LINE GROUNDED ON POLE 901-5038, I HAVE ALL CUSTOMER BACK ON BUT ONE, AT THIS TIME RELEASED BY CREW 078S06//VER/CRB IDC XXXX
4052 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-02-22 02:53 | 2012-02-22 22:03 | 5 | 1150 | 4475221 | 5750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CORRECT POLE # IS 190-90/NOT 89CREW REQUIRED. BAD TRANS. { 25 KVA/ 7200 }. THIS IS NOT TRUCK ACCESSIBLE. WE CAN SET TRANS. CLOSE TO BASE OF POLE, BUT CAN NOT REACH TRANS. TO CHANGE IT. WE WILL HAVE TO USE BLOCKS AND WINCH LINE. 2 CUSTOMERS OUT. RELEASED BY CREW 074S01//COD
4053 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-08-12 06:23 | 2009-08-12 09:17 | 34 | 174 | 60980-1 | 5748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402002// SERVICE FOUND PROBLEM AT THE RECL POLE. BURNED UP HOT TAP,, SERVICER MAKING REPAIRS. RECL AT MOUTH IS OUT,WILL PATROL/MADE REPAIRS AT RECL,CLOSED AND RESTORED ALL AT 0917 IDC XXXX
4054 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-10-09 06:34 | 2017-10-09 10:15 | 26 | 221 | 4431781 | 5746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED OFF ON POLE 901-43. NEED BIG BUCKET AND 1 MAN..CREW ENROUTE..BACK ON AT 10.15 VER/AWD ACB
4055 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-12-02 09:39 | 2009-12-03 09:35 | 4 | 1436 | 55176-1 | 5744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 50 T BLOWN ON POLE 73-92. WE HAVE A FAILED CUTOUT ON POLE 73-493. I ISOLATED THE TROUBLE POLE DUE TO A LOCKED GATE. I RESTORED SERVICE TO THE OTHER CUSTOMERS AT 1615. MD FILED VER/KEP L3/KEP IDCC FP NULL, PN492 XXXX
4056 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-03-27 04:03 | 2009-03-27 05:30 | 66 | 87 | 61993-1 | 5742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | JUMPER BROKE ON FUSE POLE 207-46, CC 66 GOING TO OPEN FUSE AT 38830207A00115 TO MAKE REPAIRS. FUSE OPENED AT 05:10, 33 CUSTOMERS FUSE CLOSED AT 05:30, ALL CUSTOMERS RESTORED IDC XXXX
4057 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2013-04-12 00:32 | 2013-04-12 03:50 | 29 | 198 | 4001091 | 5742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE RECLOSER OUT ON 992D3-481.PATROLLING.LINE IS UP..TREES GROWN UP INTO LINE SEVERAL PLACES..IF NO HZRDS WILL TRY RECLOSER..//..TRIED RECLOSER..IT LOCKED OUT.WILL FOOT PATROL..FOUND BAD CUTOUT PROTECTING LATERAL ON 1016C10.WILL REPLACE..//..REPLACED CUTOUT.CLOSED RECLOSER.POWER ON.JRV.04/12/13 COD-110 ISO OCR 38820992D30481 VER/HFP L3/HFP IDCC CNT110 ESTIMATED DUE TO MISSMAPPED TRANS XXXX
4058 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2021-03-25 15:48 | 2021-03-25 16:17 | 198 | 29 | 4373371 | 5742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | defective cutout on pole 37830449A40052 has failed and burnt the crossarm/ will need to take an outage on recloser 37830449C21498///bad cutout on pole 449-52.. open recloser on pole 449-1498 to change cutouts. open @ 15:48// cutouts changed. recloser closed @ 16:17///No outage till Recl was opened
4059 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-09-09 20:19 | 2015-09-10 01:38 | 18 | 319 | 4219711 | 5742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | H4219711/ B PHASE ONLY 18 CUSTOMERS/ BAD CUTOUT 38821082000187/ TO SAFELY CHANGE CUTOUT OPENED A &C PHASES 42 CUSTOMERS @0109/ ALL POWER RESTORED @ 0138/ ISO 38821082B20293/ COD 60/ B PHASE ONLY 18 CUSTOMERS RELEASED BY CREW 079H03/ VER/BOW L3/HFP XXXHFP
4060 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-09-05 20:59 | 2012-09-06 03:49 | 14 | 410 | 4021751 | 5740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | A & B OUT (14 CC) GOT TWO LEADS BURNED OFF ON LINE SIDE OF RECLOSER OPEN C PHASE (5 CC) AT 0249 AND CLOSED AT 0340 //VER/GAH IDC XXXX
4061 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-12-08 05:34 | 2010-12-08 08:05 | 38 | 151 | 64251-1 | 5738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PUT WIRE BACK UP AND REFUSED LINE M.D.I.//COD 38 // VER/DBM IDC XXXX
4062 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-11-30 10:44 | 2012-11-30 13:15 | 38 | 151 | 4433101 | 5738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PATROLLING LINE. HOT-LINE CLAMP BURNT OFF ON LINE SIDE OF RECLOSER. REPAIRING. REPLACED STIRRUP AND HOT-LINE CLAMP. CLOSED RECLOSER @ 13:15. SH ///VER/CRB L/3 CRB IDC XXXX
4063 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-01-16 01:04 | 2009-01-16 06:22 | 18 | 318 | 55448-1 | 5724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3311101// 1 SPAN PRIMARY DOWN CLOSED FUSE AT 0615 COULD NOT ISOLATE DUE TO CONSTRUCTION ON POLE VER/CRB L3/KEP
4064 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-11-26 11:30 | 2010-11-26 13:20 | 52 | 110 | H59841-1 | 5720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37889590 19-69 BURNT OFF OPENED REC. ON POLE 19-67 11;30 AM TEP. POLE 40 CLASS 5 BACK ON 13;20//VER/CRB IDC XXXX
4065 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-03-13 16:23 | 2009-03-13 18:07 | 55 | 104 | 58234-1 | 5720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409502//SERVICER OPENED RECLOSER DUE TO FAILED CUTOUT... POLE FIRE//COD 55//ALL CUST RESTORED 1807// VER/DBM IDC XXXX
4066 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-12-05 14:15 | 2013-12-05 17:55 | 26 | 220 | 4101841 | 5720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, I NEED ONE MAN AND A BIG BUCKET//COD 26// VER/DBM L3/HFP IDC XXXX
4067 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-02-23 19:12 | 2016-02-23 22:00 | 34 | 168 | 4752581 | 5712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR AND BROKEN CUT OUT ON POLE 37830223B00101..REPAIRS MADE, POWER RESTORED AT 22:00/ ISO 37830223B00030/ COD 34/ VER/BOW AJB
4068 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-04-02 11:01 | 2011-04-02 15:22 | 36 | 261 | 61321-1 | 5707 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | //ISOLATE ON POLE 122-34,. CLOSE LINE FUSE ON ON POLE 122-39 AT 13:23//37 //VER/CRB IDC XXXX
4069 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-12-13 03:58 | 2021-12-13 08:53 | 51 | 295 | 4190001 | 5706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | jumper burnt off at 3883-0044-B0-0215 affecting 18 customers, servicer to patrol line, will need crew to restore jumper has burnt open at pole 38830044B00215 not by truck. line is hot up to this point Released by crew 078S12///Open Line Fuse 38830044B00130 to make repairs at XXXX/// Open at 08:41 Closed at 08:53 ticket complete. KMG Released by crew 078H11
4070 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-08-19 04:15 | 2011-08-19 05:30 | 76 | 75 | 4728031 | 5700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SAME AS 4727911 RELEASED BY CREW 078S08... RECLOSER OPENED FROM 0415-0530 POLE 142-19 OPENED REC. 04;15 ON 05;30 POLE 142-18 LOOP BURNT ON BAD 1350 INS. REPAIRED POLE 142-17 BAD HOT TAP REPAIRED... RECL OUTAGE ON ORDER 4728031. CC = 76. VER/SDB IDC XXXX
4071 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-07-09 16:32 | 2020-07-09 19:02 | 38 | 150 | 4136671 | 5700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv cutout,C phase 1099-3616.. Released by crew 078S07 crew on site FETR 19:30 LRM all pwr restored @ 19:02 please close ticket LRM
4072 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-05-14 18:09 | 2012-05-14 21:40 | 27 | 211 | 4793671 | 5697 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE BLOWN ON PRIMARY UNDERGROUND RISER POLE, TRIED ONCE WITH A 6T CAME OUT, I ISOLATED RUN OF CABLE FRROM POLE 901-5650 TO PAD TRANSFORMER 901-5701, TRIED AGAIN, FUSE CAME BACK OUT HAVE CALLED FOR CREW TO HELP. CABLE FROM POLE TO PAD IS OLD CABLE WITH NEUTRAL ON THE OUTSIDE. RELEASED BY CREW 078S06//OPENED AT 901-7021@ 21:30 TO CLOSE AT PAD MT 901-5700 POWER RESTORED AT 21:40 BAD CABLE BETWEEN 901-5650 TO 5701 TAGGED W/HOLD CARD //VER/CRB L/3 CRB IDCC CDC94, TON2157 XXXX
4073 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-04-29 19:22 | 2008-04-29 20:47 | 67 | 85 | 55566-1 | 5695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3110903//B PHASE LOOP BURNT OPEN ON POLE 38830042000006 INSTALLED 40T ON 42-177 ///ENTERED MD-HFP VER/HFP IDCC PN11, FEC57 XXXX
4074 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-03-12 10:08 | 2021-03-13 17:46 | 3 | 1898 | 4330661 | 5694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Per Rick Ray Holding til tomorrow 03/13/2021 //bad cutout on 1134-52 opened line 1134-43 map shows solid blade but it is line fuse. Will need gate key for the head of Gabriel Branch and side by side to make repairs, Crew required. Released by crew 074S05Per repaired cutout and restored @1746
4075 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-12-03 04:21 | 2009-12-03 11:52 | 75 | 451 | 62267-1 | 5685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR 32920149 POLE 1123-4523 BURNT OFF 40/5 TRUCK TO POLE NEED 25KVA CUTOUT/LA ON POND PLU. AT THE IN OFF ACKSION OFF WINTERS DR. RELEASED BY CREW 078S08 VER/KEP L3/KEP IDC XXXX
4076 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-07-08 13:36 | 2009-07-08 17:43 | 23 | 247 | 61523-1 | 5681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TREES IN PRIMARY, BAD ARRESTOR//COD 23// VER/DBM AJB
4077 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-07-08 15:38 | 2012-07-08 22:55 | 13 | 437 | 4605411 | 5681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COMPLEETE BROKEN PRI TIE
4078 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2011-06-27 17:51 | 2011-06-28 11:51 | 22 | 1080 | 4422061 | 5679 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFRM CUTOUT BROKE @ POLE 440-81 ON ERIKA LN.,ISOLATED TROUBLE,POWER RESTORED TO ALL BUT 1 CUST.@ 21:30,NO ONE @ THIS TRL & NEIGHBOR SAYS THEY ONLY STAY THERE OCCASIONLY.,DRIVEWAYS & FAULT POLE MARKED WITH RIBBONS.WILL NEED XCO(7.2 KV),ARRESTOR,FIB.BRKT<(LINE CREW)..RGP. RELEASED BY CREW 077E09 RESTORED POWER TO CUSTOMER AT 1151 JKC//COD 22// VER/DBM IDC XXXX
4079 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-10-21 16:30 | 2016-10-21 20:17 | 25 | 227 | H4040481 | 5675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 66 FROM BEGINNING//POLE 1123-7126 BURNT OFF POLE 1123-7060 OPENEDFUSE 16;30 NEED TWO 8FT. CROSS ARMS AND 2-CUTOUTS SEND TO VERNONPOLE 1123-7126 BURNT OFF POLE 1123-7060 OPENEDFUSE 16;30 NEED TWO 8FT. CROSS ARMS AND 2-CUTOUTS SEND TO VERNON RELEASED BY CREW 078S08/FETR2100/VEM/REPAIRS MADE AND ALL CUST RESTORED 2017/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB AJB
4080 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-07-18 06:44 | 2010-07-19 14:15 | 3 | 1891 | 52363-1 | 5673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | I FUSE TRANSFOMER YESTERDAY, CUSTOMER ISAID POWER WENT OFF AGAIN, GARY HAS A JOB TO REPLACE TRANSFOMER AT THIS LOCATION... NEED LINE CREW TO REPLACE TRANSFORMER, CAN USE TRUCK. RELEASED BY CREW 074S05//CREW ON SITE STARTING REPAIRS TCM// IDC XXXX
4081 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-04-09 19:13 | 2015-04-09 21:00 | 53 | 107 | 4299461 | 5671 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L/A ON PL 38830069C24661 CUT IN CLEAR HAD 2 RESTORED POWER30-T KWB/COD 53// VER/ ADH AJB
4082 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-09-29 16:20 | 2008-09-29 16:55 | 162 | 35 | H51920-1 | 5670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3413401//OPENED A PHASE OCR AT POLE 65-162 B AT 14:55//ISO 37830065D00162//COD 16//,OPENED B & C PHASE AT 16:20, REPACED 8 ARM, BRACES AND INSULATORS, ON AT 16:55, ALL WORK COMPLETE / GXJ IDC XXXX
4083 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-09-02 00:01 | 2020-09-02 05:55 | 16 | 354 | 4417071 | 5664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | patrolling line, found wire off insulator at pole 253-223, calling for help. power restored//cod 16
4084 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2018-07-21 22:10 | 2018-07-22 11:39 | 7 | 809 | 4831381 | 5663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | kyddc tags//255-234 line fuse open,,,pole 255-92 broke and 2 spans #4 solid copper down ,,,need 15kva, cutout,clevis ,pole top pin,,trucks to poles,,WINDSTREAM POLE ,,255-234 isolated G&T TO KYDDC Released by crew 078S05//arrived RM removing DDC TAGS &tagging to RM fuse in at 11:39 one cust still out of power cust,pole broke will need to call in when he makes repairs please close tic RM
4085 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-07-31 14:35 | 2022-07-31 20:08 | 17 | 333 | 4643471 | 5661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | crew required.///// 7200 deadend bell is busted out on fuse pole 92-49 and tracking over.//// crew will need a 7200 deadend bell and a #4 copper shoe.its hot up to fuse on pole 92-49 Released by crew 074S03 / isolated Tap @ pole 92-49 restored @ 20:08
4086 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-05-18 16:05 | 2010-05-18 16:51 | 123 | 46 | 64804-1 | 5658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35175327 // HOT -TAP FAILED ON POLE 44-B-2004 COD-123 VER/HFP L3/HFP IDC XXXX
4087 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-10-19 04:14 | 2010-10-19 05:55 | 56 | 101 | 60849-1 | 5656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER BASKET AT POLE 99-3893 FAILED *A PHASE. 49 CC.RECLOSER BASKET AT POLE 99-3893 FAILED A PHASE. 49 CC. RELEASED BY CREW 078H12 VER/PDP IDC DCMT XXXX
4088 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2009-10-15 08:28 | 2009-10-15 14:45 | 15 | 377 | 64300-1 | 5655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ISOLATION POLE APPEARS TO BE 1152B-211 (ACCORDING TO POWER ON) FOUND BAD CABLE BETWEEN 1235 &1292 ALL CUST RESTORED, CABLES TAGGED ON BOTH ENDS CREATED AEP AND MAP DISC IDC XXXX
4089 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2015-04-08 16:44 | 2015-04-09 11:33 | 5 | 1129 | 4291231 | 5645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2150105--RELATED TO 4291091 WHICH IS A ROANOKE DDC TICKET--KY SERVICER PATROLLED LINE & TRIED LINE FUSE AT 1031-C-101 BUT SOURCE SIDE OF LINE IS DE-ENERGIZED FROM WV APCO SIDE--APCO CREW TO PATROL LINE IN RELATED OUTAGE THURSDAY MORNING DUE TO DIFFICULT LOCATION-- POWER RESTORED AT 11:36 RELEASED BY CREW 079S02 ONLY "A" PHASE OUT COD 5 FROM LOOP BURNT OPEN ON WV APCO SIDE AT POLE 1017-B-28 RESTORED WHEN THEY GOT LOOP RESTORED AT 1133 VER/SEF L3/DKGXXX
4090 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-05-25 17:46 | 2008-05-25 19:20 | 60 | 94 | 51205-1 | 5640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000802//REPLACING BASKET AND HOTTAP ON B PHASE DISCONNECT // ISO 38830271C00256 // 60 COD ON B PHASAE // VER/TOM IDC XXXX
4091 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-08-18 05:27 | 2014-08-18 08:35 | 30 | 188 | 4377311 | 5640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER LATE NIGHT GUIDELINES, WILL LOOK AT ON REG. SHIFT IN A.M.BAD CUTOUT @ POLE 182B43781 LINE FUSE IN @ 0835 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/CRB AJB PH C.
4092 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-08-13 12:55 | 2014-08-13 13:05 | 564 | 10 | 4366261 | 5640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO 4365671//HAD TO OPEN RECLOSER TO REPAIR BURNT UP LOOP//COD 553// VER/DBM AJB SEE 4365671 FOR INLT OUTAGE.
4093 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-08-22 14:27 | 2010-08-22 18:10 | 30 | 223 | 59312-1 | 5640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 44-7183 80T UNDERGROUND FUSE OUT B/ PHASE RELEASED BY CREW 078S08//VER/CRB IDCC CNT21, CDC83 XXXX
4094 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-08-04 19:33 | 2015-08-04 21:28 | 49 | 115 | 4978151 | 5635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSSARM FIRE//NO OUTAGE TILL RECLOSER 37830092000170 OPENED @ 1933. PLACED GROUNDS AND TAGGED FOR MYSELF AT RECLOSER POLE 92-170. REPAIRS MADE CLOSED RECLOSER BACK IN AT 21:28 EVERYTHING OK VER/CRB L3/HFP XXXHFP AJB
4095 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-07-31 08:28 | 2009-07-31 10:30 | 72 | 122 | 61848-1 | 5634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REC OUT ON POLE 927, PATROLLED LINE FOUND LOOP BURNT OPEN ON POLE 286 1 SPAN TAP, R/W PROBLEM, RESTORED POWER TO ALL CUST EXCEPT 1 AT 9:45, L/A CLEARED UP LAST CUST RESTORED AT10:30 IDCC MCCNI XXXX
4096 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-04-20 16:11 | 2009-04-21 13:56 | 38 | 1305 | 61580-1 | 5634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 1 FUSE OUT ON POLE 278-264, PATROLLING LINE , FUSE BACK IN ON 264 AT 17:35, POLE BROKE (254-72) PAST LAST FUSE IN HOLLOW, CALLING FOR HELP. TALKED WITH CUST THAT IS STILL OUT, HE SAID OK TO REPAIR TOMORROW RELEASED BY CREW 077S02//COD 38// DID TEMP FIX ON BROKEN POLE WILL M//VER/CRB IDCC PN45, TON1825, FEC57 XXXX
4097 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-08-27 09:32 | 2008-08-27 11:00 | 64 | 88 | 55982-1 | 5632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3311101//REPLACED BAD 6 DISC//COD 64// VER/DBM IDC XXXX
4098 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-01-01 08:54 | 2022-01-01 15:36 | 14 | 402 | 4244191 | 5628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required fuse blown also on 222-164 took out line fuse also 222-116 change to 12 t/line fuse broken needs replaced Released by crew 078S03///Replaced LF c/o///Complete BR
4099 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-06-05 13:07 | 2020-06-05 17:48 | 20 | 281 | 4963811 | 5620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Rec. open @1058-C2-954, checking. 1 span of primary down between pole 38821058D00175 and 38821058D00278. Sleeve pulled out, will be making repairs. Released by crew 074S05// REPAIRED AND RESTORED 1748
4100 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-07-07 10:13 | 2019-07-07 12:30 | 41 | 137 | 4672521 | 5617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 55-254 L3/HFP
4101 | Hazard | 3420001 | SOFT SHELL | VEST | 2012-01-11 22:09 | 2012-01-12 04:00 | 16 | 351 | 4249411 | 5616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE, BAD CUTOUT, WILL HAVE TO REPLACE POLE. POLE # 157-7 // VER/TOM L3/TOM IDC XXXX
4102 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2008-06-01 15:11 | 2008-06-01 19:15 | 23 | 244 | 54061-1 | 5612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3400602//SERVICER OPENED RECLOSER IN ORDER TO MAKE REPAIRS TO BURNT UP LOOP ON POLE 164-47//SEE ORDERS 53751-1 & 53940-1//COD 23// VER/DBM
4103 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-12-03 04:10 | 2012-12-03 08:25 | 22 | 255 | H4437421 | 5610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED PRC CREW--NEED FLAGERS--OPEN AND TAGED SWITCHES ON POLE 39831123D37003 AT 04:10/// CLOSED B AN C PHASE RECLOSERS IN ON POLE 39831123D26526 AT 04:24--NEED HD ARM 3 PINS AND INSULATORS--CUTOUT ARRESTOR--TOP OF POLE BURNT OFF--CAN LOWER EVERYTHING? RELEASED BY CREW 078S07//COD 575 + 22 // IDCC CNT724, TOF252 XXXX
4104 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-06-26 06:36 | 2009-06-26 13:47 | 13 | 431 | 61642-1 | 5603 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE 723-A-242 50 KVA.CLOSED TRANSFORME RIN BLEW TAP FUSE ON POLE 723-A-240 RELEASED BY CREW 079H02 FUSE 41 COD IDCC NEED ANOTHER OUTAGE
4105 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2009-02-12 04:20 | 2009-02-12 16:00 | 8 | 700 | 65895-1 | 5600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPAIRED RISERS IDCC CCO XXXX
4106 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-09-11 19:23 | 2010-09-11 23:07 | 25 | 224 | 65631-1 | 5600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36839751 // DON THIS IS A STEPDOWN THAT IS OUT... LOW SIDE FUSE ON STEPDOWN TRANS. IS BLOWN. I AM PATROLLING LINE NOW. CUTOUT ON POLE 169-97 IS BROKEN DOWN, I AM GOING TO CHANGE CUTOUT. WE CHANGED CUTOUT AND CLOSED TRANS. FUSE IN AT 23:07. IDC XXXX
4107 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2015-09-09 21:56 | 2015-09-09 23:48 | 50 | 112 | 4220301 | 5600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ==== CHANGED CUTOUT N=== REFUSED STEP DOWN POWER OK VER/ARN L3/HFP XXXHFP AJB
4108 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2013-08-28 20:04 | 2013-08-28 22:59 | 32 | 175 | 4716901 | 5600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 50T L.F. A PHASE OUT ON POLE 20D2-6524///PATROLING LINE ///FOUND NOTHING//TALKED TO CUST @ 2408 1ST ST. ALL OK AT RESIDENCE///BAD LA ON POLE 38830020D26541//CLEARED///50T LF BACK IN @ 22:59///PWR CK OK RELEASED BY CREW 078H16//COD 32//AED FILED// VER/DBM IDC XXXX
4109 | South Williamson | 3411401 | DEWEY | INEZ | 2010-04-08 11:11 | 2010-04-08 14:15 | 76 | 184 | 60816-1 | 5599 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 743-C-127. LINE FUSE BLOWED ON POLE 743-C-199 CLOSED LINE FUSE AT 12:06 RELEASED BY CREW 079S01//CREW ON SITE STARTING REPAIRS TCM/ / BACK ON AT 14:15 CHANGED CUTOUT . 16 APARTMENTS WHERE OUT, TCM// CCCC ENTERED MD...HFP IDCC PN48 XXXX
4110 | Hazard | 3302703 | HAZARD | HAZARD | 2012-04-01 16:06 | 2012-04-01 18:05 | 688 | 119 | 4637921 | 5597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 1606 / FEEDER BREAKER OPENED VIA SCADA FOR CREW TO SAFELY ISOLATE BROKEN ARRESTER AT POLE 272-B4-323. CC 688 ---- SDB / 1612 / FEEDER BREAKER CLOSED VIA SCADA, REST 675 CC==== CUTOUT AND ARRESTOR REPLACED AND ALL POWER RESTORED AT 18:05//LAST 13 CUST ON @ 1805 // VER/DBM IDC XXXX
4111 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2021-08-06 19:20 | 2021-08-07 05:55 | 26 | 635 | 4013441 | 5590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Riser fuse on 785-C2-1525 is blown with 10 customers out. I closed fuse @ 21:05 and it came back out also blowing L/F 785-D1-1733. I have called for line crew to assist with trouble shooting. Closed fuse on 785-D1-1733 @ 21:35 restoring all but customers out under fuse 1525/// Located cable to be bad near juct. box 785-C2-9001 isolated @ 785-C2-9002 to make repairs. Closed riser and restored customers on xfmr 785-C2-893 @00:45/// Repaired cable and restored @05:55//
4112 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-05-05 17:37 | 2010-05-05 18:20 | 130 | 43 | 56170-1 | 5590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 34989344 //ONLY C PHASE OPEN //COD 130,, BAD HOTLINE CLAMP ON SOURCE SIDE RECLOSURE, REPLACED CLAMP AND BASKET/// VER/DBM IDC XXXX
4113 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-05-08 02:05 | 2012-05-08 11:24 | 10 | 559 | 4757891 | 5590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CHECKING LINE FUSE STAYED IN FOR 2-MINUTE , ARRESTOR MAY BE BAD RELEASED BY CREW 078S09 VER/KEP IDC HAD TROUBLE FINDING FAULT XXXX
4114 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-11-01 11:09 | 2013-11-01 19:37 | 11 | 508 | 4999451 | 5588 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | DC RECLOSER POLE 146 OPEN CAN NOT CLOSE TILL STATION BREAKER IS REPAIRED TAGGED TO DDC // STA BREAKER BYPASS FUSED DISCS CLOSED AND RESTORED AT 1823 // RESTORED RECLOSER AT 1937 //VER/GAH L3/HFP IDC XXXX
4115 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-06-16 04:55 | 2011-06-16 10:44 | 16 | 349 | 4325311 | 5584 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | TRUCKS TO ALL POLES-ARM BURNT IN TWO ON POLE 38830070A41597-NEED TO REPLACE ARM AND ALL 3 CUTOUTS AND ARRESTORS ON BANK POLE--NEED TO REPLACE 3 200 AMP LINE FUSE CUTOUTS ON POLE 38830070A4106 THESE HAVE 200K FUSES IN THEM--ELLIOT CREWS TO REPAIR AT START TIME RELEASED BY CREW 078S07//COD 16// VER/DBM IDC CHANGED TIME OFF FROM 0354 XXXX
4116 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-01-22 05:52 | 2014-01-22 08:58 | 30 | 186 | H4300171 | 5580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER UNABLE TO RESPOND TO THIS CALL AT THIS TIME DUE TO TERRIBLE ROAD CONDITIONS//THIS WILL BE LOOKED AT WHEN CONDITIONS IMPROVE//*** DAVE SAMMONS LIVES AT HEAD OF THIS HOLLOW , HE WAS DISPATCHED TO CK ** REPORTS POLE BURNED OFF WILL NEED TO OPEN LINE FUSE . AT 0552 (30 CUST) // 2 CUST ON TR @ 38831150000315 // COD-32 ISO LF 38831150000028 DUP IN HOIS VER/HFP L3/HFP IDC XXXX
4117 | South Williamson | 3411401 | DEWEY | INEZ | 2022-04-24 10:17 | 2022-04-24 16:54 | 16 | 397 | 4795071 | 5580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF OPEN BROKE CUTOUT ON POLE 38830768C00125 / HAD TO OPEN TRANSFORMER ON POLE OPENED @1643 ON@1654 RESTORING ALL
4118 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-02-21 11:38 | 2015-02-21 13:08 | 62 | 90 | 4063021 | 5580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPEN RECLOSER 37830273A00041 TO CHANGE TRANSFORMER 37830273A00043/ ISO 37830273A00041/ COD 62/ VER/BOW AJB
4119 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-10 18:31 | 2016-01-10 19:16 | 124 | 45 | H4598731A | 5580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38831027D00064/ CUTOUT FAILED AND BURNT POLE OFF. AJB OUTAGE FOR SEC CB OP. OUT 124.
4120 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-08-08 17:51 | 2011-08-08 20:40 | 33 | 169 | 4683481 | 5577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | REC. OPEN @ 37830311000151// PATROLING//WIRE OFF INS. @ 37830311000006 TIE WIRE BROKE// POWER IS RESTORED COD-33 ISO OCR 37830311000151 VER/HFP L3/HFP IDC XXXX
4121 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-05-30 22:24 | 2010-05-31 05:33 | 13 | 429 | 53796-1 | 5577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE BROKE OUT OF SHOE ON POLE BEHIND FIRST HOUSE 104 DEAD MARE BR. WILL NEED 3 MAN CREW..STEP DOWN HIGH AND LOW SIDE FUSES OPEN LIN NOT GROUNDED RELEASED BY CREW 077H12//STS WR# 35341416 //COD 13 // REPLACED INSULATOR AND DEAD END CLAMP RESTORED POWER AT 0533 JKC IDC XXXX
4122 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-02-13 09:30 | 2014-02-13 12:49 | 28 | 199 | 4380561 | 5572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 2/13/14 AT 11:28 RISER BURNT LOOSE FROM CUTOUT. ON POLE 38831127B00324 CREW REQUIRED CAN GET BUCKET TO POLE RELEASED BY CREW 074M01 VER/HFP L3/HFP
4123 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-09-06 06:07 | 2011-09-06 14:05 | 17 | 478 | 4828301 | 5566 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT IN TWO AT 91-C-327,WILL NEED BIG BUCKET TO ISOLATE AT POLE 91-325,FUSE OUT AT POLE 92-A-663WILL NEED TRACK MACHINE TO SET POLE NO TRUCKS TO POLE L INE CREW AND TREE TREE WILL BE NEEDED TECH TO WRITE UP BURNT POLE POLE RELEASED BY CREW 078S09 VER/HFP L3/HFP IDCC FP NULL XXXX
4124 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-10-24 17:55 | 2010-10-24 19:40 | 53 | 105 | 62610-1 | 5565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER LAYING AGAINST POLE REMOVED RISER NOT SERVING ANYTHING//COD 53// VER/DBM IDC XXXX
4125 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-06-08 04:03 | 2010-06-08 11:11 | 13 | 428 | 58563-1 | 5564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEPDOWN FUSE IS BLOWN, CHECKING LINE//// HIGH SIDE FUSE BLOWN, CHECKED XFMR AND OIL IS LEAKING OUT AROUND LID, NO OIL ON GROUND. 250 KVA STEPDOWN BAD. //COD 13// REPLACED XFMR RESTORED POWER AT 1111 077H01// VER/DBM IDC XXXX
4126 | Pikeville | 3402002 | KEYSER | STONECOAL | 2019-10-18 07:54 | 2019-10-18 10:00 | 71 | 126 | 4164851 | 5564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECL OPEN ON POLE 38821129D00254 ¦¦ RECL CLOSED @ 0831 (38 CUST)RECL OPEN ON POLE 38821129D00254 Sleeve pulled out and 1 span #4 cu down between 1-47 and 1-201, isolated trouble with S/B @1-43, closed rec. @0831.RECL OPEN ON POLE 38821129D00254 Sleeve pulled out and 1 span #4 cu down between 1-47 and 1-201, isolated trouble with S/B @1-43, closed rec. @0831. Got wire put back up and closed S/B @1-43 @1000. L3/HFP
4127 | Hazard | 3310502 | HADDIX | CANOE | 2017-09-01 13:15 | 2017-09-01 14:56 | 55 | 101 | 4316701 | 5555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE 4317211/ BROKE SWITCH CUTOUT ON POLE 37840216000001/ ISO 37840216000001/ COD 55/ VER/BOW SJG (RELATED TO 4317211)
4128 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-05-09 05:39 | 2011-05-09 07:10 | 61 | 91 | 4020781 | 5551 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE BURNED OUT OF HOT TAP ON POLE 239-347. I OPENED RECLOSER ON POLE 239-362 SO I CAN REPLACE HOT TAP. I REPLACED HOT TAP AND CLOSED RECLOSER IN AT 07:10. VER/KEP IDC XXXX
4129 | South Williamson | 3200302 | BELFRY | TOLER | 2011-03-06 08:19 | 2011-03-06 12:01 | 25 | 222 | 50399-1 | 5550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39052274 // FUSE BLOWN ON POLE 1040-7. LEFT TURKEY TOE OUT. POLE TOP BURNED OFF FAILED CUTOUT ON 1040-A-17. CONTACTING CREW MAY LOWER. // ENTERED MD..HFP//IT FORCE CLOSED IDCC PN81 XXXX
4130 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-03-26 07:20 | 2009-03-26 13:20 | 16 | 360 | 61630-1 | 5550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE 902-123, WHICH IS A 405 POLE TO BE BURNTED OFF ABOUT FOOT OF THE TOP, DOES NOT LOOK LIKE WE CAN LOWER IT DOWN, WILL HAVE TO REPLACE THIS POLE, CAN USE TRUCK, NEED CREW ALSO WILL NEED CUTOUT, EVERYTHING ELSE WILL GO BACK RELEASED BY CREW 078S06/CRE//COD 16// VER/DBM IDCC TOF0711 XXXX
4131 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-10-01 02:17 | 2009-10-01 08:27 | 15 | 370 | 60520-1 | 5550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 2206403// ONE SPAN #4 SOLID COPPER PRIMARY DOWN FROM POLE 190-69 TO 190-70. NEED LINE CREW ,TRUCKS TO POLE OK. PULLED OUT QUICK SLEVE. RELEASED BY CREW 078S01..PUT FUSE IN @ 07:20...STAYED IN ABOUT ONE MINUTE...PATROLING ONCE MORE BEFORE RAISING FUSE SIZE ...BLR...ISOLATED TRANSFORMERS PUT ON ONE AT A TIME...COLD LOAD PROBLEMS..ALL POWER BACK ON @ 08:27 DID NOT RAISE FUSE SIZE..BLR VER/KEP L3/KEP IDC XXXX
4132 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2011-09-27 13:42 | 2011-09-27 16:47 | 30 | 185 | 4925141 | 5550 | DISTRIBUTION STATION | EQUIPMENT FAILURE | RELAY | 69-12KV TR 1 TRIPPED DURING MOBILE TRANSFORMER INSTALLATION - SDB / 1647 / ALL CUST RESTORED. 30CC VER/SDB IDC XXXX
4133 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-01-05 17:05 | 2013-01-05 19:53 | 33 | 168 | H4571891 | 5544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CHECKING ///J BAKER & G. WHITAKER & R AMBURGEYCHECKING.PHASE DOWN HOT ON HILLSIDE AT POLE 448-133, , CREW COMING TO MAKE REPAIRS., OPENED BOTH L/F AT POLE 448-130 TO ISOLATE AT 1705, CREW COMING TO MAKE REPAIRS.MADE REPAIRS CLOSED BOTH L/F AT POLE 448-130 AT 19:53. COD-41 ISO LF 37830448B00130 THIS DUP FOR C FROM 4571891 VER/HFP L3/HFP IDC XXXX
4134 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-02-11 11:06 | 2010-02-11 13:54 | 33 | 168 | 56688-1 | 5544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE NOT OUT--HOT TAP LOOP BURNT OPEN ON POLE 38830091C00066--CALLING CREW--SEND TO B FRALEY // WORK REQ 33833469 // 33 OUT AT THIS POINT// BACK ON @ 1354 IDC CHECK TIMES... IDC XXXX
4135 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2017-05-11 21:51 | 2017-05-11 23:54 | 45 | 123 | 4784031 | 5535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIDDLE B PHASE ONLY/ ISO 37820147A00409/ COD 45/ VER/BOW AJB
4136 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2010-04-26 14:21 | 2010-04-26 16:36 | 41 | 135 | 51450-1 | 5535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSERS POLE 917-D-439 DUE TO POLE FIRE AT POLE 917-D-58. OPENED AT 14:21 CLOSED AT 16:36. //VER/GAH IDCC CNT3, TOF1411 XXXX
4137 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-04-06 13:10 | 2015-04-06 17:51 | 20 | 281 | 4280681 | 5530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | HOLD ORDER FOR CREW TO SAFELY REPLACE FAILED GOAB VER/KEP AJB
4138 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-04-25 04:24 | 2010-04-25 08:35 | 22 | 251 | 50568-1 | 5522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF 1056-340, ISOLATE ON POLE 1056-194//VER/CRB IDC CHANGED FROM WEATHER UNKNOWN PER CONF CALL XXXX
4139 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2012-04-25 00:48 | 2012-04-25 02:20 | 60 | 92 | 4705281 | 5520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, FOUND BAD CUTOUT ON POLE 231-45, REPLACED AND RESTORED POWER. CC = 544. VER/SDB IDC XXXX
4140 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-03-05 23:34 | 2011-03-06 04:50 | 25 | 316 | 50257-1 | 5520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING. CUTOUT BROKE DOWN AND BURNT XFMR POLE 38830834D00366 OFF. CREW ENROUTE TO ASSIST. ISOLATED FAULT AT 834-350 AND CLOSED FUSE ON 834-242 @ 2:00 RESTORING UP TO 350. REPAIRS COMPLETE. RESTORED @ 4:50. SH RELEASED BY CREW 076S02 IDC XXXX
4141 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-03-13 12:35 | 2012-03-13 14:53 | 40 | 138 | 4575311 | 5520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FUSE IS STILL IN ON POLE 45//GOING TO PATROL BACK ON THREE PHASE FOR LOOP OPEN//HOT TAP LEAD BURNT INTO ON POLE 794-223//NO TRUCK///CALLED CREW AND THEY ARE COMING TO HELP///LEAD HAD BURNT OPEN AT 794-223///WE HAVE POWER RESTORED A 14:53//HAD TO PUT IN TEMPORARY JUMPER USING STICK//PLEASE PUT IN ABNORMAL DATABASE SO THEY CAN COME SQUEEZE STIRRUP ON ON DRY DAY WHEN CAN WORK WITH TRUCK//COMPLETE//EM VER/HFP L3/HFP IDCC PN45 CNT37 XXXX
4142 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-12-25 11:17 | 2008-12-25 12:17 | 92 | 60 | 63889-1 | 5520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP OPENED CB @ 1117 -- CREW HAD TO OPEN CB TO ISOLATE POLE THAT HAS THE TOP BURNT OFF DUE TO CUTOUT FAILING.. FAULT POLE 37830064000218 L3/HFP IDC XXXX
4143 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-02-12 22:13 | 2020-02-13 00:43 | 37 | 150 | 4399041 | 5517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp burnt off at pole 37830445000067 37cc, isolated stepdown on pole 445-273, replaced clamp at 00:10 37830445000067 1cc, patrolled line didnt see anything restored power at 00:43 37830445D10273 36cc. L3/HFP
4144 | Cannonsburg | 3001401 | LOUISA | CITY | 2014-10-10 15:21 | 2014-10-10 22:25 | 13 | 424 | 4603101 | 5512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ALL THREE FUSES ARE OPEN ON 38830454B10093, POLE 38830454B33159 ARMS BURNT OFF./ CHANGED POLE 38830454B33159// 25T A&C PHASE FUSE/ CENTER B PHASE 50T FUSE/ SEND COPY TO TECHNICIAN TO DETERMINE CORRECT FUSE SIZES PUTTING BACK LIKE IT IS FOR NOW/ HAVE TECHNICIANS SEND CORRECT SIZES TO MAPPING WHEN DONE/ CLOSED LINE FUSE-OPEN POINT @ 22:25// VER/BOW AJB FEC60
4145 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-05-22 18:17 | 2011-05-23 17:15 | 4 | 1378 | 4124701 | 5512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA TRANSFORMER BAD ON POLE 38831151D00111 NEED TO REPLACE 150 HP BULB RELEASED BY CREW 074M01 REPAIRS MADE ON AT 17:15 COD-4 ISO TF 38831151D00111 VER/HFP L3/HFP IDC XXXX
4146 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-07-21 14:49 | 2014-07-22 03:28 | 13 | 759 | 4269471 | 5506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | BAD UG CABLE BETWEEN 115-489 AND 115-477/ BAD FEED THRU AT JUNCTION 115-468/RELEASED BY CREW 078H12 RELEASED BY CREW 078H03..DKG/PER LOG AND SWITCH COORDINATOR/5 CUST REST AT 2000,7 CUST AT 2225,1 CUST AT 0328. VER/DKG/ L3/DKG IDC UG WAS NOT BAD XXXX
4147 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2013-05-06 06:53 | 2013-05-06 10:03 | 140 | 190 | 4075401 | 5502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP ON 880-73 AND TRANSFORMER ON THAT POLE , GOING BACK TO OCR TO PICK UP CUSTOMERS TCM// CLOSED OCR IN AT 07:29 ALL SHOULD BE BACK ON BUT 2 CUSTOMERS, CREW IN ROUTE TO REPAIR BURNT POLE TCM// POLE TOP REPLACED 2 CUSTOMERS BACK ON AT 10:03 TCM// RELEASED BY CREW 076H01 COD-140 ISO OCR 38830881A10246 VER/HFP L3/HFP IDC XXXX
4148 | Hazard | 3303902 | LESLIE | WOOTON | 2010-03-03 11:40 | 2010-03-03 13:45 | 44 | 125 | 62475-1 | 5500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED LINE FUSE TO ALLOW THEM TO SAFELY REPLACE A POLE COD-44 VER/HFP L3/HFP IDC CHANGED CAUSE FROM SCHEDULED PER CONF CALL XXXX
4149 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-07-16 14:45 | 2011-07-16 15:20 | 157 | 35 | 4553861 | 5495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | MIDDLE PHASE RECLOSER BY PASSED//VER/CRB
4150 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-09-27 13:32 | 2013-09-27 18:50 | 33 | 318 | 4892861 | 5494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED BROKEN POLE TRUCKS OK/ISOLATED ON 249-90/40/5 POLE BROKEN 15 KVA TRANSFORMER DEAD END POLE IS 250-219 250-117 BACK ON AT 1530 HRS TO 249-90 RELEASED BY CREW 078S03/FETR 19:00JEH/POWER REST. @18:50// CLOSE TICKET//JEH VER/SEF IDC XXXX
4151 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2008-03-19 16:42 | 2008-03-19 19:45 | 30 | 183 | 58744-1 | 5490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3307303// CKT BREAKER LOCKED OUT SERVICE ENROUTE TO STATION// 1301 INSULATOR BROKE AT POLE 37830224D00056 IDC XXXX
4152 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-07-16 11:24 | 2017-07-16 12:13 | 112 | 49 | 4131281 | 5488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ASSOCIATED WITH ORDER 4130151. OPENED SWITCHES ON POLE 37830024B40352 TO SAFELY MAKE REPAIRS TO LOOP THAT BURNED OPEN. OPENED @ 1124 TO OUTAGE ADDITIONAL 74 CUSTOMERS. 1213 VER/AWD L3/HFP HFPC CNT74 MLR
4153 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-05-06 13:00 | 2017-05-06 20:02 | 13 | 422 | 4761701 | 5486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 37830482B00152//L/F 25T OPENED ON POLE 37830482A00039 NOT SHOWN ON MAP//MADE MD//COD 13//FUSE FEEDS BOTH TAPS//OPEN LINE FUSE ON POLE37830482A00039,,POLE37830482B00152 HAS BAD CUTOUT BURNT 3FT OF POLE OFF, NEED 4 MAN LINE CREW WITH YARD DOG,NEED 45C4 POLE, DOUBLE DEAD END COMPLETE 1 RIDGE PIN,25KV TRANSFORMER,1 CUTOUT,2 CLEVIS,1 GUY VER/CRB
4154 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-07-02 09:58 | 2012-07-02 17:35 | 12 | 457 | 4206371 | 5484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSES OPENED TO ISOLOATE POLE FIRE, FUSES OPEN - CLAMPS STILL ON, 40T, POLE 272-378 IS BURNT OFF NEED 40/4, 1-CUTOUT AND ARRESTOR, 2-8FT ARMS, 1-SET BRACES, 1-GUY COMPLETE, 4-ANGLE PINS, 3 CLEVIS W/SPOOLS, MAY WANT TO HAVE "FORMEN" LOOK AT THIS MAY MOVE VAN AND SOME LUMBER OR MAY BE ABLE TO USE YARD DOG. OKAY PER CUSTOMER -- CAN CLOSE TICKET MWL
4155 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-02-12 13:15 | 2011-02-12 16:38 | 27 | 203 | 56414-1 | 5481 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE CUTOUT ON POLE 38830070B43590 IS BROKEN-CALLING CREW--NEED 200AMP CUTOUT AND BIG BUCKET--E MAIL TO G BELL--REPLACED 200AMP CUTOUT WITH 100AMP CUTOUT AND REPLACED 140K FUSE WITH 100T FUSE-- VER/KEP IDC XXXX
4156 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-02-14 18:35 | 2015-02-15 06:00 | 8 | 685 | 4019461 | 5480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | MAY NEED UP GRADING FOR CAUSE BAD 50 KVA 19.9 SINGLE BUSHING TRUCK OK US E DRIVEWAY TO WORK CREW REQMAY NEED UP GRADING CAUSE BAD 50 KVA 19.9 SINGLE BUSHING TRUCK OK US E DRIVEWAY TO WORK CREW REQ RELEASED BY CREW 078S09,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED// VER/TOM L3/TOM AJB
4157 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2022-01-29 19:15 | 2022-01-29 21:43 | 37 | 148 | 4415231 | 5476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burnt up on pole 187/99. repairs made, power restored
4158 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-03-10 03:25 | 2011-03-10 09:30 | 15 | 365 | 52678-1 | 5475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 1077-D-164---BAD CUTOUT ON AN INACTIVE XFMR AT POLE 1077-C-174--WILL ISOLATE BAD CUTOUT & REFUSE LINE FUSE-- THIS WAS A 40T FUSE POWER ON AT 9:30 MD FILED ON FUSE VER/KEP IDC XXXX
4159 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-01-30 00:26 | 2014-01-30 00:43 | 322 | 17 | 4326421 | 5474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER AT 194-A-115 @ 0026 TO ALLOW CREWS TO SAFELY MAKE REPAIRS// WORK REQUIRED IS DE-ENERGIZED WORK// SHOULD BE APPROX 15-20 MINUTES// CLOSED @ 0043 - THIS RESTORED 322 CC ON THIS ORDER AND 142 ON ORDER 4325941 VER/TOM L3/TOM IDC XXXX
4160 | Whitesburg | 3401301 | FLEMING | NEON | 2011-02-08 11:28 | 2011-02-08 14:00 | 36 | 152 | 55281-1 | 5472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR #38736262 // CUTOUT WENT BAD ON POLE NO. 355-84 AND BURNED TOP OF POLE OFF CREW IS OWN THEIR WAY TO MAKE REPAIRS COD-36 ISO LF 37830355D30017 VER/HFP L3/HFP IDC XXXX
4161 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-19 09:28 | 2015-06-19 14:32 | 18 | 304 | 4609331 | 5472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REC. OUT ON POLE 1016-76/// FOUND ARRESTOR BAD ON POLE 1016-60, WILL HAVE TO CUT PATH TO GET TO POLE WILL LIFT CLAMP OFF XFMR DOSENT SERVE ANYTHING.// REMOVED ARRESTOR OFF LINE, POLE 1016-86 REMOVED GROUNDS, HOLD CARD AND PUT TAP BACK ON LINE. WENT TO REC. POLE 1016-76 AND ENERGIZED IT // POWER RESTORED/FIX IT IN HOIS// VER/ ADH
4162 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-12-21 00:08 | 2012-12-21 00:24 | 342 | 16 | H4493161 | 5472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART OF 4493161//OPENED SWS 454-1651 @ 1208//CLOSED EVERYTHING BACK @ 1224//ISO//COD 342// VER/DBM IDC XXXX
4163 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-12-16 20:55 | 2016-12-16 22:05 | 78 | 70 | 4201501 | 5460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 500KV STEP DOWN TRUCK TO POLE/ NO ONE OUT ORIGINALLY/ OPENING RECLOSER 38830117A00200 TO DROP LOAD SO CAN REPLACE STEP DOWN ON POLE/ OPEN A PHASE LINE FUSE 38830117A00106 AND RECLOSER 38830117A00714 AT THE SAME TIME 2055 / ISO 38830117A00106/ COD 78/ ALL POWER RESTORED 2205/ VER/BOW AJB
4164 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-01-04 03:24 | 2008-01-04 06:00 | 35 | 156 | 53469-1 | 5460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400303////WIRE BROKE IN TWO VER/ARN IDC XXXX
4165 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-09-29 08:28 | 2020-09-29 13:22 | 42 | 260 | 4506911 | 5460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse blown on 195-16 will patrol/// Patrolled line found nothing obvious,Refused line fuse @ 09:57 and came back out will need someone to help me look @ this/// Bad pole top insulator on pole 195-23 will make repairs//repairs made closed switch on pole 195-95 in @ 13;22 and restored all customers Released by crew 074S02
4166 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-01-01 14:17 | 2022-01-01 15:15 | 94 | 58 | 4248461 | 5452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | PART OF OUTAGE EARLIER AND A PHASE RECLOSER DID NOT PICK UP// RESTORED @1515
4167 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2015-04-02 11:57 | 2015-04-02 15:54 | 23 | 237 | 4258711 | 5451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE "A" ONLY//COD 23A PHASE FUSE IS BLOWN AT POLE 38820917D20056. BAD CUTOUT ON POLE 38820917D00134, I WILL REPLACE IT.A PHASE FUSE IS BLOWN AT POLE 38820917D20056. BAD CUTOUT ON POLE 38820917D00134, I WILL REPLACE IT. ALSO TREES IN THE LINE AT POLE 917-B-279 NEEDS CUT.A PHASE FUSE IS BLOWN AT POLE 38820917D20056. BAD CUTOUT ON POLE 38820917D00134, I WILL REPLACE IT. ALSO TREES IN THE LINE AT POLE 917-B-279 NEEDS CUT. SEND TO RYAN ROWE/EMAILED FORESTRY/ADH// VER/ ADH L3/HFP XXX AJB
4168 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2013-10-21 13:54 | 2013-10-21 15:13 | 69 | 79 | 4951881 | 5451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW FOUND PHASE OFF INSULATOR AND HAD TO OPEN SWITCH TO MAKE REPAIRS - NO TRUCK ACCESS OPENED LINE ON POLE 443-19 AT 1354 MADE REPAIRS AND RESTORED POWER AT 1513 CREW 077H01 // COD-69 ISO PO @ 37830443000019 VER/HFP L3/HFP IDC XXXX
4169 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-07-27 16:59 | 2014-07-27 23:02 | 15 | 363 | 4294561 | 5445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, TOP OF POLE BURNTED OFF WILL HAVE TO CHANGE OUT POLE, IS A 405, CAN USE TRUCKS, HAVE LINE FUSE OPEN ON POLE 1121-2002 AND GROUNDED AND TAGGED TO JOE HEMPLEPP RELEASED BY CREW 078S06/CREW ON SITE MAKING REPAIRS/JEHREPAIRS COMPLETE POWER REST. @ 23:02// CLOSE TICKET PLEASE///COD 15// VER/DBM
4170 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-11-24 01:25 | 2018-11-24 12:46 | 9 | 681 | 4471231 | 5444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | will work in the AM 11/24/18 per late night guidelines/ xfmer cutout broke on pole 38830140A00601. isolated, tagged & grounded @ pole 38830140A00329 to R. Morgan. line fuse back in @ 10:29 Released by crew 078H17/arrived RM/ cutout changed and power restored @ 1246 // Xfer on pole 140-329 was off also L3/HFP
4171 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2021-01-15 03:27 | 2021-01-15 11:00 | 12 | 453 | 4870371 | 5436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND CABLE FROM JUNCTION BOX 72-C-544 TO PADMOUNT TRANSFORMER 72-C-480, WILL BE MAKING REPAIRS; REPAIRS COMPLETE ON AT 11:00
4172 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-12-01 11:21 | 2010-12-01 13:52 | 36 | 151 | 61988-1 | 5436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNED OFF CREW ENROUTE //VER/GAH IDC XXXX
4173 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-05-17 09:17 | 2021-05-17 11:48 | 36 | 151 | 4591351 | 5436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no cust out at moment/cutout broke on pole 69d28168/crew reqd/may reach w big bucket. Released by crew 078S04 / had to open rec. on pole 69-8038 due to cutout failure while going over job briefing LRM // RECLOSER OPENED @1130 CLOSED @1148 LR-The first Part Out call came in at 09:17 and all out call at 09:34.
4174 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-12-17 02:25 | 2010-12-17 13:00 | 17 | 635 | 53046-1 | 5431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3PHASE POLE BURNED OFF,WILL CLEAR UP.NEED CREW AND DAYLIGHT.POLE #241-31?/////////HAS TAKEN 3 FUSES OUT AT 217-123 AND ALSO 1 AT 217-37,WILL RE-FUSE THE ONE RELEASED BY CREW //074S06///DEH - CREW ON SITE, WILL MAKE TEMP REPAIRS - WILL HAVE JOB WRITTEN TO REPLACE POLE AT LATER DATE. CLOSED AT 13:00. RELEASED BY CREW 074H03//VER/CRB IDC XXXX
4175 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2021-08-31 17:36 | 2021-08-31 19:05 | 61 | 89 | 4186821 | 5429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND LOOP BURNT OPEN AT POLE 10-5 // repairs made and restored @1905
4176 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-09-18 11:17 | 2018-09-18 17:40 | 23 | 383 | 4125301 | 5427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD TOP OF POLE BURNT OFF. A PHASE WAS BLOWN OPEN OTHER PHASES @1415 Released by crew 077S01 made repairs and restored power at 17:40 L3/HFP
4177 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-02-20 07:56 | 2015-02-21 14:05 | 3 | 1809 | 4051611 | 5427 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED TRUCK APPROACH NEED FLAGGERS WILL HAVE TO SET UP ON U.S. 460. THERE IS AN OIL SPILL I HAVE ALREADY CONTACTED BOB SHURTLEFF TO GET THE OIL SPILL CLEANED UP.. NEED 37.5 2 MEN 2/0 RISER. TIM MCCOY RELEASED BY CREW 074H10/ REPLACED XFMR & RESTORED POWER @ 14:05.MTH RELEASED BY CREW 074E11
4178 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-12-16 18:27 | 2020-12-16 18:36 | 602 | 9 | 4777401 | 5418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on phase A of capacitor bank pole 423-B-53. open recloser on pole 423-C-278 @ 18:27 closed back @ 18:36. removed broke cutout from capacitor bank pole.. cutout needs to be put in abnormal // recloser off@1827 on@1836
4179 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2021-06-09 11:56 | 2021-06-09 14:02 | 43 | 126 | 4696461 | 5418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 6A copper broke @ pole top pin @ 38830067D00112 held up by HT, 65T open @ 67-20. Crew required, No trucks to pole Released by crew 078S02 all pwr restored 14:02
4180 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2020-07-07 20:36 | 2020-07-08 00:42 | 22 | 246 | 4126131 | 5412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 100 kva 7200 trans. @48-A3-357, Steve Ray crew coming to help change out. Released by crew 074S05
4181 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-08-13 20:02 | 2018-08-14 14:04 | 5 | 1082 | 4950491 | 5410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WILL NEED TO CUT DEADENDS AND INSTALL GUY OR REPLACE POLE WITH 40FT CL 4 CUST AGREED TO WAIT IN THE MORNING Released by crew 077S01//DEADENDED @ POLE 37830245A00133 ON THE LOAD SIDE//SENT TO LINE AND TECH /// L3/HFP
4182 | Hazard | 3309302 | VICCO | JEFF | 2018-07-01 13:41 | 2018-07-01 15:45 | 50 | 124 | 4694921 | 5408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED STEP-DOWN @ 1520//LINE OPEN @ 37830348B00094 FROM THE BEGINNING OF OUTAGE//COD 42//CLOSED STEPDOWN IN @ 1545 P/U ALL CUSTS//HOT LINE CLAMP BURNT OFF @ POLE 37830348B00094
4183 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-01-07 14:45 | 2009-01-07 19:19 | 34 | 274 | 52769-1 | 5407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3002107/SERVICER OPENED FUSE TO ISOLATE A BURNING POLE ON ORDER# 52729 POLE#45-532 BURNT NEEDS REPLACED. RELEASED BY CREW 078H143002107/SERVICER OPENED FUSE TO ISOLATE A BURNING POLE ON ORDER# 52729 POLE#45-532 BURNT NEEDS REPLACED. LOOP CUT AT 45-528/FETR2000/VEM FAULT POLE 38830045A20532 ORDER 52989-1 FOR FUSE OPENED TO ALLOW CREW TO MAKE UP LOOPS.3002107/SERVICER OPENED FUSE TO ISOLATE A BURNING POLE ON ORDER# 52729 POLE#45-532 BURNT NEEDS REPLACED. L3/HFP IDC XXXX
4184 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-10-24 11:18 | 2017-10-24 12:05 | 115 | 47 | 4492041 | 5405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PART OF DOL 780444 & PO 4485111/ OPENED SWITCHES TO RESTORE LOOPS/ VER/KEP L3/HFP XXXHFP ACB
4185 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-11-14 18:09 | 2019-11-14 21:45 | 25 | 216 | 4035581 | 5400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Tackett, Bobby A, Fannin, Jacob S,Stevens, Dustin T. & Griffith, Kevin M. pole fire, all wire intact, angle pole w ridge pins, burnt down to guy wire. Could possibly use pole top extenstion, need to move guy wire up on the pole top. may need to splice into the guy wire to move up. truck ok. Released by crew 078H17,repairs made all cust restored @ 2145 please close ticket thanks.bt
4186 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2021-01-07 11:11 | 2021-01-07 14:56 | 24 | 225 | 4854021 | 5400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Lead burnt out of bottom of line fuse cutout. Replaced cutout and restored @ 14:56. sh
4187 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-05-04 22:14 | 2009-05-05 03:14 | 18 | 300 | 53782-1 | 5400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410502//LINE FUSELINE FUSE.REPLACE BAD CUTOUT //VER/GAH
4188 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2011-11-28 21:59 | 2011-11-29 02:30 | 42 | 271 | 4123481 | 5396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 150-179. CC 42. --- SDB / 0004 / FUSE AT POLE 151-69 CLOSED, RESTORES 41 CC. CUTOUT FAILED ON POLE 150-179 --- SDB / 0230 / 1 CC RESTORED. VER/SDB IDC XXXX
4189 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-04-26 09:42 | 2009-04-26 10:40 | 93 | 58 | 62345-1 | 5394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 30008001//HOTTAP ON C PHASE RECLOSER//COD 93// VER/DBM IDC XXXX
4190 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-03-14 19:01 | 2010-03-14 23:45 | 38 | 284 | 50027-1 | 5392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED BROKEN CUTOUT AT 38830400000070, ALL CUSTOMERS RESTORED BUT 2, L MCCARTY IS ON HIS WAY TO REPAIR, NO TRUCKS RELEASED BY CREW 078S05/ALL HILLSIDE WORK IDC XXXX
4191 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-06-29 12:23 | 2009-06-29 18:00 | 16 | 337 | 51241-1 | 5392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP NO CREW REQUIRED COD-16 ISO LF 38830295000001 L3/HFP IDC XXXX
4192 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-11-21 02:25 | 2011-11-21 12:24 | 9 | 599 | 4095911 | 5391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FUSE BLOWN ON 1013-B4-308..POLE 1013-D-97 HAS ROTTED OFF & BROKE IN HALF JUST BELOW XFMR..WIRE DOWN.XFMR ON GROUND BUT NOT LEAKING..NEED CREW..NEED 40 CLASS 4 POLE & 25KVA XFMR.CAN ACCESS WITH TRUCK..PLEASE ROLL UP TO LINE FUSE & SEND TO JOEY REED..CREW WILL WORK JOB @ DAYLIGHT..CHECK WITH PKVLLE ENGNRNG..THERE IS A WO ALREADY WRITTEN FOR THIS ROTTEN POLE..THANX.JRV RELEASED BY CREW 080S01 VER/KEP IDC XXXX
4193 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-05-27 15:03 | 2016-05-27 16:21 | 69 | 78 | 4265271 | 5382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 075H02. REC. OPEN AT POLE 427-30, BAD INSULATOR ON POLE 427-60, WILL BE MAKING REPAIRS. MADE REPAIRS CLOSED REC. AT POLE 427-30 AT 1621./ ISO 37830427A00030/ COD 69/ VER/BOW AJB
4194 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-01-17 01:53 | 2010-01-17 05:20 | 26 | 207 | 55106-1 | 5382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT NEEDS REPLACED/ NEED LARGER BUCKET/CALLING CREW RELEASED BY CREW 078S07CREW ON SITE VER/ARN IDC XXXX
4195 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-04-15 18:11 | 2018-04-15 22:58 | 56 | 287 | 4230741 | 5380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Isolated fault on 37830362000316 by opening at 37830362000112 (transformer will be off).OPENED TAP ON 362-112 WILL NEED CREW TO MAKE REPAIRS ON XFMR CUTOUT TO SAFETY ENERIGIZE BY ..power restored @PRIMARY TAP Released by crew 077S01. power restored @ 22:58 hrs .p.hicks Released by crew 077H09 /// QUESTION ABOUT XFMR ON POLE 37830362000316 NONE ON MAP IN POR - HFP
4196 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-01-10 03:05 | 2016-01-10 07:48 | 19 | 283 | 4598351 | 5377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINEF IS OUT,WILL PTRL//////////BAD INSULATORS,CUTOUT,ARRESTOR ON 1058-118,REPLACED ALL AND RESTORED,ALL OK AFTERWARDS VER/KEP AJB
4197 | Hazard | 3309302 | VICCO | JEFF | 2019-11-11 21:36 | 2019-11-12 03:12 | 16 | 336 | 4021801 | 5376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Looks like bad insulators on 37830323D00316 calling help repairs comp. power ok/ ISO 37830323D00569/ COD 16 L3/HFP
4198 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-11-04 11:55 | 2021-11-04 15:30 | 25 | 215 | 4057061 | 5375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse out on pole 32A-16.had a arrester on pole 32B-66 blow and take out line fuse.i made rapairs and got the 30T line fuse on pole 32A-16 back in @ 15:30
4199 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-12-14 09:42 | 2020-12-14 13:01 | 27 | 199 | 4766441 | 5373 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 W/ETA 0935//NO OUTAGE TILL L/F 38830247000036 OPENED//OPENED @crew required open 247-36 at 0942 hrs /pole388302470001322 no trucks//CREW ENROUTEcrew required open 247-36 at 0942 hrs tagged to ddc/pole 247-132 no trucks Released by crew 078S03///repairs made///LF closed @13:01///complete BR
4200 | South Williamson | 3200301 | BELFRY | BELFRY | 2019-01-12 18:44 | 2019-01-13 01:07 | 14 | 383 | 4662251 | 5362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B Ph only (left hand phase)//cod 14//B phase line fuse is open. Bad transformer cut out. Need big bucket truck.//cod 14 L3/HFP
4201 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-01-05 09:26 | 2013-01-05 11:40 | 40 | 134 | 4570311 | 5360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER BURNDT INTO ON L/F AT POLE 426-258, PATROLLED REST OF LINE, NO TROUBLE, WILL BE MAKING REPAIRS. OPENED THE TRANS ON THIS POLE AT 11:26, CLOSED IT AND THE L/F AT 11:40. SEE 4571491 FOR TR OUTAGE // COD-40 ISO PO @ 37830426B00258 VER/HFP L3/HFP IDC XXXX
4202 | Pikeville | 3421001 | BREAKS | CITY | 2014-03-31 11:15 | 2014-03-31 14:08 | 32 | 173 | 4546891 | 5360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING CUTOUTS AND CROSSARMS ON POLE 37820243D00034 BOBBY TACKETT WILL KEEP TRACK OF THE OUTAGE TIME. RELEASED BY CREW 074S02//COD 28// VER/DBM IDC XXXX
4203 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2015-09-16 13:10 | 2015-09-16 15:04 | 47 | 114 | 4243081 | 5358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND HOT TAP BURNTEDD OFF SOURCE SIDE OF RECLOSER REPLACED AND POWER IS RESTORED TO ALL CUST AT THIS LOC AT 1500 VER/CRB L3/HFP XXXHFP AJB
4204 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-04-18 11:05 | 2012-04-18 12:50 | 51 | 105 | 4683671 | 5355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | C PHASE ONLY// COD 51//STEVE BREWER HELPING//REPLACED BASCKETT ON C PHASE ON POLE 164-110. ///VER/CRB IDC XXXX
4205 | Hazard | 3310502 | HADDIX | CANOE | 2010-04-25 07:42 | 2010-04-25 15:15 | 15 | 453 | 50611-1 | 5355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF MANUAL 40 /FT DEAD END SINGLE PHASE 4 MEN LINE TRUCKTOP OF POLE BURNED OFF MANUAL 40 /FT DEAD END SINGLE PHYSE--RESTORED POWER UP TO POLE # 146-57 FROM FUSE POLE # 145-16 15T AT 09:15 /// COD-15 VER/HFP L3/HFP IDC XXXX
4206 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-01-31 00:53 | 2013-01-31 10:47 | 9 | 594 | 4766981 | 5346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08 CREW REQ, NO 4 CU,TRUCK O.K WIRE BROKE AT RUN-AROUND SHOE, LINE STILL HOT WILL NEED TO OPEN UP LINE FUSE TO WORK FAULT POLE 137-13 WIRE NEED RE-SAG ON POLE 137-297SLIP THRU TIE WIRES TWO POLES TO WORK RELEASED BY CREW 078S09 ///VER/CRB L/3 CRB IDCC CNT13 4 CUSTOMER NOT OUT XXXX
4207 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-07-24 09:01 | 2021-07-24 23:52 | 6 | 891 | 4951041 | 5346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad primary underground cable on pole 172-147. tech coming to look at relocating Released by crew 077S10//WILL JONES(DHE) IS WORKING THIS ORDER//
4208 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-06-03 20:04 | 2010-06-04 01:38 | 16 | 334 | 56138-1 | 5344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE POLE 454/3509; PATROLLING LINE; BAD CUTOUT ON POLE 454/3356; CHANGING CUTOUT; LINE FUSE IN AT 0138 HRS; CLOSE TICKET//COD 16// VER/DBM IDC XXXX
4209 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-06-22 13:57 | 2013-06-22 14:55 | 92 | 58 | 4386111 | 5336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 1147-149 HOT TAP BURNT OFF REPAIRED OPENED REC. 14;45 CLOSED 14;55 COD-92 ISO PO 39831147D10149 VER/HFP L3/HFP IDC XXXX
4210 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-03-09 09:46 | 2012-03-09 12:50 | 29 | 184 | H4566101 | 5336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4566101//OPENED GOAB ON POLE 37830200C00088 @ 0946 (COD + 29), TOP OF POLE 37830200C00091 IS BURNT OFF. --- CUTOUT FOR LATERAL BROKE AND BURNT TOP OF POLE OFF. CREW ON SITE.// IDC NEED 2 ORDERS// VER/DBM IDC XXXX
4211 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-03-14 17:40 | 2009-03-14 19:12 | 58 | 92 | 58567-1 | 5336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN POLE 1104-57,WILL REPLACE THEN GO BACK TO RECLOSER AND RESTORE // C PHASE RECLOSER OUT - 58 COD// // VER/TOM L3/TOM IDC XXXX
4212 | Hazard | 3302704 | HAZARD | KENMONT | 2009-05-12 16:32 | 2009-05-12 17:37 | 82 | 65 | 65846-1 | 5330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3302704//OPENED RECLOSER TO REPLACE CROSSARM == TOOK 16:32 BACK ON AT 17:37 == POWER OK ==//VER/CRB IDC XXXX
4213 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-09-25 23:51 | 2012-09-26 02:50 | 53 | 179 | 4087781 | 5327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT @ POLE #38831124D00065 &ALSO 38831124D00267 POLE FIRE IS @POLE#38831148000314. AM WAITING FORE LINE CREW TO REPAIR.REFUSED @38831124D00267 WITH 30T @ 00:40. CLOSED FUSE ON38831124D00065@02:50 CREATED MD ////// VER/ARN IDCC TOF2248 XXXX
4214 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-01-23 07:01 | 2013-01-23 10:18 | 27 | 197 | 4731691 | 5319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OLD CONDUCTORS FULL OF SPLICES FELL DOWN, PLEASE SEND TO DOUG CHRISTIAN AND MIKE LASSLO. CECIL SEXTON AND HIS CREW ARE ON THEIR WAY TO PUT UP THE WIRE. WE OPENED OTHER TWO RECLOSERS AT 09:50 (SEE ORDER H4731691 COD + 32)//COD 27 (+32) // VER/DBM IDC XXXX
4215 | Pikeville | 3413402 | GARRETT | LACKEY | 2014-12-02 04:53 | 2014-12-02 11:42 | 13 | 409 | 4824351 | 5317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK DURING NORMAL WORK HOURS , CUTOUT FAILED POLE 37830111000076, TOP OF POLE BURNED APART, #6CW,#2AA, # DEADEND INSULATORS, 1 CUTOUT AND ARRESTER, NO TRUCK ACCESS, CAN LOWER EQUIPMENT ON POLEWORK DURING NORMAL WORK HOURS , CUTOUT FAILED POLE 111-76, TOP OF POLE BURNED APART, #6CW,#2AA, # DEADEND INSULATORS, 1 CUTOUT AND ARRESTER, NO TRUCK ACCESS, CAN LOWER EQUIPMENT ON POLE . REPAIRS COMPLETE / GXJ VER/CRB L3/HFP
4216 | Hazard | 3309301 | VICCO | REDFOX | 2008-06-16 22:03 | 2008-06-17 10:42 | 7 | 759 | 66256-1 | 5313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL NEED 7200 CUTOUT REPLACED ON XFMR NEEDS TWO MEN RELEASED BY CREW 077S04 // VER/TOM IDCC CNT1 XXXX
4217 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-09-07 10:20 | 2021-09-07 15:15 | 18 | 295 | 4215931 | 5310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | opened xfmr at 1020. paussed wile waiting on tree crew. bad 50kva 7200 you can get a squit boom to this pole Released by crew 078S12 crew on site fetr 16:00
4218 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-06-29 04:48 | 2020-06-29 07:41 | 98 | 173 | 4087111 | 5310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Wire out of a hot line clamp on pole 222-B-48 (16 COD).//OPENED RECLOSER 37830246C00439 @ 0710 TOTAL COD NOW 98Wire out of a hot line clamp on pole 222-B-48. Recloser on pole 246-C-439 opened from 7:10 to 7:41. Released by crew 077H20
4219 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-11-03 12:18 | 2008-11-03 12:57 | 136 | 39 | 61813-1 | 5304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP POLE 46-2156 CUTOUT BURNT UP 80T FUSE COD-136 IDCC TOF1228 XXXX
4220 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-04-18 13:59 | 2013-04-18 16:35 | 34 | 156 | 4022641 | 5304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | "A" PHASE ONLY COD-34FUSE PULLED INTO VER/KEP IDC XXXX
4221 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2017-07-19 16:46 | 2017-07-19 17:10 | 221 | 24 | 4144011 | 5304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OUTAGE TO REPAIR RECLOSER HOTTAP//COD 221// VER/DBM MLR
4222 | Hazard | 3302703 | HAZARD | HAZARD | 2011-03-06 06:30 | 2011-03-06 06:41 | 482 | 11 | H50279-1 | 5302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SCADA INDICATED THE HAZARD 12KV CB C IS LOCKED OUT// PATROLLING LINE // POLE 296-415 BURNT OFF// IN PROCESS OF ISOLATION TROUBLE AND TRANSFERRING SOME CUSTOMER TO ALTERNATE SOURCE// UPDATED FETR FROM FIELD IDC CORRECT CUSTOMER COUNT IDCC TOF0201, CNT1414 XXXX
4223 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-11-14 15:20 | 2022-11-14 19:45 | 20 | 265 | 4142171 | 5300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out broke and was on metal bracket burning arm in half @ pole 181-10 .will need line crew. Released by crew 077H20.. all power restored @ 19:45 p.hicks // cod 20 // iso 37830181B00007
4224 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-07-26 09:36 | 2009-07-26 09:46 | 529 | 10 | 64905-1 | 5290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 296A-1033.....OPEN GOAB ON POLE 296A-1042 AND MADE BRKR HOT AT 09:46 HRS FOR A PARTIAL RESTORE......CONTRACT CREW ON SIGHT WORKING TO CHANGE INSULATOR. MANUAL CANNOT GET BUCKET TO. REPLACED INSUALTOR & CLOSED GOAB POLE 296-A-1042 AT 1108 RESTORING 97 CUSTOMERS //VER/GAH IDC XXXX
4225 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-04-29 13:14 | 2021-04-30 00:47 | 34 | 383 | 4495031 | 5286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser open @71-162, checking. Isolated URD elbow going from 71-205 to 71-206. Primary bad between junction box 71-163 going to junction box 71-164, going to set a new pole to retire URD line, only 2 padmounts still out 71-201 and 202. Got new riser pole set and picked up 201 and 202 @0047. Released by crew 074S05
4226 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-07-22 16:34 | 2013-07-22 20:58 | 20 | 264 | 4576911 | 5280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PRI. DIP FUSE BLOWN ON 38831152B20211// WILL REFUSE// FUSE CAME BACK OUT// CREW WILL BE EN ROUTE// CABLE BAD BETWEEN 1152-215/ 1152-216/// CABLE PARKED & TAGGED TO DDC RELEASED BY CREW 074S05 VER/SEF IDC XXXX
4227 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-01-24 13:02 | 2008-01-24 16:42 | 24 | 220 | 59415-1 | 5280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LINE FUSE OPEN ON POLE 190-16 FUSE AT FOOT OF POLE. LOOP BURNT OPEN ON POLE 190-17 RELEASED BY CREW 078S01 REPAIRED LOOP CONNECTION ALL POWER RESTORED AT 16:42 VER/KEP IDC XXXX
4228 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-02-15 09:50 | 2017-02-15 11:40 | 48 | 110 | 4399251 | 5280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED APART AT POLE 571//COD 48// REPLACED STIRRUP AND HOT LINE CLAMP POLE 571 , ALL WORK COMPLETE / GXJ//C PHASE ONLY FEEDING TOWARD REC 38830955D20508 VER/CRB L3/HFP XXXHFP AJB
4229 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-12-22 17:12 | 2013-12-22 18:40 | 60 | 88 | 4193201 | 5280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BADNTRANSF ON POLE 37830272B30981 ==== TRANSF JUST SERV D/D LIGHT WILL CHANGE LATER === MADE OPS ORDER TO CHANGE IT === NO CUST JUST ST LIGHT//COD 60// VER/DBM L3/HFP IDC XXXX
4230 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-12-20 19:06 | 2012-12-20 20:04 | 91 | 58 | 4491321 | 5278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RECLOSER IS OPEN ON 478-602 PATROLLING LINE, ONE SPAN OF PRIMARY NEEDS RESAGGED. APR CLOSE TICKET//COD 91// VER/DBM
4231 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-10-16 06:14 | 2019-10-16 13:00 | 13 | 406 | 4144071 | 5278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | cust has checked breaker and reports neighbors are out//. upon further inspection, primary bushing broke & burnt up on xfmer. crew reqd. backyard. should be able to use yard dog. bring xfmer bag. bad 50kva Released by crew 078H17 restored 13:00 L3/HFP
4232 | Hazard | 3302704 | HAZARD | KENMONT | 2017-05-11 20:12 | 2017-05-11 23:35 | 26 | 203 | 4783351 | 5278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE37830320C00058/ ISO 37830320C00017/ COD 26/ VER/BOW AJB
4233 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-02-21 10:24 | 2015-02-22 19:20 | 6 | 1976 | 4062581 | 5276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON PL 37820150000037 6 CUSTOMERS OUT. CREW REQUIRED. NEED AL. PRIMARY DEAD END, CUTOUT AND BRACKET./ ALL ON AT 1555/ WILL HAVE TO LEAVE 37820150000156 OFF UNTIL COUNTY CAN SCRAPE ROAD POLE BURNT OFF, BAD CUTOUT AND BAD TRANSFORMER 15-156/ LINE FUSE OUT ON PL 37820150000037 6 CUSTOMERS OUT. CREW REQUIRED. NEED AL. PRIMARY DEAD END, CUTOUT AND BRACKET. POLE IS 40-4 CREW REQUIRED. MAY BE ABLE TO USE TRACK MACHINE /T, NEEDS MAP DISCREPANCY DONE/ DUPLICATE HOIS
4234 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-03-12 19:59 | 2021-03-12 23:30 | 25 | 211 | 4333061 | 5275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | stirrup and clamp burnt off on load side of step down pole 374-93. repairs made power restored @ 23:30../ ISO 37830374D00093/ COD 25
4235 | South Williamson | 3411401 | DEWEY | INEZ | 2011-09-05 16:17 | 2011-09-05 16:25 | 659 | 8 | 4821681 | 5272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW OPENED RECL AT 767-C-111 TO DE-ENEGIZE TR BANK IN TROUBLE SHORT OUTAGE 3-5 MIN. IDC XXXX
4236 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2008-01-25 11:13 | 2008-01-25 13:44 | 37 | 151 | 59823-1 | 5272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400602// 50T FUSE OUT ON POLE 187C271. IHAVE GOT ONE TRANSFORMER OFF LINE AT POLE 187C305//COD 38////VER/CRB IDC XXXX
4237 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-12-31 04:03 | 2008-12-31 07:52 | 23 | 229 | 65309-1 | 5267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | STS WR# 27856975 // TIE WIRE BROKE. CONDUCTOR HAS FALLEN OFF INSULATOR AND IS LAYING AGAINST POLE TOP PIN. CREW ENROUTE TO ASSIST. OPENED REMAINING 2 PHASES AT 07:15. COMPLETED REPAIRS AND RE-FUSED AT 07:52. SH 23 CUST TOTAL - 18 BC 4 AB & 1 ABC VER/KEP DALE THIS LOOKS LIKE "B" PHASE WHICH MAKES IT 23? NOT SURE ON THIS L3/KEP IDC XXXX
4238 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-12-23 03:05 | 2012-12-23 06:20 | 27 | 195 | 4510191 | 5265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER FOUND LOOP OPEN AT POLE 345-406 NEED 1 MAN & BIG BUCKET. @ 0548 SERVICER OPENED FUSE AT POLE 45-C-45
4239 | Pikeville | 3408101 | SALISBURY | PRINTER | 2020-01-22 16:45 | 2020-01-22 21:22 | 19 | 277 | 4330081 | 5263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN @ POLE 38831147000151//CONDUCTOR CAME OUT OF SLEEVE//COD 19//L/F OUT ON POLE 38831146D00023// L3/HFP
4240 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-01-24 23:22 | 2008-01-25 21:15 | 4 | 1313 | 59974-1 | 5252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303903//REPLACED 15 CSP - ISO/FLT 37830338000026 COD 4// ADDED ONE DUE TO MAP DISC - MAP DISC ISSUED// THESE CUSTOMERS NEVER CAME BACK ON FROM ORIGINAL OUTAGE 59961-1 THE 4 CUSTOMERS HERE WERE REMOVED FROM STEP 3 ON THAT OUAGE//// VER/TOM IDC XXXX
4241 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-10-11 07:58 | 2017-10-11 15:55 | 11 | 477 | 4445441 | 5247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200-50 KVA 69-150, LOW VOLTAGE 1 LEG. CREW REQD. TRK TO POLE. RELEASED BY CREW 078S07 ISO 38830069A10150/ COD 11 MD DONE/ VER/BOW L3/HFP XXXHFP ACB
4242 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-01-12 06:03 | 2010-01-12 14:00 | 11 | 477 | 52963-1 | 5247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33404127 //POLE FIRE // HAD TO OPEN @ POLE 38830429D6009 TO ISOALTE SECTION OF LINE// POLE MAY HAVE TO BE REPLACED// WILL UPDATE FETR ONCE ASSESSMENT IS MADE// ASSOCIATED WITH OUTAGE 52938-1 // COD-11 VER/HFP L3/HFP IDC XXXX
4243 | South Williamson | 3200301 | BELFRY | BELFRY | 2008-02-13 16:43 | 2008-02-13 18:45 | 43 | 122 | 62765-1 | 5246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200301//POLE TOP BURNT OFF 1014-B3-357. CALLED FOR HELP.// C PHASE OUT - 42 SINGLE AND 1 3 PHASE// ISO - 38821014B30377// VER/TOM IDC XXXX
4244 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-08-12 15:09 | 2020-08-12 19:45 | 19 | 276 | 4315351 | 5244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6t transformer fuse out on pole 1098-c-263 due to bad connection on open wire sec burning wire down called crew on the way. wire up fused up bad transformer. changed bad transformer closed fuse in @19:45 everything ok
4245 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-07-07 13:21 | 2010-07-07 21:20 | 26 | 479 | 63042-1 | 5244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR#35885556 POLE 1148-865 80T FUSE OUT SEND TO GREWS A PHASE OUT RELEASED BY CREW 078S08 21:20 POWER ON VER/HFP L3/HFP IDCC CNT154, POSSIBLE 2 MISSMAPPED CUSTOMERS ADDED TO COUNT XXXX
4246 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-08-22 00:23 | 2016-08-22 01:55 | 57 | 92 | 4823351 | 5244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECLOSER TO SAFELY MAKE REPAIRS ON 4823091 VER/KEP // VER TIME PER VOICE REC = L3/HFP XXXHFP AJB
4247 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-10-11 07:00 | 2012-10-11 11:20 | 32 | 260 | 4130531 | 5240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RECLOSER IS OPEN ON 473-28 PATROLLING LINE. POWER RESTORED AT 9:30 TO 449-38 WHERE SOLID BLADE WAS OPENED. PLEASE HAVE ADDED TO MAPS. ALL REPAIRES MADE AND APR AT 1120 CLOSE TICKET. VER/KEP IDC XXXX
4248 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-12-20 16:39 | 2014-12-20 21:01 | 20 | 262 | 4872551 | 5240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 1148-865 80T FUSE OUT CALL VERNON 23 RELEASED BY CREW 078S08/BAD PRIMARY UG/B PHASE/WILL TRY TO SWITCH BAD CABLE OUT/IF SWITCHING GOES WELL SHOULD RESTORE ALL CUST BY 2200/VEM/ALL CUST RESTORED 2101 FROM THE RUSSELL/KENWOOD/DDC TO CREATE ABNORMAL/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP L3/HFP HFPC CDC83 AJB
4249 | Hazard | 3309301 | VICCO | REDFOX | 2016-01-22 07:25 | 2016-01-22 11:47 | 20 | 262 | 4640201 | 5240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS WENT BAD ON POLE 276-154 BURNING PRIMARY INTO ON POLE 276-201, PRIMARY LOOP BURNT INTO ON POLE 276-24. THE LINE FUSE ON POLE 277-38 SHOULD BE ON TAP TOWARDS 218, PLEASE CORRECT MAPS. CREW IS ON THE WAY TO REPAIR. OPENED RECLOSER AT 10:12, ALL POWER RESTORED AT 11:47// VER/ ADH AJB
4250 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-05-16 22:54 | 2015-05-17 03:45 | 18 | 291 | 4437191 | 5238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OPEN ON POLE 375-34, BAD DEADEND BELL ON POLE 375-110 RELEASED BY CREW 077S11..MADE REPAIRS RESTORED POWER AT03:45 AJB
4251 | Hazard | 3303903 | LESLIE | HALSFORK | 2008-02-20 12:26 | 2008-02-20 15:00 | 34 | 154 | 65682-1 | 5236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3303903//SERVICER IS ONSITE//SPAN #4 SOLID COPPER PRIMARY AND NEUTRAL DOWN//COD 34// VER/HFP IDC XXXX
4252 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-03-31 14:05 | 2013-03-31 17:12 | 28 | 187 | 4969811 | 5236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT AT POLE #37820009C00190 POLE TOP BURNED OFF AT POLE 9-C-86. HOMER AND RICHARD IS ON THE WAY. POWER RESTORED AT 17:12. COD-28 ISO LF 37820009C00190 VER/HFP L3/HFP IDC XXXX
4253 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2020-10-01 15:51 | 2020-10-01 20:00 | 21 | 249 | 4518411 | 5229 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hendrix down between 45-4105 and 45-4437 Released by crew 078S07 no outage till 1810/// 21 customers On @hendrix down between 45-4105 and 45-4437 Released by crew 078S07 no outage till 1810/// 21 customers On @20:00///complete BR. LR- The customer call show the person as All Out at 15:51 on 10-1-20.
4254 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2009-05-11 05:41 | 2009-05-11 13:20 | 12 | 459 | 58585-1 | 5228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 353-58, I AM PATROLLING LINE. I DID NOT FIND ANY TROUBLE ON THIS LINE. I AM GOING TO GIVE IT A SHOT. FUSE CAME BACK OUT. I FOUND A BAD CUTOUT AND STRING OF INSULATORS THAT LOOK BURNED ON POLE 329-89. I HAVE OPENED A LOOP ON POLE 329-25 AND I CLOSED LINE FUSE IN AT 1007 PICKING UP ALL BUT ONE CUSTOMER RELEASED BY CREW 077S07 WE MADE REPAIRS AND MADE HOT M.D.I. 05-11-09//VER/CRB
4255 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-07-17 09:55 | 2014-07-17 10:21 | 201 | 26 | 4256271 | 5226 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-525 SPACER BROKE 460 BLACKBURN AVE SEND TO CREWS CAN OPEN 45-505 --- SDB / 201 CC INTERRUPTED AT 0955. --- SDB / 1021 / 201 CC RESTORED AND CKTS RETURNED TO NORMAL. VER/DKG L3/DKG AJB
4256 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2013-11-18 11:38 | 2013-11-18 12:01 | 227 | 23 | 4052951 | 5221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER TO MAKE REPAIRS ON TICKET 4051541 VER/CRB L3/HFP IDC XXXX
4257 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-06-27 15:32 | 2010-06-27 21:20 | 15 | 348 | 58148-1 | 5220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REMOVED ALL ARRESTORS OFF LINE TRIED DIDNT STAY/GOT DOWN TO 6 POLES FOUND BAD LOOKING PIN INSULATOR ON /295-16 GOING TO TRY FUSE IF DONT STAY NEED A CREW/CREW REQUIRED/INSULATOR BETWEEN 295-16 AND 295-22 RELEASED BY CREW 078S03 VER/KEP L3/KEP
4258 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2022-08-27 15:28 | 2022-08-27 22:09 | 13 | 401 | 4803121 | 5213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LF OPEN 901-C2-4579 POLE BROKE AT 39830901C24582 // LINE CREW REQ // TRUCK ACCESS 45 CLASS 4 SINGLE PHASE DEAD END POLE//on site RM LF tag to RM .LF in @ 22:09 please close tic RM
4259 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-09-13 11:47 | 2020-09-13 17:59 | 14 | 372 | 4456841 | 5208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | lifted hottap @ 1148-194 isolating 1148-218 bad 12kv c/o. crew reqd. trk to pole Released by crew 078S07---Crew on site--Tagd & Gndd to RMV--
4260 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-06-21 23:12 | 2013-06-22 08:50 | 9 | 578 | 4384541 | 5202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1147-5016 BAD 50KVA TRUCK OK RELEASED BY CREW 078S08, CREW ON SITE, CHANGED XFMR AND CUTOUT, ALL POWER RESTORED /// COD-9 ISO TF 39831147C35016 VER/HFP L3/HFP IDC XXXX
4261 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-08-06 21:10 | 2011-08-06 21:35 | 208 | 25 | 4673361 | 5200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECLOSERS TO MAKE REPAIRS VINES ON POLE, BROKEN LINE FUSE CUTOUT, CUTOUT BROKE AND FELL ON ARM, OPENED RECLOSERS ON POLE 37830224D00007 AT 21:10, CLOSED AT 21:35, POWER RESTORED. IDCC TOF1839, CNT212 XXXX
4262 | Pikeville | 3407103 | TOPMOST | KITE | 2014-04-01 12:05 | 2014-04-01 14:15 | 40 | 130 | 4550911 | 5200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP HAS BURNED INTO ON RECLOSER POLE 209-25 ON CENTER PHASE ON LOAD SIDE. RECLOSER IS STILL CLOSED. I THINK I CAN OPEN CENTER RECLOSER AND REWORK LEAD. I CHANGED HOT TAP AND RECONNECTED IT TO STIRRUP. I CLOSED CENTER RECLOSER IN AT 14:15//COD 40// VER/DBM IDC XXXX
4263 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-04-21 08:32 | 2012-04-21 12:18 | 23 | 226 | 4691941 | 5198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE-TRIED FUSE ,CAME BACK OUT, NEED 3 MAN PRC CREW TO ASSIST RELEASED BY CREW 078S07PATROLING LINE-TRIED FUSE ,CAME BACK OUT, NEED 3 MAN PRC CREW TO ASSIST--LIFTED HOT TAP AT FAULT POLE-LIGHTING CIRCUIT--WILL REPAIR MONDAY--EMAIL TO MCCARTY//COD 23// VER/DBM IDC XXXX
4264 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-06-17 09:49 | 2008-06-17 13:45 | 22 | 236 | 66508-1 | 5192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREES,VINES, BAD CUTOUT // VER/TOM IDC XXXX
4265 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2018-10-23 20:56 | 2018-10-24 17:35 | 5 | 1239 | 4316961 | 5191 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Customers off transformer 38820966A20495 were already part power (4cc) Open transformer 966-a2-495 at 22:15. Primary dead end pole is rotten at the ground line and is leaning. I cannot climb the pole to see why customers have part power. Pole needs replaced, no truck access. Need 40/5 pole and 25 kva 7200, dead end material/ Opened transformer 38820966A20489 at 1340 and closed 1735 (1cc) L3/HFP
4266 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-03-24 21:52 | 2020-03-25 00:45 | 30 | 173 | 4507411 | 5190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN 1057-65,NEED 1 MAN,19.9 CUTOUT.OUT IN BOTTOM AWAY FROM TRUCK.TOOK LINEF OUT@1057-30 WHERE THIS TAPS OFF THE 3PHASE,WILL REPLACE CUTOUT,THEN CLOSE LINE BACK IN@FUSE POLE////////////RESTORED
4267 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-04-17 14:32 | 2013-04-17 19:05 | 19 | 273 | 4019421 | 5187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WIRE BURN DOWN AT POLE 37830560000008 WIRE OFF INSULATER ON POLE 37830560000010 == NEED LINE CREW AND BIG BUCKET MADE REPAIRES === POWER OK ///VER/CRB L/3 CRB IDC XXXX
4268 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-10-04 10:36 | 2010-10-04 17:30 | 23 | 414 | 56629-1 | 5187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED CALLED TECH 45/4 BURNT OFF TRUCKS MAYBE BAD LOCATION BEHIND TRAILOR/ISOLATED ON 250 141 5 CUSTOMERS WIL STILL BE OF226-17 BACK IN AT 1315HRS RELEASED BY CREW 078S03 ALL POWER RESTORED AT 17:30 RELEASED BY CREW 078H02 //VER/CRB IDC XXXX
4269 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-07-17 14:04 | 2012-07-17 18:11 | 21 | 247 | 4749141 | 5187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | MULLINS, VERNON & MORGAN, RICKY &TACKETT, BOBBYFUSE BLEW ON 116-127 ON 12KV SIDE OF STEPDOWN PATROL LINE REFUSE 40T FUSE CAME BACK OUT PATROL AGAIN POWER RESTORED 18:10 BAD LIGHTNING ARR. COD-21 ISO LF 38830116B00127 VER/HFP L3/HFP IDC XXXX
4270 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-03-04 14:57 | 2015-03-04 19:45 | 18 | 288 | 4102151 | 5184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SAME AS 4099971/// OPEN ALL THREE LINE FUSES ON POLE 39830901D34616 TO CHANGE OUT BAD CUTOUTS ON ALL THREE PHASES ON POLE 39830901D37069/ ISO 39830901D34616/ COD 18
4271 | Pikeville | 3402003 | KEYSER | MULLINS | 2020-08-08 07:07 | 2020-08-08 09:27 | 37 | 140 | 4300961 | 5180 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ALL FUSES ARE IN,1 DEAD LEG@SEC SIDE OF UG PADMOUNT XFR.PRIM SHOWS TO BE OK/////HOTAP LEAD@RECLR1151-108 HAS BURNED OFF@STIRRUP,IS HANGING IN CLEAR.WILL MAKE REPAIRS//////MADE NECESSARY REPAIRS&RESTORED@09:27 // B phase only out COD 37//
4272 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-08-28 02:15 | 2009-08-28 08:00 | 15 | 345 | 54661-1 | 5175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | VER/HFP 3302701// WIRE DOWN OFF FUSE POLE == NEED 3 MEN & ROW CREW ==WIRE DOWN OFF FUSE POLE == NEED 3 MEN & ROW CREW == OH SPLICE WENT BAD == PUT WIRE BACK UP == COD-15 ISO LF 37830343A00035 L3/HFP IDC XXXX
4273 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-10-04 12:16 | 2017-10-04 13:25 | 75 | 69 | 4409741 | 5175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CALLED CUSTOMER: NO ANSWER 39830975000026 LOOP BURNT OPENCALLED CUSTOMER: NO ANSWER FOUND LOOP BURNTED OPEN ON POLE 975-26, HAVE REPAIRS MADED ALL POWER IS RESTORED AT THIS LOC AT 1325 BY AMG 39830975000017 VER/AWD L3/HFP XXXHFP SJG
4274 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-03-01 16:19 | 2016-03-01 19:38 | 26 | 199 | 4793231 | 5174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD XFMER AT 458-196 ISOLATED AND TRYING FUSE/BROKE C/O ON POLE 548/196 TRANS NOT IN USE VER/KEP L3/HFP XXXHFP AJB
4275 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-06-12 11:57 | 2014-06-12 16:03 | 21 | 246 | 4075501 | 5166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4056931//OPENED RECLOSER IN ORDER TO MAKE REPAIRS TO LINE// PULLED OFF AT 14:10 BACK ON AT 16:03 TIM MCCOY RELEASED BY CREW 074H10//COD 21 AJB
4276 | Whitesburg | 3314401 | MAYKING | ERMINE | 2014-06-03 08:14 | 2014-06-03 10:20 | 41 | 126 | 4963631 | 5166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 426-368//COD 41// VER/DBM L3/HFP AJB
4277 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-12-21 20:21 | 2014-12-21 21:50 | 58 | 89 | 4873701 | 5162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | "B" PHASE ONLY COD-58 B PHASE FUSE OUT ON POLE 1052-389, PATROLLING LINEPATROLLING LINE, FUSE WAS BROKE, REFUSED POWER BACK ON VER/KEP AJB
4278 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-07-18 16:48 | 2010-07-19 10:00 | 5 | 1032 | 52667-1 | 5160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SEND TO DAVE LEWISS SPEC. HOT WIRE IN OPEN SEC. COND. PULLED OUT OF SLEEVE. I HAD TO OPEN TRANS. ON POLE 120-264 UNTIL CREW CAN PUT WIRE BACK UP. . RELEASED BY CREW 074E06. ELLIOT CREW IS GOING TO PUT WIRE BACK UP. ELLIOT CREWS PUT UP WIRE AND CLOSED TRANS IN AT 10:00 IDC XXXX
4279 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2018-11-20 19:39 | 2018-11-20 22:50 | 27 | 191 | 4465561 | 5157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 cu primary conductor burnt in two at dead end clamp. Made repairs and restored @ 22:50. sh/opened fuse at pole 417 to isolate no additional customers L3/HFP
4280 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-07-09 20:51 | 2015-07-10 11:10 | 6 | 859 | 4759581 | 5154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED/ BAD 19.9KV CUTOUT MANUEL RELEASED BY CREW 077S01; CAN CLOSE TICKET POWER RESTORED AT ROUGHLY 11:10 AM MWL// VER/ ADH
4281 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2018-11-12 20:02 | 2018-11-12 21:54 | 228 | 112 | 4393191 | 5152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase cutout was burning. Opened up @2002 cod 180/bad cutout on pole37830296A20608,need flaggers and line crew,opened a& c at 2140 cod 47/2154 L3/HFP/// trouble tickets showing C phase out at start, then A and B phase opened later at 2140
4282 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-10-17 06:37 | 2010-10-17 15:12 | 10 | 515 | 60366-1 | 5150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND OUT POLE 68-941 30T RELEASED BY CREW 078S08// CANT FIND FAULT ON CABLE WITH UG EQUIP STILL SEARCHING/ @ 11:16 SHOT FIRST RUN OF CABLE WITH 6 T CAME BACK OUT TRYING TO LOCATE FAULT/ BAD BETWEEN 68-941 AND 68-942/ LOCATED BAD PLACE @ 12:40 STARTING TO DIG AT 12:45/ AT 14:50 HAVE CABLE SPLICED STARTING TO BACKFILL // POWER ON AT 15:12 HAVE SOME CLEANUP LEFT //VER/GAH IDCC CDC94 XXXX
4283 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-03-17 06:59 | 2020-03-17 10:11 | 57 | 192 | 4484351 | 5148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 38831077B00099// opening line fuses on 1077-98 to make repairs TOOK OTHER FUSE OUT @ 0917 CLOSED @ 1011
4284 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-02-07 04:41 | 2018-02-07 08:35 | 22 | 234 | 4810491 | 5148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines // L/F OPEN ON POLE 37830247A00307//COD 22//bad insulator on pole 37830247A00202
4285 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2020-04-06 15:44 | 2020-04-06 18:07 | 36 | 143 | 4565001 | 5148 | PARTIAL POWER | EQUIPMENT FAILURE | OTHER EQUIPMENT | at pole 21-57 got a stirrup burnt up going to be crew required Released by crew 078H09//arrived RM repairs made fuse in at 18:07 please close tic RM
4286 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-01-07 02:41 | 2009-01-07 05:00 | 37 | 139 | 52239-1 | 5143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT AND ARRESTOR, HAVE THEM CHANGED AND POWER IS RESTORED TO ALL CUST//3000701//VER/CRB L3/KEP IDC XXXX
4287 | Hazard | 3301401 | COMBS | COMBS | 2016-04-15 20:05 | 2016-04-16 10:22 | 6 | 857 | 4095261 | 5142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | TAGGED TO KYDDC// BAD UNDER GROUND BETWEEN PAD MOUNT 37830271C31077 AND 37830271C41017,100FT PRIMARY CABLE//DUT SAID TO AT 7:30AM 3 MAN LINE CREW AND A STORES ATTENDANT,NEED 100FT 72KV PRIMARY UNDER CABLE AND 2 72KV ELBOWS. FT PRIMARY CABLE/ ..B PASE LINE FUSE ALSO BLOWN ON POLE 37830271C31071,NEED TO RESET//0824 GAVE G SHOUSE PERMISSION TO REPLACE DDC TAG WITH HIS OWN// ISO 37830271C41077/ COD 6/ VER/BOW
4288 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2021-06-12 06:27 | 2021-06-12 15:00 | 10 | 513 | 4721881 | 5130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 1112-B-41..cut out broke on pole 1112-B-47 taking out the line fuse on pole 41.got my repairs made and heated the fuse up on pole 1112-B-41 @ 15:00.make note for pole 1112-B-47 to be looked at.. very bad shape at the top..
4289 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-01-18 09:55 | 2014-01-18 14:25 | 19 | 270 | 4292031 | 5130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE IS BLOWN ON POLE 57-A-28, WILL BE PATROLLING THE LINE. /// THOMAS & THORNBURY CALLED OUT TO HELP SERVICER PATROLL LINE TO DETERMINE TROUBLE//LINE FUSE IS BLOWN ON POLE 57-A-28, WILL BE PATROLLING THE LINE. REPLACED BAD LIGHTNING ARRESTER ON POLE 57-B-37. COD-19 ISO LF 37820057A00028 VER/HFP L3/HFP IDC XXXX
4290 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-10-07 05:00 | 2012-10-07 13:33 | 10 | 513 | 4120461 | 5130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 159-13 ON FIRE, PROBABLY FROM THE LINE C/O OR THE XFMR C/O. WILL NEED CREW TO CHANGE OUT BOTH. 2-CUTOUTS, 2-ARRESTOR, 2-BRKTS 12KV. IF POLE NOT DESTROYED. NO OUTAGE AT THIS TIME./// AT POLE 37830159000009 WILL OPEN 3 LINE CUTOUTS UNTIL WE GET POLE CHECKED OUT AND C/OS CHANGED. TIME OPENED 05:00HRS. RELEASED BY CREW 077S08//COD 10//ISO 37830159000009 IDC PN13, CNT8 XXXX
4291 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-03-26 16:45 | 2010-03-26 21:34 | 38 | 289 | 54788-1 | 5126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830182D00304, ISOLATED AT 38830182D00299, FUSE CLOSED AT 17:30, ISOLATED HOT TAP IS CLOSE TO HOT CUTOUT. RELEASED BY CREW 078S05/ ONLY HAVE MCCARTY AND RUGGLES/OPENED LINE FUSE @ 21:29 TO PUT HOTTAP ON CLOSED BACK IN AT 21:34 VER/KEP L3/KEP IDC XXXX
4292 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2010-04-24 21:23 | 2010-04-25 18:38 | 26 | 1275 | 50315-1 | 5125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34818242 //.....BAD C/O, 7.2 KV. ON TRANSFORMER, POLE 467-46, REQUIRES 2 MEN , MANUAL POLE NEXT TO LAST HOUSE IN HOLLOW, ON LEFT OF ROAD . OVER HILL... ISOLATED BAD C/O. ONLY ONE CUSTOMER OUT. P.HICKS RELEASED BY CREW 077H01/// C/O CHANGED POWER RESTORED. 18:38 TIME ON. VER/HFP L3/HFP IDC XXXX
4293 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-08-16 14:08 | 2018-08-16 16:10 | 42 | 122 | 4960681 | 5124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 674-251//line fuse also blown on pole 674-97 side tap up williams br.//found broke cutout on pole 674-513//i replaced cutout and refused tap on pole 674-97//now going back to pole 674-251 to restore customers//restored at 16:10//complete//em L3/HFP
4294 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-04-12 16:14 | 2015-04-12 17:15 | 84 | 61 | 4310181 | 5124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE @ POLE 38830206D02316//CUTOUT BROKE @ POLE 206D-2316 REPAIRS MADE ALL CUST RESTORED @ 1715 PLEASE CLOSE TICKET THANKS.BT VER/CRB AJB
4295 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2021-04-13 16:20 | 2021-04-13 18:09 | 47 | 109 | 4448981 | 5123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER OPEN ON 38821088A40417//COD 47//BUSTED CUTOUT ON POLE 38821088A00161//REPAIRED @cutout broke on pole 38821088A00161.iso, tagged and grounded the recloser on pole 1088-417. replaced cutout and got recloser on pole 1088-417 back to normal at 18:09
4296 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2016-06-02 17:41 | 2016-06-02 20:58 | 26 | 197 | H4287201 | 5122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 120-240 50 KVA. ALLEY WAY RELEASED BY CREW 078S07---0CREW ON SITE ENTERED MD FOR 25T LINE FUSE.BAD 7200, 120-240 50 KVA. ALLEY WAY RELEASED BY CREW 078S07---0CREW ON SITE---REPLACED 50KVA VER/AWD //// LINE FUSE OUT? REST TIME? COULD NOT FIND ON VOICE RECORDER VER/HFP AJB
4297 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-04-13 17:43 | 2018-04-13 21:00 | 26 | 197 | 4222321 | 5122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | The cutout on pole 810-39 has the lead burned out of the bottom of it. The cutout is probably damaged. The pole is up on the hill about 150 feet and the cutout is mounted on the arms. This will require a crew with hard coverup and a qualified observer./ ISO 38830810C00039/ COD 26.repairs made L3/HFP
4298 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-05-13 10:50 | 2017-05-13 10:59 | 569 | 9 | H4794581A | 5121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SEE DOL CASE 741489///BELFRY - BELFRY ISOALTION FOR BUS DISCS REPLACEMENT///ORIGINAL OUTAGE RECORD FOR OPENING BELFRY - BELFRY 12KV CB A FOR ISOLATION--TRANSFERRED PORTION OF BELFRY - BELFRY 12KV CKT TO SIDNEY - COBURN MOUNTAIN 12KV CKT/// VER/DKM AJB
4299 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-01-07 04:43 | 2010-01-07 12:52 | 106 | 489 | 64594-1 | 5118 | TRANSMISSION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STS WR # 33348897 // PART OF IDC OTHER OUTAGE, MAY BE SEPARATE FROM TRANS OUTAGE , COLD LOAD P.U. VER/PDP IDC XXXX
4300 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-09-29 17:04 | 2012-09-29 22:05 | 17 | 301 | 4099211 | 5117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE FUSE ON STEPDOWN TRANS. IS BLOWN. I AM GOING TO PATROLL LINE. WE HAVE A BAD 250 STEPDOWN TRANS. I CALLED FOR DALES TOY. RELEASED BY CREW 074S01 //VER/GAH IDC XXXX
4301 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-02-21 06:01 | 2015-02-21 08:00 | 43 | 119 | 4060391 | 5117 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | B PH FUSE ONLY // COD 43//PATROLLED LINE DIDNT SEE ANYTHING. LINE FUSE WAS BLOWN THIS TIME. CLOSED FUSE IN AT 08:00 AND RESTORED POWER. TIM MCCOY RELEASED BY CREW 074H10// VER/DBM AJB
4302 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-04-29 12:07 | 2008-04-29 12:38 | 165 | 31 | 55450-1 | 5115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116102//C PHASE ONLY, CUSTOMER COUNT NOT CORRECT//COD 165//VER/CRB IDC XXXX DEB OK ROAD PHASE
4303 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-08-12 16:42 | 2010-08-13 09:45 | 5 | 1023 | 53841-1 | 5115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36421118 /// 2 POT BANK HERE, CUTOUT IS BROKE ON THE 25 KVA, CALLED CUSTOMER, THEY SAID WE COULD WAIT UNTILL MORNING TO REPAIR, PLEASE SEND NOTE TO BRUCE LINDON RELEASED BY CREW 077S02 COD-5 VER/HFP L3/HFP
4304 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-07-21 00:51 | 2008-07-21 11:30 | 8 | 639 | 55351-1 | 5112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LOCUST ST - KINGS ADDITION IN SOUTH SHORE// TRUCK ACCESS// MATERIAL - 50 KVA, CUT/ARRES// REEL OF 2/3// CREW IN ROUTE 9:20 AM DENSIL WHEELER/GAB DENSIL CALLED IN TO CLEAR UP ON THIS TICKET @11:30 AM. NEED TO CLOSE TICKET. DH//VER/CRB IDCC TON1319 XXXX
4305 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-08-30 02:55 | 2021-08-30 16:25 | 8 | 810 | 4173021 | 5110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser open @37830071000017, checking. Fault indicators tripped, isolated URD line going from 71-203 to 71-204, tagged to Ken Little. Closed URD riser @37830071000017 @0500, this will take a line crew with hi-pot sticks to check cable./ power on map is incorect the u/g riser fuse is on pole 37830071000017 not pole 37830071000162 setting new pole with urg to pad mount 71-204 to pick cust. up.got all cust. on at 1625 Released by crew 074H04
4306 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-07-12 23:23 | 2008-07-13 04:20 | 56 | 297 | 51755-1 | 5109 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF 1147-2011 HOT TAP OFF 1147-399 POLE 1147-760 50T IN 12;50 54 CUST ON RELEASED BY CREW 078S08//VER/CRB IDC XXXX
4307 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-02-01 04:33 | 2019-02-01 11:38 | 12 | 425 | 4745501 | 5100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | contacted customer//they and their neighbors are all out//most likey related to 4745321// bad 250 kva stepdown, also need low and high side cutouts arresters and t brackets, truck acess with flaggers, looked line over couldnt find anything else wrong Released by crew 077H14 // Restored @ 1138 ISO 37840552000131 COD 12 ¦¦ L3/HFP
4308 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-08-31 08:30 | 2015-08-31 13:30 | 17 | 300 | 4184541 | 5100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFORM ON38830045B12032 OLD CSP 50KWA BAD NEED CREW TR OK FEEDS ABOUT 15 TO 20 CUST,NEED TO INSTALL 2ND 50 KVA &SPLIT LOAD ON LASH CABLE SEND TO B TACKETT,NEU ON SER.DROP BROK AT 2201 WADE ST RELEASED BY CREW 078S04XFORM ON 45-2032 OLD CSP 50KWA BAD NEED CREW TR OK FEEDS ABOUT 15 TO 20 CUST,NEED TO INSTALL 2ND 50 KVA &SPLIT LOAD ON LASH CABLE SEND TO B TACKETT,NEU ON SER.DROP BROK AT 2201 WADE ST RELEASED BY CREW 078S04XFORM ON 45-2032 OLD CSP 50KW VER/CRB L3/DKG
4309 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-12-14 13:50 | 2008-12-14 14:50 | 85 | 60 | 58274-1 | 5100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3117601/ HOT LINE CLAMP BURNT OFF ON STEP DOWN.3117601/ POLE 140-187 BAD HOT TAP VER/LDA L3/KEP IDC XXXX
4310 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-12-08 15:17 | 2021-12-08 15:23 | 850 | 6 | 4162761 | 5100 | TRANSMISSION LINE | EQUIPMENT FAILURE | CAPACITOR | DOL 1168245 Temporary Coalton Station Outage to Isolate failed 69kV CAP Bank AA at Coalton
4311 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-10-19 08:28 | 2011-10-19 15:00 | 13 | 392 | 4997321 | 5096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /LINE FUSE OPEN ON POLE 37830296A20352, PATROLLING LINE. --BAD INSULATOR ON POLE 37830296B10358//COD 13// VER/DBM IDC XXXX
4312 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2008-06-04 19:54 | 2008-06-05 13:00 | 14 | 1026 | 57147-1 | 5095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND A PHASE RECLOSER TO BE OPEN AGAIN, I FOUND A BAD 25KVA SINGLE BUSHING TRANSFORMER, THAT IS BAD THAT CAUSE THIS, HAVE IT ISOLATED, AND THE RECLOSER IS BACK ON AT THIS, CREW REQUIRED, NEED C/0, L/A, ONE CUST STILL OFF IS ALL RELEASED BY CREW 078S06 VER/HFP
4313 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2019-05-05 10:29 | 2019-05-05 13:46 | 43 | 197 | 4225811 | 5094 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | A and C rec. open on pole 197-98////patrolling.tree fell @ pole 197-23 and broke 8ft cross arm will need one man with big bucket to make repairs.opened B phase recl @ 1218 Closed recl @ 1243 // opened sw on pole 197-22 closed sw @ 1346 L3/HFP
4314 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-06-22 12:52 | 2008-06-22 17:20 | 19 | 268 | 51793-1 | 5092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3001201// LINE FUSE OUT ON POLE 45-3138/ REPLACED BAD ARRESTOR ON POLE 45-2269//REPLACED 8T TRANSFORMER FUSE ON POLE 45-2013/ TRIED FUSE -CAME BACK OUT-RECHECKING LINE/ REMOVED ARRESTORS ON POLES 45-2270 AN 45-2013 ON LONG ST E-MAIL TO RAYBURN FOR REPLACEMENT/ LINE HELD // VER/TOM IDCC PN2269 XXXX
4315 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2013-08-13 04:10 | 2013-08-13 18:18 | 6 | 848 | 4658401 | 5088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILLL WORK AFTER DAYLIGHT BAD TRANSF === NEED A 25 KVA 19.9=== BAD TRANSF == CHANGED TRANSF === POWER OK VER/SEF
4316 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-06-09 09:09 | 2010-06-09 19:45 | 8 | 636 | 59063-1 | 5088 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | UG SECONDARY BAD CALLING FOR LINE CREW TO ASSIST RELEASED BY CREW 077S04 BAD UG SECONDARY WILL BE PUTTING IN A TEMPORARY TILL CAN BE DUG AND REPLACED NOT IN CONDUIT . TEMPORARY INSTALLED AND POWER RESTORED AT 19:45 06/09/10. VER/HFP L3/HFP IDC XXXX
4317 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-02-19 11:21 | 2013-02-19 12:14 | 96 | 53 | 4829981 | 5088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER OPEN ON POLE 424-333A , HOT CLAMP BURNT OFF STEPDOWN ON 424-333. REPLACED CLAMP RESTORED POWER AT 12:14 ///VER/CRB L/3 CRB IDC PHASE A ONLY CHANGED COUNT FROM 143 XXXX
4318 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-08-27 10:10 | 2008-08-27 10:55 | 113 | 45 | 56052-1 | 5085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401101// HAD TO OPEN RECLOSER LONG ENOUGH TO CHANGE BAD DISC INSULATOR// VER/TOM IDCC PN49 XXXX
4319 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2020-06-28 16:18 | 2020-06-28 19:02 | 31 | 164 | 4084711 | 5084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 Cutout broke on C phase step down @ 37830139A40485. Opened up reclosers on 37830139A40429@ 16:18 due to customers recieving low voltage due to back feeding. Repairs made and restored @ 19:02
4320 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-01-13 16:55 | 2017-01-13 19:29 | 33 | 154 | 4296181 | 5082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4294791***/ REOPENING LINE FUSES 39831123D37126 TO MAKE REPAIRS @ BURNT POLE 39831123D37212/ ISO 39831123D37126/ ISO 33/ OPENED @ 1655/ CLOSED @1929 //MADE MD TO SHOE L/F VER/CRB L3/HFP HFP AJB
4321 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-06-12 18:44 | 2008-06-13 06:50 | 7 | 726 | 63437-1 | 5082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001401//,,BAD CSP TRANSFORMER ON POLE 454-1728 NEED CREW TO CHANGE OUT,,ITS A 50KVA 7200 CSP TRANSFORMER,,CREW WILL NEED CUTOUT AND BRACKET,. OR ARM MOUNT BRACKET.. CAN GET BUCKET TO POLE,,//VER/CRB IDC XXXX
4322 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-04-22 12:45 | 2013-04-22 14:02 | 66 | 77 | 4036261 | 5082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TIE WIRE BROKE, NEED LINE CREW , OPENED REC. ON POLE AT 12:45 ON POLE 309-8 RELEASED BY CREW 078S01///RE-TIED #4CU PRIM WIRE TO PIN INSOL.///RECL BACK IN SERVICE @ 14:02////WORK COMPLTED///RMV ///VER/CRB L/3 CRB IDCC PN9 XXXX
4323 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-09-03 13:40 | 2012-09-03 14:45 | 78 | 65 | 4000041 | 5070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN RECLOSER TO DE-ENERGIZE SO FIRE DEPT COULD PUT OUT POLE FIRE// ///VER/CRB L/3 CRB IDC XXXX
4324 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-04-05 23:01 | 2009-04-06 13:06 | 6 | 845 | 65589-1 | 5070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED LOOP ON POLE AND RESTORED POWER AT 1306 JEFF COMBS VER/KEP L3/KEP IDC XXXX
4325 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-01-11 02:00 | 2008-01-11 08:30 | 13 | 390 | 55736-1 | 5070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007903/ WATING FOR CREW.//FOUND BAD CUTOUT ON POLE 57-9//REPLACED CUTOUT//COD 13// VER/DBM IDC XXXX
4326 | South Williamson | 3200301 | BELFRY | BELFRY | 2022-12-28 23:30 | 2022-12-29 01:47 | 37 | 137 | 4373471 | 5069 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot-line-clamp burning at pole 38821014B30172 // opened fuse on pole 38821014B30172 at 2330 // cod 37 // made repairs and got line fuse on pole 38821014B30172 back in at 01:47
4327 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2017-03-21 04:13 | 2017-03-21 10:15 | 14 | 362 | 4574021 | 5068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 418-68, BAD CUTOUT ON POLE 418- 269 BURNT POLE OFF, REMOVED CLAMP ON POLE 418-69 TO ISOLATE.CLOSED FUSE IN AT 10:15..CREW WILL MAKE REPAIRS . RELEASED BY CREW 077S11 REPAIRS MADE RELEASED BY CREW 075H03 /// NO CUSTOMERS ON POLE 37830418000269 VER/HFP L3/HFP
4328 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-10-31 13:31 | 2018-10-31 18:05 | 20 | 274 | 4346901 | 5062 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection burnt open on load side loop at 882-177. Difficult location. Crew enroute to assist. Will have to open rec 882-564 when they arrive. Opened rec @ 17:00. Made repairs and restored outaged customers @ 18:05. sh Released by crew 076S02 // Recl took out 2 additional customers L3/HFP
4329 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2022-09-14 23:57 | 2022-09-15 12:00 | 7 | 723 | 4883941 | 5061 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad transformer on pole 401-235. have line crew here to help me.. transformer replaced, power restored
4330 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-12-05 14:10 | 2017-12-05 16:00 | 46 | 110 | 4622871 | 5060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout is bad on pole 473-58 , I am going to open line on pole473-334, recloser 38831128000038 37830473000058
4331 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-06-01 17:38 | 2018-06-01 21:37 | 23 | 239 | 4541641 | 5057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened recloser on pole 77-35 at 18:33 bad cutout on pole37830077000037 called for couple men 2 7200 cutouts and t brackets manuel pole Released by crew 077H14//COD 15 FROM BEGINNING
4332 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2022-07-05 14:57 | 2022-07-05 17:35 | 32 | 158 | 4380251 | 5056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | (A) ph out 32codA PHASE FUSE OPENED @ POLE 930-D-26/ PATROLED LINE / RESTORED @ 17:35.
4333 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-06-21 17:25 | 2011-06-21 17:40 | 337 | 15 | 4364581 | 5055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED OFF AT RECLOSER POLE 306-148, WE HAD TO OPEN THE RECLOSER AT// 17:25 TO MAKE REPAIRS WE CLOSED IT BACK AT 17:40 AFTER REPAIRS MADE, STIRRUP WAS ON C PHASE //COD 178+463// IDCC CNT641, TOF1559 XXXX
4334 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-04 03:21 | 2022-01-04 06:05 | 297 | 164 | 4296681 | 5048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a broke Trans cutout at pole 190-B-129,This is a Manual pole,Todd MCcoy is coming to Help make repairs.Opened Recloser at 190-C3-459 to Isolate Trans Cutout @ 05:27 and closed back in @ 05:43 replaced cutout and restored it @ 06:05.//cod 2 (+295)
4335 | Hazard | 3310502 | HADDIX | CANOE | 2015-02-02 00:42 | 2015-02-02 02:45 | 41 | 123 | 4980201 | 5043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OUT ON POLE 144-26 . PHASE OF INSULATOR @ POLE 144-27 . INSULATOR BAD ON POLE 144-27 , BURNED TIEWIRE INTO PHASE CAME OF INSULATOR ONTO POLE . REPLACED INSULATOR . CLOSED RECLOSED @ 02:45 VER/SEF L3/HFP HFPC FP37830144000027 AJB
4336 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-04-30 03:19 | 2009-04-30 08:55 | 15 | 336 | 59520-1 | 5040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403202/// 40T LINE FUSE OUT ON POLE 139A59 I WILL BE CUTTING TREES AT POLE 139-258. CLEARED UP BAD ARRESTER ON POLE 115-127. I WILL BE REPLACING BAD CUT OUT ON POLE 139A131 ROW NEEDS CUT BAD FROM FUSE TO END OF LINE. NEUTRAL WIRE GONE BETWEEN POLE 139A258 AND 139A111 . SEND COPY TO JASON BRADSHAW. AND RON RYE PIKEVILLE//VER/CRB IDC XXXX
4337 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-12-13 10:17 | 2018-12-13 10:59 | 120 | 42 | 4561001 | 5040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | ASSISTING D AKERS//CONDUCTOR OFF INSULATER @ POLE 37820025A00015//OPENED SECTIONALIZER 37820025A00063//COD 120//TO MAKE REPAIRS//OFF @ 1017 ON @ 1059 //TIE WIRE BROKE//ASSISTING D AKERS pulled off @ 10:17 back on @ 10:59 xfmr on 37820025A00063 was also off Released by crew 074S04 L3/HFP
4338 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-12-20 06:01 | 2013-12-20 09:50 | 22 | 229 | 4178211 | 5038 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK AT START OF REGULAR SHIFT.//ISO 37830116000014// HAD HIGH SIDE FUSE OUT ON STEP DOWN TRANSFORMER 15T BROKEN THIS IS 167 STEP DOWN TRANS. FUSED UP EVERYTHING OK//COD 22// VER/DBM L3/HFP HFPC CDC96
4339 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2008-04-21 12:00 | 2008-04-21 15:39 | 23 | 219 | 53015-1 | 5037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE RECLOSER LOCKED OUT - 31 CUSTON SITE, XARM BURNT OFF, ONE PHASE DOWN, CALLED R MARCUM FOR HELP// JOEY REED ALSO LOGGED ON TROUBLE ORDER/, PULLED OTHER TWO PHASES OFF AT 1445// A PHASE OUT ENTIRE TIME B/C OUT FROM 1445 UNTIL CLOSED // A (AC/ABC)=34 // B= 14 // C=9 TOTAL COD = 57 - OTHER 23 CUTOMER OUTAGED ON DUPLICATE ORDER // VER/TOM IDC PH C NOT A OUT INITIALLY XXXX
4340 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-12-25 12:09 | 2020-12-26 16:06 | 3 | 1677 | 4815791 | 5031 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 kva transformer bad at pole 38821062A00274 cew required Released by crew 074M01
4341 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-01-18 15:23 | 2011-01-18 16:00 | 356 | 37 | 62328-1 | 5030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38485472 // BAD CUTOUT ON POLE 39830901D37001 SERVICE OPENED RECLOSER TO ISOLATE TROUBLE ALL BUT 2 CUSTOMERS SHOULD BE RESTORED BEFORE 1600 HAVE CUTOUT CHANGED AND LAST 2 CUST ARE BACK ON AT THIS LOC VER/HFP L3/HFP IDC XXXX
4342 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-03-12 19:11 | 2014-03-12 20:44 | 54 | 93 | 4482061 | 5022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECL OUT POLE 140-C-44 //BAD ARRESTOR ON POLE38830140C05023 CUT IN CLEARBAD ARRESTOR ON POLE38830140C05023 CUT IN CLEAR POWER RESTORED ***CHANGE ISO POLE*** VER/SEF IDC XXXX
4343 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-05-16 10:22 | 2010-05-16 13:15 | 29 | 173 | 63166-1 | 5017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 164B-209 .. OPENED LOAD SIDE OF STEP DOWN AT 10:22.. NEED LINE CREW FOUND GRASSY ROAD TO GET BUCKET TO POLE//COD 29// VER/DBM IDC XXXX
4344 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-03-29 01:58 | 2009-03-29 04:10 | 38 | 132 | 62554-1 | 5016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REMOVED BAD CUTOUT ON INACTIVE TRANSFORMER IDC XXXX
4345 | Hazard | 3311101 | STINNETT | REDBIRD | 2017-10-08 15:37 | 2017-10-08 15:47 | 501 | 10 | 4422491 | 5010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | CLOSING OLD GOAB ON POLE 438-A-196 OPEN @ 1537 CLOSED @ 1547 VER/ARN ??? HFP ACBC FP NONE
4346 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-08-05 15:57 | 2012-08-05 20:07 | 20 | 250 | 4899331 | 5000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEFT HAND PHASE WITH BACK TO STATION OUT DUE TO LOOP BURNT INTO. NEED 2 MEN 3 CUTOUTS NOT TRUCK ACCESIBLE. THIS LOOKS LIKE A PHASE. OPENED UP B AND C PHASES AT 19:30 CLOSED BACK IN AT 20:07. REPLACE ALL 3 CUTOUT. EVERYTHING OK. A = 15 CC B/C = 40 CC. VER/SDB IDC ESTIMATED A LITTLE HIGHER XXXX
4347 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-08-02 12:57 | 2009-08-02 14:35 | 51 | 98 | 61307-1 | 4998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER WENT BAD == CUT IN THE CLEAR == TRANSF ONE ON IT == REFUSED == // VER/TOM L3/TOM IDC XXXX
4348 | Whitesburg | 3312901 | JENKINS | KONA | 2010-07-29 12:52 | 2010-07-29 14:30 | 51 | 98 | 58902-1 | 4998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD ON POLE 405-50 POLE IS MANUAL I HAVE HELP IN ROUTE REPLACED CUTOUT COD-51 VER/HFP L3/HFP IDC XXXX
4349 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-03-05 18:00 | 2013-03-05 18:15 | 333 | 15 | 4872941 | 4995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER TO REPLACE CUTOUT ON POLE ///VER/CRB L/3 CRB IDCC TOF1734, TON1800 XXXX
4350 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-05-29 05:20 | 2008-05-29 05:42 | 227 | 22 | 52450-1 | 4994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSURE SO CREWS COULD SAFELY MADE UP LOOPS OPENED @ 0520 AND RESTORED @ 0542 VER/ARN IDCC CCSCO XXXX
4351 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-02-14 10:48 | 2021-02-17 22:00 | 1 | 4992 | 4047021 | 4992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | tree fell and tore secondary between xfmr pole 219-116 to sec. pole 216-902. need 2/3 sec. & splices, manual r/w crew to cut tree. poles are truck accessible.csc Released by crew 077E05/bad transformer left 25 kva
4352 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-01-27 00:59 | 2008-01-27 02:55 | 43 | 116 | 60221-1 | 4988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3002001 HOT TAP WAS BURNTED OFF OF LINE FUSE, HAVE IT REPLACED AND POWER IS RESTORED AT THIS LOCATION//VER/CRB IDC XXXX
4353 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-11-05 15:33 | 2017-11-05 16:50 | 68 | 77 | 4532381 | 4986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap burnt off @ 19-155,line fuse in @ 1640 pole 38830043000189 rec. in 16:50/ ISO 38830019B00155/ COD 68
4354 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2012-04-14 09:07 | 2012-04-14 12:05 | 28 | 178 | 4672671 | 4984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE A NEW TIX//MADE MDC//C PHASE ONLY OPEN AT POE 61, ISOLATED BROKEN CUTOUT ON POLE 59 ( TRANSFORMER DID NOT SERVE ANY CUSTOMERS ) , REFUSED LINE CUTOUT, ALL WORK COMPLETE / GXJ ///VER/CRB IDCC CNT24 XXXX
4355 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-02-20 08:12 | 2015-02-20 18:35 | 8 | 623 | 4052221 | 4984 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY BURNED INTO. WE REPAIRED IT VER/HFP L3/HFP
4356 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-12-17 08:31 | 2022-12-17 15:07 | 15 | 396 | 4271901 | 4980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 30t lf open @ 902-155. broken xfmer pole 902-394. 45-5, new 50 kva.75 4/0 3 conductor Released by crew 078S07///isolated tap for broke pole///closed in LF 902-155 @ 13:07///repairs made///HT @306 put back online at 15:07///Complete BR Released by crew 078H22
4357 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2015-04-02 23:30 | 2015-04-03 00:30 | 83 | 60 | H4260861 | 4980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARM BURNT OFF AT POLE963C134 PHASE IS HANGING IN MIDAIR NEED CREW AND BIG BUCKET CUSTOMER SAID WE CAN GET IN THEIR YARD TO MAKE REPAIRS .// NO POWER OUT UNTIL 2118 WHEN B PHASE RECL OPENED DUE TO PHASE ON TELEPHONE CABLE (50 CUST) // OPENED A & C PHASE @ 2330 (83 CUST) /// ALL ON @ 0030 04/03 DUP OF 4260861 VER/HFP L3/HFP AJB
4358 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-02-03 06:35 | 2008-02-03 10:57 | 19 | 262 | 65806-1 | 4978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3408402/COD-18//40T LINE FUSE OUT ON POLE 37820052000222 - NOT MAPPED - MADE MD REPORT// LINE BROKE MID SPAN // NEED 2 MEN AND MATERIAL HANDLER //#4 ACSR PRIM COND DOWN,HELP ENROUTE.FUSE OUT @ 52-222MADE NECESSARY REPAIRS AND RESTORED.ALL OK AFTERWARDS VER/LDA IDCC PN211 XXXX
4359 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-12-22 18:29 | 2017-12-22 18:50 | 237 | 21 | 4664581 | 4977 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID BLADE ON POLE 37830024B40352// GAVE 911 AN ETA OF 1715//FIREMAN HAS LEFT SCENE//BAD SOLID BLADE ON POLE 37830024B40352 ARCOSING ANOTHER SERVICER OUT TO MAKE OUTAGE SHORTER//OPENING OCR THAT IS NOT ON MAP BETWEEN POLE 37830024B21214 AND 37830024B21437 TO REPLACE SB//NO OUTAGE TILL OCR OPENED @ 1829//COD 237//CLOSED@ 1850
4360 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-09-21 16:02 | 2011-09-21 17:55 | 44 | 113 | 4893921 | 4972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS GOT BROKE CUTOUT ON POLE 1135-17 VER/KEP IDC XXXX
4361 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-03-16 18:35 | 2014-03-17 00:30 | 14 | 355 | 4498211 | 4970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLLE 929-95 BURNED OFF .POLE CHG POWER BACK ON AT 12.30.. VER/ARN IDC XXXX
4362 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-06-22 19:58 | 2010-06-22 21:30 | 54 | 92 | 55087-1 | 4968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DAMAGED CUTOUT. AREA SERVICER (JOHN VENTURINO) ON SITE TO REPLACE BAD CUTOUT. RELEASED BY CREW 074E08 //VER/GAH AJB IDC XXXX
4363 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-20 08:34 | 2015-02-21 12:10 | 3 | 1656 | 4052741 | 4968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER 1159 02/20 AND THEY SAID TRANSFORMER FUSE OUT AT HOUSE - HAVE GENERATOR PLEASE LET THEM KNOW WHEN POWER IS BACK ON ;//BAD TRANS 38820673A20298// RESTORED 1210/ COD 3/ ISO 38820673A00012/ VER/BOW
4364 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-09-09 18:14 | 2010-09-09 22:57 | 24 | 283 | 65067-1 | 4962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 80T UG FUSE ON A PHASE ON POLE 39831148B20865 IS OUT. SERVICER HAS CALLED CREW WITH TEST EQUIPMENT. RELEASED BY CREW 078S07/VE MULLINS HAS NOTES ON OUTAGE/VEM RELEASED BY CREW 078H14 AED SUBMITTED. IDCC CDC83 XXXX PAF
4365 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-06-13 16:33 | 2017-06-13 19:08 | 32 | 155 | 4962231 | 4960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LOAD SIDE STEP-DOWN FUSE OPEN AT 1101-126 WILL PATROL/// FOUND BAD CSP X-FMR 25KVA HAVE ONE ON THE WAY/// CHANGED X-FMR AND INSULATOR ON PL# 1101-463 38831101D30126 38831101D30463 VER/AWD SJG
4366 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2008-05-26 10:13 | 2008-05-26 15:23 | 16 | 310 | 51321-1 | 4960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409003// BAD 100 KVA TRANSFORMER. DUTY SUP. NOTIFIED - CREW ENROUTE. RELEASED BY CREW 076S02 RELEASED BY CREW 076H02/// CHANGED 100 KVA POWER BACK ON TC MILLER//COD 16// VER/DBM IDC XXXX
4367 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2012-07-08 23:13 | 2012-07-08 23:19 | 826 | 6 | 4626611 | 4956 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | STATION DE-ENERGIZED DUE TO FAILURE OF TRACE CREEK BREAKER AT COALTON STATION //VER/GAH IDC XXXX
4368 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2021-03-21 17:41 | 2021-03-21 23:35 | 14 | 354 | 4359931 | 4956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ran the line out and founda bad insulator on pole 38830188D00073. not by truck 7200 Released by crew 078H03,bad cutout @ pole 188-305 repairs made all cust restored @ 2335 please close ticket thanks.bt Released by crew 078H02
4369 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-09-09 21:15 | 2015-09-09 23:22 | 39 | 127 | 4220071 | 4953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOW SIDE FUSE OF STEPDOWN XFM BLOWN WILL PATROL////FOUND CUTOUT BROKEN ON POLE 120B-177...WILL CHANGE OUT.CLOSED REC.37830120B00367 IN @ 23:22.../ ISO 37830120B00404/ COD 39/ VER/BOW L3/HFP XXXHFP AJB
4370 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-01-28 20:45 | 2018-01-28 23:15 | 33 | 150 | 4779921 | 4950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary down in clear at pole 936-8//into at a squeezon where lead of a switch is made up//going to open recloser on 936-5 and make repairs//repairs made//restored at 23:15//complete//em
4371 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-11-11 17:00 | 2022-11-11 17:45 | 110 | 45 | 4129221 | 4950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Primary off the insulator at pole 154-1 at Mandy LN. Switches on pole 37830129D30119 are opened and tagged to Russel Akemon. Opened at 17:00. Released by crew 077S04//TIE WIRE BRIKE//
4372 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-02-25 08:36 | 2011-02-25 16:51 | 10 | 495 | 61339-1 | 4950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED INSULATOR VER/HFP L3/HFP IDC XXXX
4373 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-11-24 09:05 | 2010-11-24 18:15 | 9 | 550 | 59248-1 | 4950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 37878613 // BAD SEC UNDERGROUND/WAITING ON EXCAVATOR STS WR # 37878613 // BAD SEC UNDERGROUND RELEASED BY CREW 078S08///SPLICED OUT 4/0 UG CABLE//SERV RESTORED 18:15 RELEASED BY CREW 078H16//COD 9// VER/DBM IDC XXXX
4374 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-02-19 07:02 | 2015-02-19 11:53 | 17 | 291 | 4041871 | 4947 | PARTIAL POWER | EQUIPMENT FAILURE | SWITCH, OH | AEP EQUIP FAILURE 600 AMP SWITCH FAILED ON POLE 45-4022 CREW REQ.//COD 19//CREW ON SITE/FETR1145/VEM/NEW SWITCH NOT COMPATIABLE SWITCH/NEW FETR1215/VEM/REPAIRS MADE AND POWER REST TO ALL 1153/PLEASE CLOSE TICKET/THANKS/VEM // A PHASE 17 CUST INITALLY OUT OPENED B & C 5 CUST (ON 17TH ST SIDE SEE H4041871) @ 1059 VER/HFP L3/HFP
4375 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-10-26 15:00 | 2010-10-26 16:55 | 43 | 115 | 64274-1 | 4945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRIMARY TIE BROKE AND FELL ON NEUTRAL,, I TIE PRIMARY BACK IN AND RESAGED WIRE POWER RESTORED IDC XXXX
4376 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-02-02 12:35 | 2014-02-02 18:28 | 14 | 353 | 4336811 | 4942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE A FUSE IS BLOWN ON POLE 38821137D00271 , WILL BE PATROLLING THE LINE. CALLED FOR HELP TO FIND THE FAULT. I TRIED THE FUSE AND IT CAME BACK OUT, I THINK THAT IT MIGHT BE A ARRESTER. FOUND A BAD CUTOUT, CREW IS REPLACING THE //COD 14// VER/DBM IDC XXXX
4377 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-12-15 07:20 | 2015-12-15 09:30 | 38 | 130 | 4533531 | 4940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON P-679-76 BROKE DOWN BURNING TOP OF POLE OFF.LINE GRD AND TAGGED FOR MYSELF.655-99.FRAMING DOWN ON POLE.//. VER/CRB AJB
4378 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-07-02 19:20 | 2012-07-04 12:30 | 2 | 2470 | 4292481 | 4940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGE OUT BAD XFMR ON POLE#286-133, NO TRUCK. POWER IS BACK ON ALL IS OK
4379 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2020-09-07 06:42 | 2020-09-07 14:15 | 18 | 453 | 4438381 | 4934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C phase recloser open @ 37830066C00061.C phase recloser (14 COD)open @ 37830066C00061. Lifted hot tap @ 66-15 to isolate section of line to identify trouble. Lifted hot tap Closed C phase recloser in @ 10:25 up to pole 66-15 // LIFTED A AND B PHASE TAPS ON POLE 66-15 TO MAKE REPAIRS // REPAIRS MADE AND RESTORED @ 1415
4380 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-05-25 12:22 | 2009-05-25 13:50 | 56 | 88 | 63746-1 | 4928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401802//..CUTOUT BROKEN...654-436--CHG CUTOUT... IDCC PN467, CNT9, CDC83 XXXX
4381 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-04-25 21:01 | 2020-04-25 22:18 | 64 | 77 | 4750331 | 4928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | servicer found failed insulator at 38830069C45527 FETR 2300 line fuse back in @ 22:18
4382 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-07-05 17:16 | 2022-07-05 20:00 | 30 | 164 | 4387831 | 4920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary off insulator/ power restored 20:00
4383 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-01-11 14:17 | 2011-01-11 16:17 | 41 | 120 | 60661-1 | 4920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREWS REPLACING BROKE CROSSARM ON POLE 1083D4 36 // COD 41 // OPENED FUSE @ 1417 AND CLOSED @ 16-17 // WR# 38402992 // VER/DBM IDC XXXX
4384 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-11-05 06:40 | 2010-11-05 17:05 | 8 | 625 | 53065-1 | 4920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF 45-4. FAILED CUTOUT. CREW REQUIRED. RELEASED BY CREW 074S02// CLOSED IN FUSE ON 37830240000156 UP TO POLE 37830240000160 AT 1545//PICKED UP REMAINING CUSTOMERS AT 1705 RELEASED BY CREW 074H01//VER/CRB IDC XXXX
4385 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-06-04 10:50 | 2008-06-04 12:53 | 40 | 123 | 55951-1 | 4920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3001102//FOUND BAD L/A ON POLE 66-113//COD 40//ALSO @ 8534 DANIELS FRK POLE 66-82 ISOLATED HOTTAP//VACANT HOUSE BUT NEED ROW TRIMMED TO GET HOTTAP BACK ON//FOUND BAD L/A ON POLE66-113 REM HOT TAP ON POLE 66-82 OLD HSE AT 8534DANIELS FRK, IS EMPTY CAN WORK ANY TIME NO TRUCKS MAY CHECK FOR REMOVAL OF METER// VER/DBM
4386 | Hazard | 3302703 | HAZARD | HAZARD | 2013-01-17 14:30 | 2013-01-17 15:10 | 123 | 40 | 4615941 | 4920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN DUE TO FAILED SQUEEZE ON// OPENED TO REDUCE LOAD IN ORDER TO OPEN SWS//OPENED REC ON 37830296A30746AT 14:30, OPENED SWITCHES ON 37830296A30149 AT 14:34=== CLOSED SWITCHES ON 37830296A30149 AT 15:10, CLOSED REC. ON 37830296A30746 AT 15:16 RELEASED BY CREW 077S04 VER/TOM L3/TOM IDC XXXX
4387 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-01-17 14:34 | 2010-01-17 16:34 | 41 | 120 | 55514-1 | 4920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MAY JUST HAVE 1 OCR OPEN // LEFT HAND RECL. OUT W/ BACK TO STA. 1127-592 HAVE 3 C/O ON POLE ONE C/O BROKE ISO. ALL 3 C/O BANK POLE NOT BEING USED. IDC XXXX
4388 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-05-14 12:36 | 2012-05-14 13:15 | 126 | 39 | 4791901 | 4914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED SECT TO ISOLATE BURNING POLE VER/KEP IDCC TOF1209 XXXX
4389 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-08-03 15:42 | 2015-08-03 17:00 | 63 | 78 | 4971191 | 4914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE SEE H4971191**** CONTRACT CREW TRANSFER CONDUCTOR PUT WIRE IN SLEEVE AND IT BROKE TOOK OUT MIDDLE PHASE RECLOSER (63 CUSTOMERS)// OPEN OTHER TWO PHASES @1549 (57 CUSTOMERS)/ ISO 38821062C00279/ COD 120/ ALL POWER RESTORED 1700// DUPLICATE IN HOIS/ VER/BOW L3/HFP XXXHFP AJB
4390 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-02-28 16:48 | 2011-02-28 16:57 | 546 | 9 | H64136-1 | 4914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | STS WR # 38966933 // WIRE LOOSE FROM HOT TAP NEED LINE CREW & BIG BUCKET TREE CREW ALSO TREE FELL ON SERVICE DROP ON POLE 1137D450 MAY ALSO NEED FLAGGERSWIRE LOOSE FROM HOT TAP NEED LINE CREW & BIG BUCKET TREE CREW ALSO TREE FELL ON SERVICE DROP ON POLE 1137D450 MAY ALSO NEED FLAGGERS RELEASED BY CREW 079H03 // 1648 OPENED RECL CLOSED @ 1657 IDC NEEDS CLEANING UP
4391 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-02-04 20:44 | 2014-02-06 13:36 | 2 | 2452 | 4348951 | 4904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 8T LINE FUSE OUT 426-42 PATROLL CLEARED HOT TAP ON BROKEN LINE CUTOUT HANGING FROM POLE, NEED 3MAN LINE CREW NO TR. CUTOUT, BRK. AN BASKET 7200 RELEASED BY CREW 078S04 CREW REPLACED CUTOUT & POWER RESTORED VER/HFP L3/HFP IDC XXXX
4392 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-09-18 05:14 | 2016-09-18 06:11 | 86 | 57 | 4902461 | 4902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FAULTED ON POLE 737-19 AND LOCKED PH. C RECLOSER OUT. TRANSFORMER FUSE OPEN (BOBBY) ON ANOTHER CASE OF TROUBLE. RESTORED REC @ 6:11. SH(86CC)/// VER/DKM L3/HFP XXXHFP AJB
4393 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-06-17 17:18 | 2019-06-17 22:00 | 111 | 282 | 4527971 | 4902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown lightning arrester on bank pole 217-31.will have to have manual row crew to cut path to pole so pole can be climbed and cut arrester in clear.once row cleared will have to open rec. on pole 217-395 so work can be done safely.//OPENED 2118 CLOSED 2200//AED MADE ON ARRESTOR//
4394 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-07-13 18:54 | 2010-07-13 22:10 | 25 | 196 | 66383-1 | 4900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | "C" PHASE ONLY COD-25C PHASE ONLY COD-25----CALVIN COMING WITH BUCKET,OLD 4 COPPER TWIST SPLICE FAILED-SEVERAL FROM FUSE TO END--BE GOOD TO RECONDUCTOR--SERVICERS NOT HOME --I FOUND GOING HOME AND CALL IN TO MAKE SAFE-JIM VER/KEP L3/KEP IDC XXXX
4395 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-03-02 02:50 | 2017-03-02 14:30 | 7 | 700 | 4483371 | 4900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY FUSE BLOWN ON POLE#1137-595IFLINE FUSE DOOR BURN OUT 1137-595 DOOR OUT NEED DOOR AND FUSE ONLY CUST OUT THAT TAP FEEDS TOMMCCOWN TRYING TO FIND DOORLINE FUSE DOOR BURN OUT 1137-595 DOOR OUT NEED DOOR AND FUSE ONLY CUST OUT THAT TAP FEEDS TOMMCCOWN TRYING TO FIND DOOR RELEASED BY CREW 074F13
4396 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-01-09 17:03 | 2013-01-09 18:12 | 71 | 69 | 4581251 | 4899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED--NEED FLAGGING CREW--500 KVA STEPDOWN LEAKING OIL--OIL IN ROAD-- RELEASED BY CREW 078S07 RELEASED BY CREW 078H16CREW REQUIRED--NEED FLAGGING CREW--500 KVA STEPDOWN LEAKING OIL--OIL IN ROAD-- RELEASED BY CREW 078S07///REPLACED STEP DOWN BACK ON 18;12 COD-71 ISO LF 38830092B00124 VER/HFP L3/HFP IDC XXXX
4397 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-12-28 07:49 | 2008-12-28 11:22 | 23 | 213 | 64527-1 | 4899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LED IN BOTTOM OF CUTOUT IS BROKEN CALLED LINKOUS CREW/NEED BIG BUCKET CREW REQUIRED RELEASED BY CREW 078S03 REPLACED CUTOUT//VER/CRB L3/JMS (CHANGED FEC) IDC XXXX
4398 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2011-06-08 09:06 | 2011-06-08 10:15 | 71 | 69 | 4266821 | 4899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR #40300437POLE 69-1047 BAD CUTOUT//C PHASE ONLY 67 COD //VER/CRB IDC ADDED 4 MISSMAPPED CUSTOMERS CHANGED COUNT FDROM 67 XXXX
4399 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-13 19:53 | 2008-07-14 00:25 | 18 | 272 | 52035-1 | 4896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3008701//RELEASED BY CREW 078S08 @ 2115 - BOBBY REYNOLDSAND CREW ENROUTE TO FOOT PATROL LINE ** UPDATE 2307- BAD ARRESTER IDC XXXX
4400 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-05-21 09:08 | 2017-05-22 12:19 | 3 | 1631 | 4833341 | 4893 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WE HAVE A BAD STRING OF INSULATORS AND A ARM PIN AND INS. ON POLE 306-261 , NEED CREW WITH KOBOTA AND ROW CREW TO CUT PATH TO POLE. WE WILL WORK TOMMOROW/ ISO 37830306000211/ COD 4. RESTORED POWER ATY 12:19 5/22/2017 RELEASED BY CREW 077H17 VER/CRB
4401 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-02-20 15:37 | 2013-02-20 18:45 | 26 | 188 | 4835371 | 4888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON POLE 37830205C00275//// BAD 50KVA XFMR. CAN BE WORKED WITH MATERIAL HANDLER COD-26 ISO TF 37830205C00275 PN80 XXXX
4402 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-05-12 08:56 | 2011-05-13 12:05 | 3 | 1629 | 4070831 | 4887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT,BURNED UP,WILL NEED 7.2 KV CUTOUT AND ARRESTOR, HOT LINE CLAMP.,LINE CREW AND TREE CREW. NO TRUCK ACCESS,,RP,JDM RELEASED BY CREW 077E09 ALL ON 12:05 PM RELEASED BY CREW 074F12
4403 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-19 15:00 | 2016-02-19 15:14 | 349 | 14 | 4737381 | 4886 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED 1500 CLOSED @ 1514/FAILED CUTOUT ON DA RECLOSER POLE 141-C-423/RELATED TO 4737881// VER/ ADH // PER IDC FP WAS 38830141D00389 L3/HFP XXXHFP AJB
4404 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-02-25 23:20 | 2012-02-26 04:25 | 19 | 305 | H4506771 | 4885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN & BURNING AT POLE 295-24 - 10 CC INTERRUPTED - OPENED REC POLE 295-A-26 @ 2320 INTERRUPTING 19 CUSTOMERS //2 SPANS OF #4 COPPER DOWN FROM POLE 37830295C00024, ALL MANUAL, NEED 100 FT OF WIRE AND 3 MEN. JEFF COMBS, BRIAN CLEMONS & VIRGIL HURT TO ASSIST //INSTALLED 300 AMP DISC. ON POLE 37830295000217, OPENED SAME & CLOSED RECL AT 0315 // //VER/GAH IDC XXXX
4405 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-10-09 16:43 | 2009-10-09 23:30 | 12 | 407 | 52208-1 | 4884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 100 KVA XFMR BAD...TIM MILLER IS BRINGING ONE TO CHG OUT...BB RESTORED AT 1130 VER/KEP L3/KEP IDC XXXX
4406 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-07-29 16:24 | 2018-07-29 17:29 | 75 | 65 | 4868941 | 4875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Short crossarm broke and let 1 span of spacer cable hit the ground between poles 48-A2-1131 and 1129. Will have to open 3 l/f @47-D-166 to make repairs. Paul Layne coming with a material handler to help put back up. Opened all 3 l/f @1624, mae repairs and closed back in @1729. no outage until line fuse was opened
4407 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-10-15 00:59 | 2009-10-15 16:34 | 7 | 935 | 63882-1 | 4875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830272C30805 BURNED INTO DUE TO FAILED XFMR CUTOUT WILL REQUIRE TECH AND LINE CREW TO RELOCATE POLE FIRST THING TODAY. PLEASE HAVE CREW CALL SANDY ON CELL 438-5628 AFTER ARRIVING ON SITE. NEEDS 40 FT POLE AND 25 KVA 7200 RELEASED BY CREW 077S04 // ISOLATED TROUBLE AND CLOSED IN FUSE @ 1100 // IDC XXXX
4408 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-10-13 08:16 | 2016-10-13 11:10 | 28 | 174 | 4989651 | 4872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MDC ON L/F //REPLACED CUTOUT AND ARRESTER AT POLE 238, REPOSITIONED LINE CUTOUT AT POLE 141-53 TO PROTECT BOTH TAPS INDEPENDANTLY, REFUSED BOTH LINE CUTOUTS AT POLE 53 WITH 30TS / ALL WORK COMPLETE / GXJ VER/CRB L3/HFP XXXHFP AJB
4409 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-08-14 03:26 | 2013-08-14 13:35 | 8 | 609 | 4663401 | 4872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE 353-15 BURNT OFF AT CUTOUT. INLINE POLE MAY PUT TALL INSULATOR ON TOP OF POLE. NO TRUCKS TO POLE . MAY NEED YAR DOG OR TRACK BUCKETT. 35/5 POLE. NEED LINE CREW, NO TREE CREW NEEDED. RELEASED BY CREW 078S01 VER/CRB L/3 CRB
4410 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-04-27 15:33 | 2008-04-27 18:10 | 31 | 157 | 54641-1 | 4867 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3409401// CENTER LINE FUSE IS OUT ON POLE 151-45. I AM PATROLLING LINE NOW. I FOUND A BAD ARRESTER ON POLE 151-83. I CLEARED IT AND CLOSED FUSE AND IT STAYED.// + 2 COD DUE TO MISMAPPED CUSTOMERS// SENT MAP DISC// - ONLY A PHASE OUT// COD 29 +2// 31 // VER/TOM IDC XXXX
4411 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-09-14 14:44 | 2015-09-14 15:48 | 76 | 64 | 4237401 | 4864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BRACES BROKE ON POLE 158-8, RECLOSERS ON POLE 158-3, WILL NEED TO OPEN THEM LONG ENOUGH TO MAKE REPAIRS, HOPEFULLY 1 HOUR OR LESS. OPENED AT 2:44, CLOSED AT 3:48/ ISO 37830158000003/ COD 76/ VER/BOW L3/HFP XXXHFP AJB
4412 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2008-01-09 05:15 | 2008-01-09 11:19 | 61 | 364 | 55000-1 | 4864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116101//POLE FIRE AT 180-101, ISOLATED AT 38830180000091, NEED LINE CREW AND 45-5 POLE AND CUTOUT, 1 CUSTOMER OUT, TRUCK OK RELEASED BY CREW 078S05//LAST CUSTOMER RESTORED @ 1119 PER LLOYD RAYBURN// VER/DBM IDC XXXX
4413 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-10-06 11:44 | 2015-10-06 17:00 | 46 | 316 | 4321861 | 4861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ISOLATED TROUBLE BY LIFTING CLAMP ON POLE 134-241, MADE FUSE BACK HOT AT 13:25 HRS, WILL NEED A XFMR, 15 KVA, 7.2 KV. ALL POWER RESTORED AT 17:00// VER/ ADH L3/HFP XXXHFP AJB
4414 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-20 19:25 | 2008-06-20 20:25 | 81 | 60 | 51294-1 | 4860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3008702//REPLACED BAD HOT TAP ON THE RECLOSER//RECLOSER WAS STILL IN, BUT HOTTAP ON THE RECLOSER FAILED//COD 81// VER/DBM IDC XXXX
4415 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-07-02 22:20 | 2012-07-04 14:50 | 2 | 2430 | 4246741 | 4860 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ASSIGNED TO ACCESSORS,,,ENTERGY///CUSTOMER HAS PART POWER LOOSE CONNECTION , RESTORED @ 14:50 JDM
4416 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-07-16 10:55 | 2008-07-16 12:25 | 54 | 90 | 53211-1 | 4860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830222B00238, C PHASE ONLY, CHANGED 2 BAD CUTOUTS//COD 54//3103101//VER/CRB IDC XXXX
4417 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2021-06-17 16:05 | 2021-06-17 17:53 | 45 | 108 | 4764441 | 4860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Loop burned off at 1148-B4-504 opened Line Sw at 1148-B4-977 (not on map-45 COD) to make repairsLoop burned open @ 39831148B40504, opened 300amp switch (not on maps @ 39831148B40977)Loop burned open @ 39831148B40504, opened 300amp switch (not on maps @ 39831148B40977) Switch closed, power restored @ 17:53
4418 | Hazard | 3310502 | HADDIX | CANOE | 2015-09-26 04:24 | 2015-09-26 12:45 | 18 | 501 | 4272611 | 4853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830169C00281 HAD BAD CUTOUT AND HAS BURNED OFF AT CUTOUT CAN LOWER EVERTHING NEED CREW AND D.E. UNIT CUTOUT AND T BRKT FOR 7200 TOOK CLAMP OFF ON POLE 37830169C00079 AND PUT LINE FUSE IN AT 0840 RELEASED BY CREW 077S05 MADE REPAIRS AND RESTORED LAST CUSTOMER T 12:45 VER/HFP L3/HFP
4419 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-09-27 06:57 | 2010-09-27 10:48 | 21 | 231 | 53996-1 | 4851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CONFIRMED LINE FUSE OUT AT POLE 273-328 PATROLLING LINE//ATTEMPTED RESTORE UNSUCCESSFULLY CALLING FOR ASSISTANCE//REPLACED BAD 7.2 XFMR CUTOUT AT POLE 37830273D00232//PLEASE SHOW A 20-T FUSE ON POLE 273-328//ISO 37830273C10328//COD 21//MD FILED// VER/DBM IDC XXXX
4420 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-04-12 02:47 | 2011-04-12 11:46 | 9 | 539 | 55494-1 | 4851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WILL HOLD TIL AM PRIMARY OFF THE INSULATOR FIRST POLE OUT FROM THE FUSE, KENNY BROOM HAS A JOB HERE TODAY TO PUT UP A PRIMARY NEUTRAL RELEASED BY CREW 077S12 COD-9 ISO LF 37830496000037 VER/HFP L3/HFP IDC XXXX
4421 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-08-24 04:06 | 2022-08-24 11:27 | 11 | 441 | 4787041 | 4851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Fuse open on 37830226000031. One span of primary down on 37830226000035. Sleeve pulled out of 6A. Need manual ROW crew to make repairs. Power restored @ 11:27
4422 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-03-19 20:29 | 2008-03-20 04:34 | 10 | 485 | 59061-1 | 4850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000202//FOUND CUTOUT BROKEN ON FUSE POLE ** AT 0205- CREW ENROUTE TO HELP REPLACE.3// RELEASED BY CREW 078H04///OPENED RECLOSER ON POLE 334-141 TO REPAIR BAD CUTOUT @ 03:50// VER/PDP IDC XXXX
4423 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-08-26 15:18 | 2008-08-26 18:32 | 25 | 194 | 55167-1 | 4850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP NEED TO PUT POLE EXTENTION ON TOP OF POLE AND CHANGE CUT-OUT COMPLETE M.D.I. COD-25 ISOLATION POLE 37830497000139 IDC XXXX
4424 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2018-06-13 22:29 | 2018-06-14 04:15 | 14 | 346 | 4599531 | 4844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 39830879C00278 20t lat fuse blown---39830879C00295 c/o and arrester bad ,,replaced c/o cleared arrester--20 t lat in at 03:45--allgood-ds061418
4425 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-05-25 18:28 | 2008-05-25 21:15 | 29 | 167 | 51211-1 | 4843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 3410501//BAD U.G TRANSFORMER 7200, REPLACE PRIMARY BUSHING ON PAD MOUNT TRANSFORMER. VER/LDA IDC THIS POLE IS NOT FOUND ON MAP AND THE CLEARING POLE IS OVERHEAD XXXX
4426 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2021-03-28 02:11 | 2021-03-28 09:31 | 11 | 440 | 4388211 | 4840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held per KYPCO late night callout guidelines. Will be worked in daylight hours//bad cutout/replaced/pls close. tre
4427 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-12-23 16:20 | 2012-12-23 18:05 | 46 | 105 | 4511981 | 4830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE OUT ON POLE 57A3 PATROLLING LINE.//MADE MDC TO SHOW FUSE ON POLE 57-3 AND ADD CUST ///VER/CRB L/3 CRB
4428 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-06-08 22:23 | 2020-06-09 04:08 | 14 | 345 | 4982051 | 4830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | DDC HOLD TAGS // DOL 1025897 // pole broken at phone 188-80/lie crew required 4 way deadend pole/40/5 need 45/4 // crew on site FETR 4:00 all pwr restored @ 4:08// sent copy to p. thovson // cod 14 // DDC HOLD TAGS // Released by crew 078M01 Released by crew 078M06
4429 | Hazard | 3309003 | JEFF | VIPER | 2022-03-31 07:35 | 2022-03-31 15:38 | 10 | 483 | 4698871 | 4830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A&B line fuses are open on pole 416-110, with B phase off of the insulator laying on the arm at pole 417-167 which is manual. C phase on 416-110 will need to be opened to make repairs. The phase on the arm is at Lick Br. of Middle fork and the fuses are located on Right Fork. Crew required. No tags or grounds placed. Released by crew 077S04
4430 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-07-14 20:08 | 2009-07-14 23:13 | 78 | 185 | 58285-1 | 4824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001401//CUTOUT FAILED AND BURNED CROSSARMS (SEE ORDER 54064-1)//CREWS OPENED RECLSOERS TO REPLACE XARMS//COD 78//CUT LOOPS AND ISOLATED @ POLE 454-203// VER/DBM MLR OK IDC XXXX
4431 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-10-22 10:43 | 2012-10-22 17:25 | 12 | 402 | 4162401 | 4824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE NOT OUT--TRANSFORMER OUT ON POLE 39831147C14139--CREW REQUIRED--BAD 37.5,NEED 50 KVA RIGHT BESIDE RD--NEED NEW CUTOUT--SEND TO B FRALEY RELEASED BY CREW 078S07// VER/DBM IDC XXXX
4432 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-03-10 14:19 | 2015-03-10 18:20 | 20 | 241 | 4178081 | 4820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | RECLOSE IS IN AT POLE 38821012D00055, PATROLLING THE LINE. PHASE B SWITCH IS OPEN ON POLE 38821036C00175 IT DOES NOT LOOK LIKE ANYTHING IS WRONG WITH IT. SWITCH IS BAD, CREW IS EN-ROUTE. // THIS IS FOR THE B PHASE INITAL OUTAGE FOR 20 CUST // SEE H4178081 FOR CKT OUTAGE --- VER/HFP L3/HFP AJB CAUSE ? AJB
4433 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-05-09 18:20 | 2015-05-11 10:30 | 2 | 2410 | 4406881 | 4820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA RISERS CUTOUT WILLNEED SOME ONE WITH TWIC CARD/BACK UP TRANSFORMER FOR SYSTEM, SPOKE TO CUSTOME WILL BE OK TO HOLD UNTIL MONDAY, NOT TRUCK ACCESSIBLE REPLACED TRANSFOMER AND C/O/ ISO 38830166C10204/ COD 2/ VER/BOW
4434 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-11-27 11:51 | 2022-11-27 17:35 | 14 | 344 | 4184481 | 4816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE L/F OPEN ON POLE 38830761000265 (COD 17)//wire wrapped up p-760-84.line fuse blown on p- 761-265. cutout bad on p- 761-265.. back on at 17:35 LR- There shows 14 customers on Phase C
4435 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-05-19 17:45 | 2013-05-19 20:15 | 69 | 150 | H4133841 | 4815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE ONLY 135..OPENED OTHER 2 REC AT 17.45 ISOLATED ON POLE 875-245 ..GRD TAGGED..REC ON P 875-206 BACK ON 18.12.. RELEASED BY CREW 076S01 IDCC DUP TO OPEN A AND B XXXX
4436 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-04-01 11:54 | 2008-04-01 17:15 | 15 | 321 | 62732-1 | 4815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2206403//SERVICER ETA 1230// POLE TOP BURNT OFF ON POLE 190-108, NEEDS LINE TO REPLACE 45-4 POLE. MAY GET TRUCKS TO POLE. RELEASED BY CREW 078S01, VER/HFP IDCC PN52 XXXX
4437 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-08-02 20:32 | 2009-08-03 01:53 | 15 | 321 | 63104-1 | 4815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3007904// WAITING ON TREE CREW TO CLEAR WAY TO RECLOSER.,,,BACK ON, POWER RESTORED, RECLOSER IS BAD HAD TO PUT IN BYPASS IDC XXXX
4438 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-08-16 01:53 | 2020-08-16 10:48 | 9 | 535 | 4333991 | 4815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | crew required trucks ok/tagged to mccoy and grounds at 925-75 Released by crew 078S03 crew on site FETR 11:30 LRM 925-154 broke 15 kva on ground, have called brandon beltcher to report spill// all pwr restored @ 10:48 please close ticket LRM
4439 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-06-10 13:28 | 2019-06-10 16:33 | 26 | 185 | 4474471 | 4810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 335-16////will patrol..xfm. cutout broken on pole 335-103////will make repairs..non truck approach.. L3/HFP
4440 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2015-07-15 17:38 | 2015-07-15 19:48 | 37 | 130 | 4883911 | 4810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | L/F BLOWN ON 37830024B40504 // REPAIRED BROKEN TIE WIRE LAYING ON POLE TOP PIN @ POLE 37830048A30451// POWER RESTORED @ 19:48 AJB
4441 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-04-19 10:22 | 2019-04-19 14:13 | 266 | 231 | 4133291 | 4809 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on center phase //crew opened on pole 387-c-292 at 13:59 to safely make repairs on pole 363-140 all power restored at 14:13 //cod 3 (+263) L3/HFP/// B phase showing out first on fuse 37830363000140
4442 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-03-26 06:08 | 2010-03-26 06:35 | 178 | 27 | H54533-1 | 4806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34409227 / COD-109 / /PATROLLING LINE, SOLID BLADE LINE CUTOUT BROKE DOWN ON 72-78/ @ ____ OPENED RECLOSER ON POLE 72-A-80 (COD-176) TO REPLACE BAD CUTOUT., OFF AT 6:08 ON AT 06:35 (*_&*)&()*^&(*^&)*(&_)+*+ IDC LOOKS LIKE ALL 3 PHASES WERE OUT? AJB IDC XXXX
4443 | Pikeville | 3421001 | BREAKS | CITY | 2008-04-12 11:50 | 2008-04-12 17:00 | 27 | 310 | 50427-1 | 4806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGED TRANSFORMER RESTORING LAST 3 CUSTOMERS AT 1700 / WR VER/ARN MLR OK, RESTORATION COUNTS PER POWERON MATCH
4444 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2019-10-31 13:50 | 2019-11-01 16:13 | 5 | 1583 | 4232741 | 4799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout broken. Will have to climb pole to fix cant get to it. Released by crew 074M01//opened line fuse up on pole 171D-101 at15:48 closed back in at 16:13//all power restored/ ISO 37820171D00101/ COD 5/// cust call at 1350 all out.
4445 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-06-02 22:40 | 2016-06-03 01:05 | 33 | 145 | 4289511 | 4785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SOLID CUTOUT BROKEN ON 876-367..CHANGING.. MIDDLE B PHASE (33) OUT ORIGINALLY. OPENED OTHER 2 PHASES (5) AT 1230. CLOSED ALL IN AT 0105. 38830876B00367 VER/AWD L3/HFP HFPC FPNONE CDC83 AJB
4446 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-12-25 17:24 | 2020-12-26 13:20 | 4 | 1196 | 4818881 | 4784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out on pole 1062-272, refused and blew again. bad xfmr. need 25 kva 7.2kv ..crew required.TRT Released by crew 074E11. Replaced trans. and closed back in @1320.
4447 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2008-10-08 15:44 | 2008-10-08 22:23 | 20 | 399 | 54394-1 | 4784 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | EMERG SW TO TRANSFER LOAD FROM THE HAZARD/BLACKGOLD 34KV TO THE HAZARD/KENMONT 34KV CKT. TO ALLOW TRANSMISSION CREWS TO MAKE REPAIRS TO OVERBUILT 69KV LINE AT STRUCTURE 333-2 AND DIST. POLE 296-233 IDC XXXX
4448 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2017-04-02 14:58 | 2017-04-02 19:57 | 16 | 299 | 4607491 | 4784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 265-318 RESTORED AT 1957 37820265B00070 37820265B00318 16 VER/AWD AJB
4449 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2016-04-05 02:17 | 2016-04-05 13:58 | 21 | 701 | 4052361 | 4784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 67-355 ROTTEN FELL DOWN TOOK PRI. AND NU. DOWN 67-354 NEED NEW POLE 40/5 TELEPHONE POLE NEED ALL POLE HARDWARD HAS UNDERGROUND ON POLE 50KVA 12KV. TRANSFORMER TRUCK TO POLES POLE 67-46 30T IN 05:15 1CUST OUTPOLE REPLACED ALL POWER RESTORED AT13:58 PLEASE CLOSE TICKET THANKS DWW RELEASED BY CREW 078Q06// VER/ ADH // VER TIME PER VOICE RECORDER = L3/HFP HFPC TON1318 L3/IDC XXXX AJB
4450 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-08-10 23:22 | 2022-08-11 10:45 | 7 | 683 | 4723521 | 4781 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken xfmr c/o // restored @ 10:45
4451 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2022-07-21 13:33 | 2022-07-21 21:56 | 34 | 503 | 4543061 | 4777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Opened DA Reclosers at 321-B-439 at 1335 to allow crews to safely open 34kV Line SWS at 321-A-606 At 1343 closed DA Reclosers 9 customers remain out till 1900
4452 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-07-29 20:13 | 2021-07-30 06:10 | 8 | 597 | 4978371 | 4776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole# 351C-95 is broke, will need 40 ft pole, 25 KVA xfmr, 2- 7200 Dead end units Released by crew 077H07repaired and restored power at 6:10//cod 8
4453 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2012-05-14 14:12 | 2012-05-14 18:37 | 41 | 265 | 4792531 | 4775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /POLE BURNED OFF CREW ENROUTE RELEASED BY CREW 074S02 VER/KEP IDC XXXX
4454 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2019-02-08 12:02 | 2019-02-08 16:43 | 143 | 281 | 4770461 | 4774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | No truck access. Will need to open recloser on pole 38821062D00451 to make repairs Crossarm is rotten on pole 38821062D00133 and let the side tap cutout fall that goes to tap pole 38821062D00408. Need eight foot arm, crossarm braces, two arm pins and 7200 insulators, 7200 cutout and bracket. Also will need to put the primary neutral back up. Released by crew 079S02 RECLOSUER 1606 ON 1628No truck access. Will need to open recloser on pole 38821062D00451 to make repairs Crossarm is rotten on L3/HFP
4455 | Pikeville | 3401001 | ELWOOD | DORTON | 2012-04-17 00:38 | 2012-04-17 12:00 | 7 | 682 | 4679091 | 4774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH SERVICER AT REG WK . CUSTOMER CALLED , FLASH AND ARC AT TIME OF OUTAGE , TR NOT ARCING AT THIS TIME. TOP OF POLE HAS BURNED OFF. { 310-164 }. IT BLEW LOW SIDE FUSE ON STEPDOWN TRANS. ON POLE 310-181. I AM CALLING FOR HELP. TIM HALL IS SENDING HELP. WE LOWERED EVERYTHING ON POLE AND MADE LINE HOT AT 12:00//COD 7// VER/DBM IDC XXXX
4456 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-01-04 05:06 | 2009-01-04 07:35 | 32 | 149 | 51172-1 | 4768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3413401///I FOUND BAD ARRESTER ON POLE 41-113. I CHANGED IT AND CUTOUT. 40T FUSE OUT ON A PHASE POLE 41B35. VER/KEP L3/KEP IDC XXXX
4457 | Hazard | 3303901 | LESLIE | HYDEN | 2019-04-14 17:01 | 2019-04-15 12:52 | 4 | 1191 | 4098071 | 4764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | line fuse still in on pole 388-b-284. pole 388-b-50 primary loop not made up to energize rest of line. will need to open line fuse 388-b-284 to make repairs on pole 388-b-50 (manual), will require flaggers.csc Released by crew 077E05 power restored at 12:52 ¦¦ HAVE NO IDEA ABOUT THIS ONE - HAZARD OFFICE WAS IN DISPATCHING TROUBLE
4458 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-07-02 15:50 | 2012-07-04 07:30 | 2 | 2380 | 4229241 | 4760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. BAD TRANSFORMER. NEED 25KVA { 7200 }, CUTOUT AND ARRESTER. THIS IS TRUCK ACCESSIBLE WHEN GROUND IS DRY. RELEASED BY CREW 074S01 REPLACED TRANS. AND CUTOUT AND ARRESTER ANDBRACKET POWER RESTORED AT 19:30
4459 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-09-13 00:25 | 2021-09-13 10:20 | 8 | 595 | 4234181 | 4760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Original outage 4233711/Bad underground, one span of two replaced but other must be completed in daylight/cable bad from 71-207 to 208 restored @ 1020
4460 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-09-09 08:50 | 2008-09-09 13:40 | 31 | 290 | 60689-1 | 4760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303//, BAD CUTOUT AT POLE#1064-34, PICKING ALL CUST UP EXCEPT CUST WHERE CUTOUT IS BAD, PICKED UP ALL CUST BUT ONE AT 1119 A M RELEASED BY CREW 080S01 - WORKED OVER RADIO CREW NO MDC - REPLACED CUTOUT AND POWER RESTORED @ 1340// // VER/TOM
4461 | Pikeville | 3408401 | KIMPER | LONGFORK | 2012-04-25 15:55 | 2012-04-25 16:02 | 680 | 7 | 4707311 | 4760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED CKT TO DE-ENERGIZE FAILED EQUIPMENT VER/ARN IDCC 346 XXXX
4462 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-03-26 16:49 | 2010-03-26 19:33 | 29 | 164 | 54791-1 | 4756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR #34418875 //PATROLLING LINE.POLE TOP BURN 1063-D137. VER/KEP L3/KEP IDC XXXX
4463 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-02-24 10:01 | 2016-02-24 17:59 | 10 | 478 | 4755061 | 4755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ENROUTE//3783041700016337830417000163 == BAD CUTOUT CHANGED === GOT MAIN LINE ON AT 17:55 === GOT TAP AT POLE3783041700095 ON 17:59 === GOT TAP ON AT POLE 37830417000163 ON AT 17:54 === ALL POWER ON AT 17:59 ===37830417000163 == BAD CUTOUT CHANGED === GOT MAIN LINE ON AT 17:55 === GOT TAP AT POLE3783041700095 ON 17:59 === GOT TAP ON AT POLE 37830417000163 ON AT 17:54 === MADE MDC VER/CRB L3/HFP XXXHFP
4464 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-03-12 23:38 | 2014-03-12 23:45 | 679 | 7 | 4482421 | 4753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 98-B-623 BURNED INTO BY C/OUT. OPENED GOAB 122-236 @ 23:38 FOR FIRE DEPT TO SPRAY POLE. CLSD GOAB @ 23:45. LINE FUSE FEEDING SINGLE TAP OFF 98-B-623 STILL OUT. POLE IS 60 CL 2 WILL NEED REPLACED. TRACK MACHINE NEEDED. RELEASED BY CREW 074H03 //VER/GAH IDCC TOF1928, XXXX
4465 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2018-10-21 09:49 | 2018-10-21 16:25 | 12 | 396 | 4299621 | 4752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop into on pole37830224D00050 power reswtored at 16:25 L3/HFP
4466 | Pikeville | 3408101 | SALISBURY | PRINTER | 2015-02-20 09:31 | 2015-02-21 11:55 | 3 | 1584 | 4053961 | 4752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED : MATERIAL: 25 KVA 7.2KV / 120/240, CUTOUT // TRUCK ACCESS WITH CHAINS RELEASED BY CREW 074S03// WILL NEED FLAGGERS//COD 3// VER/DBM
4467 | Hazard | 3301101 | CHAVIES | CHAVIES | 2020-03-29 05:40 | 2020-03-29 09:50 | 19 | 250 | 4521071 | 4750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | got wire off insulator on pole 196126
4468 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-06-04 09:20 | 2013-06-04 11:25 | 38 | 125 | 4218051 | 4750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 116-553 BAD LA ON CSP TRANS. REPAIRED INSTALLED CUTOUT 10T TRANS FUSE CUST SAID TREES ARKING IN RAIN SEND NOTE TO TREE PEOPLE SEND RAYBURN NOTE CSP TRANS. ON POLE 116-542-555-577 NEED CUTOUTS INSTALLED NO TRUCK 116-555 BAD LA ON CSP ///VER/CRB L/3 CRB IDC XXXX
4469 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-08-29 15:06 | 2020-08-29 19:40 | 32 | 274 | 4400751 | 4748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole top burnt off @ 38831098D00741 lifted hot tap @ 38831098D00234 to isolate. Fuse blown @ 38831098B00523.Closed 50T fuse @ 1098B523 @ 17:26. Repairs made tap on @ 19:40 Released by crew 074S11
4470 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-05-22 09:00 | 2013-05-22 09:47 | 101 | 47 | H4145941 | 4747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PATROLLING LINE., B PHASE ONLY OUT COD-54 NEED TO ADJUST CUST. COUNT.BROKE POLE @ 225D-164 ON 1PH TAP.,WILL GET MATERIAL LIST. B PHASE PULLED OUT OF SLEEVE @ POLE 225B-36.(OK TO LEAVE HOT UP TO THIS POLE UNTIL MORNING). OPENED ALL PHASES AT 225-28 AT 0900 --- REPAIRS MADE, POWER RESTORED AT 09:47 - CAN CLOSE TICKET MWL //VER/GAH IDCC DUP TO OPEN OTHER PHASES XXXX
4471 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-01-05 22:01 | 2009-01-06 13:50 | 5 | 949 | 51735-1 | 4745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830206C02340 AND 38830206C02341 ARE BROKE, NO TRUCKS, BOTH XFMR POLES, NO VISIBLE CAUSE. // WORK REQUEST # 27934449 //NO WAY TO USE YARD DOG HAVE TO WINCH POLES IN RELEASED BY CREW 078S10 RELEASED BY CREW 078S05 VER/KEP L3/KEP IDC XXXX
4472 | Hazard | 3309901 | SLEMP | DEFEATED CREEK | 2011-04-20 08:08 | 2011-04-20 18:01 | 8 | 593 | 61014-1 | 4744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | STS WR # 39643671 /// CONFIRMED THE SLEMP/DEFEATED CREEK 34KV CB A IS LOCKED OUT// SERVICERS PATROLLING // TRIED BREAKER AT 1107 - CAME BACK OUT// CALLED HAZARD ASSISTANCE == POLE GROUND FELL ON TO PHASE LINE == GOT LAST CUST ON AT 20:03 RELEASED BY CREW 077S03// IDC XXXX
4473 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-04-09 19:33 | 2015-04-10 03:27 | 10 | 474 | 4299681 | 4740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2-PH OF SPACER CABLE DOWN WILL NEED CREW REQ MAP SHOWS 556 TO MAKE REPAIRS TRUCKS OK IN ALLEY PL.38830045C14435 FAULT RELEASED BY CREW 078S09/OPEN SWITCHES @ 45-C1-4022 TO SAFELY MAKE REPAIRS/APPROX 2 HOUR OUTAGE/VEM/SWITCHES OPEN @0153/VEM/JOB GOING WELL/NEW FETR0345/VEM/REPAIRS MADE AND ALL CUST RESTORED 0327/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP
4474 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2018-02-21 15:10 | 2018-02-21 17:04 | 53 | 114 | 4869371 | 4740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A phase rec. open @1053-B-230, checking. Line fuse open @1053-A164, busted c/o on pole1053-A-166. Closed A phase rec. on pole 1053-B-230 @1605. Changed c/o and closed l/f @1053-A-164 @1704. Released by crew 074S05
4475 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2012-05-04 07:12 | 2012-05-04 09:50 | 30 | 158 | 4742051 | 4740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REC. POLE 90-38 B PHASE OPEN, RESTORED 9:50 PHELPS NEUT. DOWN POLE 66-20,21 4 COPPER. L/A BLOWN POLE 66-26.//COD 30//MADE AED ///VER/CRB L/3 CRB IDC XXXX
4476 | Hazard | 3302703 | HAZARD | HAZARD | 2014-05-27 15:00 | 2014-05-27 15:07 | 677 | 7 | 4935281 | 4739 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | SCHEDULED OUTAGE TO MAKE REPAIRS AT STATION// RELEASED BY CREW 077S04 OPENED 1712 AND CLOSED @ 1713 ON RESTORE// IDCC CNT1354 XXXX AJB MCCDL PER SDS PROBLEM WAS IN STATION.
4477 | Hazard | 3309302 | VICCO | JEFF | 2019-11-07 19:16 | 2019-11-08 00:12 | 16 | 296 | 4008601 | 4736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulators on pole 37830323D00316 need tree crew and three man line crew 2 19.9 de insulator and 19.9 kv cutout L3/HFP
4478 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-03-23 23:57 | 2011-03-24 11:30 | 27 | 693 | 58377-1 | 4736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RECLOSER OPEN--PATROLING LINE--BAD 37.5 TRANSFORMER ON POLE 39831123B00566-NEED CREW-TRUCK OK RIGHT BESIDE RD--CLOSED RECLOSER IN AT 02;11-ONLY 1 CUSTOMER OUT / TRANSFORMER TO BE REPLACED AFTER DAYLIGHT ON THE 24TH//COD 27// VER/DBM IDC XXXX
4479 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-06-01 01:42 | 2011-06-01 04:10 | 32 | 148 | 4216841 | 4736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD LIGHTING ARRESTER AND CUTOUT ON POLE 287-13. //VER/GAH IDC XXXX
4480 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-04-14 16:58 | 2009-04-14 19:26 | 32 | 148 | 52265-1 | 4736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007906//BROKE CUTOUT AT OLD OIL WELLBROKE CUTOUT AT OLD OIL WELL ,,BACK ON//COD 32// VER/DBM AJB
4481 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-07-25 11:43 | 2012-07-25 14:32 | 28 | 169 | 4824531 | 4732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A PHASE FUSE BLOWN 454-3005// PATROLING LINE/ FAILED ARRESTOR 454-3019/ BAD CUTOUT 454-3005/REPAIRS COMPLETE POWER REST. @ 14:32 JEH//COD 28// VER/DBM
4482 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-01-29 08:02 | 2008-01-29 09:25 | 57 | 83 | 60569-1 | 4731 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3000202// BAD ARRESTER ON POLE 286-224 VER/KEP IDC XXXX
4483 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-12-12 13:51 | 2010-12-12 20:25 | 12 | 394 | 65613-1 | 4728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38077747 // POLE FIRE AT 38830182B43779, ISOLATED AT 38830182B43567 COD-26, SHOULD BE ABLE TO LOWER EQUIPMENT, CREW ENROUTE RELEASED BY CREW 078S05 DUPLICATE FOR 3 CUST ON POLE 38830182B43779 @ 1544 WHEN HOT TAP LIFTED... ISO LF 38830182B43779 COD-23 SEE H65613-1 & 6573-1 (CAME OUT ON COLD LOAD) VER/HFP L3/HFP IDC XXXX
4484 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2010-06-17 09:50 | 2010-06-18 12:06 | 3 | 1576 | 50512-1 | 4728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35614952 //, CUST CAN WAIT UNTILL MORNINGBAD 15 KVA ON POLE 1146-338, NO TRUCKS CAN USE YARD DOG RELEASED BY CREW 078S09 NETURAL INTO ON SERVICE DROP TRANSFORMER GOOD VER/HFP L3/HFP
4485 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2018-08-29 00:06 | 2018-08-29 15:51 | 5 | 945 | 4009821 | 4725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 37830144D00122 broken just below telephone but still attached to stub-no truck access-will have to wait till mnorning-on side of mountain
4486 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-02-25 06:48 | 2011-02-25 09:03 | 35 | 135 | 61162-1 | 4725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STINGER BURN OFF AT POLE 38830254B00239, 2 WAY FEED POLE, STINGER HANGING DOWN IS HOT. DID NOT FIND WIRE DOWN AT 1511, SEND TO V MULLINS. RELEASED BY CREW 078S05/CREW ON SITE/WILL NEED TO OPEN RECLOSER 254-277 FOR REPAIRS/FETR FOR ALL CUST 0930/VEM/OPEN RECLOSER 0839(IN SEPARATE ORDER)/ALL CUST RESTORED 0903/PLEASE CLOSE TICKET/THANKS/VEM//COD 35// VER/DBM IDC XXXX
4487 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-06-21 20:40 | 2015-06-21 22:25 | 45 | 105 | 4633081 | 4725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CALLED FOR CREW TO CHANGE CUTOUT AND PROBLEY CROSSARM RELEASED BY CREW 077S12OPEN BLADES ON POLE 425-411 AT 20-40 CLOSED AT 22:25//COD 45// VER/DBM L3/DKG AJB
4488 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-07-07 13:15 | 2012-07-07 18:10 | 16 | 295 | 4575101 | 4720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE STEPDOWN FUSE OUT ON POLE 37830069000005 STEPDOWN IS ON POLE 37830069000233 GOING TO CHANGE STEPDOWN// RAY, STEPHEN HIGH SIDE STEPDOWN FUSE OUT ON POLE 37830069000005 STEPDOWN IS ON POLE 37830069000233 GOING TO CHANGE STEPDOWNHIGH SIDE STEPDOWN FUSE OUT ON POLE 37830069000005 STEPDOWN IS ON POLE 37830069000233 GOING TO CHANGE STEPDOWN XFMR CHANGED AND POWER RESTORED @ 18:10 COD-16 ISO LF 37830069000005
4489 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2022-12-23 17:00 | 2022-12-23 18:20 | 59 | 80 | 4329421 | 4720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse burned out on pole 963D-71.back in at 18:20
4490 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-08-08 06:35 | 2011-08-08 11:30 | 16 | 295 | 4677521 | 4720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | POLE 140-581 40T UNDERGROUND FUSE OUT NEED TO BRING 19.9 CUTOUT AND LA RELEASED BY CREW 078S08 BAD SECTION OF PRIMARY UG CABLE BETWEEN 140-582 AND 140-583, ISOLATING AND PREPARING TO BACK FEED.BAD CABLE IS ISOLATED AND BACKFED FROM OPEN POINT @ 140 - 586 BAD CABLE IS TAGGED AND DDC IS NOTIFIED TO PUT THIS IN THE ACDB.BLR//CREATED AED AND PLACED NOTES ON MAP.//COD 16// VER/DBM IDCC CDC83 XXXX
4491 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-02-01 15:58 | 2022-02-02 03:12 | 7 | 674 | 4422481 | 4718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 75kva 7200, double bushing, 120/240 transformer. Crew required, trucks to pole Released by crew 078S02//arrived RM replaced xfm volatge good all cust on please close tic RM
4492 | Hazard | 3303902 | LESLIE | WOOTON | 2009-11-30 16:53 | 2009-11-30 22:30 | 14 | 337 | 52228-1 | 4718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830341000055 WE HAVE BAD C/O BURNT TOP OF POLE OFF. PROBABLY LOWER CONDUCTORS ON POLE. TO CHANGE IT OUT WILL BE MANUAL. LOWERED PRIMARY, LOWERED GUY, POWER RESTORED.//COD 14// VER/DBM IDC XXXX
4493 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-03-13 05:32 | 2020-03-13 12:05 | 12 | 393 | 4474051 | 4716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | recloser open on pole 398-297, bad insulators on pole 398-124.manual pole.. Released by crew 077S11 power restored at 12:05 replaced 6 deadend insulators
4494 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2018-06-18 06:07 | 2018-06-18 06:24 | 277 | 17 | 4614591 | 4709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | related to 4614391//loop burnt open on 38830503D10052//opened MOAB 38830478D40294 in order to make repairs//cod 277
4495 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-10-08 16:56 | 2009-10-08 20:12 | 49 | 196 | 65383-1 | 4708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT RE PLACED BAD CUT-OUT VER/KEP L3/KEP IDCC CDC92 XXXX
4496 | Pikeville | 3413401 | GARRETT | GARRETT | 2013-11-24 11:58 | 2013-11-24 13:45 | 44 | 107 | 4070001 | 4708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTED APART AT POLE 16-192, PRIMARY NEUTRAL IS 14 FT ABOVE HWY 550//C PHASE ONLY //GUY WIRE RUSTED APART AT POLE 16-192, PRIMARY NEUTRAL IS 14 FT ABOVE HWY 550.C PHASE OPEN ONLY . CREW ENROUTE TO REPLACE ANCHOR, REFUSED LINE CUTOUT, ALL POWER RESTORED / GXJ VER/CRB L3/HFP IDC XXXX
4497 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-04-08 13:29 | 2021-04-08 16:30 | 26 | 181 | 4431141 | 4706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HT burnt off @ 39831124B22565, No trucks to pole. Crew required Released by crew 078S02,repairs made all cust restored @ 1630 please close ticket thanks.bt
4498 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2013-01-30 15:09 | 2013-01-30 16:05 | 84 | 56 | 4760301 | 4704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 38830183D00169, CLEARED ARRESTER, PATROLED LINE, ALL POWER RESTORED, B PHASE ONLY, A PHASE DID NOT LOSE POWER B PHASE 84 CUST ISO OCR 38830183D26091 VER/HFP L3/HFP IDC XXXX
4499 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-05-26 12:21 | 2020-05-26 13:55 | 50 | 94 | 4908941 | 4700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 302 burnt off riser for cutout, Crew required. Trucks to pole. Repairs made, line fuse restored @ 13:55
4500 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-12 10:42 | 2008-03-12 11:32 | 94 | 50 | 56483-1 | 4700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401// SERVICER FOUND HOT LINE CLAMP BURNT ON RECLOSER POLE (FAULT/ISO) 37830181B00385- WILL HAVE TO OPEN OTHER TWO PHASES TO MAKE REPAIRS/// /CLOSED @ 1132/ HOT LINE CLAMP BURNT OFF MIDDLE PHASE, OPENED RECLOSER TO REPAIR// B PHASE OPEN FROM ENTIRE TIME CLOSED // COD ON B -190// 323 ON A/C - MAP DISC ISSUED FOR WRONG PHASE CUSTOMERS THAT CALLED IN// IDCC DUP TO OPEN RECLOSER PH A IS MIDDLE NOT B IDC XXXX
4501 | South Williamson | 3200203 | BARRENSHE | SLATE BRANCH | 2013-07-07 02:21 | 2013-07-07 21:55 | 4 | 1174 | 4477491 | 4696 | DISTRIBUTION STATION | EQUIPMENT FAILURE | ARRESTER | COLEMAN-SPRIGG 69KV LINE LO // 69 CONDUCTOR DOWN T-LINE CREWS TO MAKE REPAIRS - TRANSFER CUSTOMERS TO ALT SOURCES WHERE AVAILABLE. ** UPDATE MULTIPLE T- LINE CREWS AND HEAVY CRANE ENROUTE TO ASSIST. . *** UPDATE TIME TO 2000 *******SA FAILED AT BARREHSHE, UPDATED FETR TO 2330 // SEE DDC LOG //VER/GAH IDC XXXX
4502 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-07-16 13:55 | 2015-07-17 16:00 | 3 | 1565 | 4893561 | 4695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BAD CLF CAN USE SERVICE BUCKET RELEASED BY CREW 074H02 THE CURRENT LIMITING FUSE FAILED.
4503 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-11-01 14:24 | 2012-11-01 20:25 | 13 | 361 | 4321861 | 4693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 20-5523 35/5 POLE BROKE NO TRUCK TRANS POLE 20-5521 10T OPEN RELEASED BY CREW 078S08/CREW ON SITE/FETR2100/VEM RELEASED BY CREW 078H14 ///VER/CRB L/3 CRB IDC XXXX
4504 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2013-02-07 16:09 | 2013-02-07 20:45 | 17 | 276 | 4799201 | 4692 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | RAY & WORRIX & GARRETTURD. SER. TO APT. BUILDING IS ONLY GETTING PATR POWER// CREW ENROUTE TO REPAIR SPLICED SERVICE TO BUILDING OUT /// COD-17 ISO TF 37830048C11055 VER/HFP L3/HFP IDCC PN1054 XXXX
4505 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-12-13 06:18 | 2017-12-13 08:36 | 34 | 138 | 4644511 | 4692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse melted out complete
4506 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-02-06 07:28 | 2008-02-06 13:59 | 12 | 391 | 50977-1 | 4692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GOING TO REFUSE LINE, FUSE CAME BACK OUT, I FOUND SOME 6A CU STRAINS BROKE AND LAYING ON NETURAL, CALL BRUCE AND GOT CREW COMMING//3312202/VER/CRB IDC XXXX
4507 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2016-03-22 15:11 | 2016-03-22 17:25 | 35 | 134 | 4871551 | 4690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESSTER ON POLE 37830187C00306/ ISO 37830187C00271/ COD 35. MOVED 50T FUSE BACK 1 POLE TO POLE 187-C-159. POLE 187-C-271 WE MADE THAT A SLOID BLADE./ VER/BOW AJB
4508 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-02-19 06:03 | 2013-02-19 09:10 | 25 | 187 | 4828811 | 4675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A BAD ARRESTOR IS ALL FOUND ///VER/CRB L/3 CRB IDC XXXX
4509 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-03-24 07:33 | 2008-03-24 10:40 | 25 | 187 | 60166-1 | 4675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// LINE FUSE OUT, PATROLLING LINE, BAD CUTOUT ON POLE 37830155000118 VER/HFP IDC XXXX
4510 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-08-22 22:36 | 2014-08-23 08:20 | 8 | 584 | 4409221 | 4672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT DOOR AT 69-1676, REPLACED DOOR, ALL POWER RESTORED VER/CRB
4511 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-06-30 22:01 | 2019-07-01 05:48 | 10 | 467 | 4624761 | 4670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad c/o on 251-166//cod 10. power restored at 5:48. change cutout complete on pole 251-166//
4512 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-04-27 02:25 | 2010-04-27 09:44 | 31 | 439 | 51775-1 | 4669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 595/08; PATROLLING LINESBURNT POLE 595/55; ISOLATED LINE AT 595/53 AND GROUNDED; PWR RESTORED TO ALL BUT TWO CUSTOMERS AT 0446HRS; CREW REQUIRED; SINGLE PHASE DEAD-END; NEED 40 CLASS 5 POLE, CUTOUT AND ARRESTOR, BRACKET, AND GUY WIRE; RELEASE TO LINE CREW RELEASED BY CREW 078S12// LOWERING EVERYTHING DOWN WORKING IN MUDDY GARDEN PUT DOWN MOLE PADS / WILL NEED TO LOWER PHONE LINES/ LAST 2 CUSTOMER ON @ 9 : 44 VER/KEP L3/KEP IDCC FP8, CHANGED FAILED EQUIPMENT FROM POLE XXXX
4513 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-01-14 01:39 | 2008-01-14 04:20 | 29 | 161 | 56482-1 | 4669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401101/ COD-29// HAD TO OPEN RECLOSER DUE TO POLE TOP FIRE - HELP ON WAY TO MAKE REPAIRS/ ETR 0500 // VER/LDA IDCC TOF0006 XXXX
4514 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2011-08-22 18:55 | 2011-08-22 19:39 | 106 | 44 | 4743751B | 4664 | TRANSMISSION LINE | EQUIPMENT FAILURE | POLE | SYDNEY STATION INTERRUPTED DUE TO TRANSMISSION.. TDC WORKING TO RESTORE STATION AS SOON AS POSSIBLE. VERIFIED BY DKG/TRANSMISSION POLE SPLIT ALLOWING STATIC WIRE TO FALL ON CONDUCTOR ..THIS OUTAGE FOR 106 CUST INTERRUPTED GOING BACK TO NORMAL IDC XXXX
4515 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2021-04-17 21:32 | 2021-04-18 10:24 | 17 | 772 | 4458801 | 4664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 kva transformer on pole 38820967B00115 is bad.climbed pole and could not get any voltage readings. will need crew.non truckable Released by crew 079S03//opened L/F on 967-389 at 09:17 to make repairs//closed fuse i at 10:24 Released by crew 074H07
4516 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-02-16 05:24 | 2009-02-16 13:10 | 10 | 466 | 62300-1 | 4660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 28528623 /// BAD CUTOUT GOT CREW COMMING TO HELP
4517 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-02-19 08:16 | 2009-02-19 10:33 | 34 | 137 | 64990-1 | 4658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN PATROLLING LINE// POLE FIRE AT POLE 37830129A00220 WILL ISOLATE FOR A PARTIAL RESTORE//TROUBLE ISOLATED ON INACTIVE XFMR POLE 37830129A00220 RESTORED COMPLETE//VER/CRB IDC XXXX
4518 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-01-20 15:57 | 2010-01-20 20:02 | 19 | 245 | 56949-1 | 4655 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO REPLACE. CREW ON-SITE - WORK UNDERWAY. OPENED XFMR @ 19:10 TO REPLACE. XFMR CHANGED. CLOSED @ 20:02. SH VER/HFP L3/HFP IDC XXXX
4519 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-06-09 23:20 | 2010-06-10 08:05 | 13 | 525 | 59556-1 | 4655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007906// WILL DISPATCH IN THE A.M. 3007906 45 POLE BURNT DUE TO CUTOUT BREAKAGE. WILL NEED 45POLE, POLE IS DOUBLE DEAD END 7200 WITH A 25KVA TRANSFORMER AND THE WIRE SIZE IS #2 ALUM. POLE IS TRUCK ACCESSIBLE I HAVE ISOLATED ON POLE 477-238 BY CUTTING LOOP WILL BE HOT TO THAT POINT,,,POLE #S IN FIELD COMPARED TO POLE#S ON FIELDVIEW ARE NOT RIGHT. WHEN YOU TURN ON SPRINGDALE ESTATES OFF OF 23 TURN ON ROAD TO RIGHT THERE WILL BE A ORANGE CONE THERE BURNT POLE WILL BE ON LEFT.45 POLE BURNT DUE TO IDC XXXX
4520 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-06-09 13:32 | 2008-06-09 15:11 | 47 | 99 | 60590-1 | 4653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3309104//CUSTOMERS MAPPED TO WRONG PHASE// LOOPS BURNT OPEN ON B PHASE ON POLE 401-11 (SEE 60546-1)//WILL HAVE TO OPEN THIS RECLOSER LATER IN ORDER TO REPAIR//PLEASE ADJUST START TIME AND USE THIS ORDER FOR THAT OUTAGE SINCE THIS ORDER IS PREDICTING THE RECLOSER ALREADY////VER/CRB
4521 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-02-28 07:50 | 2011-02-28 13:00 | 15 | 310 | 63698-1 | 4650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON XFORM. ON HENDRIX NEED LINE CREW POLE 69-545 ON FLOYD ST.SEC.ALSO DOWN ON POLE FEEDING SCHOOL FLASHING LIGHT IN FRONT OF VERITY SCHOOL ON BLACKBURN.LADDER IS LAYING ON THE GRASS AT THIS TIME AT ELLIOT AVE. 1698 HOUSECUTOUT REPAIRED AT FFLOYD ST. AT 12:30.SEC. AT VERITY SCH. COMP. AT 13:00 IDC CHANGED COUNT FROM 15 XXXX
4522 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-12-04 22:51 | 2020-12-05 02:40 | 48 | 229 | 4746491 | 4647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c ph l/f out on 737-221/48cc/Transformer cutout failed on 737-303 and burnt top of pole off. Isolated hot-line clamp on 737-279. Closed PH C line fuse on 737-221 @ 00:25 restoring all except xfmr 737-303. Crew enroute to make repairs.Transformer cutout failed on 737-303 and burnt top of pole off. Isolated hot-line clamp on 737-279. Closed PH C line fuse on 737-221 @ 00:25 restoring all except xfmr 737-303. Crew enroute to make repairs. Restored final customer @ 2:40. sh
4523 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-02-19 14:13 | 2014-02-19 17:05 | 27 | 172 | 4402621 | 4644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | THE CENTER PHASE RECLOSER IS OPEN ON POLE 356-71 COD 27 B PHASEI AM GOING TO OPEN THE OTHER TWO TO MAKE IT SAFE B PHASE OUT ORIGINALLY COD 27 OPENED OTHERS @_15:10_____INTERRUPTING 32 MORE WIRE IS DOWN AT POLE 332-88 , WE NEED CREW TO PUT WIRE BACK UP . THE CENTER PHASE RECLOSER IS OPEN ON POLE 356-71 I AM GOING TO OPEN THE OTHER TWO TO MAKE IT SAFE. IOPENED AT 15:10 ON @1705 ***DUPLICATE IN HOIS FOR ADDITIONAL 32 FROM 1519 TILL 1705 VER/SEF
4524 | Pikeville | 3421002 | BREAKS | GRASSY | 2010-01-05 09:47 | 2010-01-05 11:13 | 54 | 86 | 61076-1 | 4644 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | TRANSMISSION OUTAGE// VER/DBM IDC XXXX
4525 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-01-29 04:53 | 2018-01-29 13:10 | 29 | 497 | 4780321 | 4641 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO FIRE///CSC HIT WRONG BUTTON//ALL OUT/// Dispatched in accordance with KYPCo Late Night Callout Guidelines.//cutout broke on pole 936-14//back on hill above rock cliff///need 3 men///need hard cover up//crew enroute//opened switch on pole 936-8 to make repairs@ 1042//NO FIRE///CSC HIT WRONG BUTTON//ALL OUT/// OPENED SW @ 1042 CLOSED 1310//MADE MD TO SHOW FUSE ON POLE 38830936C00014
4526 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-08-22 08:13 | 2019-08-22 14:10 | 13 | 357 | 4925781 | 4641 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | R AKEMON // @ 0936 PATROLLING LINE/// BAD 167KVA STEPDOWN@ 0936 PATROLLING LINE/// BAD 167KVA STEPDOWN Released by crew 077S01 L3/HFP
4527 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-18 09:00 | 2010-01-18 13:50 | 16 | 290 | 55777-1 | 4640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF ON POLE 353-21 ( 40 / 5 ) TRUCKS TO POLR OK . LINE FUSE OPENED AND GROUNDED ON POLE 377-20. NEEDS LINE CREW. RELEASED BY CREW 078S01//COD 16//ISO// VER/DBM IDC XXXX
4528 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-11-18 18:24 | 2015-11-19 00:50 | 12 | 386 | 4465481 | 4632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE #120-84 WILL PATROLL/// CUTOUT BROKE UP ON SIDE OF HILL WILL CHANGE// CHANGED BAD CUTOUT AND CLOSED LINE FUSE IN @ 12:50/ ISO 37830120A00084/ COD 12/ VER/BOW
4529 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-09-10 13:12 | 2020-09-10 15:04 | 65 | 112 | 4449031 | 4630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURNT OFF ON C PHASE RECLOSER 38830833C00498//COD 15 FROM BEGINNING OF OUTAGE//WILL HAVE TO OPEN A & B PHASES TO REPAIR//OPENED @ 1405 CLOSED @15:04 Released by crew 076S03
4530 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-10-14 04:23 | 2020-10-14 10:55 | 75 | 392 | 4553701 | 4629 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Opened Recl @ 0602//Closed recl @ 0635wire down on pole 228-2, isolated on this pole, will need line crew and manuel r-o-w crew // RESTORED @1055
4531 | Hazard | 3309302 | VICCO | JEFF | 2022-11-09 19:28 | 2022-11-09 23:45 | 18 | 257 | 4119021 | 4626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva transformer 7200 also need cutout and t bracker Released by crew 077H05 . changed xfmr
4532 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2022-07-01 15:16 | 2022-07-01 16:23 | 69 | 67 | 4356301 | 4623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Crew will need to open rec to make repairs to crossarm on pole 37830443000003 (69COD) Crew will need to open rec to make repairs to crossarm on pole 37830443000003 (69COD) off at 15:16 on at 16:23 repairs comp.
4533 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-08-13 01:08 | 2015-08-14 15:39 | 2 | 2311 | 4129861 | 4622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | WORK IN THE AM/ PADMOUNT XFMR HAS PADDLES BURNING.CAUSEING FLICKERING & SHORT OUTAGES. THIS IS A 50 KVA 7200/120/240 FEED THROUGH. PLEASE SEND TO TIM HALL HE SAID HE WOULD HAVE THIS CHANGED OUT EATHER THIS EVENING OR IN THE MORNING.//OPENED BAYONET @ 1230 //WILL HAVE TO REPLACE TRANSFOMER//CLOSED @ 1539 SEE 4135161 - OUTAGE TO REPLACE TR VER/CRB L3/HFP XXXHFP
4534 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-06-11 12:55 | 2019-06-11 14:45 | 42 | 110 | 4481841 | 4620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER XFRF IS OUT,WILL RE-FUSE//////////CUTOUT IS BROKEN,WILL HAVE TO REPLACE IT,WILL REPLACE ALL SINCE POLE HAS TO BE CLIMBED//////RICK RAY ENROUTE SHORTLY////////MADE REPAIRS&RESTORED,OFF 12:55,ON14:45
4535 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-09-10 05:19 | 2015-09-10 12:20 | 20 | 421 | 4221511 | 4620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK DURING NORMAL WORK HOURSWILL WORK DURING NORMAL WORK HOUR.. 50T LF OPEN @ 68-2003, HOT TAP LIFED @ 68-B-646 @ 0900 , POLE 68-1222 ON FIRE,WILL WORK DURING NORMAL WORK HOUR.. 50T LF OPEN @ 68-2003, HOT TAP LIFED & GROUNDED @ 68-646, POLE 68-1222 ON FIRE, 50T RESTORED @ 09:00 MP RELEASED BY CREW 078S07 VER/CRB L3/HFP XXXHFP AJB
4536 | Whitesburg | 3312901 | JENKINS | KONA | 2018-08-29 20:20 | 2018-08-29 23:05 | 28 | 165 | 4013121 | 4620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 403-1 , I changed it out
4537 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-11-19 08:30 | 2017-11-19 12:21 | 20 | 231 | 4581771 | 4620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no crew required
4538 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-07-05 16:09 | 2022-07-05 18:54 | 28 | 165 | 4384831 | 4620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | Recloser open on pole 122-235 will patrol///Isolated primary metering on 122-355 customer said fire was coming out around 34.5 metering///Closed recloser in @ 18:54 and restored all customers except for mines beyond primary metering///Made 4390141 outage for mines will need to check metering///Tagged metring to DDC
4539 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-05-11 06:05 | 2016-05-11 14:15 | 17 | 490 | 4196331 | 4618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | . LINE FUSE OUT ON POLE 423-113, WIRE OUT OF SAG FROM POLE 399-341 TO 342 THINK IT IS BLOWING TOGETHER .CLOSED LINE FUSE IN AT 10:23, XFMR FUSE BLEW ON POLE 399-345 BAD XFMR. RELEASED BY CREW 077S11 REPLACED TRANSFORMER POWER RESTORED AT 14:15 RELEASED BY CREW 075H03/ ISO 37830423A00113/ COD 17/ VER/BOW
4540 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-04-14 16:28 | 2009-04-14 16:55 | 171 | 27 | 52231-1 | 4617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JRV ON SITE @ 16:00.....POLE 1088-A-147.....BURNT UP CUTOUT ON RECLOSER POLE.....CALLED CREW....CAN REPLACE....WILL HAVE TO OPEN AND CLEAR BOTH RECLOSERS ON THIS POLE TO CHANGE....// OPENED RECLOSERS @ 1628 TO MAKE REPAIRS//OPENED & CLEARED BOTH RECLOSERS @ 16:28...REPLACED BOTH BYPASS CUTOUTS....CLOSED RECLOSERS//COD 171// VER/DBM IDCC PN31 XXXX
4541 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2012-09-28 12:03 | 2012-09-28 13:08 | 71 | 65 | 4095771 | 4615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED AT 1220 TO SAFELY REPAIR CROSS ARMS ASSOCIATED WITH PO 4094751 CLOSED AT 1308 IDCC TOF1203, CDC89 CHANGED COUNT FROM 4 XXXX
4542 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2019-07-24 12:00 | 2019-07-24 13:34 | 49 | 94 | 4787481 | 4606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RECLOSER 38830473000125 OPEN//COD 49//TRANSFORMER 38830473000048 ALREADY OPEN ON ANOTHER OUTAGE 4787161//broken tie wire located pole 473-15. primary/neutral contact. closed @ 1334
4543 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-07-28 16:03 | 2009-07-28 21:10 | 15 | 307 | 55785-1 | 4605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 901-5003, SPLITTED IN HALF, ALSO BURNTED THE END OF THE ARM OFF, WELL NEED CREW, 8 FT CROSSARM AND CUTOUT, THIS IS CREW REQUIRED, CAN USE BUCKET, IS STRAIGHT LINE 3 PHASE POLE, NO PINS JUST 8 FT CROSSARM, IS ALL, ALSO HAD TO OPEN UP 3 RECLOSER ON POLE 901-5559, LONG ENOUGH TO CLEAR UP CUTOUT, HAVE RECLOSER BACK IN AND EVERYONE IS BACK ON BUT THE CUSTOMER OF THIS TRANSFORMER POLE 901-5003//COD 15// VER/DBM IDCC TON2010 XXXX
4544 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-03-24 15:39 | 2018-03-25 10:50 | 4 | 1151 | 4049481 | 4604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPen Line Fuse pole857-276 . replaced cutout gate and refused , ALL WORK COMPLETE / GXJ/ ISO 38830857000276/ COD 4/
4545 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-07-20 08:55 | 2011-07-20 12:15 | 23 | 200 | 4564521 | 4600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREW REQUIRED--CAN USE SMALL BUCKET--NEED TO REPLACE RISERS ON 75KVA TRANSFORMER AND SPLIT LOAD ON CONNECTORS RELEASED BY CREW 078S07 // NO CUSTOMERS OUT AT THIS TIME, CREW TO RETURN TOMORROW AND REPLACE TRANSFORMER AND BREAK UP LOAD AND INSTALL SECOND TRANSFORMER //CREW REQUIRED--CAN USE SMALL BUCKET--NEED TO REPLACE RISERS ON 75KVA TRANSFORMER AND SPLIT LOAD ON CONNECTORS RELEASED BY CREW 078S07 WILL WORK IN THE AM,//VER/CRB
4546 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-10-14 12:25 | 2010-10-14 16:35 | 88 | 250 | 59671-1 | 4600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37327210 // POLE 69-8220 BURNT OFF HOT OFF 69-8033 POLE 69-4518 50T 0N 1;15 INSTALLED 30T ON 69-6027 RELEASED BY CREW 078S08 COD-88 VER/HFP L3/HFP IDC XXXX
4547 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-04-03 03:23 | 2009-04-03 05:18 | 40 | 115 | 64361-1 | 4600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BLOWED-UP ARRESTOR,CLEARED IT UP AND RE-FUSED VER/KEP L3/KEP AJB
4548 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-12-19 00:35 | 2015-12-19 06:31 | 17 | 356 | 4543981 | 4596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ONE SPAN OF PRIMARY IS DOWN AT POLE 355A-202. PRIMARY PULLED OUT OF SLEEVE. WILL NEED ONE MAN AND A BIG BUCKET. ISOLATED AND GROUNDED TROUBLE AT 355A-201. CLOSED LINE FUSE 355B-187 AT 05:00 RESTORING POWER TO ALL CUSTOMERS EXCEPT ONE. MADE REPAIRS AND CLOSED X-FMR FUSE ON POLE 355A-202 THUS, RESTORING POWER AT 06:31, 12/19/2105. RELEASED BY CREW 077H17
4549 | South Williamson | 3411401 | DEWEY | INEZ | 2019-02-08 00:31 | 2019-02-08 13:39 | 6 | 788 | 4767111 | 4592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HELD PER KPCO CALLOUT GUIDELINES///Line fuse blown 745-B-35.. I isolated broken XFMR cutout on pole 769-A-96 and closed line fuse745-B-35 @ 13:05 restored all customers but one I will go back and replace broken cutout//replaced cutout & restore final customer @13:39 Released by crew 074H06
4550 | Hazard | 3311102 | STINNETT | BEECH FORK | 2010-05-06 03:26 | 2010-05-06 18:44 | 5 | 918 | 56279-1 | 4590 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | TRANSMISSION OUTAGE / PATROLLING BY HELICOPTER / - FETR 2000 -// TRANSMISSION STRUCTURE DAMAGED WILL BE WORKING THROUGH THE DAY TO RESTORE THE REMAINING 5 CUSTOMERS. IDC XXXX
4551 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2018-07-09 13:22 | 2018-07-09 17:52 | 17 | 270 | 4754051 | 4590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | MADE AED ON L/A //line fuse out on 1113-A-3 bad arretser on 1112-C-51,cut arreser in the clear restored power at 17:52 .
4552 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-12-05 14:05 | 2012-12-05 14:25 | 229 | 20 | 4444781 | 4580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW OPENED TO SAFELY MAKE REPAIRS ON 4444071 VER/KEP IDC XXXX
4553 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2013-04-15 02:14 | 2013-04-15 17:29 | 5 | 915 | 4009121 | 4575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL BE DISPATCHED AT REG WK TIME TODAY.BAD XFMR , IT WILL TAKE LINE CREW AND YARD DOG. CECIL SEXTON IS COMMING PLEASE SEND HIM TICKET RELEASED BY CREW 077S12 COD-5 ISO TF 37830449A40673 VER/HFP L3/HFP IDC XXXX
4554 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-03-04 11:50 | 2016-03-05 13:15 | 3 | 1525 | H4813901 | 4575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | **SEE 48139901** #4 COPPER PRIMARY DOWN AT 574-10,,BROKE IN CLEAR AT FUSE POLE, FAULT POLE IS ENERGIZED,,NO TRUCK, COULD USE 6-WHEELER,,PULLED OUT OF SLEEVE,,ISOLATION POLE IS 574-10/ OPENED LINE FUSE 38830374A10082 @ 1150 TO REPAIR PRIMARY @ 38830374000010/,,OPENED FUSE 38830374A10082 AT 11:50/ ALL REPAIRS MADE & ALL POWER RESTORED/ FINAL RESTORATION 13:15/ DUPLICATE IN HOIS/ VER/BOW AJB
4555 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-01-18 14:50 | 2010-01-18 15:45 | 83 | 55 | 56131-1 | 4565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPLACING JUMPER//COD 83// VER/DBM IDC XXXX
4556 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-08-18 14:25 | 2017-08-18 15:20 | 83 | 55 | H4275131 | 4565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RIGHT HAND RECLOSER LOCKED OUT ON 794-29/PATROLNG/A PHASE COD:14 //PIN ISULATOR FAILED ON POLE 794-33 AND BURNED CONDUCTOR INTO//BEING HELD UP BY HOT TAP///CREW ENROUTE///WILL HAVE TO OPEN OTHER TWO RECLOSERS WEN CREW GETS HERE TO MAKE REPAIRS////PIN ISULATOR FAILED ON POLE 794-33 AND BURNED CONDUCTOR INTO//OPENED 2 OCR 1425 VER/AWD SJG
4557 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-11-10 11:51 | 2018-11-10 14:34 | 28 | 163 | 4386641 | 4564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE RECLOSER 37830378C00152 OPEN//COD 28//hot line clamp on stirrup burned off. I replaced it//DID NOT OPEN A & C PHASES L3/HFP
4558 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2021-04-30 06:59 | 2021-04-30 12:50 | 13 | 351 | 4500131 | 4563 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | step down pole 771-d-85 burned off due to cut out failure/// //need line crew and flaggers//crew enroute//DIG # 2104300320 Released by crew 079S01
4559 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2012-10-28 20:24 | 2012-10-29 05:15 | 33 | 531 | 4179691 | 4563 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, POLE FIRE AT POLE 38830329000144, ISOLATED AT 38830329000128, ONLY ABOUT 1 OF 40 POLE GONE AND NO PHONE, CAN PROBABLY LOWER AND BE OK, NEED 4 WHEEL DRIVE IT IS IN BACK YARD AND WET. CLOSED FUSE AT 22:30 (LOWER EVERYTHING ON POLE NO CLEARANCE ISSUES ;ALL POWER RESTORED AT 05:15). VER/SDB IDC XXXX
4560 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2021-11-03 17:30 | 2021-11-03 19:25 | 222 | 83 | 4054691 | 4562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER/ DOL 1160230/ Crossarm failed on pole 38820992D00433/
4561 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-05-11 17:40 | 2010-05-11 20:50 | 24 | 190 | 59708-1 | 4560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35073159 // CREW REQUIRED. CUTOUT ON POLE 168-129 BROKE DOWN AND BURNED TOP OF POLE ALMOST INTO. I OPENED LINE CUTOUT ON POLE 168-6 AT 17:40 AND PUT FIRE OUT. I WILL CALL FOR HELP. ONLY DEADENINGFK. IS OUT OF POWER. WE REPAIRED POLE AND CLOSED LINE FUSE IN AT 20:50. COD-24 VER/HFP L3/HFP IDC XXXX
4562 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-01-25 15:31 | 2008-01-25 17:25 | 40 | 114 | 59927-1 | 4560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HIGH SIDE CUTOUT ON STEPDOWN TRANSFORMER IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CAN NOT REACH CUTOUT WITH MY TRUCK. THEY ARE SENDING ONE OUT OF PIKEVILLE THAT WILL REACH. WE CHANGED CUTOUT.//3411901//VER/CRB IDCC CDC92 XXXX
4563 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-29 07:43 | 2014-01-29 10:10 | 31 | 147 | 4322091 | 4557 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLLING LINE. FUSE BROKE COD-31 ISO 38830833C00589 VER/HFP L3/HFP IDC XXXX
4564 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-12-18 13:44 | 2016-12-19 00:35 | 7 | 651 | 4216071 | 4557 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED CUSTOMER THEY SAID THEIR LIGHTS ARE VERY DIM AND HAPPENING ALL THE TIME THEY SAID NEIGHBORS HAVING SAME ISSUE AND THEY HAVE TURN THEIR POWER OFF/CREW REQUIRED NO TRUCKS NO. 4COPPER BY CREEK RELEASED BY CREW 078S03,REPAIRS MADE XFMR FUSE IN @ 0035 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/KEP
4565 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-05-03 02:59 | 2010-05-03 04:38 | 46 | 99 | 54596-1 | 4554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE A OUT LOOKING LINE OVER. COD-40 BAD CUTOUT ON RECLOSER POLE 1038-444 THAT FEEDS COBURN HOLLOW. //VER/GAH IDC XXXX
4566 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-11-20 11:09 | 2012-11-20 13:00 | 41 | 111 | 4410881 | 4551 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY LEAD HAS BURNT OFF RECLOSER, POWER RESTORED COD-41 ISO PO 37830274000036 VER/HFP L3/HFP IDC XXXX
4567 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-12-07 05:20 | 2011-12-07 11:10 | 13 | 350 | 4147291 | 4550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 425-25, FUSE OPEN ON 425-21. LINE CREW REQUIRED RELEASED BY CREW 078S11 COD-13 ISO LF 38830425000021 VER/HFP L3/HFP IDC XXXX
4568 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-10-01 04:30 | 2011-10-01 10:20 | 13 | 350 | 4936541 | 4550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3314401//WILL CHECK AT REGUAR WORK TIME AS PER SET GUIDELINES WHEN ABOVE FREEZING //BAKER HEADED TO MARSHALL.3314401//WILL CHECK AT REGUAR WORK TIME AS PER SET GUIDELINES WHEN ABOVE FREEZING //. ,WIRE DOWN AT POLE NO.426-140, OPEN AT POLE NO. 426-186 , I WILL NEED ANOTHER MAN AND A BIG BUCKET COD-13 ISO LF 37830426B00186 VER/HFP L3/HFP IDC CHANGED CAUSE FROM OTHER XXXX
4569 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-03-01 21:55 | 2018-03-01 22:40 | 101 | 45 | 4896271 | 4545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Pole fire on pole 38830069C14030, Bad poletop insulator. Crew required, No trucks. Will need to take outage on pole 38830069C14027. Released by crew 078H04 deenergized line at 21:55, power restored at 22:40
4570 | Pikeville | 3413402 | GARRETT | LACKEY | 2020-04-17 15:40 | 2020-04-17 16:20 | 173 | 40 | 4712351 | 4544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3413402; associated with 4710851; LF assembly failure at pole 87-D-8 is causing fuse cutout door to track across, shorting the A-phase primary on the Garrett/Lackey ckt; servicer measured ~67V phase-to-ground on A-phase; load-breaking sws at pole 87-D-75 (xfmr on pole will stay hot) to alleviate low-voltage condition; cc 111; opened sws from 1604 to 1620; per S. Garrido (circuit coordinator), we can check for hazards and let R. Quick close these sws when he's ready;
4571 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-02-17 04:00 | 2014-02-18 05:14 | 3 | 1514 | 4395761 | 4542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 39831098C00580 IS ROTTEN SECONDARY PROBLEM ON POLE 39831098C00580--NO TRUCK TO POLE RELEASED BY CREW 078S07///BURNT UP XFMR RISER CONNECTIONS ON 1/0 SEC//REPLACED CONN AND CHANGED BROKEN CUTOUT//VOLT 122.8/245.4///PWR CK OK/RESTORED @ 05:14//SEND NOTE TO S MARTIN TO HAVE WINDSTREAM CHANGE POLE VER/PDP
4572 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2019-06-19 20:18 | 2019-06-20 00:05 | 20 | 227 | 4550701 | 4540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @172-232, patrolling. Found a bad trans. cutout @37820172000274, cutout wasnt feeding anything so I removed it and closed l/f back in @0005.
4573 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2013-01-30 15:31 | 2013-01-30 16:34 | 72 | 63 | 4758321 | 4536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 37830296A31306 ROTTED OFF AT GROUND, LEANING TOWARD FIRE DEPT.--- LINE CREW ENROUTE. RELEASED BY CREW 077S04POLE 37830296A31306 ROTTED OFF AT GROUND, LEANING TOWARD FIRE DEPT.--- LINE CREW ENROUTE. --- POLE REPLACED OPENED FUSES ON 37830296A30449 AT 15:31, CLOSED AT 16:34, POWER RESTORED.//ISO 37830296A30449//COD 72// VER/DBM IDC XXXX
4574 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2011-11-22 09:25 | 2011-11-22 11:50 | 35 | 145 | 4100031 | 4535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REC CLOSED, FUSE OPEN AT POLE 329-40, ALSO LINE FUSE OPEN ON POLE 330-45, REPLACED BOTH FUSES, FOUND BAD INSULATOR AT POLE 329-41, REPLACED INSULATOR, ALL POWER RESTORED AT 11:50, FUSE ON POLE 330-45 CLOSED AT 11:20,//COD 35// VER/DBM IDCC STP MISSING, TON XXXX
4575 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2010-11-29 04:46 | 2010-11-29 11:38 | 11 | 412 | 60423-1 | 4532 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | ONLY GETTING 47 VOLTS FROM ONE SIDE OF TRANSFORMER, CREW REQUIRED. TRUCK ACCESSIBLE, RELEASED BY CREW 077S04 POWER AT 11;38 W.MELTON OPENED AT 11;00//COD 11// VER/DBM IDC XXXX
4576 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-01-10 07:40 | 2016-01-10 20:15 | 6 | 755 | 4598591 | 4530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 50T OPEN @ 1148-147, POLE TOP @ 1148-845. NO TRK RELEASED BY CREW 078S07---CREW ON SITE---NO TRUCK ACCESS--HAVE TO USE YARDDOG TO MAKE REPAIRS---GNDD & TAGD TO RMV--PLEASE RE-ASSIGN TKT TO ME-- RELEASED BY CREW 078H1650T OPEN @ 1148-147, POLE TOP @ 1148-845. NO TRK RELEASED BY CREW 078S07---CREW ON SITE---NO TRUCK ACCESS--HAVE TO USE YARDDOG TO MAKE REPAIRS---GNDD & TAGD TO RMV--PLEASE RE-ASSIGN TKT TO ME--REPAIRS MADE--50T LF 1148-147 IN @ 20:15---TBL TKT COMP. VER/CRB AJB
4577 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-10-02 05:18 | 2012-10-02 10:20 | 15 | 302 | 4106071 | 4530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW -LINE BUCKET--NEED TO REPLACE CUTOUTS AND ARRESTORS ON TRANSFORMER BANK AT WESTWOOD FIRE DEPT , BREWER WILL FOLLOW UP WITH CREW AT STARTING TIME.NEED CREW -LINE BUCKET--NEED TO REPLACE CUTOUTS AND ARRESTORS ON TRANSFORMER BANK AT WESTWOOD FIRE DEPT RELEASED BY CREW 078S07/FETR 10:30 JEH/// A PHASE C/O OPENED WILL OPEN B PHASE/ B PHASE OPENED @ 09:20// REPAIRS COMP. POWER REST. @ 10:20 // JEH IDC XXXX
4578 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-01-02 00:28 | 2021-01-02 10:20 | 32 | 592 | 4842791 | 4529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 291-10 broken cutout isolated/line fuse back in at 0235 hrs /crew required no trucks Released by crew 078S03 FETR 10:45 all pwr restored 10:20 pleaseclose ticket Released by crew 078H06
4579 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-01-30 15:57 | 2009-02-02 19:25 | 1 | 4528 | 52750-1 | 4528 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | COINS CALL 1-31-09 AT 1830 POWER OFF\ASSESSORS ASSIGNED 2/2/09\PRB/SERVICE CONNECTIONS BURNT UP AT XFMR/NO TRUCK/VEM REPAIRES SERVICE ON AT 19:25 }
4580 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-07-22 17:37 | 2018-07-22 22:20 | 16 | 283 | 4836101 | 4528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke down on p-786-183.burning primary down on786-52. opened rec on 786--728 at 19.20..open xfmr bank on 786-183.rem hot taps on786- 52..grd and tagged to myself /// TALKED TO SERVICER ABOUT THIS ONE - PRIMARY BURNT DOWN AT POLE 38830786B00052 FEEDING TOWARD RECL POLE 38830786B20728 COD-16 ISO PO @ 38830786B00052
4581 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-05-16 09:04 | 2008-05-16 09:35 | 146 | 31 | 64637-1 | 4526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3008702/ RISER BURNT OFF B PHASE RECLOSER POLE 38830142A00144-- 146 CUSTOMERS OUT// SENT EMAIL TO LLOYD RAYBURN TO HAVE NEW BASKET INSTALLED ON B PHASE RECLOSER...HFP VER/HFP IDC XXXX
4582 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-09-26 16:31 | 2009-09-26 19:25 | 26 | 174 | 64242-1 | 4524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED FUSE POLE#1123-166 COD-26 TO ISOLATE BURNING POLE OPENED RECLOSER AT 1900 TO MAKE REPAIRS RESTORED ALL POWER AT 1925 CALL ON ORDER 64152 MADE DUP VER/KEP L3/KEP IDC XXXX
4583 | Whitesburg | 3409503 | BURDINE | JENKINS | 2009-11-04 05:32 | 2009-11-04 10:55 | 14 | 323 | 59344-1 | 4522 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #6 COPPER PRIMARY BROKE AT POLE 358-115 WILL NEED LINE CREW TO MAKE REPAIRS, WILL HAVE TO OPEN LINE FUSE AT POLE 358-118 TO ISOLATE WHEN CREW IS READY TO MAKE REPAIRS RELEASED BY CREW 077S11// OPENED FUSE AT 1032 RESTORED ALL AT 1055 VER/KEP L3/KEP IDCC CNT7, PN114, DID NOT MAKE NEW OUTAGE, NO MORE CUSTOMERS OUTAGED, USED LINE FUSE AS ORIGINAL CLEARING DEVICE XXXX
4584 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-08-01 10:39 | 2008-08-01 14:25 | 20 | 226 | 63347-1 | 4520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG PRIMARY LINE FUSE OUT/ B REYNOLDS TO WORK RELEASED BY CREW 078S07UG PRIMARY LINE FUSE OUT/ B REYNOLDS TO WORK //BAD PRIMARY CABLE BETWEEN 69-288 AND 69-289-ISOLATED AN TAGED CABLE ENTERED AED ENTRY - HFP VER/HFP IDCC CDC83 XXXX
4585 | South Williamson | 3411401 | DEWEY | INEZ | 2017-05-25 13:25 | 2017-05-25 17:00 | 21 | 215 | 4858761 | 4515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RT HAND PHASE OUT `B` PHASE 21 CUST//OPENED OTHERS AT 1545RIGHT HAND RECLOSER OPEN ON 649-202//TREE FELL AT POLE 649-56 AND SMALL LIMB HANGING ON LOOP AND CROSS ARM//HAVE LIMB REMOVED//INSULATOR BAD ON POLE 649-56 WHERE THE LIMB HAD FALLEN//OPENING OTHER TWO RECLOSER TO MAKE REPAIRS//REPAIRS MADE//RESTORED ALL AT 17:00// RELEASED BY CREW 079S01 38820649B00202 38820649B00056 VER/AWD AJB
4586 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-10-03 20:19 | 2021-10-04 11:22 | 5 | 903 | 4313011 | 4515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout very manual will need 3 man line crew and R O W crew Released by crew 077H02.. restored power at 11:22..
4587 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-06-11 12:45 | 2011-06-11 14:30 | 43 | 105 | 4293161 | 4515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1123-4561 BAD CUTOUT AND LA LIGHTING//COD 43// VER/DBM IDC STAYED ON ONLY 1/2 HOUR FROM LAST RESORED ORDER XXXX
4588 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-10-25 10:40 | 2010-10-25 17:30 | 11 | 410 | 63056-1 | 4510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-5501 BURNT OFF NEED 40 CLASS 4 POLE RELEASED BY CREW 078S08//CREW ON SITE WILL NEED TO HAND DIG POLE HOLE FETR19:00 P TOLLIVER//COMPLETE AT 17:30 ALL CUST. RESTORED. P TOLLIVER //VER/CRB IDC XXXX
4589 | Whitesburg | 3401301 | FLEMING | NEON | 2015-02-20 04:45 | 2015-02-20 13:06 | 9 | 501 | 4047081 | 4509 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | I OPENED XFMR FUSE ON BURNING XFMR AT 04:45,WE NEED NEW XFMR AND LEADS50 KVA 7200 LINE CREW AND MATERIAL HANDLER BUCKET RELEASED BY CREW 077S12 // THIS MAY BE ASSOCIATED WITH 4056611 - NEED MORE INFO VER/HFP L3/HFP
4590 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-01-25 15:16 | 2013-01-25 16:02 | 98 | 46 | 4740871 | 4508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | C- PHASE OUT INITALLY 98 CUST BAD ARRESTER ON POLE 1060-163BAD ARRESTER ON POLE 1060-163 RELEASED BY CREW 077S05 COD-98 ISO OCR 38831083C30532 VER/HFP L3/HFP IDC XXXX
4591 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-07-16 15:16 | 2009-07-16 20:27 | 31 | 311 | 66607-1 | 4508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT ON PL#27-120 WILL PATROL R RAY PL#27-182 BURNED OFF AT CUT OUT ISOLATED AT PL#27-146 REPLACED 25T FUSE AT PL#27-120 ONLY 1 CUST OUT @ 1730//COD 31// VER/DBM MLR IDC XXXX
4592 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-05-09 05:45 | 2008-05-09 11:51 | 42 | 366 | 58820-1 | 4507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000701/// RECLOSER LOCKED OUT ON OHIO RIVER RD. SERVICER PATROLING AT THIS TIME. NO HAZARDS REPORTED. RELEASED BY CREW 078S06// POLE BURNT OFF -//VER/CRB MAF TON1145, CNT178 A PHASE ONLY PER SERVICEMAN PER CONF CALL IDC XXXX
4593 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-03-28 19:49 | 2008-03-28 23:28 | 64 | 219 | 61710-1 | 4503 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602//CREW REQUIRED//POLETOP BURNT OFF//BAD CUTOUT//COD 63//@ 2057 RESTORED ALL BUT THE FAULT POLE//3308602// BAD CUTOUT BURNET TOP OF POLE OFF. VER/PDP IDCC TOF1747 XXXX
4594 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-12-22 22:45 | 2010-12-23 02:55 | 18 | 250 | 55191-1 | 4500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38193850 //OPENED FUSE @ 2245 - 18 CUST//,, SHOULD BE ENOUGH CLEARANCE TO LOWER, BACK YARD, ACCESS ISSUES, CREW NOTIFIED.,,, ALL REPAIRS MADE, POWER RESTORED VER/ARN IDCC PN6089 XXXX
4595 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2021-07-13 13:10 | 2021-07-13 19:15 | 16 | 365 | 4906211 | 4500 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | bad transformer on pole 426-C-88 Released by crew 077S11 //transformer was no bad found failed cutout opened both line fuses and transformer on 37830426C00087 to replace failed cutout off@ 1845 repaired and restored all @1915
4596 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2019-06-16 19:47 | 2019-06-16 22:47 | 25 | 180 | 4515511 | 4500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ///broken cutout on pole 38830067D00317 NBT CREW REQ NO TAGGS NO GROUNDSbroken cutout on pole 38830067D00317 NBT CREW REQ NO TAGGS NO GROUNDS Released by crew 078H01. Repairs made, tickett complete. closed at 22:47
4597 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-03-06 10:50 | 2021-03-06 15:00 | 18 | 250 | 4309181 | 4500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 116-18 25T Line fuse blown, bad step down on 116-746. Crew required, trucks to pole Released by crew 078S02
4598 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-06-22 05:42 | 2021-06-22 08:35 | 26 | 173 | 4788831 | 4498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 819-1//found broke cutout on pole 818-91//making repairs//repairs made//restored at 8:35//complete//em
4599 | South Williamson | 3411401 | DEWEY | INEZ | 2021-09-22 11:41 | 2021-09-22 16:22 | 16 | 281 | 4270431 | 4496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 744-290//cutout broke on pole 744-419//replaced cutout/also blew fuse on pole 744-405///restored at 16:22//complete//em
4600 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-05-27 06:41 | 2022-05-27 14:48 | 13 | 487 | 4959881 | 4486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire slipped out of sleeve on pole 828-32.. primary is hot up to p-828-42..line fuse on 828-27 is in..need to open line fuse on 27 and ground line.need line crew. no truck access,,, Released by crew 076S01
4601 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-13 08:00 | 2012-02-13 08:38 | 118 | 38 | H4343871 | 4484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CENTER PHASE WIRE HAS BURNED DOWN AT RECLOSER POLE { 97-346 }. ALL 3 RECLOSERS ARE STILL IN. I AM WAITING FOR TIM HALL TO CALL ME BACK TO SEE WHAT HE WANTS TO DO. TIM SAID HE WOULD JUST WAIT UNTIL START TIME AND SEND A CREW. I WILL STAY AND WATCH WIRE. WE OPENED THE 3 RECLOSERS AT 97-346 AT 08:00, PUT WIRE UP, AND CLOSED THEM BACK IN AT 08:38. VER/KEP IDC XXXX
4602 | Hazard | 3309301 | VICCO | REDFOX | 2017-05-25 13:40 | 2017-05-25 15:03 | 54 | 83 | 4858881 | 4482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REPLACING LEAKING STEPDOWN TRANSFORMER OFF @ 1358 ON 1503 ISO LF37830276000136 VER/HFP L3/HFP AJB
4603 | Pikeville | 3308402 | BECKHAM | CARR CREEK | 2017-01-10 16:59 | 2017-01-10 18:22 | 54 | 83 | 4284141 | 4482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER OPEN ON POLE 230C-341 , SHOWING BPHASE TO GROUND FAULT . FOUND BAD RECLOSER ON POLE 231B-199 . CLEARED RECLOSER . CLOSED RECLOSER ON POLE 230C-341 @ 18:22 .//MADE AED AND NOTES ON MAP VER/CRB // NOTE THIS CKT CROSSES OMS BOUNDS & DUPLICATED FOR THAT REASON - SCADA AGREES WITH TIMES - L3/HFP XXXHFP AJB
4604 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-02-03 22:00 | 2014-02-03 22:28 | 160 | 28 | 4345911 | 4480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE 600 AMP DISC ON POLE 39831124A20582 IS ARCING AT LOAD SIDE PAD--NEEDS REPLACED ASSAP RELEASED BY CREW 078S07//NO OUTAGE AT THIS TIME 1850//.OPENED 600 AMP SWITCHES TO SAFELY MAKE REPAIRS..APPROX 30 MINUTE OUTAGE 160 CUSTOMERS OFF 2200 ON 2228 VER/ARN IDC XXXX
4605 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-06-10 15:23 | 2021-06-11 10:03 | 4 | 1120 | 4707821 | 4480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SPOKE WITH DUTY AND GOING TO HOLD THIS TIL MORNING // Bad trans. cutout @37830093000013, this is an active account but no one is living there. This will take at least a couple men, can only get a pickup up the hill in a blind curve, will also need a manual r.o.w. crew to cut path to pole. Will need a 19.9 cutout and bracket. Released by crew 074S05////bad 15kv 19.9 xfm.will need line crew to replace..non-truck...xfm. pole is 93-13.please send copy to PR and Steve Released by crew 074H09// Email
4606 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2016-08-21 01:29 | 2016-08-21 10:49 | 8 | 560 | 4820151 | 4480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK IN THE AM. BAD 12 KV,120-240, 37.5 XFMER, TRK OK. BLACKBURN & MCGUIRE. PLEASE CHANGE C/O & L/A RELEASED BY CREW 078S07/FOREMAN ON SITE/CREW LOADING MATERIAL/FETR1145/VEM/REPAIRS MADE AND ALL CUST RESTORED 1049/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830045A10077/ COD 8/ VER/BOW L3/HFP XXXHFP
4607 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-10-02 13:36 | 2012-10-02 18:33 | 96 | 297 | 4108101 | 4477 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 147-170 POLE BURNT OFF//// POLE CHANGED OUT WIRE TRANSFERRED, POWER RESTORED. COD-96 ISO OCR 37830147000054 VER/HFP L3/HFP IDC CHANGED OFF TIME FROM 1205 ESTMATED XXXX
4608 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2009-03-11 05:46 | 2009-03-11 08:45 | 25 | 179 | 57130-1 | 4475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VER/HFP 3000601 -HIT TAP BURNT THRU BASKET. REPLACED HOT TAP. NEED TO REPLACE BASKET. SEND TO L. RAYBURN. L3/HFP IDC XXXX
4609 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-09-22 12:00 | 2021-09-22 14:52 | 26 | 172 | 4270971 | 4472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse out on 248C/52 patrolling bad cutout 224D/327 send to tech. to replace pole 224D/237///emailed Rob Pigman for follow up
4610 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2008-10-17 04:23 | 2008-10-17 05:06 | 104 | 43 | 56410-1 | 4472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/ARN IDC XXXX
4611 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2022-01-23 05:46 | 2022-01-23 11:30 | 13 | 344 | 4397631 | 4472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2340 Sellars Street Ashland Ky, Customer Tameka Griffith states lights flickered then heard loud boom and power went out/ customer states meter is blank/bad 25kva/crew reqd, truck ok. Released by crew 078S04. complete br
4612 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-02-27 04:14 | 2019-02-27 08:37 | 17 | 263 | 4930781 | 4471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | will work in the AM 2/27 per latenight guidelines/// Hot tap lead burnt open on line fuse 194-82 will ake repairs// Replaced hot tap lead and closed line fuse in @ 08:37 and restored service L3/HFP
4613 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-07-11 16:53 | 2021-07-11 18:05 | 62 | 72 | 4892931 | 4464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STURRIP BURNT OFF ON RECLOSER POLE 241-284 WILL BE MAKING REPAIRS///REPLACED BURNT OFF STIRRUP AND CLOSED RECLOSER IN @ 18:05 AND RESTORED SERVICE
4614 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-11-30 11:23 | 2021-11-30 13:47 | 31 | 144 | 4134021 | 4464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Primary is energized and is laying 3-4 feet from ground. This is a Windstream pole that is broken. Will need 1 manual tree crew to clear path to make repairs. Possibly need flaggers, W. Happy Ridge is narrow and busy at times for pole to be drop off. Released by crew 078X05///no outage till opened Recl 38830067A16022 at 1123///crew on site resagged primary@67-A-6036 broke pole @67-A-132 to be set at latter date rec in @13:47 please close tic RM WO to be wrote
4615 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-05-31 08:37 | 2008-05-31 10:14 | 46 | 97 | 53122-1 | 4462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3300602//A PHASE RECLOSER OPEN ON POLE #296-1477.... TWO SPANS PRIMARY BURNT DOWN//COD 46 ...WILL HAVE TO OPEN ALL 3 PHASES TO MAKE REPAIRS (WILL INTERRUPT 14 MORE CUST)//CHECKING FOR CAUSE//OPENED RECLOSERS AT 9:55 & CLOSED THEM AT 10;14...RESTORED POWER//FAILED QUICKSLEEVE WAS CAUSE// VER/DBM IDC XXXX
4616 | Hazard | 3309301 | VICCO | REDFOX | 2010-09-11 06:51 | 2010-09-11 08:28 | 46 | 97 | 65396-1 | 4462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830326B00040 REC. OPEN, CHECKING LINE////// BAD C/O ON POLE 326-71/////// REPLACED C/O, POWER RESTORED COD-46 VER/HFP L3/HFP IDC XXXX
4617 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-07-06 15:33 | 2018-07-07 16:18 | 3 | 1485 | 4741201 | 4455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 2 poles are broke, pole # 159-13, and pole # 159-46, one is 3 phase, the other is single phase deadend, arms are stripped on a third pole, 159-14. all work is manuel. Released by crew 077S02
4618 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-02-10 11:37 | 2008-02-10 18:30 | 41 | 413 | 53392-1 | 4453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000102//BAD XFRMR ON POLE 46-555, TOOK OUT LINE FUSE// ISOLATED XFRMER AND CLOSED FUSE @ 1200//CREW REQUIRED//DUTY SUPERVISOR CONTACTING CREW//COD 41//RESTORED 32 CUST @ 1200//CREW ENROUTE//PROJECTED ETR 2000//NEED FETR-------POWER ON @ 18:30// VER/DBM IDC XXXX
4619 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2012-06-15 12:38 | 2012-06-15 14:24 | 42 | 106 | 4918291 | 4452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//COD 42// VER/DBM IDC XXXX
4620 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-12-27 15:04 | 2009-12-28 15:48 | 3 | 1484 | 56876-1 | 4452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | VNJ/3312202/HAZARD, ALL OUT/AIRPORT OUT OF POWER/REGIONAL AIRPORT RD/// SAME AS TICKET #61160 , REPLACED PADMOUNT TRANSFORMER JKC
4621 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2009-04-30 15:09 | 2009-04-30 20:35 | 59 | 326 | 60700-1 | 4444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE IS OUT//COD 59//A PHASE RECLOSER ON POLE 1099-161 OUT///POLE TOP BURNT OFF--M PHELPS CUT LOOP AN INSTALLED GROUND ON POLE 39831098D06024--RECLOSER BACK IN AT 16:20A PHASE RECLOSER ON POLE 1099-161 OUT//POLE TOP BURNT OFF--M PHELPS CUT LOOP AN INSTALLED GROUND ON POLE 39831098D06024--RECLOSER BACK IN AT 16:20-- CLOSED OPEN LOOPS AR 2035 VER/KEP L3/KEP IDC XXXX
4622 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-11-03 19:30 | 2010-11-03 23:20 | 53 | 230 | 51464-1 | 4442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED BAD CUTOUT ON POLE 38830140C05008-CALLING CREW-RECLOSER BACK ON AT 20:51 1 CUSTOMER STILL OUT RELEASED BY CREW 078S07//CREW ON SITE NO TRUCK TO POLE PRT///COMPLETE AT 23:20 ALL CUST. RESTORED P TOLLIVER// RELEASED BY CREW 078H03// COD 53// VER/DBM IDC XXXX
4623 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-01-04 05:13 | 2008-01-04 10:09 | 15 | 296 | 53487-1 | 4440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000202///WIREDOWN POLE TO POLE #6A 3 TO 4 MAN CREW NEEDED NO TRUCK TO POLE FUSE SIZE IS INCORRECT ON FIELVIEW 25 TIS CORRECT RELEASED BY CREW 078H04 VER/KEP IDC XXXX
4624 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2008-12-14 13:42 | 2008-12-14 16:10 | 30 | 148 | 58270-1 | 4440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 3000103//100 REQUEST TO MOVE SPAN GUY DOWN POLE SLAPPING PHASE INTO SPAN GUY POLE 45-5590//COD 30 VER/KEP L3/KEP IDC XXXX
4625 | Hazard | 3302704 | HAZARD | KENMONT | 2017-02-06 08:48 | 2017-02-06 11:15 | 67 | 147 | 4360481 | 4434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FAILED ARRESTOR ON POLE 37830320C00006//CLOSED L/F @ 0940//37830320C00002 REFUSED LINE AT 9:40 === ARRESTER WENT BAD ON POLE 37830320C00006 === REPLACED CUTOUT AND ARRESTER POWER ON AT 11:15 === VER/CRB L3/HFP XXXHFP AJB
4626 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-12-20 09:13 | 2020-12-20 13:50 | 16 | 277 | 4788071 | 4432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Secondary connection failed on xfmr pole and burnt neutral and hot in two. Additional personnel enroute to assist. Made repairs and restored @ 13:50. sh//ALL CUST HAD PART POWER FROM BEGINNING
4627 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2009-11-23 14:50 | 2009-11-23 14:57 | 633 | 7 | 62864-1 | 4431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP SCADA INDICATED THE 10TH STREET-10-02 CB OPENED AT 1450. 10TH STREET-10-12 LOAD WAS TRANSFERED TO THIS CB WHICH HAS NO CUSTOMERS ON IT DUE, TO CONVERSION WORK. /// CAUSE UNDETERMINED WHEN THIS ORDER WAS CLOSED....REPORTED SEEING A FLASH WHILE CB IN NON-RECLOSE L3/HFP IDC BAD CABLE CAUSED FLASH DURING COVER UP, THIS BREAKER WAS NOT ACTUALLY OUT BUT SINCE ONLY THIS CIRCUIT CUSTOMERS WERE AFFECTED, THE OUTAGE WAS LEFT ON THIS BREAKER. NO OUTAGE CREATED FOR 10-02 BECAUSE IT HAS NOT CUSTOMERS XXXX
4628 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-04-05 13:17 | 2011-04-05 13:27 | 443 | 10 | 66060-1 | 4430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREWS OPENED RECLOSER IN ORDER TO ISOLATE BUCKARM POLE THAT HAS DAMAGED CROSSARMS//COD 443// RELEASED BY CREW 078H02 IDC XXXX
4629 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-10-02 10:45 | 2013-10-02 12:48 | 36 | 123 | 4904671 | 4428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | COD-36 ENTERED MD /// ISO 38820941B00112// VER/DBM L3/HFP IDC XXXX
4630 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-06-11 21:31 | 2011-06-12 12:15 | 5 | 884 | 4298971 | 4420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NEED CREW HOT TAP BURNT OF ON POLE 24-668 NO TRUCK RELEASED BY CREW 074H07NEED CREW HOT TAP BURNT OF ON POLE 24-668 NO TRUCK ;;;; HOT TAP REPLACED POWER BACK ON//COD 5//ISO// VER/DBM IDC XXXX
4631 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-10-25 19:10 | 2010-10-25 22:51 | 20 | 221 | 63618-1 | 4420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37475942 // 256-53 POLE BURN ALMOST INTO WILL OPEN LINE UP ON POLE 37830256000012. OPENED LINE FUSE UP AT 19:10. WORK COMPLTED// VER/CRB IDC XXXX
4632 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2017-01-03 16:10 | 2017-01-03 19:00 | 26 | 170 | 4265631 | 4420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CLAMP BURNED OF @ POLE 181C-176 , HAVE HELP ON WAY .POWER BACK ON @ 19:00/ ISO 37830181C00176/ COD 26/ VER/BOW L3/HFP XXXHFP AJB
4633 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-08-14 20:48 | 2010-08-15 14:52 | 14 | 1084 | 54879-1 | 4412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND LINE FUSE BLOWN ON POLE 1121-164, PATROLLED FOUND BAD TRANSFORMER ON POLE 1121-167, 25 KVA, CAN USE TRUCK, NEED CREW TO MAKE REPAIRS,HAVE ALL CUST BACK ON BUT 2 CLOSED IN LINE FUSE AT 2355 RELEASED BY CREW 078S06 RELEASED BY CREW 078H01 VER/HFP L3/HFP
4634 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-02-28 07:39 | 2011-02-28 15:40 | 31 | 481 | 63667-1 | 4411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE 188-162 40/4 , NEED NEW 37.5 KVA XFORMER, 100 WATT D/D LIGHT , NO TRUCKS TO POLE. NEED YARD DOG. NEEDS LINE CREW. RELEASED BY CREW 078S01/REPAIRS COMPLETE POWER RESTORED @ 15:40 J, HEMLEPP 078H05 RELEASED BY CREW 078H05//VER/CRB IDCC TON STEP ONE 1540 CHANGED FROM WEAHTER WIND, XXXX
4635 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-12-20 13:57 | 2012-12-20 15:00 | 70 | 63 | 4488281 | 4410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 92-124 BAD 19.9 LA NEED LINE CREWPOLE 92-124 BAD 12KV LA REPAIRED VER/KEP
4636 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-08-16 09:11 | 2021-08-16 12:41 | 21 | 210 | 4076891 | 4410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | L/F blown on 881-20 will patrol/// Tried fuse @ 11:12 and came back out will patrol again/// Found and replaced bad DE insulator on pole 881-181. Also changed oversized line fuse on pole 881-21 from a 30t to a 12t (please show on map). Restored all customers @ 12:41.
4637 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-09-13 19:30 | 2019-09-13 23:00 | 21 | 210 | 4015291 | 4410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap burned off B phase on 38821058C00042// repairs made // on @ 23:00 L3/HFP
4638 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-01-01 03:32 | 2022-01-01 10:53 | 10 | 441 | 4242791 | 4410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew reqd/C & B phase line fuse blown/ B phase xfmer fuse open & C phase cutout broke on pole 39831123C35093 no truck Released by crew 078S04////replaced 3 C/Os ///Complete BR
4639 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-07-25 11:16 | 2013-07-25 15:45 | 28 | 269 | 4591891 | 4404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | THE WIRE IS DOWN BETWEEN POLES 402-57 AND 402-58 , I CAN ISOLATE ON POLE 402-56 AND GET THE REST OF THE POWER BACK ON. I CLOSED THE FUSE ON POLE 402-69 IN AT 13:29 RELEASED BY CREW 077S12 POWER RESTORED@15:45 VER/KEP IDC XXXX
4640 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-02-24 05:53 | 2011-02-24 12:00 | 12 | 367 | 60600-1 | 4404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD 19.9KV//VER/CRB IDC WAITED ON SECOND SHIFT GUY AT 1000 XXXX
4641 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2009-05-16 23:17 | 2009-05-17 03:42 | 27 | 265 | 59807-1 | 4403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNED TOP OF POLE OFF..728-86..ISOLATED ON POLE 728-85...HAVE TO WALK BACK ON THE MTN TO REFUSE 728-15..REFUSED AT .12.50.AM..BB.. VER/KEP L3/KEP IDCC CNT38 XXXX
4642 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-02-06 06:14 | 2008-02-06 16:43 | 7 | 629 | 50532-1 | 4403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER// SMALL OIL LEAK AROUND BUSHINGS// TRUCK OK// BESIDE SEWER PLANT ON PARK ST// NEED CREW RELEASED BY CREW 078S07 RON VIRGIN WILL CALL IN WHEN COMPLETE RELEASED BY CREW 078H02 VER/KEP IDC XXXX
4643 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-10-04 05:20 | 2012-10-04 14:30 | 8 | 550 | 4113001 | 4400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK AFTER REGULAR WORKTIME AS PER SET GUIDELINES // TRANSFORMER BAD, 19.9 KV 120/240 25 KVA, WE SHOULD REPLACE WITH A 50 KVA. CAN USE TRUCK. RELEASED BY CREW 074S02####REPLACED BAD TRANS RESTORED POWER AT 14:30 R. WORRIX ///VER/CRB L/3 CRB IDC XXXX
4644 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-09-18 15:26 | 2014-09-18 18:22 | 25 | 176 | 4509431 | 4400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKE PRIMARY P 38821138A00118/// POLE LAYING OVER IN TREES// OP OCR ISO 38821114D00130/// COD 25/// POLE 1138A118 IS BROKEN/// R/W CREWS ON SITE./// LINE CREW ENROUTE./// KY POWER POLE BROKE WHILE TELEPHONE CONTRACTOR WAS CLIMBING POLE AND IT FELL OVER WITH HIM ON IT/// NO INJURIES REPORTED@THIS TIMEBROKE PRIMARY POLE/// POLE LAYING OVER IN TREES// OPEN RECLOSE ISO 38821114D00130/// COD 25.POLE 1138A118 IS BROKEN. R/W CREWS ON SITE. LINE CREW ENROUTE.REPAIRS MADE. REMOVED INACTIVE S VER/CRB AJBC TOF14:51
4645 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-09-22 18:01 | 2014-09-22 20:57 | 25 | 176 | 4520571 | 4400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER IS OPEN ON 645-194 PATROLLING LINE//WIRE DOWN// , FOUND LINE DOWN AT 645-13 TO 14 6A POSSILE TO GET SERVICE BUCKET TO POLE, ISOLATED GROUNDED&TAGGED TO V MULLINS AT 645-194/CREW ON SITE/FETR2200/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST2057/PLEASE CLOSE TICKET/THANKS/VEM /// COD-25 ISO OCR 38830645000194 VER/HFP L3/HFP AJB
4646 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-10-09 15:02 | 2015-10-10 01:30 | 7 | 628 | 4332761 | 4396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE38830222D00159 NEED CREW FLOAT PRI, TONIGHT, WILL NEED S IX WHEELER 2 AL, TECH TO WRITE UP JOB NXT WEEK ///WILL HAVE TO CHANGE POLE---YARDDOG ONLY--CALLING FOR 2 MORE MEN AND TECH--POLE ROTTED AND FELL--NOT ENUF CLEARANCE TO SPAN--REPLACING POLE W/40CL5---REPLACED POLE--PWR RESTORED @ 01:30---TBL TKT COMP VER/SEF L3/HFP HFPC CC0 FEC57
4647 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-03-08 13:17 | 2008-03-08 18:15 | 40 | 298 | 55130-1 | 4395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702//FAILED CUTOUT ON POLE 142-4006, POLE FIRE//COD 40//ISOLATED ON POLE 142-204 AND RESTORED @ 1440//CREW ENROUTE//NEED CUTOUT /LA RELEASED BY CREW 078S08 POWER ON @ 18:15 BLR// VER/DBM IDC XXXX
4648 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-05-22 11:28 | 2013-05-22 12:29 | 72 | 61 | H4154211 | 4392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TWO COND. BURNT DOWN AT 171/181 PUT C PHASE ON TO A PHASE TO PICK UP CUST. RELEASED BY CREW 077H04 -- ONLY AND C PHASES OUT -- OPENED PHASE A AT 11:28 TO WORK ON LINE -- PUT ALL LOAD ON PHASE A AT POLE 171-181 WILL NEED FIX AT A LATER TIME -- ALL POWER RESTORED AT 12:29 MWL IDCC DUP TO OPEN PH C XXXX
4649 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2014-05-10 23:46 | 2014-05-11 11:25 | 8 | 699 | 4684471 | 4392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN DAYLIGHT..BAD CUTOUT . BURNED TOP OF POLE OFF 776-39 ISOLATED ON P-776-37..TAGGED AND GRD..LINE FUSE BACK IN AT 8.05. RELEASED BY CREW 076S01// REPAIRS COMPLTED// RESTORED AT 11:25 RELEASED BY CREW 076H02 IDCC TON0815 XXXX
4650 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-04-15 16:42 | 2011-04-15 17:06 | 183 | 24 | H57094-1 | 4392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY BURNT IN TWO ON 785-350 <<PHASE A ONLY>>. OPENED A PHASE REC ON 785-640 TO ISOLATE @ 16:15. CREW ENROUTE. OPENED PH B & C REC @ 16:42 TO MAKE REPAIRS. REPAIRS COMPLETE. CLOSED ALL THREE REC ON 785-640 @ 17:06 RESTORING ALL CUSTOMERS. SH RELEASED BY CREW 076S02 IDC XXXX
4651 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-01-24 23:21 | 2010-01-25 03:40 | 29 | 259 | 59060-1 | 4391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, LINE FUSE OUT, PATROLLING LINE WR#33571690 BAD CUTOUT VER/KEP L3/KEP IDC XXXX
4652 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2018-03-21 15:34 | 2018-03-21 22:53 | 10 | 439 | 4039741 | 4390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Crew required, bad 50kva two bushing transformer/ 7200v on pole 45-7131. on the corner of 29th st, and central ave./ ISO 38830045D37131/ COD 10*** 3 Mismapped customers/crew on site/FETR 2330/vem/all cust restored 2253/please close ticket/thanks/vem
4653 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-05-24 15:40 | 2017-05-24 15:54 | 313 | 14 | 4851061 | 4382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO 4848741//OPENED RECLOSER IN ORDER TO REPLACE BAD INSULATOR//COD 313//OPENED RECLOSERS AT 15.40.CLOSED THEM BACK IN AT 15.54 VER/HFP L3/HFP AJB
4654 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-05-13 12:00 | 2017-05-13 12:12 | 365 | 12 | H4794581B | 4380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SEE DOL CASE 741489///BELFRY - BELFRY ISOALTION FOR BUS DISCS REPLACEMENT///RECORD FOR OPENING FOR RESTORATION OF BELFRY - BELFRY 12KV CB A/// VER/DKM AJB
4655 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-05-21 19:26 | 2016-05-21 19:46 | 219 | 20 | 4245391 | 4380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENING SWITCH 164-275 TO ALLOW CREW FINISH REMOVING SWITCH 164-250/OPEN @1926 CLOSED 1946// VER/ ADH AJB
4656 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-06-26 03:04 | 2009-06-26 07:14 | 20 | 250 | 61391-1 | 4376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116703//PATROLING LINE--PEPLACED BAD CUTOUT ON POLE 38830019A00086--CLOSED LINE FUSE IN ON POLE 38830019A00086 AT 06:35--LINE FUSE STILL OPEN AT POLE 39831147B00503- REMOVED IA SERVICE ON POLE 39831147B00986 VER/KEP L3/KEP IDC XXXX
4657 | Hazard | 3311103 | STINNETT | WENDOVER | 2012-10-28 08:46 | 2012-10-28 13:20 | 24 | 274 | 4177881 | 4376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 911 ETA 0940. TOP OF POLE BURNT OFF OPENED LINE @ 435-40 AND RESTORED POWER UP TO THAT POINT @ 1000 POWER RESTORED @1320 RELEASED BY CREW 077S01//COD 24// VER/DBM IDC XXXX
4658 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-07-23 07:52 | 2008-07-23 22:27 | 5 | 875 | 58444-1 | 4375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. IS BAD. 50KVA. I WILL CALL PIKEVILLE. RELEASED BY CREW 074S01//3401001//VER/CRB IDC XXXX
4659 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-05-25 11:56 | 2010-05-25 12:34 | 115 | 38 | 50652-1 | 4370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONTRACT CREW (LARRY LAWSON 3664) WAS TRANSFERING CONDUCTORS WHEN A ROTTEN SECTION OF LINE BROKE @ POLE 295-69 //CREW PUTTING WIRE BACK UP//COD 115 // VER/KEP L3/KEP IDC XXXX
4660 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2012-07-26 23:20 | 2012-07-27 02:30 | 23 | 190 | 4838991 | 4370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD DEAD END BELL AT 38830350B20183, NEED ASSISTANCE TO CHANGE, J MORELAND BEING CALLED. RELEASED BY CREW 078S05/REPAIRS COMPLETE ON 207-222 REPLACED DEAD END BELL/40T LINE FUSE VER/ARN IDC XXXX
4661 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-04-20 00:46 | 2020-04-20 15:20 | 5 | 874 | 4721281 | 4370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.broke 7200 cutout, manual. need line crew, 7200 cutout, bracket and arrester. Released by crew 077S10
4662 | Hazard | 3303901 | LESLIE | HYDEN | 2015-09-06 05:40 | 2015-09-06 12:17 | 11 | 397 | 4208831 | 4367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WILL HAVE SERVICER CHECK AT START OF REGULAR SHIFT//TOM . FOUND LOOP INTO ON POLE37830413A00009 FEEDING TO POLE 413A-7 . GOING TO PATROL REST OF LINE .//MADE MDC TO SHOW L/F ON POLE 37830413A00009//SERVICER INSTALLED L/F HERE VER/CRB L3/DKG
4663 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2008-01-10 14:53 | 2008-01-10 16:30 | 45 | 97 | 55552-1 | 4365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 31176602//REMOVED HOT TAP 138-115 DO NOT PUT BACK ON LINE INACTIVE PRI. LINE// VER/TOM IDC XXXX
4664 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-10-25 09:38 | 2011-10-25 11:07 | 49 | 89 | 4018541 | 4361 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 501-34 PATROLLING LINE,, FOUND CUTOUT STARTING TO BREAKDOWN ON 501-424 LIFTED HOTTAP ON THAT POLE, ISOLATING FAOULT, FUSE BACK IN ON 501-34 AT 1107, ONE CUSTOMER REMAINNING OFF AT THIS TIME. XMF BACK ON AT 1200 ON 501-424 APR NO ACCT ON LAST TRANS ////VER/CRB IDCC CDC92 XXXX
4665 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-02-06 11:32 | 2008-02-06 17:35 | 12 | 363 | 51368-1 | 4356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR HAS BROKEN DOWN ON POLE 263-191. TIM HALL IS SENDING HELP. WE CUT R/W AND CHANGED INSULATORS. VER/HFP IDC XXXX
4666 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-03-04 19:10 | 2015-03-05 19:22 | 3 | 1452 | 4102181 | 4356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | TRIED FUSE, CAME BACK OUT, NEED TO HOLD UNTILL DAYLIGHT. NO ACCESS. CREEK FLOODED/ RELEASED BY CREW 077S04/ ISO 37830225C00176/ COD 3 ANCHOR ROTTED AND LET POLE LAY OVER POLE 225-172 MADE REPAIRS AND RESTORED POWER AT 1922 O77HO1 VER/ARN
4667 | Hazard | 3303902 | LESLIE | WOOTON | 2022-06-15 21:42 | 2022-06-16 15:50 | 4 | 1088 | 4132911 | 4352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | attempted to cut path to pole almost got snake bite, also cust has dog in lot and cant get to pole through lot, cant get cust to door , bad 50 kva 19.9 manuel, need ROW CREW Released by crew 077S07.repairs comp
4668 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2017-01-09 10:08 | 2017-01-09 14:40 | 16 | 272 | 4280271 | 4352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER. CREWS WORKING TO REPLACE. REPLACED WITH 75 KVA AND RESTORED @ 14:40. SH/ ISO 38830785D20337/ COD 16 L3/HFP
4669 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2013-02-21 14:11 | 2013-02-21 15:13 | 70 | 62 | 4837961 | 4340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | <<PHASE A RECLOSER ONLY>> LOAD SIDE HOT-LINE CLAMP BURNT OFF ON RECLOSER. COD-70 ON A PHASE REPLACED CLAMP AND CLOSED PHASE A RECLOSER @ 15:13 RESTORING OUTAGED CUSTOMERS. SH COD-70 ISO PO @ 38830834D00239 VER/HFP L3/HFP IDC XXXX
4670 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-05-06 19:16 | 2010-05-06 19:24 | 542 | 8 | 56709-1 | 4336 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | SWITCHING TO RESTORE STINNETT STATION NORMAL SOS 1617 REV91 .. OPENED AT 1916. CLOSED AT 1924 VER/PDP IDC XXXX
4671 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-11-30 01:59 | 2022-11-30 06:30 | 16 | 271 | 4203791 | 4336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | line fuse out on 679-142.patrolling . 678-63 wire laying on take off tap.. causing fault.. bad location. tying main line back in..grd on p-678-63
4672 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-09-25 14:28 | 2014-09-25 14:45 | 255 | 17 | 4528681 | 4335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SERVICER OPENING SWITCH TO SAFELY CHANGE OUT POLE 38831039000014// COD 255// OFF @ 14:28 ON @ 14:45 L3/IDC XXXX AJB
4673 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-02-16 16:55 | 2022-02-16 18:20 | 51 | 85 | 4489021 | 4335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary burnt up got cleared up and repaired// needs tech to come out to get job wrote up for this pole between poles 38830044B00178 and 38830044B00179 may need pole added mid span to raise this up// email sent
4674 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-04-16 00:48 | 2010-04-16 04:05 | 22 | 197 | 63676-1 | 4334 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO. 4 COPPER WIRE PULL LOOSE FROM SLEEVE. WIRE BROKE BETWEEN POLE 47-52-53 VER/LDA IDCC FP69 CHANGED COUNT FROM 36 XXXX
4675 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-01-20 14:15 | 2008-01-20 15:31 | 57 | 76 | 58033-1 | 4332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SAME AS 57891 C PHASE OPENED ON SWITCH POLE 49 (PER SERVICER J.SHEPHERD) DURING RESTORATION RECLOSER POLE 70-151 WAS ALREADY OPEN COD-57 VER/KEP IDC XXXX
4676 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-10-31 04:32 | 2022-10-31 10:33 | 12 | 361 | 4079741 | 4332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. had a broke 7200 cutout at pole 189-A-227 that took line fuse at pole 189-A-53 got xformer cutot changed out on pole 227 and got line fuse restored at pole 189-A-53 at a time of 10:33
4677 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-05-25 09:33 | 2011-05-26 09:37 | 3 | 1444 | 4170121 | 4332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER TO CHECK IN THE AM --- BAD CUTOUT, POWER RESTORED.//COD 3//CUSTOUT WAS BREAKING DOWN BUT POWER STAYED ON UNTIL SERVICER OPENED IT TO REPLACE IT//OPENED @ 0933 AND CLOSED @ 0937// VER/DBM
4678 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2011-04-06 14:04 | 2011-04-06 15:55 | 39 | 111 | 50710-1 | 4329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTNING ARRESTOR POLE212-212,, REPLACED ARRESTER COD-39 ISO LF 37830187C00271 VER/HFP L3/HFP
4679 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2012-10-27 12:10 | 2012-10-27 18:01 | 27 | 351 | 4176071 | 4328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LINE FUSE BLOWN ON POLE 1122-109, 20T, PATROLLED FOUND BURNTED OF 405 POLE ON COMPTON LANE, WELL BE CREW REQ, CAN USE TRUCKS, HAVE HOT TAP LIFTED ON POLE 1098-524, DO NOT HAVE GROUNDED OR TAGGED AT THIS TIME, WELL NEED NEW CUTOUT AND EVERYTHING ELSE WILL WORK BACK, HAS UNDERGROUND SERVICE ON THIS POLE. RESTORED POWER OT ALL CUST BUT 8 AT 1330 RELEASED BY CREW 078S06//ISO 39831122C00109//COD 27//MD FILED// VER/DBM IDC XXXX
4680 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-07-11 10:31 | 2010-07-11 15:40 | 14 | 309 | 65109-1 | 4326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER DIDT PICK UP WHEN THE FIRST ONE WAS PUT IN == RESET RECLOASER == POWER OK//COD 14//THIS RECLOSER HAS BEEN PROBLEMATIC PER SERVICER//WHEN PREVIOUS (LARGER) OUTAGE WAS RESTORED THIS RECLOSER OPENED UP//SERVICER PATROLLED AND CLOSED REC BACK IN //EMAILED TO ENGINEER IDC XXXX
4681 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-10-14 18:27 | 2014-10-14 21:35 | 23 | 188 | 4626561 | 4324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD POST TOP INSULATOR//CREW ENROUTE//COD 23 --- POWER RESTORED.// VER/DBM L3/HFP AJB
4682 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-12-17 15:45 | 2019-12-17 17:19 | 46 | 94 | 4163901 | 4324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED STEP-DOWN ON POLE 37830397000010 @ 1545//COD 46//NO OUTAGE TILL THEN// replaced cutout on pole 397-20, restored power at 17:19
4683 | Whitesburg | 3309302 | VICCO | JEFF | 2008-05-05 08:35 | 2008-05-05 09:11 | 120 | 36 | 57051-1 | 4320 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | 3309302//STATION SERVICER ISOLATING EQUIPMENT THAT FAILED NOW, POTENTIAL TRANSFORMER FAILED. VER/HFP IDC XXXX
4684 | Hazard | 3310502 | HADDIX | CANOE | 2019-12-27 02:10 | 2019-12-27 06:10 | 18 | 240 | 4184371 | 4320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | # 4 al pull into need two men and big bucket
4685 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-12-11 01:57 | 2018-12-11 07:50 | 24 | 353 | 4549981 | 4314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Transformer failed and damaged cutout, post=top insulator and dead-end ins. Opened rec 852-16 @ 5:15 to make repairs. Repairs underway. Had xfmrs 38830852000249, 211 & 84 off from start. Made repairs and closed rec 852-16 @ 7:50 restoring all cust. sh L3/HFP
4686 | Hazard | 3303902 | LESLIE | WOOTON | 2018-04-23 16:38 | 2018-04-23 20:25 | 19 | 227 | 4267731 | 4313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Released by crew 077S01 BAD 250KVA STEPDOWN, 2 SPANS OF WIRE DOWN
4687 | South Williamson | 3202201 | LOVELY | LOVELY | 2011-02-27 16:53 | 2011-02-27 20:40 | 19 | 227 | 63498-1 | 4313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED UP FUSE TO ISOLATE POLE FIRE // COD 19 // WR# 38958245 // CREW ENROUTE TO REPAIR. CREWS MADE REPAIRS AND ARE TRIMMING SOME LIMBS THAT ARE CONTACTING PRIMARY. INSTALLED POLE-TOP EXTENSION. RESTORED @ 20:40. SH//COD 19// VER/DBM IDC XXXX
4688 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-06-21 14:04 | 2011-06-21 17:20 | 29 | 196 | 4363521 | 4309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OPEN ON 446-263, WIRE OFF INSULATOR AT POLE 446-22 BURNING CROSSARM, LIFTED CLAMP ON 446-90 TO ISOLATE .. CLOSED RECLOSER AT 15:15 RELEASED BY CREW 077S11 OPENED RECLOSER AT 1710 CLOSED IT AT 1720//COD 29// VER/DBM IDC XXXX
4689 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-05-21 18:44 | 2018-05-22 05:55 | 100 | 283 | 4389251 | 4308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Crew Required All Power Restored But Need Cutout Changed/ Line fuse cutout is cracked and broken/ closed line fuse in and its holding for now but needs a crew to change cutout will have to open main line to change/ ISO 38830116A00135/ COD 12 L3/HFP
4690 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2009-02-22 11:37 | 2009-02-22 15:40 | 51 | 243 | 50304-1 | 4308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | //VER/CRB IDCC TOF1124 XXXX
4691 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-08-02 15:17 | 2013-08-05 15:03 | 1 | 4306 | 4617561 | 4306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO SEND 4 WHEEL DRIVE PICKUP OR 6 WHEELER, CANNOT DRIVE BUCKET TRUCK TO SITE / GXJ //WILL WORK MONDAY 8-5 BAD XFMR GETTING HELP TO REPLACE, XFMR CHANGED ON AT 15:03 VER/CRB L/3 CRB
4692 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-20 20:14 | 2015-02-21 14:10 | 4 | 1076 | 4059321 | 4304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, REPLACING NOW. POWER RESTORED 4 CUST OUT FROM 2014 TILL 1410 VER/SEF L3/DKGXXXX
4693 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-11-30 14:21 | 2015-11-30 15:47 | 50 | 172 | 4495961 | 4300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | LINE FUSE MELTED ON POLE 38821060C00022, PATROLLING THE LINE TO MAKE SURE NOTHING IS WRONG. PRIMARY IS OFF THE INSULATOR AT POLE 38821060B00028. REPAIRS MADE, ON POLE 38821036C00175 OPENED THE C PHASE AT 15:40 TO CHANGE THE FUSE FROM A 40T TO A 65T, CLOSED BACK IN AT 15:47. (CREATED NEW OUTAGE FOR FUSE ON POLE 1036-C-175)
4694 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-03-27 13:59 | 2008-03-27 14:10 | 390 | 11 | 61199-1H | 4290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116102//REPLACING CUTOUT/HAD TO OPEN 206-1122 AT 1359HRS OFF ABOUT 20 MIN./BACK ON AT 1410HRS RELEASED BY CREW 078S03 VER/KEP IDCC CNT395 XXXX
4695 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-09-08 17:51 | 2018-09-09 18:18 | 39 | 1467 | 4059781 | 4289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAD UG XFR 1103-367,ISOLATED IT@1103-356.CLOSED UG FUSE IN@01:15////////ELBOW OR XFR IS BAD,LOT OF SMOKE AROUND WHERE ELBOW PLUGS IN Released by crew 074S06 DONT HAVE GROUND PARK FOR PADMOUNT WILL OPEN LINE FUSE AT POLE#1103-303 WILL NOTIFY CUST AND KEEP TIME- OFF AT 16:52 ON AT 18:18
4696 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-01-29 08:41 | 2018-01-29 17:45 | 8 | 544 | 4780791 | 4289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole37830244000014,//MADE MD TO SHOW TRANS ON THIS POLE//burnt top of pole off.35c5 pole,7200 kv,dead end complee,cutout complete, guy,all manual,4 man line crew,may be able to relocate to make truck accessible, Released by crew 077S04//CLOSED 244-11 1736/CLOSED 244-14 AT 1745bad cutout on pole37830244000014,burnt top of pole off.35c5 pole,7200 kv,dead end complee,cutout complete, guy,all manual,4 man line crew,may be able to relocate to make truck accessible, Released by crew 07
4697 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-05-27 17:20 | 2009-05-27 21:48 | 16 | 268 | 57122-1 | 4288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD- 15 ISO 38830857000148 CUSTOMER SAID POWER WENT OFF DURING LIGHTNING STRIKE. WILL TRY TO RE-FUSE. FUSE DID NOT HOLD. PATROLLING. BAD CSP XFMR ON POLE 857-226. ISOLATED XFMR AND CLOSED LINE FUSE RESTORING ALL BUT ONE CUSTOMER AT 21:02. CHANGED XFMR AND RESTORED LAST CUSTOMER AT 21:48. SH L3/HFP
4698 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-05-10 22:41 | 2013-05-13 13:45 | 5 | 3784 | 4100961 | 4280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQ, PRIMARY DOWN AT POLE 38830376000074 AND ISOLATED AT SAME, #4 ALUM NO TRUCK, CAN NOT GET MY TRUCK DOWN ROAD, EXTREMELY FOGGY, NEEDS TO BE PATROLED AND REPAIRED IN DAYLIGHT, NO ONE LIVES AT THIS LOCATION, CLOSED FUSE AT 00:45, RELEASED BY CREW 078S05 RELEASED BY CREW 078H05 2 SPANS #2 AL PRI. 1SPAN #2 NUT. DOWN. NO TRUCKS COMP @ RESTORED 13:45 MP RELEASED BY CREW 078H12 ///VER/CRB L/3 CRB IDC CHANGED CAUSE FROM UNKNOWN XXXX
4699 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-07-06 17:24 | 2022-07-07 03:52 | 20 | 628 | 4405301 | 4280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | line fuse on pole 1123d7022 back in at 18;40 leaving tranformer open on pole39831123D37094 (sse 4411701) will be line and tree crew required to get line back up no trucks Released by crew 078S09 03:30 FETR LRM bad 25KVA newfetr5:30 LRM//closed fuse @ 1840 and restored 9 cc//11 remain out on order 4411701//
4700 | South Williamson | 3411401 | DEWEY | INEZ | 2014-12-23 20:59 | 2014-12-24 00:05 | 23 | 186 | 4878041 | 4278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE 23 COD CUTOUT OPEN ON POLE 768-109 ORIGINALLY/ SERVICER OPENING C PHASE ADDING 195 COD TO SAFELY RESTORE POWER//SQUIRT BOMM WOULD NOT REACH///RYAN NEWSOME BRINGING BIG BUCKET TO CHANGE CUTOUT//WILL STILL HAVE TO OPEN OTHER PHASE//WILL KEEP UP WITH TIMES//REPAIRS MADE///RESTORED ALL CUSTOMERS AT00:05// *****DUPLICATE ORDER FOR ADDITIONAL 195 CUSTOMERS FROM 2344 TILL 0005****** VER/SEF AJB
4701 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2020-02-04 07:39 | 2020-02-04 12:12 | 16 | 273 | 4359581 | 4278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REST 3 CUST @ 1142 (13 REMAING OUT) // closed solid blade @ 1212
4702 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-02-28 12:01 | 2011-02-28 17:30 | 13 | 329 | 64516-1 | 4277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQD. LINE FUSE OPEN AT POLE 38830044D47505 THREE SPANS DOWN ON POLE 38830044D47509 PRIMARY PULLED OUT OF GRIP AND IS ON THE NEUT. TRUCK TO POLE RELEASED BY CREW 078E04/COMPLETE-PLS CLOSE//VER/CRB IDCC CCWU XXXX
4703 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-09-06 07:26 | 2012-09-06 17:37 | 7 | 611 | 4022981 | 4277 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNED INTO ON A BUCKARM , HENDRIX CABLE . WILL REQUIRE AN OUTAGE FROM POLE # 38831083C20868 , SETTING UP SCHEDULED OUTAGE FOR THIS EVENING . RELEASED BY CREW 077H03LOOP BURNED INTO ON A BUCKARM , HENDRIX CABLE . WILL REQUIRE AN OUTAGE FROM POLE # 38831083C20868 , SETTING UP SCHEDULED OUTAGE FOR THIS EVENING . REPAIRS MADE AND CLOSED GOAB SWITCH AT 1737 RESTORING POWER . SEE 4024941 FOR LARGER OUTAGE COD-7 ISO PO @ 38831083C20304 VER/HFP L3/HFP IDC XXXX
4704 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2017-05-27 17:27 | 2017-05-27 22:56 | 13 | 329 | 4870911 | 4277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINE FUSE BLOWN ON 728-28..30 T FUSE..NEED 2 MEN AND UG FAULT LOCATOR..U/G PRIMARY BAD ON 928-28..SPLICING../ ISO 38830728000028/ COD 13(BEST GUESS CUSTOMER COUNT PER SERVICER MAPS ARE WRONG)/ VER/BOW
4705 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-08-07 09:36 | 2014-08-07 14:20 | 35 | 284 | 4339181 | 4276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE /// PATROLLING/// COD 35 CCC******// PLACED OPEN POINT ON POLE 37820265A00224 TO ISOLATE FAULT ON POLE 37820265A00351/// PLACING TAGS FOR DDC///C PHASE/// PATROLLING/// COD 35 CCC // PLACED OPEN POINT ON POLE 37820265A00224 TO ISOLATE FAULT ON POLE 37820265A00351/// PLACING TAGS FOR DDC/// CREW ENROUTE RELEASED BY CREW 074S02C PHASE/// PATROLLING/// COD 35 CCC // PLACED OPEN POINT ON POLE 37820265A00224 TO ISOLATE FAULT ON POLE 37820265A00351/// AJB PH C.
4706 | Hazard | 3309302 | VICCO | JEFF | 2021-02-27 10:00 | 2021-02-27 11:35 | 45 | 95 | 4261211 | 4275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A phase line fuse open (37 COD) upon arrivalbad insulator on pole 323-109. replaced and restored power at 11:35
4707 | Pikeville | 3407103 | TOPMOST | KITE | 2014-08-20 14:25 | 2014-08-20 17:39 | 22 | 194 | 4390661 | 4268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON 37830233000087/// REPAIRED AND TRYING LINE FUSE ON 37830233B40149// CLEARED TRANSFORMER ARRESTER AT POLE 233-87 AND REFUSED LINE CUTOUT , ALL WORK COMPLETE / GXJ// VER/BOW AJB
4708 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-11-12 17:06 | 2013-11-12 23:01 | 12 | 355 | 4033201 | 4260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TECH/NEED --INSTALEED GROUND ON POLE 38830091C00647--NEED CREW TRUCK TO POLES RELEASED BY CREW 078S07/CREW LOADING MATERIAL/FOREMAN ON SITE/FETR 2330/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2301/NO AS BUILT TECH WROTE JOB/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L3/HFP IDC XXXX
4709 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-06-19 15:20 | 2011-06-19 15:40 | 213 | 20 | 4345291 | 4260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4344621 WHEN LINE FUSE CLOSED IN ON THAT ORDER CUTOUT EXPLODED ALL RESTORED @ 1540 COD-215 ISO LF 38830188B09001 VER/HFP L3/HFP IDC XXXX
4710 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-07-20 07:11 | 2014-07-20 09:43 | 28 | 152 | 4265341 | 4256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHECKING NOW.FOUND CUTOUT BROKE ON 850-22 MIDDLE PHASEGOING TO OPEN @ 850-9 MIDDLE 600AMP SWITCH.. OPENED @9:18 (SEE 4265521) CLOSED BACK IN @9:43//COD 28// VER/DBM AJB
4711 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2011-10-12 02:14 | 2011-10-12 02:46 | 133 | 32 | 4967561 | 4256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 420-2, OPENED RECLOSERS ON 419-366 AT 02:14 REPLACED CUTOUT RESTORED POWER AT 02:46 VER/ARN IDC XXXX
4712 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-03-10 05:41 | 2011-03-10 09:25 | 19 | 224 | 52663-1 | 4256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830223B00252 TOOK CUTOUT OFF LINE PUT MAIN LINE BACK ON ATBAD CUTOUT ON POLE 37830223B00252 TOOK CUTOUT OFF LINE == CHANGED CUTOUT == PUT LINE BACK ON == POWER OK VER/SDB IDC DCMT XXXX
4713 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2019-02-07 20:12 | 2019-02-07 23:17 | 23 | 185 | 4765891 | 4255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 180-144 replaced xfr cutout ,,only 1 customer ,,complete
4714 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-08-12 14:15 | 2017-08-12 21:04 | 11 | 409 | 4253611 | 4251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE 472-44 BACK IN @ 20:33 UP TO SOLID BLADE @ 472-56,,,SOLID BLADE 472-56 BACK IN @ 21:04,,,FOUND BAD LIGHTNING ARRESTOR @ 472-68 ALL CUTOMERS RESTORED COMPLETE RELEASED BY CREW 078S05//COD 11// VER/DBM SJG
4715 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2010-01-20 23:45 | 2010-01-21 05:00 | 30 | 315 | 57046-1 | 4250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BURNT TOP OF POLE OFF. ISOLATED ON 785-1115 AND CLOSED FUSE @ 01:40 LEAVING TWO XFMRS OFF. CREW ENROUTE. CREW ON SITE - REPAIR IN PROGRESS. REPAIRS COMPLETE. RESTORED LAST TWO XFMRS @ 05:00. SH RELEASED BY CREW 076S02 VER/LDA IDC XXXX
4716 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2020-10-24 16:51 | 2020-10-24 20:47 | 18 | 236 | 4581621 | 4248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @38820989A00139 (18 CC), checking. Cutout went bad @ 38820989B00300 burning top of the pole off, will be making repairs. Got poletop ext. installed and c/o changed,closed L/F back in @2047.
4717 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-01-20 08:04 | 2012-01-20 10:21 | 31 | 137 | 4277151 | 4247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED REPAIRING LOOP ///VER/CRB IDC XXXX
4718 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-03-28 18:38 | 2020-03-28 21:43 | 45 | 185 | 4520401 | 4243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Loop open on 128.31/opened GOAB on 128-23 to make repairs @2315/Pole 128/31 loop brunt into on A phase open GOAB at 21:15 closed at 21:43
4719 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2016-02-10 17:06 | 2016-02-10 20:28 | 21 | 202 | 4688031 | 4242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRUP AND HOTLINE CLAMP FELL.. VER/CRB L3/HFP XXXHFP AJB
4720 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-06-09 18:50 | 2017-06-09 20:31 | 42 | 101 | 4927801 | 4242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OPENED OCR37830256000017 TO SAFELEY REPLACE POLE ON ORDER 4926771//FAULT POLE 37830280000091//OUTAGE 1850 TO 2031 VER/CRB SJG CCO, FEC57 (ROTTEN POLE PER 4926771)
4721 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-06-26 19:15 | 2010-06-27 00:18 | 14 | 303 | 57909-1 | 4242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 35745931 / 37830223B00017 LINE FUSE OPEN === WIRE DOWN OFF POLE 37830223B00042 == NEED 3 MEN AND ROW CREW37830223B00042 == UP ON HILLSIDE ==37830223B00042 == RELEASED BY CREW 077S03WR# 35745931 / 37830223B00017 LINE FUSE OPEN ==== REPAIRED LINE == REFUSED B== POWER OK VER/LDA IDC XXXX AJBC FEC57
4722 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-07-16 08:40 | 2013-07-16 10:21 | 42 | 101 | 4528451 | 4242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNT OFF, ROLL UP INTO BIGGER OUTAGESTIRRUP BURNT INTO ON 388-08, REPLACED STIRRUP.ALL POWER RESTORED @10:21HRS P.HICKS VER/CRB L/3 CRB IDC XXXX
4723 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-05-11 14:07 | 2015-05-12 03:50 | 13 | 823 | 4411501 | 4242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | SCADA INDICATES DA RECLOSER LOCKOUT @ 1407// BAD TRANS 115-470 SEND TO VERNON M. //CREW ON SITE/SWITCHING OUT BAD XFMR/FETR1800/VEM/XFMR 115-470 STILL OFF/ALL OTHER CUST RESTORED 1803/VEM RELEASED BY CREW 078H14 VER/SEF L3/DKGXXX AJB
4724 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2020-12-25 17:43 | 2020-12-26 07:51 | 5 | 848 | 4819001 | 4240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate burndt up @ 1113-B-195, got gate replaced and power restored @0751.
4725 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-09-11 23:25 | 2009-09-12 03:20 | 18 | 235 | 51783-1 | 4230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FUSE OUT ON POLE 38830020D16048 ON PRIMARY UG=CALLEXD P TOLLIVER--CABLE BETWEEN PAD 38830020D16050 AND 38830020D16053 IS BAD-ISOLATED AND TAGGED TO DDC //VER/GAH IDCC PN6050, CNT9 XXXX
4726 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-12-22 06:32 | 2012-12-22 10:30 | 20 | 238 | 4505291 | 4228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER DISPATCHED. CUTOUT ON POLE 50-129 BROKE DOWN AND BURNED TOP OF POLE OFF. I OPENED LINE FUSE ON 49-21 AT 06:32 TO ISOLATE FAULT. CREWS ARE ON THE WAY.//MADE MDCSERVICER DISPATCHED. CUTOUT ON POLE 50-129 BROKE DOWN AND BURNED TOP OF POLE OFF. I OPENED LINE FUSE ON 49-21 AT 06:32 TO ISOLATE FAULT. CREWS ARE ON THE WAY. WE CLOSED LINE FUSE IN AT 10:02. THIS JUST LEFT 1 TRANS. OFF ON POLE 50-129. WE CLOSED IT IN AT 10:30. RELEASED BY CREW 074S01 ////VER/CRB L/3 CRB
4727 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-12-19 13:18 | 2008-12-19 18:20 | 14 | 302 | 60362-1 | 4228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP LINE FUSE BLOWN----37830120A00084--CUT L/A IN CLEAR ON A CSP, RETRIED LINE FUSE CAME BACK OUT. CALLED DUTY SUP. FOR SOME HELP L3/HFP IDC XXXX
4728 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-08-22 19:46 | 2014-08-23 13:23 | 4 | 1057 | 4407221 | 4228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SOMEONE WITH TIME WARNER CABLE CALLED TO REPORT A POWER OUTAGE// POLE 69-5535 BAD 10KVA// NEED 15 OR 25// TRUCK OK FLAGGERS// RELEASED BY CREW 078S08// CHANGING TO 15 KVA NEW PP 14A061883 OLD CP 92NC100013// VER/BOW
4729 | Hazard | 3303902 | LESLIE | WOOTON | 2016-06-24 14:01 | 2016-06-25 13:30 | 3 | 1409 | 4462891 | 4227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BAD,WILL NEED LINE CREW,,8 X-ARM,,LCO (7.2 KV),HLC,,X-ARM BRKT,,WILL TAKE OUTAGE TO MAIN LINE (MANUAL).RGP. RELEASED BY CREW 077E09 REPLACED POLE
4730 | Hazard | 3302704 | HAZARD | KENMONT | 2022-01-06 21:52 | 2022-01-07 09:36 | 6 | 704 | 4317211 | 4224 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE, MADE REPAIRS
4731 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-24 12:50 | 2018-11-24 17:58 | 36 | 308 | 4473511 | 4224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40/5 pole crew required/no trucks yard dog behind house tractor wont start might cutoff but wont give clearence/221b129/isolated at 221-85 no grounds/fuse in at 1430 hrs Released by crew 078S03/ARRIVED RM/repairs made/ line energized on 221-85 @ 1758/ all customers restored/ please close ticket/ RM L3/HFP
4732 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2017-10-08 18:25 | 2017-10-09 12:00 | 4 | 1055 | 4423301 | 4220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA XFMR 7200, 120/ 240 BANK , CAN USE TRUCK MAY HAVE TO PAD TRUCK IN .. RELEASED BY CREW 077S11 POWER RESTORED AT 12:00 VER/AWD L3/HFP XXXHFP
4733 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2020-03-18 18:33 | 2020-03-19 11:55 | 15 | 1042 | 4489701 | 4218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser open @1152-B2-211, checking. No fault indicators are tripped, Paul Layne coming to help test cable to find the bad spot. Found a fault incator tripped going from Feed through 1152-214 to trans. 1152-218, isolated that span and closed L/F @1152-B2-211 @2113.Bad Urd between pad 1152-218 and 220, got 218 back on @2140, Paul Layne coming back in am for repairs. Released by crew 074S05/all repairs made restore at 11:55 Released by crew 074H07
4734 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-03-27 20:38 | 2012-03-27 22:32 | 37 | 114 | 4623471 | 4218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE SOLID DISCONNECT FAILED (43 CUSTOMERS), OPENED OCRS ON POLE 38831074D00092 AT 22:20 AND CLOSED AT 22:32 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 ISO PO @ 38831074C00490 VER/HFP L3/HFP IDC CHANGED COUNT FROM 43 XXXX IDC XXXX
4735 | Hazard | 3303902 | LESLIE | WOOTON | 2008-06-02 18:48 | 2008-06-02 22:30 | 19 | 222 | 54673-1 | 4218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLED LINE .LOOKS OK.CLOSED FUSE AND FUSE CAME BACK OUT.CUST SPOTTED FLASH ON XFRM POLE.//3303902//VER/CRB
4736 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-03-01 18:20 | 2018-03-02 17:45 | 3 | 1405 | 4895031 | 4215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 19.9 cutout on pole 38830573000027. Crew reqd. may try to get big bucket to pole but probably to wet. Elliott track machine would be best. Released by crew 078H17
4737 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-12-10 08:59 | 2016-12-10 14:00 | 14 | 301 | 4182301 | 4214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 167 KVA XFMR, 19.9 KV, ONE PRIMARY BUSHING, 4 SECONDARY BUSHINGS WITH PADDLES, 120/240 VOLTAGE. 120/208 3 PHASE VOLTAGE VER/CRB L3/HFP XXXHFP
4738 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-09-01 13:23 | 2009-09-01 19:46 | 11 | 383 | 59380-1 | 4213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE TOP ON POLE 238-117 , NO TRUCKS TO POLE , NEEDS LINE CREW AND TREE CREW. //COD 11// VER/DBM IDC XXXX
4739 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2017-07-07 15:18 | 2017-07-07 16:39 | 52 | 81 | 4089061 | 4212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830190000066 BROKE C/O--15T LAT--38830214000052 REC IN AT 16:39--ALLGOOD-DS070717 VER/CRB SJG
4740 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2020-11-30 13:55 | 2020-11-30 18:18 | 16 | 263 | 4731811 | 4208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse out @ 37830139A10047.Will be patrolling. Cutout broke down @ 37830139A20419 burning top of pole off. Repairs made and restored @ 18:18
4741 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2022-05-07 06:51 | 2022-05-07 13:48 | 11 | 417 | 4857261 | 4207 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LF open on pole 1108-42// checking// bad dead end ins. on 1109-B-24, installed a switch on pole 1109-B-23, switch is open to isolate trouble, will restore all customers but 1// fuse did not hold// LF on 1108-42 res. @ 13:05// switch on 1109-B-23 res @ 13:48, we put a 20T in the fuse Released by crew 074S09//MD MADE
4742 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-07-14 11:38 | 2012-07-14 18:00 | 11 | 382 | 4722511 | 4202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 074S03. DEAD END INSULATOR IS BAD ON POLE 1149-161. IT BLEW LINE FUSE ON POLE 1149-161. PAUL LAYNE IS BRINGING INSULATOR. WE CHANGED 3 INSULATORS AND CLOSED LINE FUSE IN AT 18:00//COD 11 IDC XXXX
4743 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-03-23 05:34 | 2016-03-23 08:45 | 22 | 191 | 4872481 | 4202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 116-127 BAD 19.9 LA ALSO REPLACED OLD 12KV LA VER/HFP L3/HFP IDC XXXX AJB
4744 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-08-31 09:00 | 2014-08-31 19:00 | 7 | 600 | 4440361 | 4200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-7569 6T TRANS FUSE BROKEPOLE 45-7569 BAD 25KVA TRANS TRUCK TO POLEPOLE 45-7569 BAD 25KVA TRANS TRUCK TO POLE RELEASED BY CREW 078S08///REPLACED 25KVA---VOLT CK GOOD---TBL TKT COMP//COD 7// VER/DBM AJB
4745 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2013-11-08 08:04 | 2013-11-08 09:28 | 50 | 84 | 4021141 | 4200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON CSP TRANS. ON POLE 37820172000099//COD 50//AED CREATED// VER/DBM L3/HFP IDC XXXX
4746 | South Williamson | 3411401 | DEWEY | INEZ | 2011-04-13 11:20 | 2011-04-13 11:45 | 168 | 25 | 56296-1 | 4200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW FOUND UNSAFE CONDITION WHILE DOING ROUTINE WORK OPENED FUSE#672-134(MD FILED NOT ON MAP) TO ISOLATE AND REPAIR ALSO ADDED 21 CUSTOMERS FROM 647-3 N.O. SWITCH SHOWN INCORRECTLY(MD FILED) VER/KEP AJB
4747 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2021-01-14 17:02 | 2021-01-14 19:02 | 35 | 120 | 4868861 | 4200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 38830045A31030, 454 windstream pole, rotted off @ base. Released by crew 078S02///Vernon Mullins states we will replace pole this eve/on site RM open LFon pole 45-A1030@17:02 closed @ 19:02 Released by crew 078H20// NO OUTAGE TILL 1702
4748 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2009-12-12 23:25 | 2009-12-13 03:30 | 39 | 245 | 65949-1 | 4197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT ON POLE 48-43 - SEVICER PATOLLLING.LINE FUSE 48-43 WAS OUT,FOUND BAD XFR,TOOK IT OFF-LINE,CLOSED FUSE IN AND RESTORED TO ALL BUT THE OFF-LINE XFR.CREW COMING TO CHANGE XFR MCCOY AND GARRETT.
4749 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-02-17 17:13 | 2008-02-17 21:06 | 18 | 233 | 64305-1 | 4194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308001// POLE 1083-210 TOP BURNT OFF AND FELL OVER INTO JACKSON ELEMENTRY SCHOOL. NEED 4 MAN CREW BIG BUCKET & LINE TRUCK. JIM MULLINS SAID LOOK LIKE EQUIPENT OK AND COULD TRANSFER BACK. WILL BE ABLE TO PUT EVERY THING BACK AND NOT CHANGE POLE RESTORED POWER AT 2106 P HICKMAN AND CREW IDC XXXX
4750 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-03-15 05:34 | 2009-03-15 13:20 | 9 | 466 | 58697-1 | 4194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BROKE ON POLE 835-8 GOING TO SEE IF CAN REACH WITH TRUCK .T GOBLECHANGED LINE FUSE WHEN CLOSED IT COME BACK OPEN THE FAULT MUST BROKE CUT OUT CHECKING LINE NOW. HAVE POLE 835-10 BURNT OFF CALLING CREW //VER/GAH IDC XXXX
4751 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2020-03-25 22:12 | 2020-03-26 11:00 | 6 | 768 | 4511011 | 4193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad xfm crew needed. ¦¦ WILL NEED TO OPEN TAP TO REPLACE XFMR SAFELY (5 CUST) ¦¦ TAP OFF @0922 ALL ON @0937-- closed new xfmr at 11:00, on pole 188-113 Released by crew 074H07 // cod 1 XFMR//
4752 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-12-14 11:21 | 2015-12-14 15:43 | 16 | 262 | 4530481 | 4192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 69-7179.NO TRUCK/NEED LINE CREW/CREW ON SITE/VEM RELEASED BY CREW 078H14BROKE CUTOUT ON POLE 69-7179.NO TRUCK/NEED LINE CREW/CREW ON SITE/VEM/OPEN SOLID BLADE 69-7050@1449/FAULT POLE IN DIFFICULT LOCATION/FETR 1630/VEM // SEE ALSO 4531481 //BROKE CUTOUT ON POLE 69-7179.NO TRUCK/NEED LINE CREW/CREW ON SITE/VEM/OPEN SOLID BLADE 69-7050@1449/FAULT POLE IN DIFFICULT LOCATION/FETR 1630/VEM/REPAIRS MADE AND ALL CUST RESTORED @1543/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH
4753 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-03-31 12:36 | 2015-03-31 18:25 | 12 | 349 | 4247321 | 4188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RIGHT HAND PHASE FUSE BLOWN (A PHASE 14 CUST) ON POLE 794-246///AT POLE 794 -98 PHASE OUT OF SAG DOWN BELOW NEUTRAL BEEN BLOWING INTO NEUTRAL WHEN WIND BLOWS//CREW ENROUTE//NO TRUCK//WILL HAVE TO OPEN OTHER TWO PHASES WHEN CREW ARRIVES TO REPAIR//OPENED OTHER 2 PHASES AT 17:15//REPAIRS MADE//RESTORED AT 18:25//COMPLETE//EM COD-37 TOTAL SEE H4247321 FOR B & C PHASE OUTAGE VER/HFP L3/HFP
4754 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2021-07-28 16:16 | 2021-07-28 22:05 | 12 | 349 | 4972751 | 4188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50kva truck ok/crew reqd. tre Released by crew 078S04bad 50kva truck ok/crew reqd. tre Released by crew crew on site FEtr 22:15bad 50kva truck ok/crew reqd. tre Released by crew crew on site FEtr 22:15 all pwr restored 22:05 pleaseclose LRM//cod 12
4755 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-01-14 15:44 | 2018-01-14 17:25 | 52 | 101 | 4746991 | 4188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE CUTOUT FAILED ON POLE 38820723A00237//COD 38//MADE MD TO SHOW THE L/F HERE ARE SOLID BLADES//WILL HAVE TO OPEN A & B PHASES TO MAKE REPAIRS COD 14 MORE CUSTS//300 amp cutout failed on pole middle phase at pole 723-237///i opened othe two phases at 17:00 to make repairs//repairs made//restored at 17;25//complete//em. Changed Time off to match first trouble call
4756 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-09-03 01:43 | 2019-09-03 05:27 | 22 | 224 | 4973911 | 4186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | recloser open on pole 328-867, wire burnt into at pole 328-130 one span primary down #2 all.opened line fuse on pole 328-55 to isolate, closed recloser in at 03:41..made repairs restored power at 05:27. //cod 22 ¦¦¦ FAULT WENT THRU 65T FUSE ON POLE 37830328C00055 TAKING OUT RECLOSER ¦¦ L3//HFP
4757 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-03-11 12:52 | 2008-03-11 13:30 | 110 | 38 | 56218-1 | 4180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116703///RELATED TO ORDER 56181-1 // CREW NEEDED TO OPEN RECLOSER TO MAKE REPAIRS TO CONDUCTOR WHERE LOOP BURNT OPEN VER/HFP IDC XXXX
4758 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2012-06-17 15:52 | 2012-06-17 16:02 | 418 | 10 | 4923321 | 4180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED STATION BREAKER TO OPEN SWS AT POLE 272-2 ON ORDER 4922341 //VER/GAH IDC XXXX
4759 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2008-12-14 13:30 | 2008-12-14 16:49 | 21 | 199 | H58185-1 | 4179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003702// 138-229 40/5 BURNT OFF // ONLY CUSTOMERS OUT ARE ON POLE 138-229 AND THE FUSE OFF OF POLE 229 (NOT ON MAP, 15T FEEDS TOWARDS POLE 230)//COD 5//CREW ON SITE/LINE FUSE ON POLE#138-196 OPEN AT 1330 TO MAKE REPAIRS, THIS TOOK OUT 20 MORE CUST///FETR1830/POLE CHANGED AND POWER RESTORED AT 1649/NEED TO SEND NOTE TO MAPPING/15T ON POLE 138-229//SENT REPORT TO MAPPING DBM VER/KEP L3/KEP IDC XXXX
4760 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-05-11 19:29 | 2019-05-12 18:40 | 3 | 1391 | 4254361 | 4173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout is bad you need two men and a cutout, probley manual Released by crew 077S12
4761 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-01-12 05:32 | 2020-01-12 22:55 | 4 | 1043 | 4279171 | 4172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | transformer pole 205d/241 rotted off and fell with 25 kva transformer, will need line crew Released by crew 077F05, need 454 pole pri. de 25 kva, anc & guy (78 ) ins. 3 # conduits standoff bkts for conduit clevis cutout bkt and cutout (19.9) kva will need flagging..lc Released by crew 077E07
4762 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-05-12 14:49 | 2011-05-12 23:30 | 8 | 521 | 4075451 | 4168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-5137 TRANS. BANK OVERLOADED 2- FUSES MELTED OUT CHGED TRANS.BANK REMOVED 2-25KVA 1-75KVA INSTALLED 1-100KVA 2-50KVA ALSO CHGED OLD CUTOUTS AND LA// VER/DBM
4763 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-02-20 03:07 | 2019-02-20 09:54 | 17 | 407 | 4808881 | 4168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MD//TRANS 38830188B02003 & 38830188B02002 ARE ON B PHASE //COD 5 //// crew required bad 19.9 cutout bring 2 and big bucket send to RM Released by crew 078H06//COD 7 FROM OUTAGE /arrived R //arrived RM open line fuse@09:40 closed both uses@09::54 replaced both cutouts please close tic RM/// trouble tickets show A phase was out from start/// Phasing was shown incorrect. Going off of what comments said, and removed RL4
4764 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2022-08-16 13:06 | 2022-08-16 13:55 | 85 | 49 | 4747121 | 4165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | will need braces talked to rick ray he is going to fix it in the morning. OPENED OCR TO MAKE REPAIRS ( COD 84) NO OUTAGE TILL THEN OPENED @ CLOSED @will need braces talked to rick ray he is going to fix it in the morning.. Released by crew 079S02// had to replace crossarm also///opened @ 13:06//closed @ 13:55
4765 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-01-09 09:37 | 2018-01-09 10:34 | 73 | 57 | 90007111 | 4161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B phase recloser out (73 CUST) , patrolling line. crossarm braces broke letting arms get into top of cutout, pole # 154-6 T. Smith to look at first thing in morning // O937 OPENED A & C PHASE RECLS (73 CUST) CLOSED A & C @ 1035 73 CUST// HAVING PROBLEMS PICKING UP ALL CUST DUE TO COLD LOAD PICKUP//1218 ALL CUST REST FROM RECL 129-42 // NOTE THIS IS FOR THE A & C PHASE OUTAGE
4766 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-07-24 11:59 | 2017-07-24 12:09 | 416 | 10 | 4172731 | 4160 | TRANSMISSION STATION | EQUIPMENT FAILURE | CAPACITOR | DOL 759516//SDB / 1159-1209 / EMERGENCY 138KV BUS 1 OUTAGE TO SAFELY REMOVE 138KV CAP BANK FROM SERVICE. 416 CC// VER/DBM. L3/HFP XXXHFP SJG
4767 | Paintsville | 3401101 | FALCON | FALC-OILS | 2013-07-16 01:23 | 2013-07-16 04:03 | 26 | 160 | 4527781 | 4160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE. FUSE DOOR ON OLD CUTOUT IS BURNT UP. PATROLLED LINE AND FOUND NO OBVIOUS PROBLEMS. CHANGING LINE FUSE CUTOUT. CUTOUT CHANGED AND REFUSED @ 4:03. SH IDC CHANGED TIME OFF FROM 0057 PER CUSTOMER COMMENTS XXXX
4768 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-06-03 13:00 | 2009-06-03 14:44 | 40 | 104 | 66643-1 | 4160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WRONG -LINE FUSE PREDICTED--40T FUSE OUT ON POLE 39831123D26551--TRANSFORMER ON THAT POLE UNDER THAT FUSE--E MAIL TO RAYBURN--BAD ARRESTOR NEEDS REPLACED-AT END OF NAIPER ST-BIG BUCKET OK WHEN DRY IDCC PN6542 CNT71 XXXX
4769 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-01-24 02:36 | 2019-01-24 12:30 | 7 | 594 | 4714251 | 4158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines. pole 38830452000136 NBT with need fourwheeler tagged pole 452-121 to rick morgan Released by crew 078H01/arrived RM fuse in @ 12:30 please close tic RM
4770 | Whitesburg | 3401301 | FLEMING | NEON | 2010-12-25 23:41 | 2010-12-26 01:20 | 42 | 99 | 55730-1 | 4158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP CAME OFF MAIN LINE .. SERV. MAKING REPAIRS. ON 37 CC B PHASE ONLY.HOT LINE CLAMP ON POLE NO.355-40 CAME OFF FEEDING RECLOSER ONPOLE NO.355-41 VER/PDP IDCC CNT37 XXXX
4771 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-12-31 04:56 | 2010-12-31 12:38 | 9 | 462 | 57245-1 | 4158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | ANCHOR PULLED OUT OF GROUND ON HILLSIDE POLE 199-32. FUSE BLOWN POLE 199-188 IS 40T, MAP DISCREPANCY CREATED. ANCHOR PULLED OUT OF GROUND ON HILLSIDE POLE 199-32/SEND TO LINKOUS CREW REQUIRED RELEASED BY CREW 078S03. ALL POWER RESTORED AT 12:38 I THINK POLE LABELED WRONG IN FIELD..HFP COD-9 ISO LF 38830199000183 VER/HFP L3/HFP IDC XXXX
4772 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-02-26 12:58 | 2008-02-26 14:05 | 62 | 67 | 50527-1 | 4154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3116702// B-PHASE HOT BURNT OFF AT RECLOSER// K BROWN 3328 ASSISTING/ REPLACED BAD HOTTAP VER/HFP IDCC CNT208 XXXX
4773 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-03-10 19:04 | 2021-03-11 00:05 | 47 | 301 | 4324421 | 4151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire at 182-3614,,lifted hot tap @ 182-2592,,line fuse 182-3535 restored @ 20:07,leaving off 1 xfr,,crew required ,,wooden pole top ,cutout and bracket needed //crew on site FETR 01:00 LRM all pwr restored 00:05//cod 47
4774 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-02-06 16:57 | 2019-02-06 18:05 | 61 | 68 | 4760001 | 4148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Burnt up cutout on 38830092C00577 Tree fell and brushed line at 92-578. Cutout changed, reclosure back in at 18:05 L3/HFP
4775 | Pikeville | 3120102 | STANVILLE | TRAM | 2021-05-10 07:07 | 2021-05-10 15:45 | 8 | 518 | 4568441 | 4144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | all 3 UG riser fuses out on pole 38831077D00434 no hazards found will try fuse// fuse came back out// crew requred with 1/0 UG Released by crew 074S09/bad 3 phase UG cable/power restored at 15:45
4776 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-06-19 13:20 | 2020-06-19 16:58 | 19 | 218 | 4046631 | 4142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad cutout on pole 38831124D00044, made repairs and restored line at 1658
4777 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2012-01-04 07:49 | 2012-01-04 10:07 | 30 | 138 | 4231671 | 4140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED OPENING IN LINE HOT TAP AT 280-87/NO.4 COPPER TRUCKS OK JUST PRIMARY RELEASED BY CREW 078S03 OPENED REC AT 1004 CLOSED AT 1007 TO MAKE UP LOOP VER/KEP IDC XXXX
4778 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-10-30 00:05 | 2011-10-30 00:25 | 207 | 20 | 4036361 | 4140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN RECLOSER TO REPAIR BURNT LOOP AT POLE 378-10// RECLOSER OPENED AT 1200 AND CLOSED AT 1225 // ASSOCIATED WITH ORDER 4036221 IDCC TON0032 XXXX
4779 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2016-10-20 22:56 | 2016-10-21 11:27 | 23 | 751 | 4034701 | 4139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PH ONLY COD-23/TRANS CUTOUT FAILED ON 1145C67 BURNING UP 1 SET OF 8 FT CROSSARMS AND TAKING OUT FUSE ON 1145C20 CREW REQUIRED 2 MEN AND FOREMAN NEED TWO 8 FT CROSSARMS BRACES 7200 CUTOUT AND ARRESTOR ARM BRACKET TRK APPROACH WILL HAVE TO OPEN UP OTHER PHASE TO MAKE REPAIRS I ISOLATED TRANS CUTOUT ON 1145C67 AND RESTORED POWER ON 1145C20 AT 01:30 // OPENED FUSE AGAIN @ 1009 ON @ 1127 SEE H4034701 VER/HFP L3/HFP AJB
4780 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-06-07 17:47 | 2009-06-07 21:04 | 21 | 197 | 53260-1 | 4137 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP WR # 30169824 // COD-21 ISO 38831059D00021 L3/HFP IDC XXXX
4781 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-04-03 05:07 | 2009-04-03 07:46 | 26 | 159 | H64363-1 | 4134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 64363-1//DUTY SUP ASSISTING IN TRYING TO FIND PROBLEM. FOUND BAD XFMR CUTOUT. REPLACING. REPAIRS CP. CL PH B REC ON POLE 53 AT 07:46 RESTORING UP TO REC 832-33 (26 CUST) (WE OP WHILE TROUBLE-SHOOTING LINE). CL POLE 33 REC AT 07:52 RESTORING REMAINING CUST. SH//ISO 38830833D00053// VER/DBM AJB INT OUTAGE ON OCR 832/33 W/120 CUST, @5:07 OP B PH OCR 833D/53 W/26 CUST. @7:46 CL 833D/53 REST 26 CUST, @7:52 CL 832/33 REST 120 CUST. SEE H64363-1 FOR 833D/53 OUTAGE, SEE 64363 FOR 832/33 OUTAGE.
4782 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-05-29 14:29 | 2010-05-29 15:50 | 51 | 81 | 53347-1 | 4131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER OPEN ON POLE 37820073D00589 WILL PATROL-----REMOVED BAD ARRESTER ON POLE 74-20 VER/KEP L3/KEP IDC XXXX
4783 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2018-05-08 11:31 | 2018-05-08 12:30 | 70 | 59 | 4324021 | 4130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | found blown l/a on pole 925-99, have cut in the clear, closed in rec on 925-24, at 1230 restoring power to all cust by amg/ ISO 39830925000024/ COD 70
4784 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-09-06 12:15 | 2016-09-06 22:15 | 7 | 600 | 4871621 | 4128 | TRANSMISSION LINE | EQUIPMENT FAILURE | CROSSARM | KY DDC TAGS AND GROUNDS IN PLACE AT 38830165B00211// T-LINE AND D-LINE WILL NEED TO TAKE HOLD ORDERS// WILL FINISH AT DIF TIMES// CROSS ARMS ON TRANSMISSION STRUCTURE FAILED// PROJECTED TIME OF RESTORATION 0200 - WILL UPDATE AS MORE INFORMATION BECOMES AVAILABLE GROUNDED AND TAGGED TO KY DDC AT POLE 165-B-211 ONE SPAN OF PRIMARY AND NEUTRAL DOWN FROM POLE 165-255 TO POLE 165-256 WILL HAVE TO WAIT UNTILL T-LINE MAKES REPAIRES TO WORK OUR LINESGROUNDED AND TAGGED TO KY DDC AT POLE 165-B-2/// VER/DKM AJB
4785 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-08-15 15:42 | 2009-08-15 16:30 | 86 | 48 | 58984-1 | 4128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP PATROLING LINE-BROKEN FUSE COD-86 LF 38830069C24518 PAUL SENT EMAIL TO GREG BELL ABOUT FUSES THAT ARE NOT ON MAP & ENTERED MD L3/HFP IDC XXXX
4786 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2012-11-02 13:45 | 2012-11-02 16:30 | 25 | 165 | 4338591 | 4125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE//LINE FUSE OUT ON POLE 1127-A-199,POSSIBLE TREE CONTACT WAS ACTUALLY DUE TO CUTOUT FAILING COD-25 ISO LF 38831127A00199 VER/HFP L3/HFP IDC XXXX
4787 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-07-21 02:07 | 2022-07-21 15:52 | 5 | 825 | 4533531 | 4125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke xfrm cutout on pole 448-441. Made repairs. Power restored at 15:52.//cod 5
4788 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-01-01 04:03 | 2022-01-01 06:48 | 25 | 165 | 4242801 | 4125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO broke on pole 1105-B-260, will be making repairs
4789 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-12-23 10:08 | 2019-12-23 13:15 | 23 | 187 | 4177581 | 4124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse cutout broke, stirrup is also broken. Will require linecrew to go hands on to replace Released by crew 078S11//arrived RM cutout replaced power on @ 13:15 please close tic RM Released by crew 078H20 Tap off @ 1303 on @ 1313
4790 | Hazard | 3309302 | VICCO | JEFF | 2022-12-23 16:52 | 2022-12-23 18:50 | 38 | 118 | 4329231 | 4124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STEPDOWN OPEN ON POLE 37830322B00310 (COD 38) GOING TO TRY AN ENERGY C PHASE in @ 1750 (cod 32 now)STEPDOWN OPEN ON POLE 37830322B00310 (COD 38) GOING TO TRY AN ENERGY C PHASE, closed A phase at 18:50 Released by crew 077S07
4791 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-02-04 09:38 | 2013-02-04 14:55 | 13 | 317 | 4789461 | 4121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 272-42 BASKET BURNT OFF TRYING TO REPAIR/PRIMARY BROKE ON 272-42 CLIMB ONE POLE CREW REQUIRED/NO.4 COPPER RELEASED BY CREW 078S03/CREW ON SITE/FETR1545/VEM/REPAIRS MADE AND ALL CUST RESTORED 1455/PLEASE CLOSE TICKET/THANKS/VEM//ISO // COD 13// VER/DBM IDC XXXX
4792 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-07-12 17:27 | 2017-07-12 23:41 | 11 | 374 | 4111731 | 4114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 1131-13 IS BROKEN OFF AT NUETRAL NTA NUETRAL IS DOWN PRIMARY IS STILL UP BUT IS CONTACTING POLE MAY BE ABLE TO INSTALL POLE TOP EXTENSION ON POLE AND GET PRIMARY UP CREW REQUIRED ROW CREW REQUIRED RELEASED BY CREW 079H03 TEMP REPAIRS MADE ON AT 23:41 D SAMMONS/ ISO 38821131000008/ COD 11/ VER/BOW SJGC FP 38821131000120
4793 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-03-20 11:28 | 2011-03-20 19:05 | 9 | 457 | 56051-1 | 4113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAD UNDERGROUND TRANSF == NEED LINE CREW RELEASED BY CREW 077S03 CHANGED XFMR AND RESTORED POWER AT 1905 CREW 077H01//COD 9// VER/DBM IDC XXXX
4794 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-08-09 13:28 | 2013-08-09 17:45 | 16 | 257 | 4640231 | 4112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DIP FUSE BLOWN ON 37830024B20666 // WILL DO SOME CHECKING// BAD CABLE FROM 24-666 TO 24-1081// CREW EN ROUTE// REPLACED CABLE// POWER IS RESTORED VER/CRB L/3 CRB IDC XXXX
4795 | Whitesburg | 3309302 | VICCO | JEFF | 2022-08-02 14:50 | 2022-08-03 13:40 | 3 | 1370 | 4663801 | 4110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Primary riser broke off at top of transformer on 373/11, opening LF on 373/126 to make repairs..,Restored @ 1340. COMPLETE.
4796 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-12-10 04:26 | 2008-12-10 06:43 | 30 | 137 | 55968-1 | 4110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501/ STS BAD CUTOUT ON POLE 1037 - 15 CUTOUT DOES NOT SERVICE ANY CUST, GOING TO TAKE OFF LINE //VER/GAH L3/KEP IDC XXXX
4797 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-09-05 09:46 | 2022-09-05 11:35 | 164 | 109 | 4839321 | 4106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 38830189000055 / crew req//OPENED RECLOSER 38830164D00110 TO MAKE REPAIRS AT 1111// CLOSED AT 1135
4798 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-11-15 12:07 | 2020-11-16 10:55 | 3 | 1368 | 4680721 | 4104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT MANUAL 19.9 //LINECREW REQ//
4799 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-05-08 15:20 | 2018-05-18 03:22 | 23 | 357 | 4324911 | 4104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Scada DA indicates recl 115-d-453 to be open @ 1517 Released by crew 078S07,,switching and repairs complete on 5/18/18 @ approx 03:20 (a.m.) BLR Released by crew 078H07
4800 | Hazard | 3302704 | HAZARD | KENMONT | 2008-02-17 18:11 | 2008-02-17 18:38 | 152 | 27 | 64332-1 | 4104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3302702/// CREW OPENED RECLOSERS TO ALLOW THEM TO SET POLE IN ORDER 64126-1 // VER/HFP IDC XXXX
4801 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-05-25 14:36 | 2015-05-25 15:51 | 55 | 75 | 4462161 | 4103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE 1080-54,34.5 COND BROKE OUT OF XARM.WILL NEED TO REPLACE XARM,NEED FOREMAN AND 1 A LINEMAN WITH A BUCKET TRUCK/RECLOSER 1080-53 OPENED @ 1436//SWITCH1104- 167 OPENED @1445/CLOSED SWTICH 1104-167 @ 1540/POLE 1080-54/CLOSED RECOSTER 1080-53 @1551/53+2, DUPLICATE IN HOIS/ NO OUTAGE UNTIL OPEN REC// VER/ ADH AJB
4802 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2016-05-16 12:46 | 2016-05-16 13:00 | 293 | 14 | 4222821 | 4102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | REGULATOR NEEDS REPLACED // CREW UNABLE TO GET TO NEUTRAL SO OUTAGE IS REQUIRED//OPEND @ 1246 //CLOSED @ 1300 //COD 293// VER/DBM AJB
4803 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2020-03-29 02:34 | 2020-03-29 13:10 | 31 | 636 | 4520971 | 4096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 39831122C00210 a 35/5 pole broke at ground and will need screw anchor--opened line fuse 39831122C00078 @ 1016 isolated fault @ pole 39831122C00092 and closed fuse in @ 1030 crew on site FETR 13:45 LRM 13:10 all pwr restored LRM Released by crew 078H06
4804 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-03-29 11:35 | 2020-03-29 22:50 | 21 | 675 | 4523091 | 4095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | p-875-844 burned off..tommy goble called.811 dig# 2003290163..14.00..isolated on p-875-635..grd tagged for myself. center phase line fuse back in at 14:..opened 3 line fuses on 875-518 at 20.55.. back on at 22: 50 Released by crew 076S01
4805 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-11-10 16:45 | 2008-11-10 17:20 | 117 | 35 | H1111950-1 | 4095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PLEASE DON`T FORGET THE FETR...THANKS A PHASE INITIALLY OUT 58 CUSTOMERS @ 1645 OPENED B&C PHASES 62 CUSTOMERS.RISER OFF RECLOSERRISER OFF RECLOSER//REPLACED CLAMP ON RECLOSER AND RESTORED POWER IDC HAS THE 3 PH RECLOSER BEEN REPLACED? MAFC TOF1616, CNT175 RECLOSER DID NOT NEED REPLACING ONLY THE CLAMP
4806 | South Williamson | 3411401 | DEWEY | INEZ | 2014-12-23 23:44 | 2014-12-24 00:05 | 195 | 21 | H4878041 | 4095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE 23 COD CUTOUT OPEN ON POLE 768-109 ORIGINALLY/ SERVICER OPENING C PHASE ADDING 195 COD TO SAFELY RESTORE POWER//SQUIRT BOMM WOULD NOT REACH///RYAN NEWSOME BRINGING BIG BUCKET TO CHANGE CUTOUT//WILL STILL HAVE TO OPEN OTHER PHASE//WILL KEEP UP WITH TIMES//REPAIRS MADE///RESTORED ALL CUSTOMERS AT00:05// *****DUPLICATE ORDER FOR ADDITIONAL 195 CUSTOMERS FROM 2344 TILL 0005********* VER/SEF AJB
4807 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-12-05 00:05 | 2008-12-05 03:11 | 22 | 186 | 54596-1 | 4092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302/// 27560507ON SITE, POLETOP BURNT OFF, POLE#1038-A4-410, CALLED R MARCUM FOR HELP VER/JHM ADDDED MISMAPPED CUSTOMERS FROM 54599-1 L3/KEP IDC XXXX
4808 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-01-03 08:48 | 2022-01-03 12:35 | 18 | 227 | 4268861 | 4086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Load side fuse open on step down at 263-B-362,Primary burned into at pole 263-B-256,Spoke with Steve Ray is sending help to make repairs.Restored at 12:35.
4809 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-03-09 14:44 | 2011-03-09 19:50 | 36 | 306 | 52263-1 | 4086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAULT POLE 38830623000014 ISOLATED TROUBLE BY LIFTING HOTTAP ON POLE 623-11;; CLOSED FUSE IN ON POLE 600-8 AT 1620 RELEASED BY CREW 078S11//ALL POWER RESTORED AT 19:50 P R TOLLIVER //COD 36// VER/DBM IDC XXXX
4810 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2016-02-16 20:02 | 2016-02-17 01:09 | 18 | 307 | 4724281 | 4086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT @ 278-190 ISO @ POLE 278-116,RECLOSER IN @ 2209,TAG TO RON VIRGIN RELEASED BY CREW 078S05--CREW ON SITE-REPLACED CUTOUT AND ARRESTOR ON PL#278-190---HOTTAP AND XFMR IN ON PL#278-116 BOTH IN AT 01:09---TBL TKT COMP RELEASED BY CREW 078H16//COD 100
4811 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-06-16 20:49 | 2019-06-17 13:50 | 4 | 1021 | 4518051 | 4084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 50 kva no trucks Released by crew 078S03Replaced bad KVA power restored at 13:50
4812 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2021-03-12 12:30 | 2021-03-12 14:38 | 109 | 68 | 4331071 | 4084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout for xfmr on pole bad also burned pole, send ticket to George Whitaker Released by crew 077S12 // opened line fuse on 37830427A00050 @1230 closed back in @1250 // opened recloser on pole 37830427A00030 to try and make temp repairs on 427-a-50 OFF@1350 ON@1438
4813 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2011-08-21 18:12 | 2011-08-21 20:28 | 30 | 136 | 4736941 | 4080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD L/A ON CSP XFMR PL#901-5568///25T LF OUT ON PL#901-5562//CLEARING L/A AND INSTALLING CUTOUT ON CSP XFMR////REFUSED 25T LF AT 20:28///ALL CHECKS OK COD-40 ISO LF 39830901C45562 IDC FROM NOTES AND CALLS IT APPEARS PHASE C ONLY CHANGED COUNT FROM 40 XXXX
4814 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-06-12 05:02 | 2012-06-12 13:37 | 11 | 515 | 4904371 | 4076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORKTIME AS PER GUIDELINES //CREW REQUIRED POLE BURNT OFF/45/5 POLE/ISOLATED 198-35/TRUCKS OK NO FLAGGERS REQUIRED/198-29 30T BACK ON AT 0950 HRS RELEASED BY CREW 078S03//COD 11//{{ FETR 15:00 JEH//REPAIRS COMP. ALL REMAINING CUST. RESTORED @ 13:37 078H05/ J. HEMLEPP (4 CUST.) RELEASED BY CREW 078H05//COD 11// VER/DBM IDC XXXX
4815 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-12-24 05:06 | 2011-12-24 08:20 | 21 | 194 | 4199781 | 4074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20T FUSE OUT DUE TO BAD CUTOUT CHANGED CUTOUT FUSED UP EVERYTHING OK. SEND COPY TO ROW PIKEVILLE. ALL OF NEDS FORK NEEDS CUT FROM RECLOSER POLE 92-170 TO 116-42. GROWED UP REAL BAD //VER/GAH IDC XXXX
4816 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-04-15 15:06 | 2020-04-18 11:00 | 1 | 4074 | 4700341 | 4074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tap wire burnt @ HLC, arrester wire burnt off also, service drop ok. Released by crew 036E27
4817 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-05-25 03:09 | 2016-05-25 11:38 | 8 | 509 | 4256791 | 4072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL WORK AT START TIME 5-26-16.CLEARED ARRESTOR ON POLE# 21-104 REFUSED 25T LINE FUSE ON POLE# 21-40 FUSE IS NOT SHOWN ON MAP.ENTERED MD. VER/AWD L3/HFP HFPC CNT6
4818 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-08-29 16:55 | 2014-08-29 20:00 | 22 | 185 | 4436941 | 4070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 1147-5136 50T RELEASED BY CREW 078S08/// BAD ARRESTER ON POLE 1147-5140// VER/BOW AJB
4819 | Hazard | 3309901 | SLEMP | DEFEATED CREEK | 2020-01-13 01:40 | 2020-01-13 18:37 | 4 | 1017 | 4295251 | 4068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Slemp/Defeated cr. breaker out waiting on side by side to patrol line bad cutout on 538C/207
4820 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-05-19 08:03 | 2020-05-19 10:47 | 125 | 81 | 4853691 | 4066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | oPH A & B REC Openo Opened PH C rec @ 8:45. Isolated hotline clamps on 809-841 to isolate burned-off crossarm on 809-276. Closed recs @ 9:10 restoring up to open clamps.//cod58 from beginning@ 0845 outed 67 more//0910 p/u 28//OPENED RECLOSER BACK UP @ 1033//ALL CUSTOMERS RESTORED @ 1047
4821 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-10-28 17:29 | 2010-10-28 22:00 | 15 | 271 | 66359-1 | 4065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR# 37536114 // POLE 44-5103 BAD 50KVA TRUCK OK TRANS. ON BREWER RD, TRANS STILL ON RELEASED BY CREW 078S08 ALL POWER RESTORED AT 22:00 //VER/CRB IDC XXXX
4822 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-07-05 20:01 | 2011-07-05 22:08 | 32 | 127 | H4471551 | 4064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1074-350 FAULT POLE//RECLOSER NEVER OPENED//COD 96//SWITCH AT 1074-339 OPENED AT 2001//PRIMARY CAME LOOSE FROM SLEEVE RESAGE PRIMARY WIRE THAT WAS DOWN RELEASED BY CREW 074S05//VER/CRB IDCC CDC83, CNT 98 ONLY PHASE B INITIALLY CREATED OUTAGE FOR OTHER 2 PHASES XXXX
4823 | Pikeville | 3413401 | GARRETT | GARRETT | 2010-05-16 14:58 | 2010-05-16 22:35 | 19 | 457 | 63272-1 | 4063 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTED APART CAUSING 40-5 PRIMARY POLE TO FALLPOLE 16D-170, REWORKED AND ADDED STIRRUPS, INSTALLED CUTOUT ( 40 T ) , GRONDED AND ISOLATED TROUBLE, WILL ENERGIZE TO POLE 16-288 INCLUDING TRANSFORMER ON POLE 170... ALL CUSTOMERS RESTORED, ALL WORK COMPLETE / GXJ IDC STEP TIME INCORRECT CHANGED COUNT FROM 24 XXXX
4824 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2010-03-26 07:34 | 2010-03-26 13:21 | 36 | 347 | 54577-1 | 4062 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34409443 //POLE BURNT OFF 1123-5503 1123-5045 HOT TAP REMOVED 1123-5006 65T BACK ON 08;40 SEND TO VERNON M. RELEASED BY CREW 078S08/FOREMAN ON SITE/CREW LOADING MATERIAL/FETR1400/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1321/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP IDC XXXX
4825 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-03-10 08:53 | 2019-03-10 09:13 | 203 | 20 | 4966871 | 4060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | tried closing goab and locked reclosure out See ticket 4964861 Off @ 0853 on @ 0913 L3/HFP
4826 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2012-12-07 12:00 | 2012-12-07 12:58 | 70 | 58 | 4449271 | 4060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD BAD CUTOUT LINE FUSE ON POLE 925-95, HAD TO OPEN UP RECLOSER ON POLE 925-24, OPENED AT 1200, CHANGED CUTOUT AND CHECK POLE FOR DAMAGE, NO DAMAGE, CLOSED IN RECLSOER AT 1258, RESTORING POWER TO ALL 70 CUST AT THIS LOC//COD 70// VER/DBM IDCC TOF1115 XXXX
4827 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-11-18 02:05 | 2014-11-18 07:30 | 106 | 325 | 4739901 | 4057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN RECLOSER TO SAFELY CUT LOOPS @ 1083-C3-561// WILL WORK AS HOT// VER/SEF L3/DKGXXXX LISTENED TO VOICE RECORDER/CUT LOOPS AT 0205 ON THE 18TH CLOSED AT 0223 ALL BACK ON 0730 THIS IS RELATED TO ORDER 4738681 AJB
4828 | Hazard | 3302704 | HAZARD | KENMONT | 2008-12-12 20:00 | 2008-12-12 22:30 | 27 | 150 | 57853-1 | 4050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP ISO POLE 296-466 L3/HFP IDC XXXX
4829 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-11-05 05:05 | 2013-11-05 08:50 | 18 | 225 | 4010191 | 4050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SERVICER DISPATCHED CREW REQ, HOT TAP BURNTED OFF BASKET, NEED BIG BUCKET TO MAKE REPAIRS, CAN REACH FROM ROAD, MY TRUCK WOULD NOT REACH IT, MATERIAL LIST, NEW BASKET, AND NEW HOT TAP RELEASED BY CREW 078S06,,CREW ON SITE, REPAIRS MADE, ALL POWER RESTORED//COD 18 VER/HFP L3/HFP IDC XXXX
4830 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-09-29 17:25 | 2008-09-29 18:10 | 90 | 45 | 51989-1 | 4050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3413401// B PHASE OCR BAD, BYPASSED AND TAGGED B PHASE OCR / GXJ - MADE ABRNOMAL// 90 COD ON B PHASE VER/TOM IDC XXXX
4831 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-02-16 02:20 | 2016-02-16 04:50 | 27 | 150 | 4699721 | 4050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 263-103..WILL PATROL////FOUND BAD CUTOUT ON POLE 263-110 LIFTED HOT TAP..THIS FEEDS A VACANT HOME..//COD 27// VER/CRB L/3 CRB AJB
4832 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-07-16 15:07 | 2012-07-16 19:20 | 16 | 253 | 4740311 | 4048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100KVA TRUCK TO POLE RELEASED BY CREW 078S08 IDC XXXX
4833 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-08-03 15:49 | 2015-08-03 17:00 | 57 | 71 | H4971191 | 4047 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A& B PHASES SEE 4971191***** CONTRACT CREW TRANSFER CONDUCTOR PUT WIRE IN SLEEVE AND IT BROKE TOOK OUT MIDDLE C PHASE RECLOSER (63 CUSTOMERS)// OPEN OTHER TWO PHASES A&B @1549 (57 CUSTOMERS)/ ISO 38821062C00279/ COD 120/ ALL POWER RESTORED 1700// DUPLICATE IN HOIS/ VER/BOW L3/HFP XXXHFP AJB
4834 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2022-11-14 10:05 | 2022-11-14 10:42 | 138 | 33 | 4140401 | 4047 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | dol 1251878///Outage for crew make temporary repairs.
4835 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-08-22 18:32 | 2014-08-22 23:21 | 14 | 289 | 4406191 | 4046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S09 WILL NEED FLAGGER CALL TREE CREW TO FLAG BAD CUT-OUT AT FUSE POLE39831097A00067 FLAG CREW ARRIVE POWER RESTORED KWB//COD 14
4836 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-11-23 07:42 | 2010-11-23 12:22 | 20 | 280 | 58880-1 | 4046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ISOLATED AT POLE 38831098C10002, C PHASE FUSE AT POLE 38831098C00011 ON AT 08:40 RELEASED BY CREW 074S03 REPAIRS MADE ON AT 12:22 D SAMMONS RELEASED BY CREW 074H02//VER/CRB IDC XXXX
4837 | Paintsville | 3401802 | INDEX | HOSPITAL | 2012-01-17 00:05 | 2012-01-17 08:30 | 8 | 505 | 4266071 | 4040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE CHECKED AFTER REGULAR WORKTIME AS PER SET GUIDELINES //BAD CUTOUTBAD CUTOUT..CHG CUTOUT RE FUSED TRANSFORMER.. ////VER/CRB IDC XXXX
4838 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2010-06-12 07:47 | 2010-06-12 21:15 | 5 | 808 | 60567-1 | 4040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400602 STS 35538596 BAD 25 KVA XFMR ON POLE 187-167. CAN TRUCK - NEED FLAGGERS. ALSO NEED NEW #2 SECONDARY RISERS. RELEASED BY CREW 076S02 REPLACED XFMR ON AT 21:15 D SAMMONS//COD 5// VER/DBM
4839 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-06-26 23:48 | 2011-06-27 06:55 | 22 | 427 | 4418031 | 4039 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT PL 208-69 BURNED 40/5 POLE TOP OFF. CUT LOOP TO ISOLATE FAULT PL AT 208-68 AND GROUNDED.. NEED LINE CREW TRUCKS OK.. CLOSED FUSE BACK IN PL 209-51 AT 2:40 RESTORED EXCEPT FAULT POLE RELEASED BY CREW 078H22/TECH. CALLED/@03:00/REPAIRS COMP. REPLACED 40-5 POLE/// POWER REST.@ 06:55 J. HEMLEPP RELEASED BY CREW 078H05 //COD 22// VER/DBM IDC XXXX
4840 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2008-02-26 16:52 | 2008-02-26 17:39 | 120 | 47 | 50666-1 | 4034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2150103// HAD TO OPEN RECLOSER DUE TO POLE FIRE - WAS ABLE TO OPEN FUSE AND CLOSE RECLOSER AND STILL HAVE TROUBLE ISOLATED//// IDC CNT 178 XXXX
4841 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2017-05-13 19:33 | 2017-05-13 23:45 | 16 | 252 | 4796491 | 4032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 30T FUSE OUT POLE 188-6 DUE TO WIRE DOWN BETWEEN POLE 188-6 AND 188-102 8A WIRE.
4842 | Hazard | 3303901 | LESLIE | HYDEN | 2013-07-11 15:51 | 2013-07-11 18:39 | 24 | 168 | 4508711 | 4032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1700-1715 IDCC FP NULL XXXX
4843 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-08-11 12:01 | 2018-08-11 15:45 | 18 | 224 | 4940551 | 4032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 20t open on 1148-230, patrolling. Primary untied off pole 39831148B20307. Fixed. Fuse back in at 15:45 L3/HFP
4844 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-05-14 06:21 | 2014-05-14 06:33 | 336 | 12 | 4697851 | 4032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENED RECL AT 194 A 33 LOAD TRANSFERRED TO TO JOHNS CREEK/RACCOON N.C SW OPEN & TAGGED AT POLE 98-730 FAULTED SW N.O. SW 74-190 CLOSED ** RESTORES 336 CC TO JOHNS CREEK/RACCOON CKT ALSO ISULATOR BROKEN ON THIS SW NEEDS REPLACED. . N.C. SW ON POLE 98-730 ON FIRE G.O.A.B. SWITCH IS BAD @ 37820098000730// OPENED SWITCH & TAGGED /// CLOSED N.O. ON 37820074000190 @ 6:33 AED CREATED VER/HFP L3/HFP IDC REMOVED 5 MIN STEP TO OTHER ORDER XXXX
4845 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-02-10 13:08 | 2008-02-10 15:00 | 36 | 112 | 54134-1 | 4032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3403201/40 T FUSE OUT ON POLE 141-53. FOUND BAD ARRESTER ON POLE 141-55.//COD 36// VER/DBM IDC XXXX
4846 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2022-09-15 11:13 | 2022-09-15 12:25 | 56 | 72 | 4885641 | 4032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broken line fuse cutout on pole 69-4549. back in @ 12:25. complete
4847 | Pikeville | 3413401 | GARRETT | GARRETT | 2012-12-20 09:58 | 2012-12-20 14:33 | 61 | 275 | 4485551 | 4031 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED TRANSFORMER AT POLE 90-40 , CLOSED SECTIONALIZER AT POLE 66-83 AT 10:57, WILL NEED BIG BUCKET TRUCK TO REPLACE CUTOUT / GXJ RELEASED BY CREW 074S03 REPLACED BAD CUTOUT RE-ENERGIZED AT 14:33 ROBBIE WORRIX VER/KEP
4848 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-02-18 17:21 | 2011-02-18 19:07 | 38 | 106 | 58995-1 | 4028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 374-320... REPLACED CUTOUT RESTORED POWER AT 19:07//VER/CRB IDC XXXX
4849 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-07-05 05:30 | 2016-07-05 11:36 | 11 | 366 | 4533201 | 4026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 850-20//REPAIRS MADE//RESTORED AT 11:36//COMPLETE//EM
4850 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-07-19 06:38 | 2014-07-19 09:19 | 25 | 161 | 4261851 | 4025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE MELTED CUTOUT DOOR BURNED UP VER/ARN AJB
4851 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2017-08-12 17:13 | 2017-08-12 19:54 | 25 | 161 | 4254121 | 4025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 195-16/////WILL PATROL..XFM. CUTOUT BROKEN ON POLE 195-24...WILL MAKE REPAIRS/ ISO 37820195000016/ COD 25/ VER/BOW SJG
4852 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-05-08 02:38 | 2012-05-08 10:05 | 9 | 447 | 4757951 | 4023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED IN TWO ON LOAD SIDE OF RECLOSER ON POLE #38831077D00001. WILL HAVE TO OPEN BREAKER IN TO ISOLATE.WILL GET LINE CREW TO REPAIR. RECLOSURES NEED TO BE RELOCATED NOT TRUCK ACCESSABLE. PLEASE SEND A THIS TO BOB SHURTLEFF & SEE IF HE CAN GET THEM RELOCATED. //PHASE A ONLY (9 CC) // OPENED STA BREAKER TO REPLACE HOT TAP AT POLE 1077-D-1 AT 0950 (946 CC)HOT TAP BURNED IN TWO ON LOAD SIDE OF RECLOSER ON POLE #38831077D00001. WILL HAVE TO OPEN BREAKER IN STA //VER/GAH IDC XXXX
4853 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-02-12 13:58 | 2009-02-15 09:00 | 1 | 4022 | 53117-1 | 4022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OPEN XFMR FUSE, SERVICES ARE UP / POSSILE BAD TRANSFORMER (5KVA) PER CHERYL ON 2/14 AT 1826 LS POWER RESTORED AT 09:00 HRS RELEASED BY CREW 077S02 //VER/GAH
4854 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2022-06-18 22:50 | 2022-06-19 10:00 | 6 | 670 | 4248151 | 4020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Open neutral in secondary. Advised customer to turn main breaker off. Will need manual ROW crew to make repairs in daylight hours. // I repaired a broken neutral, full power restored at 9:45.
4855 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2010-12-31 10:45 | 2010-12-31 14:45 | 61 | 240 | 57285-1 | 4020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38256185 //B PHASE RECL OUT 20 CUSTOMERSSTS WR # 38256185 // BPHASE REC. LOCKED OUT --BAD CSP XFMR ON POLE 72-181 COD-20 ISO RECL 37830048D20985 VER/HFP L3/HFP IDCC CNT20 ADDED 3 PHASE CUSTOMERS XXXX
4856 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2018-08-05 23:38 | 2018-08-06 09:12 | 7 | 574 | 4911991 | 4018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | will work in the AM per guidelines Transformer fuse link appears to have broke. Restored @ 9:12. sh
4857 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-11-09 12:58 | 2013-11-09 14:20 | 49 | 82 | 4024261 | 4018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 473-246 REPLACED CUTOUT POWER RESTORED AT 14:20//COD 49// VER/DBM L3/HFP IDC XXXX
4858 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-08-08 16:31 | 2011-08-08 18:09 | 41 | 98 | 4681541 | 4018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A ON POLE 351-508...WILL CLEAR UP AND RESTORE//COD 41//BAD L/A ON POLE 351-508.WILL CLEAR UP AND RESTORE. BAD ARRESTER ON POLE 351-108. REMOVED ARRESTER AND RESTORED POWER AT 18:09 8/08/2011. J.S.B.// AED CREATED.// VER/DBM IDC DCMT XXXX
4859 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2009-06-18 09:29 | 2009-06-18 14:16 | 14 | 287 | 54621-1 | 4018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | VER/HFP WR # 30352902 //CREW ONSITE, SUSPECT BAD UG TRANSFORMER TOOK THIS OUT//WORKING TO REPAIR/ISOLATE// L3/HFP IDCC CDC83 XXXX
4860 | Hazard | 3303902 | LESLIE | WOOTON | 2022-12-14 14:15 | 2022-12-14 17:58 | 18 | 223 | 4259711 | 4014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Bad dead end insulator on 37830439000006 Pole is manual. Power restored @ 17:58
4861 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2022-01-10 10:12 | 2022-01-10 13:55 | 18 | 223 | 4332461 | 4014 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | crew reqd/broke cutout on xfmer bank 45c4287/steel structure has #45-8049 in between 15 & 16 street in alley. Released by crew 078S04 Opened remaining xfmrs at 13:18.Repairs made closed at 13:55. Ticket complete
4862 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-07-15 16:11 | 2010-07-15 18:58 | 24 | 167 | 50663-1 | 4008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 2746 JACKSONPATROLED LINEPATROLED LINE--BROKEN FUSE VER/KEP L3/KEP IDC XXXX
4863 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-06-18 20:39 | 2017-06-19 10:00 | 5 | 801 | 4993651 | 4005 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE 70-3564 B/C PHASE OUT PUT B IN C OUT BAD CUTOUT TRUCK TO POLE 5200 WIN IN FRONT OF BOB BEAM HOUSEB/ PHASE ON 11;00 PM RELEASED BY CREW 078S08///CHANGED CC DUE TO C PHASE OUT ONLY/// VER/DKM
4864 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-11-13 10:48 | 2014-11-13 12:15 | 46 | 87 | 4724231 | 4002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CHANGING POLE 37820057A00058 OPENED AT 10:48 OPENED AT 10:48 CLOSED AT 12:15. REPLACED ROTTEN POLE. CUT R/W RELEASED BY CREW 079H07//COD 46 VER/HFP L3/HFP AJB
4865 | Pikeville | 3421001 | BREAKS | CITY | 2012-10-24 22:24 | 2012-10-25 07:55 | 7 | 571 | 4169891 | 3997 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED A 50KVA 7.2KV & MAT BUCKET & 1 MAN // WORRIX, ROBERT // VER/KEP IDC XXXX
4866 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-02-19 21:52 | 2015-02-20 03:25 | 12 | 333 | 4045261 | 3996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S04 WILL NEED 50 KVA SECONDARY RISER WIRE ,MATERIALHANDLER & 1 MAN VER/TOM L3/TOM
4867 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-07-17 17:31 | 2013-07-18 10:10 | 4 | 999 | 4539841 | 3996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRIED TRANS. FUSE AT POLE 446-91, CAME BACK OUT WILL DO FURTHER CHECKING. BAD 19.9 , 25 KVA TRANS. WILL NEED MATERIAL HANDLER BUCKET. 1 CUST. AND GUARD SHACK FEEDS OFF OF THIS TRANS. RELEASED BY CREW 075H01 VER/KEP IDC XXXX
4868 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-03-12 11:33 | 2014-03-12 12:58 | 47 | 85 | 4470581 | 3995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 182B-43712,REPAIRS MADE ALL CUST RESTORED @ 1258 PLEASE CLOSE TICKET THANKS.BT IDC XXXX
4869 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-05-10 10:53 | 2021-05-10 14:23 | 19 | 210 | 4555671 | 3990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | crew required ,,182-192 ky power 40-5 pole broke off at ground ,,all power still on ,,tied pole off need replaced tonight if possible ,,need 3 sticks 2 inch conduit ,,straight line primary pole Released by crew 078S05 Released by crew 078H02 opened line fuse @ 1053 closed @ 1423
4870 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-05-31 23:55 | 2012-06-01 11:00 | 6 | 665 | 4857381 | 3990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT HAS BROKEN ON POLE 145 - 103 AND TOOK OUT LINE FUSE ON 145-72. I HAVE TO GO INTO OFFICE AND PICK UP CUTOUT. I CHANGED CUTOUT. SEND TO CORY FARMER. R/W IS TERRIBLE AROUND THIS POLE. IT IS ALSO UP IN 2 SPANS OF OPEN SEC. CONDUCTOR. IT IS GOING TO BURN IT DOWN. THIS IS WHAT BURNED CUTOUT UP AND BLEW LINE FUSE. THIS HAS BEEN TURNED IN NUMEROUS TIMES. CUSTOMERS ARE VERY UPSET. EMAIL THIS TO BOB SHURTLEFF AND TIM HALL ALSO. VER/KEP IDC XXXX
4871 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-09-14 04:51 | 2020-09-14 12:14 | 9 | 443 | 4460071 | 3987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | B phase trans. open @ bank pole 24-D2-1588, checking. Bad 100 kva trans., line crew coming to help change out. Will have to open other 2 trans. to make repairs. Released by crew 074S05.replacing transformer..restored at 12:14
4872 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-04-06 05:22 | 2009-04-06 14:51 | 7 | 569 | 66147-1 | 3983 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701/// POLE FIREPRIMARY POLE BURNT OFF BELOW STEPDOWN, POLE 212-11. NEEDS LINE CREW AND NEW POLE. 50-2 POLE./ OPENED LINE FUSE ON POLE 188-9001 AT 06:35/RELEASED BY CREW 078S01/ SAME AS 66162 VER/KEP L3/KEP AJBC SEE 66162 FOR LINE FUSE OUTAGE. SEE 66154 FOR DUP ORDER.
4873 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-03-10 15:12 | 2014-03-10 15:35 | 173 | 23 | 4465621 | 3979 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED REC. ON POLE 37830249B10346 AT 15:12, REPLACED BAD INSULATOR ON POLE 37830273A00005. CLOSED REC. AT 15:35//COD 173// VER/DBM L3/HFP IDC XXXX
4874 | Hazard | 3303902 | LESLIE | WOOTON | 2010-03-29 09:03 | 2010-03-29 10:45 | 39 | 102 | 55445-1 | 3978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE BROKE AT 316-122 ISOLATED AT 316-171 POLE WILL BE CHANGED AT A LATER TIME CLOSED OCR AT 1045 VER/KEP L3/KEP AJB
4875 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-10-25 02:58 | 2015-10-25 04:35 | 41 | 97 | 4374161 | 3977 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FAILED ARRESTOR AT POLE#1023-16 RESTORED AT 0435 VER/KEP L3/HFP XXXHFP AJB
4876 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-03-06 20:51 | 2013-03-07 11:49 | 28 | 898 | 4885341 | 3976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT 1121-213,BURNTED OFF POLE 1121-348, MAYBE ABLE TO USE A POLE EXTENDS,LIFFTED HOT TAP 11121-125, TAGGED AND GROUNDED AT THIS POINTED, CREW REQ. CAN USE TRUCKS,, ALL CUST ARE RESTORED AT 2245, EXCEPT 1 WHERE POLE IS BURNTED OFF * AT 0510 , CALLED SERVICER TO ON CUST CONCERN OF WIRE STILL ARCING. *** HE REPORTS POLE IS STILL SMOLDERING & GROUNDEDFUSE OUT 1121-213, TAGGED AND GROUNDED AT THIS POINTED, CR VER/KEP IDC XXXX
4877 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-04-06 21:13 | 2017-04-06 23:35 | 28 | 142 | 4625051 | 3976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | LINE FUSE OUT ON POLE 420-21, GUYWIRE RUSTED INTO AT GROUND FALLING INTO CSP XFMR ON POLE 420-5 TAKING FUSE OUT, CAUGHT GUYWIRE OFF FOR NOW WILL GET CREW TO REPLACE TOMORROW. RESTORED POWER AT 23:35.. RELEASED BY CREW 077S11 VER/CRB L3/HFP XXXHFP AJB
4878 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-01-03 08:01 | 2008-01-03 10:23 | 28 | 142 | 53128-1 | 3976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STS GOT LEAD BURNED OFF ON LINE FUSE, CALL JIM MULLINS AND HE IS GETTING CREW TO COME TO HELP//3308001//VER/CRB IDC XXXX
4879 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-10-15 04:48 | 2009-10-15 10:47 | 15 | 359 | 64040-1 | 3969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP FO 40/5 POLE BURNT OFF, BAD CUTOUT. NO TRUCKS TO POLE . CUT LOOP ON POLE 262-80 AND PLACED GROUNDS. NEES LINE CREW.. RELEASED BY CREW 078S01POLE IDCC CNT22, TON FIRST STEP XXXX
4880 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-03-31 17:46 | 2009-03-31 19:25 | 40 | 99 | 63572-1 | 3960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3401103//..RISER BURNED INTO COMING OUT OF RECLOSER. B PHASE RECLOSER......ALL 3 REC. OFF AT 19.10...BACK ON AT 19.25...BB IDCC TON1945 XXXX
4881 | South Williamson | 3411401 | DEWEY | INEZ | 2022-08-06 09:05 | 2022-08-06 11:05 | 33 | 120 | 4690061 | 3960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse out on 768-231//bad insulator on pole 768-239//making repairs//repairs made//restored at 11:05//complete//em
4882 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-11-30 08:02 | 2019-11-30 14:38 | 10 | 396 | 4104671 | 3960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | dead end insulators bad on pole 304-55, we need two men to change insulators or to cut dead end next pole backboth poles manual walk to only Released by crew 077S12. Insulator changed on pole 304-55. Power restored at 14:38
4883 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-11-30 08:39 | 2011-11-30 11:57 | 20 | 198 | 4129081 | 3960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON POLE 1123 -7215 CREW REQ, NEED TO BRING 4- CUT-OUT TO CHG OUT, LINE BUILT AT SAME TIME//C PHASE ONLY//COD 20 RELEASED BY CREW 078S09/REPAIRS COMPLTED POWER REST. @ 11:57 J. HEMLEPP 078H05 VER/ARN IDC XXXX
4884 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2021-10-26 01:11 | 2021-10-26 10:45 | 16 | 574 | 4014681 | 3959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 kva csp transformer is bad,678-101 blew line fuse on 654-255.. isolated csp xfmr on 678-101. re fusing line fuse. line fuse back in at 2:50.need 1 man , 50kva xfmr, cutout and arrester.. //cod 16 //
4885 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-07-28 19:47 | 2017-07-31 13:42 | 1 | 3955 | 4198611 | 3955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | WORK AS AVAILABLE-TALKED WITH CUSTOMER-NO IMMEDIATE NEED TO REPAIR.CHG METER NO CREW REQUIRED 38830246B40189
4886 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-03-15 07:06 | 2009-03-15 12:49 | 44 | 343 | 58706-1 | 3955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000202 -POLE TOP BURNT OFF ON A 40/5 XFORMER POLE (334-180) ,MAY NEED YARD DOG , OR POLE TOP EXT. PLACED GROUNDS ON 334-143 AND LIFTED HOT TAP.NEEDS LINE CREW./FETR1400 FOR ONE CUST THAT IS STILL OFF/VEM/REPAIRS COMPLETE AND LAST CUST RESTORED 1249/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 // VER/TOM L3/TOM IDC XXXX
4887 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2014-08-21 08:49 | 2014-08-21 10:05 | 52 | 76 | 4393541 | 3952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | OPEN RECLOSER FOR TREE CREWS TO CUT TREE OUT OF PRIMARY AT POLE 38820892D00004/// ISO 38820892C00253//// COD 53 OPENED ALL THREE RECLOSERS ON POLE 892-C-253 AT 8:51.// OUTAGE EXTENDED FOUND CRACKED RECLOSERS GOING TO REPLACE ALL 3 WHILE RECLOSER IS OPENOPEN RECLOSER FOR TREE CREWS TO CUT TREE OUT OF PRIMARY AT POLE 38820892D00004// FOUND ALL THREE BYPASSES CRACKED ON RECLOSER POLE 892-C-253.// VER/BOW AJB
4888 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-06-29 17:47 | 2018-06-29 19:31 | 38 | 104 | 4688911 | 3952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole is broke , rotted off below the ground. we are changing out. we will have to kill the power when we get set up Johnny Lawson will be in charge, we will be opening fuse at pole 402-69 Released by crew 077S12//NO OUTAGE TILL L/F 37830402B00069 OPENED//COD 38// opened @ 1747 rstored @ 1931
4889 | Hazard | 3308502 | BONNYMAN | HAZARD | 2009-10-11 20:53 | 2009-10-12 18:50 | 3 | 1317 | 57409-1 | 3951 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | //3308502//UG BAD WILL HAVE TO WAIT TIL MORNING TO LOCATE ADVISED CUSTOMERSUG BAD WILL HAVE TO WAIT TIL MORNING TO LOCATE ADVISED CUSTOMERS RELEASED BY CREW 077S04 //VER/CRB IDC XXXX
4890 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-12-28 11:09 | 2008-12-28 17:44 | 10 | 395 | 64625-1 | 3950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 118-101 BURNT OFF 25T LINE FUSE OUT 94-201 45/4 POLE RELEASED BY CREW 078S08//3008003/// COMPLETE AT 17:44 P R TOLLIVER//SENT TO S.MARTIN TO FIX MAPPING//VER/CRB ROADSAND LINES WERE WRONG ON MAP HAVING TECH CHECK L3/KEP IDCC PN6609 XXXX
4891 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-07-29 13:03 | 2011-07-29 15:41 | 25 | 158 | 4637861 | 3950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKE ON POLE 56-42, GOT CREW COMMING TO HELP REPAIR ARM AND PUT WIRE OPEN STEPDOWNS AT 1303 AND CLOSED AT 1541 VER/KEP IDC XXXX
4892 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-04-03 06:25 | 2015-04-03 12:24 | 11 | 359 | 4262301 | 3949 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUTFAILED CUTOUT ON POLE 193-44. NEED BIG BUCKET TRUCK, ROBBIE WORRIX ENROUTE./ ISO 37820193D00013/ COD 11 L3/DKGXXX
4893 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-05-15 18:18 | 2018-05-16 10:45 | 4 | 987 | 4354791 | 3948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got broke 7200 cutout broke up on side of hill, need three man crew and 7200 cutout and arrestor Released by crew 077S05..replaced cutout arr & brkt..p.hicks/ ISO 37830196B00054/ COD 4
4894 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-11-02 19:25 | 2009-11-02 20:59 | 42 | 94 | H56302-1 | 3948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WORK 32499861//2 PHASES ON SPACER CABLE DOWN-NEED LINE CREW--FLAGMAN2 PHASES ON SPACER CABLE DOWN-NEED LINE CREW--SEND TO LLOYD RELEASED BY CREW 078S07 IDC LOOKS LIKE PH A AND B INITIALLY AND WE OPENED C AROUND 1925 IDC XXXX
4895 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-11-25 05:36 | 2008-11-25 06:23 | 84 | 47 | H51808-1 | 3948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3010602//POLE FIRE ON POLE 1124-8018 CREW REQ, ALL CUST RESTORED BUT 5 RELEASED BY CREW 078S09/CREW ON SITE/FETR 11-25-08/0730/VEM/WORK COMPLETE0623/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDCC DUP TO OPEN AND MAKE UP LOOP XXXXX
4896 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2016-06-02 17:17 | 2016-06-02 21:40 | 15 | 263 | 4287201 | 3945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 120-240 50 KVA. ALLEY WAY RELEASED BY CREW 078S07---0CREW ON SITE ENTERED MD FOR 25T LINE FUSE.BAD 7200, 120-240 50 KVA. ALLEY WAY RELEASED BY CREW 078S07---0CREW ON SITE---REPLACED 50KVA VER/AWD //// LINE FUSE OUT? REST TIME? COULD NOT FIND ON VOICE RECORDER VER/HFP
4897 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-09-30 00:40 | 2011-09-30 07:58 | 9 | 438 | 4933221 | 3942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001401 - WILL HOLD TIL REGULAR WORK TIME AS PER GUIDELINES WITH TEMPERATURE ABOVE FREEZING / REFUSED XMF DOOR OUT OF CUTOUT BROKE REPLACED DOOR AND REFUSED XMF APR AT 0758 CLOSE TICKET COD-9 ISO PO 38830454A41658 VER/HFP L3/HFP IDC XXXX
4898 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-02-21 21:53 | 2011-02-22 08:50 | 6 | 657 | 59966-1 | 3942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 38889020 // BAD L/A // COD 6// VER/DBM IDC XXXX
4899 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-07-07 03:10 | 2017-07-07 12:33 | 7 | 563 | 4086291 | 3941 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 1-29 FAILED INSULATOR/ 1-27 BROKEN BRACE VER/CRB L3/HFP XXXHFP SJG
4900 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-10-05 13:31 | 2010-10-05 20:05 | 10 | 394 | 57052-1 | 3940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 68-941 30T FUSE OUT PRI UNDERGROUND OUT RELEASED BY CREW 078H08//BAD RUN OF PRIM UG CABLE. TRYING TO LOCATE AND REPAIR... CABLE WAS BAD 78 FT FROM 68-942 TOWARDS 68-943 ALL POWER RESTORED AT 20:05 //VER/CRB IDCC CDC83 XXXX
4901 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-09-07 09:17 | 2011-09-07 14:20 | 13 | 303 | 4842151 | 3939 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSLATOR-- CUTOUT GATE AT FOOT OF FUSE POLE RELEASED BY CREW 077S10 MADE REPAIRS AND RESTORED POWER AT 1420 CREW 077H01 IDC XXXX
4902 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-10-06 14:32 | 2015-10-06 14:56 | 164 | 24 | 4322431 | 3936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | EMERGENCY OUTAGE TO REPAIR BROKEN TIE WIRE = PHASE OFF INSULATOR AND LAYING ON ARM // COD-164 ISO OCR 38830164D00110 REC OPENED ON POLE 164-110 AT 14:32 BACK ON AT 14:56 COD-164 ISO OCR 38830164D00110 VER/HFP L3/HFP AJB
4903 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-11-27 08:04 | 2022-11-27 12:10 | 16 | 246 | 4182921 | 3936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | K Little assisting/LF open on 92-28// checkingLF open on 92-28// checking// busted cutout on pole 92-31, made repairs
4904 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-07-21 04:53 | 2010-07-21 09:15 | 15 | 262 | 54654-1 | 3930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 36079026// POLE 1147-5509 CUTOUT DOOR BURNT UP 15T TRANS. FUSE//COD 5 PER SERVICER// VER/DBM IDC CHANGED COUNT TO 15 APPEARS TO BE AN APARTMENT HERE XXXX
4905 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-01-26 09:54 | 2009-01-26 13:45 | 17 | 231 | 59866-1 | 3927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3408103// POLE 1 , CROSSARM BROKEN, FUSE ON NEW POLE 1098-854......ALL WORK COMPLETE / GXJ//MADE 3-4 MDC`S//VER/CRB IDC XXXX
4906 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-11-09 00:03 | 2010-11-09 00:15 | 327 | 12 | 54149-1 | 3924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO ALLOW CREW TO REPAIR SWITCH/CUTOUT THAT FAILED // RELATED TO ORDER 54144-1 // COD- 327 //VER/GAH L3/ JKW IDC XXXX
4907 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-09-28 08:04 | 2009-09-28 11:20 | 20 | 196 | 66391-1 | 3920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 15T LINE FUSE/CREW REQUIRED BROKEN CUTOUT/GENTS CREW ENROUTE RELEASED BY CREW 078S03 RESTORED AT 1120 IDC XXXX
4908 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2016-05-02 16:29 | 2016-05-02 19:45 | 20 | 196 | 4161701 | 3920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE INSULATOR WENT BAD AND BURN LINE DOWN ==== REPAIRED LINE ==== REFUSED LINE POWER OK VER/AWD AJB
4909 | South Williamson | 3200302 | BELFRY | TOLER | 2017-12-31 22:29 | 2017-12-31 23:18 | 80 | 49 | 4690891 | 3920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse had melted out at pole 38821015D00076, I replaced it with a 300 amp solid door like fieldview is showing. Recloser was not opened, all power is restored.//cod 80//
4910 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-11-30 20:11 | 2020-12-01 04:21 | 8 | 490 | 4733101 | 3920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Open neutral on UG service to home. Pulled meter @ 22:45 to disconnect power. Crew enroute to help locate and repair. Will be opening xfmr when crew arrives to locate./// Could not locate fault opened xfmr 728-A2-69 @03:58 and installed temp neutral. Restored @04:21// Line crew will be back in daylight tore locate and make permanent repairs//
4911 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-12-12 12:20 | 2016-12-12 13:00 | 98 | 40 | H4186401 | 3920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | /CENTER PHASE RECLOSER IS OUT PATROLLING COD 55/CENTER PHASE RECLOSER IS OUT PATROLLING..TIE WIRE BROKEN, CONDUCTOR OFF PIN AND LYING ON THE CROSS ARM.ON P-777-15..ALSO PRIMARY NEUTRAL DOWN ON POLE- 777-19..#2 ALUMN.ALL CLIMBERS. A&C OPENED AT 1220./TIE WIRE BROKEN, CONDUCTOR OFF PIN AND LYING ON THE CROSS ARM.ON P-777-15..ALSO PRIMARY NEUTRAL DOWN ON POLE- 777-19..#2 ALUMN.ALL CLIMBERS.OPENED THE OTHER 2 REC AT 12.20..ISOLATED GRD AND TAGGED FOR MYSELF A&C OPEN 1220-1300 VER/AWD L3/HFP XXXHFP AJB
4912 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-03-02 11:13 | 2014-03-02 15:34 | 15 | 261 | 4443531 | 3915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN AT POLE 38821111B00111, PATROLLING THE LINE. BAD TAP CUTOUT ON POLE 38821111B00024 BACK ON HILLSIDE, NO TRUCK. VER/CRB IDC XXXX
4913 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-02-21 07:10 | 2010-02-21 10:00 | 23 | 170 | 59460-1 | 3910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WR#33951735 /LEAD IN XFMR BURNED INTO..I HAVE TO RUN TO PAINTSVILLE OFFICE TO GET 350 LEAD AND BIG PRESS..BB/ RESTORED AT 1000 / COD-23 VER/LDA IDC CHANGED TIME OFF FROM 0702 XXXX
4914 | South Williamson | 3200302 | BELFRY | TOLER | 2011-08-07 21:38 | 2011-08-08 10:40 | 5 | 782 | H4676881 | 3910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PREDICTED DEVICE NOT OUT..RECLOSER IS OPEN ON PHASE A (112 CUSTOMERS ON RECLOSER ) ON 1039A17.BURNT UP DOOR ON XFMR CUTOUT ON 1039A21 WHERE HAZRD CALL WAS..REST OF LINE LOOKS OK..//.CLOSED RECLOSER ON 1039A17 @ 00:05..JRV.08/08/11 VER/KEP IDC DUP FOR ORIGINAL OUTAGE 1 TRANSFORMER. IDC XXXX
4915 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-02-11 05:40 | 2014-02-11 08:30 | 23 | 170 | 4372391 | 3910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BURNED CONNECTION OFF SECONDARY NEED TO SEND TO CLIFF FRREMAN..LOAD NEEDS TO BE SPLIT UP TAKE CUSTOMERS OFF THIS BANK..ADD TRANSFORMER.BACK ON AT 8.30 VER/CRB IDC XXXX
4916 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-08-03 21:32 | 2012-08-04 16:26 | 5 | 1134 | 4893011 | 3908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 2 PRIM UGS OUT,POLES 24-659&24-666,TRIED BOTH,FUSES BLEW,NEED HELP//TOLD THAT MORNING CREW WILL REPAIR RELEASED BY CREW 074S06 CREW ON SITECABLE F>24-659 >24-1097 GOOD REFUSE 30T AT 24-659 NEED TO HIPOT FROM 1097>1099//PAD 1097 IS HOT PARTIAL RESTORED AT 01:45 CABLE BAD AT PAD 1099 REPAIRS BEING MADEOPEN ON POLE 24-659 AT 9:45 CLOSED AT 18:26 RESTORING ALL CUSTOMER IDCC CNT6, STP 1 MISSING, FP 659 XXXX
4917 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-02-14 23:09 | 2009-02-15 15:26 | 4 | 977 | 61840-1 | 3908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP BURNT INTO AT POLE 1123B32. NEED CREW TO REPAIR. 65T FUSE OUT ON POLE 1123B5 B PHASE. JUST OFF RT 122 MEADE DRIVE. NEEDS WORKED WITH 58803-1//THIS WAS REPAIRED @ 1526 PER PIKEVILLE OFFICE//COD 4
4918 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-06-29 22:18 | 2019-06-30 04:13 | 11 | 355 | 4620151 | 3905 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Pole # 1089/17 wire came off ins. and laid on pole replaced ins. and tied wire back in power on at 04:13 could not find cause//cod 11//
4919 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2010-02-06 19:53 | 2010-02-06 23:57 | 16 | 244 | 51124-1 | 3904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR 33768520// BAD 37.5 NEED 50 OR 75 KVA RELEASED BY CREW 078S08 //VER/GAH IDC XXXX
4920 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-04-18 18:22 | 2018-04-18 20:25 | 47 | 123 | 4252341 | 3901 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Center phase out on stepdown 37830165000226 (cod: 7). Opened other two phases at (cod: 40) The riser burned out of the low side of the stepdown at pole 165-226 I opened th other 2 at 1956 made repairs and closed all 3 reclosers at 2025 /// PER CALLS & PHASING ON MAP IT WAS A PHASE INITALLY OUT // 27 CUST L3/HFP/// trouble tickets show A phase out at first
4921 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-11-15 15:08 | 2008-11-15 17:18 | 30 | 130 | 65372-1 | 3900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302//MD FILED FUSE MISMAPPED COD-30/CUTOUT WENT BAD BURNED TOP OF POLE OFF == REPAIRED == PUT POWERR ON == VER/KEP MLR OK
4922 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2008-09-25 09:15 | 2008-09-25 10:30 | 52 | 75 | 50422-1 | 3900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309101// CUTOUT BAD ON POLE 448-690 GOING TO REPLACE CUTOUT//COD 52//ISO 37830448C30690// VER/DBM MLR OK IDC XXXX
4923 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-06-28 13:21 | 2010-06-28 14:36 | 52 | 75 | 59068-1 | 3900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSER IN ABNORMAL//OPENING BY-PASSES AND CHANGING OUT RECLOSER
4924 | Hazard | 3303902 | LESLIE | WOOTON | 2022-09-06 18:11 | 2022-09-07 10:25 | 4 | 974 | 4848691 | 3896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Per Phillip Hicks hold til morning Line Crew and Tree Crew Required / Broke cutout 19.9 on pole 342-5 going to need T bracket and arrestor. power restored 10:25
4925 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-01-11 09:00 | 2014-01-11 12:25 | 19 | 205 | 4271311 | 3895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE SIDE FUSE ON STEPDOWN BLOWN AT POLE 398-232, TIE WIRE BROKE ON POLE 398-163 LETTING PRIMARY MAKE CONTACT WITH NEUTRAL, MADE REPAIRS RESTORED POWER AT 12:25.//COD 19// VER/DBM L3/HFP IDC XXXX
4926 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-01-25 12:22 | 2013-01-25 14:20 | 33 | 118 | 4740251 | 3894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 222 36 ,,, CHANGEING IT OUT NOW ,,,REPLACED CUTOUT POWER RESTORED AT 14..20 COD-33 ISO OCR @ 37830222D10383 VER/HFP L3/HFP IDC XXXX
4927 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-02-17 23:43 | 2022-02-18 02:40 | 22 | 177 | 4500561 | 3894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Load side fuse open on stepdn 476-260 patrolling////// Nothing found refused stepdn and restored all power with recloser on 476-261 at 0240 close ticket
4928 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-11-18 15:30 | 2009-11-18 16:24 | 72 | 54 | 52801-1 | 3888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQUEST 32745421 // BAD CUTOUT HAS BURNT UP CROSS ARM /CREW ON SITE /FETR1730/ VEM/FETR1730/ VEM/OPENED SOLID BLADES ON 166-196 AT 1537/ NEW FETR1700/VEM // VER/TOM L3/TOM IDCC TOF1537, TON1537 XXXX
4929 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-06-06 16:09 | 2009-06-06 19:14 | 21 | 185 | 51226-1 | 3885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP WR # 30168373 // STS GOT D. E. INSULATOR GONE BAD, TIM SMITH IS BRING BIG BUCKET AND MATERIAL COD-21 ISO 38831083C10648 ENTERED MD...HFPWR # 30168373 // STS GOT D. E. INSULATOR GONE BAD, TIM SMITH IS BRING BIG BUCKET AND MATERIAL RELEASED BY CREW 077S05 L3/HFP IDCC PN641 XXXX
4930 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-04-22 10:30 | 2010-04-22 11:45 | 76 | 75 | 66295-1 | 3875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSE RECLOSER IN AT 11;20 AM//VER/CRB IDCC CNT79 XXXX
4931 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-12-24 18:46 | 2008-12-24 21:35 | 58 | 169 | 63646-1 | 3874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3402802// LIMB THAT WAS ON XFMR BUSHING EARLIER HAS DAMAGED LIGHTNING ARRESTER AND POSSIBLY XFMR(TANK MOUNTED ARRESTER BLEW UP). HAVE XFMR ISOLATED - WILL CLOSE REC. CLOSED AT 19:51. ONLY ONE CUSTOMER SERVED FROM ISOLATED XFMR. WILL HAVE TO CLIMB UP AND I//LAST CUST ON @ 2135// VER/DBM L3/KEP IDC XXXX
4932 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-01-06 20:34 | 2019-01-06 23:30 | 22 | 176 | 4635731 | 3872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | B phase only cod-9/ when line goes to single phase at pole 829-38 its C phase not B phase/line fuse blown on 829-78 patrolling lineline fuse blown on 829-78 patrolling line.fuse broken.pulled apart./// Trouble tickets show B and C out from start
4933 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-06-14 08:47 | 2022-06-14 14:39 | 11 | 352 | 4100191 | 3872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse one pole 1137-D-386 is open have a bad 7200 cutout on that pole is on the side of the hill manual talked to jamie smallwood he said he would get it changed on his way to other case of trouble Released by crew 079S02// restored @1439
4934 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2021-11-28 23:23 | 2021-11-29 06:33 | 9 | 430 | 4130531 | 3870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | pole # AB-60 burnt up 80% at bottom phase vertical construction..transmission notified and inroute. city blocking off greenup ave 11th st to 9th st-ds112921 Released by crew 078S01
4935 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2013-06-08 09:39 | 2013-06-09 13:47 | 3 | 1688 | 4238891 | 3864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN BETWEEN POLE 517-43 AND 517-44. 700 FOOT SPAN. PRIMARY BROKE BETWEEN INSULATORS ON POLE 517-44, POLE 44 IS MANUAL. NEED MANUAL R/W CREW. MANUAL POLE#44 WILL BE REPLACED ON 6-9 LAST TRANS OFF TILL THEN NEED MANUAL R/W CREW. POLE 43 AND 44 IS ROTTEN. CANNOT BE CLIMBED. WILL HAVE TO COME BACK IN THE MORNING WITH MORE MEN TO REPLACE BOTH POLES. BETWEEN POLE 517-43 AND 517-44. 700 FOOT SPAN. PRIMARY BROKE BETWEEN INSULATORS ON PO VER/PDP IDCC CNT2, STP MISSING XXXX
4936 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2020-03-15 07:21 | 2020-03-15 08:45 | 46 | 84 | 4479371 | 3864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3420101/gaj/0735/all out disp 3523 T Goble & 3524 B Bowerstock rec on 785-1266 shows in but is out. patrolled line all lines up. Tommy Goble enroute. rec battery dead in recloser cabinet, send to byron combs need to replace battery back on at 8:45..
4937 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2016-04-27 07:35 | 2016-04-27 12:01 | 20 | 266 | 4130711 | 3864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSTALLED FAULT INDICATORS AT 270-57/CALLED FOR A CREW /LINE FUSE BACK IN AT 1030HRS RELEASED BY CREW 078S03/CREW ON SITE/INSPECTING POLES FOR CAUSE/FETR1230/VEM/BAD DEAD END BELL 270-D-6003/REPAIRS MADE AND ALL CUST RESTORED 1201/PLEASE CLOSE TICKET/VEM VER/HFP L;3/HFP AJB
4938 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2011-08-11 18:37 | 2011-08-11 21:25 | 23 | 168 | 4698081 | 3864 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | STATION OUTAGE TO REPAIR CB DISCONNECTS OPEN AT 1831. CREWS WORKING TO REPLACE DISCS. VER/PDP IDC XXXX
4939 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-10-22 08:56 | 2012-10-22 10:35 | 39 | 99 | 4161831 | 3861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE HAS PULLED LOOSE FROM BOTTOM OF LINE FUSE ON 38821058B00067// WILL REPAIR// REPAIRED CUTOUT// POWER IS RESTORED VER/KEP IDC XXXX
4940 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-08-20 07:53 | 2014-08-20 11:40 | 17 | 227 | 4387791 | 3859 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | RECLOSERS SHOW TO BE IN. GOING TO THE UPPER JOHNS CREEK SIDE OF MOUNTAIN TO CHECK FOR PROBLEM. LOOKS LIKE ONLY THE C PHASE IS OUT. PATROLLING THE LINE. C PHASE RECLOSER ON POLE 37820007C30123 IS BAD, BYPASSED RECLOSER WITH A 100 T FUSE.// NEEDS PUT IN ABNORMAL BEFORE BEING CLOSED DKG ENTERED ABNORMAL
4941 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-03-17 19:19 | 2011-03-17 22:42 | 19 | 203 | 55316-1 | 3857 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39211674 // BAD LA SOMEWHERE TRYED LINE FUSE BLOW FUSE SEND TO BILL RELEASED BY CREW 078S08 COD-19 ISO LF 38830092A00458 VER/HFP L3/HFP IDC CHANGED FROM ARRESTER PER CONF CALL FOUND CRACKED CUTOUT XXXX
4942 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-08-30 02:47 | 2021-08-30 05:00 | 29 | 133 | 4173011 | 3857 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Line fuse open @71-17, checking. This section is mismapped, a fault on the URD line caused the overhead line fuse to blow here, closed L/F back in @0500./ ISO 37830071000017/ COD 29
4943 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-04-14 15:54 | 2017-04-14 17:28 | 41 | 94 | 4646461 | 3854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MD TO SHOW L/F ON POLE 38830478A31104//PLEASE DO MD ON 38830478A31104 THEY ARE TWO 40T FUSES ON THAT POLE THANKS, REPLACED BAD CUTOUT APR AT 1728 CLOSE TICKET. DWEST VER/CRB L3/HFP XXXHFP AJB
4944 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-05-17 08:53 | 2021-05-17 12:27 | 18 | 214 | 4591241 | 3852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 40t open on 116-184, tried once and came back out, patrolling. Bad bell insulators on pole 38830116B00262, No trucks, crew required Released by crew 078S02 Crew on site Closed at 12:27 Ticket complete.
4945 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2020-05-19 17:47 | 2020-05-19 21:21 | 18 | 214 | 4859571 | 3852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced 3 cutouts and arresters,,,all customers nresstored @ 21:21 complete
4946 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-08-16 18:52 | 2013-08-16 20:42 | 35 | 110 | 4672261 | 3850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FAILED ARRESTER ON POLE 122-233 PUT IN ABNORMAL DATABASE VER/SEF IDCC CDC96 XXXX
4947 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2022-01-17 07:13 | 2022-01-17 09:47 | 25 | 154 | 4366041 | 3850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on 147-345 will patrol///Cutout failed and burnt top of pole 147-164 ///Might can lower will be making repairs///Lowered primary and changed bad cutout///Refused line fuse 147-345 @ 09:47 and restored all customers////Send copy to Ryan Thornberry to write job up to change pole 147-164 @ later date///sent email to Bill Johnson for follow up
4948 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-12-10 05:09 | 2008-12-10 10:59 | 11 | 350 | 55979-1 | 3850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3116701// NEED 75KVA 4/0 SEC. NO TRUCKS HANG BY ROAD RELEASED BY CREW 078S08//REPLACING 50KVA WITH 75KVA ALSO CUT-OUT AND ARRESTOR P R TOLLIVER/// WR#27623467 COMPLETE 10:59 PR TOLLIVER//VER/CRB L3/KEP IDC XXXX
4949 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-04-02 14:20 | 2015-04-02 23:13 | 13 | 533 | 4259361 | 3845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /230-32 BACK IN AT 1856 HRSLINE FUSE ON 230-32 OPEN/CALLED FOR TREE CREW /TAGGED TO MYSELF TO CUT TREES /BAD DEADEND ON 230-285 ISOLATED ON 230-268 CREW REQUIRED /230-32 BACK IN AT 1856 HRS (12 CUST) ///CREW ON SITE/FETR2330/VEM/1 CUST RESTORED 2313/PLEASE CLOSE TICKET/THANKS/VEM COD-13 ISO LF 38830230000032 --- FIXED IN HOIS ENTERED MD // VER/HFP L3/HFP
4950 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-09-03 15:26 | 2011-09-03 17:30 | 31 | 124 | 4792271 | 3844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 45-109 BAD LA ALSO POLE 45-1212 TREES BURNING IN PRI. CALLED TREE CREW POLE 45-5 40T LINE FUSE//COD 31// VER/DBM IDC XXXX
4951 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2019-02-23 20:53 | 2019-02-23 22:57 | 31 | 124 | 4851111 | 3844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout @ 330-22,,recloser 305-132 back in @ 22:57 complete
4952 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-01-23 17:39 | 2020-01-23 18:40 | 63 | 61 | 4333151 | 3843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Attempted to notify customers/ Opened XFMR fuse and Line Fuse/ Crew replacing cutout/ ISO 37830487000056/ COD 62/ OFF1739 ; ON1840 L3/HFP
4953 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-04-29 05:00 | 2008-04-29 09:00 | 16 | 240 | 55351-1 | 3840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3400301//SERVICER UNABLE TO DETERMINE WHATS CAUSING PROBLEM... PHASE A RECLOSER ON 45-249 IS BLOWN... THINK CUSTOMERS ARE REPORTING DIM LIGHTS DUE TO BACK-FEED FROM COAL MINE//PATROLLING LINES//3400301// BAD RECLOSER ON POLE 20-116. A PHASE RECLOSER IS OFF LINE AND TAGED.SEND COPY OF THIS TO PERRY FARMER. THIS INFO WAS SENT TO PERRY VIA AN ABNORMAL DATABSE ENTRY//COD 35// VER/DBM IDC IDC SPOKE WITH HARVY MARTIN TO GET DETAILS XXXX
4954 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-04-04 13:30 | 2015-04-04 14:10 | 96 | 40 | 4274981 | 3840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELATED TO ORDER 4270511/ 1330 OPENED UP THE OTHER B PHASE RECLOSER TO PUT WIRE BACK UP BETWEEN 37830278D30335A AND 37830279B10250// CLOSED RECLOSER 37830278D30335A @ 1410 SEE 4270511 & H4270511 ALSO --- VER/HFP L3/HFP AJB
4955 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-07-24 16:24 | 2012-07-24 18:00 | 40 | 96 | 4814701 | 3840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DC APPEARS TO BE OPEN LOOP OR FUSE MISSING FROM LOOKING AT THE CALLS, ESTIMATING FUSE LOCATION NEAR 247A-1182 LINE CUTOUT ON POLE 37830247A01182 IS BAD === REPLACED CUTOUT, POWER RESTORED AT 18:00//ISO//MD FILED//COD 40//
4956 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-09-14 12:32 | 2013-09-14 14:40 | 30 | 128 | 4854331 | 3840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 25T FUSE OUT ON STEP DOWN TRANSFORMER. DUE TO BAD ARRESTER. WILL BE CHANGING ALSO CHANGE CUTOUT VER/SEF L3/HFP HFPC CDC92 IDCC XXXX
4957 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-10-14 05:39 | 2010-10-14 13:27 | 27 | 468 | 59487-1 | 3836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR - 37322479// FAULT POLE 38830067C00500 ISOLATED & GROUNDED AT POLE 38830067C00430WR - 37322479// POLE 67-500 BURNT OFF REMOVED HOT TAP 67-430 POLE 43-150 30T ALSO POLE 43-214 BAD CUTOUT CHGED ITWR - 37322479// POLE 67-500 BURNT OFF REMOVED HOT TAP 67-430 POLE 43-150 30T ALSO POLE 43-214 BAD CUTOUT CHGED IT RELEASED BY CREW 078S08/CREW ON SITE/FETR1400/VEM/ONLY ONE CUST OUT ON 67-500/REPAIRS MADE AND POWER RESTORED 1327/PLEASE CLOSE TICKET/THANKS RELEASED BY CREW 078H14 COD-27 VER/HFP L3/HFP IDC X
4958 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-03-14 17:22 | 2015-03-14 19:39 | 28 | 137 | 4194521 | 3836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND TO A TECH TO RELOCATE POLE// POLE 524-224 BURNT OFF FROM BAD CUTOUT/ FUSE IS OPEN ON 524-168 PATOLLING LINE/ FUSE IS OPEN ON 524-168 PATOLLING LINE, POLEFIRE ON 524-224 TEMP REPAIRES MADE APR AT 1939, PLEASE SEND COPY TO TECH TO HAVE POLE CHANGED OUT LATER NEED NEW 25 KVA INSTALLED ON POLE AS WELL; CLOSE TICKET/ ISO 38830524000168/ COD 28 AJB
4959 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-01-05 12:08 | 2013-01-05 13:07 | 65 | 59 | H4571081 | 3835 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | INTERNAL PROBLEMS WITH THE STATION TRANSFORMER - TRANSFERRING LOAD TO ALT SOURCES & CALLING STATION CREW TO INSTALL MOBILE TR AT CANNONSBURG STATION //VER/GAH IDC XXXX
4960 | Hazard | 3302704 | HAZARD | KENMONT | 2013-12-13 07:01 | 2013-12-13 08:00 | 65 | 59 | 4158441 | 3835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BAD, REPLACED CUTOUT DOOR. POWER RESTORED AT 08:00 VER/CRB L3/HFP IDC XXXX
4961 | Hazard | 3309301 | VICCO | REDFOX | 2014-11-25 12:00 | 2014-11-25 13:11 | 54 | 71 | 4780361 | 3834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND LIGHTNING ARRESTOR BAD ON HIGH SIDE OF STEPDOWN, REPLACED IT. POWER RESTORED COD-54 ISO LF 37830276000136 VER/HFP L3/HFP AJB
4962 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-05-28 19:24 | 2021-05-29 11:22 | 4 | 958 | 4640211 | 3832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr, manual, will need line crew, 25 kva 7.2 kv Released by crew 077S02//hold untildaylight per Philip Hicks // Released by crew 077H09.. restored power at 11:22..
4963 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2018-07-16 19:20 | 2018-07-16 23:45 | 20 | 265 | 4783591 | 3830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 100 kva 7200 bad truck acess Released by crew 077H14 power restored at23:45 // lifted hot tap at 2250 Xfer and Tap on Same pole L3/HFP
4964 | Whitesburg | 3314401 | MAYKING | ERMINE | 2014-02-01 15:57 | 2014-02-01 16:03 | 638 | 6 | 4335281 | 3828 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | OPENED CB TO SAFELY BYPASS STATION REGULATOR VER/KEP VER/HFP L3/HFP IDC XXXX
4965 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-01-23 11:32 | 2008-01-23 15:53 | 31 | 261 | 59172-1 | 3828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | MIDDLE PHASE OPEN POLE 129-42 C PHASE COD-31/SERVICER PATROLING CLOSED RECLOSER AT 1326 MIDDLE PHASE DOWN ON POLE 129-53 WILL HAVE TO PUT BACK UP 2 CUST VER/KEP IDC XXXX
4966 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2008-10-24 23:38 | 2008-10-25 01:05 | 44 | 87 | 58760-1 | 3828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CALLED CREW *** ON SITE MAKING REPAIRS.CALLED CREW/REPLACED INSULATOR VER/PDP IDC XXXX
4967 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-12-12 11:19 | 2008-12-12 16:38 | 12 | 319 | 57623-1 | 3828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP PATROLED LINE GOING ON HILL TO CLOSE CUTOUT WIRE OFF POLE TOP PIN ON POLE703-39 CALLED ROGER ON HIS WAY RELEASED BY CREW 076H06// 50T FUSE BLOWN ON POLE 703-13// REPAIRED CONDUCTOR AND REFUSED LINE. ROGER MAYNARD COD-12 L3/HFP IDC XXXX
4968 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-07-13 22:02 | 2010-07-13 22:45 | 89 | 43 | 66556-1 | 3827 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TRAVIS BURTON, CALLED IN BAD INS. I OPENED UP RECLOSER ON POLE 1098-3155, GROUNDED AND I CHANGED BAD INSULATOR ON POLE 1098-3536, POWER IS RESTORED TO ALL CUST AT THIS LOC, AT 22 VER/KEP L3/KEP IDC XXXX
4969 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-05-08 21:01 | 2008-05-08 22:30 | 43 | 89 | 58500-1 | 3827 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRIMARY CAME OFF OF INSULATOR, RETIED AND RESTORED AT 22:30//3001003 IDC XXXX
4970 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-12-18 16:25 | 2016-12-18 17:40 | 51 | 75 | 4217381 | 3825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4213281***/ OPENING STEP DOWN TRANSFORMER TO REPLACE CUTOUT ON POLE 37830236000015/ ISO 37830236000002/ COD 51/ 1625-1740/ VER/BOW AJB
4971 | Hazard | 3308502 | BONNYMAN | HAZARD | 2021-01-25 18:09 | 2021-01-26 10:05 | 4 | 956 | 4891651 | 3824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke manual 7200 cutout on pole 199-112. need line crew Released by crew 077S10
4972 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-03 08:06 | 2021-06-03 13:00 | 13 | 294 | 4661641 | 3822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse blown on pole 601-b-50//insulator failed on pole 601-54 and primary burned down//need line crew and manual tree crew//repairs made//repairs made//restored @ 13;00//complete/em
4973 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-07-15 11:09 | 2015-07-16 19:00 | 2 | 1911 | 4875731 | 3822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEEDS REFUSED SERVICE ONLYTRANSFORMER FUSE BLEW /DID NOT OPEN. CUSTOMER SAID CUT OUT HAS MADE A FIRE BEFORE. ON SAME POLE MAY WANT TO USE A TBKT WITH ARRESTER AND CUTOUT THIS TIME. LAC RELEASED BY CREW 077E05// THIS WILL TAKE COUPLE 2 MEN, C/O BROKEN ON POLE 227-236, MANUAL POLE. REMOVE PRIMARY TAP ON POLE 227-59 BEFORE GOING TO POLE 227-236 TO CHANGE C/O. RELEASED BY CREW 077S08
4974 | Hazard | 3303902 | LESLIE | WOOTON | 2009-12-24 20:42 | 2009-12-27 12:18 | 1 | 3816 | 61238-1 | 3816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIM DOWN BETWEEN POLES 559-8 & 559-10 CLAMP REMOVED AND LINE OPEN AT POLE 559-6 WILL NEED R/W CREW NOT TRUCK ACCESSIBLE/ REPAIRED LINE & RESTORED POWER // POWER RESTORED AT 1218 122709 CAN CLOSE TICKET MWL
4975 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2014-03-03 11:50 | 2014-03-03 19:47 | 8 | 477 | 4447211 | 3816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECEIVED FROM SCADA: 12:13 3-3-14/HAVE 454 BUCK ARM POLE BURNTED OFF ABOUT 3 FT OF THE TOP, AT THE BOTTOM SET OF ARMS, BAD C/O CAUSE THIS, CREW REQ, AND AWP, HAD TO OPEN UP BREAKER IN ORDER TO PUT OUT FIRE AND ISOLATED C/O, OPEN BREAKER AT 1212, CLOSED BACK IN A 1239, ALL RESTORED BUT COUNTY GARAGE, MATERIAL LIST: 4 9 FT ARMS, 4 BRACES, 6 ARM PINS AND INS, 3 C/O ALSO SEE PO#4448091RECEIVED FROM SCADA: 12:13 3-3-14/ VER/ARN IDCC CNT1311 TOF1212 XXXX
4976 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-10-06 00:31 | 2014-10-06 11:06 | 6 | 635 | 4556121 | 3810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ISOLATEDHOT TAP ON POLE 357-93 CUT ARRESTOR IN CLEAR ON 357-49/PATROLED LINE OVER HILL TO 357-49 IN DARK AND RAIN TRIED 30 T FUSE ON 357-48 HEARD LOUD NOISE UP HILL PUT 357-93 BACK NORMAL /SERVICER PLUS HELP TO FIND PROBLEM SEND TREE CREW AS WELL--PRIMARY OFF OF INSULATOR LAYING ON RIDGE PIN COD-6 ISO LF 38830357000048 VER/HFP L3/HFP AJB
4977 | Hazard | 3303902 | LESLIE | WOOTON | 2010-06-23 14:55 | 2010-06-24 01:30 | 6 | 635 | 55984-1 | 3810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 LEG OF SEC IS BROKE RELEASED BY CREW 077S01....ON SITE NOW,..P.HICKS..BAD 19.9KV, 50KVA TRANSFORMER, HAVE CONTRACTORS ON SIGHT NOW,...ALL POWER RESTORED @ 01:30 IDC CHANGED POLE FROM 7 XXXX
4978 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-01-07 16:46 | 2019-01-07 18:45 | 32 | 119 | 4638181 | 3808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PRIMARY OFF PIN /// R NEWSOME ENROUTE TO ASSISTtie wire broke off pin letting primary to fall. 901-75 replacing L3/HFP
4979 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-09-09 12:06 | 2008-09-09 16:38 | 14 | 272 | 60816-1 | 3808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311401//CUTOUT IS BAD ON POLE 306-51 C SEXTON IS IN ROUTE TO BRING ME A CUTOUT AND HELP // VER/TOM VER/DKG IDC XXXX
4980 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2021-06-17 12:04 | 2021-06-17 15:48 | 17 | 224 | 4763401 | 3808 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Found connection burnt open at weather head causing partial power. I made repairs and restored to full voltage @ 15:48
4981 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2009-07-07 17:07 | 2009-07-07 20:51 | 17 | 224 | 58782-1 | 3808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2150103-CC17---LOOP PULLED OUT OF HOT TAP , ARIEL SAW CUT LINE TODAY RELEASED BY CREW 080S04 IDC XXXX
4982 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-06-26 17:22 | 2011-06-27 00:25 | 9 | 423 | 4417791 | 3807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED TO SAFELY REPAIR PRIMARY NEUTRAL, OUTAGE FOR TICKET 4417111 VER/ARN IDCC TOF1722, PN121 XXXX
4983 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-06-01 12:37 | 2012-06-01 18:23 | 11 | 346 | 4861581 | 3806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE--TOP OF POLE BURNT OFF--IN BACK YARD--CAN GET EQUIPMENT TO IT--RAYBURN GETTING CREW RELEASED BY CREW 078S07// 45-4 POLE, PARSONS TECH//LMR/FOREMAN ON SITE/CREW ENROUTE/FETR1830/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1823/PLEASE CLOSE TICKET/THANKS/VEM // COD 11// VER/DBM IDC XXXX
4984 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2008-01-30 04:43 | 2008-01-30 10:00 | 12 | 317 | 61621-1 | 3804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED CREW//TRANSFORMER RISER BURNT OFF AT BUSHING/ OPEN WIRE NEEDS RESAGED/ IN DIRT ALLEY/ 4WD MATERIAL HANDLER SHOULD REACH IT// 371/2 TRANSFORMER NEED NEW RISER WIRE N TRANSFORMER IN CASE BUSHING DAMAGED RELEASED BY CREW 078S07//3001202-------POWER ON AT 1000 VER/KEP IDC XXXX
4985 | South Williamson | 3411401 | DEWEY | INEZ | 2018-12-11 19:31 | 2018-12-12 14:04 | 20 | 1113 | 4555311 | 3801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 838-D-98 broke just above telephone//no truck access//across creek up on hill//cutout open on pole 838-9001//can restore all but 2 cust.and their okwith waiting til daylight//need 45 class 5 pole//single phase 19.9 double dead end material//#2 al wire//restored up to 838-9001 at 22:20// OPENED L/F BACK UP @ 1048 ON 1054// 838-3 fuse off @ 1334 ON @ 1404
4986 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2016-09-30 13:40 | 2016-09-30 16:50 | 20 | 190 | 4948981 | 3800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED 40T ON 69D16001 @ 13:40, POLE 69D16025 TOP BURNT OFF. NO TRK,,CREW ON SITE,,ONLY LOST ABOUT 8 OF POLE TOP. WILL BE ABLE TO INSTALL RIDGE PIN AND HAVE PROPER CLEARANCE..ALL POWER RESTORED/ ISO 38830069D16001/ COD 20/ VER/BOW AJB
4987 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2013-02-01 10:12 | 2013-02-01 11:52 | 38 | 100 | 4781731 | 3800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | B PHASE IS OFF ON MAIN NORTH BIG CREEK ROAD. B PHASE ONLY RELEASED BY CREW 079H06 ///VER/CRB L/3 CRB IDCC CNT108 XXXX
4988 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-02-15 13:55 | 2012-02-15 16:06 | 29 | 131 | 4350761 | 3799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT 1148-1558 BAD LA POLE 1124-1550 REPAIRED INSTALLED 10T TRANS FUSE AND CUTOUT ON 1124-1545 OLD CSP TRANS. ///VER/CRB IDC XXXX
4989 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-04-15 06:28 | 2014-04-15 13:30 | 9 | 422 | 4605411 | 3798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW AND TECH POLE 38830066000077 BURNT OFF RELEASED BY CREW 078S07.. CREW ON SIGHT.. POLE REPLACED AND TICKET COMPLETE..20T LINE FUSE BACK ON AT 13:30 VER/CRB IDC XXXX
4990 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-02-08 01:29 | 2011-02-08 14:15 | 17 | 766 | 55159-1 | 3797 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON POLE 38830429B00030 PATROLLING LINE 0222 ** UPDATE AT 0300 FUSE DID NOT HOLD ** SERVICER PATROLLING. 0222 LIFTED HOTTAP AND TRANSFORMER ON POLE 38830429B00188 CLOSED FUSE ON POLE 429-30 AT 0400 CREW WILL RETURN AT DAYLIGHT TO PATROL REST OF LINE AND MAKE REPAIRS INSTALLED 12T FUSE AT POLE#188 MD FILED VER/KEP IDC GOT GO TRACK FROM PIKEVILLE XXXX
4991 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-04-23 04:32 | 2012-04-23 08:45 | 15 | 253 | 4695191 | 3795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ON POLE 262-221 FAILED APPEARED TO HAVE BROKEN CHANGED FUSE AND RE-ENRGIZED LINE // COD-15 ISO LF 38830262000221 VER/HFP L3/HFP IDC XXXX
4992 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-03-19 05:41 | 2021-03-19 10:12 | 14 | 271 | 4352061 | 3794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | /fuse open 351-105 primary down at pole38830351000125
4993 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-11-22 16:40 | 2019-11-22 16:57 | 223 | 17 | 4057251 | 3791 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SWITCH ON POLE 38830655B00106 ARCING //GOING TO OPEN GOAB ON POLE 38830654B00456//COD 832//OUTAGE WILL LAST APPROX 1 HOUR//300 amp solid switch is bad on p-655-106.opening switches on p-654-456 to chg OPENED @ 1640 CLOSED 1657//THE OPEN POINT BETWEEN THE INDEX-WEST LIBERTY AND FALCON -SALYERSVILLE IS BEING CHANGED DAILEY AS THEY RECONDUCTOR IN THIS AREA
4994 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-01-13 11:25 | 2017-01-13 19:29 | 34 | 484 | 4294791 | 3784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4296181*** OPENED LF @ 39831123D37126 @ 1125 (34 CUST), POLE FIRE @ 1123-7212. WINDSTREAM POLE/ /LIFTED HT ON XFMR BANK/WILL NEED TO CHG POLE/DIFF LOCATION/WILL NEED TO OUTAGE FUSES ON 1123-7126 FOR TWO TO THREE HOURS/VEM/ 39831123D37126 ON @ 1305 (33 CUST) UP TO 39831123D37212/ 39831123D37212 ON @1305 (1CUST) MADE MD TO SHOW L/FOPENED LF @ 1123-7126, POLE FIRE @ 1123-7212. WINDSTREAM POLE RELEASED BY CREW 078S07/LIFTED HT ON XFMR BANK/ VER/CRB L3/HFP HFP AJB
4995 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2008-06-04 12:42 | 2008-06-04 13:17 | 108 | 35 | 56118-1 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3417602//, ON SITE, PATROLLING LINE//FUSE MELTED OUT//COD 108// VER/DBM
4996 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-03-13 01:35 | 2015-03-13 01:42 | 540 | 7 | 4189091 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | OPENED RECLOSER TO SAFELY BYPASS RECLOSER 38830292C00325 ON PO#4188881 OPENED 0135 CLOSED 0142 COD-540 CALL AT 2118 SAW OPERATION WHEN RECLOSER OPERATED VER/KEP IDCC TOF0135 3/12 XXXX AJB
4997 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-07-03 00:44 | 2022-07-03 13:20 | 5 | 756 | 4368011 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Crew required in the a.m. Bad 25 KVA transformer on 834-448 - no truck access, behind address 117 Cherry Hill Ln. Released by crew 076S02// REPAIRS MADE // ON @ 13:20
4998 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-12 17:44 | 2008-04-12 19:50 | 30 | 126 | 50643-1 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CALLED LINKOUS//REPLACED CUTOUT AND ARRESTOR VER/HFP IDCC CDC92 XXXX AJB
4999 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-06-16 20:30 | 2019-06-17 11:20 | 8 | 890 | 4516001 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25kva no trucks Released by crew 078S03 Lifted hot tap on pn 38830045A41710 at 10:25 changed kva and restored power at pn38830045A41710 at 11:20 ALL POWER RESTORED//COD 4 FROM THE BEGINNING OF OUTAGE
5000 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2022-02-14 07:50 | 2022-02-14 12:20 | 14 | 270 | 4479851 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | i have a bad transformer on pole 1062A-248. talked to myles and he is going to bring a crew and 25kva and head this way Released by crew 079S03// replaced xfmr & c/o //on @ 12:20
5001 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-12-01 05:13 | 2020-12-01 07:28 | 28 | 135 | 4733931 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | L/F 728-15 & riser fuse 728-28 was both blown/// Padmount xfmr 728-A2-69 is bad.Isolated cable that feeds @ padmount 728-A2-70 and tagged to Rick Ray. Closed L/F 728-15 @07:28 and riser fuse 728-28 @08:15 this restored all but 3 customers that are fed from bad pad. NO GROUNDS PLACED Released by crew 076S03. CHANGED X-FMR RESTORED POWER AT 11:00
5002 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-02-28 13:28 | 2017-02-28 17:40 | 15 | 252 | 4428621 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOAD SIDE CUTOUT BROKEN ON STEPDOWN XFM. POLE37830237B00169..WILL MAKE REPAIRS..CUTOUT MADE CONTACT WITH SIDE OF STEP-DOWN XFM. AND BLOWED HOLE IN SIDE OF XFM.TIM HALL IS SENDING CREW TO MAKE REPAIRS.. RELEASED BY CREW 074S01 VER/CRB
5003 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-01-13 04:41 | 2016-01-13 12:05 | 15 | 444 | 4615591 | 3780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DDC HOLD TAGS// POLE 267-2 CREW REQUIRED WITH FLAGGERS TRUCKS OK #2 ACSR/OPENED LOOP ON 267-1 TAGGED TO DDC NO GROUNDS/268-79 20T BACK IN AT 0645 HRS RELEASED BY CREW 078S03//1112 GAVE RON VIRGIN PERMISSION TO REPLACE DDC TAGS WITH HIS OWN//DDC HOLD TAGS// POLE 267-2 CREW REQUIRED WITH FLAGGERS TRUCKS OK #2 ACSR/OPENED LOOP ON 267-1 TAGGED TO DDC NO GROUNDS/268-79 20T BACK IN AT 0645 HRS RELEASED BY CREW 078S03-- VER/CRB AJB
5004 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-07-20 20:16 | 2008-07-21 17:15 | 3 | 1259 | 54746-1 | 3777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 2206403//214-177 LOOPS BURNT OPEN//L MCCARTY TO SEND CREW//POLE 214-177 PRIMARY LOOP OPEN.POLE 214-177 PRIMARY LOOP OPEN. OPEN FUSE ON POLE 216-16 TIME OFF 17:10 ON @ 17:15 RELEASED BY CREW 078H12//COD 3//ISO// VER/DBM IDC XXXX
5005 | Paintsville | 3401802 | INDEX | HOSPITAL | 2017-03-02 11:43 | 2017-03-03 19:10 | 2 | 1887 | 4499881 | 3774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR.TRUCK ACCESSIBLE..ONLF FEEDS A STREET LIGHT.654-28.CORNER OF OSCAR LANE AND HARRIS LANE RELEASED BY CREW 076S01 VER/CRB
5006 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-06-19 19:17 | 2014-06-20 16:15 | 3 | 1258 | 4116411 | 3774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFORMER ON POLE 92-241 (7200 ) NO TRUCKS TO POLE .HAVE CREW MOVE CUTOUT OFF XARM MOUNT ON POLE. NEED 4 MAN LINE CREW. RELEASED BY CREW 078S01-- COMPLETE/SNC // COD 3// VER/DBM
5007 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-09-15 07:47 | 2012-09-15 17:24 | 12 | 577 | 4049741 | 3772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE APPEARS BLOWN ON POLE 38831027C00402 CSP XFMR BAD ON POLE 38831027C00501 ISOLATED XFMR, GOING TO TRY LINE FUSE CLOSED LINE FUSE @ 10:50, THIS RESTORES ALL BUT POLE POLE 1027-501 PULLED SERVICER TO HELP SWITCH ON 4050131 CREW ONSITE MAKING REPAIRS ALL POWER RESTORED @ 17:24 //COD 12// VER/DBM IDC XXXX
5008 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-09-17 16:15 | 2018-09-18 13:18 | 11 | 1263 | 4120491 | 3768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | crew required.line fusr out on 30-19.primary pole 31A31 broken TA.need 40-5 pole 25 7200 kva trans,cuutout and bracketannd deadend insulator. isolated tap at 31A32 crew will make repairs tomorrow customer is not staying at residence at this time.restored at 18:33 Released by crew 079H03
5009 | Pikeville | 3407102 | TOPMOST | CANEY | 2009-05-26 15:03 | 2009-05-27 00:01 | 7 | 538 | 52064-1 | 3766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP COD-56 // AT 1606 OPENED FEEDER - OPEN LINE SW 161D-220 THEN CLOSED FEEDER AT 1607 RESTORING 3 CUSTOMERS // RELEASED BY CREW 074S03 ON AT 12:01 D SAMMONS L3/HFP IDC 3/11/10 MOVED 55 CUSTOMERS TO BECKHAM CARR FORK PERMANENT LOAD TRANSFER ON 3/27/09 XXXX
5010 | South Williamson | 3200301 | BELFRY | BELFRY | 2018-05-16 22:35 | 2018-05-16 22:50 | 251 | 15 | 4362951 | 3765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | was reported a cutout was arching opened // recl 38821014C10632 to safely replace cutout on pole 38821014D00225 // opened @ 2235 closed @ 2250 // no customers out until recloser was opened /// L3/HFP
5011 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-07-01 13:54 | 2021-07-01 17:56 | 45 | 242 | 4836441 | 3762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4 solid sleeve pulled loose at pole 38830334b00048, not buy truck no tree crew needed could use flaggers Released by crew 078H03 opened and tagged rec 334-A0-141 at 17:12 Closed at 17:56 Released by crew 078H11
5012 | Whitesburg | 3401301 | FLEMING | NEON | 2014-02-06 03:42 | 2014-02-06 10:40 | 9 | 418 | 4361401 | 3762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS IS ACTUALLY ON POLE 37830355D40069 50 KVABAD 50 KVA 7200 XFMR, WE NEED CREW AND MATERIAL HANDLER BUCKETBAD 50 KVA 7200 XFMR, WE NEED CREW AND MATERIAL HANDLER BUCKET RELEASED BY CREW 077S12//MADE MDC// IDCC PN58 XXXX
5013 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-07-12 12:44 | 2009-07-12 13:03 | 198 | 19 | 62986-1 | 3762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP RELATED TO ORDER 62545-1 ~ CREW HAD TO OPEN RECLOSER TO MAKE REPAIRS TO PHASE THAT HAS COME OFF INSULATOR AND LAYING ON CROSSARM /// COD-198 ISO REC 37830394B00225 L3/HFP AJB
5014 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2011-05-13 20:48 | 2011-05-14 09:20 | 5 | 752 | 4088141 | 3760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | RELEASED BY CREW 074S02//CREW REQUIRED// MANUAL R/W CREW// TREES NEED CUT AROUND XFMR TO CHANGE BAD CLF RELEASED BY CREW 074H14 ONLY ONE CUSTOMER OUT OF POWER CREW WILL RETURN IN A.MRELEASED BY CREW 074S02//CREW REQUIRED// MANUAL R/W CREW// TREES NEED CUT AROUND XFMR TO CHANGE BAD CLF RELEASED BY CREW 074H14 ONLY ONE CUSTOMER OUT OF POWER CREW WILL RETURN IN A.M,,,,BAD CLF ALL REPAIRS MADE POWER BACK ON, MAP # WRONG ONLY 1 CUST OUT
5015 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-02-24 12:45 | 2022-02-24 16:40 | 16 | 235 | 4540291 | 3760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CHANGING ROTTEN POLES 38831016000059 //off@1245 on@1640
5016 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-08-28 18:56 | 2017-08-29 01:12 | 10 | 376 | 4306001 | 3760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER SAID LOUD NOISE AND SOMETHING FELL OFF POLE..BROKEN CUTOUT BETWEEN PHASES ON ARM, NEED 2 MEN TO CHANGE,,, RELEASED BY CREW 076S01// REPAIRS COMPLETE, RESTORED AT 01:12 VER/KEP L3/HFP XXXHFP SJG
5017 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-01-07 09:43 | 2013-01-07 10:30 | 80 | 47 | 4574171 | 3760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BLOWN LINE FUSE ON POLES 38830182B22534 AND 206-1-0054, REPLACED FUSE ON POLE 2534 AND REPLACED BURN UP CUTOUT ON POLE 206-1-0054, PATROLED LINE AND FOUND NO HAZARDS, ALL POWER RESTORED VER/KEP IDC XXXX
5018 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-03-31 12:01 | 2014-03-31 15:00 | 21 | 179 | H4547861 | 3759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 4547861//OPENED B & C @ 1313//COD +11//BAD CUTOUT BURNED ALLEY ARM BRACE OFF AND IT WENT BETWEEN PHASE B AND C. I OPENED PHASE A & C RECLOSER ON POLE 38820939C00020 AT 13:13, PHASE B WAS ALREADY OPENED. JOEY IS ENROUTE TO REPLACE THE ARM AND CUTOUT. RELEASED BY CREW 079S02.MADE REPAIRS.REPLACED ARM AND CUTOUT.// VER/DBM IDC XXXX
5019 | Hazard | 3303902 | LESLIE | WOOTON | 2019-05-27 00:15 | 2019-05-27 21:07 | 3 | 1252 | 4346471 | 3756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #2 acsr down at 37830340000037, broke at d.e. clamp, need 4 man line crew and 2 manual row crews, very manual and down across macintosh creek and steep hillside near mortons farm Released by crew 077E10/ ISO 37830340000037/ COD 3
5020 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-04-11 09:09 | 2008-04-11 14:33 | 12 | 324 | 66004-1 | 3756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 473-77 VER/HFP MLRC CNT STEP 1 - 12
5021 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-02-21 21:31 | 2011-02-21 22:53 | 57 | 82 | 59956-1 | 3756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38888980 // CUTOUT BROKEN ON POLE 247-774 ONLY FEEDS STREET LIGHTS, WILL REPAIR 02=22=11 IDCC CNT63 XXXX
5022 | Hazard | 3303901 | LESLIE | HYDEN | 2010-03-20 16:46 | 2010-03-20 19:05 | 27 | 139 | 52034-1 | 3753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKE POLE PULLED OVER LETTING B PHASE AND NEUTRAL CONTACT EACH OTHER. TRYING TO PULL POLE BACK.//// REPULLED GUY ,POWER RESTORED. WILL SEND JOB TO DOUG CHRISTIAN, FOR REMOVAL//COD 27//ONLY B PHASE RECLOSER OUT// VER/DBM IDC XXXX
5023 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-03-26 17:51 | 2015-03-27 11:24 | 28 | 1053 | 4232281 | 3753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF AT POLE 37820032D00147. I ISOLATED THE POLE, THE TRANSFORMER HERE IS TO A VACANT TRAILER. I TALKED TO THE PROPERTY OWNER AND THIS CAN WAIT TILL TOMARROW TO BE REPAIRED. ALL POWER IS BACK ON EXCEPT FOR THE ONE VACANT TRAILER. RELEASED BY CREW 079S02. MADE REPAIRS TO/CLOSED 1931, LAST CUSTOMER 1124// VER/ ADH AJB
5024 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-03-15 15:31 | 2008-03-15 17:50 | 27 | 139 | 57499-1 | 3753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3 MAN CREW NEEDED TRUCKS OK 4 OR 6 A WIRE/CREW ON SITE/FETR 1915/REPAIRS MADE AND POWER RESTORED/1750/PLEASE CLOSE TICKET/VEM VER/HFP IDCC CCO XXXX
5025 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-09-07 02:00 | 2014-09-07 02:15 | 250 | 15 | 4476161 | 3750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FIELD PERSONS HAVE TO OPEN RECLOSERS TO SAFELY MAKE REPAIRS TO CENTER PHASE CONDUCTOR WHERE LOOP HAS BURNT OPEN// FROM START IF ALL GOES WELL SHOULD TAKE NO MORE THAN 30 MINUTES TO MAKE REPAITS// WILL UPDATE AS NEEDED// ASSOCIATED WITH OUTAGE 4475851// THIS HAS A & C PHASES INTERRUPTED AND B PHASE CUSTOMERS UP TO OPEN LOOP// 250 CC - OPENED @ 0200 CLOSED @ 0215 RESTORING ALL CC VER/HFP L3/HFP AJB
5026 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-10-09 08:05 | 2009-10-09 12:15 | 15 | 250 | 66454-1 | 3750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | (WREQUEST 32130511) POLE 140-579 BURNT OFF 50 CLASS 2 19.9 INS. CUTOUT LA T-BRACKET SEND TO JOE HEMLETT LINE FUSE ON 140-512 RELEASED BY CREW 078S08/ CREW ON SITE J. HEMLEPP // VER/TOM IDC XXXX
5027 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-12-16 04:19 | 2019-12-16 06:24 | 30 | 125 | 4156911 | 3750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bottom side of cutout burnt in clear// repaired and power restored at 06:24
5028 | Cannonsburg | 3000101 | ASHLAND | 25-25STREET | 2018-08-05 12:10 | 2018-08-05 16:13 | 16 | 243 | 4910651 | 3748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ad 7200, 50 kbva xfmer. alley between lex. & hilton. 24th side.trk ok. Released by crew 078S07//opened trans @ 1210//NO OUTAGE TILL THEN//crew on site/FETR 1730/vem/10 cust restored at 1559 from pole 45-D3-7212/6 cust restored at 1613 from 45-D3-7213/please close ticket/thanks/vem Released by crew 078H14//v mullins is sending everything to mapping
5029 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2011-05-01 08:20 | 2011-05-02 05:09 | 3 | 1249 | 53108-1 | 3747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS W#39771912 SEND TO JIM LINKOUS RELEASED BY CREW 078S08 //VER/GAH IDC XXXX
5030 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-06-18 09:53 | 2013-06-18 11:40 | 35 | 107 | 4363661 | 3745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HIGH SIDE STEPDOWN BLEW CHECK REPLACE ARR. ON LOW AN OPEN LOW SIDE ,CHANGED CUTOUT ON HIGH SIDE REFUSE WITH 6T ,HIGH SIDE GOOD REFUSE HIGH SIDE AN CLOSED //VER/GAH IDC XXXX
5031 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2021-11-12 04:40 | 2021-11-12 09:28 | 13 | 288 | 4082801 | 3744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DDC TAGS DOL 1162598/Lifted HT @ pole 39831123C35022 @ 04:40, grounded and tagged to ddc. Pole 1123-c3-5023 in back yard still smoldering. Crew required, no trucks. Pole can be lowered @ this time. Released by crew 078S02 crew on site FETR 12:00 LRM all pwr restored pleasecloseLRM 09:28 (no outag till tap was lifted)
5032 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-02-22 23:11 | 2008-02-23 01:08 | 32 | 117 | 66399-1 | 3744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3408303///I THINK THE FUSE BROKE.//VER/CRB IDC XXXX
5033 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-03-07 14:39 | 2016-03-07 16:48 | 29 | 129 | 4824591 | 3741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON 24-401 NEED ONE MAN AND BIG BUCKET IN PRIMARY ZONE REPLACED CUTOUT RESTORED POWER AT 16:48 VER/KEP AJB
5034 | Hazard | 3309302 | VICCO | JEFF | 2019-02-08 16:11 | 2019-02-08 16:45 | 110 | 34 | 4770981 | 3740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | Ploe leaning need line crew and flaggers right pole #347D/194 between Couch dr. and Bridge ln. at wide spot pole on right of road telephone guy has pulled out Released by crew 077S03 will need to open rec 37830347A00316 phases wrappedPloe leaning need line crew and flaggers right pole #347D/194 between Couch dr. and Bridge ln. at wide spot pole on right of road telephone guy has pulled reC OFF 1611 ON 1645 L3/HFP
5035 | Hazard | 3310502 | HADDIX | CANOE | 2008-08-27 08:07 | 2008-08-27 17:25 | 7 | 558 | 55842-1 | 3736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310502// PATROLLED LINE // TRIED LINE ONCE, BUT DID NOT STAY//OPENED LOOP ON POLE 216-77, WILL TRY TO PUT POWER ON UP TO NEW ISOLATING PT// VER/DBM IDC XXXX
5036 | Paintsville | 3401802 | INDEX | HOSPITAL | 2015-02-20 02:49 | 2015-02-20 08:00 | 12 | 311 | 4046951 | 3732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE MELTED OUT.654-198..25T FUSE.UP TO A 40T.. // COD-3 ISO LF 38830654D00198 SENT ENGINEERING AN EMAIL ON THIS CHANGE AND WIL DO MD IF NECESSARY WHEN I HEAR BACK FROM THEM - HFP VER/HFP L3/HFP
5037 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-03-16 17:28 | 2014-03-16 18:09 | 91 | 41 | 4497871 | 3731 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER WAS CLOSE ON ARRIVAL SOURCE SIDE LEAD HAD BURNT STIRRUP INTO HAD TO REPLACE STIRUP AND HOT TAP APR AT 1809 CLOSE TICKET//COD 91// VER/DBM L3/HFP IDC XXXX
5038 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2011-09-03 07:49 | 2011-09-03 09:20 | 41 | 91 | 4790501 | 3731 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | <<PHASE B ONLY>> STIRRUP BURNT OFF ON RECLOSER RISER. REPLACED STIRRUP AND HOT LINE CLAMP. RESTORED @ 9:20. SH//COD 41// VER/DBM IDC XXXX
5039 | Hazard | 3302703 | HAZARD | HAZARD | 2021-01-25 10:32 | 2021-01-25 11:05 | 113 | 33 | 4889171 | 3729 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A primary tap on pole 272-D2-736 feeding towards pole 272-D2-1563 has broken in the deadend shoe and is now low but still energized near telephone lines. Reclosers on pole 296-A3-746 off at 10:32, restored at 11:05.
5040 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2013-10-04 15:19 | 2013-10-04 19:12 | 16 | 233 | 4911031 | 3728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON 235-31.CROSSARM BURNT OFF ON POLE 235-43.CAN USE TRUCK..NEED 8 FT ARM, 2 STEEL PINS AND INSULATORS, CUTOUT, ARRESTOR, AND CROSSARM MOUNT T BRACKET, BRACES.NO WIRE DOWN.FLOATING. RELEASED BY CREW 074H08 CREW ON SITE MAKING REPAIRS/ REPAIRS MADE SERVICE RESTORED AT 19:12 COD-16 ISO LF 37830235000031 VER/HFP L3/HFP IDC XXXX
5041 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-08-10 16:53 | 2009-08-11 08:25 | 4 | 932 | 58306-1 | 3728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP RELEASED BY CREW 078S07 BAD 25KVA TRUCK TO POLE WR/ 31161730 RELEASED BY CREW 078S08 COD-4 ISO TF 39831123B00266 L3/HFP IDC XXXX
5042 | Hazard | 3303902 | LESLIE | WOOTON | 2018-10-26 10:21 | 2018-10-26 17:15 | 9 | 414 | 4324981 | 3726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEAD END INSULATOR WENT BAD ON 438-121//L/F ON 37830438000028 OPEN //MADE MD TO SHOW THERE IS A C PHASE FUSE HERE ALONG WITH A PHASE //COD 9//DEAD END INSULATOR WENT BAD ON 438-121 CUTOUT GATE BURNT ON FUSE POLE Released by crew 077S01// ISO 37830438000028/ COD 9 L3/HFP
5043 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2010-04-27 11:49 | 2010-04-27 16:15 | 14 | 266 | 52080-1 | 3724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3 PHASE TAP OFF FROM SAME FUSE VER/KEP L3/KEP IDC XXXX
5044 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-02-25 06:22 | 2022-02-25 10:48 | 14 | 266 | 4543481 | 3724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | cutout went bad and burned top of pole 246-30 off wire is 3 foot high crossing the road, need 40 foot pole flying corner clamp 1 de unit and 2 de insularors 2 clevis and spools 7200 cutout and tee brkt, pole is manual but might can set new pole off old one took clamp off 246-25 got recloser in at 1048 Released by crew 077S05
5045 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-04-23 02:15 | 2017-04-23 17:00 | 15 | 885 | 4670131 | 3720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-953 BURNT OFF POLE 68-88 40T ON 04:45 AM POLE 68-953 NO TRUCKS 1-CUST OFF 4134 PINE TERRACE CT. OFF PINE ST. IRONVILLE NEED DAY LIGHT RELEASED BY CREW 078S08 13 CUST RESTORED 0445/ LEAVING 2 CUST OFF ON 38830068A00953 ISOLATED BY TAP ON 38830068A00591 CLOSED AT 1700 VER/AWD AJB
5046 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-11-22 22:26 | 2020-11-23 05:00 | 30 | 394 | 4716221 | 3720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout failed and caught deadend xfmr pole 1121-29 on fire Released by crew 078H03 Released by crew 078H07
5047 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-07-12 10:06 | 2021-07-12 14:24 | 16 | 258 | 4897981 | 3720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Opened line fuse 38830069A31043 due to transformer fire on pole 38830069A31059 (A phase customers were already out due to order 4897351 and B and C pghases opened at 1040)/// repaired and restored @1424
5048 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-02-09 04:56 | 2017-02-09 10:06 | 12 | 310 | 4374421 | 3720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUST/. B PHASE HOT LINE CLAMP BURNDT THROUGH THE STIRRUP @38831152000241, MAY HAVE TO OPEN THE OTHER 2 FUSES ON POLE 152-264 TO MAKE REPAIRS, POLE IS NOT TRUCK ACCESSIBLE. DID NOT HAVE TO OTHER 2 PHASES, MADE REPAIRS AND CLOSED B PHASE L/F @1006./ ISO 38831152000038/ COD 12/ VER/BOW L3/HFP XXXHFP
5049 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-01-09 00:47 | 2011-01-09 03:10 | 26 | 143 | 59990-1 | 3718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ASSOCIATED WITH POWERON ORDER 59981-1// OUTAGE ON POWELL CREEK // WIRE DOWN, BROKE BETWEEN POLES - SINGLE PHASE PRIMARY DOWN// THIS OUTAGE WAS NECESSARY TO DE-ENERGIZE CONDUCTOR TO SAFELY MAKE REPAIRS - WILL UPDATE FETR AS SOON AS FIELD PERSONNEL ARE ABLE TO PROVIDE // RESTORED AT 0310 VER/TOM IDC XXXX
5050 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2019-02-04 13:12 | 2019-02-04 16:01 | 22 | 169 | 4752891 | 3718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGH ARRESTOR ON @ 1601 L3/HFP
5051 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-11-18 10:06 | 2017-11-19 17:05 | 2 | 1859 | 4564561 | 3718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva CSP 7200 trans. on pole 1104-132, this will take a line crew, pole has no truck access and will need a 7200 c/o and bracket, this shoulb be worked in daylight hours. Released by crew 074S05 1705
5052 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2019-11-07 20:50 | 2019-11-08 01:36 | 13 | 286 | 4009091 | 3718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | No outage on arrival--pole fire at 39831098D00808-lifted hot tap at pole 39831098D00692 at 2050--Tagged to Bobby Reynolds and grounded. No trucks, back yard work, L3/HFP
5053 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-08-10 04:31 | 2012-08-10 04:38 | 531 | 7 | 4920881 | 3717 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RELEASED BY CREW 078S08 LOOP BURNED INTO INSIDE CSX, WILLREQUIRE TRANSMISSION BUCKET 4/0 AU WIRE, AND 4/0 TO 4/0 AU CRIMP WILL MAKE REPAIRS TO ALL PHASES// AT THIS POINT 167 CUSTOMER OUTAGED// RELEASED BY CREW 078S08 RELEASED BY CREW 078H02 IDC XXXX
5054 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-02-08 14:25 | 2011-02-08 16:04 | 47 | 99 | 55352-1 | 3717 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38739266 ///TOP OF POLE BURN OFF 1126-769, CUTOUT BROKE DOWN CAUSING POLE FIRE. NEED POLE TOP EXTENSION , AND CUTOUT AND ARESTORTOP OF POLE BURN OFF 1126-769, CUTOUT BROKE DOWN CAUSING POLE FIRE. NEED POLE TOP EXTENSION , AND CUTOUT AND ARESTOR. PART ON AT 15:25 COD-47 ISO LF 38831126A00585 VER/HFP L3/HFP IDCC TON1604 STEP 1 XXXX
5055 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-06-23 23:32 | 2015-06-24 15:00 | 4 | 928 | 4648471 | 3712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME . BAD CUTOUT ON POLE 552-45 . REPLACED CUTOUT , CLOSED XFMR BACK @ 15:00// VER/ ADH
5056 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-11-10 16:16 | 2008-11-10 17:20 | 58 | 64 | 63713-1 | 3712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP PLEASE DON`T FORGET THE FETR...THANKS A PHASE INITIALLY OUT 58 CUSTOMERS @ 1645 OPENED B&C PHASES 62 CUSTOMERS.RISER OFF RECLOSERRISER OFF RECLOSER//REPLACED CLAMP ON RECLOSER AND RESTORED POWER MAF
5057 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2012-06-27 15:39 | 2012-06-27 19:05 | 18 | 206 | 4968761 | 3708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED PRC CREW--CAN USE BUCKET--HOT TAP LEAD BURNT OUT OF B PHASE LINE FUSE CUTOUT--CUTOUT NEEDS REPLACED RELEASED BY CREW 078S07.REPAIRS MADE..POWER ON @ 19:05.BLR //VER/CRB L/3 CRB
5058 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2018-07-23 12:58 | 2018-07-23 23:16 | 6 | 618 | 4841441 | 3708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase line fuse blown on pole 184-201, calling for Asplundh crew to cut path to pole, was checking fuse on A phase and cutout broke opened rec on pole 231-329 to isolate broke cutouts on pole 184-201. opened at 22:22 and closed back in at 22;36. all power restored at 23:16 please send ticket to D. Christian, every time wind blows the least bit hard these fuses blow, need pole in long span going to baseball field//cod 6//emailed to techs L3/HFP
5059 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-05-27 22:34 | 2016-05-28 02:00 | 18 | 206 | 4266871 | 3708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT//// POWER RESTORED @ 02:00
5060 | Pikeville | 3407103 | TOPMOST | KITE | 2017-03-21 04:43 | 2017-03-21 08:50 | 15 | 247 | 4574031 | 3705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 14 ISOLATED , TAGGED FOR G. JUSTICE, AND GROUNDED .POLE 18 BURNED APART AT CUTOUT BRACKET, I WILL BE ABLE TO LOWER PRIMARY AND RESAG, NO CREW REQUIRED . ALL WORK COMPLETE / GXJ COD-15 ISO LF 37830233000014 VER/HFP L3/HFP
5061 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-01-31 06:33 | 2013-01-31 14:16 | 8 | 463 | 4770001 | 3704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQUIRED PRIMARY ONLY TRUCK OK TO POLE 271-88/#4 SOLID COPPER BROKE IN RUNAROUND/LEFT ORANGE FLAG AT ENTRANCE/FUSE OPEN ON 272-73 TAGGED TO ASH LINE RAYBOURN RELEASED BY CREW 078S03 RAYBURN TAG REMOVED, INSTALLED TAG TO JENT//LMR IDCC CCWW XXXX
5062 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-08-04 19:11 | 2012-08-05 03:10 | 17 | 479 | 4897421 | 3703 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WELL I HAVE A POLE BURNTED OFF, POLE NUMBER 879F-321, I CUT LOOP AND INSTALLED HTSP ON POLE 879-320 AND GROUNDED LINE AT THIS POLE, ALSO 879-F-321 IS A 40/5 POLE EVERYTHING WILL WORK BACK, JUST NEED NEW CUTOUT, WELL BE CREW REQ, ALSO NEED TO SEND A TECH PHONE CO POLE, 7TH HOUSE ON THE RIGHT ON CLIFFORD LOOP.ALSO REMOVED TREE LIMB FROM POLE 879-294 (ALL POWER RESTORED AT 03:10) VER/KEP IDC XXXX
5063 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-09-24 22:55 | 2010-09-25 01:12 | 27 | 137 | 53401-1 | 3699 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TIME ON IS 0112AM CUTOUT FAILURE //VER/GAH IDC XXXX
5064 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-03-02 08:32 | 2010-03-02 08:41 | 411 | 9 | 62105-1 | 3699 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | SEE ORDER 62082 AND 62126 VER/KEP L3/KEP IDC XXXX
5065 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-11-30 08:10 | 2011-11-30 10:58 | 22 | 168 | 4129021 | 3696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | CENTER PHASE RECLOSER MIGHT BE BAD // COD 22 // BYPASSED REC AT 1058 PICKED UP ALL BUT TAP AT 144-297 COD-1 AT 1058 //LEAVING FOOTBALL FIELD OFF PER CUSTOMER REQ // PLACED RECLOSER IN ABNORMAL DB // VER/DBM IDC XXXX
5066 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-08-29 19:04 | 2010-08-30 00:40 | 11 | 336 | 61721-1 | 3696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED #4 COPPER PRIMARY ONLY FROM 181-53 TO 54 BROKE AT BASKET ON THE HILL NO TRUCK TO THAT POLE/181-18 IS LINE FUSE SEND TO REYNOLDS RELEASED BY CREW 078S03 //VER/GAH IDC XXXX
5067 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-07-09 22:22 | 2010-07-10 00:56 | 24 | 154 | 64526-1 | 3696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER BLOWN NEXT TO XFMER CUTOUT ON ONE PHASE OF BANK ON 966-B-604...DONT THINK FUSE IS BLOWN....WILL RAISE UP ABOVE LIGHTS TO TAKE CLOSER LOOK...//...MIDDLE PHS FUSE BLOWN....ARRESTER ON LEFT PHASE BLOWN UP....ALL 3 ARRESTERS NEED REPLACED....NEED CREW....R MARCUM CALLED....GETTING CREW...//...OPENED BLADES ON 966-B-629 @ 00:12..REPLACED 3 ARRESTERS, & ONE CUTOUT ON POLE 966B604.....CLOSED BLADES ON 966B629 @ 00:56....ALL OK....JRV....07/10/10 IDC XXXX
5068 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-01-03 11:12 | 2021-01-03 12:40 | 42 | 88 | 4845281 | 3696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 38830188C00180 rec line side sturup failed--temp repair-in at 12:40-ds010321
5069 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-11-18 22:46 | 2017-11-19 11:05 | 5 | 739 | 4573091 | 3695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Primary riser burnt off of xfmr cutout. Replaced xfmr cutout, primary riser and hot-line clamp. Restored @ 11:05. sh
5070 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2011-02-05 13:47 | 2011-02-05 20:43 | 53 | 416 | 54260-1 | 3692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WR# 38705920 // POLE 69-4757 POLE BROKE, ROTTEN//CREW REQUIRED//ISOLATED AT FAULT POLE AND RESTORED MAIN LINE @ 1450//COD 53// NEED 45 CLASS 5 15KVA OIL SPILL BAG//COD 53 VER/KEP IDC XXXX
5071 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-05-05 06:15 | 2019-05-05 13:19 | 25 | 424 | 4223671 | 3691 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole burned off at 39831123B00497 (Crew Required) Trucks to pole, can lower everything, Loop cut on pole 1123-491, and ground placed. Customers at 1123-497 and at 1123-B1-8065 still off. Line fuse on 1123-475 closed in at 07:50 partially restoring customers. Tagged to rick morgan at 1123-491 Released by crew 078H04//arrived RM hot tap on @ 13:19 lease close tic RM ¦¦¦ PER GATLIN HICKS A CUTOUT FAILED CAUSING THE POLE FIRE - L3/HFP
5072 | Hazard | 3310502 | HADDIX | CANOE | 2015-05-19 15:22 | 2015-05-19 17:25 | 30 | 123 | 4446241 | 3690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RECLOSER OUT ON POLE 144-45 , FOUND BAD ARRESTER ON POLE 120-37 .CLOSED RECLOSER @ 17:25/MADE AED/ADH/COD 30// VER/ ADH L3/DKGXXX AJB
5073 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-05-25 08:25 | 2011-05-25 14:55 | 21 | 390 | 4165261 | 3690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT ON 57A28/BAD CUTOUT/BURNT OFF POLE TOP ON 57B84/NEED CREW/WILL EXTINGUISH FIRE & WILL ISOLATE BY OPENING SOLID BLADE LINE CUTOUT ON 57B41 & THEN RE-FUSE CUTOUT ON 57A28.....//...CREW ENROUTE FR PKVLLE...CLOSED LINE FUSE ON 57A28 ENERGIZING LINE UP TO OPEN CUTOUT ON 57B41 @ 10:45...//....REPAIRS MADE....CLOSED CUTOUT ON 57B41 @ 14:55....PICKING UP REMAINING CUSTOMERS...JRV...05/25/11 //COD 21// VER/DBM L3/WDH
5074 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-03-21 06:10 | 2013-03-21 13:00 | 9 | 410 | 4943531 | 3690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OVER LOADED 50 KVA REPLACING WITH 75 KVA--TIM SMITH CREW ON THE WAY RELEASED BY CREW 077S10 ON SITE WORKING IDC XXXX
5075 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-11-07 16:09 | 2013-11-07 19:20 | 27 | 191 | 4020201 | 3687 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MASSEY, CAMPBELL & GARRETTPOLE 1126-830 BURNED OFF AT TOP..ISOLATED FAULT ON POLE 1126-874.XFMR ON POLE 874 IS OFF ALSO.CLOSED STEPDOWN ON POLE 1126-972 AT 17:35..NEED 3 MAN CREW, BIG BUCKET, POLE TOP EXT. , CUTOUT, ARRESTOR, AND BRACKET.CAN TRUCK. RELEASED BY CREW 074H08 CREW ON SITE RESTORED 19:20 RELEASED BY CREW 074S10 COD-27 VER/HFP L3/HFP IDC XXXX
5076 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-12-04 23:43 | 2010-12-05 13:45 | 22 | 842 | 63190-1 | 3684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQEUSTS # 37990237// ISOLATED AT POLE 37830138000091, POWER RESTORED AT POLE 90 AT 01:23 ... POLE 187 IS 45-4 POLE , CAN LOWER PRIMARY AND GUYS TEMP., 25KVA ON POLE SERVES OL ONLY ( MAY OR MAY NOT BE ACTIVE) SQUIRT BOOM ONLY AND THREE MEN / GXJ RELEASED BY CREW 074S03WORK REQEUSTS # 37990237/ ... OPENED AT POLE 90 AT 13:30 ALL CUSTOMERS RESTORED AT 13:45 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03//COD 22// VER/DBM IDC DCMT XXXX
5077 | Pikeville | 3421001 | BREAKS | CITY | 2014-10-06 18:52 | 2014-10-06 21:20 | 25 | 148 | H4559121 | 3680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FELL BURNED CROSSARM// NEED 3 MAN LINE CREW WITH BIG BUCKET AJB SEE 4559121
5078 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-06-02 19:13 | 2013-06-02 20:45 | 40 | 92 | 4211181 | 3680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-40 ISO PO @ 38831078000069 VER/HFP L3/HFP IDCC PN8 XXXX
5079 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-02-22 04:00 | 2009-02-22 05:15 | 49 | 75 | H50115-1 | 3675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409002 - FOUND C PHASE RECLOSER AT POLE 784-68 OPEN INTERRUPTING 68 CUSTOMERS. WIRE DOWN - DIFFICULT LOCATION. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. CLOSED PH C REC ON POLE 68 AT 02:10 RESTORING CUSTOMERS UP TO SW ON POLE 783-118. OPENED OTHER TWO SWS AT 0400 AND RESTORED ALL CUSTOMERS RESTORED AT 0515 //VER/GAH IDCC CNT100 XXXX
5080 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-12-08 15:05 | 2010-12-08 16:20 | 49 | 75 | 64453-1 | 3675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT ON 941-B-110.....//....LINE LOOKS OK...NO HAZRDS...WILL RE-FUSE....//....BAD CUTOUT DOOR...DETERIORATED....CAUSED FUSE TO OVERHEAT & MELT OUT....REPLACED DOOR & RE-FUSED.....JRV...12/08/10//COD 49// VER/DBM IDC XXXX
5081 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-05-11 08:20 | 2013-05-11 17:05 | 7 | 525 | 4102701 | 3675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F OPEN ON 841-148// POLE TOP BURNED OFF ON 841-123 // WILL NEED TO CHANGE POLE // NEED CREW // REED & THOMAS & JUSTICE & HAWKINSL/F OPEN ON 841-148// POLE TOP BURNED OFF ON 841-123 // WILL NEED TO CHANGE POLE // NEED CREW RELEASED BY CREW 074S05 COD-7 ISO LF 38820841A00148 VER/HFP L3/HFP IDC XXXX
5082 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-12-20 20:02 | 2012-12-21 16:27 | 3 | 1225 | 4494181 | 3675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 1124-2044 OPEN WIRE NEEDS RESAGED ALL THREE SERVICES ON POLE DAMAGED NO TRUCK GO PAST POLE 1124-2008 TO FIRST HOUSE ON RIGHT TO GET TO POLE EASYER RELEASED BY CREW 078S08 ////VER/CRB L/3 CRB
5083 | Whitesburg | 3312901 | JENKINS | KONA | 2014-06-28 09:43 | 2014-06-28 12:10 | 25 | 147 | 4164421 | 3675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE SPAN OF 8A PRIMARY CONDUCTOR DOWN LEAVING POLE 404-79 WILL BE PUTTIN WIRE BACK UP. PUT WIRE UP & RESTORED POWER AT 1210//WIRE BURNT DOWN//NO ROW ISSUES EVIDENT//COD 25// VER/DBM AJB
5084 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-03-23 19:17 | 2011-03-23 21:05 | 34 | 108 | 57988-1 | 3672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOW SIDE FUSE ON STEPDOWN TRANS. AT POLE#-168-144 IS BLOWN. I AM PATROLLING LINE NOW. PRI. CONDUCTOR WAS OFF INSULATOR AT POLE 168-32. I TIED CONDUCTOR BACK ON INSULATOR AND I GOING TO TRY FUSE AT STEPDOWN. I CLOSED LOW SIDE STEPDOWN FUSE IN AT 21:05 AND IT STAYED. IDCC FP144, CDC92 XXXX
5085 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-07-25 03:27 | 2020-07-25 06:00 | 24 | 153 | 4230141 | 3672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | The cutout on pole 37830538000040 is really loose/ couldnt hardly get it to stay shut/ the cutout may open back up in the near future/ servicer is going to make an order to have cutout changed/ Power restored 0600/ ISO 37830538000040/ COD 24
5086 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-02-07 16:26 | 2017-02-07 16:35 | 408 | 9 | 4367521 | 3672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CAPACITOR | EMERGENCY OUTAGE NECESSARY TO ALLEVIATE SYSTEM CONDITION// OUTAGE SHOULD BE 30 MINUTES// DUPLICATE OUTAGE VER/TOM L3/TOM L3/HFP HFPC MCCNI CCDOT FEC57 AJB
5087 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-06-08 08:28 | 2020-06-08 13:34 | 12 | 306 | 4978541 | 3672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN @ POLE 37830226000037, APPEARS TO HAVE PULLED OUT OF SLEEVE, CREW ENROUTE//COD 12
5088 | Paintsville | 3401802 | INDEX | HOSPITAL | 2010-06-12 08:27 | 2010-06-12 09:35 | 54 | 68 | 60585-1 | 3672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" PHASE CUTOUT BROKEN//COD 54 //CUTOUT BROKEN...654-219...CHANGED CUTOUT...BB// VER/DBM
5089 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-05-23 00:05 | 2014-05-23 06:12 | 10 | 367 | 4743401 | 3670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 426-635, WILL NEED BIG BUCKET TO REPLACE.OPENED LINE FUSES ON POLE 426-635 AT 02:19 TO ISOLATE . KENNY LITTLE TO ASSIST // BAD CUTOUT ON POLE 426-635, WILL NEED BIG BUCKET TO REPLACE.OPENED LINE FUSES ON POLE 426-635 AT 02:19 TO ISOLATE . RELEASED BY CREW 077S11 //VER/GAH
5090 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-02-18 12:51 | 2015-02-18 16:04 | 19 | 193 | 4039241 | 3667 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PHASE A ONLY//COD 19// REPLACED CUTOUT AND JUMPER, ALL WORK COMPLEE / GXJ// VER/DBM L3/HFP XXX
5091 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-08-19 08:08 | 2015-08-19 09:26 | 47 | 78 | 4151211 | 3666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL RECLOSER OPENED @ 0808//CUT OUT BROKE ON POLE # 74-204 WHICH CAUGHT POLE ON FIRE/// OPENED RECLOSER UP ON POLE # 589 @ 8:08 TO PUT FIRE OUT AND CHANGE CUT-OUTCUT OUT BROKE ON POLE # 74-204 WHICH CAUGHT POLE ON FIRE/// OPENED RECLOSER UP ON POLE #73-589 @ 8:08 TO PUT FIRE OUT AND CHANGE CUT-OUT/// CHANGED BAD CUT OUT AND PUT POLE FIRE OUT/// CLOSED RECLOSER IN @ 09:26 AND RESTORED SERVICE VER/CRB L3/HFP XXXHFP AJB
5092 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-05-27 18:27 | 2022-05-27 23:09 | 13 | 282 | 4971621 | 3666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 38821130000022 got it replaced and back on at at 23:09//cod 13
5093 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-08-29 01:21 | 2017-08-29 11:32 | 6 | 611 | 4306311 | 3666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40` C5 POLE 38830223000169 (PER MAP) BURNT OFF NEED CREW // SEND TO BOBBY TACKETT/TAGGED AT LINE FUSE TO TACKETT AND PLACED GROUNDS AT 223-140/ ISO 38830223000140/ COD 6/ VER/BOW L3/HFP XXXHFP SJG
5094 | South Williamson | 3200302 | BELFRY | TOLER | 2008-07-29 13:46 | 2008-07-29 15:20 | 39 | 94 | H61762-1B | 3666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ON SITE, POLETOP BROKE OFF , POLE#1064-67, MAKING REPAIRS, TWO PHASES ALREADY OUT, OPENED OTHER PHASE AT 1346// BACK ON @ 1520 IDC BELFRY TOLER CUSTOMERS WERE TRANSFERED TEPORARILY TO BARENSHEE POUNDING XXXX
5095 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-05-07 22:54 | 2012-05-08 14:10 | 4 | 916 | 4757581 | 3664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7.2KV NEED MATERIAL BUCKET & FLAGMAN OR WILL NEED TO CLOSE RD - NEED CUTOUT & T-BRACKET (CSP TRANSFORMER) 3 MEN REQUIRED/FETR 14:30/JEH/ REPAIRS COMP. POWER REST. @ 14:10 J. HEMLEPP 078H05 ( CORRECT CUST COUNT 1 CUTOMER) VER/KEP IDC CHANGED COUNT FROM 1 PER MAP AND NO MD XXXX
5096 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-02-15 21:06 | 2009-02-16 00:55 | 16 | 229 | 62272-1 | 3664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308401//PRIMARY BROKE LOOSE AT STIRUP ON POLE #203-77 VER/LDA
5097 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-02-07 16:26 | 2017-02-07 16:35 | 407 | 9 | H1255186-1 | 3663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CAPACITOR | EMERGENCY OUTAGE NECESSARY TO ALLEVIATE SYSTEM CONDITION// OUTAGE SHOULD BE 30 MINUTES// THIS IS FOR THE 407 HAZARD AREA CUSTOMER ON THIS BREAKER, DUPLICATE OF 4367521 - VER/TOM L3/TOM AJB
5098 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-08-01 19:15 | 2008-08-01 19:24 | 407 | 9 | 63585-1 | 3663 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | OUTAGE FOR STATION CREW TO SAFELY MAKE REPAIRS ON FAILED REGULATOR. SHOULD BE OPEN ONLY A FEW MINUTES 6-15 MINUTES. OPENED BREAKER AT 1915 AND CLOSED AT 1924 VER/ARN IDC XXXX
5099 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-06-03 11:35 | 2016-06-03 11:47 | 305 | 12 | 4288401 | 3660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD FOR AM. POLE 38830811B00014 IS LEANING. 40-5 IN DIFFICULT LOCATION NEEDS TO BE CHECKED IN DAYLIGHT. POLE IS ROTTED OFF AT GROUND LINE. CREW TO SEE ABOUT TEMPORARILY GUYING IT OFF. RELEASED BY CREW 076S02//NO OUTAGE TILL RECLOSER 38830810D00066 OPENED @ //1135 CLOSED 1147 VER/CRB AJB
5100 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-07-25 17:50 | 2010-07-26 00:10 | 21 | 380 | 56927-1 | 3660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT--LOOKING LINE---REFUSED 40T HELD AT 1940-CSP 50 ON POLE1083-187MADE LOUD NOISE-NO POWER-CALLED FOR TR AND 1 MAN--,BUCKET JOB-ETR 2330-STORM--JIM--TR ON AT 07-26 AT 0010-- RELEASED BY CREW 077S06 IDC XXXX
5101 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-08-19 14:00 | 2009-08-19 14:30 | 122 | 30 | H50785-1 | 3660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP BAD POST TYPE INSULATORS ON POLE # 178-16, HELP ON THE WAY, CAN OPEN GOAB ON POLE 178-297 WHEN HELP ARRIVES AND THEN CLOSE RECLOSER ON 194 @ 1416 REST 111 CUST//BAD POST TYPE INSULATORS ON POLE # 178-16, HELP ON THE WAY, CAN OPEN GOAB ON POLE 178-297 WHEN HELP ARRIVES AND THEN CLOSE RECLOSER ON 194. CLOSED RECL AT 14:06 AND GOAB AT 14:30 L3/HFP IDC LOOKS LIKE PH A OUT INITIALLY XXXX
5102 | Hazard | 3310502 | HADDIX | CANOE | 2019-08-20 21:34 | 2019-08-21 12:49 | 4 | 915 | 4916841 | 3660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | tree fell at pole 37840240000041 and got two span of #4al down need tree crew and line crew Released by crew 077S05
5103 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-11-09 10:58 | 2009-11-09 14:01 | 20 | 183 | 52141-1 | 3660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER POLE 43-123. I HAVE ARRESTER CHANGED IDCC FP NULL XXXX
5104 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-07-17 13:27 | 2015-07-17 21:04 | 8 | 457 | 4901491 | 3656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN TRANSFORMER CUTOUT AT POLE 261-129...JJ
5105 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-12-16 14:20 | 2008-12-16 17:45 | 31 | 205 | 59034-1 | 3655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 27704666 ./// FAULT POLE 38830282000031 COD-31 BAD CSP TRANSFORMER // PLEASE DONT FORGET THE FETR...THANKSRELEASED BY CREW 078S01 VER/HFP L3/KEP IDC XXXX
5106 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-02-09 03:35 | 2019-02-10 03:54 | 10 | 423 | 4774251 | 3655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Phase C sectionalizing line cutout failed on 875-106. Flagging crew and big bucket enroute to replace. Opened other two phases at 3:35, replaced cutouts and restored @ 3:54. sh all 3 phase customers L3/HFP
5107 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-10-20 01:32 | 2022-10-20 13:43 | 5 | 731 | 4045561 | 3655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines //. A broken cutout has burnt the top off of pole 247-D-1098. The line fuse is open on pole 247-D-907 with a ground placed and a tag to Russel Akemon. Crew has material list and are coming to make repairs. Released by crew 077S04
5108 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-08-29 13:20 | 2020-08-29 22:21 | 7 | 541 | 4400261 | 3655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Tim Smith reports customer has pole burning in back yard // customer name LOVENIA COMBS at 608 HIGHWAY 1087 E, LEBURN, KY Pole 110/157 brunt offf opened line fuse and transformer fuse on 110/11 to isolate trouble send to R.Maggard he knows what he needs Released by crew 077S03
5109 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-02-14 20:04 | 2014-02-15 00:45 | 13 | 281 | 4388231 | 3653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT TRUCK ACCESS OK RELEASED BY CREW 077S01 ;;ON SITE NO TRUCK CUTOUT CHANGED AND POWER RESTORED AT 00;45//COD 13 IDC XXXX
5110 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-04-11 14:05 | 2011-04-11 16:31 | 25 | 146 | 54899-1 | 3650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39522340 // BROKEN CUTOUT ON POLE 38830327D00340, TRUCK OK, CREW REQUIRED, ON ARM OF 3 PHASE IN APPROACH. RELEASED BY CREW 078S05/CREW ON SITE/FETR1715/VEM/CUTOUT CHANGED AND POWER RESTORED TO ALL CUST 1631/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP IDC XXXX
5111 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-08-02 21:39 | 2022-08-03 09:49 | 5 | 730 | 4666471 | 3650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester @ 38821057D00131 // replaced & RESTORED @ 09:49
5112 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2010-08-14 21:40 | 2010-08-15 12:52 | 4 | 912 | 54994-1 | 3648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5 7200 SINGLE BUSHING 120/240 TRUCK OK RELEASED BY CREW 078S09 COD-4 VER/HFP L3/HFP
5113 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-09-27 22:10 | 2010-09-27 22:34 | 152 | 24 | 54498-1 | 3648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TO ALLOW WORK TO BE DONE ON ORDER 54491//VER/CRB IDCC MCCNI, TOF2213, TON2234 XXXX
5114 | Whitesburg | 3314401 | MAYKING | ERMINE | 2020-03-10 23:36 | 2020-03-10 23:42 | 608 | 6 | 4467551 | 3648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Outage to safely isolate cutout Off @ 2336 On @ 2342
5115 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-08-20 21:14 | 2013-08-21 05:55 | 7 | 521 | 4684641 | 3647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR CUT IN THE CLEAR ON POLE 379-454 //VER/GAH IDC XXXX
5116 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-07-09 14:05 | 2008-07-09 15:26 | 45 | 81 | 65737-1 | 3645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 078S08 FAULT POLE 38830070A20645 3 - 80 T FUSES ON POLE 38830070A20605 ENTERED MD-HFP & CHANGED FUSES ON POLE 70-A-645 TO 50T FUSES PER GREG BELL - ENTERED MD-HFP HENDRIX CABLE BURNT DOWN. VER/HFP IDCC PN637 XXXX
5117 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-07-03 10:30 | 2012-07-03 17:15 | 9 | 405 | 4262261 | 3645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA REPAIRED
5118 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2022-11-11 18:32 | 2022-11-11 23:00 | 24 | 268 | 4130851 | 3642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1940// pole 1123-514 burnt off bring pole topper possibly lower truck to pole. lifted hot tap on pole 1123-490 to isolate. LF on pole 1123-475 back in @ 20:25. Released by crew 078H33/ crew making repairs/ hot tap on 1123-490 made up @ 2300/ please close ticket
5119 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-11-29 14:35 | 2011-11-29 15:15 | 91 | 40 | 4127301 | 3640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW HAD TO OPEN RECLOSER TO ALLOW THEM TO SAFELY REPLACE BAD INSULATORS THAT COULD NOT BE REPLACED WITH LINE ENERGIZED COD-91 ISO OCR 38831040000018 VER/HFP L3/HFP IDC XXXX
5120 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2016-04-17 06:56 | 2016-04-17 11:36 | 13 | 280 | 4097211 | 3640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIM COND DOWN AT STEPDOWN,BURNED INTO AT STIRRUP.NEED 1 MAN,#4 COPPER,BUCKET TRUCK/ ISO 37820007A29000/ COD 13/ MADE NECESSARY REPAIRS AND RESTORED,ALL OK.SEND TO PEGGY.COND,WHEN IT FELL,LANDED ON VEHICLE AND SCRATCHED IT UP IN SEVERAL PLACES,CUST WILL BE CALLING ABT THIS.I TOOK PICTURES AND WILL SEND THEM TO HER/ VER/BOW
5121 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-04-01 14:41 | 2022-04-01 17:01 | 26 | 140 | 4713361 | 3640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required 249-172 can reach big bucket Released by crew 078S03 crew on site to make repairs repairs made lf in @ 17:01 complete
5122 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-10-19 14:17 | 2011-10-19 18:37 | 14 | 260 | 4999331 | 3640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | NEED NEW ANCHOR AND GUY ON POLE 427-51, NEED LINE CREW. NO TRUCKS TO POLE. RELEASED BY CREW 078S01//PRT ON SITE//COMPLETE P TOLLIVER ///VER/CRB IDC XXXX
5123 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-01-07 06:47 | 2018-01-07 11:27 | 13 | 280 | 4715181 | 3640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *4717081* A phase cutout busted and laying on the arm hot on S/D pole 1101-C4-563, will have to open 3 rec. on pole1101-C4-87 to make repairs, also will need Greg R. to come help isolate, will keep track of times on rec./ ISO 38831101C40563/ COD 13/ made repaired 1127
5124 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-11-02 23:01 | 2009-11-02 23:18 | 214 | 17 | H56728-1A | 3638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP LEAD ON B PHASE-OPENED A AN C PHASE UP AT 2301 TO MAKE REPAIRS-CALLED CREW// CLOSED C AN B PHASE IN AT 2318-INSULATOR FAILED-B PHASE FUSE BLEW AT 2330-OPENED A PHASE AT 2338 // IDC XXXX
5125 | South Williamson | 3411401 | DEWEY | INEZ | 2009-02-18 06:00 | 2009-02-18 06:17 | 214 | 17 | H63512-1 | 3638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTING ARRESTER BAD ON POLE 768-D-109 A CC 102 PHASE ONLY OUT UNTIL AT 0600 ALL RECLS OPENED RECLS AT POLE 768-C-184 THEN CLOSED AT 0617. MADE DUPLICATE TICKET H1116135-1 TO SHOW ABOVE RECLS OPEN. VER/PDP IDC XXXX
5126 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-12-31 08:03 | 2018-12-31 13:06 | 12 | 303 | 4614871 | 3636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew req /// broke cutout 155-118 fuse blown on 155-118, patroling , p.hicks, fuse blown on 155-118, patroling , .bad cutout on line fuse pole 155-118, requires big bucket, 7.2kv cutout and t bracket, 2 men Released by crew 077H09 RESTORED AT 1306
5127 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-01-31 06:17 | 2014-01-31 08:55 | 23 | 158 | 4332271 | 3634 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNED INTO ON SECONDARY.OPEN 2 XFMRS AT 0750 ..WAITING ON PRESS AND 350 WIRE.FROM PAINTSVILLE.BACK ON AT 855//COD 23//ALL CUST EXPERIENCED PARTIAL POWER FROM THE OUTSET OF THE ORDER// VER/DBM IDC XXXX
5128 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-10-28 09:22 | 2008-10-28 12:00 | 23 | 158 | 59865-1 | 3634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 420-21. I AM PATROLLING LINE//3308602. I HAVE FOUND A LOOP TOUCHING POLE AND BURNING AT POLE 445-48, I HAVE ALSO FOUND A CRACKED CUTOUT ON POLE 445-49. ONE MAN AND BIG BUCKET ARE ON THE WAY TO HELP ON THIS.//3308602//VER/CRB IDC XXXX
5129 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-08-04 21:50 | 2019-08-04 23:40 | 33 | 110 | 4840241 | 3630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT broke fuse back in at 23:40 L3/HFP
5130 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-01-18 11:14 | 2012-01-18 14:25 | 19 | 191 | 4272791 | 3629 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPEN LOOP ON POLE 195-60--CREW IS ON THE WAY IDCC PN117, CDC83 XXXX
5131 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-04-30 07:08 | 2017-04-30 08:41 | 39 | 93 | 4696801 | 3627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DKM/ACTUALLY ALL OUTS ALONG CONSECRATION DR ON CAMPUS/// C PHASE RISER(39CC) ON RECLOSER IS HANGING DOWN ON POLE 184B-265, POWER RESTORED AT 0841/// VER/DKM L3/HFP XXXHFP
5132 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-10-04 19:50 | 2010-10-04 21:47 | 31 | 117 | 56859-1 | 3627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND HOTLINE CLAMP BURNT OUT OF STIRRUP AT LINE FUSE--FETR--2230- //VER/CRB IDC XXXX
5133 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2021-10-08 01:25 | 2021-10-08 03:30 | 29 | 125 | 4329521 | 3625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 274-9 rotten pole send to tech cut arrestor on same pole
5134 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-02-12 10:39 | 2011-02-12 14:00 | 18 | 201 | 56379-1 | 3618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE BURNT UP ON POLE 117-63//REPAIRING NOW//RESTORED AT14:00//COMPLETE//EM VER/KEP IDCC PN29 XXXX
5135 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-07-23 17:30 | 2008-07-24 03:08 | 11 | 578 | 59185-1 | 3618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003//POLE #183-116 BURNT OFF. CUT LOOP ON PLOE#183-398. RE-ENERGIZED ON POLE#183-119 AT 18:00HRS. APPROX. 6 CUSTUMERS OFF. LINE IS NOT GROUNDED. RELEASED BY CREW 078S04//LOOP CUT ON 119 HAD TO CUT BRUSH AROUND POLE . GROUNDED @ 116/@ 1:00 HAVE NEW POLE S//VER/CRB IDCC TOF1619, STP XXXX
5136 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-01 14:40 | 2008-04-01 18:01 | 18 | 201 | 62826-1 | 3618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3008702// BAD LA ON POLE 117-404 TRUCK OK SEND TO PRC CREW. POWER RESTORED AT 18:01, M.PHELPS RELEASED BY CREW 078H12//COD 15//ISO 117-66// VER/DBM IDC XXXX
5137 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-08-02 17:12 | 2014-08-02 19:21 | 28 | 129 | 4322071 | 3612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | HOLD ORDER REQUIRED/CREW REQUIRED POLE 249-30 BROKEN AT TOP ISOLATED AT 249-31 ALSO ISOLATED RECLOSER POLE 273-44 TAGGED TO DDC NO TRUCKS/NEEDS SENT TO TECH TO HAVE POLE REPLACED 249-181 BACK IN AT 1921 HRS NOBODY OFF /LOG ENTRY 8-2-14 @1828/ AJB
5138 | Pikeville | 3411801 | JOHNSCREEK | META | 2022-04-22 12:02 | 2022-04-22 14:54 | 21 | 172 | 4789961 | 3612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE SPAN PRIMARY&NEUT DOWN///RESTORED @ 14:54
5139 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-01-27 04:41 | 2022-01-27 06:50 | 28 | 129 | 4407901 | 3612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Broken fuse, restored @ 06:50
5140 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-07-24 00:41 | 2011-07-24 10:37 | 12 | 596 | 4606011 | 3612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR POLE 1097-307/BURNT OFF/CUT LOOP ON 1097-306/WILL BE ABLE TO RESTORE ALL BUT ONE CUST BY 0530/VEM/FUSE ON1097-67 BACK IN AT 0443/ONE CUST STILL OFF/POLE IS ENROUTE/VEM/REMAINING CUST RESTORED 1037/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14// COD 12 IDC XXXX
5141 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-04-08 10:27 | 2010-04-08 11:49 | 44 | 82 | 60770-1 | 3608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE// CALLED B FRALEY TO ASSIST//WR#34583375 REPLACED BAD CUTOUT//VER/CRB IDC XXXX
5142 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2017-08-23 13:50 | 2017-08-23 15:12 | 44 | 82 | 4293361 | 3608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DUE TO BAD CUTOUT ON POLE 188-175. I OPENED SOLID BLADE SWITCH ON POLE 188-B-121 AT 13:50. I HAVE CUTOUT REPLACED. CLOSED SOLID BLADE 300AMP SWITCH POLE 188-121 AT 15:12/ IOS 37830188B00121/ COD 44/ VER/BOW SJG
5143 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-05-04 03:20 | 2009-05-04 03:55 | 103 | 35 | H64830-1 | 3605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S01 REPLACED BAD CUTOUT ON POLE 188-325. ALL CUSTOMERS RESTORED // VER/CRB IDCC DUP TO OPEN OTHER 2 PHASES XXXX
5144 | Hazard | 3301401 | COMBS | COMBS | 2014-09-16 08:22 | 2014-09-16 09:30 | 53 | 68 | 4502321 | 3604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 37830271C00454, CUT IN CLEAR...POWER RESTORED.//MADE AED VER/CRB L3/HFP AJB
5145 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2018-12-07 14:06 | 2018-12-07 16:30 | 25 | 144 | 4515901 | 3600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | had fuse out on pri mtr, pole, someone from railroad rep the 12t with a 25t, when pri mtr when bad, it took out the l/f on 879-54, closed in l/f on 879-54 at 1500, then came back to pri mtr pole fuse was blown again, found pri mtr to be bad, so i bypassed mtring, closed in l/f at this 879-195 at 1630. restoring power to all cust, by amg please send to john sodie L3/HFP
5146 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-07-09 16:20 | 2014-07-09 18:50 | 24 | 150 | H4220921 | 3600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE ONLY OPEN AT THIS TIME . WILL NEED TO OPEN C PHASE WHEN CREW ARRIVES, FAILED TRANSFORMER CUTOUT AT POLE 220 HAS CROSSARM BURNED APART, D. MASSEY HAS ROW AND KYPCO CREWS ENROUTE / GXJ . OPENED C PHASE AND TRANSFORMER ON POLE 1145-20 AT 16:20. ALL CUSTOMERS RESTORED AT 18:50 / GXJ RELEASED BY CREW 074S03//COD 8 + 16// AJB SEE 4220921 FOR INLT OUTAGE.
5147 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-03-07 03:12 | 2015-03-07 05:36 | 25 | 144 | 4154561 | 3600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED CUTOUT & SOLID BLADE//COD 25// VER/DBM AJB
5148 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-05-04 02:56 | 2009-05-04 03:55 | 61 | 59 | 64830-1 | 3599 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S01 REPLACED BAD CUTOUT ON POLE 188-325. ALL CUSTOMERS RESTORED // VER/CRB IDCC TOF0212, CNT167 PH B OUT INITIALLY AFTER SEVERAL FLICKERING LIGHT CALLS. TON0407 XXXX
5149 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-02-20 11:47 | 2016-02-20 20:21 | 7 | 514 | 4740541 | 3598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O 1123-D3-7109. SMALL BKT MAYBE? BESIDES FLATWOODS POOL RELEASED BY CREW 078S07//COD 7//WILL SEND TO TECH TO HAVE CUSTS MAPPED CORRECTLY//REPAIRS MADE AND ALL CUST RESTORED 2021/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L3/HFP XXXHFP
5150 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-11-20 16:41 | 2018-11-20 21:44 | 16 | 303 | 4465061 | 3594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire down at pole 38830309000081 it will have to be climbed to sleeve wire should be able to work pole 38830309000082 with big bucket opened reclosure 309-12 at 18:35 (isolated grounded and tagged to BOB RENOLDS at this location) Released by crew 078H01 L3/HFP
5151 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-04-23 07:47 | 2011-04-23 22:45 | 4 | 898 | 62361-1 | 3592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED--BAD 25KVA CSP TRANSFORMER--ON RT 168 TRUCK OK NEED FLAGGERS RELEASED BY CREW 078S07 VER/KEP IDC XXXX
5152 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-07-17 19:47 | 2022-07-18 10:45 | 4 | 898 | 4506101 | 3592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DDC TAGS // DOL #1222918 //Broke cut-out on 37830363000162. Cant reach with small bucket. Need 2 men and big bucket to safely replace cut-out. May need to drop line out at recloser 387C-292once they arrive. Released by crew 077S06 . closed cutouts on pole 363-162 @ 10:45 Released by crew 075H04
5153 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-08-16 21:41 | 2009-08-17 05:10 | 8 | 449 | 59824-1 | 3592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001202//TRANSFORMR FUSE OUT ON POLE 38830069A31251--CALLING TREE CREW-OPENED LINE FUSE ON POLE 38830069A31059 AT 12:52 BACK ON AT 02:35-- BAD 25KVA TRANSFORMER ON POLE 38830069A31251 WITH 8 CUSTOMERS OM IT-TRUCK OK-CALLING CREW RELEASED BY CREW 078S07 //VER/GAH IDCC CNT12 XXXX
5154 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-06-05 19:51 | 2014-06-06 02:30 | 9 | 399 | 4988161 | 3591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BURNED TOP OF POLE OFF. NOT TRUCKACCESSABLE WILL NEED FOREMAN ,2 LINEMAN POLE EXTENSION 7200 CUTOUT LIGHTNING ARRESTOR //D MASSEY & R RAY & B CAMPBELL
5155 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-12-20 17:56 | 2013-12-21 23:50 | 2 | 1794 | 4180011 | 3588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 6 WHEELER & BUCKET TRUCK , BLOCKS AND ROPES (NO TRUCK) 7.2 25KVA TR & CUTOUT - CALL HARVEY AND CHECK WITH HIM BEFORE COMING OUT //T MCCOY , J GARRETT, R WORRIX & J SMITH6T FUSE OUT DUE TO BAD TRANSFORMER. CREW ON THE WAY RELEASED BY CREW 074S11 VER/HFP L3/HFP
5156 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-07-21 02:35 | 2018-07-21 12:33 | 6 | 598 | 4818121 | 3588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT BROKEN,WILL REPLACE IT//////////REPLACED BROKEN CUTOUT&RESTORED POWER,ALL OK AFTERWARDS
5157 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-10-25 23:17 | 2015-10-26 12:06 | 10 | 769 | 4375651 | 3586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 251-54, PATROLLING LINE. FOUND POLE 251-60 BURNT OFF, WILL CUT DEAD ENDS ON POLE 251-59 AND RESTORE ALL CUST BUT 1, NEED 1 MAN AND STUFF TO CUT DEAD-ENDS. POWER RESTORED AT 04:30 RELEASED BY CREW 077S02/ LAST ONN AT 1206 37830251000059/ ISO 37830251000054/ COD 1037830251000059/ VER/BOW L3/HFP XXXHFP
5158 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-07-24 14:48 | 2011-07-24 16:40 | 32 | 112 | 4608961 | 3584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 116-610 BAD LA CHGED IT INSTALLED 15T LINE FUSE POLE 116-286 30T//MD FILED//COD 32//ISO 38830116A00286// VER/DBM IDC XXXX
5159 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-08-19 19:17 | 2022-08-20 01:15 | 10 | 358 | 4766291 | 3580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse open 190-D-32,Bad Deadend bell on pole 190-D-32,Rick Ray on the way to help make repairs..Replaced 2 Deadend Bells and Line fuse cutoutRestored 01:15..
5160 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-03-17 18:53 | 2017-03-17 21:15 | 34 | 142 | 4565671 | 3580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRIED RECLOSER IN ONE TIME AND CAME BACK OUT, ISOLATED AT 38830478A17084, CLOSED RECLOSER UPTO 7084 AT 1957, FOUND AND RE LACED BAD CUTOUT AT7094, CLOSED IN AT 7084 APR AT2115 DWEST RELEASED BY CREW 078S11 VER/KEP AJBC TOF1751 INL CALL FLK LGHT.
5161 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2008-05-17 10:14 | 2008-05-17 18:45 | 7 | 511 | 65054-1 | 3577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3010601// FAULT LOCATION 39831148B30650 // RELEASED BY CREW 078S08 VER/HFP IDC XXXX
5162 | Pikeville | 3407103 | TOPMOST | KITE | 2013-07-24 09:00 | 2013-07-24 12:48 | 25 | 228 | 4586011 | 3575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON POLE 37830161D00030 AT 09:00 . INSTALLED ADDITIONAL LINE CUTOUT ( 80T ) FOR ROARING BR ( TO POLE 31 ) AND RESTORED ROARING BR AT 10:43 . ALL RESTORED AT 12:48, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/CRB L/3 CRB IDCC STP MISSING XXXX
5163 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-02-08 06:19 | 2019-02-08 08:04 | 34 | 105 | 4768341 | 3570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Nothing found fuse was broken. Please send copy to have maps corrected. From pole 597-4 to 597-5, fieldveiw shows two spand to be 4 phase. It is only single phase. Apr at 0804 close ticket dwest
5164 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-07-09 11:33 | 2019-07-09 15:33 | 19 | 240 | 4684531 | 3570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | B PHASE L/F 38821082000055 WAS OPEN FROM BEGINNING OF OUTAGE//COD 9//OPENED A & C @ 1312 THIS OUTED 10 MORE CUSTS//NEED CREW,1106-51,#2ACSR DOWN,CAN USE BUCKET////////OPENED@1082-55@13:12,ISOLATED THERE.APPEARED TO HAVE PULLED OUT OF A SLEEVE@1106-51//////CREW ENROUTE L3/HFP
5165 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-01-24 05:45 | 2010-01-24 14:15 | 7 | 510 | 58613-1 | 3570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400301XFMR FUSE OUT . WILL REFUSEXFMR BAD ON POLE 37830094000069.WILL MOST LIKELY BE A HAND JOB .MATERIAL HANDLER WILL GET XFMR CLOSE. 50 KVA 4 MEN. RELEASED BY CREW 074S04// CAN GO BACK WITH 37.5KVA CREW AT SITE/WR#33565703/ OPENED STEPDOWN POLE 94-242 AT 11:35AM REPLACED C/O ON POLE 94-69 TRANSFORMER REPLACED AND ALL REPAIRS MADE CLOSED STEP DOWN AT 13:22 CREW CHECKING FOR MORE TROUBLE ON THE SECONDARY SIDE OF TRANSFORMER//COD 7// VER/DBM IDC ONLY CUSTOMERS SHOWING ONE OF THE THREE TRANSFORMERS XXXX
5166 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-11-20 19:01 | 2012-11-20 22:59 | 15 | 238 | 4412031 | 3570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 50T LINE FUSE RELEASED BY CREW 078S08/CREW ON SITE/FETR 2215/VEM /C PHASE/VEM RELEASED BY CREW 078H14/VEM/BAD CUTOUT 65T LINE FUSE //VEM /CHANGED ALL 3 LINE FUSES/POWER RESTORED TO ALL CUST 2259/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB IDC XXXX
5167 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-12-14 07:32 | 2011-12-14 11:15 | 16 | 223 | 4175881 | 3568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON 92-499 PATROL LINE,REFUSE LINEFUSE BLEW PATROL AGAIN BAD XFORM CUTOUT 7200 ON 68-745 NEED LINE CREW NO TR. BEHIND HS. 6105 ON HOEING DR. RELEASED BY CREW 078S04//REPAIRS MADE-POWER RESTORED AT 11:15-PLEASE CLOSE-PRB ///VER/CRB IDC XXXX
5168 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-06-20 12:05 | 2009-06-20 14:00 | 31 | 115 | 63068-1 | 3565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | SERVICE DROP BURNT DOWN. REPAIRED DROP AND RESAGGED. TURNED TRANSFORMER OFF AT13:40, BACK ON AT 14:00
5169 | Hazard | 3302703 | HAZARD | HAZARD | 2020-07-18 08:21 | 2020-07-18 18:15 | 6 | 594 | 4178701 | 3564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse open on pole 272-D2-736, dead end insulator is broken/burnt in the clear on pole 272-D2-955 with the primary sagged below the neutral and being held up by the cutout jumper. Need a crew and a 7200 deadend insulator. No grounds or tags placed. Released by crew 077H20..repairs made, all power restored @18:15
5170 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-07-16 17:56 | 2016-07-16 22:30 | 13 | 274 | 4648111 | 3562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-7505 BAD 50KVA NEED 75 KVA RELEASED BY CREW 078S08.PLZ SEND THIS TO A TECH TO SEE IF LOAD SHOULD BE SPLIT//COD 13//EMAILED TO S MARTIN// VER/DBM
5171 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-06-10 03:24 | 2008-06-10 13:17 | 6 | 593 | 61219-1 | 3558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001102//TREES GROWING UP INTO XTRM. SHOULD BE BACK ON BY0730 IF XTRM NOT BAD // TRANSFORMER IS BAD NEED A37.5 7200 SINGLE BUSHING XTRM//COD 6// VER/DBM IDC XXXX
5172 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-05-29 02:49 | 2009-05-29 14:40 | 5 | 711 | 63441-1 | 3555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ANOTHER FAILED CUTOUT. CAN USE TRUCK RELEASED BY CREW 074S02 COD-5 VER/KEP L3/KEP IDC XXXX
5173 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-05-08 04:41 | 2021-05-08 14:27 | 9 | 586 | 4550071 | 3552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.// Broke cutout on 293-186 lifted clamp on 293-185 to isolate. closed line fuse in @0940. restored power at14:27..
5174 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-06-15 00:02 | 2022-06-15 01:13 | 50 | 71 | 4118231 | 3550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 1214016/// Outage to make emergency repairsx arm replaced all cust restored @0113 please close ticket thanks.bt Released by crew 078H02
5175 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-12-17 08:20 | 2016-12-17 13:29 | 28 | 309 | 4202551 | 3541 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 140-49 BURNT OFF OPEN REC. POLE 140-40 08:20 POLE 140-4008 CUT LOOP INSTALLED GROUND HOLD CARD FOR DDC POLE 140-40 REC IN 09:00 RELEASED BY CREW 078S08/CREW ON SITE/FETR 1330/VEM RELEASED BY CREW 078H14 VER/TOM L3/TOM AJB
5176 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-07-30 10:50 | 2009-07-30 11:10 | 177 | 20 | 52948-1 | 3540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW OPENED RECLOSER TO SAFELY REPLACE A BROKEN INSULATOR AND REPAIR LINE VER/KEP L3/KEP IDC XXXX
5177 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-01-06 15:00 | 2022-01-06 16:44 | 34 | 104 | 4313091 | 3536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got broke cutout on pole 29-228 going to be change it out
5178 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2019-05-30 22:30 | 2019-05-30 23:22 | 68 | 52 | 4391601 | 3536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | from pole 45B2221 to pole 45b2220 C phase down. no bucket broken chicken wing, all wire intact no one out of power at this time, will need to isolate to make repairs. Released by crew 078H17,open switchs @ pole 38830044D37065 @ 2230,repairs made all cust restored @ 2322 please close ticket thanks.bt
5179 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-07-15 10:15 | 2016-07-15 10:31 | 221 | 16 | H4639041 | 3536 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | OPENED 34KV CB S VIA SCADA @ 0159 TO REMOVE LOAD FROM SWITCH INSIDE SUBSTATION WHICH IS ARCING//COD 1570///DUPLICATE OUTAGE SEE ORDER 4638971/THIS IS THE ORDER FOR PLACING THE CKT BACK TO NORMAL--OIPENED N.O. TIE SWS AT 318-B-282 AT 1015 THEN CLOSED THE RECLOSER AT 270-D-61/ AT 1031// /VER/DKM AJB
5180 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-04-26 11:09 | 2010-04-26 12:50 | 35 | 101 | 51326-1 | 3535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED ON 250-229 40/5 POLE BURNT OFF/NEED TO SEND TECH OUT TO WRITE UP TO REMOVE OR REPAIR VER/KEP L3/KEP IDC XXXX
5181 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2015-05-15 13:50 | 2015-05-15 15:31 | 35 | 101 | 4432811 | 3535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OPEN PAT. LINE BROKEN OR MELTED FUSE ALL PWR RESTORED PLEASE CLOSE TICKET @15:31/ ISO 38830235000068/ COD 35 L3/DKGXXX AJB
5182 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-05-07 20:45 | 2016-05-07 23:51 | 19 | 186 | 4185901 | 3534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 420-64,OPENED SOLID BLADE ON POLE 420-56 TO ISOLATE AT 22:45, REPLACED CUTOUT RESTORED POWER AT 23:51. SEPERATE OUTAGE FOR THE SOLID BLADE OUTAGE VER/KEP
5183 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-07-21 17:41 | 2013-07-21 19:35 | 31 | 114 | 4572061 | 3534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HIGH SIDE CUT-OUT DOOR BURNED UP. WILL REPLACE CUT-OUT. VER/CRB L/3 CRB IDCC CDC92 XXXX
5184 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2018-09-24 14:46 | 2018-09-24 15:22 | 98 | 36 | 4151161 | 3528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | TIE WIRE BROKE & PHASE OFF PIN AT POLE 248-4 PER E BAIER//ON @ 1522 L3/HFP
5185 | Hazard | 3308001 | JACKSON | S.JACKSON | 2019-07-03 10:10 | 2019-07-03 12:16 | 28 | 126 | 4645841 | 3528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad csp transformer on pole 1107-25 truck acces will need 15 kva 7200 transforme also cutout and t bracket
5186 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-10-26 13:32 | 2017-10-26 14:15 | 82 | 43 | 4500561 | 3526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN STRANDS OF CONDUCTOR ON POLE 37830199B00019/ OPENING RECLOSER TO REPAIR/ ISO 37830223A10576/ COD 82/ 1332-1415/ VER/BOW L3/HFP XXXHFP ACB
5187 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-04-08 16:50 | 2010-04-08 17:05 | 235 | 15 | 61096-1 | 3525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELATED TO ORDER 60944-1 NOTES FROM THAT ORDER ~~~ ONLY A PHASELOOP OPEN @ 37830021000031 WILL OPEN RECLOSURE @37830021000031 WHEN READY TO MAKE REPAIRS & WILL TAKE APROX 45 MIN. VER/HFP L3/HFP IDC XXXX
5188 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2019-04-10 19:37 | 2019-04-11 00:15 | 42 | 278 | 4080151 | 3521 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CALLED CUSTOMER//NO ANSWER//THERE IS A 50T L/F ON POLE 37830211C00254 THAT FEEDS THE ONE POLE TO P[OLE 37830211C00261//COD 7//MADE MD//THERE 7 CUSTOMERS OUT FROM THE BEGINNING WILL HAVE TO OPEN L/F 37830211C00216/ this outed 35 more custs//CALLED CUSTOMER//NO ANSWER// 30t fuse out on pole 211-c-254 due to bad insulator. we will have to open 50t fuses on pole 211-c-216 to make repairs will keep up with time. opened up line fuses at 23:30 closed line fuses back in at 00:15 everything ok changed L3/HFP
5189 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2017-01-03 15:35 | 2017-01-03 15:57 | 160 | 22 | 4264851 | 3520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW REQUIRED TO REPLACE BAD INSULATOR ON 37830537000089 FOUND DURING CIRCUIT INSPECTION. VER/AWD // VER TIMES PER VOICE RECORDER = L3/HFP XXXHFP AJB
5190 | Hazard | 3310502 | HADDIX | CANOE | 2020-06-25 04:04 | 2020-06-25 11:24 | 8 | 440 | 4071581 | 3520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held in accordance with KPCO late night callout guidelines. had bad cutout on pole 50-49 and trees in line at 50-39
5191 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-07-10 12:47 | 2021-07-11 04:00 | 15 | 913 | 4881991 | 3517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 300 Lakeridge Rd Cust reporting TR hanging from pole///// Pole 38830499000105 needs anhor and dn guy also needs new 25kva 7200. manual job unless you can get truck to pole. Customer said he didnt care what you had to do. Lifted H.T. on 499-102Tagged to Brian R. Fuse 499-38 in @1553 one customer off. Crew required Released by crew 078S11///HT on @ 04:00///Complete BR Released by crew 078H22
5192 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-10-31 14:36 | 2009-10-31 17:00 | 39 | 144 | 53707-1 | 3516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 286- 196 BURNT OFF CK LATER LAST CUST ON 5;00 PM REC. ON 4;00 PM RELEASED BY CREW 078S08 VER/KEP L3/KEP IDC XXXX
5193 | Pikeville | 3402002 | KEYSER | STONECOAL | 2017-06-24 01:51 | 2017-06-24 21:22 | 3 | 1171 | 4033221 | 3513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CO BROKE-BESIDE ROAD 12KV. BJ RELEASED BY CREW 074E04//2122 CLOSED VER/CRB
5194 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-11-07 14:50 | 2015-11-07 20:39 | 29 | 349 | 4418251 | 3513 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL 1623 WHEN L/F OPENED WHEN POLE TOP FELL//OPENED LOOP ON POLE 37830338000012 CLOSED L/F ON POLE 3 @1643 //POLE 37830338000113 BURN OFF AT CUTOUT ,BAD CUTOUT,NEED 40C4 POLE, 72KV CUTOUT AND DEAD END INSULATOR ,GUY ATTACHMENT 2 CLEVIS,MAY BE ABLE TO LOWER FOREMAN CALL.TRUCK ACCESSABLE. RELEASED BY CREW 077H07REPAIRS MADE POWER RESTORED AT 2039 RELEASED BY CREW 077H03// VER/DBM L3/HFP XXXHFP AJB
5195 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-02-20 01:37 | 2015-02-20 16:15 | 4 | 878 | 4046651 | 3512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE PULLED OUT OF SLEEVE..PRIMARY DOWN BETWEEN 930-12 AND 930-34.25 T FUSE ON P 930-12..BLOWN..NEED 6A COPPER SLEEVES AND 3 MAN CREW..TAGGED FOR DDC. RELEASED BY CREW 074H04 ENTERED MD VER/HFP L3/HFP
5196 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-10-27 20:48 | 2015-10-28 04:07 | 8 | 439 | 4382061 | 3512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL L/F ON POLE38830854000004 OPENED 2048 //POLE FIRE DUE TO BAD CUTOUT ON POLE 854-53///OPEND LINE FUSE ON POLE 854-4 @ 20:48 TO MAKE SAFE///GOING TO PUT FIBERGLASS EXT ON POLE FOR REPAIRSPOLE FIRE DUE TO BAD CUTOUT ON POLE 854-53///COD 8// VER/DBM L3/HFP XXXHFP AJB
5197 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-11-15 14:40 | 2011-11-15 15:25 | 78 | 45 | 4079261 | 3510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S12//OPENED TO REPLACE BAD CUTOUT ///VER/CRB IDC XXXX
5198 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2021-06-08 12:55 | 2021-06-08 14:25 | 39 | 90 | 4688721 | 3510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser from cutout burnt up/replaced wire. pls close. tre
5199 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-03-10 01:16 | 2013-03-10 11:00 | 6 | 584 | 4894481 | 3504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TR POLE 942-961 // NEED 3 MAN CREW // WILL ARCOS CREW AT 0645 // RELEASED BY CREW 079S02 CCC COD-6 ISO TF @ 38820942B10961 VER/HFP L3/HFP IDC XXXX
5200 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-08-13 18:57 | 2012-08-13 22:23 | 17 | 206 | 4933691 | 3502 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 45-6163 4/0 SEC. LOOPS BURNT OFF NEED 4/0 RISER WIRE SEND TO BOB R. RELEASED BY CREW 078S08 OFF 2212 ON 2223. REPAIRED.BLR//COD 17// VER/DBM IDC XXXX
5201 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2020-09-10 21:27 | 2020-09-10 23:10 | 34 | 103 | 4450351 | 3502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout on pole 1123c/6, power restored at 1110 // cod 34
5202 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-02-25 22:35 | 2012-02-26 04:25 | 10 | 350 | 4506771 | 3500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN & BURNING AT POLE 295-24 - 10 CC INTERRUPTED - OPENED REC POLE 295-A-26 @ 2320 INTERRUPTING 19 CUSTOMERS //2 SPANS OF #4 COPPER DOWN FROM POLE 37830295C00024, ALL MANUAL, NEED 100 FT OF WIRE AND 3 MEN. JEFF COMBS, BRIAN CLEMONS & VIRGIL HURT TO ASSIST //INSTALLED 300 AMP DISC. ON POLE 37830295000217, OPENED SAME & CLOSED RECL AT 0315 // //VER/GAH IDC XXXX
5203 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-06-24 19:20 | 2010-06-24 21:00 | 35 | 100 | H56739-1 | 3500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE ON STEPDOWN WILL BE CHANGING OUT OTHER 2 OPEN 3 SINGLE RECL. ON POLE 69-143 AT 19:20 HAVE A STEPDOWN BUSHING BROKE GOING TO CHANGE STEPDOWN HAVE SD CHANGEDCLOSED IN AT 21:00 IDCC DUP TO OPEN TWO PHASES XXXX
5204 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-03-24 18:41 | 2020-03-24 23:10 | 13 | 269 | 4507261 | 3497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolling--38830452000088 broke c/o, replaced with crew--38830452000001 30t lat blown --in at 23:10--allgood-ds032420
5205 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-10-14 14:19 | 2014-10-14 16:36 | 43 | 137 | 4622761 | 3497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND B PHASE OPEN , PATROLLING NOW TCM/ BAD UG RISE @ 38830810B00319// ISOLATED ON POLE 30810B00303FOUND B PHASE OPEN , PATROLLING NOW TCM/FOUND BAD RISER CUTOUT ON POLE 810-319 ISLOATED ON 810-303 CLOSING NOW / CLOSED MAIN LINE IN AT 15:39 STAYED , WORKING ON RISER CUTOUT NOW TCM/ CLOSED RISER CUTOUT IN @ 1636// VER/DBM // PER B.O. & IDC C PHS WAS OUT 43 CUST & MAP NOT SHOWING U/G// L3/HFP HFPC CNT106 FP38830810000319 AJB
5206 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2009-11-14 03:39 | 2009-11-14 07:32 | 15 | 233 | 56548-1 | 3495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 38831121D00081... REPLACED LINE CUTOUT, ALL WORK COMPLETE / GXJ IDCC PN236 XXXX
5207 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-06-20 16:11 | 2011-06-21 00:30 | 7 | 499 | 4356581 | 3493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 TRANSFORMER AT POLE 255-106, CREW REQUIRED, NEED 15 KVA, CUTOUT, BRACKET, AND SPILL BAG FOR OLD TRANSFORMER. SHOULD BE ABLE TO GET TRUCK TO POLE. LINE FUSE OPEN AT 255-52//ALSO BAD 50 KVA 7200 XFMR ON POLE 38830255000052, TRUCK OK.//COD 7// VER/DBM IDC XXXX
5208 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-04-04 15:32 | 2014-04-04 16:08 | 97 | 36 | H4571461B | 3492 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE#448-C3-114 BURNT/ISOLATED 448-530 CLOSED CB AT 0602/FBR LOCKED OUT , BAD INSULATOR ON POLE 448-114, CUT LOOPS ON POLE 448-530 & PLACED TAGS FOR DDC.FBR LOCKED OUT , BAD INSULATOR ON POLE 448-114 POLE BURNT OFF, CUT LOOPS ON POLE 448-530 & PLACED TAGS FOR DDC. RELEASED BY CREW 077S11 SEE DDC LOG // //VER/GAH IDC XXXX
5209 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-12-27 16:12 | 2022-12-28 09:54 | 8 | 1062 | 4368001 | 3491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Line fuse and trans. fuse open @1127-B-294, checking. Got L/F restored @1713, bad 25 kva 7200 here, needs upgraded to a 37.5 kva. Talked with customer and they are fine with changing in the morning. Myles R. gonna upgrade this in the morning. Released by crew 074S05// REPAIRS MADE // ON @ 9:54
5210 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-02-05 07:01 | 2010-02-05 09:35 | 72 | 154 | 63189-1 | 3491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE#478-536 "C" PHASE OUT ON POLE# 411 COD-71/ CREW ON SITE MAKING REPAIRS. J. HEMLEPP & CREW IN ROUTE FROM ASHLAND. ETA 09:00 A.M./ CREW ON SITE MAKING REPAIRS. COMPLTED 09:35 IDCC CNT370 XXXX
5211 | Hazard | 3307301 | BULAN | ARY-HEINE | 2017-11-06 16:09 | 2017-11-06 18:14 | 72 | 125 | 4536061 | 3488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Cust still out. Primary broke at shoe on 37830153D00006. Will re-open recloser on 37830153A40273 for brief outage to make repairs. Opened ocr 1755-1814.
5212 | Pikeville | 3403001 | PIKEVILLE | CITY | 2013-07-10 16:42 | 2013-07-11 01:00 | 7 | 498 | 4499081 | 3486 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | RESTORED 0100 VER/KEP IDC XXXX
5213 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-04-03 04:39 | 2010-04-03 05:21 | 83 | 42 | H1134045-1 | 3486 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | LINE SWITCH ON 1129-382 IS BROKEN,HAVE TO REPLACE IT.WILL ALSO REPLACE ALL 3 WHILE ON POLELINE SWITCH ON 1129-413 IS BROKEN,HAVE TO REPLACE IT.WILL ALSO REPLACE ALL 3 WHILE ON POLE///OFF AT 04:39 ON AT 05:21 //VER/GAH IDC XXXX
5214 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-03-03 15:40 | 2008-03-03 19:05 | 17 | 205 | 52317-1 | 3485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 3103101// REPAIRING GUY POLE 222-76 20T LINE FUSE VER/HFP IDC XXXX
5215 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-12-25 11:45 | 2009-12-25 13:10 | 41 | 85 | 51735-1 | 3485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRI . BURNT OFF AT CUTOUT REPAIRED POLE 116-117 / COD-41 /
5216 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2010-06-11 16:25 | 2010-06-11 21:55 | 26 | 330 | 60192-1 | 3480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35534276 // POLE 1099-6079 BAD 50KVA TRUCK TO POLE POLE MARKED TAPE RELEASED BY CREW 078S08/ XFMER CHANGED OUT ALL CUST. RESTORED @ 21:55 J. HEMLEPP RELEASED BY CREW 078H05 COD-20 VER/HFP L3/HFP IDC LISTEN TO CALL
5217 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2015-04-14 14:10 | 2015-04-14 16:35 | 24 | 145 | H4316881 | 3480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE OUT/PARTROLLING NOW//COD 49//XARMS BURNT ON POLE 954-C-683, LOAD BUSTING SWITCHES ON POLE 954-A4-908//INTERRUPTED 28 ADDTL CUSTOMERS//OPENED SWITCHES 954 908 AT.13.50..CLOSED REC OFF AT 14.10.TOOK REC OFF AT 16.21 BACK ON AT 16..35./OPENED AGAIN DUE TO SWITCH FAILURE/ RELEASED BY CREW 076S01/ FIX IT IN HOIS//BACK IN WHEN RECLOSER WAS OPENE A SECOND TIME/VER/ ADH L3/DKGXXX AJB
5218 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2019-02-20 15:10 | 2019-02-20 15:25 | 232 | 15 | 4816931 | 3480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened recl to safely replace cutout at pole 38820893A00236/ Opened 1510 Closed 1525
5219 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-01-02 16:23 | 2014-01-03 01:45 | 19 | 562 | 4219491 | 3478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 173 41 BURNT OFF FOREIGN POLE CUSTOMER SAID WE COULD GET IN YARD TO SET POLE/CREW REQUIREDDOUBLE DEAD END POLE WITH OPEN WIRE SECONDARY/NEED 40/5 POLE/ISOLATED ON 173-1 WITH HOT TAP/149-9 15 T BACK IN AT 1745 HRS 4 CUSTOMERS STILL OFF RELEASED BY CREW 078S03 RELEASED BY CREW 078H01//COD 19// VER/DBM IDC XXXX
5220 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2022-05-18 14:14 | 2022-05-18 16:52 | 22 | 158 | 4907361 | 3476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | had a bad arrester on xformer pole 930-D-162 cut in clear and got restored at a time of 16:52
5221 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-06-27 20:16 | 2011-06-28 15:34 | 3 | 1158 | 4423911 | 3474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT-OUT ON POLE 329-86. POLE IS MANUAL. WILL NEED R/W CREW AND TWO-MAN CREW TO CHANGE CUT-OUT. NEED ONE 19.9 CUT-OUT, BRACKET, AND ARRESTER. RELEASED BY CREW 075H01//COD 3//ISO 37830329000015// VER/DBM IDC XXXX
5222 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-12-07 11:44 | 2010-12-07 12:40 | 62 | 56 | 64048-1 | 3472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38018553 // POLE 69-5092 BAD CUTOUT 65T LINE FUSE ENTERED MD...HFP COD-62 ISO PO 38830069C35092 VER/HFP L3/HFP IDC XXXX
5223 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-06-09 06:14 | 2015-06-09 14:30 | 7 | 496 | 4541301 | 3472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WAIT TIL AM SHIFT PER CALLOUT GUIDELINES, POLE 178-115 TOP BURNED OFF, 40/4 TRUCK ACCESS, GAVE MATERIAL LIST TO KEITH CAMPBELL. LIFTED CLAMP ON POLE 178-161 TO ISOLATE TROUBLE.@ 1045 VER/CRB L3/DKGC TOF1045 FUSE WAS OPEN ON POLE 37830178000115 FROM BEGINNING OF OUTAGE LIFTED HOT LINE TAB AT 1045 OUTAGED ZERO CUST ON TRANSFORMER POLE 178-115 DID NOT MAKE AN ADDITIONAL OUTAGE TO REFLECT THIS
5224 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2022-07-24 00:44 | 2022-07-26 10:35 | 1 | 3471 | 4565341 | 3471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Crews will work on 7/26/22 per Steve Ray // Difficult location to access in dark/conductor broke in the clear/needs to be worked in daylight1/0 sec down on pole 48-1928 to p48-1526, will need to walk down RR tracks to get to secondary pole // restored at 10:35
5225 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-03-20 01:41 | 2008-03-20 06:30 | 12 | 289 | 59206-1 | 3468 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3411801//FUSE IS OUT AT STEPDOWN XFR,WILL PATROL FOR CAUSE.POLE-961-110// SLEEVE FAILED AND CONDUCTOR FELL VER/LDA IDC XXXX
5226 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2014-08-03 08:23 | 2014-08-03 09:40 | 45 | 77 | 4326261 | 3465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 70-605 65T OUT LOOKS LIKE BAD 1350 ON POLE 70-675 LEFT CUTOUT OPEN TAGGED FOR DDC MADE AED VER/CRB AJB
5227 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-10-26 16:45 | 2010-10-26 23:10 | 9 | 385 | 64174-1 | 3465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT, BURNED POLE 1/2 IN TWO. NEED CREW TO MAKE TEMP REPAIRS, WILL OPEN LINE FUSE ON POLW 955-43. FIELD VIEW NOT CORRECT. MANUAL WORK - NOT TRUCK ACCESSIBLE. NEED MORE R/W TRIMMED AROUND POLE. 7 CUSTOMERS OUTAGED. OFF AT 16:45, ON AT 23:10. RELEASED BY CREW 074H03 //VER/CRB IDC XXXX
5228 | Hazard | 3302703 | HAZARD | HAZARD | 2022-12-20 09:52 | 2022-12-20 11:37 | 33 | 105 | 4279211 | 3465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | STATIC WIRE | off @ 0950 on @ 1129
5229 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2016-06-28 13:51 | 2016-06-28 14:02 | 315 | 11 | 4494641 | 3465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKEN CROSSARM ON 37830328D00211. RELEASED BY CREW 075H03 VER/AWD
5230 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-11-18 23:29 | 2017-11-19 13:55 | 4 | 866 | 4575401 | 3464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Primary riser broke on latteral take-off pole 38831100000036 due to wind. Difficult location. Replaced hot-line clamp and riser and restored @ 13:55. sh
5231 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-06-02 19:32 | 2009-06-03 09:58 | 4 | 866 | 61558-1 | 3464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TREE CREW AND REPLACE TRANS//COD 4// VER/DBM IDC XXXX
5232 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2020-06-19 13:49 | 2020-06-19 23:26 | 6 | 577 | 4046961 | 3462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C phase only open at recloser 38820771D00433 patrolling line/cc130 isolateing trouble at recloser pole 820c3-309C phase only open at recloser 38820771D00433 patrolling line/cc130 opened & isolated recloser 38820820C30309 & energized up to there at 17:05, tree fell wire off of insulators at 821B6,111,&7, pole 821B7 & 821B8 are rotted and leaned over all NTA, should be able to dig around poles and jack them back and stub them with arms for now, bring 4 arms, ptp & insulator & 2 hand dig anchors l
5233 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-09-04 01:12 | 2011-09-04 04:05 | 20 | 173 | 4801701 | 3460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PRI. UNDERGROUND OUT CALLED CREW SEND TO LLOYD MC. 20 CUSTS OFF RELEASED BY CREW 078S08 /// BAD UG FROM 69-288 TO 69-289 ALL CUSTOMERS RESTORED AT 4:05 //VER/GAH IDCC CDC83 XXXX
5234 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-04-10 21:23 | 2018-04-11 03:09 | 10 | 346 | 4208331 | 3460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50KVA XFMR/ ISO 38830785D20805/ COD 10crew required bad 50 kva 7200 trans trk app crew arrived replaced trans restoored power at 03:09
5235 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-08-26 18:22 | 2008-08-26 21:24 | 19 | 182 | 55264-1 | 3458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3309001//REPLACED INSULATOR ON POLE # 389 -21 , RESTORED POWER AT 2124 //VER/CRB JEFF COMBS IDC XXXX
5236 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-12-21 14:34 | 2008-12-21 19:00 | 13 | 266 | 61550-1 | 3458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27766586 // FOUND 405 POLE BURNTED OFF, NEED POLE AND TECH AND LINE CREW TO MAKE REPAIRS, HAVE TALKED TO MR. REYNOLDS, ALSO HAVE FIRE OUT ON THIS POLE AT THIS TIME FAULT POLE 38830018000215 L3/HFP IDC XXXX
5237 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-08-18 11:13 | 2017-08-18 15:20 | 14 | 247 | 4275131 | 3458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RIGHT HAND RECLOSER LOCKED OUT ON 794-29/PATROLNG/A PHASE COD: 14 //PIN ISULATOR FAILED ON POLE 794-33 AND BURNED CONDUCTOR INTO//BEING HELD UP BY HOT TAP///CREW ENROUTE///WILL HAVE TO OPEN OTHER TWO RECLOSERS WEN CREW GETS HERE TO MAKE REPAIRS////OPENED 2 OCR 1425 VER/AWD
5238 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-09-05 00:04 | 2008-09-05 04:52 | 12 | 288 | 59468-1 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3116701// COD-12// WR26121749// POLE 1147-5524 65T 1147-5576 300A SB RELEASED BY CREW 078S08/CREW PREPARING TO TEST UNDER GROUND CABLE/VEM/FETR0600/BAD UG CABLE/POSSIBLE DIG IN/ISOLATED CABLE AND PLACED IN ABNORMAL DATA BASE/BACKFEED REMAINING XFMRS FROM XFMR 1147-635/POWER RESTORED AT 0452/PLEASE CLOSE TICKET/THANKS/VEM// 1147-628 & 1147-624 OUTAGED ONLY - COD 12 VER/LDA IDCC CDC83 XXXX
5239 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2017-01-07 10:46 | 2017-01-07 12:54 | 27 | 128 | 4275131 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | I REPLACED A FAILED HOT TAP ON POLE 211-358. RESTORED AT 1254. 37830211C00358 VER/AWD L3/HFP XXXHFP AJB
5240 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-16 14:00 | 2013-01-16 14:27 | 128 | 27 | 4611951 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ASSOCIATED WITH POWERON ORDER 4609341 - BAS INSULATOR // LOAD TRANSFERRED // OPENED NORMAL OPEN POINT TO MAKE UP LOOPS AND RESTORE CUSTOMERS TO THEIR NORMAL FEED// BACK ON AT 1427// 128 RESTORED ON THIS OUTAGE// OTHER 5 ON 4609341 // VER/TOM L3/TOM IDC XXXX
5241 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-12-12 01:20 | 2011-12-12 06:18 | 24 | 298 | 4169911 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SDB / 0120 / LINE FUSE OPEN AT POLE 1125-A-253. CC 24. --- SDB / 0330 / BAD TR AT POLE 1125-A-257, ISOLATED & LINE FUSE CLOSED AT POLE 253, REST 22 CC. VER/ARN IDCC CNT26 XXXX
5242 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-02-04 16:18 | 2020-02-04 23:30 | 8 | 432 | 4362111 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DDC Tags DOL 990228 // 297-1 to 297-8 crew required trucks to 1 pole tagged 297-6 to ddc no grounds flaggers required #2 alum Released by crew 078S03///repairs made///complete BR/ ISO 38830297000006/ COD 8 L3/HFP
5243 | Hazard | 3303902 | LESLIE | WOOTON | 2013-08-13 17:39 | 2013-08-13 18:51 | 48 | 72 | 4662371 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKEN,WILL HAVE TO OPEN MAIN LINE TO REPLACE OPENED LINE AT POLE 366-D-37 AT 17:39 VER/SEF
5244 | Pikeville | 3421001 | BREAKS | CITY | 2019-07-27 07:12 | 2019-07-27 12:00 | 12 | 288 | 4797991 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Line fuse blown on pole 220-228 will patrol/// Cross arm split out on pole 243-5/// will need crew talked to Dennis Massey he knows what material we need/// Changed bad crossarm Closed line fuse in @12:00 and restored service L3/HFP
5245 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-08-01 13:54 | 2008-08-01 15:30 | 41 | 96 | 63456-1 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 139-293. I WILL LIFT HOT LINE CLAMP ON POLE 139-46. GO TO RECLOSER AND PICK EVERYTHANG ELSE UP. GOT HOT LINE CLAMP ON AT POLE 139-46 EVERYTHAG SHOULB BE BACK ON. VER/HFP IDCC PN471 CHANGED COUNT FROM 141 LOOKS LIKE ONE MISSMAPPED CUSTOMER AND CUSTOMERS ON PH A NOT B XXXX
5246 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-09-15 19:06 | 2011-09-16 14:18 | 3 | 1152 | 4874761 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | U.G. TRANSFORMER, CUSTOMER AT 182 WALNUT DR STILL OUT WILL SOMEONE TO LOCATE U.G. SERVICE AND MAKE REPAIRS, NEED TO SEND E-MAIL TO TIM HALL AND HAVE A CREW TO WORK THIS. RELEASED BY CREW 074S05 //VER/CRB IDC XXXX
5247 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2020-02-06 11:57 | 2020-02-06 19:09 | 8 | 432 | 4369911 | 3456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @73-C-199, checking. Inactive cutout busted @ 49-355, isolated and closed L/F back in @1909.//cod 8
5248 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-09-13 20:23 | 2010-09-13 20:53 | 115 | 30 | 66216-1 | 3450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPLACE BROKEN CROSSARM AT POLE 1099-6547. OPENED RECLOSER AT POLE 1099-3593 AT 2023/FETR2130/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST AT 2053/PLEASE CLOSE TICKET/THANKS/VEM // COD 115// VER/DBM IDC XXXX
5249 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-06-27 15:54 | 2015-06-27 16:24 | 115 | 30 | H4676061 | 3450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | *** SEE 4676061** C PHASE SWITCH BROKE ON 38830777000006 (41 CUTOMERS)/ OPENED RECLOSER 38830777000020 (115 CUSTOMERS) @ 1554 AND CLOSED @ 162438830777000006/ ISO 38830777000020/ COD 156/ DUPLICATE IN HOIS/ VER/BOW L3/DKG SEE 4676061 FOR ORIGINAL OUTAGE
5250 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-05-17 13:50 | 2016-05-17 16:20 | 23 | 150 | 4226081 | 3450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | POLE 818-180 ON FIRE//GOING TO OPEN LINE FUSE ON POLE 819-1 TO PUT FIRE OUT AND CHANGE CUTOUT//POLE BURNED HALFWAY INTO///MADE SAFE WITH CROSSARM//PLEASE SEND TO CLIFF FREEMAN TO HAVE JOB WRITTEN TO BE CHANGED//OPENED FUSE AT 13:50///CLOSED AT 16:20//COMPLETE//EM/ ISO 38820819A00001/ COD 23/ VER/BOW AJB
5251 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-01-02 17:44 | 2020-01-02 20:59 | 30 | 195 | 4204991 | 3447 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c phase 30t open @ 1147-4036.restored @ 19:30.. bad c/o @ 1147-4038 Released by crew 078S07///repairs made///complete BR//cod 30// L3/HFP
5252 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-08-16 14:29 | 2019-08-16 15:22 | 65 | 53 | 4897311 | 3445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot tap burnt off sturrip on rec pole 164-110 servicer to make repairs c phase only L3/HFP
5253 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-12-26 12:20 | 2009-12-27 17:02 | 2 | 1722 | 66420-1 | 3444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE BACK TO NORMAL
5254 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-05-15 18:11 | 2018-05-15 19:35 | 41 | 84 | 4354851 | 3444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | right hand recloser out on pole #194-262 will patrol// Bad cutout on pole #194-91 /// this cutout is open and feeds nothing/// will isolate ctout/// Isolated bad cutout and closed recloser in @ 19:35 and restored service COD-66 IOS OCR 37820194C00264/// C phase only
5255 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2009-07-05 14:13 | 2009-07-05 19:00 | 12 | 287 | 66344-1 | 3444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, P, TATROLLING LINE//C PHASE ONLY IS OUT//COD 12// @ 1745 BOB SHOT LINE DID NOT HOLD. WILL CONTINUE PATROLT, BAD CUTOUT, POLE#1040-D-143,// VER/DBM IDC XXXX
5256 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2018-08-06 10:20 | 2018-08-06 17:30 | 8 | 430 | 4912971 | 3440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | pole 1086-60,prim bushing blowed out of a 25kva csp xfr.will have to replace it.crew enroute shortly.if we set up in road,will need flaggers.need long reaching bucket to work this also.NOTE NEW FETR/////////REPLACED XFR&RESTORED POWER,ALL OK AFTERWARDS
5257 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-02-02 18:00 | 2014-02-03 08:19 | 13 | 859 | 4337891 | 3439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW REQUIRED YARD DOG 3 MEN ARRESTOR AND VINES BACK YARD/FUSE BACK IN AT 2135 HRS 1 CUSTOMER AT 185-184 STILL OFF RELEASED BY CREW 078S03 /CREW ON SITE/FETR0900/VEM/REPLACE D LA POWER RESTORED TO ONE CUST @0819/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB IDC XXXX
5258 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-07-29 12:09 | 2008-07-29 15:20 | 18 | 191 | 61762-1 | 3438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ON SITE, POLETOP BROKE OFF , POLE#1064-67, MAKING REPAIRS, TWO PHASES ALREADY OUT, OPENED OTHER PHASE AT 1346// BACK ON @ 1520 IDC BELFRY TOLER CUSTOMERS WERE TRANSFERED TEPORARILY TO BARENSHEE POUNDING XXXX
5259 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-02-22 02:49 | 2022-02-22 06:00 | 18 | 191 | 4525831 | 3438 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 900-27, transformer cutout on p-900-31 broken and hanging down pole wraooed around neutral.changing cutout/ transformer on pole 38830900000027 is fed by line fuse on pole 38830900000027 added 4 customer to customer count
5260 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-07-17 14:41 | 2013-07-17 20:30 | 17 | 349 | 4537881 | 3433 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 45-7269 REPAIRED SEC. ON TRANS. POLE CUT LOOPS ON POLE 45-7270//RESTORED APPROX 10 CUST @ 1620// SEND TO BOBBY R. BEING TRANS. TO INSTALL ON 45-7275 50KVA RELEASED BY CREW 078S08//COD 17// VER/DBM IDCC STP MISSING XXXX
5261 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-07-31 13:00 | 2022-07-31 13:33 | 104 | 33 | 4642681 | 3432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recl 38820841A00146 opened when servicer attempted to restore a TR and cutout broke at 38820841B00139 when he closed it--TR 38830912C00007 never opened
5262 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2014-04-12 22:28 | 2014-04-13 08:00 | 6 | 572 | 4599111 | 3432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 1123-6560 35/6 TELEPHONE POLE ROTTEN FELL ON HOUSE NEED 40/5 25KVA TRAN. OIL BAG TRUCKS TO POLE OPENED LINE FUSE ON 1123-6559 SEND TO BOB REYNOLDS RELEASED BY CREW 078S08 VER/TOM L3/TOM IDC XXXX
5263 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-06-05 13:06 | 2020-06-05 20:15 | 8 | 429 | 4963821 | 3432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout on pole 1057-D-11 will make repairs..Got line fuse back in at 20:15,Customer at METER #533 745 924 a Piece of cutout cracked window and chipped paint on hood of truck.//SENT TO CLAIMS
5264 | Hazard | 3420001 | SOFT SHELL | VEST | 2012-05-09 07:03 | 2012-05-09 15:13 | 7 | 490 | 4763281 | 3430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830133000107 TOP OF POLE BURNT OFF 40/4 NEED REPLACED, C/O, ARRESTOR, BRKT, DEADEND COMPLETE, CLEVIS SPOOL, GUY. CREW REQUIRED. RELEASED BY CREW 077S08///ON ITE CHANGING POLE.. ///VER/CRB L/3 CRB IDC XXXX
5265 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-06-02 23:28 | 2016-06-03 01:35 | 27 | 127 | 4289651 | 3429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 80T FUSE OUT ON POLE 1098 -260. DUE TO BAD CUTOUT ON POLE. C PHASE OUT ONLY. REPAIRS MADE CHANGED BAD CUTOUT. FUSED UPEVERYTHING OK VER/AWD L3/HFP XXXHFP AJB
5266 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-01-04 14:31 | 2018-01-04 15:30 | 58 | 59 | 4706471 | 3422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line basket burnt off hendrix, crew to replace Released by crew 078S07 back on 1530
5267 | Whitesburg | 3401301 | FLEMING | NEON | 2014-11-24 08:43 | 2014-11-24 09:42 | 58 | 59 | 4760501 | 3422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER ON POLE 331-229 IS OPEN. CUT OUT BROKE DOWN ON POLE 331-256 CATCHING POLE ON FIRE. POWER RESTORED AT 9:42 11/24/2014. COD-58 ISO OCR 37830331D00229 VER/HFP L3/HFP AJB
5268 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-04-20 17:59 | 2009-04-20 19:15 | 45 | 76 | 61722-1 | 3420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3301402//CUTOUT BROKE DOWN AND CAUSED POLE FIRE . SAWED POLE OFF AND LOWERED , RESTORED POWER AT 1915 JKC ISO POLE 37830274000036 COD-45 L3/HFP IDCC TOF1713 XXXX
5269 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2019-08-28 05:51 | 2019-08-28 09:09 | 24 | 198 | 4954401 | 3420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse blown on pole 98-536..patrolled and found arrester bad on pole 98-31.will make repairs.//MADE MD TO SHOW L/F FEEDS BOTH TAPS//line fuse blown on pole 98-536..patrolled and found arrester bad on pole 98-31.will make repairs.restored.. Released by crew 074S01 L3/HFP
5270 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-03-02 21:51 | 2021-03-03 09:15 | 5 | 684 | 4294301 | 3420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfr fuse bad restored @0915
5271 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2009-02-18 11:27 | 2009-02-18 12:12 | 76 | 45 | H63604-1 | 3420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 63604-1//OPENED LINE AT 11:27 (INTERRUPTING 76 MORE CUSTOMERS, SEE H63604-1)//CLOSED 12:12////ISO// VER/DBM IDC XXXX
5272 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-12-05 02:55 | 2012-12-05 04:30 | 36 | 95 | 4443171 | 3420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE BLOWN ON 37820074000021// PATROLING/// L/A BAD ON CSP XFMR ON POLE 37820074000024// CLEARED // REFUSED //POWER IS RESTORED //VER/GAH IDC XXXX
5273 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2022-06-27 17:59 | 2022-06-28 00:18 | 9 | 379 | 4336501 | 3411 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @26-54, cutout failed @26-99 and burnt the top of a double dead end off, Paul Layne's crew coming to help with repairs. No truck access. Got pole lowered and closed the L/F back in @0018.//cod 9
5274 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2018-09-10 09:53 | 2018-09-10 21:15 | 5 | 682 | 4074491 | 3410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burnt in two on pole38821013B00017/servicer/crew required NTA Released by crew 074E09 replaced trans cutout door on 1013B17.restored power at 21:15
5275 | Pikeville | 3403001 | PIKEVILLE | CITY | 2010-06-12 10:44 | 2010-06-12 15:28 | 12 | 284 | 60669-1 | 3408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT ON POLE 48-805 BROKE DOWN AND BURNED CROSSARM ON FIRE. I OPENED ALL 3 CUTOUTS ON POLE 48-805 AT 12:00. I AM CALLING FOR LINE CREW. RELEASED BY CREW 074S01//DEWEY AKERS` CREW REPLACED THE CUTOUTS HERE, ARMS WERE NOT DAMAGED //THIS POLE IS SCHEDULED TO BE REWORKED SOON//COD 12//ISO 37830048C30805 // VER/DBM
5276 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-07-12 11:18 | 2011-07-13 15:42 | 2 | 1704 | 4530231 | 3408 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | NO POWER COMING INTO CUSTS METER BASE ON ONE LEG..UG SERVICE.NO TRUCK ACCESS..IN-GROUND SWIMMING POOL DIRECTLY BETWEEN CONDUIT COMING DOWN OUR POLE & CUSTS METER BASE.NEED TECH TO LOCATE FAULT.JRV.07/12/11 RELEASED BY CREW 080S01 // BAD SECONDARY RISER - REPLACED IDC XXXX
5277 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-10-08 23:33 | 2017-10-09 03:55 | 13 | 262 | 4426391 | 3406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CALLED CUSTOMER//NO RESPONSE// CUT ARRESTOR IN CLEAR AT POLE 429-164//COD 13//CREATED AED ENTRY ACB
5278 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-08-22 16:08 | 2011-08-22 20:30 | 13 | 262 | 4744891 | 3406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SEND TO P TOLLIVER RELEASED BY CREW 078S07/PT ON SITE FETR 21:00 WILL REPLACE CUTOUT//POWER RESTORED AT 20:30 CLOSE TKT.///COD 13// VER/DBM IDCC CDC92 XXXX
5279 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-06-05 01:27 | 2020-06-05 07:45 | 9 | 378 | 4959951 | 3402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE ON 54-29 IS BLOWN/////////LA BLOWN UP@54-163,WILL CLEAR IT UP&RE-FUSE LINE////////CLEARED LA,RE-FUSED&RESTORED
5280 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-12-23 16:12 | 2013-12-23 17:15 | 54 | 63 | 4197481 | 3402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BROKEN HOT TAP LEAD VER/CRB L3/HFP IDC XXXX
5281 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-12-26 12:55 | 2015-12-26 13:22 | 126 | 27 | 4562151 | 3402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO 4561311//CREW OPENED SWITCH BACK UP IN ORDER TO PUT LINE BACK TO NORMAL// VER/DBM AJB
5282 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2016-09-19 17:45 | 2016-09-19 21:05 | 17 | 200 | 4909891 | 3400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENING TRANSFORMER ON 69-4006. OPENED TRANS 17:45 NEED 50KVA AND 4/0 RISER MELTING OFF POLEOPENED TRANS 17:45 NEED 50KVA AND 4/0 RISER MELTING OFF POLE RELEASED BY CREW 078S08,REPAIRS MADE ALL CUST RESTORED @ 2105 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830069C14006/ COD 17/ VER/BOW L3/HFP HFPC TOF1806
5283 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2018-02-17 14:28 | 2018-02-17 16:44 | 25 | 136 | 4854971 | 3400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Bad side tap dead end insulator at pole 38820991D20101. The fault went through the 15 T on that pole. I replaced the bad insulator and all power is restored at 16:44./ ISO 38820991D40051/ COD 25
5284 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2008-03-10 00:08 | 2008-03-10 05:48 | 10 | 340 | 55767-1 | 3400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 34009001// BAD XFMR. DIFFICULT LOCATION. CREW EN-ROUTE TO REPLACE. XFMR REPLACED AND SERVICE RESTORED. SH IDC XXXX
5285 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-07-17 15:24 | 2016-07-17 20:33 | 11 | 309 | 4650271 | 3399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 ALUMINUM PRIMARY IS ROTTEN AND BROKE MID SPAN. GROUND PLACED ON THE LOWER SIDE OF TROUBLE AT POLE 37820034C40028, AND ON THE UPPER SIDE AT POLE 37820034C00031. NEED BUCKET THAT WILL REACH THE FARTHEST AND THREE MAN CREW. I TALKED TO THE FOREMAN AND WE ARE GOING TO REPLACE THIS SPAN OF WIRE. POWER RESTORED.//COD 11// VER/DBM
5286 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-07 15:37 | 2012-08-08 10:30 | 3 | 1133 | 4908591 | 3399 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 375-470, SERVES 3 CABINS WILL NEED CREW TO REPLACE 10 KVA 7200 XFMR TOMORROW RELEASED BY CREW 077S11 REPLACED XFMR POWER RESTORED VER/KEP IDCC CNT1 XXXX
5287 | Pikeville | 3421001 | BREAKS | CITY | 2008-06-29 09:48 | 2008-06-29 16:05 | 9 | 377 | 59223-1 | 3393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | THE LINE FUSE WAS BLOWN ON POLE 220-6, C PHASE COD-6 AND WE WERE GETTING BACKFEED VOLTAGE FROM ANOTHER PHASE THROUGH A TRANSFORMER BANK. VER/KEP IDC XXXX
5288 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-02-19 15:19 | 2014-02-19 17:05 | 32 | 106 | H4402621 | 3392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | THE CENTER PHASE RECLOSER IS OPEN ON POLE 356-71 COD 27 B PHASEI AM GOING TO OPEN THE OTHER TWO TO MAKE IT SAFE B PHASE OUT ORIGINALLY COD 27 OPENED OTHERS @_15:10_____INTERRUPTING 32 MORE WIRE IS DOWN AT POLE 332-88 , WE NEED CREW TO PUT WIRE BACK UP . THE CENTER PHASE RECLOSER IS OPEN ON POLE 356-71 I AM GOING TO OPEN THE OTHER TWO TO MAKE IT SAFE. IOPENED AT 15:10 ON @1705 ***DUPLICATE IN HOIS FOR ADDITIONAL 32 FROM 1519 TILL 1705 VER/SEF
5289 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-04-05 20:54 | 2010-04-06 00:05 | 26 | 191 | 59147-1 | 3391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BROKEN CUTOUT AT POLE 38830206C02209, CUTOUT REPLACED AND ALSO REPLACED BLOWN FUSE AT 38830206A31197, BAD 50 KVA ON POLE 38830206A31197, LINE FUSE CLOSED AT 22:50, TRUCK OK, CREW NOTIFIED, 1 XFMR OUT VER/LDA AJB
5290 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2019-06-20 00:47 | 2019-06-20 14:54 | 4 | 847 | 4551721 | 3388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer no answer//bad transformer,manual,need r/w crew and line crew,25kva 19.9kv and cutout//bad dogs Released by crew 077S04
5291 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2011-11-16 19:07 | 2011-11-17 00:15 | 11 | 308 | 4085211 | 3388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT ON POLE 24-375 BROKE INTO. SEND TO STEVIE RAY. HE SAID HE WOULD PICK IT UP ON HIS WAY IN. RELEASED BY CREW 074S01 IDC XXXX
5292 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-11-14 14:23 | 2011-11-14 15:40 | 44 | 77 | 4075431 | 3388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY BURNED TI TWO UNDER A STURRIP ///VER/CRB IDCC PN702 XXXX
5293 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2013-04-29 12:21 | 2013-04-29 15:42 | 45 | 201 | 4056311 | 3387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE351-70, BAD CUTOUT ON POLE 351-135 CAUSING TOP OF POLE TO BURN OFF, ISOLATED ON POLE 351-78.CLOSED LINE FUSE ON 351-70 AT 13:24. MADE REPAIRS & INSTALLED LINE FUSE ON POLE 351-78 WITH 10T FUSE. RESTORED POWER AT 15:42//COD 45// VER/DBM IDC XXXX
5294 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-08-18 09:32 | 2009-08-18 12:40 | 18 | 188 | 63927-1 | 3384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100KVA XFMR. I WENT AHEAD AND OPENED AT 10:10 __CUSTOMERS ONLY HAD HALF POWER. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. RELEASED BY CREW 076S02. CREW ONSITE- REPAIRS UNDERWAY. REPAIRS COMPLETE. RESTORED AT 12:40. VER/KEP L3/KEP IDC XXXX
5295 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-05-14 04:58 | 2009-05-14 11:14 | 9 | 376 | 54582-1 | 3384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3010601 -BAD CUTOUT ON POLE 39831148B20282 BURNT TOP OF 40 CL V5 POLE OFF AT 111 FLORIDA DR--RIGHT BESIDE RD VER/KEP L3/KEP IDC XXXX
5296 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-09-25 19:42 | 2018-09-26 09:48 | 4 | 846 | 4157941 | 3384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20T lf open 115-94,,bad c/o @ 115- 319. No trucks to pole/arrived RM power on @09:48 please close tic RM COD-4 ISO 38830115D00094
5297 | Hazard | 3309302 | VICCO | JEFF | 2013-11-25 07:22 | 2013-11-25 13:00 | 10 | 338 | 4071771 | 3380 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEAD BURNT INTO ON XFMR POLE, CALLING FOR BIGGER XFMR LEADS, P HICKS TO BRING WIRE // ALSO LIFTED TAP TO TR 185 @ 1240HOT LEAD BURNT INTO ON XFMR POLE, CALLING FOR BIGGER XFMR LEADS, P HICKS TO BRING WIRE. TOOK TAP OFF AT 12;41, BACK ON AT 13:00 COD-10 PART OUT & 3 OUT SEE H4071771 VER/HFP L3/HFP IDC XXXX
5298 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-09-29 05:33 | 2012-09-29 13:57 | 14 | 504 | 4098011 | 3372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / WILL CHECK AT REGULAR TIME POLE 1123-4116 40/5 POLE BURNT OFF TRUCK TO POLE POLE 1123-4023 CUT LOOP POLE 1123-4042 50T ON 08;50 RELEASED BY CREW 078S08/CREW ON SITE/NEW POLE ENROUTE/FETR 1530/VEM ///VER/CRB L/3 CRB IDC XXXX
5299 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-06-09 08:13 | 2010-06-09 12:30 | 21 | 257 | 59024-1 | 3372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | FOUND A BAD 8 FT CROSSARM ON POLE 1098-9001, AND BAD CUTOUT, HAVE LOOPS CUT ON POLE 1098-3514, CLOSED IN LINE FUSE ON POLE 1098-3107 AT 10:15, REPAIRS COMPLETE POWER RESTORED AT 1230 IDC XXXX
5300 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2011-07-07 09:14 | 2011-07-07 14:09 | 13 | 295 | 4480231 | 3371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1099-6093 BAD 50KVA NEED 75 KVA 350MC RISERS 4/0 SEC. RISERS MELTED OFF POLE SEND TO VERNON RELEASED BY CREW 078S08/CREW ON SITE/CHANGING XFMR AND INSTALLING NEW XFMR TO SPLIT LOAD/NEW XFMR ON 1099-6027/FETR1430/VEM// @ 1311 GOT 8 CUST BACK ON/POWER RESTORED TO REMAINING CUST 1409/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14//COD 13//SERVICER SENDING CHANGES TO MAPPING// VER/DMB IDC XXXX
5301 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-01-18 10:14 | 2011-01-18 15:51 | 10 | 337 | 62243-1 | 3370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED A BAD CUTOUT ON POLE 265-171 PLEASE CLOSE THIS ORDER//IT FORCE CLOSED IDC XXXX
5302 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-05-01 13:58 | 2011-05-01 17:05 | 18 | 187 | 53227-1 | 3366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | // ON POLE 955-D-291 THERES A LOOP BURNED OPEN// REC @ 979-C-48 NOT OPEN THIS IS BEFORE THE REC, I WILL OPEN TO MAKE REPAIRS// REPAIRS MADE ALL BACK TO NORMAL//COD 18//ISO 38830955D00291 // VER/DBM IDC XXXX
5303 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-10-23 22:44 | 2021-10-24 02:02 | 17 | 198 | 4006961 | 3366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Cutout 38830020D16046/ broke cutout on pole 20-6046/ crew required no trucks/ grounded and tagged to B. Ramey at pole 20-6015//Complete BR
5304 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2018-05-10 15:07 | 2018-05-10 17:40 | 22 | 153 | 4332421 | 3366 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | Replacing bad cutout on pole 48-244//MADE MD TO SHOW RISER ON THIS POLE
5305 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-06-19 18:41 | 2014-06-20 13:22 | 3 | 1121 | 4116941 | 3363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S09//BAD CSP XFMR//TRUCKS TO POLE//45-B1-2224// 25KVA %26 C/O.LMRRELEASED BY CREW 078S09//BAD CSP XFMR//TRUCKS TO POLE//45-B1-2224// 25KVA %26 REPLACED 25 KVA ALL POWER RESTORED AT 13:22 PLEASE CLOSE TICKET THANKS DWW
5306 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2014-06-25 14:40 | 2014-06-25 16:02 | 41 | 82 | 4155571 | 3362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE MAKING REPAIRS TCM// FRAMED DOWN CUT BURNT PART OFF TCM// AJB
5307 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-07-27 23:22 | 2020-07-28 01:07 | 32 | 105 | 4241521 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | Bellefonte/Westwood 12kV Ckt to replace sws at 38830020C41026, load was transferred on SOS: 20-176061 Rev: 3 & remaining 32 CC out at 2331 (7/27/20) On at 0107 (7/28/20)
5308 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-08-06 04:39 | 2008-08-06 07:19 | 21 | 160 | 65804-1 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3007903 -BAD RECLOSER PUT IN BYPASS BACK ON COD-21 VER/HFP IDC XXXX
5309 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2009-09-26 10:29 | 2009-09-26 12:29 | 28 | 120 | 63680-1 | 3360 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOST TRANSMISSION LINE CREWS WORKING TO RESTORE VER/KEP L3/KEP IDC XXXX
5310 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2012-07-25 20:55 | 2012-07-25 21:27 | 105 | 32 | 4829311 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEE ORDER 4828521//OPENED RECLSOER IN ORDER TO MAKE REPAIRS//COD 122// VER/ARN
5311 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-01-23 17:21 | 2015-01-24 01:21 | 7 | 480 | 4953571 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT. 8FT ARM BURNT IN TWO. STATION ZONE. CREW REQD. RELEASED BY CREW 078H12/ 69-611/ CREW ON SITE ///FETR 02:00//// JEH/ REPAIRS COMPLETE POWER RESTORED @ 01:21 RELEASED BY CREW 078H05 SEE ORDERS 4955391, 4954241, 4953571// VER/DBM L3/HFP HFPC MCCNI CCAE CDC85 FEC57 TON0132 AJB
5312 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-08-10 17:50 | 2022-08-10 20:38 | 20 | 168 | 4719211 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A Phase rec open // broken xfmr c/o on 1080-157 // repairs made & restored @ 20:38
5313 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-02-20 00:15 | 2015-02-20 04:55 | 12 | 280 | 4046221 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE IS BLOWN WILL REFUSE/// BAD 50 KVA 19.9 TRANSFORMER CAN USE TRUCK/// STREET IS SNOW COVERED NEED 4 -WHEEL DRIVE BUCKET AND CREW RELEASED BY CREW 074H17CREW ON SITEXFORMER CHANGED RESTORED AT 04:55AM 37830215A00009 VER/CRB L3/DKGXXXX
5314 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2013-04-17 18:48 | 2013-04-17 23:28 | 12 | 280 | 4020291 | 3360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RECLOSER OUT DUE TO BAD 6 INCH DISC INSULATOR ON B PHASE RECLOSER LOAD SIDE. CREW ON THE WAY. OPENED A AND C PHASE AT 22:59 CLOSED BACK IN AT 23:28. REPAIRS MADE EVERYTHING BACK ON. VER/ARN IDCC PH A IS CENTER CHANGED COUNT FROM 16 XXXX
5315 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-03-19 13:37 | 2009-03-19 17:35 | 38 | 238 | 60128-1 | 3356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP FOUND POLE 901-5052, TO BE BURNTED OFF, ABOUT 3 FT OF THE TOP, HAVE HOT TAP LIFTED ON POLE 901-5038, CLOSED IN LINE FUSE ON POLE 902-4627 AT 14:27, RESTORED ALL POWER BUT FOR 2 CUST, WHERE POLE IS BURTNED OFF,MR. TOLLIVER IS HERE NOW TO MAKE REPAIRS RELEASED L3/HFP IDC XXXX
5316 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-02-09 15:16 | 2018-02-09 17:25 | 26 | 129 | 4821281 | 3354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Stirrup burnt off on 37830378C00273. Single phase out (a-cod: 26). Opned A ph recl on 37830378C00015. Made up stirrup and re-energized between 378-273 and 378-15 at . Closed recloser on 378-15 @ stirrup burnt on pole 278-273.. replaced stirrup and hotline clamp. closed recloser, power restored @ 17:25
5317 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2022-02-11 22:48 | 2022-02-12 02:05 | 17 | 197 | 4475921 | 3349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830309000012 rec open--38830309000022 wire down-crew req--ds021222 Released by crew 078S01,repairs made all cust restored @ 0205 please close ticket thanks.bt//cod 17
5318 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-09-11 06:44 | 2017-09-11 11:23 | 12 | 279 | 4345341 | 3348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED CUST BACK - STILL OUT & NEIGHBORS LOOP BURNED INTO ON POLE 426-197 CALLING CREW FOR HELP RELEASED BY CREW 077S12. POWER RESTORED @11:23 COD-12 ISO PO @ 37830426B00197 VER/HFP L3/HFP SJG
5319 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-04-03 14:21 | 2010-04-03 19:25 | 11 | 304 | 58030-1 | 3344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ROTTEN FELL 820-182. LINE FUSE BLOWED ON POLE 820-180 VER/KEP L3/KEP IDC XXXX
5320 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-05-26 00:54 | 2012-05-26 03:50 | 19 | 176 | 4832181 | 3344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "C" PHASE 12KV FUSE TO STEPDOWN BLOWN - 19 CC // OPENED "C" PHASE RECL AT POLE 121-258// CHECKED FUSE TO STEPDOWN, CUTOUT CRACKED, OPENED "C" PHASE 34KV FUSED DISCS, REPLACEDE CUTOUT, CLOSED "C" PHASE 34KV FUSED DISC, REFUSED 12KV FUSE ON PH C // CLOSED "C" PHASE RECL ON POLE 121-258 RESTORING ALL CUST AT 0350 //VER/GAH IDCC CDC92 XXXX
5321 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-04-29 14:28 | 2014-04-29 17:24 | 19 | 176 | 4647901 | 3344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ONPOLE 9-C-74 TOOK OUT TR FUSE & LINE FUSE ON SAME POLE (19 CUST TOTAL) REST @ 1724 ISO LF & TF @ 37820009C00074 VER/HFP L3/HFP IDCC TON1729 XXXX
5322 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-10-13 10:32 | 2015-10-13 16:26 | 30 | 354 | 4344241 | 3341 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED LINE @338-141 HAVE POLE BURNT OFF @ 338-142 LIN RESTORE @1215 RELEASED BY CREW 077S01/FINAL CUST. 1626// VER/ ADH L3/HFP XXXHFP AJB
5323 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-01-14 12:50 | 2017-01-14 15:18 | 31 | 148 | 4297331 | 3340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 450-58 BURNED OFF DUE TO BROKEN CUTOUT. OPENED FUSE ON POLE 37830450B00223 AT 12:50 (31 CUST) LINE CREW IN ROUTE TO MAKE REPAIRS. ISOLATED TROUBLE ON POLE 450-256 AND CLOSED FUSE 37830450B00223 AT 1400. REPAIRED AND RESTORED POWER 37830450B00256 AT 1518 (15 CUST)/ VER/BOW L3/HFP HFP AJB
5324 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-09-21 10:22 | 2013-09-21 21:30 | 5 | 668 | 4872871 | 3340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OPEN 496-80 POLE TOP BURN OFF 496-69 LINE CREW AN FLAGGERS BIG BUCKET TO POLE CAN LOWER PRI AN NEU DOWN ON POLE ,DOUBLE DEAD END POLE//DDC HOLD TAG PLACED ON FUSE POLE// NO. 2 AL. WIRE PRI AN NEU DOWN ON POLE ,DOUBLE DEAD END POLE, GR. AN TAG 496-80 TO DDCLINE FUSE OPEN 496-80 POLE TOP BURN OFF 496-69 LINE CREW AN FLAGGERS BIG BUCKET TO POLE CAN LOWER NO. 2 AL. WIRE PRI AN NEU DOWN ON POL VER/ARN IDC XXXX
5325 | Pikeville | 3407103 | TOPMOST | KITE | 2009-01-11 07:48 | 2009-01-11 10:35 | 20 | 167 | 54199-1 | 3340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830233B40149 3407103// POLE FIRE ON 37830233000138, FUSE OPEN ON POLE 233-149 //ISO//COD 20// TEMP REPAIRS MADE ON POLE 138, WILL SEND ORDER TO TECH FOR PERMNT REPAIRS, SPAN TO POLE 138 DE-ENERGIZED / GXJ MD FILED VER/LDA L3/KEP IDCC PN240 XXXX
5326 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-05-03 21:55 | 2010-05-04 04:51 | 8 | 416 | 55434-1 | 3328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100KVA 7200 120/240, TRUCK OK, CREW REQUIRED, SEND TO V MULLINS RELEASED BY CREW 078S05/CREW TRYING TO LOCATE NEW XFMR/FETR0600/VEM/CREW ON SITE CHG CUTOUT AND LA/TAKING DOWN OLD CAN/NEW XFMR COMING FROM HUNTINGTON W.VA./VEM/REPAIRS MADE ALL CUST RESTORED 0451/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDC XXXX
5327 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-11-20 13:29 | 2017-11-20 14:33 | 52 | 64 | 4588381 | 3328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Step down on pole 38831126A40841 has a broken weld and is leaking oil, talked with Tim Hall, he is getting a line crew and Enviro-Pro to come and take care of this, they will need a 333 S/D. No outage yet but crew will have to open up to make repairs. All truck accessible. Released by crew 074S05//repairs made opened @ 13:29 // closed 14:33/ ISO 38831126A40841/ COD 52
5328 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-04-28 02:47 | 2016-04-28 09:43 | 8 | 416 | 4136011 | 3328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING LINE/MD FILED FOR MISMAPPED CUSTOMER, BAD DEAD-END INSULATOR, ALSO NEED NEW CUTOUT AND T-BRACKET, FAULT POLE IS 250-161, WILL NEED CREW RELEASED BY CREW 077S02 MADE REPAIRS AND RESDTORED POWER AT 0943 CREW 077H01
5329 | Hazard | 3303902 | LESLIE | WOOTON | 2015-10-01 14:01 | 2015-10-01 20:10 | 9 | 369 | 4299511 | 3321 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD BURNT TOP OF POLE INTO//ISO 37830485000023//ISO 37830485000023/ COD 9/ VER/BOW L3/HFP XXXHFP
5330 | Hazard | 3303901 | LESLIE | HYDEN | 2019-05-11 12:28 | 2019-05-12 16:08 | 2 | 1660 | 4253001 | 3320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | MADE MD TO SHOW A MIS-MAPPED CUST//COD SHOULD BE 2//. pole 37830340000124 broke. manual. crew req. row crew req. will work 5/12/19 Released by crew 077H11 Isolated grounded and tagged to jeff combs will work on it AM//ENERGIZED @ 1608 ON 5-12-2018
5331 | Hazard | 3310502 | HADDIX | CANOE | 2015-10-24 12:06 | 2015-10-24 14:44 | 21 | 158 | 4373151 | 3318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN ON POLE 75-73 PULL OUT OF SLEEVE I WILL BE WORKING ON THIS WHILE CREW COMES OF OTHER TROUBLE// VER/ ADH --- SEE EMAIL TIME SEQUENCE ISSUE IN POWERON // CHANGING TIME OFF ON THIS TO TIME OF FIRST CALL -- L3/HFP HFPC TOF 1150 AJB
5332 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2009-01-18 18:45 | 2009-01-18 22:00 | 17 | 195 | 58117-1 | 3315 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 28107945 @ 1928 POLE TOP BURNT OFF, NO TRUCK ACCES POLE IS ABOUT 30-40` OFF ROAD, CREW ENROUT TO ACCESS POSSIBILITIES OF GETTIN YARD DOG IN TO SET POLE. / COD-17 / VER/LDA L3/KEP
5333 | Pikeville | 3421001 | BREAKS | CITY | 2013-09-12 12:36 | 2013-09-12 15:00 | 23 | 144 | 4842431 | 3312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED INTO AT POLE 220-332. I AM GOING TO OPEN LINE FUSE ON POLE 220-389 LONG ENOUGH TO REPAIR LOOP. I OPENED LINE FUSE ON POLE 220-389 AT 14:40, (5 CUSTOMERS) REPAIRED LOOP, AND CLOSED LINE FUSE IN AT 15:00 COD-28 ISO PO @ 37820220D10332 SEE H4842431 FOR 5 CUST VER/HFP L3/HFP IDC XXXX
5334 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-20 08:34 | 2015-02-21 12:10 | 2 | 1656 | 4062511 | 3312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED LINE FUSE ON POLE 38820673A00012 TO CHANGE BAD TRANSFORMER ON 38820673A20298 IN ORDER # 4052741/ ISO 38820673A00012/ COD 2/ VER/BOW
5335 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-07-13 01:29 | 2010-07-13 04:56 | 16 | 207 | 65787-1 | 3312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNT OFF TOP OF POLE 188-257 ( 45/5 ), TRUCKS TO POLE, MAY GET BY WITH EXT. NEED BUCKETT TREE CREW AND LINE CREW. NEW FUSE IN LINE FUSE. RELEASED BY CREW 078S01/WR#35959059/ VER/LDA IDC XXXX
5336 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2020-12-20 03:12 | 2020-12-20 05:30 | 24 | 138 | 4787831 | 3312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 38830501000467
5337 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-10-26 14:10 | 2016-10-26 15:35 | 198 | 85 | 4055191 | 3310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 BAD CUTOUTS ON 37830449A40070 BURNT CROSSARM INTO/ OPENED RECLOSER 37830449C21498 (198 CUST) @ 1410 TO LIFT CLAMPS ON 449-70/ REC 37830449C21498 CLOSED @ 1415 (169 CUST)/ RESTORED 3 CUTOUTS AND TRANSFORMER ON 37830449A40070 @ 1535 (29 CUST)/ VER/BOW L3/HFP HFPC FP3783O449000070 AJB
5338 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-03-02 07:33 | 2017-03-02 21:20 | 4 | 827 | 4500921 | 3308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED INLINE FUSE AT 2100 20T ON POLE1137-595 TOM MCCOWN 38821137A00595
5339 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-12-18 08:29 | 2016-12-18 11:23 | 19 | 174 | 4212901 | 3306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 853-77////BAD CUT OUT ON POLE 853-108////MAKING REPAIRS////REPLACED BAD CUTOUT///CLOSED LINE FUSE ON POLE 853-77 IN AT 11:23///COMPLETE BR 3883085300007738830853000108
5340 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-02-28 08:37 | 2011-02-28 14:10 | 13 | 333 | 63818-1 | 3306 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FL.A FOUND L.A. BLOWN ON POLE 925-43, ALSO C PHASE BLOWN ON 901-21 , CHECKING NOW TCM// ISLOATED HOT TAP CLOSED 901-21 IN AT 12:37 , CREW IN ROUTE TO REPLACE L.A.OR CUTOUT, BANK ON 925-43 STILL OFF, BANK BACK ON AT 14:10 TCM RELEASED BY CREW 076H01 COD-35 VER/HFP L3/HFP IDCC CNT35 CUSTOMER WAS PART POWER SO ASSUMING ONLY ONE PHASE OPEN, NO OTHER CUSTOMER CALLS XXXX
5341 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-05-12 03:43 | 2008-05-12 09:50 | 9 | 367 | 62365-1 | 3303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT AT MOUTH OF HOLLOW BAD TRANSFORMER CSP ALL CUSTOMER ON AT 0815, WILL NEED REPLACE TRANSFOMER 24-528//3403001//VER/CRB IDC XXXX
5342 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-03-31 06:46 | 2017-03-31 11:00 | 13 | 254 | 4600611 | 3302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE IS OUT ON POLE# 95-38 WILL BE PATROLLING LINE. BAD ARRESTER ON 202. MADE UP LOOPS ON 228. OPENED TRANSFORMER ON 4602531.LINE FUSE IS OUT ON POLE# 95-38 WILL BE PATROLLING LINE.BAD ARRESTOR ON POLE #37830095000202. ALL BACK ON NOW. PULLED XFMR ON 37830095000202 @ 12:29 BACK ON @13:08 VER/AWD AJB
5343 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-12-29 10:39 | 2013-12-29 15:30 | 15 | 291 | 4209551 | 3301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNED OF , BAD CUTOUT 269B-275 . OPENED TAP ON POLE 269B-67 THIS CLEARS TROUBLE . CLOSED LINE FUSE ON POLE 269B-67 BACK IN @ 14:14 (14 CUST) , LEAVING 1 CUST. OUT ON POLE 269B-275.RELEASED BY CREW 075H04 POLE BURNED OF , BAD CUTOUT 269B-275 . OPENED TAP ON POLE 269B-67 THIS CLEARS TROUBLE . CLOSED LINE FUSE ON POLE 269B-67 BACK IN @ 14:14 , LEAVING 1 CUST. OUT ON POLE 269B-275. PUT TAP BACK ON @ 15:30 , ALL POWER BACK ON. ENTERED MD COD 15 ISO LF 37830269B00067 VER/HFP L3/HFP IDC XXXX
5344 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-11-29 01:37 | 2015-11-29 02:07 | 110 | 30 | H1237574-1 | 3300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | **THIS IS DUP OF 4490401** TO REFLECT WHEN B PHASE OCR OPENED**POLE 43-12 BAD CO, BURNT OFF 8ARM//WILL HAVE TO OPEN B PHASE RECLOSER WHEN READY TO MAKE REPAIRS//TOMPOLE 43-12 BAD CO, BURNT OFF 8ARM RELEASED BY CREW 078S07.. CREW ON SITE TO CHANGE CROSSARM ETR 0300.. OPENED B PHASE RECLOSER ON 44-606 TO SAFELY CHANGE CROSSARM AT 01:37 (OUTAGED 110 CC) - CLOSED B&C PHASE RECLOSERS AT 0207 RESTORING ALL CUSTOMERS// - WILL NEED TO DUPLICATE OUTAGE IN HOIS TO ACCOUNT FOR SECOND OUTAGE//TOM VER/TOM L3/TOM
5345 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-15 21:40 | 2009-01-15 23:52 | 25 | 132 | 55352-1 | 3300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3409301// REPORT OF WIRE DOWN // ROGER AND TOMMY GOING TO HELP STEVE//3409301// REPORT OF WIRE DOWN PRIMARY DOWN. LOOKS LIKE IT HAD A BAD SPOT IN WIRE AND LOAD BURNT IT DOWN. CREW ENROUTE TO ASSIST. REPAIRS COMPLETE. CLOSED AT 11:52. SH VER/TOM L3/TOM AJB
5346 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-06-17 09:41 | 2013-06-17 12:18 | 21 | 157 | 4354531 | 3297 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IN DELTA BANK COD-21 ISO TF 38830045D47673 VER/HFP L3/HFP IDC XXXX
5347 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-09-21 12:26 | 2017-09-21 15:29 | 18 | 183 | 4379171 | 3294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 40T OPEN @ 116-B-184, FUSE BLEW 2ND TIME, WALKED LINE. BAD ARRESTOR 118-442 38830116B00184 38830116B00442 VER/AWD VER/ALB SJG TOF12:28 (RELATED TO 4379151)
5348 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-11-25 08:14 | 2008-11-25 13:43 | 10 | 329 | 52041-1 | 3290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF,WILL NEED CREW AND MATERIALS.HAVE NOTIFIED PVILLE.NOTE FETR.POLE # 987-2.LINE IS OUT FRM STEPDOWN POLE 986-146 RELEASED BY CREW 074S06//3411801//VER/CRB IDC XXXX
5349 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-12-29 15:15 | 2013-12-29 19:28 | 13 | 253 | 4210371 | 3289 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE @ 1515 ***TAGGED FOR DDC****TOP OF POLE 38831150000251 IS ABOUT BURNED IN TWO//OPENED LF @ 1151-228 AT 15:15// GROUNDED & TAGGED TO DDC///NEED CREW // NO TRUCK APP.// DOUBLE DEAD END //CAN LOWER// RELEASED BY CREW 074S05OPENED LINE FUSE @ 1515 TAGGED FOR DDC TOP OF POLE 38831150000251 IS ABOUT BURNED IN TWO//OPENED LF @ 1151-228 AT 15:15// GROUNDED & TAGGED TO DDC///NEED CREW // NO TRUCK APP.// DOUBLE DEAD END //CAN LOWER// COD-13 ISO LF 38831150000228 VER/HFP L3/HFP IDC XXXX
5350 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2015-09-04 18:18 | 2015-09-04 20:35 | 24 | 137 | 4201301 | 3288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T OPEN 0N 1147-4676, BAD CO @ 1147-4576 WILL MAKE REPAIRS// VER/ ADH L3/HFP XXXHFP AJB
5351 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-11-23 05:44 | 2010-11-23 07:30 | 31 | 106 | 58857-1 | 3286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | PIECE OF CROSS ARM ON CUTOUT 45-7,//VER/CRB IDC CHANGED CAUSE FROM OTHER XXXX
5352 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-11-01 07:15 | 2013-11-01 13:20 | 9 | 365 | 4991181 | 3285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHECKING NOW POWER RESTORED TO 8 CUST HAD ANOTHER TICKET FOR BROKE POLE 1-CUST ON TRANSFORMER STILL OUT AT 935 GILLEY. VER/CRB L/3 CRB
5353 | Hazard | 3309302 | VICCO | JEFF | 2015-10-28 14:35 | 2015-10-28 15:42 | 49 | 67 | 4388111 | 3283 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURN OFF === MAY BEABLE TO LOWER EVERYTHING NEED LINE CREW ===HAD TO OPEN MAIN LIINE TO MAKE REPAIRES ON LOOP ON 178 TO WORK SAFE ON 14:35 CLOSED 15:42 AND MADE REPAIRES TO POLE 370 - 195 ==ALL POWER ON AT 15:42// VER/ ADH L3/HFP XXXHFP AJB
5354 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-06-01 16:21 | 2008-06-02 10:35 | 3 | 1094 | 53885-1 | 3282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400301//XFMR IS BURNED UP . IT WILL HAVE TO BE CHANGED//CREW REQUIRED// CHANGED TRANSFORMER 6 2 08 WILLIE ROBINSON VER/HFP IDCC CNT1 XXXX
5355 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2018-01-23 11:29 | 2018-01-23 14:42 | 17 | 193 | 4766641 | 3281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed and burnt top of pole off at 1112C50 i can make repairs C phase line fuse open at 1113A3 and tagged to myself made temporary repairs to 1112C50 plz send copy to Cliff Freeman to replace pole 1112C50 45-4 trk app restored power at 14:42/ ISO 38821113A00003/ COD 17 L3/HFP
5356 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-09-21 18:40 | 2020-09-21 21:53 | 17 | 193 | 4483931 | 3281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | LINE FUSE BLOWN ON POLE150-1//6A/PRIMARY DOWN FROM 150-1 TO 150-2 WILL NEED LINE CREW//NOTIFIED NORFOLK & SOUTHERN RR TO STOP ALL TRAIN TRAFFIC AND THEY DID @ 2008//APPROX 2 HOURS///oPENED OTHER FUSE UP @ 21:25//REPAIRS MADE CLOSED LINE FUSES IN @ 21:53 AND RESTORED ALL CUSTOMERS
5357 | Hazard | 3309302 | VICCO | JEFF | 2014-08-20 12:22 | 2014-08-20 13:44 | 40 | 82 | 4389901 | 3280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POSSIBLE LINE DOWN IN BACKYARD PER PAUL PRATT === INSULATOR BURN OFF POLE === HOT LINE LAYING ON TOP POLE 37830346A00315 === NEED LINE CREW POLE IS UP ON HILL MANUAL ===///OPENED STEP DOWN TRANSFROMER IN ORDER 4388421/// SAME OUTAGE === OPEN LINE AT 12:28 CLOSED AT 13:25 RELEASED BY CREW 077S03 AJB
5358 | Pikeville | 3403001 | PIKEVILLE | CITY | 2010-05-13 12:02 | 2010-05-13 14:46 | 20 | 164 | 61485-1 | 3280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLOSE LINE FUSE IN AT 14:46 ON POLE 25-59 IDCC TON1500 CHANGED COUNT FROM 38 PH C ONLY XXXX
5359 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-07-24 07:21 | 2011-07-24 09:50 | 22 | 149 | 4606661 | 3278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY C PHASE IS OPEN//COD 22// RECLOSER ON 576-140 IS OPEN PATROLLING LINE, FOUND BROKE CUTOUT ON 600-76, REPLACED CUTOUT, ALL POWER RESTORED AT 0950 CLOSE TICKET// VER/DBM IDC XXXX
5360 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2013-03-06 05:27 | 2013-03-06 10:00 | 12 | 273 | 4877471 | 3276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 168--161 AND BURNED TOP OF POLE OFF. THIS CAUSED LINE FUSE ON POLE 168-12 TO BLOW. I AM CALLING FOR HELP. WE SPLICED POLE AND CLOSED LINE FUSE IN AT 10:00 VER/TOM L3/TO, IDC ORIGINALLY FULL POWER BUT LEFT AS IS DO NOT KNOW WHEN IT BLEW XXXX
5361 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-06-21 17:26 | 2022-06-21 17:54 | 117 | 28 | 4271571 | 3276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL 1215436 // switching to restore ckt normal // cod 117//cutout on 38820721D00024 broke while trying to close it. Will need to replace //
5362 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-11-25 06:27 | 2008-11-25 14:15 | 7 | 468 | 51999-1 | 3276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830230000155, NO ISOLATION POLE, CREW REQUIRED, 45 POLE, TRUCK OK RELEASED BY CREW 078S05//3001003//VER/CRB IDC XXXX
5363 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2011-08-24 05:25 | 2011-08-24 14:30 | 6 | 545 | H4749621 | 3270 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3301701 - "B" PH RECL OUT (131 CUST) - TOP OF POLE 420-137 ROTTED OFF, OPENED OTHER 2 PH RECLS (6 MORE CUSTS) CUT DEADENDS IN POLE 419-40 TO ISOLATE, CLOSED RECLS AT 0624 RECLOSER OPEN ON POLE 419-366,.. OPENED RECLOSERS AT 05:35 CLOSED AT 06:24 ENERGIZING UP TO 419-403301701 - . OPENED RECLOSERS AT 05:35 CLO IDC XXXX
5364 | Pikeville | 3413401 | GARRETT | GARRETT | 2019-02-26 11:31 | 2019-02-26 19:18 | 7 | 467 | 4926071 | 3269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout is broke i will change..Replaced cutout and restored power @ 19:18 L3/HFP
5365 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-01-11 21:52 | 2011-01-11 23:53 | 27 | 121 | 60750-1 | 3267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38410760 //FOUND HOT TAP BURNTED OFF OUT OF THE TOP OF LINE FUSE CUT, ON VERY TALL POLE, CAN NOT REACH WITH MY BUCKET, NEED BIG BUCKET TO MAKE REPAIRS AND TWO MEN /// COD-27 ISO LF 39831097A00009 VER/HFP L3/HFP IDC XXXX
5366 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2014-11-06 21:54 | 2014-11-07 03:24 | 10 | 330 | 4709331 | 3266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LEAKING 7200-50 KVA, YARD DOG, OR MO-PADS. OPENED CAN @ 23:08 RELEASED BY CREW 078H12,,CREW ON SITE,,ALL REPAIRS MADE,,ALL POWER RESTORED AJB
5367 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-08-27 06:52 | 2008-08-27 11:55 | 14 | 303 | 55726-1 | 3264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301101//TOP OF POLE172-35 IS BURNT OFF//CALLED IN BY ERIC PRATT// VER/TOM IDCC PN37 XXXX
5368 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-10-26 06:21 | 2013-10-26 09:45 | 16 | 204 | 4964111 | 3264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE POLE 426-635 - NEED 1 MAN & BIG BUCKET - J. BAKER TO ASSISTLINE FUSE CUTOUT IS BROKE, I NEED A BIG BUCKET AND A CUTOUT , JEFF BAKER IS COMMINGLINE FUSE CUTOUT IS BROKE, I NEED A BIG BUCKET AND A CUTOUT , JEFF BAKER IS COMMING. CHANGED CUTOUT AND REFUSED COD - 16 ISO LF 37830426C00635 VER/HFP L3/HFP IDC CNT16 PHB ONLY XXXX
5369 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-10-25 05:59 | 2008-10-25 13:11 | 27 | 432 | 58822-1 | 3264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT WENT BAD BURNED TOP OF POLE OFF 272C2-1471 == WILLNEED REPLACED == OPEN ON POLE 272C2-559 == PUT MAIN LINE BACK ON AT 7:35 AM == CALLEWD FOR CREW IDC XXXX
5370 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2019-11-30 19:03 | 2019-11-30 22:15 | 17 | 192 | 4107631 | 3264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | High side of cutout broke at pole 45-528, crew required Released by crew 078H04
5371 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-03-28 12:37 | 2021-03-28 20:23 | 7 | 466 | 4391631 | 3262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Fuse is open on 374-82 patrolling /// primary needs resagged between 374-8 & 9. Linecrew required. Ground& tag placed @ 374-82. T Bobby T. Neutral cond is missing leaving fuse pole toward fault. Need 2nd ground at work location. Released by crew 078S11--RESAGD PRIMARY--PWR RESTORED @ 20:23 TBL TKT COMP RMV // DID NOT ACTUALLY OPEN SWITCH ALL PICKED UP WITH THE LINE FUSE
5372 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2015-05-13 08:29 | 2015-05-13 16:15 | 7 | 466 | 4424571 | 3262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 CUTOUT IS BAD WILL CHG ALL 3 IN BANK.POWER IS NOW RESTORED 37830048B30080 L3/DKGXXX
5373 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-01-20 06:03 | 2011-01-20 06:23 | 163 | 20 | 62903-1 | 3260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / RECLOSERS AT POLE 177D/64 OPEN AGAIN WHEN CREWS INSTALLED LOOPS AT POLE 154/149 (OUTAGE 62871-1). CC = 163. --- SDB / 0623 / RECLOSER RESTORED. FAILED CUT OUT AT POLE 178A/353 (OUTAGE 62903-1). VER/SDB IDC XXXX
5374 | Hazard | 3302703 | HAZARD | HAZARD | 2010-10-24 09:14 | 2010-10-24 12:15 | 18 | 181 | 62479-1 | 3258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE #37830272D20437 PATROLLING LINE BAD INSULATOR ON POLE #272D2-280 CREW REQUIRED.//COD 18// VER/DBM IDC XXXX
5375 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-02 17:52 | 2015-04-02 19:20 | 37 | 88 | 4260391 | 3256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT ON POLE 815-152 IS BROKEN///CUTOUT CHANGED///CLOSED LINE FUSE ON POLE 815-152 @ 19:20///COMPLETE BR COD-37 ISO LF 38830230000032 VER/HFP L3/HFP AJB
5376 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2019-10-21 12:41 | 2019-10-21 14:14 | 35 | 93 | 4176721 | 3255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL STEP DOWN OPENED ON POLE 37830445D10273//COD 35//OFF @ 1241 ON @ //CUTOUT FAILED ON POLE 445-144 burning top of pole off, made repairs restored power at 14:14.. L3/HFP
5377 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-11-03 10:50 | 2010-11-03 12:15 | 90 | 85 | 51232-1 | 3250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECL @ 1050 - 1125 TO SAFELY ISOLATE CUTOUTBAD CUTOUT ON POLE 37830201B00035 OPENED C PHASE RECLOSER ON POLE 37830225000114 FROM 10:50 UNTIL 11:25 TO SAFELY ISOLATE CUTOUT.-----ALL POWER RESTORED AT 12:15 COD-109 VER/HFP L3/HFP IDC PH A NOT C CHANGED COUNT FROM 109 XXXX
5378 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-03-05 16:32 | 2016-03-05 21:57 | 10 | 325 | 4820141 | 3250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S02 VER/ARN L3/HFP XXXHFP
5379 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-12-02 07:25 | 2009-12-02 11:35 | 13 | 250 | 54982-1 | 3250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402002/// LINE FUSE IS BLOWN AT POLE 1151-240. I AM PATROLLING LINE NOW. CUTOUT HAS BROKEN INTO ON POLE 1151-276. I AM GOING TO REPLACE CUTOUT. RELEASED BY CREW 074S01 IDC XXXX
5380 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2018-09-27 15:48 | 2018-09-27 16:45 | 57 | 57 | 4168851 | 3249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | same as outage 4168941 Released by crew 079S02
5381 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2010-07-13 10:22 | 2010-07-13 13:13 | 19 | 171 | 65906-1 | 3249 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 35962898 //LF OUT PL#280-195/SERVICER PATROLLING LINE/VEM/BAD DEAD END BELL 256-32/FETR1330/VEM/REPAIRS MADE /POWER RESTORED TO ALL CUST 1313/PLEASE CLOSE TICKET/THANKS/VEM COD-12 VER/HFP L3/HFP IDC XXXX
5382 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-01-15 13:50 | 2008-01-15 17:13 | 16 | 203 | 56923-1 | 3248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312202// HAD TO OPEN STEP DOWN TO REPAIR BROKEN POLE////VER/CRB IDC XXXX
5383 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-01-08 12:33 | 2015-01-08 13:29 | 58 | 56 | 4920081 | 3248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 68D141 BASKET BURNT OFF 556 PRI. RELEASED BY CREW 078H12/CREW ON SITE/FETR1415/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1329/PLEASE CLOSE TICKET/THNAKS/VEM// COD 58// VER/ ADH L3/HFP AJB
5384 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-08-14 22:10 | 2010-08-15 11:42 | 4 | 812 | 55074-1 | 3248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA ON POLE 38830069D47580 REFUSED AND CAME OUT. TRUCK TO POLE OK C/O DOOR AT BASE OF POLE ALSO ON THE NEXT POLE 38830070B22597 HAS XFMER C/O OPEN CANT REACH NEED A 60 STICK OF SERVICE TRUCK POLE IS NEXT TO ROAD........STAMPER RELEASED BY CREW 078E04 COD-4 VER/HFP L3/HFP
5385 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-11-25 12:57 | 2014-11-25 16:24 | 16 | 207 | 4780561 | 3247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | WILL BE REPLACING BROKEN CROSSARMS ON POLE 38830045D16030 (BUCK ARM POLE) NO CUST OUT NOW. WILL NEED TO OPEN RECLOSER ON POLE 38830045D26676 T DID NOT OPEN RECLOSERS GOING TO CUT LOOPS AT POLE 45-6033 AND ONLY HAVE 16 CUSTOMERS OFF 15:00 CLOSED LOOPS ON POLE 45-6033 AT 16:17 CLOSED CUTOUTS ON POLE 45-6030 AT 16:19 AND CLOSED CUTOUTS ON POLE 45-6071 AT 16:24 RELEASED BY CREW 078Q09 VER/CRB
5386 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-11-05 08:50 | 2010-11-05 12:18 | 32 | 208 | 53095-1 | 3246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURN-INTO POLE 1151-661. ISOLATE ON POLE 1151-471. MAIN LINE ON AT 10:28 RELEASED BY CREW 074S05 REPAIRS MADE UNTIL POLE IS REPAIRED ON AT 12:18 D SAMMONS RELEASED BY CREW 074H02//VER/CRB IDC XXXX
5387 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2010-02-13 12:10 | 2010-02-13 13:40 | 36 | 90 | 57427-1 | 3240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#33862923// POLE 20-1041 CUTOUT BURNT UP 40T FUSE//VER/CRB IDC XXXX
5388 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-08-10 12:45 | 2016-08-10 15:45 | 18 | 180 | 4757491 | 3240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM NEEDS REPLACED TODAY/,,WILL OPEN LINE FUSES AND GROUND AT 20-5509,,1 COMMERCIAL CUSTOMER HAS BEEN CONTACTED,,BAD CUTOUT HAS BURNT ARM IN HALF.CREW ON SITE,,OPENED @12:45,,,ALL REPAIRS MADE,ALL POWER RESTORED VER/KEP
5389 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-08-01 01:35 | 2018-08-01 10:35 | 6 | 540 | 4885871 | 3240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva xfr/truck accessible/may need TRAFFIC CONTROL/in curve,repairs made all cust restored @ 1035 please close ticket thanks.bt
5390 | Paintsville | 3401802 | INDEX | HOSPITAL | 2022-11-20 08:21 | 2022-11-20 09:40 | 41 | 79 | 4164561 | 3239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse melted out.. no problems on line found . refusing.p- 655-375
5391 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-03-03 20:16 | 2009-03-03 21:39 | 39 | 83 | 54747-1 | 3237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP L3/HFP IDC XXXX
5392 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-11-26 11:00 | 2010-11-26 15:09 | 13 | 249 | 59844-1 | 3237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1030-9 BURNED OFF,WILL GET CREW ENROUTE SOON AS POSSIBLE.HAVE CONTACTED D SAMMONS RELEASED BY CREW 074S06 REPAIRS MADE ON AT 15:09 D SAMMONS//VER/CRB IDC XXXX
5393 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-12-16 22:08 | 2019-12-16 23:25 | 42 | 77 | 4160351 | 3234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole fire at pole 39831147B01028, Primary put back up, and crossarm added to brace pole and make safe. 40t line fuse on 1147-686 back in at 23:25. Please send copy to tech and vernon mullins to replace pole 1147-1028 at later date, safe at this time. GH//SENT TO TECH AND LINE DEPT
5394 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-05-08 17:30 | 2012-05-08 21:21 | 14 | 231 | 4761721 | 3234 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD UNDERGROUND. NEED CREW. SEVERAL CUSTOMERS HAVE SAME PROBLEM.//// DUG UP PEDISTAL AND REPLACED HOT CONNECTORS THAT WERE BAD. POWER RESTORED. SEND THIS TO CLAIMS DEPT. THANKS OUTAGE FROM 4762181 COD-14 ISO LF 37830178A00361 VER/HFP L3/HFP IDCC CDC83, TOF1647 ESTIMATED TIME OFF, CNT1 XXXX
5395 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-07-27 12:15 | 2016-07-27 14:49 | 21 | 154 | 4689551 | 3234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I SET A HOT TAP OFF ON A BAD TRANSFORMER CUTOUT THAT DOES NOT SERVE ANYTHING NOW. POWER RESTORED AT 14:49. VER/AWD AJB
5396 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2010-03-16 10:30 | 2010-03-16 13:34 | 21 | 184 | 50641-1 | 3232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DUE TO BAD CUTOUT POLE 139B78 ABOUT 2 FOOT OF TOP OF POLE IS BURNT OFF. 30T FUSE OUT ON POLE 139B451. HOT LINE CLAMP LIFTED AT POLE 139B77. HOT TO THAT POLE. AT 12:15 FROM FUSE POLE 139B451. SEND TO DAVE SAMMONS RELEASED BY CREW 074S11 REMAINING CUSTOMERS ON AT 13:34 D SAMMONS//COD 21 IDC ORIGINAL CALL WAS FULL POWER ESTIMATED TIM OFF FROM 1007 XXXX
5397 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-03-14 03:40 | 2015-03-14 07:02 | 16 | 202 | 4192271 | 3232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY LOOP BURNT OPEN ON FIRST POLE IN LATTERAL. OPENED LINE FUSE 737-212 AND PLACED TEMPORARY GROUNDS AND TAG. REPAIRING. COMPLETED REPAIRS AND CLOSED LINE FUSE @ 7:02 RESTORING ALL OUTAGED CUSTOMERS. SH VER/TOM L3/TOM AJB
5398 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-06-16 18:04 | 2008-06-17 05:10 | 15 | 666 | 65943-1 | 3230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000802//40/5 POLE CALLED FOR CREWISOLATED ON 295-75 2 CUSTOMERS WILL BE OFF/LINE FUSE 295-1 15T BACK ON AT 2030 HRS/CREW REQUIRED //COD 15//RESTORED ALL BUT//CREW ON SITE/FETR0530 FAULT POLE 38830295000080 15T BACK ON AT 2030 HRS/CREW REQUIRED //COD 15//RESTORED ALL BUT//CREW ON SITE/FETR0530/POLE CHANGED AND POWER RESTORED 0457/PLEASE CLOSE TICKET/THANKS /VEM VER/HFP IDC XXXX
5399 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-08-26 15:05 | 2017-08-26 15:22 | 190 | 17 | 4301231 | 3230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | ASSOCIATED WITH 4300591. OPENED RECLOSERS ON 37830224D00007 TO SAFELY REATTACH WIRE ON POLE 37830225D00308. OPENED 1505-1522 VER/AWD L3/HFP HFPC CNT190 (PER NOTES ON MAP ABOUT RELOCATION OF RECL), SJGC TOF15:08
5400 | Hazard | 3309301 | VICCO | REDFOX | 2016-01-22 10:12 | 2016-01-22 11:47 | 34 | 95 | H4640201 | 3230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS WENT BAD ON POLE 276-154 BURNING PRIMARY INTO ON POLE 276-201, PRIMARY LOOP BURNT INTO ON POLE 276-24. THE LINE FUSE ON POLE 277-38 SHOULD BE ON TAP TOWARDS 218, PLEASE CORRECT MAPS. CREW IS ON THE WAY TO REPAIR. OPENED RECLOSER AT 10:12, ALL POWER RESTORED AT 11:47// VER/ ADH AJB
5401 | Hazard | 3308001 | JACKSON | S.JACKSON | 2018-12-21 12:43 | 2018-12-21 21:41 | 6 | 538 | 4586311 | 3228 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | had sec lead burned off and repair it but when closed cutout on open bank high leg transformer cutout broke and my truck wont reach it, need big bucket to change cutout open transformers at 1706 and closed one at 1724 Released by crew 077S05 L3/HFP
5402 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-04-02 16:45 | 2014-04-03 10:40 | 3 | 1075 | 4557111 | 3225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//// REMOVED SECONDARY REFUSED FUSED STAYED IN, CUT SECONDARY LEADS TO PEDISTAL AND REFUSED IT STAYED GARAGE HAS POWER. WILL LEAVE OTHER CUSTOMERS OUT TONIGHT WILL HAVE TO HAVE BACKHOLE TO FIND BOX. SEND TICKET TO GLEN AND JIM TO WORK TOMORROW VER/CRB
5403 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-07-12 08:50 | 2015-07-12 09:15 | 129 | 25 | H4779731 | 3225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE STIRRUP BURNT OFF AT STEPDOWN. COD 53 // OPENED A& B PHASES ADDITIONAL 129 CUSTOMERS AT 0850 CLOSED ALL 3 PHASES AT 0915.//C PHASE STIRRUP BURNT OFF AT STEPDOWN. COD 53 //. WE OPENED RECLOSERS AT 287-286 AT 08:50, MADE REPAIRS AND CLOSED THEM BACK IN AT 09:15. RELEASED BY CREW 074S01
5404 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-12-17 08:29 | 2016-12-17 09:00 | 104 | 31 | 4202961 | 3224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EMERGENCY OUTAGE TO ISOLATE POLE FIRE// SERVICER ON SITE WILL REQUIRE FIRE DEPT ASSISTANCE// ETA UNKNOWN AT THIS TIME// ASSOCITAED WITH 4202541 ALL CUSTOMER OUTAGED ON THIS ORDER - 108 COD//TOM - OPENED @ 0825 AND CLOSED @ 0900 RESTORED ALL BUT 4 CC// VER/TOM L3/TOM AJB
5405 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2012-07-08 23:13 | 2012-07-08 23:19 | 537 | 6 | 4602591 | 3222 | DISTRIBUTION STATION | EQUIPMENT FAILURE | BREAKER | STATION DE-ENERGIZED DUE TO FAILURE OF TRACE CREEK BREAKER AT COALTON STATION //VER/GAH IDC XXXX
5406 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-10-28 00:52 | 2022-10-28 09:49 | 6 | 537 | 4073081 | 3222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @24-B3-545, checking. Trans. fuse had melted out, refused @0949.
5407 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-03-26 06:06 | 2012-03-26 09:05 | 18 | 179 | 4616641 | 3222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WILL DISPATCH AT REG WORK TIME. LOAD SIDE PRIMARY RISER ON LINE CUTOUT HAS BURNT OPEN. REPAIRING. REPAIRS COMPLETE. RESTORED @ 9:05. SH//COD 18// VER/DBM IDC XXXX
5408 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-02-05 10:25 | 2009-02-05 14:15 | 14 | 230 | 55873-1 | 3220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NO ONE OUT TILL 1045//WR- 28381212 NEED 2- 50KVA TRANS. 4/0 RISERS 2-SEC. BRAKERS 20CUST OUTUSED 75KVA COD-14 RESTORED AT 1415/ MD FILED VER/KEP L3/KEP
5409 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2018-11-20 08:18 | 2018-11-20 17:35 | 51 | 557 | 4462631 | 3219 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED,,Pole Broke wire holding up,pole 206-2206 windstream 40-5 ,broke @ground and layed over,no interuption @ this time ,,no trucks straight line pole with xfr ,cutout,2 service drops Released by crew 078S05//opened ocr 38830206A31167 @ 1505 CLOSED IN @ 1525 UPTO SW 38830206A31170 THAT IS JUST INSTALLED//MADE MD// Released by crew 078H07 L3/HFP
5410 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2016-03-04 08:09 | 2016-03-05 10:57 | 2 | 1608 | 4814171 | 3216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND SOMEONE TO CLOSE FUSE/ ACCESSED LINE, WALKED TO TOP OF HILL TO WATER TOWER LINES O.K., FUSE OPEN AT 38830524000177, ONE HOUSE AND WATER TANK OUT. ACCESSED THIS MORNING ALL LINES UP. NEEDS CLOSED IN AT POLE # 524-177 // @ 2048 03/04 ERIC MCCOY REPORTED CUTOUT BROKEN ON TAKE OFF POLE 524-177 NEED MAN CREW TO REPLACE SEND SOMEONE TO CLOSE FUSE/ ACCESSED LINE, WALKED TO TOP OF HILL TO WATER TOWER LINES O.K., FUSE OPEN AT 38830524000177, ONE HOUSE AND WATER TANK OUT. ACCESSED THIS MORNING// VER/ ADH
5411 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-10-15 13:37 | 2009-10-15 18:05 | 12 | 268 | 65961-1 | 3216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE ON POLE 60 IS BLOWED ,, WIRE DOWN ON POLE 158 76 TREE CREWS AND LINE CREW IN ROUTE TO HELP IDC THERE ARE TWO ORDERS MIXED TOGETHER MOST OF THE CALLS DO NOT BELONG IN THIS ORDER XXXX
5412 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-08-07 09:07 | 2017-08-07 15:04 | 9 | 357 | 4233241 | 3213 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE ONLY 4 CUST FAILED CUTOUT BURNED CROSSARM IN TWO POLE 287-108. C PHASE LINE FUSE OUT. CREW ARRIVED AND WE OPENED THE OTHER TWO PHASES AT 1340. (31 CUST). CLOSED AT 1504./// PER B.O. INITAL CALLS ON `A` PHASE 9 CUST VER/HFP L3/HFP SJG
5413 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-02-10 07:08 | 2010-02-10 13:30 | 19 | 382 | 54881-1 | 3212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED AT POLE 288-22 CLOSED FUSE IN ON POLE 265-70 AT 0932. RELEASED BY CREW 074S02 2FT. OF POLE BURNT OFF MAY LOWER ON POLE S.RAY GOT 2 CUST. BACK ON AT13:30WR 33812767//VER/CRB IDC XXXX
5414 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-06-26 06:57 | 2009-06-26 20:20 | 4 | 803 | 61689-1 | 3212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RESEND RELEASED BY CREW 078S07 NEED 50KVA120/240/7.2KV,, WILL NEED 4 MEN AND YARD DOG CAN GO THROUGH GATES TO GET TO TRAN FROM 2923NEW HAVEN COURT,, , MAKE SURE TRANS HAS LIGHT ARRESTER RELEASED BY CREW 078H08---CREW ON SITE WAITING FOR TRACK BUCKET,//COD 4// VER/DBM IDC XXXX
5415 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-05-08 19:59 | 2020-05-08 22:48 | 19 | 169 | 4814831 | 3211 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP OPEN POLE 38821058B00069 ,WILL REPAIR LOOP WITH HOTTAP//////////MADE NECESSARY REPAIRS&RESTORED@22:48,ALL OK AFTERWARDS
5416 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-10-11 14:07 | 2018-10-11 17:41 | 15 | 214 | 4222521 | 3210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | top of three phase pole burnt off at 810- 298 opened fuses at pole 810-297 crew on there way// arms an cutout changed// work complete // power restored// complete tt // NOTE: WHEN FUSES OPENED ON POLE 38830810A30297 NO ADDITIONAL CUST INTERRUPTED = L3/HFP
5417 | Cannonsburg | 3110901 | WURTLAND | WURTLAND | 2009-01-22 00:54 | 2009-01-22 02:31 | 33 | 97 | 59029-1 | 3201 | TRANSMISSION STATION | EQUIPMENT FAILURE | INSULATOR | 3110901//A 69KV INSULATOR ON THE TRANSMISSION LINE HAS FAILED OPENING THE TRANSMISSION LINE VER/KEP L3/KEP AJB
5418 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-07-09 10:35 | 2012-07-09 13:15 | 20 | 160 | 4639691 | 3200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | HIGH SIDE FUSE BLOWN ON STEPDOWN AT 501-112, RECLOSER BUSHINGS LOOK BURNT, PATROLLING LINE, POSSIBLE BAD RECLOSER. PATROLLED LINE NOTHING FOUND, ISOLATED RECLOSER AND PLACED TAG, PLEASWE PUT INTO ABNORMAL. ALL POWER RESTOREED AT 1315. CLOSE TICKET DWEST//COD 20//ISO 388305010000112//AED CREATED IDC XXXX
5419 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-09-29 10:04 | 2017-09-29 23:24 | 4 | 800 | 4399071 | 3200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELEASED BY CREW 078S08, 30T OPEN @ 45-6184.CONSTRUCTION @ PADMOUNT 45 D1 6230 GO TO ELAM TO WEST HOLT (FRED MANNINGS)THROUGH GATE TO WHITE HOUSE ON HILL RELEASED BY CREW 078S07,BAD UG PRIMARY @ 45-D1-6229 REPAIRS MADE ALL CUST RESTORED @ 2324 PLEASE CLOSE TICKET THANKS.BT/// VER/DKM
5420 | Pikeville | 3120102 | STANVILLE | TRAM | 2022-02-17 12:39 | 2022-02-17 16:45 | 13 | 246 | 4491611 | 3198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM open on 1053-A-121//checking// bad 25 KVA 7.2 XFM, may have to open line up to change safely, all manual, Myles is on his way to help out// will have to open LF on 1053-A-117// will keep up with times// opened LAT @ 16:06// LAT restored @ 16:45// checking voltage on new XFM// all customers restored Released by crew 074S09
5421 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2018-07-31 15:09 | 2018-07-31 19:15 | 13 | 246 | 4880711 | 3198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | changed out 2 deadend bells and 1 insulator Restored power at 19:15/ ISO 38830429D36020/ COD 13
5422 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-02-26 03:11 | 2017-02-26 05:30 | 23 | 139 | 4423451 | 3197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP STIRRUP BURNT OFF ON POLE 286-101..WILL PATROL LINE TO MAKE SURE NOTHING IS ON IT...//COD 23// VER/DBM L3/HFP XXXHFP AJB
5423 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-02-13 13:00 | 2018-02-13 13:34 | 94 | 34 | 4837551 | 3196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Opening recloser to repair broke crossarm at 37820241C00111/ ISO 37820241C00103/ COd 94// Opened @ 13:00 and closed back in @ 13:34
5424 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-07-06 04:35 | 2009-07-06 10:30 | 9 | 355 | 51244-1 | 3195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP WR # 30597353 /// 3008003//// WELL DISPATCH IN THE MORNINGWR # 30597353 /// 3008003//// WELL DISPATCH IN THE -OPEN WIRE SPACER BROKEWR # 30597353 /// 3008003//// WELL DISPATCH IN THE -OPEN WIRE SPACER BROKE-REPLACED SPACER L3/HFP IDC XXXX
5425 | South Williamson | 3411401 | DEWEY | INEZ | 2009-12-02 22:08 | 2009-12-03 04:03 | 9 | 355 | 60702-1 | 3195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 766-B-28 RELEASED BY CREW 079S01// CHANGED CUTOUT AND RESTORED SERVICE AT 04:03 VER/KEP L3/KEP IDC XXXX
5426 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-07-03 15:50 | 2012-07-03 16:35 | 71 | 45 | 4274681 | 3195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED INTO AT 153-9, OPEN RECLOSER AT POLE 153-273 AT AROUND 15:50 TO WORK ON LOOPS.LOOP BURNT OPEN ON POLE 37830153D00009 OPENED REC. ON POLE 37830153D00253 AT 15:50 REPAIRED LOOP, CLOSED REC. AT 16:35. POWER RESTORED. ///VER/CRB L/3 CRB AJB SEE H4274681
5427 | Hazard | 3303902 | LESLIE | WOOTON | 2022-05-23 18:40 | 2022-05-24 16:13 | 5 | 1293 | 4936201 | 3193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | PER GLEN COMBS WILL BE HELD TIL MORNING TO WORK /pole burnt off at xfmr, will have to replace pole, 45/5 8 foot arm braces 2 straight arm pines 1 poletop pin 1cutout and t-bracket 3 19.9 post top insulators clevis and spool manuel, line is not isolated taged or grounded, 25 kva xfmr Released by crew 077S07
5428 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-09-20 06:32 | 2011-09-20 13:11 | 8 | 399 | 4887221 | 3192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY PHASE "C" IS OUT // 1 RECLOSER OPEN ON POLE 37830151000199, PATROLLING LINE.1 RECLOSER OPEN ON POLE 37830151000199, PATROLLING LINE. -- BROKEN CUTOUT ON POLE 37830175000018, CREW REQUIRED, JIM MULLINS NOTIFIED.//COD 16// IDCC FIRST CALL ON PH A AND SECOND ON PH B, PH A IS IN THE MIDDLE SO USING B CHANGED COUNT FROM 37 DID NOT SAY WE OPENED OTHER RECLOSERS DID NOT MAKE A DUPLICATE XXXX
5429 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-03-12 19:05 | 2016-03-12 21:30 | 22 | 145 | 4839581 | 3190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BLOWN ARRESTER ON CSP TRANSFORMER AND ISOLATED IT CLOSED LINE FUSE 880-24 @ 21:30 RESTORING ALL OUTAGED CUSTOMERS. I WILL CREATE A JOB TO REPLACE ARRESTER LATER AS I DIDNT HAVE ONE ON MY TRUCK. SH VER/KEP AJB
5430 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2010-12-01 00:28 | 2010-12-01 11:06 | 5 | 638 | 61574-1 | 3190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK REGULAR START TIMEBROKEN CUTOUT TO CHANGEBROKEN CUTOUT TO CHANGE/////REPLACED CUTOUT ON 1113-223 AND RESTORED//VER/CRB IDC XXXX
5431 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2015-12-24 01:15 | 2015-12-24 03:05 | 29 | 110 | 4554141 | 3190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF ON POLE 38830250000161/ ISO 38830250000161/ COD 29/ HOT TAP BURNT OFF @ POLE 250-161 REPAIRS MADE ALL CUST RESTORED @ 0305 PLEASE CLOSE TICKET THANKS.BT RELEASED BY CREW 078S05/ VER/BOW AJB
5432 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2022-11-26 13:34 | 2022-11-26 17:33 | 25 | 239 | 4181981 | 3187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole top burnt off 39831147A00940rec. open.. found burnt off pole top at pole 1147-940. lifted hottap on pole 1123-592. rec back in at: 14:49. crew required.. Released by crew 078H19 Repairs made, Energized at 17:33. Ticket complete.
5433 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-07-05 16:12 | 2017-07-05 21:15 | 13 | 303 | 4076451 | 3186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREES ON LINE. CUT ROW. BAD CUTOUT ON 38831089000025.RELEASED BY CREW 077H04 MD ENETERED. CHANGED LINE FUSE SIZE ON 38831065D30122 TO A 20T. CHANGED LINE FUSE SIZE ON 38831065D40129 TO A 15T. CHANGED OUT SOLID BLADE ON 38831089000008 TO A 12T FUSE. 38831065D40129/38831089000008/38831089000017 VER/AWD SJG
5434 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-05-22 18:24 | 2014-05-23 12:06 | 3 | 1062 | 4742731 | 3186 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 4 MAN TREE CREW AND A 2 MAN LINE CREW. WE NEED TO CUT TREES AND VINES AWAY FROM SECONDARY POLE. IMPOSSIBLE TO LIMB. WE GOT POWER TEMP. FOR TONIGHT. RELEASED BY CREW 074S014 MAN TREE CREW AND A 2 MAN LINE CREW. WE NEED TO CUT TREES AND VINES AWAY FROM SECONDARY POLE. IMPOSSIBLE TO LIMB. WE GOT POWER TEMP. FOR TONIGHT. WE CUT TREES AND CHECKED CONNECTIONS. I OPENED TRANS. ON POLE 128-9 AT 11:25 AND CLOSED IT BACK IN AT 12:06.
5435 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-05-11 11:33 | 2008-05-11 14:30 | 18 | 177 | 60583-1 | 3186 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUT-OUT ON POLE 166-182 ICHG, OUT CUT-OUT GOING TOPOLE 166-108 AND TRY FUSE15 -T//3008702/VER/CRB IDC XXXX
5436 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-12-12 08:59 | 2009-12-12 15:37 | 8 | 398 | 61357-1 | 3184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BUSHING ON TRANS. HAS FAILED. WE WILL HAVE TO CHANGE TRANS. I CALLED DALE AND HE IS SENDING HELP. RELEASED BY CREW 074S01//DEH - REPLACED XFMR, RESTORED AT 15:37. VER/KEP L3/KEP
5437 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2009-10-28 07:00 | 2009-10-28 13:38 | 8 | 398 | 60381-1 | 3184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP TOP 18 OF POLE 478C14066 BURNT OFF; ISOLATED TAP AT POLE 478C14065; NEED CREW TO REPLACE 40-5 POLE OR LOWER TRANSFORMER AND SERVICE DROPS; NEED NEW 7200 CUTOUT, BRACKET AND ARRESTOR; BACKLOT POLE, UNDERGROUND TELEPHONE AT BASE OF POLE; MIGHT BE ABLE TO LOWER 50KVA TRANSFORMER AND SERVICE DROPS; NOT TRUCK ACCESSABLE RELEASED BY CREW 078S12 L3/HFP IDCC FP NULLL, PN4066 XXXX
5438 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-04-08 17:25 | 2010-04-08 23:40 | 9 | 375 | 61176-1 | 3183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 34590670 // POLE 1147-449 BURNT OFF FUSE OUT 1147-446 40 CLASS 4 POLE SEND TO BILL FRALEY RELEASED BY CREW 078S08 VER/PDP L3/DKG IDC XXXX
5439 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-09-09 13:08 | 2010-09-09 14:32 | 62 | 84 | 64951-1 | 3183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOSE STRANDS FROM STRANDED CONDUCTOR CAME INTO CONTACT WITH NEUTRAL VER/KEP L3/KEP IDC XXXX
5440 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2011-05-26 10:43 | 2011-05-26 11:55 | 52 | 72 | 4172501 | 3183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON 449-137, BAD CUTOUT ON 449-147 ISOLATED CUTOUT, CLOSED RECLOSER AT 11:44 (51 CUST)... REPLACED CUTOUT RESTORED POWER AT 11:55 (1 CUST)// VER/DBM
5441 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-05-21 15:25 | 2008-05-21 16:25 | 53 | 60 | 50207-1 | 3180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3110902//RECLOSER NOT OUT- BASKET FAILED ON POLE 39831145B00202 OPENED SWITCH ON POLE 39831145B00201 TO ISOLATE TROUBLE//FOUND HOT TAP BURNTED OFF IN LINE DEADENDS, OPENED UP SOLID BLADE ON POLE 1145-201, MADE REPAIRS AND HAVE CUST BACK ON, REPLACED BAD HOT TAP ON POLE 1145-202 VER/HFP IDC XXXX
5442 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-09-03 12:39 | 2020-09-03 16:11 | 15 | 212 | 4425611 | 3180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a broke cutout on pole 167-D-519,Will need help its a manual pole will have to ground 2 ways to handle wire..Had to open recloser on 190-D-280 from 14:38 to 14:42 to remove hottap safely,Restored line fuse at 16:11..
5443 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-06-04 16:43 | 2016-06-04 21:08 | 12 | 265 | 4298291 | 3180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE OPEN ON 502-177 PATROLLING LINE, CLEARED ONE SPAN OF PRIMARY NEUTRAL UP FROM 502-45 TO 46, THIS ALSO IS A LARGE HOLLOW CROSSING AND HAS STRANDS BROKE IN PRIMARY, PLEASE SEND COPY TO HAVE OUTAGE SCHED AND COND REPAIRED. APR AT 2108 CLOSE TICKET VER/KEP
5444 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-05-20 08:26 | 2017-05-20 10:20 | 28 | 114 | 4826501 | 3177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BURNT OFF ON POLE 39831098B43504 (28 CUST)/ REPLACED BASKET 39831098B43504 @ 1005 (1 CUST)/ CLOSED LINE FUSE IN ON POLE 39831098B43506 AT 10:20 (27 CUST) RESTORING ALL CUSTOMERS/ PLEASE CLOSE TICKET THANKS T. CANTRELL AJB
5445 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-04-26 11:33 | 2019-04-27 12:42 | 6 | 1509 | 4164651 | 3174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Line fuse is blown at pole 37820027000055. Tried the fuse and it came back out. Line needs walked from the fuse up to the road crossing///. LF ON 37820027D20252 IS OPEN NO CUST ON LINE/// LF ON 27-55 IS GOING TOWARDS POLE 27-56, OPENDED @ 2045 ON @ 2108///27-55 came back out//Line hot up to temporary dead end cut in line between pole 27-61 and 27-73. Power restored to one customer at 0051.one strand of 6A wire broke and unravelled making contact with neutral 1242
5446 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-04-10 08:54 | 2015-04-10 11:12 | 23 | 138 | 4302401 | 3174 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOOKS LIKE TR CUTOUT ON POLE 38831125A00253 MAY HAVE BROKEN & TAKEN OUT LINE FUSELINE FUSE ON POLE 38831125A00253 IS BLOWN. THERE IS A TRANSFORMER ON THIS POLE ALSO. THE TRANS. CUTOUT ON THIS POLE IS BROKEN INTO. THIS TOOK OUT THE LINE FUSE ON SAME POLE. I HAVE CALLED FOR HELP TO CHANGE CUTOUT. VER/CRB AJB
5447 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-03-25 23:10 | 2021-03-26 15:25 | 8 | 975 | 4375981 | 3173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse is blown on pole 496-28. Pole 496-248 burnt off at cutout. I believe there is enough room to re-attach primary. Will need 7200 dead-end insulator and cutout and T-bracket. Squirt bucket accessable. Clamp on tap on pole 496-247 is lifted in order to make safe to re-energize line fuse // repaired and restored @1525
5448 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-07-21 09:13 | 2016-07-21 20:13 | 7 | 660 | 4662931 | 3172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PATROLED UNDER GROUND CHECKED NEED CREW TO FIX BAD PRI. UNDERGROUND CABLE RELEASED BY CREW 078S09--CREW ON SITE--BAD PRIMARY CABLE BETWEEN PM 614 AND 617--//CLOSED RISER @ 1411//PATROLED UNDER GROUND CHECKED NEED CREW TO FIX BAD PRI. UNDERGROUND CABLE RELEASED BY CREW 078S09--CREW ON SITE--BAD PRIMARY CABLE BETWEEN PM 614 AND 617--REPAIRED BAD 1/0 PRIM URD---TBL TKT COMP AT 20:13---RMV/ VER/BOW
5449 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2022-06-04 07:37 | 2022-06-04 15:10 | 7 | 453 | 4016441 | 3171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans. fuse open @47-C-239, checking. // BAD 50 KVA NO TRUCK ACCESS. M. Robinette getting line crew to help change out. Released by crew 074S05 RESTORED AT 15:10
5450 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-06-30 20:13 | 2015-06-30 23:31 | 16 | 198 | 4700441 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BOTTOM SIDE RISER FAILED ON MIDDLE PHASE ON POLE 1012A29 I BELEIVE I CAN REPAIR ITBOTTOM SIDE RISER FAILED ON MIDDLE PHASE ON POLE 1012A29 REPAIRED IT RESTORED POWER AT 23:31
5451 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-03-07 01:37 | 2013-03-07 10:25 | 6 | 528 | 4885871 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN BURNT IN THE CLEAR CREW REQUIRED 1 POLE TAP OUT **** CREW TO BE DISPATCHED AT DAYLIGHT.. COD-6 VER/KEP IDCC PN108 XXXX
5452 | Hazard | 3310502 | HADDIX | CANOE | 2015-02-17 20:03 | 2015-02-17 20:35 | 99 | 32 | 4037481 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | A PHASE RECLOSER OUT//COD 99//RECLOSER WENT OUT WHEN FUSED XFMR ON POLE 37830169B00040//CLOSED RECLOSER @ 20:35 . RELEASED BY CREW 075H04//RESTORED 99 STILL HAVE BAD TRANS OUT TIL MORNING ON TIX 4037331 VER/CRB L3/HFP XXX AJB
5453 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-11-02 01:06 | 2021-11-02 14:18 | 4 | 792 | 4047941 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | /got one span of #4 al down on pole after fuse , james gilley and he getting crew Released by crew 077S05
5454 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2014-12-06 15:46 | 2014-12-06 16:30 | 72 | 44 | 4842131 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830045C24578// BAD CUTOUT 50T LINE FUSE VER/CRB L3/HFP AJB
5455 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-04-25 07:21 | 2014-04-25 09:33 | 24 | 132 | 4631561 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 115-166 BAD CUTOUT NEED TWO 19.9 CUTOUTS TRUCK TO POLE RELEASED BY CREW 078S08///INSTALLED 2 LF CUTOUTS IN REPLACEMENT OF THE ONE//BOTH 30T FUSED///PWR RESTORED @ 09:33///PWR CK OK///TRBL TKTCOMPLETED///RMV // COD 24// VER/DBM L3/HFP IDC XXXX
5456 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-07-18 08:48 | 2022-07-18 11:00 | 24 | 132 | 4509721 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cutout on 3783036300016 that took single phase on recloser out. Power restored on recloser @ 11:00 LR- Phase B only
5457 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2013-10-05 15:12 | 2013-10-05 16:40 | 36 | 88 | 4913041 | 3168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PORCELIN ARRESTER BLEW UP ON 954-7. CLEARING FAULT. REPLACED ARRESTER AND RESTORED @ 16:40. SH VER/SEF L3/HFP IDC XXXX
5458 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2013-01-22 21:39 | 2013-01-23 01:10 | 15 | 211 | 4730951 | 3165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT UP ON XFMR POLE. REWORKING CONNECTIONS. REPAIRS COMPLETE. CLOSED XFMR @ 1:10. SH VER/KEP IDC XXXX
5459 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-05-07 14:32 | 2018-05-07 16:14 | 31 | 102 | 4320701 | 3162 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B line fuses out on pole 449-23, bad cutout on pole 449-409, restored power at 16:14/ iso 37830449A10023/ cod 31
5460 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-04-22 12:23 | 2017-04-22 14:12 | 29 | 109 | 4667871 | 3161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 38821110B00098. LINEF IS OUT,WILL PTRL///////BROKE CUTOUT 1110-98,WILL REPLACE ITLINEF IS OUT,WILL PTRL///////BROKE CUTOUT 1110-98,WILL REPLACE IT/////////RE-FUSED&RESTORED AFTER CUTOUUT WAS REPLACED LF 38821109D00017 VER/AWD // // SENT EMAIL TO ENGINEERING TO CHECK FUSE CORRDINATION = L3/HFP HFPC FP38821110000098 AJB
5461 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-06-25 14:30 | 2009-06-25 21:05 | 8 | 395 | 59378-1 | 3160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEEDS CREW TO CHANGE OUT//COD 8//CREW NEEDED BAD CUTOUT ON 3 PHASE POLE 206-1099 BUCKET OK MAY NEED TRAFFIC CONTROL RELEASED BY CREW 078S11/MANNING AND DAVIS TO CHG CUTOUT/FETR 2230/VEM RELEASED BY CREW 078H14// VER/DBM
5462 | Paintsville | 3401102 | FALCON | SALYERSVI | 2013-05-27 22:56 | 2013-05-28 00:15 | 40 | 79 | 4189221 | 3160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP ON P 851-360 HAS BURNED TRU STIRRUP.CHG HOT TAP.AND STIRRUP VER/GAH IDC XXXX
5463 | Pikeville | 3311401 | REEDY STATION | DEANE | 2010-05-16 17:30 | 2010-05-17 19:50 | 2 | 1580 | 63329-1 | 3160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | STS WR # 35137146 // CLOSED RECLOSER IN AND IT DID NOT STAY LINE IS ALL BACK IN THE MTN AND THIS WILL BE BETTER TO HOLD THIS UNTILL TOMMOROW MORNING TOP OF POLE BROKEN OFF ALL MANUAL2 BR VER/KEP L3/KEP IDC XXXX
5464 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-10-14 13:51 | 2008-10-14 15:10 | 40 | 79 | 55710-1 | 3160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE OUT, CHECKING LINE. LINE FUSE RISER BROKEN, REPLACED POWER RESTORED!!!!! VER/KEP IDC XXXX
5465 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2018-05-19 23:51 | 2018-05-20 01:17 | 123 | 86 | 4380481 | 3158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened at 2351
5466 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-04-02 13:58 | 2008-04-02 18:21 | 12 | 263 | 63162-1 | 3156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000801//6A OPEN WIRE 1 SPAN TRUCK OKCREW REQUIRED RELEASED BY CREW 078S03/ # 4 SEC. DOWN VER/HFP IDC XXXX
5467 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-09-22 05:15 | 2009-09-22 08:01 | 19 | 166 | 59816-1 | 3154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SPECTRUM NOT WORKING - RESTORED @ 0801 - BROKEN FUSE LINK// COD 19// VER/TOM L3/TOM IDC XXXX
5468 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-12-21 11:02 | 2020-12-21 12:25 | 38 | 83 | 4790481 | 3154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke on pole 427-9. refused and restored power at 1225
5469 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-09-25 13:39 | 2020-09-26 02:47 | 4 | 788 | 4495691 | 3152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 783-148 broken at the telephone, 504..need yard dog, flaggers, line crew, 25 kva xfmr ,appears to be good, {guy att, guy wire, primary dead end, neutral all look good reuseable} .foothills owner. 811 dig #2009251398 @14:30. grd tagged783-106.. Released by crew 076S01 Released by crew 076H06
5470 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-10-28 01:52 | 2020-10-28 04:09 | 23 | 137 | 4591041 | 3151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Wire came off pole top pin at pole 263-A-407,Going to place ground at pole 263-A-253 and tag to myself so i can make repairs..Changed pole top on 263-A-407,Changed cutout on 263-A-39,Restored service at 04:09..//COD 23
5471 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2019-10-23 07:53 | 2019-10-23 10:23 | 21 | 150 | 4186561 | 3150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout bad , replaced cutout restored power at 10:23.. L3/HFP
5472 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-08-16 11:02 | 2022-08-16 11:27 | 126 | 25 | 4748481 | 3150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B phase line off insulator and laying on arm at pole 37830250D00055///open Sws 37830250B00171 (126 COD) at 1102 to make repairs///restored at 1127///B phase line off insulator and laying on arm at pole 37830250D00055 opened switches on pole 250B-171 @ 11:02 and closed back @ 11:27 .
5473 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-07-09 15:55 | 2010-07-09 17:40 | 30 | 105 | 64167-1 | 3150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON NORMAL OPEN POLE 249-181, D WHEELER IN ROUTE FOR ASSISTANCE RELEASED BY CREW 078S05//COD 30 IDC XXXX
5474 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2013-01-17 03:17 | 2013-01-17 16:24 | 4 | 787 | 4616061 | 3148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RESTORED AT 1614// WAS OPENED TO ALLOW LOOPS TO BE MADE UP SAFELY// IDCC TOF1445 OPENED WHEN BREAKER OPENED XXXX
5475 | Hazard | 3309302 | VICCO | JEFF | 2019-05-11 10:58 | 2019-05-12 13:11 | 2 | 1573 | 4252521 | 3146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | csp xfmr will not reset, we need a line crew and a25 kva 7200 xfmr ,cutout and arrestor. this is manual Released by crew 077S12//REPAIRS MADE @ 1311
5476 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-05-24 08:08 | 2010-05-24 12:10 | 13 | 242 | 50068-1 | 3146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "B" PHASE COD-8 MD FILED ON MISMAPPED CUSTOMERS 25T LINE FUSE OUT DUE TO BIRD AND ARRESTER . CLEARED UP FUSED UP EVERYTHING OK. SEND COPY TO RON RYE ENG NEED TO REPLACE ARRESTER THIS IS ON ARM NEXT TO PRIMARY. SEND COPY TO ROW PIKEVILLE COREY FARMER NEEDS CUT. AED CREATED VER/KEP L3/KEP IDC XXXX
5477 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-01-07 03:27 | 2017-01-07 07:49 | 12 | 262 | 4274711 | 3144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQUIRED #2 ALUM PRIMARY TRUCKS OK/TAGGED TO MULLINS NO GROUNDS OPEN RECLOSER AT 0458 HRS AT 199-197/ "B" PHASE BROKE IN THE CLEAR AT POLE 198-106 COD-12 FOR "B" PHASE RECL/CREW ON SITE/FETR0830/VEM/// VER/DKM L3/HFP XXXHFP
5478 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-12-29 15:53 | 2013-12-29 21:42 | 9 | 349 | 4210671 | 3141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF, WILL NEED 40, CLASS 4 POLE, CUTOUT AND ARRESSTOR, POLE TOP PIN AND INSULATOR. POLE 37830281000001 //VER/GAH IDC XXXX
5479 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-03-10 20:52 | 2011-03-11 14:19 | 3 | 1047 | 53243-1 | 3141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DANGEROUS LOCATION, ESP AFTER DARK//PER DUTY SUPERVISOR, WILL HOLD THIS FOR TOMORROWS WORK // RELEASED BY CREW 074S05 BROKE CUTOUT ON XFMR WILL REPLACE AND CUT R/W. ON AT 14:19 D SAMMONS//VER/CRB IDC XXXX
5480 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-10-06 12:26 | 2014-10-06 19:45 | 12 | 439 | 4557681 | 3136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PATROLLING CKT @ 1323 // MAIN LINE BACK ON @ 1558... POLE 6/// POLE 9 FUSE IS STILL OUT// AND POLE 10 TRANSFORMER IS BAD///LINE FUSE ON POLE 38831060D00009 IS BLOWN ALSO// 8T LINE FUSE IS ON POLE 1060-100 NOT SHOWN ON MAP MD CLOSED AT 17:07// 38831060D00103 NEUTRAL DOWN NEEDS ROW CUT AED/// SEE 4559971 FOR OUTAGE TO REPLACE XFMR / OPENED STEP DOWN @ 38831060D00205 TO REPLACE TRANSFORMER 38831060D00010 IDCC TON1553, STP MISSING XXXX
5481 | Hazard | 3309302 | VICCO | JEFF | 2021-10-27 23:56 | 2021-10-28 13:00 | 4 | 784 | 4027331 | 3136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Customer is part out/ advised customer to turn main breaker off/ Dispatched in accordance with KYPCo Late Night Callout Guidelines. Only getting 120V out of transformer all conn. good need 4 man crew 50KVA 7200V cutout and t/bracket Released by crew 077S03
5482 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-01-30 01:36 | 2014-01-30 06:21 | 11 | 285 | 4326561 | 3135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR.NEED 50 KVA TRUCK ACCESSIBLE/ADD 2 CUSTOMERS MD FILEDBAD 25 KVA XFMR.NEED 50 KVA TRUCK ACCESSIBLE ..TRANSFORMER CHG TO 50 KVA..BACK ON AT 621 VER/HFP L3/HFP IDC XXXX
5483 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-02-01 08:02 | 2021-02-01 11:12 | 25 | 190 | 4925171 | 3133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke @ 38831098B00648. Isolated cutout. Closed 65t @ 1098B-601 @ 9:55. Changed cutout and restored @ 11:12 Released by crew 074S11
5484 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-07-30 19:27 | 2009-07-30 21:15 | 29 | 108 | 57949-1 | 3132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401103// FUSE DOOR BURNT UP. WILL HAVE TO CHANGE CUTOUT BECAUSE I DONT HAVE THIS TYPE OF REPLACEMENT DOOR (OBSELETE). HAVE TO LIFT HOT-LINE-CLAMP THAT FEEDS XFMR 178 TO SAFELY PERFORM WORK. LIFTED CLAMP AT 20:50. (INTERRUPTED 1 MORE CUST) CHANGED CUTOUT AND RE-FUSED LINE FUSE RESTORING ALL CUSTOMERS AT 21:15. SH//COD 29// IDC XXXX
5485 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-05-18 10:17 | 2010-05-18 12:05 | 29 | 108 | 64559-1 | 3132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | V. MULLINS OPENED L.F. AT POLE 118-C-142 TO C/O BAD ARM AND POLE./OPENED FUSE AT 1017/WORK WILL TAKE A COUPLE OF HOURS/VEM/ALL REPAIRS MADE AND POWER RESTORED TO ALL CUST 1205/PLEASE CLOSE TICKET/THANKS/VEM COD-29 VER/HFP L3/HFP IDC XXXX
5486 | Hazard | 3303901 | LESLIE | HYDEN | 2014-01-03 22:50 | 2014-01-04 16:14 | 3 | 1044 | 4226561 | 3132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ARCOS PAUL PRATT & NEED 3 MEN BAD TRANSF 25 KVA 7200 KV ==AND 4 WHEEL DRIVE PICKUP === CAN AT DAY LIGHT ===ROADS SNOW COVERED === TALK TO CUST HE IS OK WITH THIS RELEASED BY CREW 077S03 POWER RESTORED AT 1614 CREW 077H01 VER/KEP IDC XXXX
5487 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2008-01-10 18:47 | 2008-01-10 19:55 | 46 | 68 | 55615-1 | 3128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 21-3023 BAD LA 21-57 VER/KEP IDCC PN57 XXXX
5488 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-05-15 00:33 | 2016-05-15 17:55 | 3 | 1042 | 4218961 | 3126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RM ON SITE LINE FUSE OPEN@164-01 TAGGED&GROUNDED TO CHRIS YOUNGMAN POLE 164-298 BURNT OFF NEED LINE CREW & 405 FT POLE NEED TBRACKET &199 CUTOUT &DEADEND BELL RELEASED BY CREW 078H20//C YOUNGMAN GAVE R VIRGIN PERMISSION TO REMOVE HIS TAGS AND REPLACE WITH HIS OWN// &DEADEND BELL RELEASED BY CREW 078H20---CREW ON SITE--CHANGED TAG TO SELF RMV--REMOVED TA VER/CRB
5489 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-05-15 10:43 | 2015-05-15 14:30 | 31 | 227 | 4432291 | 3122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT, LINE FUSE OUT ALSO ON POLE 270-97, FOUND BAD CUTOUT ON POLE 270-158, ISOLATED CUTOUT.. LINE FUSE RESTORED AT 12:15. WILL NEED CREW AND R-O-W CREW TO CUT AROUND POLE. T. SMITH COMING TO HELP RELEASED BY CREW 077S02/ ISO 37830270A00097/ COD 31 L3/DKG VERIFIED WITH VOICE RECORDER AJB
5490 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-09-14 17:35 | 2008-09-15 19:36 | 2 | 1561 | 63044-1 | 3122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE38830210000107 IS BROKEN, JOHN SODE IS WRITING JOB, 45-4, 25KVA XFMR, 1/0 SERVICE DROP, CUTOUT, TRUCK OK RELEASED BY CREW 078S05//3003701,JEFF CREMEANS LEADING ELLIOT CREW. VER/DKG IDCC PN107 XXXX
5491 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-10-18 09:41 | 2022-10-18 13:09 | 15 | 208 | 4039221 | 3120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | on pole 1124-1516 got a bad 50kva 7200 120-240 transformer crew required truck ok in alley way Released by crew 078S09 // xfmr was not bad replaced lug on xfmr and restored @1309
5492 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-09-27 19:33 | 2010-09-27 20:33 | 52 | 60 | 54434-1 | 3120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT//VER/CRB IDC XXXX
5493 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-05-09 20:46 | 2021-05-10 00:46 | 13 | 240 | 4566581 | 3120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken b phase cutout at at 140B-173 at closed at 0046
5494 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-06-19 16:21 | 2014-06-20 18:20 | 2 | 1559 | 4113571 | 3118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RITE-AID IS SERVED FROM BANK POLE 875-485 AND IS THE ONLY CUSTOMER AFFECTED. GOOD VOLTAGE AT XFMR BUT LOW VOLTAGE ON ONE PHASE AT CUST DISCONNECT. OOCREW REQUIREDOO RELEASED BY CREW 076S02// CHECKING NOW TCM// FOUND B LEG BAD AT CT BOX TRYING TO GET ROTATION AND TRY TO PULL OLD WIRE OUT TO INSTALL NEW UG SERVICE, TCM// AFTER NO SUCCESS REPAIRING UG, CUSTOMER WANTS USE TO RUN 3 PHASE OVER HEAD , BOB AND JOE HUBBARD WORKING ON THIS NOW. TCM// RELEASED BY CREW 076H01 VER/KEP
5495 | Hazard | 3309003 | JEFF | VIPER | 2020-05-03 19:26 | 2020-05-03 20:48 | 38 | 82 | 4791471 | 3116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot line clamp brunt off of stirup repaired power on
5496 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-04-10 08:22 | 2015-04-10 11:15 | 18 | 173 | 4301901 | 3114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | APHASE LINEF OUT AT 1082-55,WILL PTRL/////////#4 COPPER PRIM DOWN AT 1082-56 TO 1082-20,CREW ENROUTE////OPEND OTHER 2 FS AT 10:12///////MADE REPAIRS,RESTORED ALL////////DEADEND BROKE AT STIRRUP FIX IN HOIS
5497 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-08-23 17:31 | 2021-08-23 21:30 | 13 | 239 | 4141141 | 3107 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ABNORMAL VOLTAGE ON 1 LEG///////RICK RAY ENROUTE TO HELP.////////1LEG IN UG JUNCTION BOX IS BURNED ALMOST INTO,WILL REPAIR/////MADE NECESSARY REPAIRS&RESTORED
5498 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-05 08:41 | 2019-06-05 12:08 | 15 | 207 | 4429021 | 3105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT UP CUTOUT ON POLE 38830768A20446//L/F OPEN ON POLE 38830768A00189//COD 15//RESTORED 1208 L3/HFP
5499 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2017-10-17 13:23 | 2017-10-17 14:10 | 66 | 47 | 4465811 | 3102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS OPENED FUSE ON 38830070A20610 TO SAFELY REPLACE FAILED EQUIPMENT. ASSOCIATED WITH ORDER. OPENED CUTOUT SINCE UNABLE TO USE COVERUP 4464881. 1323-1410 VER/AWD /// RELATED TO 4464881 = L3/HFP XXXHFP ACB
5500 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-04-25 11:58 | 2010-04-25 16:40 | 11 | 282 | 50753-1 | 3102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURN OFF. VER/HFP L3/HFP IDC XXXX
5501 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2012-11-10 20:34 | 2012-11-10 21:40 | 47 | 66 | 4381001 | 3102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 1147-5542 HOT TAP BURNT OFF REPAIRED // 34 - A PHASE, 3 - AC, AND 3-3PHASE // 4 FROM 4381011 // TOTAL 47 CUSTOMERS OUTAGED VER/DKG RAN BUSINESS OBJECTS REPORT TO VERIFY PASES OF CUSTOMERS VER/TOM L3/TOM IDC XXXX
5502 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2010-12-01 13:16 | 2010-12-01 18:22 | 24 | 306 | 62067-1 | 3102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG RISER FUSE BLOWN. MAP IS NOT ACCURATE. DETERMINING WHAT WE HAVE OUT. BAD UG CABLE FROM RISER POLE 785-388 TO PADMOUNT XFMR 785-883. RISER FUSE BLOWN ON 785-388 ISOLATING FAULT. CLOSED FUSE ON 785-813 @ 15:00 RESTORING ALL BUT THREE CUSTOMERS SERVED FROM XFMR 785-883. ((((PRIMARY UG STOPS ON 785-883)))) CREW WORKING TO REPAIR FAULTED CABLE. FAULT LOCATED - REPAIR UNDERWAY - DIFFICULT LOCATION. REPAIRS COMPLETE. RESTORED REMAINING 3 CUSTOMERS @ 18:22. SH IDC XXXX
5503 | Paintsville | 3401101 | FALCON | FALC-OILS | 2011-07-19 18:03 | 2011-07-19 22:45 | 11 | 282 | 4564711 | 3102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON 838-38 PATROLLING LINE BAD INSULATOR ON 902-6..NEED INSULATOR AND BIG BUCKET ..INSULATOR CHG OUT CUTOUT BACK IN 22 45 COD-11 ISO LF 38830878000038 VER/HFP L3/HFP
5504 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2020-09-24 16:44 | 2020-09-25 03:30 | 5 | 646 | 4492991 | 3098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Opened line fuse @38831121C00093 at 17:28 due to broke pole 38831121C00199. Pole was rotten and broke @ ground due to limb falling on secondary. No truck access to pole. Existing pole was 35-5, need 15KVA /7200 XFM, cutout & bracket deadend pole #2 wire. Manual R.O.W crew to cut path to winch pole. Released by crew 074S11. CREW ONSITE, REPAIRS COMPLETE POWER RESTORED AT 03:30. WILL BE CLEANING UP MATERIAL
5505 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2019-11-07 09:25 | 2019-11-07 12:08 | 19 | 163 | 4005551 | 3097 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELATED TO 4004871 THIS FUSE BLEW WHEN CREW TRIED DIP FUSE IN ORDER 4004871 L3/HFP
5506 | Hazard | 3301101 | CHAVIES | CHAVIES | 2009-02-12 09:48 | 2009-02-14 13:25 | 1 | 3097 | 50315-1 | 3097 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | CUST HAD ELECTRICIAN CHECK VOLTAGE AND ONLY HAD 120V COMING IN THERE IS NO VISIBLE BREAK IN SERVICE DROP NEED SERVICER TO CHECK CONNECTIONS RELEASED BY CREW 077E02///NEED TO RELEASE TO TIM SMITH,,,JDM RELEASED BY CREW 077E01BAD CONNECTION REPAIRED 02 14 09 //VER/GAH
5507 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2012-09-26 19:48 | 2012-09-26 22:40 | 18 | 172 | 4090821 | 3096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1099-3506 2- BAD CUTOUT BURNT ARM OFF REPLACED ARM AND 2- CUTOUTS AND LA//COD 18// VER/DBM IDC XXXX
5508 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-02-19 23:48 | 2015-02-20 12:42 | 4 | 774 | 4046051 | 3096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER 7200/120/240 15 KVA. WILL NEED TO BRING A 25 KVA 4 CUSTOMERS ON IT. CREW REQUIRED. RELEASED BY CREW 074S02 RELEASED BY CREW 074H10 CREW ON SITE RESTORED AT 12:45PM COD-4 ISO TF 37820104000080 VER/HFP L3/HFP
5509 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-09-01 07:28 | 2021-09-01 13:55 | 8 | 387 | 4191441 | 3096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE CREW, NO TRUCK, A & B LINE FUSES OPEN AT 38831101C20315 C PHASE IS OFF LINE, NEED 5 DE INSULATORS 34.5KV ON POLE 38831101B00236 Released by crew 074E05/closed fuse on 1101-315 at 13:55
5510 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-03-11 15:29 | 2009-03-11 18:21 | 18 | 172 | 57278-1 | 3096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 28885971 //OPENED TR @ 1529 COD-18 50 KVA XFMR BAD ON POLE 349. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO CHANGE. RELEASED BY CREW 076S02. CREW ARRIVED WORKING NOW VER/DKG IDC XXXX
5511 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-04-20 02:48 | 2009-04-20 04:47 | 26 | 119 | 59307-1 | 3094 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408103 - CUTOUT BAD ON POLE 264, CROSSARM BURNED APART AND PHASE C LAYING IN TREE RELEASED BY CREW 074S033408103 - CUTOUT BAD ON POLE 264, CROSSARM BURNED APART AND PHASE C LAYING IN TREE .... REPOSITIONED C PHASE ON ARM AND REPLACED CUTOUT, WILL CREATE OPS ORDER TO REPLACE ARM AT LATER DATE , ALL WORK COMPLETE / GXJ //VER/GAH AJB PHASE C.
5512 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-10-11 05:23 | 2020-10-11 12:45 | 7 | 442 | 4543591 | 3094 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | tree has fell and tore primary down between poles 419-138 and 419-139, will need line crew and manuel r-o-w crew. all power restored
5513 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-04-30 17:53 | 2018-05-01 00:25 | 64 | 392 | 4292211 | 3094 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | need 19.9 cutout t bracket manuel pole , will need to open line to replace/ opened recl 37830178B00166 @ 2310/ closed recl 37830178B00166 @ 2320/ Closed new switch on pole 37830178A00076 @ 0025/ closed fuse 37830178A00101 @ 0025 L3/HFP
5514 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-06-11 08:58 | 2015-06-11 12:00 | 17 | 182 | 4553401 | 3094 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 15T OPEN @ 89-7 GROUND & TAGGED TO C. YOUNGMAN, 6A NEUT. DOWN BETWEEN 89-9 TO 11, RELEASED BY CREW 078S07.. CREW ON SITE.. ETR 12:15.. FOUND 6A PRIMARY WIRE STRAND WAS TOUCHING NEUTRAL AND WAS PROBABLY WHATS BEEN TAKING LINE OUT SO FREQUENTLY..NEED TO SEND COPY TO BRADSHAW TO HAVE LINE TRIMMED OUT BECAUSE TREES ARE LAYING ALL AROUND LINE.. COMPLETE/ ISO 38830089000007/ COD 17/ VER/BOW AJB CCTIR FEC57
5515 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-04-03 09:40 | 2015-04-03 22:33 | 4 | 773 | 4263301 | 3092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA CSP/ TRUCK ACCESSIBLEBAD 7200-25KVA CSP. TRUCK OK RELEASED BY CREW 078S07///CHANGING XFMR, CO & ARR///ETA 23:07////CHANGED XFMR///TBL TKT COMP///VOLT CK GOOD///ON @ 22:33 L3/DKGXXXX
5516 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-07-18 10:59 | 2010-07-20 14:30 | 1 | 3091 | 52477-1 | 3091 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | PAD MOUNT TRANSFORMER BURNED,PRIMARY CABLE AND SERVICE 750 MCM.SERVICE IS CUSTOMER OWNED ONE CUTOUT SHOT INTO BY SCYAMORE FIRE DEPT AND TWO FUSES AND TWO FUSES OPENED BY UNKNOWN SOURCE.FUSES FOR PADMOUNT ON POLE 265-370,WILL NEED TO REPLACE UG CABLE TO POLE AND TRANSFORMER,METER IS DESTORIED I WILL PUT ALL INFO ON FIRE REPORT RELEASED BY CREW 074S10 VER/KEP L3/KEP IDC XXXX
5517 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-07-24 18:41 | 2016-07-24 22:07 | 15 | 206 | 4674321 | 3090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER MAKING SIZZLING NOISE. 4/0 CU RISER BURNT @ CONNECTION. NEED TO REPAIR/REPLACE RISER. RELEASED BY CREW 078S07--CREW ON SITE---OPENED XFMR BANK AT 21:43--CLOSED AT 22:07---REPAIRED 350MCM CU XFMR RISER--NEW CONNECTIONS---TBL TKT COMP---RMV VER/ARN
5518 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-07-10 15:32 | 2009-07-10 18:58 | 15 | 206 | 55986-1 | 3090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 20687199 // FOUND BROKEN CUTOUT POLE COVERED WITH VINES HILLSIDE POLE 92-614 LINE FUSE OUT ON POLE 92 - 94 VER/TOM L3/TOM IDC XXXX
5519 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-06-09 11:41 | 2011-06-09 16:50 | 10 | 309 | 4274821 | 3090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#40320965 SEND TO BILL F. RELEASED BY CREW 078S08//ACCIDENTLY CLOSED/VER/CRB IDC XXXX
5520 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2018-10-09 13:44 | 2018-10-09 17:10 | 15 | 206 | 4212141 | 3090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser open on pole 1152-B2-211, bad span of URD primary between feed through 24-A1-1292 and padmount 1296, isolated last span of cable and closed l/f back in @1710. Last span is home with a generator and no one lives in, crew will take care of tommorow. Released by crew 074S05//CLOSED TICKET OUT//TECH IS GOING TO MAKE ORDER TO REPLACE CABLE L3/HFP
5521 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-07-04 06:26 | 2015-07-04 06:41 | 206 | 15 | H4718011 | 3090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWNPOLE#1062-D-39/ "A" PHASE ONLY COD-91/ CLOSED RECL AT 0359 UP TO OPEN SWS 1062-40 RESTORED 24 CUST/ OPENED OTHER 2 PHASES AT 0626 COD-206/ AND CLOSED THEM IN AT 06;41 VER/KEP L3/DKG THIS IS FOR OPENING OTHER 2 PHASES. ORIGINAL OUTAGE IS ALREADY IN APPROVED
5522 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-12-25 08:27 | 2009-12-25 08:35 | 386 | 8 | 63089-1 | 3088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33198114 // POLE TOP ON FIRE SERVICER OPENED RECLOSER TO MAKE SCENE SAFE AND ALLOW CREW TO REPAIR/REPLACE POLEPOLE -92-002 RELEASED BY CREW 078S08 MLR IDC CHECK OFF TIME
5523 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2010-05-18 02:12 | 2010-05-18 09:33 | 7 | 441 | 64428-1 | 3087 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 35165432 // T. GEORGE IS ON SITE AS OBSERV. COD-7 VER/HFP L3/HFP IDC XXXX
5524 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-05-05 11:23 | 2018-05-05 21:40 | 5 | 617 | 4310161 | 3085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuses blown on pole 88-1////#2 alum down from pole 88-66 to 88-68 two span of the three phase and pole 88-67 is stripped.only one phase is down..will need three man line crew with 3 cross arm pins and insulators and one pole top pin, 8ft cross arm and wire to splice with..non-truck access...no grounds and no tags placed... Released by crew 074S01
5525 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-06-13 12:03 | 2013-06-13 16:20 | 12 | 257 | 4272061 | 3084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRY FUSE 15;10 CAME BACK OUT CLOSED FUSE 16;20 CHGED LA ON POLES 165-116 /165-140 AND POLE 165-236 VER/CRB L/3 CRB IDC XXXX
5526 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-07-08 15:24 | 2012-07-09 17:05 | 2 | 1541 | 4604101 | 3082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACE AND MAKE XFORM BACK HOT ,POWER RESTORED 17:05
5527 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-11-27 17:44 | 2012-11-27 20:26 | 74 | 162 | 4426561 | 3080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED//OPEN LINE FUSE ON POLE 38830069C14001 AT 17:44--LIFTED HOTTAP AND INSTALLED GROUND ON POLE 38830069C14104--CLOSED LINE FUSE IN ON POLE 38830069C14001 AT 18:15 RELEASED BY CREW 078S07, REPAIRS MADE ALL CUST RESTORED @2026,PLEASE CLOSE TICKET THANKS.BT //COD 74// VER/DBM IDC XXXX
5528 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-11-28 09:08 | 2011-11-28 10:25 | 40 | 77 | 4118561 | 3080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER ON POLE 37830180000048 @ 0908 TO ISOLATE POLE FIRECUTOUT BAD ON POLE 181-149, WILL NEED CREW TO REPAIR, NEW CUTOUT AND T-BRACKET NEEDED, CAN LOWER EVERTHING ON POLE.CUTOUT BAD ON POLE 181-149, WILL NEED CREW TO REPAIR, NEW CUTOUT AND T-BRACKET NEEDED, CAN LOWER EVERTHING ON POLE. RELEASED BY CREW 077S02 MADE REPAIRS AND RESTORED POWER AT 1025 VER/HFP L3/HFP IDCC PN NULL XXXX
5529 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-04-09 12:14 | 2009-04-09 13:42 | 35 | 88 | 50756-1 | 3080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401001// LOW SIDE FUSE ON STEPDOWN TRANS. IS OUT ON POLE 215-122. I AM PATROLLING LINE NOW. LIGHTENING ARRESTER ON POLE 215-398 SHORTED OUT. I GOT IT IN THE CLEAR AND READY TO BE MADE HOT. I CLOSED FUSE IN AT 13:42 AND IT STAYED IN.//COD 35// VER/DBM IDCC CDC92 XXXX
5530 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-01-15 21:57 | 2014-01-15 23:47 | 28 | 110 | 4285091 | 3080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | A PHASE ONLY 28 COD//NO CREW REQUIRED AT THIS TIME BAD RECLOSER PUT 30T BYPASS IN TAGGED TO DDC AND ALSO CREATED ABNORMAL //VER/GAH L3/HFP IDC XXXX
5531 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-06-19 20:55 | 2014-06-19 23:15 | 22 | 140 | 4117781 | 3080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L/F BLOWN 37830335C00138 // WILL PATROL //***CHANGE ISO POLE**** COD 22 DO MD VER/CRB AJB
5532 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-04-03 23:37 | 2008-04-04 04:46 | 17 | 309 | 63652-1 | 3078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PUTTING FIBERGLASS EXTENSIONON SO CA N GET MOST EVERYBODY BACK ON/ CREW REQUIRED/REPAIRS MADE 2 CUSTOMERS WILL STILL BE OFF/FUSE BACK IN AT 0221HRS RELEASED BY CREW 078S03 VER/PDP IDC XXXX
5533 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-02-28 14:27 | 2011-02-28 15:25 | 53 | 58 | 64759-1 | 3074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED "C" PHASE ON RECLOSER TO SAFELY REPLACE CUTOUT ON ORDER 64462-1 COD-54 VER/HFP L3/HFP IDC CHANGED FROM SCHEDULED XXXX
5534 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-09-12 07:29 | 2011-09-12 14:48 | 7 | 439 | 4858861 | 3073 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE//////FUSE BLEW,HAS UG SERV,WILL DISC IT AND TRY FUSE AGAIN//////25 KVA XFR IS BAD,WILL CONTACT PVILLE RELEASED BY CREW 074S06 VER/CRB IDC XXXX
5535 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-08-24 07:47 | 2017-08-24 12:03 | 12 | 256 | 4295121 | 3072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KV 19.9 TRANSFORMER//CREW ON SITE VER/KEP SJG
5536 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-03-18 16:13 | 2008-03-18 20:29 | 12 | 256 | 58280-1 | 3072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3010602//BAD 50 KVA TRANS CALLED BILL LYNCH RELEASED BY CREW 078S08// VER/TOM IDCC CDC83 XXXX
5537 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2013-02-22 03:48 | 2013-02-22 05:27 | 31 | 99 | H4838941 | 3069 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PHASES A & B OPEN AT POLE 992-D3-481. 80CC. OPENED C PHASE RECLOSER AT 03:48. 31 CC. ALL THREE RECLOSERS RESTORED AT 05:27. IDCC DUP TO OPEN PH C XXXX
5538 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-12-14 11:15 | 2019-12-14 12:14 | 52 | 59 | 4153301 | 3068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad c/o @51-23 that has pole top almost burndt off, will have to open S/B @51-21 to make repairs. Opened S/B @1115, the solid blade also busted after I opened, will be making repairs to both cuouts. Got both c/os changed and closed S/B back in @1214.
5539 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-02-19 01:24 | 2020-02-19 11:35 | 16 | 611 | 4417041 | 3068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | URD riser open @71-162, checking. Isolated bad span of URD cable from padmount 71-206 to 71-207 and tagged to Ken Little, closed L/F back in @0259. This will take a line crew in the a.m. with hi-pot sticks. Spliced out bad spot in URD cable and put last 2 trans. back on @1135. Released by crew 074S05 LAST 2 CUST ON AT 11:35 ¦¦¦¦ L3/HFP
5540 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2017-02-20 16:40 | 2017-02-20 19:40 | 17 | 180 | 4410081 | 3060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078S08,BAD @ POLE 39831147A00671 REPAIRS MADE PLEASE CLOSE TICKET THANKS.BT VER/CRB L3/HFP XXXHFP
5541 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2020-08-13 21:50 | 2020-08-13 23:20 | 34 | 90 | 4322321 | 3060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | bad cutout brunt crossarm 37830071000134 cutout on 71-134 broke down and burnt the arm in two, had to open up the line at 71-24 and tagged to Todd McCoy, opened at 21:50.. line fuses on 71-24 restored at 23:20/ ISO 37830071000024/ COD 34
5542 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-12-14 09:17 | 2008-12-14 12:17 | 17 | 180 | 58201-1 | 3060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402002//STS WR 27671844//HIGH SIDE STEPDOWN FUSE OPEN ON CENTER PHASE (PHASE A) ON POLE 1080-157A (NOT ON MAP YET, THIS SECTION OF LINE IS BEING REWORKED) //WILL OPEN OTHER TWO PHASES IN ORDER TO MAKE REPAIRS TO FUSE... WHICH WILL INTERRUPT 31 MORE CUST//CURRENT COD 17//OPENED OTHER 2 PHASES @ 1202//CLOSED AND ALL CUST RESTORED @ 1217//LEAD OUT OF HOT-TAP @ STEPDOWN BANK POLE 1080-157,WILL MAKE REPAIRS VER/KEP L3/KEP IDC XXXX
5543 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2013-01-05 12:08 | 2013-01-05 12:59 | 60 | 51 | H4570781 | 3060 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | INTERNAL PROBLEMS WITH THE STATION TRANSFORMER - TRANSFERRING LOAD TO ALT SOURCES & CALLING STATION CREW TO INSTALL MOBILE TR AT CANNONSBURG STATION //VER/GAH IDC XXXX
5544 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-11-24 21:45 | 2014-11-25 10:29 | 4 | 764 | 4778081 | 3056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD CONNECTION ON TRANSFORMER VER/ARN
5545 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-04-04 07:02 | 2008-04-04 08:55 | 27 | 113 | 63695-1 | 3051 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116703//A PHASE ONLY IS OUT//COD 27// BAD CUTOUT// REPLACED 2 BAD CUTOUTS// VER/DBM IDC XXXX
5546 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2012-05-08 07:58 | 2012-05-08 08:25 | 113 | 27 | 4758361 | 3051 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED REC TO CLEAR UP CUTOUT === OPENED A & C PHASE REC. ON POLE 37830225A00114 AT 07:58, CLOSED AT 08:25, SAME AS OUTAGE # 4758351 RELEASED BY CREW 077S04 VER/KEP IDC TICKETS INDICATE PH A & B CHANGED COUNT FROM 156 XXXX
5547 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-12-30 12:48 | 2011-12-30 13:15 | 113 | 27 | 4215711 | 3051 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON 34.5 SIDE OF STEP-DOWN ////VER/CRB IDC XXXX
5548 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-02-02 08:21 | 2009-02-03 09:45 | 2 | 1524 | 54434-1 | 3048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE BROKE COMPLETE JXM
5549 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-06-13 11:50 | 2013-06-13 19:05 | 7 | 435 | 4271461 | 3045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 69-C4-5559 HAS XFRM ARRESTOR BLOWN, FUSE BAR STILL IN, PWR OFF ON SECONDARY SIDE, NEED TO CHECK 25 KVA XFMR, TRUCK OK, FLAGGERS REQUIRED----- HOT TAP BURNT OFF VER/CRB L/3 CRB IDC XXXX
5550 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-01-29 08:13 | 2010-01-29 11:12 | 17 | 179 | 60951-1 | 3043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CHECKING NOW.WIRE DOWN ON POLE853-20 TO POLE 853-1 GOING TO ISOLATE CREW ON ITS WAY.OPENED ON POLE 853-77 FUSE WAS BLOWN BUT DIDNOT DROP OPEN.WIRE PULLED OUT OF A SLEEVE VER/HFP L3/HFP IDCC FPNULL XXXX
5551 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-02-28 09:25 | 2013-02-28 11:22 | 26 | 117 | 4862381 | 3042 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | FOUND BASKET BURNTED INTO ON SOURCE SIDE OF RECLOSER, WELL BE CREW REQ TO MAKE REPAIRS, HAVE TALKED TO MR. RAYBURN AND HE IS SENDING RON VIRGIN OUT TO TAKE CARE OF THIS RELEASED BY CREW 078S06//REPAIRED 2 #2 STIRRUPS AND LIGHTING ARR. ON SOURCE SIDE OF RECL.///PWR RESTORED 11:22//// ///VER/CRB L/3 CRB IDC XXXX
5552 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-03-19 22:11 | 2018-03-20 02:05 | 13 | 234 | 4028611 | 3042 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 37830134A00087, crew coming to replace
5553 | Cannonsburg | 3000101 | ASHLAND | 25-25STREET | 2020-03-12 08:22 | 2020-03-12 11:11 | 18 | 169 | 4470811 | 3042 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout busted on pole 45d7197 also service neut broke at house & pole. making repairs. tre. changed porcelian cutout on pole 38830045D37199. all repairs made. time on @ 11:11
5554 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-12-21 10:20 | 2010-12-21 11:40 | 38 | 80 | 54757-1 | 3040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREWS OPENED RECLOSER IN ORDER TO PUT WIRE BACK UP (SEE 54711-1) // COD 38 //OPENED @ 1020 // VER/DBM IDC XXXX
5555 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-04-25 07:13 | 2021-04-25 09:45 | 20 | 152 | 4477931 | 3040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp burnt off at line fuse. made repairs and restored power at 09:45
5556 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-08-16 09:29 | 2021-08-16 13:42 | 12 | 253 | 4077141 | 3036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 100 kva on pole 449-C-966.. transformer replaced, power restored
5557 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2022-07-06 17:27 | 2022-07-07 10:18 | 3 | 1011 | 4405451 | 3033 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout not by truck access from 1511 chestnut dr. may possibly reach with a super squirt Released by crew 078S12 Crew on site, climbing to make repairs. Repairs made closed at 10:18. Ticket complete.
5558 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2020-05-29 08:49 | 2020-05-29 10:08 | 50 | 79 | 4926621 | 3030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | fuse back in at 09:48 and xfer restored @ 1008
5559 | Hazard | 3311103 | STINNETT | WENDOVER | 2011-09-04 21:32 | 2011-09-05 00:30 | 17 | 178 | 4812521 | 3026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 7.2KV CUTOUT VER/KEP IDC XXXX
5560 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-03-25 12:59 | 2015-03-25 15:00 | 25 | 121 | 4226581 | 3025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 155-31 WIRE OFF POLE TOP PIN CREW REQUIRED BIG BUCKET NO WIRE DOWN/TAGGED TO BRENT TACKETT RELEASED BY CREW 078S03,,CREW ON SITE,,ALL REPAIRS MADE,,ALL POWER RESTORED VER/KEP AJB
5561 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-03-29 11:18 | 2020-03-29 21:23 | 5 | 605 | 4523011 | 3025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | xfmer pole 20-5051 open wire sec. together. needs resaggd. crew reqd. Released by crew 078S07--6T xfmr fuse in @ 21:23---tbl tkt comp---rmv
5562 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2019-02-07 01:55 | 2019-02-07 12:00 | 5 | 605 | 4760911 | 3025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held in accordance with KPCO late night callout guidelines.///broke cutout 19.9kv,manual,need line crew Released by crew 077S04 replaced cutouts and restored power at 1200
5563 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-04-12 10:16 | 2011-04-12 10:58 | 72 | 42 | 55710-1 | 3024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 55528-1 // CREW OPENED RECLOSER @ 1016 TO ALLOW THEM TO SAFELY MAKE REPAIRS TO EQUIPMENT IN THAT ORDER // COD-69 ISO OCR 39831024A00032 VER/HFP L3/HFP IDC XXXX
5564 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-06-02 17:47 | 2009-06-02 20:35 | 18 | 168 | 60845-1 | 3024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 1147-45. 15T FUSE OUT ON POLE 1147-48. CALL TIM HE IS GOING TO SEND BILLY CAMPBELL LTHIS WAY. CHANGED INSULATOR FUSED UP EVERYTHING OK. VER/KEP L3/KEP
5565 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2011-07-19 21:33 | 2011-07-19 22:00 | 112 | 27 | 4565321 | 3024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT OPEN AT POLE 38830089000002 OPENED AT 2133 - OPENED OCR TO MAKE REPAIRS // COD-112 ISO OCR 38830090000221 VER/HFP L3/HFP IDC HOW DID WE HAVE LOOP BURNT OPEN WITH NO OUTAGE?
5566 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-02-24 08:36 | 2016-02-24 11:00 | 21 | 144 | H4753731 | 3024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY 1 CUSTOMER OUT TILL FUSE 518 OPENED AT 0836_GROUNDED AND TAGGED FOR TIM THOMAS ON 875-518..OPEN CUTOUTS AT 836GROUNDED AND TAGGED FOR TIM THOMAS ON 875-518..OPEN CUTOUTS AT 836.. RELEASED BY CREW 076S01// REPAIRS MADE RESTORED POWER AT 1100 // 30T FUSES ON POLE 518//MADE MDC TO SHOW L/F AS 30T// VER/CRB AJB
5567 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-04-26 11:20 | 2022-04-26 15:32 | 12 | 252 | 4801951 | 3024 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burned in 2 at squeeze, Myles Robinette is coming to assist with repairs
5568 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-07-22 20:04 | 2014-07-22 21:00 | 54 | 56 | 4274331 | 3024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 30T FUSE 69-C2-4549 VER/CRB AJB
5569 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-04-08 15:06 | 2015-04-08 18:15 | 16 | 189 | 4290251 | 3024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ..PATROLLING LINE..LINE CUTOUT.. BURNED UP ON POLE 679-142.CHANGING../COD 16// VER/ ADH
5570 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-04-25 10:01 | 2015-04-27 12:22 | 1 | 3021 | 4364411 | 3021 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 @ 37830247D01085 === NEED LINE CREW AND A 50 KVA 7200 === CHANGED TRANSF OUT === OPEN LINE FUSE @ 37830248B11636 AT 13:45 SO CREW COULD LIFT HOT TAP @ 37830247D01085// ALL POWER BACK ON @ 14:24 POWER OK/ ISO 37830247D01085/ COD 1/ DUPLICATE IN HOIS FOR OFF TIME ON LINE FUSE 37830248B11636 6 CUSTOMERS SEE H4364411 VER/HFP L3/HFP
5571 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-09-27 12:42 | 2010-09-27 16:46 | 43 | 244 | 54217-1 | 3016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED; POLE 404/316 TOP ONE FOOT OF POLE BURNT OFF, TRUCK ACCESSABLE AND WILL BE ABLE TO LOWER EQUIP ON POLE; ISOLATED AT POLE 404/106; RE-FUSED LINE FUSE WITH 15T; PARTIAL PWR RESTORED AT 1348 HRS; RELEASE TO LINE CREW RELEASED BY CREW 078S12 POWER RESTORED AT 16:46//COD 43// VER/DBM IDC XXXX
5572 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-08-14 12:28 | 2012-08-14 18:45 | 8 | 377 | 4935801 | 3016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 117-166 1 9.9 CUTOUT FELL APART NEED CREW AND TREE CREW NO TRUCKS SEND TO BOB R. RELEASED BY CREW 078S08//COD 8// VER/DBM IDC XXXX
5573 | South Williamson | 3411401 | DEWEY | INEZ | 2019-05-26 03:05 | 2019-05-26 08:40 | 9 | 335 | 4335211 | 3015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | s.//line fuse out on pole 768-236//found broke cutout on 768-192///replaced cutout//restored at 8:40//complete//em
5574 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-02-09 23:37 | 2010-02-10 12:10 | 4 | 753 | 54707-1 | 3012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ROADS BAD IN AREA......WILL CHECK AS SOON AS POSSIBLE, LOOP BURNT OFF ON POLE # 206-20, CALLING FOR HELP//VER/CRB IDCC PN284 XXXX
5575 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-03-28 10:24 | 2016-03-28 17:30 | 20 | 426 | 4887111 | 3010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 785-12 AND BURNT POLE OFF AT BRACKET. POLE IS IN A DIFFICULT LOCATION BUT CAN BE FRAMED DOWN ON. ISOLATED HOT-LINE CLAMP, GROUNDED AND TAGGED TO MILLER ON 785-81.//COD A PHASE 20//CUTOUT FAILED ON 785-12 AND BURNT POLE OFF AT BRACKET. POLE IS IN A DIFFICULT LOCATION BUT CAN BE FRAMED DOWN ON. ISOLATED HOT-LINE CLAMP, GROUNDED AND TAGGED TO MILLER ON 785-81. CLOSED PH. A LINE FUSE ON 785-108 @ 12:40 LEAVING ONE CUSTOMER OFF. BACK ON AT 17:30 TCM/ VER/CRB L3/HFP XXXHFP
5576 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-01-06 18:07 | 2022-01-07 10:50 | 3 | 1003 | 4314661 | 3009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut-out. Waiting on help to arrive to change manual cut-out. Power restored @10:50
5577 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-05-14 16:18 | 2011-05-14 19:15 | 17 | 177 | 4092051 | 3009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | //XFMR FUSE APPEARS BLOWN @ 38830979D00116// WILL REFUSE//FUSE APPEARED TO HAVE BROKE
5578 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-11-23 15:09 | 2012-11-23 18:17 | 16 | 188 | 4416541 | 3008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 43-119 F. POLE RELEASED BY CREW 078S08//WILL LOWER ATTACH B.PARSONS TO WRITE WO TO REPLACE AT LATER DATE//POWER RESTORED 18:17 CLOSE TKT /// COD-16 ISO LF 38830043000096 VER/HFP L3/HFP IDC XXXX
5579 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2016-06-19 20:31 | 2016-06-19 20:39 | 376 | 8 | 4389271 | 3008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 2206403-DUPL//VER/WHV// //// VER TIMES PER SCADA L3/HFP HFPC MCCNI CCDOT CDC85 FEC57 AJB
5580 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-11-27 04:58 | 2016-11-27 07:45 | 18 | 167 | 4131061 | 3006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN @ 122-23 . OPENED LOOP @ POLE 146-14 .OPENED LOOP @ 07:20 . PUT LOOP BACK ON @ 07:45 . ALL POWER BACK ON . RELEASED BY CREW 075H04//COD 18 /// RELATED TO 4131131 VER/HFP L3/HFP
5581 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2016-11-19 08:36 | 2016-11-19 16:27 | 16 | 471 | 4112081 | 3006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNED 35-5 POLE 879-369.. DEADEND XFMR INSTALLATION #2 PRIMARY AND NEUT .. ISOLATED AND GROUNDED AT 879-368 TO V. MULLINS.. DROPPED PRIMARY FROM TAKE OFF POLE DUE TO IT HANGING OVER PRIMARY XFMR RISER WHEN CREWS CAME TO REPAIR AND PULLED METER ON HOUSE CUST SAID COULD BACK IN YARD TO REPAIR20T LINE FUSE IN AT 11:25 RELEASED BY CREW 078H22/CREW ON SITE/FETR 1630/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST/1627/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L3/HFP XXXHFP
5582 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-03-16 17:27 | 2014-03-16 18:58 | 33 | 91 | 4497501 | 3003 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XARM BURNED HALF INTO,MUST HAVE A CUTOUT BRKNG DOWN,NEED BIG BUCKET,1 MAN,3 CUTOUTS W STAND-OFF MOUNTS.WILL GET CUTOUTS OFF ARM & ONTO INSULATED MOUNTS.WILL TAKE OUTAGE WHEN NEEDED//COD 33 (+9 MORE @ 1810 WHEN OPENED 38821105D00150)//ISO 38821105C00082//MADE REPAIRS AND RESTORED RELEASED BY CREW 074S06 IDCC CNT42, CHANGED TIME OFF FROM 1525, ESTIMATE BASED ON LOAD XXXX
5583 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2010-05-03 03:10 | 2010-05-03 05:10 | 25 | 120 | 54600-1 | 3000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "A" FUSE OUT POLE 147-409 - COD-25// REPLACED FAILED CUTOUT ON THIS POLE.// VER/DBM IDC XXXX
5584 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2020-06-11 20:46 | 2020-06-12 13:26 | 3 | 1000 | 4007981 | 3000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | A phase riser open @38820942B41446, checking. Found no trouble closed riser and it came back out, will need a line crew to come out to test cable. Going to work in am. Released by crew 074S05
5585 | Hazard | 3309301 | VICCO | REDFOX | 2021-11-20 11:09 | 2021-11-20 15:19 | 12 | 250 | 4110691 | 3000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Released by crew 077H07//fault pole 37830277000015Released by crew 077H07.. line fuse out pole 277-80, pole 277-15 burnt offReleased by crew 077H07.. line fuse out pole 277-80, pole 277-15 burnt off.. restored power at 15:19
5586 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-03-24 23:22 | 2013-03-25 03:08 | 48 | 226 | 4953231 | 2999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PH RECL OPEN POLE 1124-3022 (44 CC) // POLE 1124-592 BURNT OFF // LIFTED HOT TAP POLE 1124-597, INSTALLED GROUND AND PLACED TAG FOR DDC // CLOSED RECLOSER @ 0021 //3 MAN CREW //B.FRALEY, D. RUGGLES, B. TACKETT // RELEASED BY CREW 078S07 RESTORED NORMAL AT 0308 //VER/GAH IDCC CNT44 XXXX
5587 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-03-14 18:17 | 2008-03-14 23:50 | 9 | 333 | 57259-1 | 2997 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FUSE ON POLE 38830350000078 BLOWN,// 9 CUSTOMERS OUT//3001002 PRIMARY OFF OF INSULATOR,NEED TO REPLACE INSULATOR ON POLE 38830374000010, ALSO NEUTRAL DOWN ON THIS POLE, COPPER PRIMARY, ALUMINUM NEUTRALFUSE ON POLE ACTUAL RESTORATION TIME 23:50 3-14-08 VER/HFP IDC XXXX
5588 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2011-03-11 09:45 | 2011-03-11 11:36 | 27 | 111 | 53360-1 | 2997 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED CUTOUTS ON POLE 785-210 AT 09:45. THEY FEED PAD MOUNT 785-735// REPLACED COTOUTS AND ARRESTERS AND RESTORED SERVICE AT 11:36// 15T FUSES IN CUTOUTS.// RDM//MADE MDC//VER/CRB IDCC CDC88 XXXX
5589 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-06-20 18:23 | 2021-06-21 11:01 | 3 | 998 | 4775801 | 2994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva transformer on pole39830902A00363///replaced XFMR///complete BR
5590 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-03-12 12:18 | 2014-03-12 14:28 | 23 | 130 | 4470961 | 2990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FUSE IS OPEN ON 501-347 PATROLLING LINE, BROKE INSULATOR ON 525-207 REPLACED 1 19.9 PIN ISUL APR AT 1428 CLOSE TICKET VER/SEF IDC XXXX
5591 | Hazard | 3303901 | LESLIE | HYDEN | 2020-12-17 12:47 | 2020-12-17 14:57 | 23 | 130 | 4782241 | 2990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 412-287 burnt top pole off , opened stepdown on pole 412-286 to isolate at 13:26..restored power at 14:57.. Released by crew 077H03 LR- The 1sr CC came in at14:47
5592 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-12-05 03:26 | 2008-12-05 04:31 | 46 | 65 | 54604-1 | 2990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301// CUTOUT DOOR BURNT-UP. REPLACED DOOR AND RE-FUSED. SH VER/JHM L3/KEP IDC XXXX
5593 | Pikeville | 3403001 | PIKEVILLE | CITY | 2014-09-11 09:52 | 2014-09-11 12:10 | 34 | 138 | 4488591 | 2987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR/ ISOLATED ON POLE REMOVED HOT TAP ON POLE 37820025A00031// BAD SIDETAP INSUL ON 25-31// LIFTED HOTTAP THERE TO ISOLATE// CLOSED LINE F AT 25-328 AT 11:15// MADE REPAIRS// CLOSED IN 25-31 AT 12:10 RELEASED BY CREW 074S06// VER/BOW L3/HFP AJB
5594 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2015-07-25 09:25 | 2015-07-25 13:10 | 22 | 225 | 4940801 | 2987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKEN CROSSARM ON POLE 37830150000199/CLOSED IN CB @ 1039 //HOT UPTO RECLOSER 150-198//REPLACE CROSSARM ON POLE 37830150000199 GOT RECLOSER CLOSED AT 1310 RELEASED BY CREW 077S05 NOTE: DELETED LAST STEP OF REST - NO CUST EFFECTED ONLY AEP LIGHTS VER/HFP L3/HFP AJB
5595 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-10-03 09:11 | 2015-10-03 12:30 | 15 | 199 | 4308181 | 2985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT LINECREW REQIRED, TRUCK OK RELEASED BY CREW 078S11.. CREW ON SITE ETR 13:45.. CUTOUT REPLACED AND LINE BACK IN AT 12:30 COMPLETE// VER/ ADH // BOTH FUSES WERE OUT = L3/HFP XXXHFP
5596 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-05-17 10:52 | 2016-05-17 13:29 | 19 | 157 | 4225511 | 2983 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 286-202,PRIM COND DOWN THERE,NEED CREW,WIRE,BUCKET///////WIRE DOWN AT STEPDOWN XFR///////REPAIRS COMPLETED,WILL RE-ENERGIZE////RESTORED,BURNED INTO AT STIRRUP
5597 | Cannonsburg | 3001401 | LOUISA | CITY | 2010-05-13 15:22 | 2010-05-13 20:20 | 10 | 298 | 61581-1 | 2980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DROPPED RISERS FROM 10 KV 120/240 DOUBLE BUSHING TRANSFORMER AND CLOSED FUSE ... VOLTAGE BAD... NEED LINE CREW ... TRUCKS OK .. REPLACED 10 KV XFMR WITH 15 KVA .. TIME BACK ON 20:20 COD-10 VER/HFP L3/HFP IDC XXXX
5598 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2020-08-02 23:49 | 2020-08-03 09:45 | 5 | 596 | 4278301 | 2980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | replaced fuse door
5599 | Hazard | 3310502 | HADDIX | CANOE | 2016-03-14 17:32 | 2016-03-14 22:30 | 10 | 298 | 4845481 | 2980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE GOING TO OPEN TRANSFORMER TO CHANGE IN ANOTHER ORDER/ ISO 37830025000009/ COD 10/ VER/BOW
5600 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2008-11-25 15:20 | 2008-11-25 23:48 | 8 | 508 | 52267-1 | 2979 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3414901//AT 1650 TERRY FIELDS CONFIRMED THE BREAKER AT FISHTRAP TO BE IN THE OPEN POSITION//STATION DIST BRKR IS OPEN,LOCKED OUT.WILL PATROL FOR PROBLEM.FOUND WIRE DOWN.TRANSFERRED CUSTS TO OTHER PHASE WE MADE HOT VER/JHM IDCC CNT6, STP XXXX
5601 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-04-28 23:18 | 2021-04-29 09:13 | 5 | 595 | 4491921 | 2975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 38830139D00092 feeding towards 38830139D00095 . Repairs made .Closed at 09:13 Released by crew 078H11
5602 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-01-13 07:31 | 2019-01-13 09:30 | 25 | 119 | 4664621 | 2975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT REPLACED CUTOUT L3/HFP
5603 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-07-15 21:05 | 2009-07-15 22:30 | 35 | 85 | 63762-1 | 2975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND HOT TAP BURNTED OFF OF LINE FUSE, BASKET IS BURNTED INTO, MADED TEMP REPAIRS, DID NOT HAVE A BASKET ON MY TRUCK, SEND TO MR. RAYBURN TO HAVE LINE CREW TO REPAIRS THIS WITH A NEW BASKET, POLE NUMBER IS 902-145, CAN USE TRUCK ON THIS//COD 35// VER/DBM MLR OK
5604 | Hazard | 3309302 | VICCO | JEFF | 2009-08-04 17:29 | 2009-08-05 10:00 | 3 | 991 | 58553-1 | 2973 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, POWER RESTORED VER/KEP L3/KEP IDC XXXX
5605 | Pikeville | 3421001 | BREAKS | CITY | 2013-08-31 19:35 | 2013-09-01 12:05 | 3 | 990 | 4809441 | 2970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 12KV 25 KVA & RISER WIRE FOR SECONDARY & CUTOUT, MATERIAL HANDLER. VER/CRB L/3 CRB IDC XXXX
5606 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2015-06-23 17:51 | 2015-06-23 20:00 | 23 | 129 | 4646281 | 2967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE NOT BLOWN JUST BAD 38830205A10112 VER/CRB AJB
5607 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-11-19 06:54 | 2012-11-19 09:48 | 121 | 174 | 4407291 | 2966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED SECTIONALIZER AT 0654 TO ISOLATE TROUBLE (121 CUST) // LAST 2 CUST ON @ 0948 // COD-121 ISO OCR 37830077000034 VER/HFP L3/HFP IDC XXXX
5608 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-12-09 05:35 | 2012-12-09 10:20 | 19 | 285 | 4452971 | 2965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON 936-517//PATROLING/POLE 960-17 BURNT OFF//CAN FRAME DOWN ON IT//NEED LINE CREW//TRUCK APROACH//NEED 7200 CUTOUT,ARRESTOR AND BRKT,POLE IS DOUBLE DEAD END,#2AL WIRE//LIFTED HOT TAP ON POLE 936-14//GOING TO RESTORE UP TO HERE//CLOSED FUSE AT 07:25 FOR PARTIAL RESTORE/RESTORED ALL AY 10:20//COMPLETE//EM// COD 19// VER/DBM IDC XXXX
5609 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-01-25 19:58 | 2014-01-26 12:26 | 3 | 988 | 4313211 | 2964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DUE TO WEATHER AND ROAD CONDITIONS THIS WILL BE WORKED 01/26/14SECONDARY LEAD BURNED OUT OF XFMR..DAMAGED SEC BUSHING..WILL HAVE TO CHG 25 KVA XFMR AND UPGRADE LEADS TO 1/0..NEED 1 MAN AND MATERIAL HANDLER..25 KVA CONV..TRUCK ACCESSIBLE. COD-3 ISO TF 38830874000009 VER/HFP L3/HFP IDC XXXX
5610 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-10-31 06:07 | 2010-10-31 08:43 | 19 | 156 | 50373-1 | 2964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH SERVICER AFTER DAYLIGHT.PREDICTED FUSE NOT OUT......FUSE OUT UP IN CANEY ON 965-A-58...DONT THINK ITS ON THE MAPS...CUST COUNT WILL BE MUCH LOWER....PATROLLING // LINE FUSE MELTED OUT AT POLE 965-A-58 // REPLACED 20T FUSE & WEAK CUTOUT DOOR // CLOSED FUSE AT 0843 //VER/GAH IDC XXXX
5611 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-07-22 20:04 | 2011-07-23 20:45 | 2 | 1481 | 4589611 | 2962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER SERVICER (GREG FUGATE) NEED SMALL TRUCK AND A COUPLE OF MEN TO CHECK THIS OUT ---- BAD 15 KVA 7200 TRANSFORMER . RELEASED BY CREW 077H03PER SERVICER (GREG FUGATE) NEED SMALL TRUCK AND A COUPLE OF MEN TO CHECK THIS OUT ---- BAD 15 KVA 7200 TRANSFORMER . REPLACED TRANSFORMER AND RESTORED POWER AT 2045 VER/KEP
5612 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-09-29 07:30 | 2016-09-29 08:44 | 40 | 74 | 4940941 | 2960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER OPEN ON POLE 184-265 (40 CUST), BAD CUTOUT ON POLE 184-215, REMOVED CUTOUT OFF LINE, POWER RESTORED, XFMR ONLY FEEDS A FEW LIGHTS, WILL REPLACE THIS EVENING OR TOMORROW// CLOSED RECLOSER @ 0846//WILLL BE WORKED 09/30/16 CHANGED 4 CUTOUTS 4ARRESTERS/ ISO 37830184B00264/ COD 40/ VER/BOW /// VER PER VOICE RECORDER TIME ON 0844 09/29/16 ALL BUT AEP EQUIP = L3/HFP HFPC LCD37830184B00264 TON1230 09/30/16 AJB
5613 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2014-01-06 22:20 | 2014-01-06 23:00 | 74 | 40 | 4242011 | 2960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT SERV TO REPAIR,REPAIRS MADE ALL CUST RESTORED @ 2300 PLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP IDC XXXX
5614 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-09-30 20:28 | 2018-10-01 13:26 | 27 | 1018 | 4183881 | 2955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW AND MANUAL TREE CREW REQU..pole 206-2138 broke need to go back with a 40-4,,will need a 25kva and deaden installation under ground service running up pole ,,trucks to pole,,cut primary and neutral down @ 206-2351,,line fuse 206-2060 back in @ 22:06 leavin off 1 customer Released by crew 078S05/on site RM opening line fuse on 206-2060 to climb pole and squees loop up om 206-2351open@12:35 closed@13:26 please close tic RM
5615 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2010-03-12 20:04 | 2010-03-12 23:21 | 15 | 197 | 65850-1 | 2955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASES OPEN ON RECLOSER//COD 15 BYPASS CUTOUT BROKE ON 1024-6. DIFFICULT LOCATION - ATTEMPTING TO ISOLATE TO RESTORE MOST CUSTOMERS. ISOLATED LINE SIDE HOT LINE CLAMP AND OPENED ALL THREE RECLOSERS @ 1024-6. CLOSED REC @ 1047-141 @ 23:21 RESTORING ALL CUST EXCEPT PRI METERING (CREW TO REPAIR IN THE MORNING) RELEASED BY CREW 076S02 CUST OKD PRIMARY METERING TO BE RESTORED THIS WEEK//VER/CRB IDC XXXX
5616 | Hazard | 3309302 | VICCO | JEFF | 2013-07-09 01:02 | 2013-07-09 11:16 | 6 | 614 | 4490341 | 2954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SDB / "WILL CHECK AT REGULAR TIME"SDB / WILL CHECK AT REGULAR TIME === LINE FUSE OUT ON POLE 37830323B00072 ==SDB / WILL CHECK AT REGULAR TIME == BAD ARRESTER ON POLE 37830323B00290 === TOOK ARRESTER OFF LINE === MADE MAIN LINE HOT AT 8:50 === ONE CUST STILL OFF WILL CHANGE ARRESTER NEED LINE CREW AND BIG BUCKETSDB / IDCC STP MISSING XXXX
5617 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-03-24 08:02 | 2010-03-24 10:05 | 24 | 123 | 53450-1 | 2952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE BURNT TOP OF POLE 168-130 OFF//SERVICER OPENED LINE FUSE 168-6 IN ORDER TO ISOLATE // I OPENED LINE FUSE ON POLE 168-6 SERVING DEADENING FK AT 08:02. TIM HALL IS SENDING CONTRACT CREW. WE CLOSED LINE FUSE IN AT 10:05.//COD 24// VER/DBM IDC XXXX
5618 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-03-05 06:11 | 2012-03-05 08:55 | 18 | 164 | 4547131 | 2952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FUSE OPEN ON POLE 38830785D20222// ISO//COD 18 // CLOSED @ 0855//65T MISSING FROM MAP, MD FILED // VER/DBM IDC XXXX
5619 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-09-03 09:22 | 2021-09-03 11:25 | 24 | 123 | 4205831 | 2952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | controls arent operating correctly on the recloser pole. bypassed recloser.. open source and load side disconnects, tagged control all to the KY DDC. bypassed recloser @ 11:25
5620 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-04-21 13:48 | 2018-04-21 15:00 | 41 | 72 | 4261251 | 2952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | lighting arrestor blew , I cut it in the clear and refused line/ ISO 37830427B00009/ COD 41 MD DONE
5621 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-12-22 08:07 | 2013-12-22 10:12 | 49 | 125 | 4188051 | 2951 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN DOWN////OPEND C PHASE UP,CLEARED BRKEN CUTOUT,RESTORED.NEED BUCKET,1 MAN,CUTOUT////////REPLACED CUTOUT AND RSTORED//COD 49// VER/DBM
5622 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2015-07-03 02:43 | 2015-07-03 06:30 | 13 | 227 | 4712791 | 2951 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 138-228 BAD LA NO TRUCK TO POLE 138-198 20T ***PUT IN AED*** VER/SEF
5623 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2009-03-28 20:02 | 2009-03-29 10:30 | 25 | 868 | 62514-1 | 2950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-25 RELEASED BY CREW 074S02 FRANK ISOLATED TROUBLE , OPEN LOOPS AT POLE 171-A-175 WIRE DOWN ACCROSS RIVER. TR`S 171-A-150 30 31 NO CUSTOMERS ARE MAPPED TO THESE XFMRS. FRANK WILL NOTIFED DAVE SAMMONS AND WILL FOLLOW UP TOMORROW.WR # 29127688 // RELEASED BY CREW 074S02 FRANK ISOLATED TROUBLE , OPEN LOOPS AT POLE 171-A-175 WIRE DOWN ACCROSS RIVER. TRS 171-A-150 30 31 NO CUSTOMERS ARE MAPPED TO THESE XFMRS. FRANK WILL NOTIFED DAVE SAMMONS AND WILL FOLLOW UP TOMORROW. L3/HFP IDC X
5624 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2011-11-15 00:33 | 2011-11-15 10:23 | 5 | 590 | 4077101 | 2950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE-CREW REQUIRED--BAD CUTOUT NEEDS REPLACED--MIGHT REACH WITH LARGE BUCKET RELEASED BY CREW 078S07//HOLDING UNTIL DAYLIGHT FOR CREW AS PER AFTER HOURS DISPATCHING GUIDELINES//COD 5//CREW ON SITE/FETR1045/VEM/NOTE TO MAPPING 10T FUSE ON POLE 1124-2032/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1023/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB IDC XXXX
5625 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-10-07 18:44 | 2017-10-08 01:45 | 7 | 421 | 4418101 | 2947 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRANSFORMER ARRESTER ON 38830875A00724 FAILED. NON TRUCK APPROACH. ISOLATED ARRESTER AS WE DIDNT HAVE ONE ON THE TRUCK TO REPLACE. CLOSED LINE FUSE ON 875-277 @ 1:45. SH // COD 7// VER/DBM ACB
5626 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-08-20 18:13 | 2019-08-21 10:35 | 3 | 982 | 4914601 | 2946 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | this is pole # 38831084A00265 sec bushing burned up , need 50kva 7200 and 4 / 0 leads , can get bucket to pole and this is behind showtime pizza Released by crew 077S05
5627 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-03-17 06:26 | 2008-03-17 07:30 | 46 | 64 | 57793-1 | 2944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLING LINE//3001101//PATROLING LINE// BAD FUSE//VER/CRB IDC XXXX
5628 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-07-10 00:10 | 2010-07-10 00:56 | 64 | 46 | 64577-1 | 2944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | EMERGENCY OUTAGE TO REPAIR ARRESTOR THAT HAS BLOWN // OUTAGE TO MAKE REPAIRS TO ORDER 64526-1 // COD-64 IDC XXXX
5629 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-04-06 18:47 | 2021-04-06 21:40 | 17 | 173 | 4424951 | 2941 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | looks like wire pull out of splice on pole need pt pin and insulator// cod 17
5630 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-09-11 15:40 | 2013-09-11 16:50 | 42 | 70 | 4838941 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE 45-2547 WIRE BURNT OFF CUTOUT BURNT CUTOUT UP VER/HFP L3/HFP IDC XXXX
5631 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-07-03 17:22 | 2019-07-04 17:52 | 2 | 1470 | 4649441 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kv 19.9 xfmr Released by crew 077S11 Released by crew 077S12 1752
5632 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2008-09-07 01:47 | 2008-09-07 03:25 | 30 | 98 | 60099-1 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3409001// BAD INSULATOR - WILL HAVE TO OPEN FUSE ON POLE 785D1-693 // AT 0147 OPENED LINE FUSE DUE TO BURNING ON POLE WITH BAD INSULATOR - COD-30 // CREW ENROUTE. CHANGED INSULATOR EVERYTHANG OK.// POWER ON AT 0325 VER/LDA MLRC PN 38830785C20388
5633 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2022-11-18 07:52 | 2022-11-18 11:08 | 15 | 196 | 4157641 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Line fuse open 125-D1-235,Primary down from 125-D1-235 to 125-51,Crew in Route to make repairs.. Released by crew 074S01// repairs made // on @ 11:08
5634 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-06-12 16:10 | 2017-06-12 17:20 | 42 | 70 | 4953631 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO OUTAGE TILL RECLOSER OPENED ON POLE 37830256000017//OPENED ON POLE 17 AT 16:10 TO REPLACE INSULATOR AND REPAIR NETURAL RESTORED POWER AT 17:20 VER/CRB SJG
5635 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-10-12 17:10 | 2011-10-12 17:22 | 245 | 12 | 4971961 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED SWITCHES TO SAFELY CHANGE CUTOUT ///VER/CRB IDCC CCO XXXX
5636 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-07-07 20:13 | 2019-07-08 00:18 | 12 | 245 | 4675341 | 2940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ Neutral riser out of transformer, Bolt in neutral bushing broke,Crew required, 50kva 7200v, Truck to pole. Can possibly change Neutral bolt in transformer. Possible lightning/replaced bad 50 kvAon 69-150/ power on @ 0018/ please close ticket/ MLH L3/HFP
5637 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2016-02-06 09:11 | 2016-02-06 10:40 | 33 | 89 | 4680471 | 2937 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER LEAD MELTED UNDER LOAD, MADE NEW CONNECTION,,OPENTRANSFORMER AT 10:23 SND CLOSE AT 10:40// VER/ ADH AJB
5638 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-11-03 14:54 | 2015-11-03 15:00 | 489 | 6 | 4406781 | 2934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED BREAKER TO SAFELY BYPASS "A" PHASE REGULATOR VER/KEP /// VER TIMES PER DOL & VOICE RECORDER L3/HFP XXXHFP AJB
5639 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2013-12-01 10:47 | 2013-12-01 13:30 | 18 | 163 | 4090701 | 2934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER HAS BURNED OUT OF THE TOP OF THE CUTOUT THAT FEEDS BURGETT BR. NEED ONE MAN TO HELP. NO TRUCK ACCESS. @ 1229 - J. REED COMING OUT TO HELP.RISER HAS BURNED OUT OF THE TOP OF THE CUTOUT THAT FEEDS BURGETT BR. NEED ONE MAN TO HELP. NO TRUCK ACCESS. CUTOUT REPLACED, AND POWER IS BACK ON.//COD 18// VER/DBM L3/HFP IDCC FEC46 XXXX
5640 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-01-01 17:02 | 2022-01-02 09:20 | 3 | 978 | 4251531 | 2934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on 37830021000253 and fell in clear blew line fuse 37830021000163//left tr 21-253 out till can replace cutout 1/2/22 and restored line fuse at XXXXfound open A ph line fuse open on p21-163, broken cutout on p21-253. tried to refuse and it blew again, will need to change CO to restore. TA.. line crew and flagging required.TRT Released by crew 074E08. CREW ON-SITE, ON AT 09:20
5641 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-06-01 00:24 | 2012-06-01 10:10 | 5 | 586 | 4857581 | 2930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED TRANSFORMER CUTOUT ON POLE 98-217//COD 5// VER/DBM IDC XXXX
5642 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2022-11-22 10:47 | 2022-11-22 12:28 | 29 | 101 | 4172611 | 2929 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Lf out on pole 449A4-62. Found a bad arrester at pole 449B3-674. Made repairs. Power restored at 12:28.
5643 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-10-09 08:24 | 2012-10-09 10:05 | 29 | 101 | 4125041 | 2929 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP AND RISER FELL OFF ON POLE 378-273 COD-51 ISO PO @ 37830378C00273 VER/HFP L3/HFP IDC LOOKS LIKE PH A CHANGED COUNT FROM 51 XXXX
5644 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-10-05 15:14 | 2020-10-05 16:55 | 29 | 101 | 4528341 | 2929 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Basket burned off @ pole 38830163000160, Step down pole. Opened line fuse on pole 38830163000148, tagged to myself. Grounds @ worksite 163-160. Repairs made, line fuse back in @ 16:55. Power restored Released by crew 078S02
5645 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2013-03-31 16:41 | 2013-03-31 20:45 | 12 | 244 | 4969951 | 2928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOW SIDE FUSE ON STEPDOWN BLOWN..WIRE DOWN POLE 7-A-7.BURNT DOWN FROM BAD CONNECTION.NEED 1 MAN & MATERIAL HANDLER.//MCKINNEY, ERICLOW SIDE FUSE ON STEPDOWN BLOWN..WIRE DOWN POLE 7-A-7.BURNT DOWN FROM BAD CONNECTION.NEED 1 MAN & MATERIAL HANDLER.//.ALSO.TREE ON LINE & 2 SPANS DOWN AT POLE 7-A-63..// COD-12 ISO LF 37820007A29000 IDC XXXX
5646 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-04-22 07:40 | 2011-04-22 09:42 | 24 | 122 | 61892-1 | 2928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNT - MAKING REPAIRS// CLOSED AT 0942 VER/TOM L3/TOM IDC XXXX
5647 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2014-02-17 22:55 | 2014-02-18 02:24 | 14 | 209 | 4395651 | 2926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE RISER CAME LOOSE //VIRGIN & HICKS & HOWARD //A 2 CC PHASE CUTOUT NEED REPLACED--1/0 LASH DOWN IN PARKING LOT-SERVERS AS PRIMARY NEUTRAL--NEED 3 CUOUTS AND 1/0 WIRE TO MAKE REPAIRS TRUCK TO POLE ** AT 0050 OPENED BC 12 CC CLOSED ALL 0224 CUTOUT TO MAKE REPAIRS.A PHASE RISER CAME LOOSE //VIRGIN & HICKS & HOWARD //A PHASE CUTOUT NEED REPLACED--1/0 LASH DOWN I IDC XXXX
5648 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-02-03 01:30 | 2014-02-03 02:45 | 39 | 75 | H4338831 | 2925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF. BROKEN CUTOUT. /// T SMITH & V HURT // TOP OF POLE BURNT OFF. BROKEN CUTOUT. OPENED LINE CUTOUT ON POLE 182-131 AT 1:30... CLOSED BACK IN AT 2:45.. COD-42 ISO LF 37830182C00131 DUP IN HOIS VER/HFP L3/HFP IDC XXXX
5649 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-04-14 15:30 | 2019-04-15 15:30 | 5 | 1440 | 4095031 | 2925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 302-103 (2 COD), manuel pole, line fuse out on 302-59(5 COD), took clamp off 103, re-fused 59,one cust still out Released by crew 077S02 opened on pole 59 at 15:15 al power restored at15:30
5650 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-04-21 14:20 | 2021-04-21 15:05 | 65 | 45 | 4467981 | 2925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed on 761-141. Opening switches on 761-131 to isolate. Crew on site.//NO OUTAGE TILL SW OPENED//OFF @ 1420 ON @Cutout failed on 761-141. Opening switches on 761-131 to isolate. Crew on site. No interruption until I opend sw @ 14:20. Made repairs and closed sw 761-131 @ 15:05. sh//MD HAS BEEN MADE TO SHOW SWITCHES
5651 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-05-10 07:32 | 2021-05-10 10:54 | 29 | 202 | 4568541 | 2924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | B phase line fuse open @ 38831098D00111.// Will be patrolling.// B phase down from 38831098D00170 to 38831098D00171.// Crew required// Opened A & C phases @ 10:15 to make repairs.Repairs made and restored @ 10:54 Released by crew 074S11
5652 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-06-18 11:35 | 2016-06-18 12:09 | 86 | 34 | 4383891 | 2924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ***SEE 4383801*** OPENING SECTIONALIZER TO REPAIR BURNT LOOPS ON POLE 37820025D00023/ ISO 37820025A00063/ COD 86/ RESTORED @ 1209/ VER/BOW AJB
5653 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2015-05-15 19:27 | 2015-05-15 22:19 | 17 | 172 | 4433881 | 2924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE( 48 CUST) BYPASS BURNT UP // NEED 19.9 CUTOUT - 3 DEAD END BELL INSULATORS & BIG BUCKET & A LINE MECH // R THOMAS COMING TO HELP SERVICER MAKE REPAIRSCUTOUT ON A PHASE BURNT UP AND DESTROYED 3 BELL INSULATORS ON A PHASE TRUCK APPROACH NEED 1A LINEMAN AND BIG BUCKETCUTOUT ON A PHASE BURNT UP AND DESTROYED 3 BELL INSULATORS ON A PHASE COD-48 SEE 4434181 NEED ITS TIME AS A STEP IN THIS ORDER - EVERYONE NOT RESTORED IN THIS ORDER AJB
5654 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-12-17 08:20 | 2016-12-17 13:29 | 26 | 309 | 4203131 | 2923 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TAGS AND GROUNDS PLAED FOR KY DDC // 0915 - NOTIFIED VM ONCE AT SITE AND VERIFIED - CAN R/T, R/O AND ASSUME DA// TOM - EMERGENCY OUTAGE - OPENED RECLOSER TO ISOLATE BURNT POLE ASSOCAITED WITH ORDER 4202551//TOM OPENED OCR @ 0820 CLOSE AND ENERGIZED TO OPEN LOOPS AT 0900// CLOSED HOT TAP @ 1329 - REMAINDER OF CUSTOMERS RESTORED ON 4202551 VER/TOM L3/TOM AJB
5655 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-06-21 14:11 | 2015-06-21 22:18 | 6 | 487 | 4629101 | 2922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 1084B-14 . MAY GET BUCKET TO POLE , NEED LINE CREW . NEED 50KVA XFMR & CUTOUT & FIBERGLASS TBRACKET . 7200V . CUST. SAID COULD TAKE BUCKET INTO YARD IF IT WILL GO . CALLED CREW JUST INCASE CANT GET TRUCK TO POLE . RELEASED BY CREW 075H04 INSTALLED NEW XFMR RESTORED POWER AT 2218 CREW 077H01//COD 6 L3/DKG
5656 | Hazard | 3308001 | JACKSON | S.JACKSON | 2022-11-11 16:20 | 2022-11-12 15:30 | 3 | 1390 | 4129411 | 2921 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out on xmfr bank on pole 38831060B00228 is bad cause arms and top of pole to smoke.cust said it can be fixed at later date.arms, cutout, and dead end bells need replaced. Released by crew 077H20//L/F 38831060B00020 WAS NEVER OPEN//COD 2//THIS IS ON JACKSON/SOUTH JACKSON//.open fuse 1060-247 @ 13:09, closed at 15:30, all restored p.hicks
5657 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-01-06 17:48 | 2020-01-06 20:07 | 21 | 139 | 4218721 | 2919 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | line fuse open on pole352-58, stirrup burnt off at that pole ..made repairs restored power at 20:07. L3/HFP
5658 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-07-26 08:06 | 2009-07-26 20:15 | 4 | 729 | 64125-1 | 2916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE BURNTED OFF, POLE NUMBER IS 1098-6018, WHICH IS A 404 POLE, EVERYTHING WILL WORK BACK, JUST NEED A NEW CUTOUT AND ARRESTOR, CREW REQUIRED//COD 4// VER/DBM IDC XXXX
5659 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-09-06 07:46 | 2011-09-06 11:49 | 12 | 243 | 4829601 | 2916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE/FUSED CUTOUT DOOR BURNT UP/NO CREW REQUIRED IDC CHANGED FROM WEATHER UNKNOWN XXXX
5660 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-08-21 09:44 | 2020-08-21 19:27 | 5 | 583 | 4353751 | 2915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | got two bad de isulators for 7200 on pole38830991000040 Released by crew 077S05. fuse open on 1015-37, replacing pole, and dead ends, p.hicks, all powe restored @ 19:27 hrs
5661 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2009-09-14 13:29 | 2009-09-14 16:31 | 16 | 182 | 55402-1 | 2912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TO REPLACE CUTOUT, POTHEAD BURN OUT OF BOTTOM OF CUTOUT. VER/KEP L3/KEP IDC XXXX
5662 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2019-04-12 11:23 | 2019-04-12 13:15 | 26 | 112 | 4085401 | 2912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 38830069D37014. Fetr 13:45 50t back in @ 13:15
5663 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-01-20 04:43 | 2017-01-20 07:30 | 21 | 167 | 4313851 | 2912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON POLE 167B-150..WILL PATROL..FOUND BAD DEADEND INS. ON POLE37830167B00441.WILL LIFT HOT TAP ON POLE 167-195 AND CLOSE BACK IN @ POLE 167-150...AND MAKE REPAIRS.//CLOSED L/F IN @ 0655//CLOSED HT @ LINE FUSE BLOWN ON POLE 167B-150..WILL PATROL..FOUND BAD DEADEND INS. ON POLE 167-441.WILL LIFT HOT TAP ON POLE 167-195 AND CLOSE BACK IN @ POLE 167-150...AND MAKE REPAIRS.REPAIRS MADE..RE-ENERGIZED @ 07:30... RELEASED BY CREW 074S01 VER/CRB L3/HFP HFP AJB
5664 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-07-22 22:41 | 2017-07-23 01:55 | 15 | 194 | 4156961 | 2910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 45-161, CRACKED CUTOUT ON POLE 45-112, CUTOUT CHANGED AND POWER RESTORED AT 01:55. 38830045A10061 38830045A10112 VER/AWD L3/HFP XXXHFP SJG
5665 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-04-11 11:47 | 2010-04-11 15:13 | 16 | 206 | 62084-1 | 2909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A//MADE A MD//VER/CRB IDCC PN28 XXXX
5666 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-01-30 13:04 | 2009-02-01 13:30 | 1 | 2906 | 52553-1 | 2906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILLEY CREW REPLACED POLE 38830069D47542, POLE FIRE. ALL POWER RESTORED.
5667 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-06-04 15:51 | 2008-06-05 16:04 | 2 | 1453 | 57527-1 | 2906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ/BAD 25KVA XFMR/NO TRUCKS/DIFFICULT LOCATION/VEM RELEASED BY CREW 078H14 VER/HFP
5668 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2012-11-05 11:14 | 2012-11-05 12:20 | 44 | 66 | 4362031 | 2904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED OFF, I REPLACED AND REFUSED//APHASE ONLY COD 34 ///VER/CRB L/3 CRB IDC PH C NOT A CHANGED COUNT FROM 34 XXXX
5669 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-10-03 19:22 | 2014-10-04 01:25 | 8 | 363 | 4549141 | 2904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69B18157 80T OPEN. BURNT POLE 69B18287 IS A 40-5. RELEASED BY CREW 078H12 VER/KEP L3/HFP
5670 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-11-11 16:09 | 2019-11-11 20:34 | 16 | 265 | 4021241 | 2903 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser open @24-B3-1147, checking. Found bad spot in URD cable, spliced out and closed riser back in @2034. ¦¦¦ NEEDS MAP CORRECTED AND POSSIBLE TAP MOVED TO MAIN LINE - L3/HFP
5671 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-01-16 14:52 | 2020-01-16 17:10 | 21 | 138 | 4313091 | 2898 | PARTIAL POWER | EQUIPMENT FAILURE | INSULATOR | neutral came off of arm pin on 1135A-6 contacting cutout riser.crew required nta .crew arrived,made repairs.resoredt 17:10. L3/HFP
5672 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-01-02 05:55 | 2020-01-02 08:36 | 18 | 161 | 4202761 | 2898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 37830361000056/broken cutout on pole 361-56, replaced Released by crew 077H14 ISO 37830361000056 COD 1837820052000036
5673 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2018-11-14 14:32 | 2018-11-14 17:06 | 181 | 154 | 4398961 | 2896 | DISTRIBUTION STATION | EQUIPMENT FAILURE | OTHER EQUIPMENT | 2150502//At 1432, opened the Nolan 12kv cb at Borderland due to a defective line disc at station//cc1118//isolated the Chattaroy 12kv Cb G and closed the Nolan cb at 1448 rest 312 custs//ckts tied thru transfer bus//806 custs remain out//crew enroute to make repairs//ckt restored at 1706//// 130 of the 311 Customers on Nolan are Apco custs. Two different clearing devices due to opening up Nolan cicruit. Those customers were not out, or feed from Chattaroy circuit, so it is not abnormal feed. ACB
5674 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-01-13 01:06 | 2014-01-13 10:45 | 5 | 579 | 4276041 | 2895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM 1-13-14//CUTOUT BROKE ON POLE 842-27//ACROSS CREEK//NEED CREW TO ASSISTWILL WORK IN THE AM 1-13-14//CUTOUT BROKE ON POLE 842-25//ACROSS CREEK//NEED CREW TO ASSIST//REPAIRS MADE//RESTORED AT 10:45//COMPLETE//EM COD-5 ISO LF 38820842B00025 VER/HFP L3/HFP IDC XXXX
5675 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-05-16 08:59 | 2020-05-16 13:00 | 12 | 241 | 4841591 | 2892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Line fuse open @1077-D-44, checking. Loop burndt into @1077-D-247 and got against neutral, will be making repairs. Got repairs made, closed L/F back in @1300.
5676 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-07-08 20:13 | 2012-07-09 08:15 | 4 | 722 | 4624861 | 2888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 424-54, REPLACED CUTOUT, ALL POWER RESTORED, BT
5677 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-10-31 17:25 | 2018-10-31 17:51 | 111 | 26 | 4347461 | 2886 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | tie wire broke @ pole 43-161. crew reqd. no trucks. crew can isolate, tag, & ground @ recloser pole 44-2004. Released by crew 078H17///open recloser 44-2004 @ 17:25 ///closed @ 17:51///all repairs made complete BR NO customers out until recl was open L3/HFP/// 1 customer was out at 15:08. restored at 18:13 after this one was restored. see related outage.
5678 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2012-07-15 01:37 | 2012-07-15 11:14 | 5 | 577 | 4729331 | 2885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED ARRESTER ON POLE 171 AND CLOSED SECTIONALIZER, ALL WORK COMPLETE / GXJ//COD 5 IDC XXXX
5679 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2018-05-20 08:03 | 2018-05-20 16:12 | 15 | 489 | 4381371 | 2883 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Riser fuse open @1152-B2-211, checking. According to fault finders, bad spot in primary cable between feed through24-A1-1292 and padmount 24-A1-1296, will need a line crew with fault finder, isolated last span of cable.//CLOSED RISER FUSE @ 1054//Riser fuse open @1152-B2-211//// found fault and making repairs now./// Reapaired bad spot in UG primary cable and closed in at 16:12 Tim McCoy
5680 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-05-25 08:19 | 2020-05-25 10:30 | 22 | 131 | 4902331 | 2882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout at pole 37830222D30547. made repaires and restored power at 10:30
5681 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-08-18 14:35 | 2022-08-18 16:05 | 32 | 90 | 4760911 | 2880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 794-45//broke cutout on 770-70//repairs made//restored at 16:05
5682 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-01-10 10:10 | 2008-01-10 12:10 | 24 | 120 | 55453-1 | 2880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3200202//, LEAD BURNT OFF AT HOT LINE CLAMP, MAKING REPAIRS, SOLID DOOR, 300 AMP//SENT REPORT TO MAPPING ON MISSING DISCONNECT DBM//COD 24// VER/DBM IDC XXXX
5683 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-02-09 18:38 | 2021-02-09 21:02 | 20 | 144 | 4952991 | 2880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | L/F door is in// will have to walk to pole and verify if fuse is blown or if wire is down/// Fuse link had broke but door did not drop down. Refused and restored @ 21:02/ ISO 38830882A00321/ COD 20
5684 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-07-27 20:30 | 2018-07-27 23:30 | 16 | 180 | 4864851 | 2880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened at 2030.bad cutout on pole 929-104,burning pole, opened line fuse on 929-237 grd snd tsgged for myself..crew enroute 38830929000104 L3/HFP
5685 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-05-03 08:05 | 2008-05-03 10:54 | 17 | 169 | 56533-1 | 2873 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110903/// 2- BAD CUTOUTS POLE 18-53 AND 18-49 RELEASED BY CREW 078S08/CREW ON SITE/DIFFICULT LOCATION/FETR1145/VEM/CUTOUT CHANGED POWER RESTORED TO ALL CUST 1054/PLEASE CLOSE TICKET/THANKS/VEM // COD 17// VER/DBM IDC XXXX
5686 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2010-10-09 22:21 | 2010-10-10 01:10 | 17 | 169 | 58384-1 | 2873 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ. POLE 137-9 BAD CUTOUT WR#37256249 RELEASED M.P. RELEASED BY CREW 078H12 VER/ARN IDC XXXX
5687 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-04-03 21:23 | 2018-04-05 21:15 | 1 | 2872 | 4170911 | 2872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Dispatched in accordance with KYPCo 4/3/18 Callout Plan// line fuse open on pole 37830387C00502, bad arrester on pole 37830387C00502, need to change 19.9 cutout arrester and bracket = crew required. Released by crew 077E10//can close power restored mwl
5688 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-02-24 13:16 | 2014-02-24 13:49 | 87 | 33 | H4430191 | 2871 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN ON RIGHT PHASE ON POLE 746-14///NEED BIG BUCKET//CREW ON SITE///REPAIRS MADE// RELEASED BY CREW 079S01 // B PHASE INITALLY OUT 245 CUST // @ 1316 OPENED A & C PHASE SWS DROPPING 87 CUST // ALL REST @ 1349 /// VER/HFP L3/HFP IDC XXXX
5689 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-08-06 10:05 | 2015-08-06 10:46 | 70 | 41 | H4102581 | 2870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | C PHASE RECLOSER OPEN @ 327-27///PATROLLING///#4 SOLID COPPER C PHASE DOWN 327-46 TO 327-71.CREW REQUIRED NO TRUCKS PULLED OUT OF SLEEVE///A&B RECLOSER STILL IN @ 327-27 RELEASED BY CREW 078S05,OPEN A& B RECLOSERS @ 1005 REPAIRS MADE A,B & C RECLOSERS IN @ 1046 PLEASE CLOSE TICKET THANKS.BT/DUPLICATE IN HOIS// VER/ ADH //// DUP OF 4102581 FOR A & B PHASE OUTAGE 70 CUST - VER TIMES PER VOICE REC -- L3/HFP HFPC DUP CCU FP38830327B00027 AJB
5690 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-02-20 10:12 | 2015-02-20 17:02 | 7 | 410 | 4054341 | 2870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE.//////////BAD 25 19.9,NEED 50//////NEED CREW,CAN USE MAT HANDLER.ALSO RE-SQUEEZE CONNECTIONS AT 2NDARY RELEASED BY CREW 074S06 VER/ARN
5691 | Hazard | 3311103 | STINNETT | WENDOVER | 2014-12-24 22:49 | 2014-12-25 05:28 | 17 | 399 | 4883171 | 2863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7.2KV CUTOUT, 40/4 POLE BURNT OFF. NEED POLE , DEAD ENDS, 15KVA 7200 XFMR, CUTOUT AND T BRKT. NEED 3 MAN CREW AND LINE TRUCK,..WILL TRY TO CUT DEAD ENDS AND GET SOME CUST BACK ON..P.HICKS.OPEN LOOP ON 435-255, CLOSED FUSE ON 435-57 @01:23 HRS VER/SEF AJB
5692 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-01-01 06:46 | 2022-01-01 13:35 | 7 | 409 | 4243301 | 2863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LF open on 38831149000119// checking// dead end insulator looks bad on pole 1140-68, will change when Paul Layne arrives// made repairs, tried fuse and it didnt stay in, found another bad insulator on 38831149000067, will be making repairs
5693 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-09 12:26 | 2022-01-09 17:44 | 9 | 318 | 4328551 | 2862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse open @ 167-B-132,(ASSESSING CONDITION)Line fuse open @ 167-B-132,Have a bad Deadend bell at pole 167-B-137,Spoke with Paul Layne and he is on way to help make repairs.Line fuse open @ 167-B-132,Have a bad Deadend bell at pole 167-B-137,This is a Manual Pole,Spoke with Paul Layne and he is on way to help make repairs .Restored at 17:44.
5694 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-05-03 11:00 | 2010-05-03 13:39 | 18 | 159 | 55014-1 | 2862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, FUSED CUTOUT ON POLE# 936-24 BAD, 50T FUSE, REPLACING IT IDC XXXX
5695 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-11-02 19:41 | 2011-11-03 00:27 | 10 | 286 | 4045811 | 2860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY RISER BURNT OFF AT POLE 38830619000032 . CC = 10. WILL NEED TO OPEN RECLOSER ON POLE 38830620A10342 TO MAKE REPAIRS (THIS WILL INTERRUPT AN ADDITIONAL 86 CUSTOMERS).HOTTAP ON FUSE BURNNED IN TWO, WAITING ON LINECREWHOTTAP ON FUSE BURNNED IN TWO, WAITING ON LINECREW;; OPENED RECLOSER ON POLE 620-342 AT 1202 CLOSED RECLOSER AT 1227 APR CLOSE TICKET. RECLOSER OUTAGE ON ORDER 4046021. IDC XXXX
5696 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-09-17 09:48 | 2014-09-17 14:34 | 10 | 286 | 4505441 | 2860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4 SOLID PRIMARY DOWN FROM POLE 350-9 TO 350-50,ISO TAG TO DDC & PLACE GROUND @ 350-5 NEED LINE CREW NO TRUCK RELEASED BY CREW 078S05----3 SPAN #4CU P&N DOWN---REPAIRED---PWR RESTORED @ 14:34---TBL TKT COMP// LOOKS LIKE IT PULLED FROM SLEEVE L3/IDC XXXX AJB
5697 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-01-16 08:08 | 2009-01-16 17:40 | 5 | 572 | 55639-1 | 2860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD TRANSFORMER CREW ENROUTE RELEASED BY CREW 074S02 COD-5 L3/HFP
5698 | Hazard | 3308502 | BONNYMAN | HAZARD | 2019-07-04 16:28 | 2019-07-04 18:51 | 20 | 143 | 4654451 | 2860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | power restored L3/HFP
5699 | Hazard | 3309302 | VICCO | JEFF | 2012-04-18 06:46 | 2012-04-18 10:26 | 13 | 220 | 4682301 | 2860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MDC// BAD CUTOUT ON POLE 37830323D00326 == TREES AROUND TRANSF == CALLED LINE CREW AND ROW CREW ALSO == REPLACED CUTOUT AND CUT AROUND TRANSF POLE ///VER/CRB IDCC CNT10 ADDED 3 CUSTOMERS FROM MISSMAPPED TRANSFORMER XXXX
5700 | Whitesburg | 3312901 | JENKINS | KONA | 2015-01-12 12:43 | 2015-01-12 14:25 | 28 | 102 | 4930361 | 2856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE LINE FUSE OUT OM PL 37830404B00068//PATROLING LINE LINE FUSE OUT OM PL 404-68 BAD CUT OUT ON POLE 37830404B00264 RELEASED BY CREW 075H03 VER/CRB // CHANGED TIME ON DUE TO RECORD 4930751 WHICH STATED "HAD TO OPEN CUTOUT AGAIN" (MADE THAT REC A DUP) L3/HFP HFPC TON1425 AJB
5701 | Whitesburg | 3312902 | JENKINS | JENKINS | 2019-09-03 04:04 | 2019-09-03 12:00 | 6 | 476 | 4973941 | 2856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva xfmr 7200 Released by crew 077S11 power restored at 12:00 L3/HFP
5702 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-04-25 14:49 | 2014-04-25 15:45 | 51 | 56 | 4634411 | 2856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON P-852-49 ON INACTIVE XFMR.ONLY A PHASE REC OUT.ISOLATED XFMR..//COD ??? CALLS CAME IN ON B AND C PHASES... NO OBVIOUS DIPS PLOTTING LOAD FROM THE STATION //SUSPECT PHASING INCORRECT ON MAPS//AED ENTRY CREATED FOR ARRESTOR// VER/DBM L3/HFP IDC CHANGED COUNT FROM 45 LOOKS MORE LIKE PH C XXXX
5703 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-12-21 15:58 | 2011-12-21 17:00 | 46 | 62 | 4193671 | 2852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 91-85 HOT TAP BURNT OFF REPAIRED ///VER/CRB IDC XXXX
5704 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2012-04-24 12:26 | 2012-04-24 14:30 | 23 | 124 | 4702741 | 2852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE. LINE FUSE CUTOUT BROKE AND LET FUSE DOOR DROP OPEN. REPLACING CUTOUT. REPLACED LINE CUTOUT AND RESTORED @ 14:30. SH COD-23 ISO LF 38831047000015 VER/HFP L3/HFP IDC XXXX
5705 | Hazard | 3420001 | SOFT SHELL | VEST | 2022-08-03 08:58 | 2022-08-05 08:30 | 1 | 2852 | 4667611 | 2852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | send to servicer customer having spikes in voltage neutral looks ok on service and transformer may need to check transformer..lc Released by crew 077E07. Hot leg broken/burnt on pole 109-21, power restored at 8:30.
5706 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-02-23 21:38 | 2008-02-23 23:10 | 31 | 92 | 66603-1 | 2852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410502// SERVICER OPENED LINE FUSE TO MAKE REPAIRS ON POLE 47-461. WE CLOSED LINE FUSE BACK IN AT 23:10.//VER/CRB IDC XXXX
5707 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-03-20 09:20 | 2009-03-20 10:06 | 62 | 46 | 60292-1 | 2852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403302//RELATED TO ORDER 60238-1//OPENED SWITCH ON POLE 38830954A40908 ( NOT ON MAP, MD FILED)//COD 62//ISO// VER/DBM IDC XXXX
5708 | Pikeville | 3410602 | E.PRESTON | LANCER | 2009-01-16 02:55 | 2009-01-16 10:50 | 6 | 475 | 55462-1 | 2850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3410602// WR# 28092118 // CSP XFMR OPENED UP DUE TO MELTED SECONDARY CONNECTIONS. REPAIR IN PROGRESS. CLOSED XFMR AT 05:45 AND IT STAYED IN FOR 45 MINUTES AND OPENED BACK UP. BAD 25KVA CSP. DIFFICULT LOCATION. RELEASED BY CREW 076S02// REPLACED TRANSFORMER WITH A 50 KVA. VER/KEP MD FILED L3/KEP
5709 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-06-19 16:51 | 2015-06-20 16:36 | 2 | 1425 | 4612121 | 2850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TAGGED & GROUNDED TO KYDDC @ POLE 38830525000048/ DISPATCH LOGGED/ LIFTED HT ON 525-48 AND PLACED G&T TO DDC OVER ROAD/ POLE 106 BURNT TO BAD TO REENERGIZE, NEED 6X6 POLETOP TO FIX POLE TRUCK OK, 526-106 OFF AT 1651LIFTED HT ON 525-48 AND PLACED G&T TO DDC OVER ROAD, POLE 106 BURNT TO BAD TO REENERGIZE, NEED 6X6 POLETOP TO FIX POLE TRUCKOK, 526-106 OFF AT 1651 RELEASED BY CREW 078S11//PLACED CREW TAG///CREW ON SITE VER/ARN
5710 | South Williamson | 3200301 | BELFRY | BELFRY | 2009-05-27 04:24 | 2009-05-27 04:34 | 285 | 10 | H53985-1 | 2850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NOTE TO SERVICER// CALL RUDY VASS FOR INFO ON THIS OUTAGE 606-794-0544 /// CUTOUT BROKEN INTO ON POLE 1014-888 SDRAY ONSITE WAITING FOR DEH CREW OPENED BELFRY/BELFRY CB AT 0424 CLOSED AT 0434 TO SAFELY MAKE REPAIRS VER/KEP L3/KEP IDCC TOF 5/26 XXXX
5711 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2011-10-23 18:14 | 2011-10-23 19:11 | 50 | 57 | 4013221 | 2850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2150103//..POLE 991-D1-303..HOT LINE CLAMP HAS BURNT OFF OF STIRRUP..THERE IS A SOLID BLADE CUTOUT ON THIS POLE.NOT ON FIELDVIEW...WILL ISOLATE CUTOUT & REPLACE HOT LINE CLAMP & RESTORE POWER..//..APCO PESONELL IN THE CLEAR..REPLACED HOT LINE CLAMP..CLOSED CUTOUT..POWER ON..JRV.10/23/11 103 CUSTOMERS VER/ARN IDCC PN266 CNT 103 XXXX
5712 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-01-24 07:55 | 2016-01-24 14:42 | 7 | 407 | 4646431 | 2849 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY ONLY DOWN POLE 1074B-191 . #6CC ,REPAIRS MADE , ALL WORK COMPLE / GXJ/ MD DONE/ LINE FUSE ON POLE 38831074A00354/ ISO 38831074A00354/ COD 7/ VER/BOW
5713 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-02-20 21:37 | 2015-02-21 13:26 | 3 | 949 | 4059601 | 2847 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW ONSITE, CHECKING CAN// BAD TRANSFORMER/ WILL OPEN RECLOSER LATER WHEN TRANSFORMER ARRIVES/ OPEN RECLOSER 37830273A00041 TO CHANGE TRANSFORMER 37830273A00043/ OPENED RECLOSEER 1138 1308// TRANSFORMER BACK IN 1326/ ISO 37830273A00043/ COD 3/ VER/BOW
5714 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-04-10 16:14 | 2020-04-10 21:30 | 9 | 316 | 4618721 | 2844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Need 45/2 pole, 50KVA Cutout & Arresters, 3 clevis, deaden assembly primary,
5715 | Hazard | 3309302 | VICCO | JEFF | 2022-11-27 11:59 | 2022-11-27 17:15 | 9 | 316 | 4184681 | 2844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP HAS COME LOOSE FROM TOP OF CUTOUT STILL CONNECTED AT HOT LINE CLAMP ON 323-D-514 MANUEL POLE Released by crew 077E02 Cutout replaced and power restored at 17:15.
5716 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-10-30 04:53 | 2008-10-30 07:15 | 20 | 142 | 60733-1 | 2840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP 3309001// WELL DISPATCH IN THE MORNING = 1 SPAN OF WIRE DOWN = WILL TRY TO PUT BACK UP == BAD WIRE == REPAIRED == REFUSED IDCC CNT19 MISSMAPPED CUSTOMER XXXX
5717 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-03-07 10:07 | 2008-03-07 11:18 | 40 | 71 | 54522-1 | 2840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116703//30T LINE FUSE OUT ON POLE 19-79--PATROLING LINE// DRT ASSISTING// BAD CUTOUT// SEND COPY OF TICKET TO S MARTIN// POLE 19-86 BURNT AT TOP AN NEEDS REPLACED//VER/CRB IDC XXXX
5718 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-05-07 22:45 | 2016-05-07 23:51 | 43 | 66 | 4186111 | 2838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED TO SAFELY MAKE REPAIRS ON 4185901 CLEARING DEVICE IS ACTUALLY A SOLID BLADE CUTOUT NOT LF MD FILED VER/KEP AJB
5719 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-08-10 19:07 | 2009-08-10 23:25 | 11 | 258 | 60372-1 | 2838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA CSP XFMR. WILL HAVE TO CHANGE IT AND INSTALL CUTOUT AND ARRESTER. DUTY SUPERVISOR NOTIFIED - . CREW ON-SITE. WAITING FOR LIGHTNING STORM TO PASS. WILL OPEN L.F AT POLE 785-42.BAD 50 KVA CSP XFMR. WILL HAVE TO CHANGE IT AND INSTALL CUTOUT AND ARRESTER. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. CREW ON-SITE. WAITING FOR LIGHTNING STORM TO PASS. OPENED LINE FUSE ON POLE 785-42 AT 22:50. VER/KEP L3/KEP IDC XXXX
5720 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-06-18 04:17 | 2020-06-18 12:10 | 6 | 473 | 4039211 | 2838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out// xfmr fuse out, bad xfmr, will need 25 kva, 19.9 kv, manuelDispatched in accordance with KYPCo Late Night Callout Guidelines xfmr fuse out, bad xfmr, will need 25 kva, 19.9 kv, manuel :Released by crew 077S02 power restored at 12:10
5721 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-04-03 16:12 | 2018-04-03 20:30 | 11 | 258 | 4169721 | 2838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100KVA TRANS ON POLE //CREW ENROUTE//xfmr fuse out, bad xfmr, calling for help. please send ticket to Tim Smith. 19.9 kv 100 kva xfmr, 120/240 Released by crew 077S02 changed out bad transformer power restored at 20:30//cod 11
5722 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-10-14 19:32 | 2014-10-14 20:15 | 66 | 43 | 4627261 | 2838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4626001//SERVICER OPENED RECLOSER IN ORDER TO SAFELY REPLACE BAD CUTOUT///COD 66// VER/DBM L3/HFP AJB
5723 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2020-10-10 09:03 | 2020-10-10 17:28 | 45 | 505 | 4541471 | 2837 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 201C/87 need 7200 cutout lighting arr. T/bracket need manual row crew tree in line at pole 87 will take outage to do work and cut tree manual ocr on pole 177D/2 but can set in road and load bust switch on pole 201C/82 send to P.Hicks can not get to pole very wet and septic tank Released by crew 077S03 // opened solid blade on pole 37830201C00082 @1635 closed in @1728
5724 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-09-01 00:46 | 2021-09-01 12:35 | 4 | 709 | 4189101 | 2836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout. power restored at 12:35. complted Josh Colley
5725 | Hazard | 3310502 | HADDIX | CANOE | 2008-04-04 05:41 | 2008-04-04 17:30 | 4 | 709 | 63686-1 | 2836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502- WILL DISPATCH SERV AT REG WORK TIME==. BAD CUTOUT LINE FUSE == WILL REPLACE == REPLACED CUTOUT VER/HFP IDC XXXX
5726 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-10-30 14:45 | 2013-10-30 15:00 | 189 | 15 | 4975171 | 2835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | DONNIE JENT OPENED RECL AT 199-96 AND SB SWS AT POLE 199-41..TIME OFF 1445-ON AT 1500 WIRE WAS BROKEN BETWEEN STIRRUP..INSTALLED 3 FT. OF 6A COPPER AND TENTION SLEEVE. VER/SEF L3/HFP IDC XXXX
5727 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-12-27 15:19 | 2011-12-27 15:54 | 81 | 35 | 4206281 | 2835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP ////VER/CRB IDC XXXX
5728 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-06-27 08:06 | 2008-06-27 14:00 | 8 | 354 | 55791-1 | 2832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401302/FAILED CUTOUT VER/KEP IDCC PN9, CNT14 XXXX
5729 | Hazard | 3303902 | LESLIE | WOOTON | 2016-05-11 05:11 | 2016-05-11 09:54 | 10 | 283 | 4196661 | 2830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT ON POLE37830438000144 BURNT UP
5730 | Hazard | 3302703 | HAZARD | HAZARD | 2014-05-22 09:57 | 2014-05-22 14:40 | 10 | 283 | 4738911 | 2830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | NEEDS CREW WITH BIG BUCKET, 8 FT ARM, BRACES, 3 7.2K CUTOUTS AND ARRESTORS, 6 ARM BRACKERS,... REPAIRS MADE, POWER RESTORED. VER/KEP
5731 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-22 15:42 | 2011-05-22 17:45 | 23 | 123 | 4122481 | 2829 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 117-249 BAD LA SEND NOTE TO TREE PEOPLE VINES NEED CUTOFF POLE 117-88 IDC XXXX
5732 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-08-17 23:58 | 2015-08-18 11:45 | 4 | 707 | 4145211 | 2828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK IN AM PER CALLOUT GUIDELINES/ SERVICER WAS @ THIS LOCATION ABOUT AN 1 1/2 HOURS BEFORE IT WENT OUT AGAIN/ SAID TRANSFORMER NEEDS TO BE CHANGED OR IT WONT STAY ON/ ISO 37830045000068/ COD 4.TRANSFORMER HAS BEEN REPLACED AND SERVICE RESTORED..D LEWIS 8-18-15// VER/ ADH
5733 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-09-14 19:38 | 2014-09-14 23:00 | 14 | 202 | 4499041 | 2828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON 343A-35 , FOUND BAD ARRESTER ON POLE 343A-285 , CLEARED ARRESTER . CLOSED LINE FUSE @ 23:00 ///CHANGE ISO POLE COD 14 VER/SEF
5734 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-07-15 19:26 | 2015-07-16 19:00 | 2 | 1414 | 4885121 | 2828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | MAD XFMR AS RICK MAGGARD. 4 MEN MANUAL.REPLACED BAD 25 KVA TRANSFOMER ; CAN CLOSE POWER RESETORED MWL
5735 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-01-30 15:08 | 2011-01-30 19:25 | 11 | 257 | 52303-1 | 2827 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | OPENED RISER FEEDING 809-1065 & 809-1066 @ 16:05 TO ISOLATE BAD UG XFMR COD 19.//FUSE PUT BACK AT 1725 WITH TRAN ISOLATED//OPENED RISER FEEDING 809-1065 & 809-1066 @ 16:05 TO ISOLATE BAD UG XFMR. RESTORED ALL EXCEPT BAD XFMR 809-1065 @ 17:25.OPENED RISER FEEDING 809-1065 & 809-1066 @ 16:05 TO ISOLATE BAD UG XFMR. RESTORED ALL EXCEPT BAD XFMR 809-1065 @ 17:25. CHANGED XFMR AND RESTORED REMAINING CUSTOMERS @ 19:25. SH//VER/CRB IDCC CNT19 XXXX
5736 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-12-23 05:49 | 2017-12-23 17:46 | 4 | 717 | 4665561 | 2826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830270C00353 is burned off need 40 foot pole and de unit guy wire cutout and arrestor and 10 kva 19.9 kv Released by crew 077S05//CLOSED L/F IN @ 1732 UPTO TRANS 37830270C00353 CLOSED 1746
5737 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-06-16 05:05 | 2008-06-16 05:30 | 113 | 25 | 65348-1 | 2825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ASSOCIATED WITH ORDER 65345-1 CREW OPENED LINE FUSE TO REPLACE CUTOUTS ON POLE 45-A-1216 IDCC CNT130 XXXX
5738 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-11-27 15:30 | 2019-11-27 18:27 | 19 | 177 | 4090271 | 2823 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 139-124 neural on cross arm construction a phase a neutral slap together/ 139-6066//opened@17:45 closed 18:27 resg conductor //Ph A only was out//opened other 2 @ 1745, closed 1827 //cod 15 (+4)
5739 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-08-16 13:23 | 2015-08-16 20:06 | 7 | 403 | 4140191 | 2821 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F IS OUT,WILL PTRL////////CUTOUT BURNED UP,NEED 1 A LINEMAN TO HELP,HAD TO CUT PATH TO POLE ABT 150FT BACK ON HILL/////REPLACED CUTOUT AND RESTORED VER/CRB L3/HFP XXXHFP AJB
5740 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-08-07 11:13 | 2014-08-07 14:50 | 13 | 217 | 4339771 | 2821 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KV DOUBLE BUSHING TRANSFORMER// TRUCK ACCESSIBLE// CREW REQUIREDNEED 50 KVA TRANS BUSHING BAD TRUCK TO POLE RELEASED BY CREW 078S08,,CREW ON SITE,,XFMR CHANGED, ALL POWER RESTORED// ISO 38830069A41570// COD 13 AJBC CDC96 REMOVED DUP STP.
5741 | Hazard | 3302703 | HAZARD | HAZARD | 2009-06-19 08:46 | 2009-06-19 12:23 | 13 | 217 | 52704-1 | 2821 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | RISER LOOSE FROM PRIMARY BUSHING ON ONE XFMR//WILL HAVE TO OPEN XFMR BANK FOR RPAIRS CUSTOMERS NOTIFIED//OPENED XFMR BANK 12:15 AND RESTORED COMPLETE AT 12:23 6-19-09 077S04//COD 13// VER/DBM IDCC TOF1215 XXXX
5742 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-03-12 14:50 | 2013-03-12 19:32 | 10 | 282 | 4901911 | 2820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF POLE 1007-121..NEED 3 MEN, MATERIAL HANDLER BUCKET AND POLE TOP EXTENSION..D LEWIS 16:34..CREW ON SITE 18:30 RELEASED BY CREW 074H08 REPAIRS MADE ON AT 19:32 D SAMMONS VER/KEP IDC XXXX
5743 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-04-17 02:58 | 2022-04-17 10:48 | 6 | 470 | 4770631 | 2820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | . No truck, crew reqd/wire came out of hot tap. tre. Released by crew 078S04///Repairs made///Complete BR
5744 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-03-27 18:17 | 2008-03-27 21:25 | 15 | 188 | 61345-1 | 2820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401002//HAD TO REPLACE FUSE HOLDER....DAH//FUSE 214-12//COD 9//ISO 37830214D00012//SENT REPORT TO MAPPING FOR MISSING FUSE// VER/DBM IDC XXXX
5745 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-03-20 17:25 | 2008-03-20 18:25 | 47 | 60 | 59508-1 | 2820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3413401// ONLY 1 PHASE B PHASE OUT AT 1630 //RELATED TO ORDER 59502-1 MOVED THIS UP TO LINE FUSE THAT SERVICER REPORTED OUT//WILL NEED TO OPEN OTHER PHASE TO MAKE REPAIRS// @ 1725 SERVICER OPENED C PHASE FUSE ON 37830016C00064//AT 1825 ALL CUST RESTORED/ THIS IS THE OUTAGE FOR C PHASE ONLY//NEED TO KEEP THIS ONE PLEASE ....THANKS HFP VER/HFP IDC XXXX
5746 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-01-11 18:22 | 2014-01-13 13:15 | 8 | 2573 | 4273441 | 2818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE FELL @ 328-42 CUT LOOP @POLE 328-137 LINE FUSE IN @ 1857,NEED LINE CREW TO REPLACE 40-5 POLE NO TRUCK TO POLE /SECURED POLE AND MADE SAFE///NEED TO FORWARD TO TECH. AND HAVE JOB WROTE///NEED TRACK EQUIPMENT(D.DERRICK AND BUCKET TO CHANGE POLE)///POLE TEMP SECURED//ONE CUST OUT(HUNT CABIN) INSTALLED 1 SET OF GROUNDS AND ISOLATED ON POLE 328-137 COD-8 ISO LF 38830328000146 VER/HFP L3/HFP IDC XXXX
5747 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-05-13 18:50 | 2014-05-13 20:58 | 22 | 128 | 4693961 | 2816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ISOLATED UNUSED TR ON POLE 37830222D00288 FUSE OUT ON POLE 37830222D00009 COD-22 ENTERED MD VER/HFP L3/HFP IDC XXXX
5748 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-01-31 18:32 | 2021-01-31 22:48 | 11 | 256 | 4924561 | 2816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F open @240-163, checking. Bad cutout on the hill @37830240000172, will also have to resag some primary 1 span back, will be making repairs. Got primary resagged and c/o replaced, closed L/F back in @2248.
5749 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-09-06 08:34 | 2009-09-06 09:50 | 37 | 76 | 50801-1 | 2812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3310501// LOOP DOWN ON THE POLE VER/TOM L3/TOM IDC XXXX
5750 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2012-04-28 16:14 | 2012-04-28 19:50 | 13 | 216 | 4720331 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD NEED 1 MAN BIG BUCKET 1655 OPENED C PHASE FUSE (10 CUSTOMERS) OPEN 2ND LINE FUSE@1900 (3 CUSTOMERS) CLOSED BOTH@1950 COD-13 ISO LF 37830449C21017 VER/HFP L3/HFP
5751 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-04-11 14:46 | 2008-04-11 15:58 | 39 | 72 | 66142-1 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED ARRESTOR AND REFUSED LINE//3308602//FUSE NOT ON MAP////VER/CRB MLR OK
5752 | Hazard | 3308001 | JACKSON | S.JACKSON | 2012-05-16 14:14 | 2012-05-16 17:50 | 13 | 216 | 4801301 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | GOT POLE 1084-44 ON THE GROUND, GOT PHILLIP HICKS COMMING TO CUT DEAD END ON POLE1084-43 . POLE THAT IS DOWN DOESNT SERV ANYTHING//COD 13// VER/DBM IDC XXXX
5753 | Hazard | 3302704 | HAZARD | KENMONT | 2009-06-02 09:38 | 2009-06-02 11:35 | 24 | 117 | 58834-1 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE LET GO == REPAIRED == REFUSED =POWER OK//VER/CRB IDC XXXX
5754 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2022-07-23 17:16 | 2022-07-23 23:07 | 8 | 351 | 4560091 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Line fuse open @24-B4-823, checking. Found a bad 25 kva CSP @24-B4-825, will be changing.. Closed L/F besides the CSP @2030, will have to reopen the L/F to change the trans., will keep track of times. Opened L/F @24-B4-823 @2142, made epairs and closed back in @2307. Released by crew 074S05
5755 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-05-10 20:39 | 2009-05-11 02:30 | 8 | 351 | 57942-1 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP HAVE A BAD 25 KVA, DOUBLE BUSHING NEED CREW CAN USE BUCKET, THIS HAS 8 SERVICE ON IT MAY WANT TO BRING A 50 KVA RELEASED BY CREW 078S06 ISO POLE 39831073B43569 COD-8 L3/HFP IDC XXXX
5756 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-08-21 06:38 | 2009-08-21 11:50 | 9 | 312 | 57895-1 | 2808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ON POLE 38831126B10112 . WILL GET HELP FROM PIKEVILLE TO REPAIR THIS. ALSO CUT TREE OUT OF PRIMARY 20T FUSE POLE#112 FEEDS BOTH TAPS COD-9 "A" PHASE VER/KEP L3/KEP IDCC PN130 XXXX
5757 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-12-04 10:26 | 2019-12-04 14:45 | 27 | 259 | 4122571 | 2807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Step down open due to failed cutout on pole 237-B-85,Made repairs, Also found customers service melted,Made repairs on it ,Restored service at Step Down at 14:45 on pole 237-B-169.
5758 | Hazard | 3309002 | JEFF | JEFF | 2010-12-15 09:49 | 2010-12-15 16:30 | 7 | 401 | 50551-1 | 2807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === NEED BIG BUCKET TO CHANGE CUTOUT == CALLED GLEN COMBS HE SAID HE WOULD GET LINE == NEED A 7200 CUTOUT , T BRACKET , AREESTER COD-7 ISO TF 37830345C00115 VER/HFP L3/HFP IDC XXXX
5759 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-06-11 06:27 | 2021-06-11 18:08 | 4 | 701 | 4712591 | 2804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines. removed tree from line and fuse didnt hold. got a broke pole top pen on pole 354/12 and 0n pole 13 it looks like the tie wire has broke. not by truck and thres no easy way to walk to it Released by crew 078H03Dispatched in accordance with KYPCo Late Night Callout Guidelines crew on site
5760 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-01-12 05:18 | 2017-01-12 07:33 | 21 | 135 | 4289371 | 2803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STURIP BURNT ON P 901-5512 OPENED XFMR ON P 901-5620 TO TAKE SOME LOAD OFF HOT TAP. 39830901C45512 39830901C45620STURIP BURNT ON P 901-5512 OPENED XFMR ON P 901-5620 TO TAKE SOME LOAD OFF HOT TAP. HOT REPAIRED LINE IN @ 07:29 AND XFMR ONLINE @P 901-5620 @ 07:33 PLEASE CLOSE TICKET LRM VER/AWD NEED TIME ON XFMR THAT WAS OPENED & NEEDS DUPLICATED HFP AJB
5761 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2011-03-17 14:05 | 2011-03-17 15:15 | 46 | 70 | 55197-1 | 2800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE ONLY BAD CUTOUT VER/KEP IDC XXXX
5762 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-04-05 23:08 | 2009-04-06 10:48 | 4 | 700 | 65582-1 | 2800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ON 3 PHASE ARMLESS CON. NO TRUCK TO POLE. NEEDS LINE CREW. NEED CUTOUT AND ARRESTER. RELEASED BY CREW 078S01 CHANGED CUTOUT ONLY NEED TO REWORK POLE SPACING AT A LATER DATE WITH SMALL SERVICE BUCKET WHEN DRY ; ALL POWER RESTORED AT 10: 48//VER/CRB IDC XXXX
5763 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-01-11 10:20 | 2009-01-11 13:40 | 14 | 200 | 54215-1 | 2800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411902//OPENED FUSE ON POLE 37830120A00084 @ 1020 DUE TO POLE FIRE//COD 14//ISO// CUTOUT BROKE DOWN AND BURNED TOP OF POLE { 120-373 } OFF. I OPENED LINE FUSE ON POLE 120-84 AT 10:20 TO ISOLATE TROUBLE. DALE IS COMING OUT TO HELP RESTORE POWER.3411902// . WE SPLICED POLE AND CLOSED LINE FUSE IN AT 13:40// VER/DBM L3/KEP IDC XXXX
5764 | Hazard | 3303901 | LESLIE | HYDEN | 2009-03-04 11:41 | 2009-03-05 10:59 | 2 | 1398 | 54947-1 | 2796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEUTRAL WIRE BROKE IN SECONDARY...5 KVA XFMR BAD WILL NEED 4 MAN LINE CREW //COD 2//ONLY SEASONAL USE ON THESE ACCOUNTS (CAMPGROUND)//CREW REQUIRED TO REPLACE TRANSFORMER//THIS WILL NOT BE TAKEN CARE OF UNTIL MONDAY PER GLENN COMBS, THIS WAS NOT CALLED IN BY CUSTOMER, WAS CALLED BY AEP METER READER... GROUNDS DO NOT OPEN UNTIL MAY///CLOSING TRBL ORDER, GLENN TO WRITE JOB TO GO BACK ON THIS NEXT MONDAY 3-9-09// VER/DBM IDC XXXX
5765 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-05-26 12:02 | 2017-05-26 15:55 | 12 | 233 | 4866661 | 2796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | C PHASE OPEN ON RECLOSER 37830172A00299// COD 12//600 AMP SWITCH BURNED UP600 AMP SWITCH BURNED UP 37830172A00307 GOT RECLOSER IN AT 1555//MADE AED & DOL ENTRY VER/CRB
5766 | Hazard | 3309301 | VICCO | REDFOX | 2011-08-22 00:13 | 2011-08-22 15:45 | 3 | 932 | 4740031 | 2796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK IN THE MORNING, XFMR FUSE OUT, LINE FUSE MUST ALSO BE OUT AT BOTTOM OF HILL. CALLED FOR A 4-WHEEL DRIVE PICK-UP, LINE FUSE OUT ON 324-151, FOUND BAD XFMR, NEED 25 KVA, 19.9 KV, BUCKET ACCESSIBLE RELEASED BY CREW 077S02 //VER/CRB IDC XXXX
5767 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-02-19 19:11 | 2015-02-20 04:30 | 5 | 559 | 4044341 | 2795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 TRANSFORMER37830273A00012, MANUAL, NEED AT LEAST 4 MEN AND 200 FT OF ROPE.//ARCOSED DHE CREW PER BRUCE LINDON//BAD 25 KVA 7200 TRANSFORMER, MANUAL, NEED AT LEAST 4 MEN AND 200 FT OF ROPE. REPLACED BAD 25 KVA WITH 50 KVA PER MIKE LEWIS, POWER RESTORED. VER/CRB L3/HFP XXX
5768 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-11-14 15:07 | 2021-11-14 19:21 | 11 | 254 | 4091031 | 2794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary is broke due to faulty Sleeve at pole 120-B-107,Going to Ground and Tag to Myself and make repairs..Restored service at 19:21.
5769 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-07-05 23:38 | 2022-07-06 15:09 | 3 | 931 | 4392921 | 2793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPEN XFMR FUSE AT 46-49. NEED SERVICER TO PUT FUSE IN.DC Released by crew 074E06. Bad 25kva 7200 trans. here, will be changing out. Got trans. replaced and power restored @1509.
5770 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-12-30 04:19 | 2014-12-30 10:08 | 8 | 349 | 4891101 | 2792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT, NEED CUTOUT AND ARRESTOR AND NEED BLACK BOARDS TO BACK BUCKET TO POLE ALSO NEED TO SEND TO DOUG CHRISTIAN FOR A REBUILD RELEASED BY CREW 077S05// COD 8//ON @ 10:08// VER/ ADH AJB
5771 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2009-09-26 10:48 | 2009-09-26 16:37 | 8 | 349 | 63700-1 | 2792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BRINGING TRACK BUCKET SEND TO LINKOUS/BRING FIBER EXTENSION RELEASED BY CREW 078S03/CREW ON SITE/FETR 1930/VEM WR#31911780/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1637/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP L3/KEP IDC XXXX
5772 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-11-27 12:40 | 2022-11-27 20:25 | 6 | 465 | 4185891 | 2790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Fuse 620-34 still in. Primary 6a broke in the clear at fuse pole. Flaggers and linecrew required. Released by crew 078S11 Repairs made, Closed on pole 620-34 at 20:25
5773 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2014-04-26 09:40 | 2014-04-26 17:25 | 6 | 465 | 4636701 | 2790 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED SWITCHES SO T LINE COULD SAFELY REPLACE STRUCTURE WITH OVERBUILD AND D LINE COULD TRANSFER TO NEW STRUCTURE RELEASED BY CREW 078H16 VER/KEP AJB
5774 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-03-02 16:06 | 2015-03-02 21:55 | 15 | 349 | 4092901 | 2785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT ON POLE 178A-504 . BAD XFMR ON POLE 178A-506 . CLOSED LINE FUSE BACK @ 19:00 , ALL POWER BACK ON EXCEPT XFMR ON POLE 178-506/ 506 BACK ON @ 21:55/ ISO 37830178A00504/ COD 15/ 1ST STEP RESTORED 14/ VER/BOW L3/HFP XXX
5775 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-02-14 18:50 | 2018-02-15 15:45 | 10 | 1255 | 4841291 | 2785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer: no answer have bad ptp and ins, opened l/f at 1850, will be crew req, pole side yard of home, grojund to wet to use truck,open l/f on pole 1071-3. 5 cust off, no grd or tagged placed. Released by crew 078S06---crew on site--G&T to RMV Released by crew 078H16//bad 25kVA no Truck// power restored at 15:45 new 25 kva transformer installed
5776 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-08-17 20:19 | 2014-08-17 23:53 | 13 | 214 | 4376531 | 2782 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08/CREW ON SITE/FETR0030/VEM/LOOP BURNT OPEN @91-C-55/NO TRUCKS/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2353/PLEASE CLOSE TICKET/THANKS/VEM DUPLICATE OUTAGE ON OTHER 2 CUSTOMER FROM 2200 TILL 2353 VER/SEF IDC AJB
5777 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-04-26 14:46 | 2010-04-26 21:03 | 8 | 377 | 51481-1 | 2781 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED 40/4 POLE BURNT OFF TRUCKS OK/223-195 IS FAULT POLE ISOLATED AND GROUNDED ON 222-70 CALLED FOR TREE ALSO TO CUT TREES OUT OF RIGHTOF WAY RELEASED BY CREW 078S03/ AT 1630 TREE CREW CUTTING OUT R/W/ TREE CREW COMPLETE AT 1755/ RESTORED LINE FUSE @ 20:16 STILL HAVE XFR OUT ON POLE195//VER/CRB IDCC CNT11, TON2058 XXXX
5778 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-05-26 20:41 | 2020-05-27 01:50 | 9 | 309 | 4911331 | 2781 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew req bad 50 kva double bushing 120/240 can use truck in alley between clark and main st // cod 9
5779 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2008-06-16 18:46 | 2008-06-16 21:05 | 20 | 139 | 65991-1 | 2780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3417602//XFORMER FUSE BLOWN, REFUSING IT, BAD 50 KVA XFORMER, CALLED R MARCUM FOR HELP//COD 20// VER/DBM
5780 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-02-25 01:53 | 2018-02-25 08:30 | 7 | 397 | 4880341 | 2779 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Released by crew 078H04 Released by crew 078H04/crew enroute/unsure of cause/changingcutout and LA in difficult location/FETR0930/vem/fuse stayed in at 0805/bad dead end bell 1123-B-639/opened fuse/FETR 0930/vem/repairs made andpower restored to all cust 0830/please close ticket/thanks/vem
5781 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-11-12 12:38 | 2021-11-12 13:15 | 75 | 37 | 4085351 | 2775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required bad hot tap
5782 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-01-02 12:14 | 2022-01-02 14:05 | 25 | 111 | 4260941 | 2775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Fuse is open on 429-27 patrolling line//////// Found and replaced bad deadend belll at 429-359 apr at 1405 close ticket
5783 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-05-10 13:31 | 2014-05-10 14:44 | 38 | 73 | 4682341 | 2774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT ON LOW SIDE OF STEP-DOWN IS OPEN ON POLE 423C-201. BROKE CUT-OUT ON POLE 423C-134. REPLACED CUT-OUT AND RESTORED POWER AT 14:44. 5/10/2014. VER/CRB L3/HFP IDC XXXX
5784 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-12-29 03:47 | 2021-12-29 09:40 | 8 | 353 | 4234081 | 2774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Held per KPCO late night callout guidelines.had C-Phase LF out on pole 1137A-580.also had transformer fuse out on pole 1137A-581.lightning arrester blew on pole 581 taking out transformer fuse and C-phase line fuse on pole 580.i made my repairs and got the transformer fuse on pole 1137A-581 back in at 09:30 and i got the C-Phase line fuse on pole 1137A-580 back in at 09:40
5785 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2015-09-04 09:26 | 2015-09-04 10:39 | 38 | 73 | 4196971 | 2774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 357-57, I ISOLATED IT.//MADE AED//ALSO MADE MDC TO SHOW L/F AS A 50T VER/CRB L3/HFP XXXHFP AJB
5786 | Hazard | 3309302 | VICCO | JEFF | 2012-08-27 16:20 | 2012-08-27 17:07 | 59 | 47 | H4976741 | 2773 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE IS OUT ON STEPDOWN 37830347A00300 === RECLOSER STILL IN ON NEXT POLE OUT === 333 KV STEPDOWN TRANSF BAD === NEED LINE CREW === A- PHASE INITALLY OUT 56 CUSTOMERSF USE IS OUT ON STEPDOWN 37830347A00300 OPENED OTHER PHASE @ 1620 = 59 CUSTOMERS /// COD-115 ISO LF 37830347A00300 DUP OF 4976741 VER/HFP L3/HFP IDC XXXX
5787 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2015-04-20 17:59 | 2015-04-20 18:06 | 396 | 7 | 4343831 | 2772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | HAD TO OPEN BREAKER TO GET SWITCH CLOSED VER/SEF L3/HFPXXX AJB
5788 | Whitesburg | 3312902 | JENKINS | JENKINS | 2009-12-14 16:14 | 2009-12-14 17:53 | 28 | 99 | 58491-1 | 2772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SOURCE SIDE TAP CAME OUT OF RECLOSER OPENED RECLOSER AND REPLACED TAP//COD 28// VER/DBM
5789 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-01-23 08:59 | 2012-01-23 11:05 | 22 | 126 | 4284021 | 2772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED TRANSFORMER CUTOUT POLE 170-76.//COD 22 IDC XXXX
5790 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-05-15 19:51 | 2008-05-15 20:57 | 42 | 66 | 64394-1 | 2772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001002// SPECTRUM NOT WORKING - DDC/SERVICER WORKED OVER RADIO - FOUND BASKET BURNT OFF - WILL CLEAR UP AND PUT BYPASS IN...CREATED ABNORMAL// CUSTOMER COUNT 42 VER/ARN IDC XXXX
5791 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-05-17 08:04 | 2019-05-17 14:40 | 7 | 396 | 4279951 | 2772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 19.9KV TRANSFORMERxfmr fuse out;;;refused came back out, crew req. bad 25kva 19.9 120/240, big bucket should reach pole Released by crew 074H07 L3/HFP
5792 | Hazard | 3308502 | BONNYMAN | HAZARD | 2016-03-31 17:29 | 2016-04-01 08:52 | 3 | 923 | 4011831 | 2769 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 PHASE ON SECONDARY IS BURNT OFF ON POLE 223-47 TRUCK ACC. CAN BE FIXED BY SERVICER RELEASED BY CREW 077E07 , REPAIRED SEC. CLOSED @ 08:52 ONLY 3 CUST. WITH PART POWER, POWER RESTORED. VER/CRB
5793 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2010-11-08 11:23 | 2010-11-08 13:53 | 41 | 150 | 53903-1 | 2768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE--BAD CUTOUT ON POLE 38830020A31072--LIFTED HOT TAP AN TAGED ON POLE 38830020A31028--LINE FUSE IN AT 12:24 3 CUSTOMERS STILL OUT//COD 41 //--CALLED K BROWN TO ASSIST// MD FILED// VER/DBM L3/ JKW IDC XXXX
5794 | Pikeville | 3421001 | BREAKS | CITY | 2010-01-02 18:07 | 2010-01-04 16:15 | 1 | 2768 | 57704-1 | 2768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S02// CUSTOMER REPORTS OKAY TO CHECK DURING DAYLIGHT 1-3-10 // CUSTOMER NOT LIVING AT LOCATION AND SAID OKAY TO CHECK LATER TIME // PER DUTY SUPERVISOR WILL WORK WHEN CREW IN AREA OF FIRST THING 01/04/10 VER/KEP L3/KEP IDC XXXX
5795 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-02-01 15:36 | 2018-02-01 17:39 | 37 | 123 | 4790111 | 2766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout 37830004D00063/ ISO 37830004D00035/ COD 37
5796 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2022-06-04 10:09 | 2022-06-04 16:44 | 7 | 395 | 4017381 | 2765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 12 t line fuse blown on 785-887..Tommy Goble to ck after switching. Released by crew 076S01.primary under ground cable bad , making repairs now
5797 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2010-04-06 11:03 | 2010-04-06 16:10 | 9 | 307 | 59499-1 | 2763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34543352 /// NEED CREW RELEASED BY CREW 078S07/ J. HEMLEPP & CREW IN ROUTE. BAD 50 KVA XFMER NO TRUCK. NEED YARD MACHINE//VER/CRB IDC XXXX
5798 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-02-01 23:15 | 2018-02-02 14:35 | 3 | 920 | 4791701 | 2760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF 37830579D00131, WILL WAIT TILL MORING/// CAN USE YARD DOG Released by crew 077S01//CLOSED L/F IN @ 1435//COD 3
5799 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-06-02 11:03 | 2011-06-02 13:21 | 20 | 138 | 4223751 | 2760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | STS WR # 40215562 // CREW OPENED LINE FUSE TO ALLOW THEM TO SAFELY REPLACE POLE STS WR # 4021/CREW CHANGING ROTTEN POLE IN BACK YARD/FETR1330/VEMSTS WR # 4021/CREW CHANGING ROTTEN POLE IN BACK YARD/FETR1330/VEM/WORK ORDER ON JOB/POLE CHANGED AND POWER RESTORED TO ALL CUST 1321/PLEASE CLOSE TICKET/THANKS/VEM // COD-20 ISO LF 38830044A00336 VER/HFP L3/HFP IDC DCMT XXXX
5800 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-07-18 13:16 | 2011-07-18 15:11 | 24 | 115 | 4558511 | 2760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF AT BASKET ---ONLY C PHASE OPENED UP--CUSTOMER COUNT WRONG--E MAIL TO RAYBURN TO HAVE BASKET REPLACED--SPACER CABLE--TRUCK OK//COD 24//EMAILED TO LINE CREWS// VER/DBM
5801 | Whitesburg | 3312902 | JENKINS | JENKINS | 2012-03-16 09:45 | 2012-03-16 10:45 | 46 | 60 | 4587171 | 2760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | EMERGENCY OUTAGE TO REPLACE INSULATORS THAT HAVE FAILED OPENED AT 09:45CLOSED AT 10:45 /// COD-46 ISO OCR 37830381D20186 VER/HFP L3/HFP IDC XXXX
5802 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-12-07 12:00 | 2015-12-07 13:29 | 31 | 89 | 4515821 | 2759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO 4514991 - SERVICER OPENED SWITCH TO ALLOW HIM TO SAFELY REPAIR LOOP THAT IS BURNT OPEN /// COD-31 ISO PO @ 37830287000170 OFF @ 1200 ON @ 1329 VER/HFP L3/HFP AJB
5803 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-09-11 13:08 | 2015-09-11 14:00 | 53 | 52 | 4228861 | 2756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 68-58 BAD CUTOUT CHGED B/PHASE 50T// VER/ ADH L3/HFP XXXHFP AJB
5804 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2009-04-18 06:04 | 2009-04-18 07:50 | 26 | 106 | 57760-1 | 2756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3451202 - WE ACTUALLY HAVE A STEPDOWN XFMR FUSE BLOWN ON POLE 381-791 WHICH IS NOT SHOWING ON OUR MAPS, I AM PATROLLING LINE. I HAVE FOUND A BAD LTNG ARRESTOR ON POLE 381-332 // CREATED MAP DISC STEPDOWN POLE BETWEEN 327 AND 295 VER/TOM L3/TOM AJB COULD NOT VERIFY CUST COUNT. STEP XFR STILL NOT ON MAP.
5805 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2022-06-26 19:13 | 2022-06-26 21:38 | 19 | 145 | 4326561 | 2755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser is open on 309-12 patrolling line////// Found bad cutout on 309-78, apr at 2138 close ticket. dwest
5806 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-06-16 20:04 | 2014-06-17 01:10 | 9 | 306 | 4099021 | 2754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-4557 BAD 15KVA NEED 25KVA 5 CUST OUT TRUCK TO POLE TRANS. VERY HOT RELEASED BY CREW 078S08,,CREW ON SITE,, UPGRADED OVERLOADED XFMR, ALL POWER RESTORED
5807 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-06-29 18:47 | 2010-06-29 21:20 | 18 | 153 | 60691-1 | 2754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO ORDER 60593-1//WHILE PULLING A LEANING POLE BACK, THE PRIMARY FAILED A FEW SPANS BACK UP THE ROAD//WILL COMPLETE REPAIRS ON DAMAGED POLE FIRST THEN PUT THIS PRIMARY BACK UP//COD 16//ON SITE REPAIRED CONDUCTOR 4 CU POWER RESTORED AT 21:20 P TOLLIVER// VER/DBM
5808 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-04-19 17:56 | 2013-04-20 01:35 | 6 | 459 | 4029931 | 2754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | REPLACED 4/0 / 3 UG SERVICE SERVING 6 CUSTOMERS , ALL WORK COMPLETE / GXJ 6 CC VER/KEP IDC XXXX
5809 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-03-26 03:44 | 2010-03-26 12:19 | 6 | 515 | 54543-1 | 2754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34409253 // POLE TOP BURNT OFF 40/5 , BACK YARD. NEED LINE CREW, TRUCKS ?. LINE FUSE OPENED ON POLE 162-D-229. RELEASED BY CREW 078S01/ LLOYD RAYBURN WILL SEND CREW AT NORMAL WORK TIME/HAD TO UNLOAD TRACK BUCKET/ GOING TO REMOVE LOOP ON POLE 162-356 WILL MAKE LINE HOT UP TO THIS POLE WILL HAVE 3 CUSTOMERS OUT/ FUSE BACK IN @ 10:27REMAINING 2 CUSTOMERS STILL OUT// ALL CUSTOMERS BACK ON AT 12:19 VER/HFP L3/HFP IDCC CNT9 XXXX
5810 | Hazard | 3303902 | LESLIE | WOOTON | 2012-09-08 07:11 | 2012-09-08 12:17 | 9 | 306 | 4029051 | 2754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830463000024 WE HAVE A BAD C/O. WILL REMOVE FROM LINE, LINE IS DE-ENERGIZED FROM THIS POLE ON UP. LINE CUTOUT ON THIS POLE IS WHATS BAD. REMOVED BAD C/O, REFUSED LINE, POWER RESTORED. //VER/GAH IDC XXXX
5811 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-07-26 00:30 | 2011-07-26 11:59 | 4 | 689 | 4622631 | 2752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HOLD THIS TICKET FOR LINE CREW, THIS WILL DONE ON DAY SHILF.NEED A 25 KVA 7200 TRANSFORMER, ONE CUTOUT, 150 W HPS D-D LIGHT, RELEASED BY CREW 074S05 HAVE ALL CUST. ON ACCEPT ONE RESETTING POLE CHANGING TRANSFORMER.CLOSED FUSE IN AT 9:31 TO GET ONE CUST. ON . HAVE OIL SPILL CONTACTED DAN DOOLEY AND EN-VIRO PRO IDCC CDC92 XXXX
5812 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-02-20 10:13 | 2010-02-20 13:05 | 16 | 172 | 59329-1 | 2752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKEN//COD 5//PHASE C CUTOUT BROKE//HAD TO OPEN OTHER PHASE (PHASE A) @ 12:50// RESTORED ALL CUSTOMERS @ 13:05 ... ALL WORK COMPLETE / GXJ IDCC CNT21 ONLY ONE PHASE OUT INITIALLY LOOKS LIKE PH A NOT C XXXX
5813 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-10-20 20:11 | 2017-10-20 20:19 | 344 | 8 | 4473811 | 2752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | B-PHASE REGULATOR BAD ON POLE 446-298 CAUSING HIGH VOTAGE. BYPASSED B-PHASE REGUATOR AND TAGGED FOR DDC.//SEE DOL CASE 779839//COD 344//EMAILED TO P WYSONG// VER/DBM /// TIMES PER DOL = L3/HFP XXXHFP ACB
5814 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-07-17 15:44 | 2013-07-17 19:27 | 15 | 223 | 4538391 | 2751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA /CUTOUT /LIGHTNINGARRESTOR/CREW ON SITE/FETR 1930/VEM/XFMR HAD 15 CUST/INSTALLED TWO NEW CANS TO SPLIT LOAD/POLE #94-1116 POWER RESTORED TO 9 CUST AT 1821/INSTALLED 50KVA 0N 94-1114 POWER RESTORED TO 6 CUST AT 1927/I WILL CONTACT GRAPHICS WITH CHANGES/VEM//COD 8 IDCC STP MISSING, CNT8 XXXX
5815 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-07-26 11:10 | 2013-07-26 13:15 | 22 | 125 | 4595021 | 2750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 208/93 GUY BRK FLIPING OVER PRI.. FETR 13:30\LRM PWR REST @ 13:15 LRM RELEASED BY CREW 078H06//COD 22// VER/DBM IDC XXXX
5816 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-03-25 17:20 | 2009-03-25 18:15 | 50 | 55 | 61489-1 | 2750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411901//COUTOUT BROKE DOWN ON POLE 74-242....NEED TO REPLACE POLE TOMORROW...SEND TICKET TO TIM HALL IN THE MORNING..POLE IS BURNT ABOUT TWO-THIRDS THRU....CAN TRUCK...D LEWIS 3-25-09...BACK ON AT 18:15//VER/CRB IDC XXXX
5817 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-07-14 15:55 | 2018-07-14 20:30 | 10 | 275 | 4773181 | 2750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Crew Required//20-d4-7549 btm side of cutout came out./flaggers/trucks ok. Repairs made, closed line fuse on pole 20D4-7549 at 20:30. Ticket complete L3/HFP
5818 | Hazard | 3303902 | LESLIE | WOOTON | 2019-07-08 12:44 | 2019-07-08 16:33 | 12 | 229 | 4679051 | 2748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON 438-39 Released by crew 077S01, ..all power restored @ 16:33.p.hicks L3/HFP
5819 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-04-01 05:14 | 2014-04-01 09:03 | 12 | 229 | 4549971 | 2748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AFTER DAYLIGHT--REPLACED BAD CUTOUT//COD 12// VER/DBM IDC XXXX
5820 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-01-23 15:36 | 2012-01-24 14:30 | 2 | 1374 | 4287031 | 2748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAVE 2 SPANS OF #2 AUL. PRIMARY & NETURAL DOWN .WILL NEED 4 MEN WIRE POLE TOP PIN INSULATOR &CUTOUT FOR 7200 PLEASE SEND THIS TO TIM HALL TO HAVE THIS DONE IN THE MORNING. RELEASED BY CREW 074S04/REPAIRED WIRE AND REP. C/O CLOSED IN 20TON POLE 68-22 AT 1430 ENTERED MD COD-2 ISO LF 37830068000022 VER/HFP L3/HFP IDCC PN185 XXXX
5821 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-10-24 10:19 | 2017-10-24 11:20 | 45 | 61 | H4490031 | 2745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS PERFORMING FUSE COORDINATION ADJUSTMENTS FOR RELIABILITY. OPENING SWITCH ON 38830621000042 TO SAFELY REPLACE A FAILING CUTOUT ON 38830621000068 FROM 1000-1100 (45 ADDL COD/6 ORIG). ADJUSTED 621-68 TO 15T/ADJUSTED 38830621C40226 TO 12T. 1019-1120 ALL RESTORED. VER/AWD L3/HFP XXXHFP ACBC FP 38830621C40226
5822 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-01-16 05:46 | 2013-01-16 17:12 | 4 | 686 | 4609691 | 2744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED NO TRUCKS BAD CUTOUT RELEASED BY CREW 078S03 COD-4 ISO LF 38830297000007 VER/HFP L3/HFP IDC XXXX
5823 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-07-30 21:53 | 2020-07-31 05:30 | 6 | 457 | 4259961 | 2742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OUTAGE STARTED @ 2153//SERVICER ACCIDENTLY CLOSED ORIGINAL OUTAGE //bad 50 kva, 120/240, 7200. truck to pole. line crew reqd.//,repairs made all cust restored @ 0530 please close ticket thanks.bt/ ISO 39831098C00501/ COD 6
5824 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2015-03-25 19:48 | 2015-03-25 20:25 | 74 | 37 | 4228391 | 2738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEAD END INSULATOR FAILED ON POLE 333-73, OPENED REC. AT POLE 333-84 AT 1948 TO MAKE REPAIRS.CLOSED AT 2025. VER/ARN AJB
5825 | Hazard | 3420001 | SOFT SHELL | VEST | 2021-08-21 13:54 | 2021-08-21 17:23 | 28 | 209 | 4132891 | 2738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken line fuse cutout on pole 156-34, will need to open recl on 156-107 for short outage to replace.. open recl on 156-107 @16:47 hrs closed in @1723
5826 | Whitesburg | 3401301 | FLEMING | NEON | 2020-06-07 07:45 | 2020-06-07 16:34 | 22 | 529 | 4974571 | 2738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | line fuse out on pole 355-D4-11. a phase transformer out.. transformer fuse out on 355-61.. line fuse back in @ 9:09. a phase transformer back in @ 9:20. bad 75kva on ple 355-61 Released by crew 077S11 ARCOS initated for line crew.. restored power at 16:34..
5827 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-10-16 18:19 | 2009-10-16 18:55 | 76 | 36 | 52764-1 | 2736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR# 32246941 POLE 142-19 HOT TAP BURNT OFF//VER/CRB IDC XXXX
5828 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2010-10-16 15:33 | 2010-10-16 16:30 | 48 | 57 | 60298-1 | 2736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37353855// POLE 139-91 BAD WESTINGHOUSE CUTOUT 30T FUSE//VER/CRB IDC XXXX
5829 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-03-30 21:21 | 2017-03-31 00:12 | 16 | 171 | 4598921 | 2736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ARRIVED AT THIS JOB POLE 975-74, IS ROTTEN AT GROUND, NEEDS TO BE REPLACED TONIGHT, 405 PHONE CO POLE, CANS USE ALL MATERIAL BACK.OPEN HTSP ON 975 63 @ 21:21,ALLL POWER RESTORED @ 00:12
5830 | Hazard | 3310502 | HADDIX | CANOE | 2016-04-07 02:57 | 2016-04-07 12:03 | 5 | 546 | 4061611 | 2730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 37830026000018 ROTTEN AND FELL ON GROUND,LIFT HOT TAP ON POLE 37830025000049 AND GROUNDED LINE,POLE IS BAD MANUAL 35C6 POLE,RIDGE PIN INSULATOR AND CLEVIS,5 MAN LINE CREW AND R/W CREW,WILL HAVE TO BLOCK ROAD.72 KV LINE.OPEN HOT TAP AT 5:30. RELEASED BY CREW 077 REPAIRS MADE AND POWER RESTORED AT 1203 RELEASED BY CREW 077H03 VER/CRB
5831 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2013-01-21 02:10 | 2013-01-21 05:40 | 13 | 210 | 4715311 | 2730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER CALLED OUT. POLE 44-6054 6A PRI. DOWN TRUCK TO POLES POLE 44-6010 50T OUT RELEASED BY CREW 078S08 VER/ARN IDC XXXX
5832 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-09-25 08:30 | 2009-09-25 16:05 | 6 | 455 | H61982-1 | 2730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE ON POLE 38830185000107 AT 08:30, CREW HAS BEEN NOTIFIED, 45 POLE. TRUCK OK, SHOULD HAVE METERIAL FOR JOB ON TRUCKS RELEASED BY CREW 078S05 COD-7 MD FILED VER/KEP L3/KEP IDC XXXX
5833 | Hazard | 3301401 | COMBS | COMBS | 2015-02-12 01:54 | 2015-02-12 11:00 | 5 | 546 | 4009341 | 2730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL HAVE SERVICER CHECK AT START OG REGULAR SHIFT-----BAD 50 KVA 7200 TRANSFORMER ON POLE37830271C00090 OIL SPILL, NEED LINE CREW WITH FLAGGERS, TRUCK ACCESS. RELEASED BY CREW 077S04 CHANGED TRANSFORMER AND RESTORD POWER AT 11;00 STILL HAVE A BIG OIL SPILL TO CLEAN UP VER/CRB L3/HFP XXX AJB
5834 | Hazard | 3302704 | HAZARD | KENMONT | 2009-01-17 17:02 | 2009-01-17 21:10 | 11 | 248 | 57754-1 | 2728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28106762 // L3/HFP
5835 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-11-26 21:22 | 2019-11-27 01:30 | 11 | 248 | 4071151 | 2728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Insulator failed on pole 37830206000079 and caused a pole fire/ wire down from pole 37830206D20304 to 37830206000080 #4 copper/ manual pole/ manual row/bad insulator manuel pole/ ISO 37830206000052/ COD 11
5836 | Hazard | 3303902 | LESLIE | WOOTON | 2020-09-08 10:57 | 2020-09-08 16:00 | 9 | 303 | 4441291 | 2727 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | crew to bring side by side and patrol line Released by crew 077S07 fuse was broke not blown
5837 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2022-01-02 09:45 | 2022-01-02 11:34 | 25 | 109 | 4260021 | 2725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse is open on 429-27 patrolling line//// Found and replaced craked cutout on 429-2018 apr at 1134 close ticket
5838 | South Williamson | 3411401 | DEWEY | INEZ | 2013-10-29 17:06 | 2013-10-29 17:12 | 454 | 6 | 4973651 | 2724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED RECLOSER TO ISOLATE REGULATOR VER/ARN L3/HFP IDC XXXX
5839 | Pikeville | 3413402 | GARRETT | LACKEY | 2010-08-10 05:53 | 2010-08-10 09:40 | 14 | 227 | 51809-1 | 2723 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT ON POLE 37830111000102 ISOLATED, FUSE AT 111-75 ON AT 09:05 // COD-14 ... LAST CUSTOMER OFF POLE 102 ON AT 9:40 ... ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/HFP L3/HFP IDC XXXX
5840 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-03-30 14:47 | 2016-03-30 18:56 | 11 | 249 | 4006231 | 2721 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD ARM PIN INSULATOR ON 1149-248 INSULATOR IS CRACKED AND MAKING SIZZLING NOISE NEED LINE CREW TO MAKE REPAIRS CREW ARRIVED WE OPENED RIGHTHAND PHASE ON1149-33 TO DEENERGIZE LINE SO CREW COULD MAKE REPAIRS THE MIDDLE AND LEFT HAND PASE LOOPS ARE CUT IN CLEAR ON POLE 1149-33 RIGHT HAND PHASE ONLY IS HOT OPENED CUTOUT ON 1149-33 AT 18:31 CLOSED CUTOUT ON 1149-33 AT 18:47
5841 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-10 21:15 | 2016-01-10 21:32 | 160 | 17 | H4598731B | 2720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38831027D00064/ CUTOUT FAILED AND BURNT POLE OFF. AJB OUTAGE TO RESTORE 38831027D00087 TO NORMAL.
5842 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-11-15 07:46 | 2020-11-15 16:50 | 5 | 544 | 4676851 | 2720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | called customer no reading on meter; Line fuse out on pole 1109-33(manual) 1 span of #6A Primary down that crosses hwy 1098. primary in the clear of the road. will need big bucket to add splices and wire to make repair, Flaggers Needed.csc Released by crew 077E05
5843 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-09-01 11:25 | 2021-09-01 14:15 | 16 | 170 | 4194631 | 2720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OPEN AT 38831124C00141, BAD DE INS AT 38831124C00196, KENNY LITTLE ON SITE TO CHANGE IT OUT. Got insulator changed and closed L/F back in 1415.
5844 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-01-01 05:27 | 2017-01-01 13:00 | 6 | 453 | 4259951 | 2718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830967000026 BURNED OFF FROM CUTOUT CHANGE POLE OUT VER/CRB L3/HFP XXXHFP
5845 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-02-06 14:38 | 2008-02-06 16:15 | 28 | 97 | 51489-1 | 2716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD SLAPPED INTO GUY WIRE.....// VER/TOM IDC XXXX
5846 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-03-05 10:01 | 2009-03-05 13:15 | 14 | 194 | 55187-1 | 2716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3409401//RISER FAILED ON POLE 151-88 AND RUINED CUTOUT//COD 14//CREW REQUIRED// VER/DBM IDC XXXX
5847 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-11-04 16:35 | 2010-11-04 20:10 | 21 | 215 | 51908-1 | 2715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37633423 // RESTORED AT 2010 RELEASED BY CREW 074S02// VER/DBM IDCC CDC92 XXXX
5848 | Hazard | 3309003 | JEFF | VIPER | 2020-07-19 15:36 | 2020-07-19 21:19 | 28 | 343 | 4183391 | 2714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Ocrs out on 37830416000032 bad cutout on 37830416000102 could not reach it took clamp off closed ocr 16:54 need 2 man big bucket 7200V cutout lighting arr. and /bracket Released by crew 077S03,changed cutout, all power restored @ 21:19,, p.hicks
5849 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-09-06 13:09 | 2018-09-06 15:07 | 23 | 118 | 4049601 | 2714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Patrolled line and found no problems. Closed 40T line fuse on 858-153 @ 15:07. sh L3/HFP
5850 | Whitesburg | 3401301 | FLEMING | NEON | 2014-06-23 06:46 | 2014-06-23 10:32 | 12 | 226 | 4139571 | 2712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE OPEN ON POLE 355-2, STINGER BURNT INTO ON BOTTOM SIDE OF CUTOUT WILL HAVE TO HAVE FLAGGERS TO MAKE REPAIRS.MADE REPAIRS RESTORED POWER AT 10:32.//COD 12// VER/DBM
5851 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-12-04 11:21 | 2022-12-04 13:30 | 21 | 129 | 4226941 | 2709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Solid blade cut out broke on pole # 245D-148, Replaced
5852 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-11-01 08:02 | 2018-11-01 13:03 | 9 | 301 | 4348851 | 2709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | TRIED RISER FUSE AND IT CAME BACK OUT//WILL START ISOLATING//30t open on 69-4671, bad cable/elbow @ 69-476630 t //,,failed primary elbow in padmount 69-4766, re - terminating,
5853 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-04-04 15:27 | 2012-04-04 23:20 | 12 | 473 | 4647161 | 2706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OPEN ON 173-84 PATROLING LINE/TRIED FUSE ONCE DIDNT STAY STILL PATROLING/BAD TRANSFORMER 15KVA TRUCKS MAYBE 173-35(ALL POWER RESTORED AT 23:20) VER/KEP IDC XXXX
5854 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-01-15 00:08 | 2011-01-15 01:30 | 33 | 82 | 61478-1 | 2706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURN-IN TWO //VER/GAH IDC XXXX
5855 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-11-29 16:07 | 2018-11-29 19:35 | 13 | 208 | 4491591 | 2704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NC SWITCH ON POLE 37830155000001 IS OPEN//COD 13//solid blade cutout is open on pole 155-1, cutout doesn't appear to be broke, cable guys were up here and could have shook door open solid blade cutout is open on pole 155-1, cutout is broke, will need a couple men and big bucket//
5856 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-10-26 01:28 | 2022-10-26 10:30 | 6 | 542 | 4065801 | 2702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout at 37830203000055 caused l/f at 37830204000002 to blow/crew required to make repairs at 203-55//Dispatched in accordance with KYPCo Late Night Callout Guidelines. power restored at 10:30
5857 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2021-06-09 17:30 | 2021-06-09 22:00 | 10 | 270 | 4698581 | 2700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad dual bushing 50kva 120/240 delta bank xfmer blown lid off/crew reqd/truck ok. Released by crew 078S04
5858 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-04-06 23:50 | 2016-04-07 03:35 | 12 | 225 | H4061211 | 2700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20-3040 CROSSARM BURNT OFF SEND CREW NEED ARM AND CUTOUT POLE 20-3031 65T BLOWN "A" PHASE COD-50 OPENED OTHER "C" PHASE COD-12 11:50 PM RELEASED BY CREW 078S0820-3040 ,,CREW ON SITE VER/KEP L3/HFP HFPC FP38830020D13040 AJB
5859 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-07-26 18:31 | 2021-07-26 20:11 | 27 | 100 | 4962471 | 2700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrestor against down guy, cleared up. Tried in once anitially, and line fuse on 38830069D37077 came out along with transformer fuse. closed in both @ 19:57. Restored
5860 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-07-03 18:02 | 2019-07-03 19:02 | 45 | 60 | 4649641 | 2700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER DOL 935830/ Bad crossarm 38830852000102/ ISO 3401102/ COD 45/ off 1802 on 1902 L3/HFP
5861 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-11-12 13:39 | 2013-11-12 14:17 | 71 | 38 | H4030301 | 2698 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE ON FIRE NEED TO OPEN RECLOSERS ON POLE 182B-3567POLE FIRE @ 182-63 RECLOSERS OPEN @ 0815 ON POLE 182-B4-3567 RELEASED BY CREW 078S05/SWITCHING TO GET MAJORITY OF CUST BACK IN SERVICE/VEM. 0929 - CLOSED A & C RECL POLE 3567 RESTORING 181 CUSTS// 0943 CLOSED BYPASS DISC TO B PHASE RESTORING 9 CUSTS/CREW WORKING ON POLE CHANGE/FETR ON REMAINING CUST 1430/VEM/APPROX 30 MINUTE OUTAGE TO REPAIR LOOPS/FETR ON ALL CUST 1430/VEM/ALL CUST RESTORED 1417/VEM RELEASED BY CREW 078H14 //VER/GAH L3/HFP IDC XXXX
5862 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-02-22 15:00 | 2013-02-22 16:27 | 31 | 87 | 4840351 | 2697 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSSARM BURNT OFF--NEED 2 ARMS-2 CUTOUTS 2 ARRESTORS AN 2 SETS OF BRACES---V MULLINS TO WORK JOB--OPENED FUSES ON POLE 38830045A10005 AT 15:00 TAGED TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/FETR 1715/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1627/PLEASE CLOSE TICKET/THANKS/VEM ///VER/CRB L/3 CRB IDC XXXX
5863 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2021-07-15 04:53 | 2021-07-15 10:30 | 8 | 337 | 4914441 | 2696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with late night callouts. broke cutout on 444-18. cutout replaced power restored
5864 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-11-20 07:23 | 2019-11-20 13:00 | 8 | 337 | 4049541 | 2696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 span of 6ACW burndt down on a span of open wire and caught the telephone on fire, will keep track of times on trans., Dennis M. is getting a DHE crew to help with repairs. opened xfmr @ 1000, made repairs and closed back in @1300.
5865 | Hazard | 3301101 | CHAVIES | CHAVIES | 2012-10-02 15:53 | 2012-10-02 20:30 | 11 | 277 | 4108801 | 2695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINE FUSE BLOWN ON POLE 194-14, POLE TOP PIN FELL OFF POLE 171-111, POLE ROTTEN AT TOP. ISOLATED LINE LIFTED CLAMP ON POLE 170-77/// FUSED LINE ON POLE 194-14, LINE HOT UP TO POLE 170-77. AT 19:46/// INSTALLED FIBERGLASS POLE EXTENSION ON POLE 171-111, PUT CLAMP ON LINE HOT AT 20:30. COD-11 ISO LF @ 37830194000014 VER/HFP L3/HFP IDC XXXX
5866 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-11-10 17:21 | 2018-11-10 18:10 | 55 | 49 | 4387301 | 2695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout failed (newer poly-cutout) L3/HFP
5867 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2014-03-29 23:41 | 2014-03-30 00:30 | 55 | 49 | 4537831 | 2695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 5- 10 MIN OUTAGE TO ALLOW CREWS TO RESTORE LOOPS ON ORDER 4535031 VER/PDP IDC XXXX
5868 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-03-15 14:33 | 2019-03-15 15:50 | 35 | 77 | 4989781 | 2695 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1147-4007 aphas basket burt off, repairs made, restored a ph. fuse @ 15:50 L3/HFP
5869 | Hazard | 3309302 | VICCO | JEFF | 2012-03-14 17:15 | 2012-03-14 17:50 | 77 | 35 | 4579721 | 2695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED SWITCH TO SAFELY WORK ON PHASE THAT HAD BROKEN OFF FROM INSULATOR VER/KEP IDC XXXX
5870 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-04-01 14:41 | 2010-04-01 15:50 | 39 | 69 | 57042-1 | 2691 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 600-08 I CHANGED OUT.BACK ON/COD 39// VER/DBM AJB
5871 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-07-16 09:15 | 2013-07-16 15:20 | 10 | 365 | 4528621 | 2690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | FAULT INDICATOR SHOW BAD CABLE BETWEEN PAD MOUNT TRANSFORMER 1073-3616 TO 1073-3614, THINK YOU CAN ISOLATED THIS SECTION OF CABLE BUT HAD NO FEED THRU, AND PARKING STANDS IN TRANSFORMER RELEASED BY CREW 078S06 RELEASED BY CREW 078H07 VER/CRB L/3 CRB IDCC CDC83 XXXX
5872 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-05-13 05:32 | 2008-05-13 14:30 | 5 | 538 | 63378-1 | 2690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402204 -REPLACED CUTOUT GATE / GXJ//VER/CRB IDC XXXX
5873 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2016-07-29 08:12 | 2016-07-29 17:10 | 5 | 538 | 4706631 | 2690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 941D379,50 KVA/7200VOLT, 7200 VOLT CUTOUT NEEDED,CUTOUT BROKE,,BEHIND 45 WILSON LOOP,TA WITH FLAGGERS ON MAIN ROAD , RT 292 JUST BEFORE ENTRANCE TO TURKEY CK. RIGHT OF WAY CREW NEEDED TO CLEAR TREE COVERING XFORMER RELEASED BY CREW 079M01//REPAIRS MADE//RESTORED AT 17:10//COMPLETE//EM/ ISO 38820941D00379/ COD 5/ VER/BOW
5874 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2010-08-30 19:26 | 2010-08-30 23:10 | 12 | 224 | 62073-1 | 2688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING. CUTOUT FAILED ON LINE FUSE POLE. POLE IS COVERED WITH VINES. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO REPLACE WITH BIG BUCKET. CREW ONSITE. REPLACED CUTOUT AND CLOSED FUSE @ 23:10. SH COD-12 VER/HFP L3/HFP IDC XXXX
5875 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-10-26 03:39 | 2016-10-26 10:03 | 7 | 384 | 4053671 | 2688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 37830104B00007/ ISO 37830104B00007/ COD 7GOT BROKEN CUTOUT ON LINE FUSE/ RESTORED 1003/ VER/BOW L3/HFP XXXHFP
5876 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-05-15 10:14 | 2018-05-15 10:35 | 128 | 21 | 4351221 | 2688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER 37830401D00017 TO REPLACE CUTOUT AND ARRESTER ON POLE 37830401C00096//OPENED RECLOSER 37830401D00017 TO REPLACE CUTOUT AND ARRESTER ON POLE 37830401C00096 open at 10:14 closed at 10:35 L3/HFP
5877 | South Williamson | 3411401 | DEWEY | INEZ | 2014-06-29 20:44 | 2014-06-29 21:12 | 96 | 28 | 4170491 | 2688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4169561//AFTER CLOSING RECLOSER, CREWS SAW CUTOUT BURNING AND HAD TO RE-OPEN RECLOSER TO MAKE REPAIRS//COD 96// VER/ARN AJB
5878 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-05-05 20:14 | 2008-05-05 21:15 | 44 | 61 | 57349-1 | 2684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP AND STIRRUP BURNT OFF//3308502//VER/CRB IDC XXXX
5879 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2010-12-07 19:59 | 2010-12-08 00:03 | 11 | 244 | 64213-1 | 2684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR - 38025624 // BAD 25KVA NEED 50KVA TRUCK OK SEND TO JOE H. RELEASED BY CREW 078S08// REPLACED 25 WITH 50 KVA CHANGED C/O & L/A POWER RESTORED @ 00:03 12/08/10 J. HEMLEPP & CREW 078H05 //VER/GAH IDC XXXX
5880 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-08-22 19:48 | 2014-08-23 03:15 | 6 | 447 | 4407251 | 2682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SIDETAP CUTOUT BROKEN ON RECL POLE,NEED CREW,BIG BUCKET TO REPLACE,WILL DO THIS ONE AFTER WE CHANGE XFR AT DOLLAR GENERAL RELEASED BY CREW 074S06SIDETAP CUTOUT BROKEN ON RECL POLE,NEED CREW,BIG BUCKET TO REPLACE,WILL DO THIS ONE AFTER WE CHANGE XFR AT DOLLAR GENERAL////////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS// COD 6// VER/ ADH
5881 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-10-20 08:34 | 2011-10-20 13:02 | 10 | 268 | 4002451 | 2680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER ETA 0830 // CREW REQUIRED--OPEN LINE FUSE AT 08:34 --ON POLE 38830116B00545--INSTALLED GROUD --CAN USE PADS TO GET TRUCK TO POLE--NEED TECH RELEASED BY CREW 078S07 MD FILED VER/KEP IDC XXXX
5882 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-10-20 10:37 | 2021-10-20 12:51 | 20 | 134 | 4368671 | 2680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed cutout on pole 38830068B00807
5883 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-04-21 09:56 | 2009-04-21 12:10 | 20 | 134 | 62782-1 | 2680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLED LINE FOUND A BAD CUTOUT GOING TO REPLACE CUTOUT//COD 20// VER/DBM IDC XXXX
5884 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-08-01 08:07 | 2010-08-01 09:50 | 26 | 103 | 60084-1 | 2678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR == REPLACED INSULATOR//VER/CRB IDC XXXX
5885 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-07-16 06:10 | 2009-07-16 09:53 | 12 | 223 | 64187-1 | 2676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP .BAD CUTOUT ON POLE 1060-D-76. WAITING FOR CREW. COD-12 ISO LF 38821060D00076 ENTERED MD...HFP L3/HFP IDC XXXX
5886 | Whitesburg | 3312901 | JENKINS | KONA | 2012-06-14 17:15 | 2012-06-14 19:02 | 25 | 107 | 4916431 | 2675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | L/F OUT AT POLE 404-79, WILL BE PATROLLING. TIE WIRE COME LOOSE AT POLE 404-95, CAUSING PRIMARY TO SAG BELOW NUETRAL, WILL BE MAKING REPAIRS.MADE REPAIRS CLOSED L/F BACK IN AT 19:02. VER/TOM L3/TOM IDC XXXX
5887 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-12-24 04:45 | 2016-12-24 06:32 | 25 | 107 | 4231951 | 2675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN AT POLE 37820009C00190. REPLACED BAD TRANSFORMER CUTOUT ON POLE 37820009C00087. POWER RESTORED AT 06:32. AJB
5888 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-06-08 18:28 | 2015-06-09 16:45 | 2 | 1337 | 4534681 | 2674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *** DDC HOLD TAGS****FOUND BAD CUTOUT ON POLE 1120-19, REMOVED HTSP ON POLE 1120-3 AND GROUNDED AND TAGGED TO DDC, CREW REQ, CAN NOT USE TRUCK, HAVE ONE CUST OUT RELEASED BY CREW 078S06DDC HOLD TAGS FOUND BAD CUTOUT ON POLE 1120-19, REMOVED HTSP ON POLE 1120-3 AND GROUNDED AND TAGGED TO DDC, CREW REQ, CAN NOT USE TRUCK, HAVE ONE CUST OUT RELEASED BY CREW 078S06 POLE 1120 HAS BURNT OFF REMOVING PRIMARY POLE AND XFER OFF OF HILLSIDE REPLACING IT WITH 2 SECONTARY VER/CRB
5889 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2014-11-24 10:48 | 2014-11-24 17:10 | 7 | 382 | 4762371 | 2674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND TO MIKE RELEASED BY CREW 078S08 CREW REQD. 2-12KV CUTOUTS & ARRESTORS NEED REPLACED IN APPROACH ON HENDRIX. RELEASED BY CREW 078H12 REPLACED CUTOUTS CLOSED IN AT 1710 VER/HFP L3/HFP
5890 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-06-23 07:51 | 2008-06-23 15:35 | 8 | 464 | 52726-1 | 2672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S04//3001102 POLE 91-961 BURNT OFF. B. FRALEY COMING TO ACCESS DAMAGE. LINE ISOLATED AND GROUNDED ON POLE97-277. LINE RE-ENERGIZED ON POLE 91-8 AT 11:15 A.M. RELEASED BY CREW 078S04----- -----POWER ON TO BARN @15:35 VER/HFP IDC XXXX
5891 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2016-02-29 10:12 | 2016-02-29 16:20 | 29 | 368 | 4787101 | 2672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T LF OPEN @ 1124-1558. RESTORED @ 11:00. HOT TAP LIFTED & GROUNDED TO D.JENT @ 1124-1550.. FAULT POLE 1552. RELEASED BY CREW 078S07/ ALL POWER RESTORED 1620 VER/HFP L3/HFP AJB
5892 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2012-06-22 16:12 | 2012-06-22 19:10 | 15 | 178 | 4947871 | 2670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T FUSE MELTED OUT ON 50KVA XFMR IN A 3 XFMR BANK GIVING CUSTOMERS LOW VOLTAGE. RE-FUSED XFMR @ 19:10. SH VER/HFP L3/HFP
5893 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-11-21 23:00 | 2011-11-22 12:12 | 26 | 792 | 4098841 | 2667 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE 18-231 TO BE BURNTED OFF, AT THE TOP, POLE IS A 404 WELL BE CREW REQ, NEED CUTOUT AND ARRESTOR, EVERYTHING ELSE WILL WORK BACK, MEN 4, EQUIP, TRACT MACHINE OR YARD DOG, I HAVE LOOP CUT ON POLE 18-110, RESTORED RECLOSER AT 1215, EVERYONE BACK ON JUST ONE CUST STILL OFF, * CREW WILL BE DISPATCHED AT REG WK TIME IN THE AM. PLEASE CONTACT RAYBURN FOR CREW THS AM.//POWER RESTORED @ 1212//COD 26// VER/DBM IDC XXXX
5894 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-06-13 15:35 | 2012-06-13 15:42 | 381 | 7 | H4912251 | 2667 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | PHASE 3 OUT AT 1421 DUE TO BUS REGULATOR DISC... MANUALLY OPENED CIRC BRK AT 1535. CLOSED AT 1542 IDC XXXX
5895 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2018-10-16 17:06 | 2018-10-16 18:20 | 36 | 74 | 4259721 | 2664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830235000068 fuse 30t open-38830282000160 pole top burnt off-can be lowered or pole topper --c/o and fiberglass t-bracket needed-crew req-ds101618 Released by crew 078S01,repairs made all cust restored please close ticket thanks.bt /// COULD WE HAVE USED SW ON POLE 38830259000053 TO ISOLATE TROUBLE? L3/HFP
5896 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-11-24 07:48 | 2018-11-24 09:49 | 22 | 121 | 4472041 | 2662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Low side fuse blown on pole#217-354 will patroll/// Hot tap lead burnt off on top of line fuse ///Repairs made closed low side fuse in @ 09:49 and restored service L3/HFP
5897 | Whitesburg | 3312901 | JENKINS | KONA | 2012-02-18 12:29 | 2012-02-18 14:30 | 22 | 121 | 4356631 | 2662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LINE FUSE OUT AT POLE 404-79, WILL BE PATROLLING.PRIMARY DOWN AT POLE 404-85, SLEEVE BURNT INTO, WILL BE MAKING REPAIRS.PUT PRIMARY BACK UP, CLOSED L/F BACK IN AT 14:30.//COD 22// VER/DBM IDC XXXX
5898 | Hazard | 3309302 | VICCO | JEFF | 2018-09-20 12:10 | 2018-09-20 12:32 | 121 | 22 | 4134781 | 2662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | by pass cutouts on recloser pole #299c-254 have failed and energized loop laying on arm,short outage required to repair, opened reclosers on 299c-254 @ 12:10 hrs..made repairs and closed in bypasses @ 12:32 hrs, all power restored..p.hickss L3/HFP
5899 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-12-03 14:51 | 2008-12-03 17:04 | 20 | 133 | 54259-1 | 2660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WE HAVE LINE FUSE BLOWN ON POLE 248-140, 30T. CHECKING LINE WILL REFUSE IF NO PROBLEM, ARRESTOR BAD, REPLACED POWER RESTORED//3300601//COD 20//MADE A MDE//VER/CRB L3/KEP IDC XXXX
5900 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-12-16 08:18 | 2008-12-16 10:31 | 20 | 133 | 58870-1 | 2660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR# 27698678 //A, POLE FIRE, LINE FUSE BLOWN AT POLE# 38821062B00144 - 20 CUST, CALLED FOR CREW ENTERED MD...HFP L3/HFP IDC XXXX
5901 | Paintsville | 3410602 | E.PRESTON | LANCER | 2020-03-29 07:19 | 2020-03-29 18:29 | 5 | 670 | 4521351 | 2657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on polo955-b-208 . need 1 a lineman & 2 d lineman. will open line @ pole #955B00200 to chg. x fmr safely opened cutout on pole 200 at 1328
5902 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-04-13 11:44 | 2010-04-13 13:07 | 32 | 83 | 62707-1 | 2656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | B PHASE 100L RECLOSER IS BAD, RED TAGGED TO DDC,, BYPASSED WITH 80T FUSE COD-32 VER/KEP L3/KEP IDC XXXX
5903 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2019-07-31 04:09 | 2019-07-31 13:00 | 5 | 531 | 4814761 | 2655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke on pole 1130-85 will make repairs/// Changed bad cutout and refused xfm @ 13:00 and restored service L3/HFP
5904 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-12-03 14:08 | 2022-12-03 14:17 | 295 | 9 | 4224301 | 2655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dead-end insulator bad on pole 37830190C00108///Will have to open recloser on37830190C30459 to make repairs when crew gets here ///Line crew enroute//OFF @1408 ON @ 1417
5905 | Hazard | 3310502 | HADDIX | CANOE | 2013-10-30 09:12 | 2013-10-30 15:31 | 7 | 379 | 4974681 | 2653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | GOT BAD INSULATORS ON POLE37830051000068AND POLE 37830051000073 GOING TO GET JEFF COMBS CREW WHEN THEY GET DONE AT BUCKHORN RELEASED BY CREW 077S05. VER/SEF IDC XXXX
5906 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2017-05-26 05:55 | 2017-05-26 13:17 | 6 | 442 | 4864771 | 2652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF TRUCK TO POLE SEND TO VERNON POLE 92-712 25T OPEN RELEASED BY CREW 078S08/CREW ON SITE/FETR 1330/VEM/REPAIRS COMPLETE AND ALL CUST RESTORED 1317/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
5907 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-06-16 02:45 | 2008-06-16 05:39 | 16 | 174 | 65345-1 | 2649 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | FAILED MIDDLE PHASE CUTOUT CREW WILL REPLACE ALL . PP UNTIL 0500 WHEN CREW OPENED OTHER TWO CUTOUTS. IDCC PN1216 XXXX
5908 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-02-28 13:27 | 2011-02-28 15:33 | 21 | 126 | 64636-1 | 2646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED BAD INSULATOR//VER/CRB IDC XXXX
5909 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-05-19 07:34 | 2020-05-19 10:33 | 22 | 179 | 4853471 | 2646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Line fuse open on pole 20-c2-4547, #2 Acsr Primary down, no truck, from 20-A4-1571 to 20-A4-1572. Crew required. Line fuse, and transformer fuse on pole 20-A4-1571 open, grounded and tagged to Bobby Tackett going towards 20-A4-1572. Line fuse on 20-c2-4542 Back on @ 09:25 Released by crew 078S02,repairs made all cust restored @ 1033 please close ticket thanks.bt Released by crew 078H02
5910 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-05-01 13:30 | 2012-05-01 18:24 | 9 | 294 | 4730461 | 2646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830248A00431 ALMOST BURNT IN TWO AT CUTOUT, OPENED LINE FUSE ON POLE 37830248A00369 AT 1330, LINE CREW ENROUTE TO REPLACE POLE. RELEASED BY CREW 077S04 ///VER/CRB L/3 CRB IDC XXXX
5911 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-12-01 11:47 | 2009-12-01 12:50 | 42 | 63 | 53503-1 | 2646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PHASE A ONLY. PATROLLING. FUSE LINK APPEARS TO HAVE BROKE. RE-FUSED 50T @ 809-413 (PHASE A ONLY). SH // 42 COD (29 + 13) IDCC CNT107 XXXX
5912 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2009-02-27 13:52 | 2009-02-27 15:30 | 27 | 98 | 52271-1 | 2646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FOUND BAD POLE TOP PIN INS, ON POLE 1122-112, HAVE IT CHANGED AND HAVE 20 T LINE FUSE BACK IN ON POLE1122-109, ALL CUST ARE BACK ON//COD 27// VER/DBM IDC XXXX
5913 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-05-24 23:48 | 2018-05-25 10:49 | 4 | 661 | 4494551 | 2644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | V MullinsDispatched in accordance with KYPCo Late Night Callout Guidelines, bad 12kv c/o, no trks narrow driveway no room Released by crew 078S07/crew on site/FETR 1130/vem/repairs made and all cust restored 1049/please close ticket/thanks/vem // COD-4 ISO LF 38830068A00077
5914 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-05-22 17:14 | 2016-05-22 20:00 | 16 | 166 | 4248551 | 2641 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER TRANSFORMER CUTOUT IS BROKE ON THREE TRANSFORMER BANK. OPENED LINE FUSE ON 954-361 @ 19:05, REPLACED ALL THREE XFMR CUTOUTS AND RESTORED XFMR BANK AND LINE FUSE @ 20:00. SH//COD 15 (+1)
5915 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-01-29 10:02 | 2015-01-29 12:47 | 16 | 165 | 4972241 | 2640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON TRANSFORMER, GOT GREG SHOUSE COMMING TO HELP CHANGE OUT CLOSED LINE FUSE AT 1247// COD 16// VER/ ADH L3/HFP
5916 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-07-07 11:42 | 2019-07-07 15:22 | 12 | 220 | 4673001 | 2640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolling line, found bad cutout and arrestor on pole 256-168, all power restored L3/HFP
5917 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2022-09-04 07:53 | 2022-09-04 10:05 | 20 | 132 | 4834641 | 2640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke transformer cutout
5918 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-09-05 03:37 | 2011-09-05 14:37 | 4 | 660 | 4815181 | 2640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /DUE TO FLOODING IN THE AREA, WILL NOT BE ABLE TO CHECK THIS UNTIL TOMORROW MORNING PER DUTY SUPERVISOR//CENTER LINE FUSE IS OUT AT POLE 287-18. I AM PATROLLING LINE NOW. INSULATOR ON POLE 287-105 HAS BROKEN DOWN ON CENTER PHASE. I AM CALLING FOR HELP. WE WILL HAVE TO OPEN THE OTHER 2 PHASES ON POLE 287-18 WHEN HELP ARRIVES // CCC COD-4 ISO LF 37830287000018 // OPENED OUTSIDE PHASE FUSES @ 1318 TO MAKE REPAIRS (A & B 33 CUSTOMERS) 1437 ALL RESTORED SEE H1158505-1 VER/HFP L3/HFP IDC XXXX
5919 | Hazard | 3302704 | HAZARD | KENMONT | 2013-12-25 10:27 | 2013-12-25 13:23 | 15 | 176 | 4200591 | 2640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSF === CALLED FOR 1 MAN AND BIG BUCKET AND 50 KVA 7200 TRANSF ===CHANGED TRANSF === POWER OK//COD 15// VER/DBM L3/HFP IDC XXXX
5920 | Hazard | 3302704 | HAZARD | KENMONT | 2010-12-15 05:08 | 2010-12-15 11:25 | 7 | 377 | 50403-1 | 2639 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD SECONARY BUSHING == CALLED FOR LINE CREW TO CHANGE TRANSF OUT === JEFF COMBS CREW == CHANGED TRANSF COD-7 ISO TF 37830321B00051 VER/HFP L3/HFP IDC XXXX
5921 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2022-07-06 17:21 | 2022-07-07 15:20 | 2 | 1319 | 4405071 | 2638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | x-fmr fuse open ple 1147-4694, Need to replace transformer C/O and Arr. 7.2kv not by truck. C/O is cracked. Crew Required.P.Thovson need Fiberglass Bkt also. Released by crew 078E06///restored at 1520
5922 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-01-02 22:42 | 2014-01-03 13:21 | 3 | 879 | 4220621 | 2637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 266-290 IS ON FIRE I LIFTED HOT TAP ON POLE#266-62 @22:42. I HAVE LINE GROUNDED AND TAGGED TO DDC AND EVERYTHING MADE SAFE . WILL NEED A 40/4 POLE AND MATERIAL FOR DOUBLE DEAD-END #2 ACSR CONDUCTOR SINGLE PHASE . ANGLE POLE RELEASED BY CREW 074H17 IDCC PN290 XXXX
5923 | South Williamson | 3411401 | DEWEY | INEZ | 2012-10-02 00:02 | 2012-10-02 11:01 | 4 | 659 | 4105751 | 2636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE CHECKED AFTER REGULAR WORKTIME AS PER SET GUIDELINES //XFMR CUTOUT BROKE ON 744-39//GOING TO OPEN SIDE TAP ON THIS POLE WHILE I CHANGE OUT CUTOUT//HAD TAP OFF FROM 10:47 TO 11:01 COD +3//HAVE CUTOUT REPLACED//RESTORED AT 11:01//COMPLETE//EM //COD 4 + 3 IDC XXXX
5924 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-12-31 20:35 | 2014-12-31 20:52 | 155 | 17 | H4895521 | 2635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A PHASE RECLOSER OUT ORIGINALLY (122CUSTOMERS & 1A&C PHASE CUST)/ PRIMARY LINE IS DOWN AT THE RECLOSER POLE/ #2 ALUM DOWN @ RECLOSER/ NEED LINE CREW TO REPAIR/ TRUCK OK/ RECLOSER OPEN & ISO @ 254D-464 & TAG TO RON/ WIRE BROKE OFF AT THE BASKET/---OPENED C PH. OCR (155 CUSTOMERS & 1 A&C PHASE CUST) @ 20:35--REPAIRED #2AA PRIM AND STIRRUP--RESTORED BOTH A & C PH. ORCS @ 20:52----TBL TKT COMP/ DUPLICATE IN HOIS/ ISO 38830254D00464/ COD TOTAL 278 AJB SEE 4895521 FOR INLT A PH OUTAGE.
5925 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-08-06 07:23 | 2015-08-06 09:58 | 17 | 155 | 4102601 | 2635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 37830270D00216, GOING TO LEAVE LINE FUSE OPEN BECAUSE CUTOUT IS CLOSE TO 19.9 LINE GOT VIRGIL HURT COMMING TO HELP// VER/ ADH L3/HFP XXXHFP
5926 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2016-08-13 13:12 | 2016-08-13 16:20 | 14 | 188 | 4770421 | 2632 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE BURNT LOOSE SEND TO BOB OPENED TRANS, 02:15 RELEASED BY CREW 078S08 VER/AWD AJB WAS ONLY PART OF THE XFR OUT AND THEN REST WHEN XFR WAS OPENED?
5927 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-01-17 01:57 | 2009-01-17 05:05 | 14 | 188 | 56599-1 | 2632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000102//BAD 50 KVA VER/KEP ADDED 3 CUSTOMERS FROM 56738 & 56737 & 56661 L3/KEP
5928 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-05-06 04:07 | 2009-05-06 11:35 | 25 | 448 | 57763-1 | 2632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29691159 //3408103 - RECLOSER OUT POLE 1097-87, ISOLATED POLE FIRE AT 1097-191 ... OCR POLE 87 ON AT 05:38 / GXJ... NEED 2 MEN AND MATERIAL HANDLER TO LOWER TRANSFOMER, MATERIAL - CUTOUT AND ARRESTER & BRACKET RELEASED BY CREW 074S03 // COD-25 RECL POLE 38831097000087 // L3/HFP
5929 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-04-25 03:35 | 2012-04-25 10:25 | 8 | 410 | 4705391 | 2630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PT INSULATOR WENT BAD AND BURNED TOP OF POLE# 174-339 OFF CUT TOP OF POLE OFF TO PUT OUT FIRE, TOOK CLAMP OFF ON POLE# 288 AND GOT FUSE IN AT 0500,, NEED PT PIN AND INSULATOR FOR 19.9 KV RELEASED BY CREW 077S05//ON SITE NEED FLAGGERS ..FLAGGERS ARE ON WAY.. RESTORED 1025 VER/KEP
5930 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2020-11-28 21:24 | 2020-11-28 23:05 | 26 | 101 | 4727371 | 2626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | unsure of cause. fuse door was hanging down but the fuse was not blown, the cutout is porcelain but shows no signes of cracks. replaced fuse with new 40t and closed the door in. power restored at 2305//cod 26
5931 | Pikeville | 3421001 | BREAKS | CITY | 2010-06-29 09:15 | 2010-06-29 11:20 | 21 | 125 | 60295-1 | 2625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY DEADEND PULLED OUT. I REATTACHED IT.
5932 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-12-20 06:31 | 2019-12-20 10:16 | 17 | 225 | 4171741 | 2625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE DOWN IN THE CLEAR AT POLE 37830092000058//COD 5 FROM THE BEGINNING//OPENED L/F 37830092000049 @ 0811 TO ISOLATE TROUBLE// Released by crew 074S11//CUSTOMERS RESTORED @ 1016
5933 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-01-06 14:36 | 2013-01-06 15:58 | 32 | 82 | 4573241 | 2624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED LINE FUSE CUTOUT DOOR THAT BURNED UP ON POLE 1037-D-96. RELEASED BY CREW 079H06 ENTERED MD COD-32 ISO LF 38821037D00096 VER/HFP L3/HFP IDC XXXX
5934 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-01-12 00:32 | 2020-01-12 11:28 | 4 | 656 | 4271901 | 2624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fault pole 37830277000186, xfmr c/o broken, bucket accessable Released by crew 077X05..replaced cutout, all power restored @ 11:28 hrs.p.hicks
5935 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-10-28 16:46 | 2018-10-28 17:50 | 41 | 64 | 4335521 | 2624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NC switch on pole 38830020A41510, basket burnt off//CHANGED COD TO 41//NO SWITCH IS OFF 1 POLE I MADE MD TO SHOW THIS// Released by crew 078H04//CLOSED 1750 L3/HFP
5936 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-05-10 18:48 | 2014-05-10 19:57 | 38 | 69 | 4683821 | 2622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LOW SIDE CUT-OUT ON STEP-DOWN ON POLE 306C-20240 IS BLOWN. PATROLLING LINE. LIGHTENING ARRESTER BLOWN TO PIECES ON POLE 282-7 . CLEARED CUT-OUT AND LIGHTENING ARRESTOR AND RE-ENERGIZED STEPDOWN AT 19:57. RESTORING POWER 5/10/2014. X-FMR ON POLE 282-7 DOES NOT HAVE SECONDARY NOR SERVICED COMING FROM IT. VER/CRB IDC XXXX
5937 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-12-17 07:25 | 2008-12-17 16:15 | 23 | 530 | 59406-1 | 2620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801/ISOLATED ON 219-62 40/5 BURNT OFF BACK YARD ON 195-98/ 1 CUSTOMER WILL BE OFF/FUSE BACK IN AT 0900 HRS//CREW REQUIRED//3000801/ISOLATED ON 219-62 40/5 BURNT OFF BACK YARD ON 195-98/ 1 CUSTOMER WILL BE OFF/FUSE BACK IN AT 0900 HRS//LAST CUST ON @ 1615// VER/DBM L3/KEP IDC XXXX
5938 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-01-08 15:01 | 2018-01-08 17:12 | 20 | 131 | 4721831 | 2620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line cutout failed on 698-D-31 i can reach pole to make repairs but will open line fuse on 698-C-13 to de-energzed line to make repairs-- opened 300 amp solid door on 698C13 at 16:30 replaced line cutout on 698B31 closed solid door on 698C13 at 17;05 closed line cutout on 69831 at 17:12 restoring all customers//MADE MD TO SHOW SOLID BLADE//NO ADDITIONAL CUSTS AFFECTED COD 20//L/F 38820698D00031 IS ON SOURCE SIDE OF TRANSFORMER//MADE MD TO SHOW THIS AS WELL
5939 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2021-07-11 20:07 | 2021-07-12 10:40 | 3 | 873 | 4892871 | 2619 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | opened transformer on 67-9 @ 17:10, pole 38830067D00010, 356 windstream pole rotted off on ground, 4/0 Ug, and 1/0 secondary on pole. Send to bobby tackett, trucks okay Released by crew 078S02,repairs made all cust restored @ 1040 please close ticket thanks.bt
5940 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2019-09-18 08:24 | 2019-09-18 13:15 | 9 | 291 | 4031091 | 2619 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 6A primary broke in the clear on 835-107 leaving line fuse in and latteral off 107 energized. Temp ground placed on 836-1. Released by crew 076S02.. put wire up at this location and found another span down at pole 38830836009011.. this pole needs to be looked at by technician.. send copy to josh smith in paintsvillle.. closed fuse on pole 835-98 at 13:15 to restore power. complete rn ¦¦¦ NEED TIME FUSE WAS OPENED ON POLE 38830835D00098 - HFP
5941 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-01-04 20:12 | 2016-01-04 23:19 | 14 | 187 | H4584961 | 2618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DIP FUSE BLOWN ON POLE# 24-548 WILL RE-FUSE/// FUSE CAME BACK OUT/// NEED CREW TO CHECK UNDERGROUND PRIMARY AND XFMS///PARTIAL RESTO FROM 1917 TO 2012 REPAIRED UG CONDUCTOR AND CLOSED DIP FUSE IN @ 23:19 AND RESTORED SERVICE RELEASED BY CREW 074H17 VER/KEP
5942 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-10-07 01:17 | 2014-10-07 05:15 | 11 | 238 | 4562081 | 2618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED NEED TO CUT BRUSH THEN FIX BASKET VER/ARN AJB
5943 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-11-12 15:15 | 2012-11-12 18:53 | 12 | 218 | 4388261 | 2616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE FUSE OUT (12 CUSTOMERS) ON 20-5509/SERVICER PATROLLING LINE/VEM //1636 SERVICER PULLED OFF THIS CASE OF TROUBLE DUE TO EMERGENCY CALL WILL RETURN TO THIS CALL ASAP //SERVICER CHECKING LINE/HOPE TO HAVE FUSE BACK IN SHORTLY/VEM/BAD CUTOUT/SERVICER TO CHG /FETR 1915/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1853/PLEASE CLOSE TICKET/THANKS/VEM COD-12 ISO LF 38830020C45509 VER/HFP L3/HFP IDC XXXX
5944 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-02-18 04:08 | 2009-02-18 07:46 | 12 | 218 | 63578-1 | 2616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSS ARM BURNT OFF POLE 69-1511 RELEASED BY CREW 078S08 *** FEEDER WILL BE OPENED TO ALLOW CREWS TO MAKE REPAIRS. APPOX 30 MINUTE OUTAGE.CROSS ARM BURNT OFF POLE 69-1511 RELEASED BY CREW 078S08 FEEDER WILL NEED TO BE OPENED TO ALLOW CREWS TO MAKE REPAIRS. APPOX 30 MINUTE OUTAGE./FETR FOR XFMR 0830/VEMCROSS ARM BURNT OFF POLE 69-1511 RELEASED BY CREW 078S08 FEEDER WILL NEED TO BE OPENED TO ALLOW CREWS TO MAKE REPAIRS. APPOX 30 MINUTE OUTAGE./FETR FOR XFMR 0830/VEMRELEASE IDC XXXX
5945 | Pikeville | 3407103 | TOPMOST | KITE | 2014-07-15 07:06 | 2014-07-15 15:49 | 5 | 523 | 4246641 | 2615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED OCR ON POLE 37830209000200 AT 07:06, ARM BURNED APART AND A PHASE DOWN AT POLE 209-191, ABC PHASES GROUNDED AND TAGGED FOR G. JUSTICE AT POLE 209-200 . A PHASE GROUNDED AT POLE 210-47 RELEASED BY CREW 074S03OPENED OCR ON POLE 37830209000200 AT 07:06, ARM BURNED APART AND A PHASE DOWN AT POLE 209-191, ABC PHASES GROUNDED AND TAGGED FOR G. JUSTICE AT POLE 209-200 . A PHASE GROUNDED AT POLE 210-47 . REPAIRS COMPLETED -ALL WORK COMPLETE / GXJ//COD 6// VER/DBM AJBC CNT6 PH B PER CUST CALL.
5946 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-09-14 04:57 | 2015-09-14 11:10 | 7 | 373 | 4235431 | 2611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL LOOK AT ON REG. SHIFT PER LATE NIGHT CALLOUT GUIDELINES, SPAN OF PRIMARY DOWN, WILL NEED CREW RELEASED BY CREW 077S02/ 1110/ ISO 37830207A00027/ COD 7/ VER/BOW L3/HFP XXXHFP
5947 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-11-11 09:45 | 2013-11-11 11:15 | 29 | 90 | 4027641 | 2610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL PULLED OUT OF SLEEVE CAUSING WIRES TO SLAP TOGETHER VER/SEF L3/HFP HFPC FEC46 IDCC XXXX
5948 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-08-22 20:00 | 2014-08-24 15:30 | 1 | 2610 | 4407391 | 2610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQD. NEED NEW U.G. SEC. CONNECTIONS & PEDESTAL. OR SEND TO B. REYNOLDS IS HAVING JOB WROTE. RELEASED BY CREW 078H12 REPAIRED U.G CONNECTION CUSTOMER HAS FULL POWER VER/CRB
5949 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-04-07 18:54 | 2014-04-07 19:50 | 112 | 56 | 4583381 | 2609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE OPEN COD 112//CUTOUT BURNT ON POLE19-B-186//CUT OPEN PT AT POLE 19-20//COD 1 AT 1917 POLE 19-186 BAD CUTOUT REPLACED VER/CRB IDC XXXX
5950 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-09-05 13:18 | 2011-09-05 14:37 | 33 | 79 | H1158505-1 | 2607 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /DUE TO FLOODING IN THE AREA, WILL NOT BE ABLE TO CHECK THIS UNTIL TOMORROW MORNING PER DUTY SUPERVISOR//CENTER LINE FUSE IS OUT AT POLE 287-18. I AM PATROLLING LINE NOW. INSULATOR ON POLE 287-105 HAS BROKEN DOWN ON CENTER PHASE. I AM CALLING FOR HELP. WE WILL HAVE TO OPEN THE OTHER 2 PHASES ON POLE 287-18 WHEN HELP ARRIVES // CCC COD-4 ISO LF 37830287000018 // OPENED OUTSIDE PHASE FUSES @ 1318 TO MAKE REPAIRS (A & B 33 CUSTOMERS) 1437 ALL RESTORED FROM 4815181 VER/HFP L3/HFP IDC XXXX
5951 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-10-13 22:01 | 2010-10-13 23:20 | 33 | 79 | 59434-1 | 2607 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BROKE CUTOUT ON POLE 478-636 I CUT IN THE CLEAR,FEEDS STREETLIGHT THAT IS NOT BEING USED ANYMORE CAN WAIT TILL MORNING,,,,,,POWER RESTORED//COD 33// VER/DBM IDC XXXX
5952 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-06-17 17:59 | 2019-06-18 02:40 | 5 | 521 | 4528391 | 2605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva,replaced xfmr all cust restored @ 0240 please close ticket thanks.bt
5953 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2010-06-16 23:29 | 2010-06-17 10:20 | 4 | 651 | 50215-1 | 2604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD SECONDARY BUSHING ON 50KVA TRANSFORMER IN A 2 POT BANK OPEN BANK AT 12:20 HOLD TILL MORNING RELEASED BY CREW 078S07/J. HEMLEPP & CREW ON SITE. PL# IN FIELD TAGGED WRONG WILL CORRECT./ CUST. RESTORED @ 10:20//COD 4// VER/DBM
5954 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-01-16 07:26 | 2009-01-16 14:40 | 6 | 434 | 55579-1 | 2604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD TRANSFORMER CREW ENROUTE RELEASED BY CREW 074S02 COD-6 L3/HFP
5955 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-01 17:12 | 2018-02-01 19:45 | 17 | 153 | 4790261 | 2601 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failled on 77-A-36 i isolated trans cutout NTA trans is servin one customer that is disconnected crew can make repairs tomorrow may reach cutout with big bucket trk restoredpower at 19:45 send copy to Tim Hall 38820770A30275
5956 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-01-22 15:27 | 2016-01-22 17:37 | 20 | 130 | 4641801 | 2600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | *****SEE H4641801*** BAD CUT OUT ON POLE 227-293, B PHASE WILL OPEN A AND C PHASE TO REPLACE CUT OUT ( OPENED A&C @1715),,,B AND C PHASE CUT OUTS WHER BAD REPLACE BOTH../ BACK ON AT 1737/ ISO 37830227A10293/ COD 23/ VER/BOW AJB
5957 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2013-08-10 16:35 | 2013-08-10 19:55 | 13 | 200 | 4647061 | 2600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. CHANGING CUTOUT DUE TO A CHIP IN PORCELIN. REPLACED CUTOUT AND RESTORED @ 19:55. SH VER/CRB L/3 CRB IDC XXXX
5958 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-12-21 12:17 | 2020-12-21 14:10 | 23 | 113 | 4790691 | 2599 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | high side stepdown fuse melted out. refused and restored power at 1410
5959 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-05-06 11:34 | 2013-05-06 17:45 | 7 | 371 | 4076711 | 2597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT ON POLE 37830249B00079 (ENTERED MD) POLE # 37830249B00286 BURNT OFF, WILL HAVE TO REPLACE, NEED 40 CL 4 CAN WORK WITH TRUCK.---- POWER RESTORED AT 17:45 COD-7 ISO LF 37830249B00079 VER/HFP L3/HFP IDC XXXX
5960 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-06-14 16:54 | 2009-06-14 20:50 | 11 | 236 | H62988-1 | 2596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3402202 LINE DOWN BETWEEN POLE#18-54 AND 18-345 //PHASE A OUT ONLY//COD 22 //OPENED SWITCH 180-54 @ 1654, INTERRUPTING 11 MORE CUSTOMERS//WIRE BACK UP SOLID BLADE CLOSED IN, ALL CUST RESTORED @ 2050//NO TREES INVOLVED... CONDUCTOR APPEARS TO HAVE FAILED//ISO 37830018000054 MLR CREATED DUP FOR OPENING OF ADDITIONAL PHASES
5961 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-04-06 10:41 | 2019-04-06 14:37 | 11 | 236 | 4063651 | 2596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew req bad 50 kva single bushing, can use trucks in peopels bank parking lot on james hannah drive same as ticket number 4063551 Released by crew 078S06 COD 11 Released by crew 078S06 COD 11---complted---14:37---rmv L3/HFP sjg
5962 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2011-04-21 13:24 | 2011-04-21 15:00 | 27 | 96 | H61623-1 | 2592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONLY B PHASE - CENTER PHASE 27 CUSTOMERSTWO SPANS OF PRIMARY DOWN CREW ENROUTE./// OPENED OTHER 2 RECLS @ 1324 ALL RESTORED @ 1500 (A & C PHASE TOTAL 27 CUST) ISO RECL 37820197000098 FROM 61623-1 VER/HFP L3/HFP IDC 27 IS THE CORRECT COUNT ON BOTH ORDERS XXXX
5963 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-12-22 22:47 | 2017-12-23 03:35 | 9 | 288 | 4665011 | 2592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Pole 237-43 has loop burnt open, can lift ht on 237-63 to make repaires, 9 customers off. Linecrew required Released by crew 078S11/on site RM installing solid blade at 237-63 power on at 03:35 please close tic RM
5964 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-03-25 12:06 | 2016-03-25 17:30 | 8 | 324 | 4881781 | 2592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD , BURNED TOP OF POLE OFF. WE NEED A7200 CUTOUT AND LOWER EVERYTHING ON POLE RELEASED BY CREW 077S12. MADE REPAIRS AND RESTORED POWER AT 1730/ ISO 37830426D00035/ COD 8/ VER/BOW AJB
5965 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-07-05 18:10 | 2009-07-05 19:20 | 37 | 70 | 50520-1 | 2590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000202//SERVICER HAD TO OPEN RECLOSER TO SAFELY REPAIR A BAD CUTOUT AND ARRESTOR//COD 37//SEE ORDER 65900-1// VER/DBM AJBC ADDED PFC#. 42 ON OCR SEE 65900-1 FOR OTHER 5 CUST PREV OUT.
5966 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-07-09 15:52 | 2018-07-10 13:25 | 2 | 1293 | 4754631 | 2586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | underground primary line fuse is out, tried fuse and it blew, xfmr looks ok, possible bad underground Released by crew 077S02,,parked 19.9.UG primary cable and fused c/o, cable is bad. will work in morn. aprox 270 19.9kv cable..p.hicks Released by crew 077H09//underground primary line fuse is out, tried fuse and it blew, xfmr looks ok, possible bad underground Released by crew 077S02,,parked 19.9.UG primary cable and fused c/o, cable is bad. will work in morn. aprox 270 19.9kv cable..p.hicks //
5967 | Hazard | 3303902 | LESLIE | WOOTON | 2018-06-25 22:17 | 2018-06-26 12:39 | 3 | 862 | 4667011 | 2586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50kva 19.9 12/240v transformer, might reach with big bucket and mud boards, serves a church , can hold till morning..p.hicks Released by crew 077H09 changed transformer
5968 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-10-27 07:00 | 2010-10-27 14:42 | 13 | 462 | 65429-1 | 2586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830472000083, ISOLATED AT 38830472000051, LINE CREW REQUIRED, NEED 45-4 POLE, CUTOUT, TRUCK OK. 10KVA FEEDING 4 HOUSES, LINE FUSE CLOSED AT 09:00. CREW ENROUTE TO REPAIR VER/KEP L3/KEP IDC XXXX
5969 | Pikeville | 3421001 | BREAKS | CITY | 2021-01-09 08:45 | 2021-01-09 12:40 | 11 | 235 | 4857971 | 2585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 KVA xfm on open delta bank 7 volts on one leg @ lighting pot///Will need line crew and flaggers////// Opened bank up @ 09:58 Released by crew 074S02// POWER RESTORED @ 12:40
5970 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-03-25 16:21 | 2018-03-25 17:37 | 34 | 76 | 4103121 | 2584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | restored 1737 // can close mwl fuse on pole 832-219.. fuse melted out under load. closed fuse back in at 17:37.. up fuse size to 25T per engineer.. complete rn
5971 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-11-28 07:11 | 2010-11-28 11:45 | 16 | 274 | 60223-1 | 2584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | RELEASED BY CREW 077S05 MADE REPAIRS ..RESTORED POWER AT 11..45/VER/CRB IDC XXXX
5972 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2008-01-16 02:19 | 2008-01-16 07:42 | 8 | 323 | 57027-1 | 2584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3003703 #4 COPPER PRIMARY DOWN ON POLE 308-59 TO 308-109 , TWO SPANS. NEEDS LINE CREW. TRUCKS OK. RELEASED BY CREW 078S01/ REFUSED CUTOUT, DOOR HANGING DOWN// ISO 38830308000005// COD 8 //VER/TOM IDC XXXX
5973 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-05-18 10:50 | 2022-05-18 12:06 | 34 | 76 | 4906551 | 2584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door dropped open due to cap on door loose, burning under load, replaced door with new door, all good..
5974 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-02-07 03:51 | 2019-02-07 08:38 | 9 | 287 | 4761041 | 2583 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held in accordance with KPCO late night callout guidelines.same as 4761051 ¦¦ ENTERED MD COD-9 TOTAL
5975 | Pikeville | 3421001 | BREAKS | CITY | 2008-01-22 20:15 | 2008-01-23 00:50 | 29 | 275 | 59028-1 | 2575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3400901//FOUND BAD 6" DISC INSULATOR - DENNIS TO GET SOMEONE TO BRING ONE OUT// ISOLATER @ POLE 37820243A00142 - CLOSED BACK IN RECLOSER 1013 @ XXX ON POLE 37820243B00254 //RESTORING ALL BUT 2 CUSTOMERS ON ISOLATED TRANSFORMER// VER/PDP IDCC CNT2 STP MISSING XXXX
5976 | Pikeville | 3413401 | GARRETT | GARRETT | 2013-11-10 08:57 | 2013-11-10 10:40 | 25 | 103 | 4025561 | 2575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 25T OUT DUE TO BAD ARRESTER ON POLE 65-195 . NEED TO PUT THIS IN ABNORMAL NOT TRUCK ACCESSIBLE POLE GROWED UP BAD WITH TREES SEND COPY TO ROW//COD 25// AED ENTRY CREATED//EMAILED TO FORESTRY// VER/DBM L3/HFP IDC XXXX
5977 | Hazard | 3302704 | HAZARD | KENMONT | 2012-04-20 18:55 | 2012-04-20 20:52 | 22 | 117 | 4691331 | 2574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4691161 CREW HAD TO OPEN CUTOUT TO SAFELY REPLACE DEFECTIVE CUTOUT OPENED @ 1855 // COD-13 ISO LF 37830296C20466 VER/HFP L3/HFP IDC XXXX
5978 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-09-11 08:18 | 2014-09-11 12:12 | 11 | 234 | 4488051 | 2574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 242-20 BAD CUTOUTBAD CUTOUT ON POLE 242-20 ISO 37820242000298/// COD 11// VER/BOW AJBC CDC96
5979 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2020-12-01 16:09 | 2020-12-01 20:03 | 11 | 234 | 4736931 | 2574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | wire down, isolated taged and grounded at fuse pole Released by crew 077S07..RESTORED POWER AT 20:03
5980 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-06-20 12:54 | 2015-06-20 14:00 | 39 | 66 | 4617101 | 2574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW OPENING RECLOSER 209-6 TO MAKE REPAIRS/RELATED TO OUTAGE 4617101/OPENED 1254 CLOSED 1400/COD 95+39 AJB
5981 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-03-04 17:05 | 2008-03-04 18:44 | 26 | 99 | 52882-1 | 2574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409302// CUTOUT BROKE ON POLE 38830905000048. REPAIRS UNDERWAY. REPAIRS COMPLETE. 65T LINE FUSE WAS BLOWN ON POLE 38830905000036. XFMR ON THIS POLE IS NOT PROTECTED BY IT. ALL CUSTOMERS RESTORED. SH ????? VER/HFP IDC XXXX
5982 | Whitesburg | 3314401 | MAYKING | ERMINE | 2010-01-24 21:17 | 2010-01-25 11:35 | 3 | 858 | 58972-1 | 2574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 428-322. INSULATOR & LOOP BURNT INTO ON POLE 426-235 WILL 2 R/WAY CREWS & 4 MAN LINE CREW IN DAY LIGHT RELEASED BY CREW 077S11// VER/HFP L3/HFP IDC XXXX
5983 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-03-12 21:08 | 2016-03-13 00:06 | 22 | 178 | 4839691 | 2572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 423-115, BAD CUTOUT ON POLE 399-35, ISOLATED CUTOUT RESTORED POWER AT 23:02..REPLACED CUTOUT RESTORED POWER AT 00:06.. RELEASED BY CREW 077S11 VER/KEP AJB
5984 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-09-30 06:07 | 2008-09-30 10:24 | 10 | 257 | 52100-1 | 2570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501//I GOT BAD CUTOUT ON POLE 54-63 AND NETURAL WIRE DOWN ON POLE 54-46. THIS IS LONG SPAN OF ROTTEN #4 AL WIRE. I THINK THAT IT WOULD BE BETTER TO LEAVE RECLOSER OPEN UNTIL WE GET WIRE UP. WIRE IS DOWN THROUGH SEVERAL CHICKEN LOTS AND FENCES.//VER/CRB IDC XXXX
5985 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2021-10-03 18:59 | 2021-10-04 09:15 | 3 | 856 | 4312641 | 2568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//cutout on arm//too close to change//no truck//need line crew//need hard cover up and 7200 cutout// Released by crew 079S01. CREW ON SITE
5986 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-02-24 19:23 | 2021-02-26 14:10 | 1 | 2567 | 4246391 | 2567 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMER CUOUT ON POLE 621-231
5987 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-10-04 09:49 | 2018-10-04 14:41 | 9 | 292 | 4196111 | 2564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | pole 38830117C00307 transformer fuse blown, causing line fuse on pole 117c71 to blow. Line fuse back in @ 14:33. xfmer back in @ 14:41. pls close. tre
5988 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-10-19 16:24 | 2020-10-19 18:26 | 21 | 122 | 4568641 | 2562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 65t open @ 20-4507, #2 al pri down between 20-1554 to1553. no trk. access 115 bellefonte dr.
5989 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-01-04 05:50 | 2009-01-04 07:52 | 21 | 122 | 51179-1 | 2562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3309001// LINE FUSE OUT ON POLE 393C - 1 == BAD DEAD END INSULATOR ON POLE 369-138 CHANGED INSULATOR == REFUSED LINE == POWER OK VER/KEP L3/KEP IDC XXXX
5990 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-05-23 21:51 | 2011-05-24 12:05 | 3 | 854 | 4149871 | 2562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//BAD 25KVA 19.9// NO TRUCK// CREW REQUIRED// THIS IS BEHIND THE COTTAGES RELEASED BY CREW 074H14/ REPLACED TRANSFORMER AN CLOSED AT 1205 VER/HFP L3/HFP
5991 | Hazard | 3310502 | HADDIX | CANOE | 2017-07-30 17:50 | 2017-07-30 23:56 | 7 | 366 | 4208121 | 2562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUSE OPEN ON POLE 51-64 . PRIMARY DOWN ON POLE 51-64 . WIRE ROTTEN & BROKE . NEEDS REPLACED 414 SPAN . RELEASED BY CREW 075H04 VER/ARN SJG
5992 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-06-19 19:47 | 2018-06-20 10:00 | 3 | 853 | 4624961 | 2559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 7200, 25kva trk to pole Released by crew 078S07//WILL WORK IN DAYLIGHT OF JUNE 20TH, WEDNESDAY REPLACED KVA POWER RESTORED AT 10:00
5993 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-08-31 09:16 | 2021-08-31 14:00 | 9 | 284 | 4183611 | 2556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TOWER SITE EXPERINCEING VOLTAGE ISSUES AGAIN Bad 25 Kva xfmr - eliminated xfmr and converted to two xfmr bank. Restored @ 14:00. sh
5994 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-01-21 07:35 | 2008-01-21 13:40 | 7 | 365 | 58295-1 | 2555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER ON POLE 167-144 IS BURNED UP. TIM HALL WILL SEND A CREW TO CHANGE IT LATER TODAY.//3401002. RELEASED BY CREW 074S01.STEVE RAY AND CREW HAS ARRIVED TO CHANGE XFMR.//VER/CRB IDC XXXX
5995 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-03-09 08:40 | 2014-03-09 09:15 | 73 | 35 | 4462431 | 2555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENED RECLOSERS AT POLE 212-A-305 TO SAFELY CLOSE OLD N.O. GOAB AT POLE 188-B-83 // CLOSED RECL & MIDDLE PH SW ARCING, RE-OPENED RECL // //VER/GAH IDCC CCO XXXX
5996 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-06-19 07:36 | 2008-06-19 09:04 | 29 | 88 | 50623-1 | 2552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED BAD CUTOUT AND RE-FUSED 30T LINE FUSE. SH VER IN PO - HFP VER/HFP AJB
5997 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-02-12 13:02 | 2020-02-12 14:47 | 319 | 12 | 4396621 | 2552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DOL 992224 //outage necessary to replace broken cross-arms on pole 852-196//will transfer customers to alternate feed but this requires a short outage to do//outage will last approx 15 min and will require a separate short outage later to put ckts back to normal feed //cod 319''
5998 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-08-15 16:35 | 2016-08-15 19:05 | 17 | 150 | 4782921 | 2550 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RISER BURNT INTO OPEN XFMR @ 1845 REPAIRS MADE XFMR FUSE IN @ 1905 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP
5999 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-10-02 08:15 | 2009-10-02 12:30 | 10 | 255 | 63989-1 | 2550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 72,00 XFORMER ON POLE 185-122. TRUCKS TO POLE. RELEASED BY CREW 078S01----CREW ON SITE,WILL HAVE ROAD COMP. BLOCKED--//VER/CRB IDC XXXX
6000 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-02-13 08:36 | 2008-02-13 14:40 | 7 | 364 | 62287-1 | 2548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401702//PART OF 62162-1//SERVICER OPENED LINE FUSE TO ISOLATE POLE FIRE//1500 FETR//COD 7// VER/DBM IDC XXXX
6001 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-06-18 22:27 | 2015-06-19 00:05 | 26 | 98 | 4605081 | 2548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | GOT A LOOP BURNT OPEN ON POLE 38830645000054/ OPENING RECLOSER IN OUTAGE 4605081 IN ORDER TO PUT LOOP BACK TOGETHER/ ISO 38830645000054/ COD 61 LOOP BURNT INTO ON 645-54 WILL HAVE TO OPEN RECLOSER ON 645-228 PLACE GROUND & TAG T297 AT0005 CLOSE TICKET/ OPENEDE RECLOSR 1142 AND CLOSED 1205/ VER/BOW AJB
6002 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-07-10 20:38 | 2012-07-10 23:40 | 14 | 182 | 4677361 | 2548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50KVA XFMR IS BAD. MAYNARD & NEWSOME 50KVA XFMR IS BAD. CREW ENROUTE TO REPLACE.50KVA XFMR IS BAD. CREW ENROUTE TO REPLACE. REPLACED XFMR AND RESTORED @ 23:40. SH COD-14 ISO TF 38830809C10060 IDC XXXX
6003 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-11-21 13:53 | 2022-11-21 14:45 | 49 | 52 | 4169231 | 2548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 14:45
6004 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-07-23 08:53 | 2008-07-23 11:07 | 19 | 134 | 58525-1 | 2546 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S08 HOT TAP BURN OFF IN BASKET REPLACE HOT -LINE CLAMP COMPLETE VER/KEP IDC XXXX
6005 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2021-06-08 20:33 | 2021-06-09 07:09 | 4 | 636 | 4692581 | 2544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse open @ 37830163B00123.// Will be patrolling// Wire off pole @ 37830162000036//Wire not broke// Need 7200 insulator and pole top pin// Crew required// No grounds Released by crew 074S11
6006 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-04-19 06:22 | 2010-04-19 11:40 | 8 | 318 | 64867-1 | 2544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 34725184 /// CENTER B PHASE (8 CUST) WIRE BROKE AT INSULATOR ON POLE 97-66. CUTOUT LEAD IS HOLDING WIRE UP. IT DID NOT BLOW LINE FUSE. POWER IS OFF FROM POLE 97-66 ON CENTER PHASE UP HOLLOW. TIM HALL IS SENDING HELP. WE WILL HAVE TO OPEN ALL 3 PHASES ON POLE 97-48 WHEN WE REPAIR WIRE. WE ONLY HAVE ABOUT 5 PEOPLE OUT AT THIS TIME. I OPENED ALL 3 LINE FUSES ON POLE 97-48 AT 10:35. (11 CUST) WE COMPLTED WORK AND CLOSED THEM BACK IN AT 11:40. SEE H64867-1 VER/HFP L3/HFP IDC XXXX
6007 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-03-15 12:20 | 2012-03-15 13:37 | 33 | 77 | 4582461 | 2541 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY WIRE RUSTED INTO AND LET POLE #29-139 LEAN OVER AND PRIMARY IN TREES , GOING TO TIE POLE OFF TO TREE NEED TO SEND DOUG CHRISTIAN A JOB TO BURRY ANCHOR ON POLE 29-2//COD 33//EMAILED TO D CHRISTIAN// VER/DBM IDC XXXX
6008 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-02-13 09:34 | 2014-02-13 18:02 | 5 | 508 | 4380691 | 2540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUS OUT ON POLE 1125-189.PATROLLING NOW. FOUND NEUTRAL DOWN ON POLE 1125B-91.MADE REPAIRS THERE.NEUTRAL BACK UP.CLOSED FUSE AT 18:02.SERVICE RESTORED. VER/KEP
6009 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-06-24 06:04 | 2017-06-24 20:10 | 3 | 846 | 4035051 | 2538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 12KV 25KVA CSP, ORIGIONAL TICKET LAST NIGHT 4022921 RELEASED BY CREW 078S07 //IDC 39831099D26518 SJG STEP2 TON20:10 CNT87 (DELETED)
6010 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-12-06 14:23 | 2017-12-06 19:05 | 9 | 282 | 4626701 | 2538 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//THEY CKD BREAKERS// Linecrew required need permanent wood poletop,pl38830499000076 burnt off//CALLED CUST//THEY CKD BREAKERS// Linecrew required need permanent wood poletop,pl 499-76 burnt off, Crew will need to ground&tag themselves//,repairs made all cust restored @1905 please close ticket thanks.bt/ ISO 38830523000031/ COD 9
6011 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-08-24 01:51 | 2017-08-24 02:34 | 59 | 43 | H4294901 | 2537 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | C PHASE CONDUCTOR HAS BURNED INTO AT THE STIRUP ON POLE 38821038B00114. I WILL NEED TO OPEN A&B PHASE RECLOSER TO MAKE REPAIRS. OPENED A&B RECLOSERS AT 01:51. CLOSED AT 0234/ ORGIANNAL 57 ADDITONAL 59// VER/ ADH SJG CHANGED OUTAGE# H4294931, SJGC TOF00:51
6012 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-01-03 07:38 | 2014-01-03 12:55 | 8 | 317 | 4222961 | 2536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT CLAMP BURNT AT 384-102 CLOSED@ 1255 TO REPLACE BAD HOT LINE CLAMP VER/CRB IDC XXXX
6013 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-06-08 15:28 | 2021-06-08 16:33 | 39 | 65 | 4689671 | 2535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 68-268. load side basket burnt off line.. new basket, recloser restored @ 16:33
6014 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-12-09 10:59 | 2022-12-09 14:00 | 14 | 181 | 4245771 | 2534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required 20t
6015 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-11-25 22:31 | 2020-11-26 01:00 | 17 | 149 | 4723801 | 2533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced and 15t
6016 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-04-03 20:02 | 2015-04-04 17:07 | 2 | 1265 | 4267681 | 2530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED FIBERGLASS POLE EXTENSION PULLED OVER ON 35A20 POLE TOP ROTTEN WIRE IS SAGGED BACK TOWARD POLE35A12 WIRE IS DOWN BETWEEN POLE 35A21 &35A22 NTA UP ON HILL VER/HFPF L3/HFP
6017 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-07-22 19:55 | 2019-07-23 09:25 | 13 | 810 | 4769391 | 2530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad CSP Xfmr on pole 1146-191. need 3 man line crew, 7200 25 kva, cutout and bracket.Bad CSP Xfmr on pole 1146-191. need 4 man line crew, 7200 25 kva, cutout and bracket. no truck approach. need manual row to clear path up hill and around pole LF OFF @ 0805 ON @ 0815Bad CSP Xfmr on pole 1146-191. need 3 man line crew, 7200 25 kva, cutout and bracket.Bad CSP Xfmr on pole 1146-191. need 4 man line crew, 7200 25 kva, cutout and bracket. no truck approach. need manual row to clear path up hill and
6018 | Hazard | 3309002 | JEFF | JEFF | 2011-02-17 06:19 | 2011-02-17 14:45 | 5 | 506 | 58363-1 | 2530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSF == NEED LINE CREW AND ROW CREW == CALLED GLEN FOR LINE CREW RELEASED BY CREW 077S03 OPENED TAP @ 37830345C00177 TO ALLOW THEM TO SAFELY REPLACE TR @ 13??BAD 25 KVA TRANSF == NEED LINE CREW AND ROW CREW == CALLED GLEN FOR LINE CREW RELEASED BY CREW 077S03 OPENED LINE FUSE AT 13.05 CLOSED AT 14.45 SEE H58363-1 FOR FUSE OUTAGE FOR 3 VER/HFP L3/HFP IDC DCMT NOT BY TRUCK XXXX
6019 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-06-05 18:05 | 2008-06-05 21:55 | 11 | 230 | 58556-1 | 2530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT - LIGHTNING OR POSSIBLE BAD TRANSFORMER. 11-12 CUSTOMERS OUT. RELEASED BY CREW 078E04----CUTOUT BURNTUP,WILL REPLACE C.O. ---//3001203//VER/CRB
6020 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-06-30 20:17 | 2014-07-01 01:33 | 8 | 316 | 4176651 | 2528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN 38830955B00539// WILL REFUSE///BAD XFMR// NEED 1 25KVA // 2 BUSHING // 7200// 1 MAN //BIG BUCKET/// POWER RESTORED @ 1:33
6021 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-02-17 09:41 | 2013-02-17 11:00 | 32 | 79 | 4824781 | 2528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THE HOT LINE CLAMP ON THE LINE FUSE WAS BURNED OFF , I REPLACED IT AND MADE THE LINE BACK HOT VER/KEP IDC XXXX
6022 | Hazard | 3303901 | LESLIE | HYDEN | 2018-01-13 01:43 | 2018-01-13 12:15 | 4 | 632 | 4741251 | 2528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Gilley will check at daylight due to location// CUTOUT BAD pole 37830290000050//Gilley will check at daylight due to location// CUTOUT BAD Released by crew 077S01
6023 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-12-22 09:22 | 2008-12-22 15:23 | 7 | 361 | 62376-1 | 2527 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE TO CHANGE IT. RELEASED BY CREW 076S02//3409302// CREW ON SITE CHANGING TRANSFORMER TCM///VER/CRB L3/KEP IDC XXXX
6024 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-04-05 18:24 | 2009-04-05 20:05 | 25 | 101 | 65491-1 | 2525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT OUT REPLACED DOOR AND 6T FUSE EVERYTHING OK. ROW ON FROZEN FORK OF JACKS CREEK NEEDS CUT. SEND COPY TO JASON BRADSHAW PIKEVILLE.//COD 25// VER/DBM AJB
6025 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-12-27 17:59 | 2015-12-28 04:30 | 4 | 631 | 4565121 | 2524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ POLE 182B43782 NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05.. CREW ON SITE ETR 04:45 BROKEN CUTOUT IS ON POLE 182-3783.. CUTOUT CHANGED AND CUSTOMERS RESTORED AT 04:30 PLEASE CLOSE TICKET CY VER/TOM L3/TOM AJB
6026 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-05-10 15:06 | 2021-05-10 19:46 | 9 | 280 | 4572261 | 2520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse is open @ 236-197(ASSESSING CONDITION)We have a broke cutout @ 236-29,Will have to climb pole to make repairs
6027 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-01-08 08:20 | 2014-01-08 13:00 | 9 | 280 | 4257491 | 2520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CUST BREAKER ON LOT 15 WAS OUT AND BAD CONNECTION ON DISCONNECT MAY REPAIR EVERYTHING OK. BUT HAD TO OPEN TRANSFORMER AT 08:20 DUE TO RISER WIRE SMOKING. CREW ON THE WAY ROBBIE BLAIR TO REPLACE RISER WIRE EST RESTORATION 13:00 RELEASED BY CREW 074S11 VER/CRB L3/HFP IDC XXXX
6028 | Hazard | 3303902 | LESLIE | WOOTON | 2015-08-05 11:18 | 2015-08-05 12:30 | 35 | 72 | 4980481 | 2520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO OUTAGE 4979111, OPENING STEP DOWN 510-157/OPENED 1118 CLOSED 1230// VER/ ADH L3/HFP XXXHFP AJBC TOF
6029 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-24 00:30 | 2011-06-24 01:40 | 36 | 70 | H4403331 | 2520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 140-130 WIRE BURNT OPEN 116-708 80T BLOWN CALL DANNY FOR INFO. RELEASED BY CREW 078S08//PHASE "A" LOOPS OPEN ON 140-130 //COD 39//PHASE C STEPDOWN OPEN ON 116-708//COD 73(TOTAL 112)//@ 1230 OPENED OTHER TWO STEPDOWNS (COD +36)//MADE REPAIRS AND RESTORED ALL CUSTOMERS @ 0140// SJG CREATED H4403331 IDC XXXX
6030 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-08-11 17:14 | 2010-08-11 21:03 | 11 | 229 | 52764-1 | 2519 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED CREW--CUSTOMER SAID NO TRUCKS--COULD USE PADS AN GET TO POLE--75KVA TRANSFORMER NEEDS NEW RISERS AND LOAD SPLIT UP ON LASH CABLE RELEASED BY CREW 078S07.. CONNECTIONS BURNED INTO ON XFMR RISERS, REWORKED .. POWER RESTORED AT 21:03//VER/CRB IDC XXXX
6031 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-05-13 19:50 | 2014-05-13 22:18 | 17 | 148 | 4694561 | 2516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOW SIDE STEPDOWN F IS OUT,WILL PTRL/////////REPLACED BAD CUTOUT 29-10/////RE-FUSED AND RESTORED COD-17 ISO LF 37820004000109 VER/HFP L3/HFP IDC XXXX
6032 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-08-10 14:23 | 2018-08-10 17:00 | 16 | 157 | 4938021 | 2512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired connections fmer off @ 16:45, on @ 17:00/ ISO 38830020D47567/ COD 16 L3/HFP
6033 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2008-03-29 06:21 | 2008-03-29 11:00 | 9 | 279 | 61860-1 | 2511 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400701/ POLE TOP BURNT OFF / CALLED FOR CREW TO HELP LOWER LINE ON POLE / //// VER/TOM IDC XXXX
6034 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-12-12 03:50 | 2012-12-12 12:12 | 5 | 502 | 4462811 | 2510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #2 INSULATED OPEN WIRE DOWN ACROSS R/R TRACKS DENNIS WILL HAVE CREW REPAIR THIS 1ST THING IN THE TODAY. WIRE IS DOWN BETWEEN 38831027C00104 & 38831027C00102.WIRE IS ROLLED UP @ POLE 102 ***DENNIS MASSEY TO ARRANGE FOR CREW AFTER DAYLIGHT // WAITING ON CSX RR XING SERVICER BEFORE WORK CAN PROCEED//REPAIRS MADE, POWER RESTORED// NOTE TO DALE, I ONLY CLOSED THIS TICKET, NOT AURE HOW MANY WAS ACTUALLY OUT VER/DBM
6035 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-05-11 10:40 | 2008-05-11 13:53 | 13 | 193 | 60137-1 | 2509 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP CAME LOSE// OPENED AT FUSE POLE 296-1287 AT 13:34// CLAMP LOOSE ON POLE 37830296000324 RESTORED COMPLETE AT 13:53 VER/KEP IDCC ICCCF, CNT1 XXXX
6036 | Hazard | 3310502 | HADDIX | CANOE | 2020-07-23 16:36 | 2020-07-23 18:48 | 19 | 132 | 4219451 | 2508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Power restored @ 18:48
6037 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-09-05 14:14 | 2019-09-05 16:08 | 22 | 114 | 4984561 | 2508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Load side of S/D open @1100-83, patrolling. Trans. pole 1100-218 has rotted off and fell over, going to isolate this tap @1100-84, this will take a linecrew with a 40-4 pole, 25kva 7200 trans., cutout and bracket, and dead ends for primary and neutral and 1/0 secondary, will also need a trans.sack . Service has been inactive for over a year @1100-218, going to clean up pole and trans. and replace pole @ later date. Got S/D back in @1100-218 @1608. L3/HFP
6038 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2012-06-17 17:40 | 2012-06-17 17:46 | 418 | 6 | 4923781 | 2508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED STA BREAKER TO CLOSE SWS AT POLE 272-2 ON P.O. TROUBLE ORDER 4922341 //VER/GAH DKG OK THIS OUTAGE FOR CUST THAT ARE RESTORED FROM BRK TO SWS AT POLE 272-2 THE SECOND TIME IDC XXXX
6039 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-12-09 14:15 | 2022-12-09 17:14 | 14 | 179 | 4246621 | 2506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | crew required bad insulator or arrestor may need to put 2 fuses instead of 1/bring fault indicators also/send to grayson Released by crew 078S03. installed second 20t lf on pole 246-26 both fuses in @ 17:14 complete lg
6040 | South Williamson | 3411401 | DEWEY | INEZ | 2012-09-03 01:43 | 2012-09-03 04:42 | 14 | 179 | 4998301 | 2506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE. NO REPLACEMENT ON TRUCK - GOING TO PICK ONE UP. REPLACED CUTOUT AND CLOSED 40T FUSE @ 4:42. SH COORDINATION ISSUE VER/KEP IDC XXXX
6041 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-09-21 08:28 | 2009-09-21 18:05 | 12 | 577 | 56281-1 | 2505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40/5 POLE CREW REQUIRED IN BACK YARD NO TRUCKS/ISOLATED ON 270-293 3 CUSTOMERS WILL BE OFF /LINE FUSE BACK IN AT 0954 HRS 3 CUSTOMERS STILL OFF.//VER/CRB IDC XXXX
6042 | Whitesburg | 3401301 | FLEMING | NEON | 2010-01-17 01:17 | 2010-01-17 04:04 | 15 | 167 | 55097-1 | 2505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD ON POLE 331-91 I WILL NEED A CUTOUT AND ONE MAN TO REPAIR THIS REPLACED CUTOUT VER/ARN IDCC CNT15 PN223 XXXX
6043 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-07-20 20:23 | 2008-07-21 17:15 | 2 | 1252 | 54766-1 | 2504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 162-218 ROTTEN AT GROUND LINE THIS IS A INLINE PRIMARY POLE EXITING 35-6 NO TRUCK TO POLE CROSS CREEK RELEASED BY CREW 078E04/DHE CREW LEWIS MAYNARD IS ON THIS JOB WITH C. TACKETT AS GUIDE.//3003701//VER/CRB IDCC CNT1 XXXX
6044 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-05-12 04:24 | 2010-05-12 09:26 | 22 | 302 | 60145-1 | 2504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3417602//, ON SITE, PATROLLING LINE// LEFTED HOT TAP ON POLE 965-55 TO ISOLATE TROUBLE ON POLE 965-143.3417602//, ON SITE, PATROLLING LINE, POLETOP BURNT OFF AT POLE#965-A-143, CLEARED WITH HOT TAP AT POLE# 965-A-55, CLOSED FUSE AT POLE# 965-A-11 AT 0559, SEND TO R MARCUM TO MAKE REPAIRS RELEASED BY CREW 080S01// SEND TO RANDEL MARCUM. MADE REPAIRS AND RESTORED SERVICE AT 09:26. //VER/GAH IDC XXXX
6045 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-06-17 17:32 | 2018-06-17 22:45 | 8 | 313 | 4612381 | 2504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEF 1057-104 IS OUT, WILL PTRL. NOTHING EVIDENT, WILL RE-FUSE. FUSE BLEW. FOUND BAD CUTOUT ON 1034-19, WILL REPLACE IT AND TRY F AGAIN///////////RE-FUSED & RESTORED//cod 8
6046 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2021-11-18 19:31 | 2021-11-19 11:46 | 14 | 975 | 4107071 | 2502 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 Xfrm on pole 353c-132. Need 7200 kva transformer and cutout complete. Will be changing out tomorrow due to unsafe conditons tonight. Released by crew 077H15///Opened tap at 37830353C00131 (12 COD) to make repairs at 1100 and restored at 1146
6047 | South Williamson | 3411401 | DEWEY | INEZ | 2015-07-06 16:24 | 2015-07-06 23:21 | 6 | 417 | 4733401 | 2502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER FUSE BLEW ON POLE 768-241///BROKEN XFMER CUTOUT ON POLE 768-241///BAD CUTOUT HAS ALSO BLOWN LINE FUSE ON POLE 744-12///CLOSED LINE FUSE ON 744-12 AT 23:21///COMPLETE BR/ ISO 38830744D00012/ COD 6
6048 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-08-29 15:32 | 2013-08-29 15:50 | 139 | 18 | H4719311 | 2502 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE OUT COD 92 STIRRUP AND HOT LINE CLAMP BURNED UP ON HIGH SIDE OF THE STEPDOWN TRANSFORMER A PHASE. CREW ENROUTE. OPENED OTHER PHASES AT 15:32 (139) CUSTOMERS.STIRRUP AND HOT LINE CLAMP BURNED UP ON HIGH SIDE OF THE STEPDOWN TRANSFORMER A PHASE. CREW ENROUTE. RELEASED BY CREW 074S02 ALL POWER ON 15:50 MAKE DUPLICATE ORDER FOR B&C PHASES VER/SEF L3/HFP HFPC CDC88 IDC XXXX
6049 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-04-30 04:56 | 2014-04-30 09:06 | 10 | 250 | 4650021 | 2500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW TRUCK TO POLE NEED FLAGGING CREW RELEASED BY CREW 078S07 OUTOUT WAS FIRING UP WHEN CREW ARRIVED AND HAD TO ISOLATE QUICKLY RESTORED AT 9:06//COD 10// VER/DBM IDC XXXX
6050 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-06-02 09:08 | 2015-06-02 15:05 | 7 | 357 | 4499691 | 2499 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 145-253. CUTOUT HAS BROKEN INTO. I TALKED TO STEVIE RAY AND HE SAID HE WOULD GET A CREW HERE AS SOON AS HE COULD. THIS IS C PHASE. RELEASED BY CREW 074S01/ ISO 37820145C10253/ COD 7/ VER/BOW
6051 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-06 10:51 | 2014-01-06 13:18 | 17 | 147 | 4236231 | 2499 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CREWS OPENED SWITCHES IN ORDER TO REPAIR LOOPS ON OUTAGE 4231561//COD 17// VER/DBM IDC XXXX
6052 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-03-13 16:18 | 2010-03-13 23:14 | 6 | 416 | 66544-1 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE ON 195-11, REPLACED POLE 40 CLASS 4CREW REQUIRED 40/4 POLE BURNT OFF TRUCKS OK 4 CUSTOMERS OUT//WR#34242040/ FIRST TICKET NEVER WOULD COME THROUGH DDC MADE NEW TICKET RELEASED BY CREW 078S10//VER/CRB IDC XXXX
6053 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-12-06 15:29 | 2022-12-06 17:13 | 24 | 104 | 4234961 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | The line fuse on pole 465-5 was open with a bad arrester on a CSP XFMR on pole 465-30. I cut the arrester in the clear and restored power at 17:13.
6054 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-06-09 22:28 | 2011-06-10 12:20 | 3 | 832 | 4281361 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN// BAD 19.9 15 KVA XFMR // THIS NEEDS TO BE CHANGED TO A 25 KVA// CUTOUT & L.A NEEDS CHANGED ALSO//CREW REQUIRED// CAN USE TRUCK// RELEASED BY CREW 074H14// I AM ON SITE. WAITING FOR CREW TO ARRIVE. MADE REPAIRS AND CHECKED VOLTAGE AND RESTORED POWER AT 12:20 TIM MCCOY//COD 3// VER/DBM IDC XXXX
6055 | Whitesburg | 3314401 | MAYKING | ERMINE | 2017-05-13 22:33 | 2017-05-14 05:29 | 6 | 416 | 4796761 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TR @ 1220 CLOSED @ 1237
6056 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-12-06 07:38 | 2009-12-06 11:06 | 12 | 208 | 61100-1 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP STS WORK REQ # 32953208 //BAD 37.5 TRANSFORMER--CALLED L MCARTY--GOING TO INSTALL 50 KVA-- MISMAPPED -CORRECT POLE# FOR TRANSFORMER 38830046B12238 APX 12 CUSTOMERS ON TRANSFORMER RELEASED BY CREW 078S07 ENTERED MD...HFP L3/HFP IDC XXXX
6057 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-05-12 04:54 | 2008-05-12 11:50 | 6 | 416 | 62378-1 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE , CORRECTION, POLE 278-99//3308402//VER/CRB IDC XXXX
6058 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-10-31 18:47 | 2009-10-31 20:05 | 32 | 78 | 53952-1 | 2496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 20-7782 BURNT OFF TEP. FIX SEND TO TEC. FOR JOB VER/KEP L3/KEP IDC XXXX
6059 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-06-19 21:12 | 2011-06-21 14:46 | 1 | 2494 | 4346851 | 2494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING. TALKED WITH CUST, OKAY TO CHECK IN THE A.M., WILL HAVE TO BE WALKED OUT, FEEDS TOWER & SHOP. RECLOSER OPEN AT POLE 306-211. I PUT RECLOSER IN AT 11:45 IT STAYED ABOUT FIVE MINUTES AND CAME BACK OUT I FOUND TWO INSOLATORS BLOWN OFF POLE NO.306-247 , I WILL ISOLATE THAT PHASE AT POLE NO.306-169 ALSO I CUT LOOPS ON ALL THREE PHASES AT POLE NO.306-270 AND CLOSED RECLOSER IN AT 17:55, COAL CO. STILL OUT OF POWER, CREW NEEDED RELEASED BY CREW 077S12OPENED RECLOSER//VER/CRB
6060 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-10-07 22:20 | 2014-10-07 23:13 | 47 | 53 | 4569651 | 2491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE DUE TO OUTAGE ON 4568461, REPLACING CUTOUT NO TRUCKS VER/KEP L3/HFP AJB
6061 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-02-07 23:05 | 2019-02-08 00:28 | 30 | 83 | 4766221 | 2490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 100 sunset st reports all out heard loud noise and saw sparks, bad 19.9 cutout on pole 205-16, line fuse blown on 205-214 ¦¦ L3/HFP
6062 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-02-12 19:32 | 2009-02-14 13:02 | 1 | 2490 | 58529-1 | 2490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | THE XFMR FUSE IS OPEN AT MS MCCOYS HOME. WHEN POWER WAS RESTORED TO CUSTOMERS ON CANEY BRANCH TODAY MS MCCOYS POWER REMAINED OFF. NEED TO REPLACE BLOWN ARRESTER AND REFUSE XFMR FUSE. RELEASED BY CREW 074E08, ARRESTER OK, BAD CUTOUT, REPLACING IT//COD 2
6063 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-09-11 12:21 | 2010-09-11 20:39 | 5 | 498 | 65509-1 | 2490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36839012 // TOP OF POLE BURNT OFF, BELIEVE WE CAN LOWER THIS. LINE FUSE BLOWN. NEED 7200 C/O AND ARRESTOR AND BRKT.//// LOWERED PRIMARY , C/O, ARRESTOR AND BRKT. POWER RESTORED. VER/HFP L3/HFP IDC DCMT XXXX
6064 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2009-06-24 13:53 | 2009-06-25 10:38 | 2 | 1245 | 56266-1 | 2490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 30447108 // CUST HAS MADE REPAIRS TO THEIR POLE & EQUIPMNT......SERVICE NOW REHOOKED.....BUT..... XFRMER IS BAD HERE.......NEED 15 KVA 7.2 KV....CLOSE THIS TICKET OUT AND GENERATE NEW TICKET FOR CREW......RANDAL MARCUM SAYS S WMSON CREW WILL TAKE CARE OF ON 06/25/09...THIS IS JUST FOR A SMALL SAWMILL WHICH IS CURRENTLY NOT RUNNING....THANX JRV....06/24/09 COD-2 ISO TR 37820081D00115 IDC XXXX
6065 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-02-01 10:43 | 2008-02-01 12:15 | 110 | 92 | 63675-1 | 2488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE FIRE ON POLE 854-28 OPENING RECLOSER ON 854- 87 LONG ENOUGH TO ISOLATE AND PUT FIRE OUT, THEN WILL CLOSE RECLOSER BACK IN ,OPENED RECLOSER AT 10:43// CLOSED RECLOSER BACK AT 11:03 ALL BUT 4 CUSTOMERS SHOULD BE BACK ON// WILL FINISH PUTTING FIRE OUT AND REPLACE CUTOUT, PUT POLE OUT REPLACED CUTOUT AND BRACKET// VER/TOM IDC XXXX
6066 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-09-03 09:40 | 2009-09-03 14:36 | 19 | 296 | 62966-1 | 2488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#31560726// POLE 1147-4186 BAD 50KVA SEND TO LLOYD MC. LINE FUSE 1147-4184 ON 11;20R#31560726// POLE 1147-4186 BAD 50KVA SEND TO LLOYD MC. LINE FUSE 1147-4184 ON 11;20 25T RELEASED BY CREW 078S08//VER/CRB IDCC PN4186 XXXX
6067 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-04-05 08:38 | 2019-04-05 13:00 | 20 | 262 | 4059251 | 2485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on pole 335-390 will patrol/// not showing on map // Failed cutout on pole 335-1029 Has burnt top of pole off// We can lower this /// this is no truck// will isolate trouble on pole 335-389/// s/// LF 335-390 ON @ 1035 HOT TAP ON POLE 37830335D30389// COD 1 /// ON @ 1300 sjg
6068 | Pikeville | 3413401 | GARRETT | GARRETT | 2011-03-06 07:41 | 2011-03-06 18:00 | 7 | 619 | 50381-1 | 2485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39052251 // LINE FUSE OPEN AT POLE 65D-42, POLE 65-514 BURNED APART, ISOLATED AT POLE 65-496, ... CLOSED POLE 42 TO POLE 496 AT 10:18 RELEASED BY CREW 074S03 COD-7 ISO LF 37830065D00042 VER/HFP L3/HFP IDC XXXX
6069 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-08-15 18:44 | 2008-08-15 21:55 | 13 | 191 | 52440-1 | 2483 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314401//LINE FUS IS OPEN ON POLE 449-599, I AM PATROLLING LINE. I HAVE FOUND 2 CUTOUTS BROKEN ON POLE 449-1166. NEED ONE MAN TO HELP ON THISRELEASED BY CREW 077S07LINE FUS IS OPEN ON POLE 449-599, I AM PATROLLING LINE. I HAVE FOUND 2 CUTOUTS BROKEN ON POLE 449-1166. NEED ONE MAN TO HELP ON THIS//COD 13// VER/DBM IDC XXXX
6070 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2017-01-25 13:31 | 2017-01-25 14:44 | 34 | 73 | 4330211 | 2482 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED (DOOR BURNT UP) ON CENTER PHASE XFMR IN BANK. WORKING TO REPAIR - CREW ENROUTE TO ASSIST. REPLACED CUTOUT AND RESTORED @ 14:44. SH VER/CRB L3/HFP HFPC MCCDL AJB
6071 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-09-11 09:40 | 2011-09-11 11:00 | 31 | 80 | 4856381 | 2480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASED ON CALLS LOOKS LIKE B PHASE RECLOSER MAY BE LOCKED OUT (CENTER PHASE) LEAD ON RECLOSURE CAME LOOSE AT POLE 38830206C02515, ALL REPAIRS MADE AND POWER RESTORED ENTERED MD COD-31 ISO OCR 38830206C02515 VER/HFP L3/HFP IDC XXXX
6072 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2008-06-18 06:55 | 2008-06-18 12:05 | 8 | 310 | 50196-1 | 2480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE//3002107PATROLING LINE/ M PHELPS CREW TO ASSIST/REPLACED CUTOUT ARRESTOR RELEASED BY CREW 078S07//VER/CRB IDC XXXX
6073 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-11-06 12:00 | 2013-11-06 12:31 | 80 | 31 | 4014601 | 2480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON LINE FUSE ON POLE 38831083A30288, TIM SMITH CREW IS COMMING TO CHANGE LINE FUSE VER/CRB L3/HFP IDC CHANGED TOF FROM 1007, ESTIMATED TIME OFF XXXX
6074 | Hazard | 3310502 | HADDIX | CANOE | 2013-04-03 16:01 | 2013-04-04 12:40 | 2 | 1239 | 4977141 | 2478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 37830196A00204---BAD TRANSFORMER AND UNDERGROUND NEED CREW IN THE MORNING 4/0 COND AND 2 COND NEED NEW 200 AMP METER BASE SEND TO GLEN AND BRUCE RELEASED BY CREW 077S10 VER/KEP IDCC PN204 XXXX
6075 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-07-29 07:27 | 2009-07-29 14:20 | 6 | 413 | 59345-1 | 2478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 6 INCH DISC ON MANUAL POLE , HIGH WEEDS TO FUSE POLE NEED ONE MAN TO HELP RELEASED BY CREW 077S10 VER/KEP L3/KEP IDC CHANGED CAUSE FROM CUTOUT XXXX
6076 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-05-14 17:37 | 2018-05-14 19:35 | 21 | 118 | 4348911 | 2478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrestor cut in clear, line fuse back in at 19:35 COD-21 ISO LF 38830118B00094
6077 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2019-10-05 19:38 | 2019-10-05 22:35 | 14 | 177 | 4099251 | 2478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /bad cutout/ ISO 37830174D00010/ COD 12*****xfmr on pole 37830174D00010 is fed by line fuse on that same pole the po maps dont show this MD Done L3/HFP
6078 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-11-29 16:55 | 2015-11-29 20:40 | 11 | 225 | 4492771 | 2475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 WITH AN ETA 1840// CREW ENROUTE//TRANS 38831074D00071 IS ON THE LOAD SIDE OF L/F//MADE MDC TO SHOW THIS//CORRECT COD 14// DEAD END CUT ON LOAD SIDE OF 1074-D-16//CLOSED L/F @ 2040//COD 5CALLED 911 WITH AN ETA 1840// CREW ENROUTE//TRANS 38831074D00071 IS ON THE LOAD SIDE OF L/F//MADE MDC TO SHOW THIS//CORRECT COD 14// DEAD END CUT ON LOAD SIDE OF 1074D-16, ON FROM 71 TO 16 AT 20:40, POLE 16 ON AT 22:00, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03
6079 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2009-09-02 21:46 | 2009-09-03 11:30 | 3 | 824 | 62647-1 | 2472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WORK REQUEST # 31556636 // CUTOUT FAILED AT POLE 172-17 AND OPEN WIRE SECONDARY DOWN & DENNIS MASSEY REPORTED WILL GET CREW TO MAKE REPAIRS AFTER REGULAR WORKTIME.3400701// RELEASED BY CREW 074S08 CUTOUT FAILED AT POLE 172-17 AND OPEN WIRE SECONDARY DOWN & DENNIS MASSEY REPORTED WILL GET CREW TO MAKE REPAIRS AFTER REGULAR WORKTIME. COD-3 ISO TF 37820172000017 L3/HFP IDC XXXX
6080 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-02-06 10:24 | 2012-02-06 12:02 | 52 | 98 | 4322631 | 2471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 44-4129 BAD LA ON 12;02 POLE 44-6549 INSTALLED 15T ON 11;20 POLE 44-6547 30T ON 11;05 ///VER/CRB IDC IT APPEARS THERE SHOULD BE THREE STEPS HERE I ADDED THE TWO STEPS ACCORDING TO THE COMMENTS XXXX
6081 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-07-06 08:22 | 2017-07-06 14:15 | 7 | 353 | 4080041 | 2471 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN @1-A2-268, PATROLLING. BAD CUT OUT ON POLE 38821129B00149, THIS IS IN REMOTE LOCATION, TIM HALL IS GETTING A R.O.W. CREW SO I CAN CHANGE THE C/O, ALSO FOUND A BAD C/O AND ARRESTOR ON POLE 1-104, WILL BE MAKING REPAIRS. MADE REPAIRS AND CLOSED REC. BACK IN @1415./ ISO 37820001A20268/ COD 7/ VER/BOW SJG
6082 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2022-03-30 16:02 | 2022-03-30 18:12 | 19 | 130 | 4692831 | 2470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke hot tap on cutout crew on site going to change cutout and new hot tap LRM FETR 18:45 LRM
6083 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-05-05 17:20 | 2016-05-05 21:27 | 10 | 247 | 4178731 | 2470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 279-105 IS BURNING, OPENEND FUSE ON POLE 279-2//NO OUTAGE TILL FUSE OPENED @ 1720// 30T IN LINE FUSE ON POLE 279-2//MADE MDC//POLE 279-105 NEEDS REPLACED//SENT TO TECHS// VER/CRB
6084 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-05-13 09:36 | 2011-05-13 14:10 | 9 | 274 | 4082081 | 2466 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED BAD 50KVA TRANSFORMER--THIS TICKET IS COMPLETED VER/KEP
6085 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-01-31 18:03 | 2009-02-02 11:08 | 1 | 2465 | 53670-1 | 2465 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, CHECKING TROUBLE, SPLICE IN ONE LEG OF SERVICE FAILED
6086 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-02-12 15:25 | 2017-02-12 16:21 | 44 | 56 | 4387721 | 2464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT ON 805-69 BAD..I WILL HAVE TO OPEN 2 LINE FUSES FEEDING UP PAINTERS LICK AND 1 LINE FUSE FEEDING IN OPPOSITE DIRECTION.NO POLE ACCESS//LINE FUSE CUTOUT ON 805-69 BAD..I WILL HAVE TO OPEN 2 LINE FUSES FEEDING UP PAINTERS LICK AND 1 LINE FUSE FEEDING IN OPPOSITE DIRECTION.NO POLE ACCESS OPEN UP 3 LINE FUSES AT 15.25.LINE FUSES BACK ON AT 1621.//NO OUTAGE TILL L/F OPENED VER/CRB L3/HFP XXXHFP AJB
6087 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-12-08 19:37 | 2012-12-09 00:45 | 8 | 308 | 4452581 | 2464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PHASES A&B FUSES OUT WILL BE PATROLLING LINE. AVE CALLED FOR HELP PATROLLING LINE BAD INSULATOR ON 1101-236 // VER/TOM L3/TOM IDC XXXX
6088 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2017-03-04 20:25 | 2017-03-05 10:05 | 3 | 820 | 4521861 | 2460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE
6089 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2014-05-14 16:52 | 2014-05-14 19:36 | 15 | 164 | 4702901 | 2460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE #26-5 WILL PATROL. BAD LIGHTNING ARRESTER ON POLE#50-83 CHANGED ARRESTER CLOSED IN LINE FUSE @19:36 AND IT STAYED /// COD-15 ISO LF 37820026D40005 VER/HFP L3/HFP IDC XXXX
6090 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2019-06-16 20:00 | 2019-06-17 16:30 | 2 | 1230 | 4515731 | 2460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7.2kv 120/240 volt 25kva ( high voltage136/275 volts, ),, no trucks to pole will need yard dog , in back yard, 4 man crew required,, checked voltage at near by transfomer and voltage ok Released by crew 078M06 / Restored 16:30 released by 078H14 bah
6091 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-06-02 11:42 | 2021-06-02 14:26 | 15 | 164 | 4658891 | 2460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F blown on 858-B3-894///Found and replaced bad xfmr cutout on pole 858-B-395. Restored @14:26// L/F size=20T//MD MADE TO SHOW CORRECT L/F SIZE
6092 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2015-06-25 17:38 | 2015-06-25 19:00 | 30 | 82 | 4656471 | 2460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830045C24668 BAD CUTOUT VER/CRB AJB
6093 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2014-03-04 12:50 | 2014-03-04 13:50 | 41 | 60 | 4450941 | 2460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L/F BLOWN @ 37830024B40504// WILL PATROL// L/A BAD ON CSP XFMR @ 37830048A30436// REMOVED L/A//POWER IS RESTORED AT 13:50 // 3-4 VER/CRB IDC XXXX
6094 | Hazard | 3301401 | COMBS | COMBS | 2015-02-10 07:37 | 2015-02-10 11:43 | 10 | 246 | 4004231 | 2460 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION AT TRANSFORMER GOING BAD, NEED LINE CREW AND 4/0 TRANSFORMER LEADS AND 5 FT OF 336 SECONDARY CONDUCTOR. RELEASED BY CREW 077S04CONNECTION AT TRANSFORMER GOING BAD, NEED LINE CREW AND 4/0 TRANSFORMER LEADS AND 5 FT OF 336 SECONDARY CONDUCTOR. OPENED TRANSFORMER AT 09:32/CONNECTION AT TRANSFORMER GOING BAD, NEED LINE CREW AND 4/0 TRANSFORMER LEADS AND 5 FT OF 336 SECONDARY CONDUCTOR./10 CUSTOMERS PART POWER FROM 737 WHEN CREW ARRIVED/FIX IT IN HOIS/COD 10+9// VER/ ADH L3/HFP HFPC CDC92 AJB
6095 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-09-23 12:16 | 2008-09-23 13:47 | 27 | 91 | 66506-1 | 2457 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP FAULT POLE 37830402B0027 COD-27 CUT ARRESTOR IN CLEAR AND REFUSED LINE MLR OK
6096 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-11-08 00:53 | 2019-11-08 06:00 | 8 | 307 | 4009581 | 2456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. pole 38830092A01017 is burnt off isolated/tagged and grounded to austin martin at pole38830092A00239 crew on site 40t restored at 06:00 L3/HFP
6097 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-03-09 18:24 | 2012-03-09 23:31 | 8 | 307 | 4567881 | 2456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED PRC CREW--BAD 25 KVA TRANSFORMER--TRUCK TO POLE--NEED 2 SECONDARY SPACERS INSTALLED BETWEEN POLE 39831099D16023 AND POLE 39831099D16024 // NEED PRC CREW--BAD 25 KVA TRANSFORMER--TRUCK TO POLE--NEED 2 SECONDARY SPACERS INSTALLED BETWEEN POLE 39831099D16023 AND POLE 39831099D16024 ///CREW ON SITE/FETR2321/ COD-8 ISO TF 39831099D16023 VER/HFP L3/HFP IDC XXXX
6098 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-12-27 08:09 | 2015-12-27 16:20 | 5 | 491 | 4563521 | 2455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN @ POLE 374-10 TO 374-11,OPEN LINE FUSE @ 374A1-82 @ 0945 ISO & TAG TO DDC NEED LINE CREW TO MAKE REPAIRS NO TRUCK RELEASED BY CREW 078S05//1136 GAVE C YOUNGMAN PERMISSION TO REPLACE DDC TAG WITH HIS OWN//PRIMARY DOWN @ POLE 374-10 TO 374-11,OPEN LINE FUSE @ 374A1-82 @ 0945 ISO & TAG TO DDC NEED LINE CREW TO MAKE REPAIRS NO TRUCK RELEASED BY CREW 078S05.. CREW ON SITE ETR 13:45 AJB
6099 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2016-01-06 15:42 | 2016-01-06 22:31 | 6 | 409 | 4590811 | 2454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA/// NO TRUCK/// NEED 50 KVA 7200 XFM ,CUTOUT AND BRACKET/// NEED LINE CREW/// REPAIRS MADE CLOSED XFM IN @ 22:31 AND RESTORED SERVICE/// SEND COPY TO MIKE HATFIELD POLE#171-127 NEEDS CHANGED VER/KEP AJB
6100 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-02-23 22:13 | 2012-02-24 11:51 | 3 | 818 | 4490101 | 2454 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE ,, MANUAL,, WILL NEED COVER UP,, RELEASED BY CREW 077H02 COD-3 ISO LF 37830202000013 VER/HFP L3/HFP IDC XXXX
6101 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-11-01 00:44 | 2011-11-01 10:57 | 4 | 613 | 4040841 | 2452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED--NEED TECH--POLE 38830044D16043 ROTTED OFF AND FELL OVER--TRUCK TO POLE--CUT SECONDARY LOOPS ON POLE 38830044D16001 RELEASED BY CREW 078S07/CREW LOADING POLE/FETR1230/VEM/ROTTEN WINDSTREAM POLE SET/FETR 1230/VEM/TECH TO WRITE JOB/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1057/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
6102 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-05-22 21:29 | 2011-05-23 17:55 | 2 | 1226 | 4134221 | 2452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 2 MAN CREW, NO TRUCK ACCESS, CUTOUT FAILED, BRING 12 KV C/O, ARR & BKT, CAN LIFT HOT TAP @ 311-35 TO PERFORM WORK SAFELY/ RELEASED BY CREW 074E11 // COD-2 ISO PO @ 37830311000035 VER/HFP L3/HFP
6103 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-12-29 15:09 | 2022-12-29 17:18 | 19 | 129 | 4375741 | 2451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 tree wire primary down from 20-a4-1563 to 20-a4-1564. No trucks to poles. Crew required. send to Bobby Tackett. Released by crew 078S02repairs made all cust restored please close ticket thanks.bt
6104 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2011-05-19 15:35 | 2011-05-19 16:45 | 35 | 70 | 4113881 | 2450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED STEP DOWN TO REPLACE DEFECTIVE CUTOUT OFF TIME 15:35. ON TIME 16:45. REPLACE CUTOUT AND ARRESTOR VER/HFP L3/HFP IDC XXXX
6105 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-01-19 12:15 | 2010-01-19 13:04 | 50 | 49 | 56478-1 | 2450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF SOS 1492 REV 40 CUTOUT BROKE CAUSING UNFORSEEN OUTAGE//THIS WAS A TEMP CUTOUT//VER/CRB IDCC PN5 CNT5, TOF1230 XXXX
6106 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-03-31 15:32 | 2015-03-31 20:38 | 8 | 306 | 4249271 | 2448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKEN @ BASKET. HENDRIX. NO CLEARANCE, CREW REQD./ XFMER @ 3418 FLOYD RELEASED BY CREW 078S07HOT TAP BROKEN @ BASKET. HENDRIX. NO CLEARANCE, CREW REQD./ XFMER @ 3418 FLOYD RELEASED BY CREW ///CHANGED CUTOUT AND LA///TBL TKT COMP VER/KEP
6107 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-10-23 10:33 | 2014-10-23 10:50 | 144 | 17 | 4655651 | 2448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4655431/ LOAD BUSTING SWITCH AND TOP OF CUTOUT BROKE AND THE LOOPS HOILDING CUTOUT FELL INTO PHASE. OPENED RECLOSER TO REMOVE IT.// VER/BOW L3/HFP
6108 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-07-05 18:15 | 2016-07-05 20:39 | 17 | 144 | 4542491 | 2448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S07. CHANGED C/O ON 1123-6630, RESTORED//IT FORCE CLOSED/ VER/BOW
6109 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-02-18 13:21 | 2009-02-18 13:33 | 204 | 12 | 64272-1 | 2448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308002//RE-OPENED RECLOSER IN ORDER TO MAKE LOOPS BACK ON ORDER 63895-1//COD 204// VER/DBM IDC XXXX
6110 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-03-04 23:37 | 2011-03-05 02:20 | 15 | 163 | 66640-1 | 2445 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR#39050214 BAD CONN. ON POLE TIME OFF 1;30 TIME ON 2;20 IDCC TOF0130 3/4 XXXX
6111 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-08-17 13:46 | 2011-08-17 14:38 | 47 | 52 | 4720891 | 2444 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREWS OPENED RECLOSER TO REPAIR DOWNED CONDUCTOR //SEE ORDER 4720271//COD 47// VER/DBM IDC XXXX
6112 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-01-26 11:01 | 2011-01-26 12:15 | 33 | 74 | 64481-1 | 2442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38580576 //PRI. BSK. BURN OFF OF LINE FUSE. INSTALLED NEW BSK. MADE LINE HOT COD-33 ISO LF 38830044B00267 VER/HFP L3/HFP IDC XXXX
6113 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-02-20 01:59 | 2015-02-20 06:30 | 9 | 271 | 4046751 | 2439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN WILL REFUSE//// BAD 50 KVA 7200 //// CAN USE TRUCK ROAD IS SNOW COVERED RELEASED BY CREW 074H17// REPLACED BAD 50KVA WITH A 75 KVA. MADE REPAIRS AND RESTORED POWER AT 6:30 TIM MCCOY RELEASED BY CREW 074H10 VER/CRB L3/DKGXXXX
6114 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-08-08 00:57 | 2011-08-08 14:30 | 3 | 813 | 4677301 | 2439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9KV 120/240 VOLT TRANSFOMER NO TRUCK WILL NEED YARD DOG, NEED TO TAKE YARDDOG UP SECOND DRIVE WAY ON LEFT AROUND BIG CURVE, CAN GET OFF ROAD WITH TRUCKS TO UNLOAD CLOSED FUSE IN ON TRANSFORMER AND IT BLEW 50T LINE FUSE BACKING IT UP, ALSO NEED TO RECONNECT 4/2 SEC CUT ON POLE DURING TROUBLESHOOTING, REFUSED CUTOUT WITH1.6 (REFUSED LINE FUSE AT10:20 OUT AT 09:15) VER/KEP IDC XXXX
6115 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-11-22 10:17 | 2011-11-22 11:15 | 42 | 58 | 4099931 | 2436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD ARRESTOR ON POLE 1023-115, HAVE IT CUT IN THE CLEAR AND CLOSED IN LINE FUSE AT 1115, POWER IS RESTORED AT THIS LOC//COD 42//AED ENTRY CREATED// VER/DBM IDC XXXX
6116 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-04-26 06:57 | 2012-04-26 10:20 | 12 | 203 | 4709631 | 2436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE ON POLE # 179-187 "C" PHASE COD-12, OPENED OTHER 2 FUSES AT 09:50 "A`&"B" PHASE`S COD-10 AND CLOSED ALL 3 BACK IN AT 10:20 VER/KEP
6117 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-07-12 15:06 | 2016-07-12 17:02 | 21 | 116 | 4616291 | 2436 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | POLE 45-2051 BAD CUTOUT ON THREE PHASE TAP TRUCK TO POLE MARYLAND PRKY, 13TH. ST. RELEASED BY CREW 078S08 CUTOUT CHANGED ALL PWR RESTORED @ 17:02 PLEASE CLOSE TICKET LRM// VER/ ADH AJB
6118 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2011-03-12 10:31 | 2011-03-12 13:25 | 14 | 174 | 53714-1 | 2436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ON SITE CKING TROUBLE RECLOSER IS OUT ON POLE #318-281 *AT 1248, CREW PATROLLED CKT AND WILL TRY SHOOTING ABOVE RECL.ON SITE CKING TROUBLE RECLOSER IS OUT ON POLE #318-281// BAD PRIMARY METER CAN , WILL REPLACE MONDAY (JS-150)SR#1202050601... (175:1, 100/200/5), 34.5 KV SEND COPY TO GLEN COMBS HAZARD.//VER/CRB IDC DCMT XXXX
6119 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-08-27 18:52 | 2018-08-27 20:48 | 21 | 116 | 4005861 | 2436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout gate replaced cutout gate
6120 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2011-09-06 07:54 | 2011-09-06 16:05 | 24 | 491 | 4829701 | 2434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISOLATED 249-39/CREW REQUIRED BURNT OFF /249-60 ISOLATED 1 CUSTOMER WILL BE OFF TRUCKS OK/40/5 DEAD END WITH TRANSFORMER/249-39 BACK ON AT 0900 HRS SEND TO REYNOLDS RELEASED BY CREW 078S03COMPLTED @ 16:05 BLR RELEASED BY CREW 078H07//VER/CRB IDC XXXX
6121 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-02-26 12:39 | 2008-02-26 19:52 | 22 | 433 | 50516-1 | 2434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003//POLE FIRE ON POLE 38830230000313, ISOLATED AT POLE #38830230000295, CREW REQUIRED, FUSE BACK ON AT 13:18 RELEASED BY CREW 078S05 ALL POWER ON AT 19:52// VER/DBM IDC XXXX
6122 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-12-25 23:32 | 2015-12-26 09:40 | 4 | 608 | 4560981 | 2432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O DOOR// VER/ ADH
6123 | Hazard | 3303902 | LESLIE | WOOTON | 2011-03-02 12:11 | 2011-03-02 12:19 | 304 | 8 | 65833-1 | 2432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | CREW HAVING TROUBLE WITH THE SWITCH ON 65821-1 365-91 VER/KEP IDC XXXX
6124 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2015-06-24 06:14 | 2015-06-24 14:20 | 5 | 486 | 4649021 | 2430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED LINE FUSE 235-28 @ 925/ DUE TO BAD CUTOUT ON POLE 235-162. POLE JUST ABOUT BURNT INTO. CREW ON THE WAY. SHOULD HAVE BACK ON BY 14:00 CLOSED FUSE BACK IN AT 14:20// VER/ ADH
6125 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-11-12 10:33 | 2015-11-12 16:20 | 7 | 347 | 4431481 | 2429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DDC GRNDS AND TAGGED// FOUND L/F OUT ON 1121-25, HAVE BURNTED OFF 355 POLE STRAIGHT LINE POLE, NEED PTP, AND CUTOUT MAYBE ABLE TO USE A EXTEND ON THIS POLE, CAN GET TRUCKS TO POLE, BUT HAVE TO COME IN FROM CALLIHAN, ROAD BESIDE OF IMEL GREENHOUSE, ALL THE WAY TO THE END OF ROAD WELL SEE POLE TOP HAVE LINE GR AND TAGGED TO DDC AT 112 RELEASED BY CREW 078S06. REPLACED TAP CUTOUT 1121-25, INSTALLED 3 POLETOP PIN & CHANGED CUTOUT AT POLE 1121-277. BURNT POLETOP. VER/CRB AJB
6126 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-02-16 18:34 | 2016-02-16 22:37 | 18 | 243 | 4723311 | 2428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 420-75, BAD CUTOUT ON POLE 420-198 , LINE FUSE OPEN ON POE 420-81 TO ISOLATE, CLOSED LINE FUSE IN AT 20:18 ON POLE 420-75 .RESTORED POWER AT 22:37// VER/ ADH L3/HFP HFPC FP37830420D00081
6127 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-08-10 20:27 | 2022-08-11 16:41 | 2 | 1214 | 4721821 | 2428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a broke Line fuse cutout at 216-152,Will be making repairs..Restored 16:41.
6128 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-01-16 09:51 | 2014-01-16 14:54 | 8 | 303 | 4285841 | 2424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BROKEN CUTOUT , REPAIRING NOW TCM//COD 8// VER/DBM L3/HFP IDC XXXX
6129 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-03-28 08:51 | 2009-03-28 11:38 | 26 | 167 | 62353-1 | 2422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP C0D- 26 PATROLING LINE WITH LINKOUS--CLOSED LINE FUSE IN ON POLE 39831147B12019-AT 09:30--FUSE ON POLE 39831146D00060 STILL OUT--POLE 39831146D00127-IS ROTTEN ANUSAFE--NEEDS REPLACED ASAP--REPLACED 2 BAD CUTOUTS ON POLE 39831146D00060 L3/HFP IDC CHANGED CAUSE FROM UNKNOWN XXXX
6130 | Hazard | 3309903 | SLEMP | BEECH FORK | 2020-08-31 18:13 | 2020-09-01 07:40 | 3 | 807 | 4411641 | 2421 | TRANSMISSION LINE | EQUIPMENT FAILURE | SPLICE, OH | no power at meter Released by crew 077S03/ CB/ outage started at 1813 on 8/31/20 due to transmission line being out de-energizing all of slemp station/ DOL 1050048 // T-Line outage // Station source is out // t-line completed repairs and restored CB 3309903@ 0740/ Transmission conductor down at the slemp station/ they thought they close this cb at 0314 but they did not there is nprobably another order for this when they thought they closed at 0314
6131 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2015-12-02 10:50 | 2015-12-02 14:52 | 10 | 242 | 4503671 | 2420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 21-85 PHASE DOWN TRUCKS TO POLES OPEN LOOP ON HENDRICKS CABLE CREW ENROUTE/OPENED BREAKER TO GIVE HOLD ORDER FOR CREW TO MAKE REPAIRS/ VER/KEP
6132 | Pikeville | 3120102 | STANVILLE | TRAM | 2021-07-17 13:09 | 2021-07-17 16:15 | 13 | 186 | 4924641 | 2418 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | secondary bushing on transformer failed paul layne en route to assist Released by crew 074S09//xfmr changed power restored @ 16:15
6133 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2017-04-12 14:30 | 2017-04-12 15:32 | 39 | 62 | 4641001 | 2418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUTS ON POLE 785-108 WE HAD TO CHANGE BURNING ON ARM ,CUT IN NEW FUSES ON 785-110 OPENED UP AT 14:30 TO MAKE REPAIRS SAFELY TCM// CLOSED IN ON 785-110 AT 15:32/ ISO 38830785D40110/ COD 39/ VER/BOW L3/HFP XXXHFP AJB
6134 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2016-10-21 10:09 | 2016-10-21 11:27 | 31 | 78 | H4034701 | 2418 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PH ONLY COD-23/TRANS CUTOUT FAILED ON 1145C67 BURNING UP 1 SET OF 8 FT CROSSARMS AND TAKING OUT FUSE ON 1145C20 CREW REQUIRED 2 MEN AND FOREMAN NEED TWO 8 FT CROSSARMS BRACES 7200 CUTOUT AND ARRESTOR ARM BRACKET TRK APPROACH WILL HAVE TO OPEN UP OTHER PHASE TO MAKE REPAIRS I ISOLATED TRANS CUTOUT ON 1145C67 AND RESTORED POWER ON 1145C20 AT 01:30 // OPENED FUSE AGAIN @ 1009 ON @ 1127 DUP OF H4034701 VER/HFP L3/HFP AJB
6135 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-07-21 20:53 | 2020-07-23 13:10 | 1 | 2417 | 4197551 | 2417 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AEP Network Outage Center reports power Outage at Engle Radio Tower. Pole 37830150000170.on top of mounain and cannot find road , will waik out in daylight, might take side by side,,p.hicks Released by crew 077H09..bad 10kva,c/o &brkt 19.9,manual, requires road to be cut out ,will work Thurs.23rd Released by crew 077H13 power stored at 13:10
6136 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2012-07-06 14:50 | 2012-07-06 16:45 | 21 | 115 | 4548311 | 2415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKE REPAIRED
6137 | Hazard | 3303902 | LESLIE | WOOTON | 2021-12-16 09:01 | 2021-12-16 11:42 | 15 | 161 | 4200681 | 2415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cleard blown lightnging arrester on 341-114. Power restored @ 11:42
6138 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-03-27 04:51 | 2011-03-27 09:26 | 11 | 275 | 59618-1 | 2415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT....BURNT OFF POLE TOP....LAST PRIMARY POLE ON LATERAL.....CALLED CREW....CAN BAYONET POLE.....// ..EXTIGUISHED FIRE..LIFTED HOT LINE CLAMP ON 1060-D-171..RE-FUSED LATERAL CUTOUT ON 1060-D-76 @ 08:25.....SEND TO JOEY REED RELEASED BY CREW 080S01. RESTORED LAST CUSTOMER AT 09:26 /// COD-11 ISO LF 38821060D00076 VER/HFP L3/HFP IDC XXXX
6139 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-10-11 14:10 | 2020-10-11 16:17 | 19 | 127 | 4545401 | 2413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bad lightning arrestoron CSP XFM @ 164-196. Cut in clear. Restored @ 16:17
6140 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-11-03 02:18 | 2018-11-03 09:00 | 6 | 402 | 4358891 | 2412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad cutout on pl 449-342 line fuse open on 449-30 power restored at 09:00 /// L3/HFP
6141 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-07-04 16:41 | 2018-07-04 18:30 | 25 | 109 | 4722331 | 2409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 198-77 fuse broke opened other 25t to do safely at 1800 hrs/other back in at 1830
6142 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2014-04-13 16:47 | 2014-04-13 18:00 | 33 | 73 | 4600281 | 2409 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BLOWN ON CSP TRANS ON POLE 354 REFUSED LINE PLEASE SEND TO RIGHT OF WAY /// COD-33 ISO LF 38821089B00022 VER/HFP L3/HFP IDC XXXX
6143 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-10-27 08:02 | 2010-10-27 12:42 | 17 | 280 | 65471-1 | 2408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RESTORED 16 CUSTOMERS. BAD TRANSFORMER ON POLE 1137B651. ONE CUSTOMER STILL OUT. WAITING ON TRANSFORMER. BRINGING TRANSFORMER FROM PIKEVILLE. FETR 12:30. VER/KEP L3/KEP IDC XXXX
6144 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-01-08 07:33 | 2016-01-08 12:13 | 13 | 280 | 4594191 | 2408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT LOOP OUT ON POLE 37830080000006 AND TRANS WILL BE HOT, PUT STEP DOWN AT 1021 CLOSED FUSE AT 1213 AND PUT 12 T IN FUSE RELEASED BY CREW 077S05 VER/CRB AJB
6145 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2014-05-20 00:01 | 2014-05-20 01:24 | 29 | 83 | 4725161 | 2407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERV PATOLLING LINE BROKEN FUSE VER/PDP AJB
6146 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-02-18 00:25 | 2014-02-18 13:47 | 3 | 802 | 4395881 | 2406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPEN SEC CABLE DOWN,MAY BE ABLE TO REM IT,WILL CHECK///////REMD SEC WIRES BUT CSP XFR IS DAMAGED,NEEDS 2B REPLACED.CANT CLOSE SEC BRKR.NEED 25KVA,NO TRUCK APPROACH.CSP IS DAMAGED.WILL ALSO HAVE TO DEAD-END SEC CABLES ON NEXT POLE. ** CREW WILL RETURN AT REG WK TIME TO COMPLETE REPAIRS .//COD 3// VER/DBM
6147 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-02-21 14:32 | 2012-02-22 10:34 | 2 | 1202 | 4469281 | 2404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFORM 7200 CUTOUT BROKEN ,HANGING DOWN POLE AND IS ON SIDE OF HILL NO TR. NEED LINE CREW, CUST. SAID NO ONE LIVES THERE BE OKAY TO DO WED. 22 RELEASED BY CREW 078S04 VER/HFP L3/HFP
6148 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-01-14 06:45 | 2017-01-14 14:37 | 6 | 472 | 4296871 | 2404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830165D00448 BROKE C/O, POLE TOP BURNT OFF .. CAN BE LOWERED--CREW REQ--/CREW ON SITE/WILL ISOLATE TROUBLE AT 165-D-445/WILL LEAVE ONE CUST OFF/FETR 1230/VEM/FETR FOR REMAING CUST 1445/VEM/ONE CUST RESTORED 1437/ACTUALLY IT LEFT TWO PEOPLE OFF AND 2 RESTORED A@ 1437/ PLEASE CLOSE TICKET/THANKS/VEM/ 38830165D00208 ON @ 1250/ 38830165D00445 ON @ 1437/ VER/BOW L3/HFP HFP
6149 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2008-02-06 03:24 | 2008-02-06 16:45 | 3 | 801 | 50423-1 | 2403 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 076H02 // REPLACED BAD 25 KVA TRANSFORMER.ON AT 16:45// VER/TOM IDC THIS WAS PART OF 50200-1 BUT SEPARATED AND CUSTOMERS REMOVED XXXX
6150 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-04 22:15 | 2010-01-05 10:35 | 4 | 740 | 60620-1 | 2402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQ 33312453 ; TOP 18 OF 403/152 BURNT OFF, DUE TO BUSTED CUTOUT; CREW REQUIRED, MAY BE ABLE TO TOP POLE AND TRIM TOPS OF TWO PINES NEXT TO POLE; SECTIONALIZED AT POLE 403/108; RE-FUSED CUTOUT POLE 403/103 WITH 10T MD FILED; LOST PART OF CIRCUIT DUE TO WIRE DOWN BETWEEN 428/58 AND 59; CIRCUIT STILL HOT BETWEEN RECLOSER 428/296 AND 428/58; RELEASE TO LINE CREW RELEASED BY CREW 078S12 RESTORED TRANS 1035 REST OF LINE OUTAGE SHOWN ON SEPERATE ORDER NO POWER TILL RES VER/KEP L3/KEP IDC XXXX
6151 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-11-16 16:40 | 2010-11-16 19:10 | 16 | 150 | 56535-1 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HIGH SIDE CUTOUT BROKE ON STEP DOWN POLE 771-85//CHANGED CUTOUT RESTORED AT 19:10/COMPLETE//EM//VER/CRB IDC XXXX
6152 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2018-09-17 20:48 | 2018-09-18 04:48 | 5 | 480 | 4122171 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 45/4 single arm 25kva /crew required grounds installed tagged to reynolds Released by crew 078S03
6153 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2021-02-04 16:15 | 2021-02-04 17:05 | 48 | 50 | 4937941 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced burnt basket and hottap restored @1705
6154 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-02-27 13:00 | 2009-02-27 13:50 | 48 | 50 | 52219-1 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601 OUTAGE FOR CREW TO SAFELY CHANGE CROSS ARM IDC XXXX
6155 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-07-09 04:47 | 2010-07-09 07:17 | 16 | 150 | 63795-1 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 35917644//30T 180-49 OUT /SERVICER PATROLLED LINE/FETR0700/VEM/FUSE CAME BACK OUT/CHECKING VINE COVERED POLE/VEM/NEW FETR0830/BAD CUTOUT DOOR 1146-52/FUSE ON 180-49 IN AT 0717/ALL CUST RESTORED/PLEASE CLOSE TICKET/THANKS/VEM //COD 16 IDCC TOF0611 XXXX
6156 | Hazard | 3301401 | COMBS | COMBS | 2008-10-22 22:12 | 2008-10-23 00:12 | 20 | 120 | 58043-1 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT ARCING AT POLE 271C-161.WILL NEED 2 MEN ,12 KV CUTOUT,HOT LINE CUTTERS,WILL HAVE TO OPEN LINE UP TO REPAIR.//330140. RELEASED BY CREW 077S09//3301401// .//OPENED LINE FUSE AT POLE 271C-9 AT 22:12 RESTORED AT 0012 ON 10-23-08 //VER/GAH IDCC PN161 XXXX
6157 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2018-06-28 16:58 | 2018-06-28 18:18 | 30 | 80 | 4685431 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Need distribution to open line for T line structure that is in trouble for 1 hr to change///opened 38830785D10693 at 1658Need distribution to open line for T line structure that is in trouble for 1 hr to change/ Opened @ 16:58.Need distribution to open line for T line structure that is in trouble for 1 hr to change/ Opened @ 16:58. Closed @ 18:18. sh Released by crew 076S02
6158 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-07-19 14:49 | 2015-07-19 18:49 | 10 | 240 | 4911511 | 2400 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 37830048C11249 // REPLACED ALL CUTOUTS ON BANK // POWER RESTORED @ 18:49/ ISO 37830048C11249/ COD 10 L3/DKG
6159 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-05-15 02:49 | 2014-05-15 12:49 | 4 | 600 | 4705341 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES //,BAD 37.5 XFMR NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05/BAD XFMR CREW ON SITE/VERY DIFFICULT LOCATION/FETR1330/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1249/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP
6160 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-12-15 16:10 | 2008-12-15 18:50 | 15 | 160 | 58691-1 | 2400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312202// STS BAD CUTOUT ON POLE 173-69//COD 15// VER/DBM L3/KEP IDC XXXX
6161 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-11-22 07:45 | 2011-11-22 11:23 | 11 | 218 | 4099301 | 2398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED TAP @ 07:45 DUE TO POLE FIRE //COD 11//--- POLE WILL HAVE TO BE CHANGED, CREW ENROUTE.//COD 11// VER/DBM IDC XXXX
6162 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2014-10-07 06:04 | 2014-10-07 09:42 | 11 | 218 | 4562431 | 2398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REMOVED BAD TRANSFORMER CUTOUT ON POLE 38820917D00073 THAT DOES NOT SERVE ANYBODY NOW. POWER IS BACK ON.// COD 2+9//VER/ ADH VER/DKG L3/DKGXXXX THE LINE FUSE HAD 9 CUST AND 2 ON TRANS WHICH WAS FED BY LINE FUSE
6163 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-02-28 01:38 | 2014-02-28 11:37 | 4 | 599 | 4439711 | 2396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE LINE FUSE DOOR BURNT UP/268D118 WIRE DOWN /#4 ASCR PRIMARY ONLY/TRUCKS OK CREW REQUIRED /LINE FUSE OPEN ON 268D29 /ISOLATED AND GROUNDED TAGGED TO DDC ***# PERSON LINE CREW NEEDED ** DUE TO NETWORK TROUBLE CREW WILL BE CALLED OUT AT REG WK TIME.//GAVE PERMISSION TO REMOVE DDC HOLD TAG...HFP// VER/KEP
6164 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-07-30 16:18 | 2016-07-30 17:00 | 57 | 42 | 4713201 | 2394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-3118 BAD CUTOUT 50T LINE FUSE ALSO BAD CUTOUT DOOR ON OTHER PHASE REPLACED 50T/ ISO 38830045B33118/ COD 57/ VER/BOW AJB
6165 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-12-19 08:36 | 2017-12-19 11:27 | 14 | 171 | 4657541 | 2394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//VOICEMAIL//broken line fuse cutout @ 38830206A31168 Released by crew 078S05CALLED CUST//VOICEMAIL//broken line fuse cutout @ 38830206A31168 replaced bad cutout complete
6166 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-05-05 14:17 | 2014-05-05 16:30 | 18 | 133 | 4665231 | 2394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 141-272 BAD LA NEEDS CUTOUT AND LA REPLACED TRUCK TO POLE INACTIVE TRANS. NEEDS REMOVED ASAP TOP RUSTED AWAY HOLE IN TOP 141-313 RELEASED BY CREW 078S08//MADE AED VER/CRB L3/HFP IDC XXXX
6167 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-11-30 06:04 | 2009-11-30 15:22 | 5 | 558 | 50865-1 | 2394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3110903// WR#32854268 / FOUND 355 POLE BURNTED OFF, THIS IS A 3 WAY DEADEND PRIMARY POLE, WILL NEED CREW, NOT SURE IF THEY WILL BE ABLE TO GET TRUCK TO THIS, WAS NO CUTOUT ON THIS POLE, LOOKS LIKE WE HAD A BAD INSULATOR, I HAVE HOT TAP LIFTED ON POLE 1098-3537, AND GROUNDED AT THIS POINT, CLOSED IN LINE FUSE ON POLE 1098-3530, AT 08:46, RESTORED POWER TO ONE CUST, STILL HAVE ABOUT 4 CUSTOMERS OFF. ALSO HAVE CALLED FOR MANUEL TREE CREW TO TRIM THIS OUT RELEASED BY CREW 07 IDCC TON0838 XXXX
6168 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-09-07 08:51 | 2011-09-07 11:40 | 17 | 169 | 4841931 | 2393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON 1127-11// PATROLLING/// BAD INS. ON POLE 38831127B00063//LIFTED HOT TAP ON 1127-366//COLSED IN AT POLE 1127-11 AT 11:00//REPLACED BAD INS. ALSO REPLACED BAD CUTOUT// REINSTALLED HOT TAP// POWER IS RESTORED TO ALL CUST. AT 11:40 VER/KEP IDC XXXX
6169 | Whitesburg | 3314401 | MAYKING | ERMINE | 2020-04-30 07:46 | 2020-04-30 10:50 | 13 | 184 | 4778471 | 2392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Wire down at pole 449D-11090. Had to open fuses on pole 449D-10530 to make it safe.//opened @ 0835 //Wire down at pole 449D-11090. Had to open fuses on pole 449D-10530 to make it safe. Released by crew 077H08 power restored at 10:50
6170 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-09-25 18:56 | 2015-09-25 22:00 | 13 | 184 | 4271171 | 2392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BROKE & WIRE DOWN ON POLE 426-140 WILL NEED 1 MAN AND BIG BUCKET TO MAKE REPAIRS. MADE REPAIRS AND RESTORED POWER AT 2200. BAD POLE NEED TO SEND TO DOUG CHRISTIAN./EMAILED DOUG/ADH// VER/ ADH L3/DKG
6171 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-12-24 12:44 | 2008-12-24 13:30 | 52 | 46 | 63414-1 | 2392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP FOUND BAD LIGHTNING ARRESSTOR, CUT IN CLEAR AND MADE LINE HOT L3/HFP IDC XXXX
6172 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-12-27 19:48 | 2017-12-27 21:20 | 26 | 92 | 4683021 | 2392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fruse broke/ ISO 38830116B00512/ COD 26
6173 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-10-12 01:37 | 2011-10-12 11:35 | 4 | 598 | 4967531 | 2392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT BROKE DOWN AND BURNED CROSSARM INTO AT POLE 336-61. WE HAVE 4 CUSTOMERS OUT NOW. WE WILL HAVE TO OPEN 3-PHASE RECLOSER AT POLE 335-305 TO CHANGE ARM. I OPENED RECLOSER AT POLE 335-305 AT 10:38. I CLOSED RECLOSER IN AT 11:35. ///VER/CRB IDC XXXX
6174 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-08-22 16:43 | 2013-08-23 06:00 | 3 | 797 | 4695651 | 2391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER RELEASED BY CREW 078H18 VER/ARN IDC XXXX
6175 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-10-28 08:36 | 2009-10-28 15:52 | 23 | 436 | 60884-1 | 2391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP B PHASE RECL OPEN 23 CUSTOMERS // OPENED A&C PHASE RECL - 19 CUSTOMERS @ 0900 // ORDER 64103-1 CREATED FOR RECL OUTAGE TO RETURN THIS TO NORMAL. DUPLICATING THIS ORDER FOR THE 30 CUSTOMERS INTERRUPTED TO RETURN THE N.O. SWITCH TO NORMAL L3/HFP IDCC CNT 42 XXXX
6176 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2011-07-28 19:56 | 2011-07-28 23:15 | 12 | 199 | 4635691 | 2388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREW REQUIRED--NEED4/0 RISER WIRE AND1/0 AL TO SPLICE RELEASED BY CREW 078S07//SENT TO TECHS FOR MAPPING WORK APPROX 12 CUST OUT//THIS TRANS DOES NOT SHOW UP ON MAP//VER/CRB IDC XXXX
6177 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-07-01 17:19 | 2019-07-01 23:00 | 7 | 341 | 4629241 | 2387 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WILL NEED RICKS BIG BUCKET///insulator on ptp. is bad. we need big bucket to change L3/HFP
6178 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-06-17 10:36 | 2015-06-17 13:15 | 15 | 159 | 4585921 | 2385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFORM CUTOUT ON 116-171 REPLACED ,STEPDOWN FUSE 7200 SIDE BLEW ON POLE 116-706 REFUSE 40 T POWER RESTORED VER/CRB
6179 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-20 09:19 | 2015-02-20 19:15 | 4 | 596 | 4053651 | 2384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR,MANUEL, NEED CREW. MIKE LEWIS TO CHECK LOAD RELEASED BY CREW 077S02 - NEED R/W CREW TOO CHANGED TRANSFORMER AND RESTORED POWER AT 1915 37830254C00028 VER/CRB
6180 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-10-25 06:14 | 2010-10-25 10:45 | 13 | 271 | 62656-1 | 2383 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37461710 //ISO POLE# 37830069000282 /HAVE BAD XFMR CUTOUT ON POLE 92-28 WILL ISOLATE IT & HAVE ALL BUT 1 COUST ON BY 09:15/ "C" PHASE ONLY COD-13/ VER/KEP L3/KEP IDC XXXX
6181 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-03-18 23:36 | 2013-03-19 09:31 | 4 | 595 | 4917761 | 2380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER AFTER HOURS DISPATCH GUIDE LINES WILL BE CHECKED THE MORNING OF 03/19/13 // BROKEN CUTOUT// COD-4 OPENED LINE FUSE ON 91-309 AT 0835 CLOSED AT 0931 COD-3 DUP MADE VER/KEP IDC XXXX
6182 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-05-11 16:49 | 2008-05-12 00:45 | 5 | 476 | 61562-1 | 2380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ORDER CREATED FOR HARVEY MARTIN *** AS PER PIKEVILLE CREW REQ. VER/HFP IDC XXXX
6183 | Hazard | 3302703 | HAZARD | HAZARD | 2008-02-21 11:03 | 2008-02-21 11:38 | 68 | 35 | 65985-1 | 2380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3302703//SERVICER HAD TO OPEN FUSES IN ORDER TO SAFELY REPAIR A DAMAGED CONDUCTOR//RELATED TO ORDER 65963-1//COD 68 VER/HFP IDC XXXX
6184 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-09-26 20:21 | 2008-09-27 03:36 | 7 | 435 | 51115-1 | 2379 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3411801 - PATROLED,NO PROBLEM FOUND.WILL RE-FUSE AND TRY TO GET POWER BACK ONTRIED FUSE,CAME BACK OUT.CONTACTED W ROBINSON ABT SOME HELP.HE IS SENDING SOMEMAIN LINE BACK ON AT 01:45,LAST CUST ON AT 03:36 IDCC PN20, STP XXXX
6185 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-07-17 13:22 | 2008-07-17 14:20 | 41 | 58 | 53641-1 | 2378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309103//CREW HAD TO OPEN MIDDLE PHASE ON REC 496-14 COD 41//BECAUSE OF PROBLEM WITH CUTOUT ON THE REC POLE//VER/CRB MLR OK
6186 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2020-03-25 17:20 | 2020-03-25 18:18 | 41 | 58 | 4510591 | 2378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 1016-D-139 on fire due to failed cutout.opened line fuse on 1016-D-250 at 17:20 to make repairs.made repairs,restored power at 18:18.plz send copy to Bill Johnson to write job to replace pole due to cutout failure and pole burnt
6187 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-07-23 10:24 | 2008-07-23 11:36 | 33 | 72 | H58553-1 | 2376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE OUT FAULT POLE TREE ON HENDRIX CABLE . SERVICER WILL OPEN ALL FUSES AND CHANGE SIZE FROM 80 T TO 60 T POLE 70-605 TREE ON POLE 70-675 LOOP BURNTING POLE 70-605 3-65T POLE 70-605 - 1-40T RELEASED BY CREW 078S08 VER/KEP IDCC DUP TO OPEN 2 PHASES XXXX
6188 | Hazard | 3309302 | VICCO | JEFF | 2011-07-21 08:39 | 2011-07-21 16:00 | 11 | 441 | 4572151 | 2376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSES BLOWN ON POLE 347-216, 347-217 AND 347-218. LINE FUSE BLOWN ON POLE 347-309. CLOSED LINE FUSE ON POLE347-309 AT 11:27, REFUSE XFMR ON P#347-217, XFMR BAD, 25KVA 19900.RESTORED POWER AT POLE 347-218 AT 12:00, RESTORED POWER TO 347-216 AT 12:30 POWER ON POLE 347-217 AT 1600//VER/CRB IDCC TON STEP 1 SPT MISSING XXXX
6189 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-01-13 15:03 | 2019-01-13 17:15 | 18 | 132 | 4667911 | 2376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | line fuse 184-255 open ,,,1 span primary burnt down at stirrup @ 184-123,,,will make repairs FETR 17:30 all repairs made ,line fuse 184-255 back in @ 17:15,,complete L3/HFP
6190 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-05-11 13:34 | 2008-05-11 13:53 | 125 | 19 | 61127-1 | 2375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STEVE OPENED FUSE TO SAFELY MAKE REPAIRS ON ORDER 60137 VER/KEP IDCC TOF1340, CNT138 XXXX
6191 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-08-19 04:42 | 2011-08-19 14:35 | 4 | 593 | 4728221 | 2372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON HILL WILL CHG.. COD-4 ISO LF 38831104000049 VER/HFP L3/HFP IDC XXXX
6192 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-05-22 05:17 | 2014-05-22 15:10 | 4 | 593 | 4736441 | 2372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F MUST BE OUT,WILL CHECK/////////LINE F CUTOUT BROKEN,NEED CREW ,AT LEAST 2 MEN,TO REPLACE.UP ON HILL ABT 150 FT,HAVE TO CUT PATH TO POLE AND UP POLE(VINES),GET RID OF CL FUSE WHILE ON POLE RELEASED BY CREW 074S06 REPAIRS COMPLETE & RESTORED @ 15:10//COD 4// VER/DBM
6193 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-03-11 21:25 | 2013-03-12 04:00 | 6 | 395 | 4899421 | 2370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURN OFF AT POLE 38830206A31150, SHOULD BE ABLE TO GO BACK WITH POLE TOP BRACKET, CREW IN ROUTE, 3 PHASE DEAD END WITH XFMR BANK, SINGLE PHASE TAP, DOWN GUY, AND 8 SERVICE DROPS . CC 6. VER/SDB IDC XXXX
6194 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-05-21 19:25 | 2016-05-21 19:48 | 103 | 23 | 4245381 | 2369 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENING SWITCH 165-267 TO ALLOW CREW FINISH REMOVING SWITCH 164-250/OPEN @1925 CLOSED 1948// VER/ ADH AJB
6195 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-09-10 22:41 | 2022-09-11 01:30 | 14 | 169 | 4863861 | 2366 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole 1123-d3-7026, Older style burnt up cutout door on crossarm. Do not have style to replace. Crew required to change cutout. Send to tyler lewis //cod 14
6196 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-03-19 21:01 | 2022-03-19 22:35 | 31 | 94 | 4649381 | 2362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened 3 40ts on pole 38830140B02009 @ 22:10 to safely change broken cutout//cod 23 + 8//
6197 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2018-10-13 07:22 | 2018-10-13 12:17 | 8 | 295 | 4246021 | 2360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | L/F open @148-27, 1 span of primary and neutral down between pole 148-27 and pole 65, Rick Ray and Tom Mccown coming to help make repairs. Got wire put back up and closed l/f @1217. L3/HFP
6198 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-07-16 22:49 | 2010-07-17 02:45 | 10 | 236 | 51209-1 | 2360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3410602 HAVE BAD XFMR, WILL NEED 1 LINEMAN ,MATERIAL HANDLER & 37&1/2 OR 50 KVA & RISER WIRE FOR SECONDARY.THIS IS 7200 PRI 120/240 SEC IDC XXXX
6199 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2020-01-18 17:07 | 2020-01-19 13:04 | 15 | 1197 | 4319231 | 2359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | pulled ellbow off @37830024A11292 feeding ug xfmr @37830024A11296 will refuse //ARCOS GREG RATLIFF AND CREW OUT @ 0800 SUNDAY MORNING//reairs ade power restored at 13:04 Released by crew 074H07 L3/HFP
6200 | Hazard | 3303902 | LESLIE | WOOTON | 2019-08-28 06:08 | 2019-08-28 11:45 | 7 | 337 | 4954541 | 2359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE ON 486-6 L3/HFP
6201 | Whitesburg | 3401301 | FLEMING | NEON | 2008-11-24 20:33 | 2008-11-25 00:15 | 24 | 222 | 51805-1 | 2358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401301// CUTOUT BROKE INTO AND BURNED TOP OF POLE OFF I HAVE ISOLATED ON POLE 307-3 AND I WILL MAKE MAIN LINE BACK HOT AND WILL CALL BACK WHEN I CLOSE LINE FUSE I CLOSED LINE FUSE AT 22 00 PM//LAST 2 CUST ON @ 0015// VER/DBM// VER/DBM MLR OK
6202 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2019-02-18 14:50 | 2019-02-18 15:21 | 76 | 31 | 4804301 | 2356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO OUTAGE UNTIL SW ON 38831121C00055 OPENED (76 CUST) OPENED @ 1450 CLOSED @ 1521 // Primary has burnt n2 and holding up by cutout lead on pole 1121-119 & also have broken line fuse cutout on pole 1097-22 no ouatge from either at this time.Harvey martin is coming to assist with repairs. Will be opening switches on pole 1121-C-55 when he arrives to safely make these repairs // L3/HFP
6203 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-08-06 10:19 | 2015-08-06 16:10 | 21 | 351 | 4103691 | 2356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, HAVE BAD CUTOUT ON POLE 1121-162, HAVE ISOLATED AND HAD LINE FUSE OUT, RESTORED POWER AT THIS LOC TO ALL BUT 2 CUST, AT 1115, NO TRUCKS RELEASED BY CREW 078S06 RELEASED BY CREW 078H19// VER/ ADH L3/HFP XXXHFP AJB
6204 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-08-09 19:38 | 2014-08-09 23:12 | 11 | 214 | 4348811 | 2354 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F OPEN AT POLE 398-356, FOUND BAD C/O ON POLE 398-369, MAKING REPAIRS.MADE REPAIRS CLOSED BACK IN AT 23:12.
6205 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-11-17 09:16 | 2022-11-17 10:18 | 65 | 62 | 4153661 | 2353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT CLAMP WAS BURNED OFF L/F 38830020C24542 (COD 22) OPENED L/F 38830020C24510 @ XXXX TO MAKE REPAIRS Opened @ 09:55, closed back @ 10:18. All power restored Released by crew 078S02
6206 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-12-27 10:41 | 2009-12-27 11:09 | 84 | 28 | 54666-1 | 2352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CLOSED IN FUSE @ 937-18 AND CAUSED RECLOSER TO OPERATE AND FUSE OPEN UP ON 937-15 // PATROLLING LINE//
6207 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-11-27 12:24 | 2019-11-27 16:45 | 9 | 261 | 4078231 | 2349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | two line fuses blown on pole 900-23 a an b phase //patrolling found nothing going to give these fuses a shot// cutout broke repaired// complete tt
6208 | Hazard | 3303902 | LESLIE | WOOTON | 2021-08-19 14:05 | 2021-08-19 20:36 | 6 | 391 | 4120701 | 2346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary conducter burnt down at pole 463-9 due to loose clamp,also need manuel ROW crew Released by crew 077S07
6209 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-06-06 01:38 | 2013-06-06 03:20 | 23 | 102 | 4226061 | 2346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER CALLED OUT TO PATROL LINE. POLE 70-661 BAD CUTOUT POLE 70-533 30T LINE FUSE VER/PDP IDC XXXX
6210 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-02-11 08:44 | 2012-02-11 15:15 | 6 | 391 | 4334021 | 2346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S08 RELEASED BY CREW 077S08 == HOT LINE CLAMP BURNED OFF === REPAIRED///VER/CRB IDC XXXX
6211 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-08-25 17:43 | 2020-08-25 18:18 | 67 | 35 | 4368021 | 2345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Primary laying on arm at 38830045B22789. laying on insulate portion of chicken wing. will need to open to repair, crew reqd. back yard. Released by crew 078S04./arrived RM opening blades 38830044D37065 opened@17:43 closed @18:18 please close tic RM
6212 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2012-04-25 15:55 | 2012-04-25 16:02 | 335 | 7 | 4707311 | 2345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OPENED CKT TO DE-ENERGIZE FAILED EQUIPMENT VER/ARN IDCC CNT680 XXXX
6213 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-05-08 03:40 | 2016-05-08 06:55 | 12 | 195 | 4186461 | 2340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RIGHT HANDPHASE BLOWN AT POLE 794-246//FOUND BROKE INSULATOR AT 794-98//LIFTED HOT TAP AT 794-51//RESTORED UP TO LIFTED HOT TAP AT 6:55////ALL CUSTOMERSRESTORED, THIS PHASE DOESNT FEED ANYTHING PAST THIS ///WILL NEED BIG BUCKET TO CHANGE INSULATOR//PLEASE SEND TO CLIFF FREEMAN FOR JOB TO HAVE CREW REPLACE INSULATOR//COMPLETE//EM RELEASED BY CREW 079S01 VER/KEP
6214 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-09-11 18:23 | 2011-09-11 21:38 | 12 | 195 | 4857971 | 2340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST MIS-MAPPED..XFMR FUSE OUT ON 942B2-956..WILL INSPECT & RE-FUSE.//.REPLACED BAD CUTOUT.REFUSED.BAD XFMR.NEED 2 MAN CREW.CAN USE MATERIAL HANDLER..CALLED J REED.HE IS SENDING 2 MEN.// RELEASED BY CREW 080S01 // 12 COD IDCC CNT19, PN786 XXXX
6215 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-07-08 04:00 | 2014-07-08 10:30 | 6 | 390 | 4202561 | 2340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | PAUL MUNCY OPENING U/G DIP ON POLE 1445 TO REPLACE LIVE FRONT PADMOUNT 1413 SCHEDULED OUTAGE FROM 0400 TO 1200// VER/CRB
6216 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-12-14 13:15 | 2015-12-14 16:15 | 13 | 180 | 4531261 | 2340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUTS ON POLE 38821137A00483 AND 38821137A00369. I GOT ONE MAN AND BIG BUCKET EN-ROUTE TO CHANGE THE TRANSFORMER CUTOUT ON THE TAKE OFF POLE./CLOSED 1615// VER/ ADH
6217 | Pikeville | 3409502 | BURDINE | LEVISA | 2016-12-24 06:11 | 2016-12-24 08:14 | 19 | 123 | 4233621 | 2337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ONPOLE#335-138 WILL PATROL//// FOUND ANOTHER BAD CUTOUT ON POLE #311-168 DOES NOT FEED ANYTHING WILL ISOLATE BAD CUTOUT//// CLOSED LINE FUSE IN @ 08:14 AND RESTORED SERVICE//COD 19
6218 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2019-09-30 15:27 | 2019-09-30 16:24 | 41 | 57 | 4075911 | 2337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hotline clamp burnt off on recloser 834-638. Making repairs. Replaced hotline clamp and restored rec @ 16:24. sh
6219 | Hazard | 3303901 | LESLIE | HYDEN | 2008-12-12 18:47 | 2008-12-13 14:15 | 2 | 1168 | 57842-1 | 2336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2 SPANS OF PRIMARY AND 1 SPAN OF NEUTRAL DOWN WILL HAVE TO WAIT TILL WATERIS DOWN MORE RELEASED BY CREW 077S01/ WR#27667546 / RESSAGED CONDUCTORS RESTORED POWER P HICKMAN MD FILED VER/LDA L3/KEP IDC CHANGED CAUSE FROM ICE XXX
6220 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-07-18 06:43 | 2012-07-18 16:27 | 4 | 584 | 4753101 | 2336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | CUTOUT WENT BAD === TOP OF POLE BURNED OFF === NEED LINE CREW == 37830345B00063 NEEDS REPLACED === NEED 45 /4 15 KVA TRANSF CUTOUT AND GO TRACK == RELEASED BY CREW 077S03 POWER RESTORED AT POLE 183 AT 16:27. 077H18 IDC XXXX
6221 | Hazard | 3309302 | VICCO | JEFF | 2012-02-21 19:32 | 2012-02-22 15:00 | 2 | 1168 | 4473271 | 2336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT ELLIOT TO CHANGE VER/HFP L3/HFP
6222 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2014-09-09 09:43 | 2014-09-09 17:30 | 5 | 467 | 4482501 | 2335 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OF UNDERGROUND SERVICE IS BAD //// DAVE SAMMONS AND BILL JOHNSON ENROUTE TO HELP LOCATE SUB-SURFACE BOX//SERVICER OPENING TRANSFORMER 24-1054 TO MAKE REPAIRS//ONE LEG OF UNDERGROUND SERVICE IS BAD //// DAVE SAMMONS AND BILL JOHNSON ENROUTE TO HELP LOCATE SUB-SURFACE BOX//// REPLACED BAD PLACES IN UNDERGROUND WITH NEW SPLICES /// GOOD VOLTAGE NOW 121/121/242// COD 5// VER/ ADH AJB
6223 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-04-21 11:53 | 2008-04-21 15:25 | 11 | 212 | 53011-1 | 2332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3001101// RELEASED BY CREW 078S08........................REPLACED ARRESTER AND CUTOUT ON POLE 68-767//COD 11// VER/DBM IDC XXXX
6224 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-05-02 12:39 | 2017-05-02 14:30 | 21 | 111 | 4732231 | 2331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 122-8 WIRE CAME UNTIED FROM INSULATOR/NO CREW REQUIRED/123-2 15T/ ISO 38830123000002/ COD 21/ VER/BOW AJB
6225 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-09-30 20:32 | 2019-10-01 09:28 | 3 | 776 | 4078171 | 2328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NC CREW REQ/ bad 15 kva xfr 160-1,,need to 25kva,,no trucks in yard,septic system,can take 6 wheeler to pole Released by crew 078S05///repairs made///complete BR
6226 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-09-12 15:56 | 2021-09-12 23:55 | 8 | 479 | 4233711 | 2328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | URD riser is open that feeds padmount 71-204 thru 71-208, checking. Isolated primary cable going between 71-206 and 207, closed riser @71-204 back in @1739. 811 Tick# 2109120216/206-207 repaired 2355/leaves 207-208 out stillURD riser is open that feeds padmount 71-204 thru 71-208, checking. Isolated primary cable going between 71-206 and 207, closed riser @71-204 back in @1739. 811 Tick# 2109120216 Released by crew 074S05//power restored on pad MT 71-208 @11:55/bad cable from 71-207 to 208 Rele
6227 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-03-06 07:13 | 2018-03-06 10:27 | 12 | 194 | 4970101 | 2328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-12 ISO OCR 37830328D00276 OPENED @ 0811 CLOSED @ bad cutout on pole 328-276, opened recloser on 328-276 & stepdown on 328-267 at 08:11 to isolatebad cutout on pole 328-276, restored power at 10:27.. COD-12 ISO OCR 37830328D00276 ENTERED MD
6228 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-02-22 08:46 | 2011-02-22 11:45 | 13 | 179 | 60075-1 | 2327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 473-69 BURNED TOP POLE OFF LINE FUSE OPEN ON POLE 473-159... MADE REPAIRS RESTORED POWER AT 11:45//COD 13//CKT# 3314401/// VER/DBM IDC XXXX
6229 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-12-23 21:50 | 2021-12-24 00:49 | 13 | 179 | 4222871 | 2327 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cleared bad arrestEr on 553-62. Power restored @ 00:49/ ISO 37830529000083/ cod 13
6230 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-08-28 19:53 | 2008-08-28 20:24 | 75 | 31 | H57119-1 | 2325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202201// TRANSF FUSE BLOWED//1957 OPENED C PHASE ON REC 746/243//COD 753202201// TRANSF FUSE BLOWED. CUTOUT BAD//VER/CRB IDC DID WE OPEN OR WAS IT OPEN IDCC DUP TO OPEN RECLOSER XXXX
6231 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-04-25 15:00 | 2011-04-25 22:45 | 5 | 465 | 64321-1 | 2325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LEAD BURNED OPEN AT XFMR//BAD 50 KVA CREW ON THE WAY RELEASED BY CREW 074H14 COD-5 ISO TF 38831125D00598 VER/HFP L3/HFP IDC XXXX
6232 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-10-16 01:05 | 2018-10-16 14:00 | 3 | 775 | 4257361 | 2325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse 183-38 open,dead end xfr,KP pole burnt off @ 183-2004, grounded @ 183-2003 Released by crew 078S0pole replaced all cust restored @ 1400 please close ticket thanks.bt L3/HFP
6233 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2013-04-28 05:50 | 2013-04-28 06:21 | 75 | 31 | H4052631 | 2325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT..SOLID BLADE CUTOUT ON C PHASE POLE 964C99.CUTOUT BROKE IN HALF.HOT SIDE HANGING IN CLEAR.CAN REPLACE SAFELY..//.MIDDLE PHASE CUTOUT ALSO GOING BAD.NEED THREE 300A CUTOUTS..2 MEN.BIG BUCKET.WILL HAVE TO DROP LINE OUT..//..OPENED RECLOSERS ON 964B153 @ 05:50..REPAIRS MADE..CLOSED RECLOSERS @ 06:21 ALL CUSTOMERS RESTORED..JRV.J REED & R THOMAS.04/28/13 VER/ARN IDC XXXX
6234 | Hazard | 3310502 | HADDIX | CANOE | 2020-06-30 21:14 | 2020-07-01 16:36 | 2 | 1162 | 4097191 | 2324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva 7200 xfm. manual. need line crew, row crew, xfm and 7200 cutout and bracket Released by crew 077S10
6235 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-02-19 14:43 | 2019-02-19 20:15 | 7 | 332 | 4807901 | 2324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on 284-30.i can make repairs. Released by crew 079H03cutout failed on 284-30.i can make repairs. replaced cutout on 284-30.restored power at 20:15
6236 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-12-29 02:38 | 2013-12-29 08:10 | 7 | 332 | 4208061 | 2324 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1108C-321. NEED 1 MAN TO HELP. MANUEL //P. HICKS TO ASSIST // LINE FUSE OUT ON POLE 1108C-57. CLOSED LINE FUSE ON 1108C-57 @ 08:10 VER/PDP L3/HFP IDCC CDC92 XXXX
6237 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2018-01-31 13:27 | 2018-01-31 13:50 | 101 | 23 | 4787431 | 2323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | pole 1123-7029 xarm braces broken, bad 8 xarm, crew reqd.truck ok Released by crew 078S07..opening fuses on 1123-7042,,opened @1327,,repairs made and closed @1350..all power restored Released by crew 078H03/ ISO 39831123D37042/ COD 101
6238 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-06-18 18:21 | 2011-06-18 22:39 | 9 | 258 | 4340741 | 2322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED C/O., RESTORED AT 2239. VER/SDB
6239 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-07-31 07:22 | 2008-07-31 08:48 | 27 | 86 | 62558-1 | 2322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3413401// CLEARED ARRESTER AND CREATED ORDER TO REPLACE AT LATER DATE / GXJ//COD 27// VER/DBM IDC XXXX
6240 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-03-16 16:39 | 2014-03-17 12:00 | 2 | 1161 | 4497711 | 2322 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT ON POLE 77-7 BAD XFMR ON POLE 77-7 . MANUEL , NEED LINE CREW & 25KV 720 XFMR , CUTOUT IS OK. ALSO NEED ROW CREW. RELEASED BY CREW 075H04 REPLACED TRANSFORMER AND RESTORED POWER AT 1200 VER/SEF
6241 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-01-07 10:43 | 2019-01-07 12:10 | 125 | 87 | 4636621 | 2319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout// opened recl at 1152 closed @ 1210 L3/HFP
6242 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2016-08-05 12:59 | 2016-08-05 14:00 | 38 | 61 | 4738671 | 2318 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 21-3577 HOT TAP BURNT OFF REPAIRED ON B PHASE VER/CRB AJB
6243 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2011-08-25 15:09 | 2011-08-25 20:40 | 7 | 331 | 4756331 | 2317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | HAVE AN UNDERGROUND FAULT. CREW AND DUTY SUPERVISOR ON SITE TO HELP TROUBLESHOOT. FIRST SPAN OF UG CABLE FROM RISER BAD. ISOLATED AND WILL BE TRYING TO FIND BAD SPOT. REPAIRED CABLE AND RESTORED @ 20:40. SH//COD 7// VER/DBM IDCC CDC83 XXXX
6244 | Hazard | 3309302 | VICCO | JEFF | 2020-05-05 07:33 | 2020-05-05 13:04 | 7 | 331 | 4799701 | 2317 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Pole 348B/444 transformer out bad lighting arr. 348/448 transformer out 348B/37 bad lighting arr. line fuse on 348B/100 and transformer out on 348B/100 power on
6245 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2017-01-05 18:56 | 2017-01-06 04:35 | 4 | 579 | 4272321 | 2316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE HAS BURNT OFF, CANT GET TO POLE, SNOW COVERED HILL VERY SLICK, CALLED FOR HELP. COMP. POWER RESTORED//COD 4 L3/HFP
6246 | Pikeville | 3409502 | BURDINE | LEVISA | 2016-12-10 05:26 | 2016-12-10 10:15 | 8 | 289 | 4182021 | 2312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNDT INTO @312-55, IT HAS BOTH TAPS OUT ON THIS POLE, WILL BE MAKING REPAIRS. PUT ON A NEW STIRRUP AND REFUSED @1015. VER/CRB L3/HFP XXXHFP
6247 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2009-08-11 23:56 | 2009-08-12 04:45 | 8 | 289 | 59473-1 | 2312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT == BAD CUTOUT ON POLE 562-6 REPLACED == REFUSED== POWER OK VER/PDP IDC XXXX
6248 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-12-17 08:07 | 2016-12-17 13:37 | 7 | 330 | 4202731 | 2310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR RUSE OUT ON POLE 225D-180 . CLOSED XFMR FUSE @ 9:35 . CAME BACK OUT @ 9:40 . NEED 50KVA XFMR 7200 , BIG BUCKET . RELEASED BY CREW 075H04 37830225D00180 VER/AWD
6249 | Hazard | 3302703 | HAZARD | HAZARD | 2010-01-10 08:45 | 2010-01-10 12:15 | 11 | 210 | 51642-1 | 2310 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY BUSHINGS AND LEADS BURNED UP ON 100 KVA CALLING FOR CREW TO ASSIST VER/KEP L3/KEP IDC XXXX
6250 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-07-23 00:20 | 2019-07-23 09:57 | 4 | 577 | 4773961 | 2308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke broke 38830850000026
6251 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-11-30 15:13 | 2010-12-01 10:27 | 2 | 1154 | 61168-1 | 2308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37930301 // BAD CUTOUT ON POLE 128-24 // WILL WORK 12/01 PER DUTY SUPERVISOR IN REMOTTE LOCATION AND WATER IN RIVER TO SWIFT TO WORK SAFELY TONIGHT.BROKEN CUTOUT ON POLE 128-24 WILL REQUIRE CREW WITH BOAT.BROKEN CUTOUT ON POLE 128-24 WILL REQUIRE CREW WITH BOAT.= VERY BAD LOCATION, DUTY SUPERVISOR DECIDED TO WAIT UNTILL DAYLIGHT TO REPAIR. RELEASED BY CREW 077S04RESTORED POWER AT 1027 JKC//VER/CRB IDC DCMT XXXX
6252 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2009-01-16 22:33 | 2009-01-17 08:10 | 4 | 577 | 56491-1 | 2308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001102// CALLED P TOLLIVER-BAD 10KVA NEED 25KVA AN NEW CUTOUT AN RISER WIRE RELEASED BY CREW 078S07 VER/KEP MD FILED L3/KEP
6253 | Hazard | 3310502 | HADDIX | CANOE | 2009-04-01 05:14 | 2009-04-01 14:50 | 4 | 576 | 63657-1 | 2304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-4 WR # 29181179 //TRANS FUSE HANGING DOWNTRANS FUSE HANGING DOWN, TRANSFORMER IS BAD CALL FOR CREW AND JIM IS GETTING TOGETHER , GREG FUGATE WILL BE COMMING TO CHANGE OUT, HE DONT START UNTIL 1000 SO HE WILL CALL FOR THIS TICKET RELEASED BY CREW 077S05 L3/HFP IDC XXXX
6254 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-10-10 11:54 | 2018-10-10 13:30 | 24 | 96 | 4215211 | 2304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30t open @ 69-1620, bad 12kv c/o @ 69-1647 L3/HFP
6255 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-11-03 17:37 | 2015-11-03 22:25 | 8 | 288 | 4407151 | 2304 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 94-1075 BAD LUG ON TRANS MELTED OFF NEED 50KVA TRANS.. TRUCK TO POLE RELEASED BY CREW 078S08.. CREW ON SITE TO REPAIR BAD XFMR.. ETR 22:30 XFMR OPENED AT 22:00 BACK ON AT 22:25 PLEASE CLOSE TICKET CAY// VER/ ADH L3/HFP XXXHFP
6256 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2009-02-18 06:26 | 2009-02-18 11:55 | 7 | 329 | 63720-1 | 2303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400601//BAD CUTOUT ON POLE37830187A00057 REPLACED CUTOUT & REFUSED LINE//COD 7// VER/DBM IDC XXXX
6257 | Hazard | 3309301 | VICCO | REDFOX | 2010-02-28 07:41 | 2010-02-28 10:38 | 13 | 177 | 61643-1 | 2301 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR# 34050585 //PATROLLING LINE, RESTORED POWER BUT HAVE BAD ARRESTER, WILL NEED BIG BUCKET AND 1 MAN // TOOK LINE BACK OFF AT 1235 ON AT 1305 SEE DUPLICATE RECORD H1132900-1 FOR OUTAGE TO REPLACE ARRESTOR VER/HFP L3/HFP IDC XXXX
6258 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-05-19 01:05 | 2012-05-19 01:30 | 92 | 25 | 4808591 | 2300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAD TO OPEN C PHASE LINE FUSE TO REPLACE CUTOUT SAFELY// 92 COD ISO POLE 1123-7042 DKG SEE ORIGINAL 4808591 WHICH WAS A FULL POWER CALL IDCC TON105, ESTIMATED TIME ON XXXX
6259 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-06-13 19:20 | 2010-06-13 20:10 | 46 | 50 | 63098-1 | 2300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREWS OPENED RECLOSER IN ORDER TO MAKE REPAIRS RELATED TO ORDER 62946-1//COD 46// VER/DBM
6260 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-12-14 10:28 | 2022-12-14 12:23 | 20 | 115 | 4258781 | 2300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout Blown at 38831003B00067had 15T line fuse open at pole 1027-C-196/// found a broke cutout a pole 1003-c-67 got 7200 cutout changed a pole 1003-C-67 ad got 15T line fuse at pole 1003-C-196 restored at a time 03 12:23
6261 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-05-29 16:45 | 2019-05-30 11:55 | 2 | 1150 | 4369911 | 2300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | c/r bad xformer 15 kva 19.9 120/240 truck accessible two man line crew material bucket Released by crew 074S10/// CREW ONSITE, REPLACED 15kva POWER RESTORED. Power on at 11:55
6262 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-04-09 18:08 | 2015-04-09 21:58 | 10 | 230 | 4298961 | 2300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CUSTOMER ON 809-338 IS FEED FROM LINE FUSE 809-744, OFF THE KENWOOD HAGER HILL, POLE WAS ON FIRE///RYAN NEWSOME HAS ARRIVED///WERE BACK ON HILL MAKING REPAIRS////PHASE CAME OFF INSULATOR ON POLE 809-872 BURNING TOP OF POLE OFF///THIS CUST FEEDS FROM XFMER POLE 809-874///CLOSED LINE FUSE ON POLE 809-744 @ 21:58///COMPLETE BR/FAULT POLE NOT ON MAP YET/MD MAP FOR CUS/ADH/ POLE 873 NOT YET ON MAP IN LINE AFTER 809-871// VER/ ADH
6263 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-07-27 21:10 | 2014-07-27 21:30 | 115 | 20 | 4296641 | 2300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO 4295271 // CREW OPENED RECLOSER TO ALLOW THEM TO MAKE REPAIRS IN THAT ORDER /// COD=115// VER/DBM AJB
6264 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2022-06-08 22:44 | 2022-06-09 11:30 | 3 | 766 | 4043481 | 2298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Defective 25kVA 700 Transformer 38821139A00106/ No Truck Access/ vines got into transformer on pole 38821139A00106 causing fuse to blow clearing vines to try to get the fuse back in..bad 25 kva 7200 120/240 on pole 38821139A00106 no truck will need line crew
6265 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-08-23 21:26 | 2022-08-24 09:50 | 4 | 744 | 4786781 | 2297 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva on pole 1056-131 19.9 will need crew..talked to shawn goble and they are going to hold it until the morning Released by crew 079S02/// Crew onsite.. Opened L?f to safely make repairs @08:45 and restored all @09:50 Released by crew 074H06
6266 | South Williamson | 3411401 | DEWEY | INEZ | 2019-01-23 20:09 | 2019-01-24 00:56 | 8 | 287 | 4712921 | 2296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout open on 744-B3-668.found bad cutout on 744A4302.replaced cutout.restored power at 00;56/ ISO 38830744B30668/ COD 8 (XFMR is on load side of Fuse on pole 744-668, Also customer premise #037360110 should be on pole 38830744B00273) MD DONE
6267 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-02-28 23:24 | 2019-03-01 01:39 | 17 | 135 | 4940331 | 2295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse out on 1016C-3.failed arrester on 1016-C-31.i can make repairs.made repairs,restored power at 01;39
6268 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-05-05 02:43 | 2017-05-05 10:22 | 5 | 459 | 4750611 | 2295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE INTO ON POLE 283-134, ONE MAN AND A BIG BUCKET IS COMMING TO ME TO CHANGE IT OUT COD-5 ISO LF 37830283000130 VER/HFP L3/HFP
6269 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-08-11 23:24 | 2021-08-12 12:08 | 3 | 764 | 4042621 | 2292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRIED TO CONTACT CUSTOMER NO ANSWER HOLDING TIL DAYLIGHT TO PATROL/bad 50 kva crew will contact dispatch Released by crew 078S03 Arrived RM replaced xfm volatge good fuse in @ 12:08 please close tic RM
6270 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-08-16 01:58 | 2018-08-16 08:20 | 6 | 382 | 4958551 | 2292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines // Pole 118-6124, cutout door failed. Fuse back in at 08:20 Xfer on pole 38830118D16123 is fed from 38830118D16124 // ADDED 1 CUST TO THIS RECORD L3/HFP
6271 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-10-14 20:18 | 2011-10-15 15:23 | 2 | 1145 | 4983681 | 2290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CONN. ON TRANS HOLD TILL SAT WILL NEED CREW BAD 50 KVA NEED TREE CREW NO TRUCKS TO POLE SEND TO JIM LINKOUS RELEASED BY CREW 078S08//ALSO NEED 4/0 RISERS PER SERVIECR // BAD XMFER CHANGED 50KVA TO 25KVA//COD 2// VER/DBM IDC XXXX
6272 | Hazard | 3310502 | HADDIX | CANOE | 2009-08-17 16:40 | 2009-08-17 19:36 | 13 | 176 | 62343-1 | 2288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WE HAVE FUSE OUT ON POLE 37830027000008 AND FUSE OUT ON POLE 37830027000030////// REFUSED BOTH LINE FUSE,S POWER RESTORED.//COD 13// VER/DBM IDC XXXX
6273 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2017-02-07 16:40 | 2017-02-07 20:08 | 11 | 208 | 4367771 | 2288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE L/F CLAMP BURNDT INTO ON POLE 22-41, POLE IS MANUAL WILL NEED 1 MAN TO HELP GRUNT, ALSO WILL HAVE TO OPEN A PHASE AND A TRANS. ON THIS POLE TO MAKE REPAIRS. MADE REPAIRS AND CLOSED L/F BACK IN @2008. //DID NOT OPEN A PHASE COD 11 VER/CRB // BUS OBJ AGREES WITH B PHASE OUTAGE = L3/HFP XXXHFP
6274 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-12-30 01:23 | 2013-12-30 10:55 | 4 | 572 | 4211321 | 2288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 644-28 LINECREW WILL NEED TO DO OWN TAGGING AND GROUNDING, POLE 28 IS BURNT OFF. NEEDS 4FT FIBERGLASS POSTTOP PIN AND INSULATOR INSTALLED. PROB TAKE SERVICE TRUCK TO POLE. LINECREW REQUIRED. WILL WORK AT REGULAR WORK TIME AS PER SET GUIDELINES // VER/CRB IDC XXXX
6275 | Pikeville | 3402002 | KEYSER | STONECOAL | 2013-04-15 14:05 | 2013-04-15 16:12 | 18 | 127 | 4010781 | 2286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SDB / OPENED SW AT POLE 1129-A-311 TO SAFELY INSTALL NEW IN-LINE SW AT POLE 1129-A309. CC 18. OUTAGE FROM 1405-1612. ASSOCIATED W/ PO ORDER 4995641. VER/SDB IDC XXXX
6276 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-04-29 04:35 | 2008-04-29 12:12 | 5 | 457 | 55321-1 | 2285 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408402///TOP OF POLE BURNED OFF,WILL CONTACT NEEDED CREWS ABT MATERIAL NEEDS RELEASED BY CREW 074S06 FRAMED DOWN ON POLE//VER/CRB IDCC CNT14 XXXX
6277 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-08-02 07:02 | 2012-08-02 09:45 | 14 | 163 | 4882811 | 2282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT ON 1115C44.PATROLLED..FUSE ALSO BLOWN ON LATERAL THAT CROSSES INTO APCO ON POLE 1115D73.BAD CUTOUT, POLE TOP BURNT OFF ON 1115D101 ON WV SIDE.PLEASE NOTIFY ROANOKE DDC.ALL OF OUR LINE IS UP & CLEAR.CHECKED HZRDS.//..RE-FUSED LINE.RESTORING ALL CUSTS EXCEPT 1 APCO CUST IN WV..JRV.08/02/12 VER/KEP IDC XXXX
6278 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-06-06 12:08 | 2008-06-06 13:05 | 40 | 57 | 59106-1 | 2280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND L/A BLOWN CUT IN CLEAR 1099-6057 LINE FUSE OPEN AT 1099-6048POWER SHOULD BE RESTORED BY 13 30 VER/HFP
6279 | Hazard | 3303902 | LESLIE | WOOTON | 2013-11-25 10:55 | 2013-11-25 11:25 | 76 | 30 | 4072511 | 2280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW FOUND PHASE OFF INSULATOR AND HAD TO OPEN RECLOSER TO ALLOW THEM TO MAKE REPAIRS SAFELY // COD-76 ISO OCR 37830415A40160 // OFF @ 1055 ON @ 1125 VER/HFP L3/HFP IDC WHERE WAS THE LINE OFF INSULATOR XXXX
6280 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-09-23 01:40 | 2021-09-23 02:20 | 57 | 40 | 4279781 | 2280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Pole 38830070B33010, crossarm braces broken, 8ft crossarm looks rotten and needs changed as well. Crew required Released by crew 078S02 / opened 3- 65T @ 0140 on 70-1048 to replace xarm/ Line Fuses back in @ 0220/ please close ticket/MLH//ISO 38830070B31048//cod 55
6281 | Hazard | 3302703 | HAZARD | HAZARD | 2008-08-21 11:58 | 2008-08-21 14:30 | 15 | 152 | 53725-1 | 2280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT & AND CONNECTION ON SECONDARY == REPLACED CUTOUT & REDONE CONNECTION ==//3302703//VER/CRB IDC XXXX
6282 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-06-02 14:19 | 2020-06-02 16:19 | 19 | 120 | 4944691 | 2280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50kva, 7200, 120/240 on pole 38830045A31143. Crew required, trucks to pole Released by crew 078S02. time restored 1619 wdr
6283 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-12-25 14:18 | 2009-12-26 09:17 | 2 | 1139 | 55339-1 | 2278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RESTORED COMPLETE 122609 14:30 SC RELEASED BY CREW 077S04
6284 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2009-10-30 12:16 | 2009-10-30 14:30 | 17 | 134 | 52798-1 | 2278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIM BROKE IN CLEAR AT POLE 1061-20,LINE FUSE NOT OUT BUT WILL HAVE TO OPEN IT WHEN READY TO PUT WIRE UP.#4 COPPER PRIM COND.WILL TRY TO GET HELP AND WIRE COD-17 /OPENED 1061-14 AT 14:16,CLOSED AT 14:30 AFT REPAIRS WERE COMPLTED VER/KEP L3/KEP IDCC PN149 XXXX
6285 | Pikeville | 3408101 | SALISBURY | PRINTER | 2019-08-02 08:12 | 2019-08-02 12:25 | 9 | 253 | 4830391 | 2277 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6t fuse out cutout broke into fell down on transformer. i will be making repairs changed cutout everything ok
6286 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-12-17 07:08 | 2016-12-17 16:37 | 4 | 569 | 4202541 | 2276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 292-4 POLE FIRE OPEN RECLOSER AT 292-402 AT 0825 HRS/RECLOSER BACK IN AT 0900 HRS 4 CUSTOMERS STILL OFF CREW REQUIRED WITH POLE TOP EXTENSION TRUCK OK 4X4 BUCKET RELEASED BY CREW 078S03/CREW ON SITE/FETR 1715/VEM/REPAIRS MADE AND ALL CUST RESTORED 1637/PLASE CLOSE TICKET/THANKS/VEM 38830292C20402 38830292C00004 VER/AWD // SEE 4202961 FOR RECL OUTAGE == L3/HFP HFPC CDC86 LCD38830292C20402
6287 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-07-04 10:14 | 2015-07-04 16:30 | 10 | 376 | 4719751 | 2275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 37830180000178 HAS BURNT OFF DUE TO BAD CUTOUT, REPLACED POLE VER/CRB
6288 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2012-09-08 07:28 | 2012-09-08 12:12 | 8 | 284 | 4029091 | 2272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | FOU ND LINE FUSE OUT ON POLE 901-5574, PATROLLED FOUNDED BURSTED 8 FT CROSSARM ON POLE 901-5013, CREW REQ, CAN USE TRUCK IN BEHIND SOUTH SHORE CHURCH OF GOD OFF CECIL ROBBINS AVE. RELEASED BY CREW 078S06 ///VER/CRB L/3 CRB IDC XXXX
6289 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-08-18 09:28 | 2010-08-18 11:50 | 16 | 142 | 57469-1 | 2272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR/VER/CRB IDC XXXX
6290 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2020-07-24 15:24 | 2020-07-24 20:30 | 11 | 306 | 4227271 | 2271 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 KVA CSP transformer, crew required to make repairs, will replace with 75KVA for load issues.//OPENED L/F 37830023D40077 TO MAKE REPAIRS//OFF @1839 ON @b 2006, crew required to make repairs, will replace with 75KVA for load issues. will have to de-energize line on pole 23-D-77 to make repairs. opened at 18:39bad 50 KVA CSP transformer, crew required to make repairs, will replace with 75KVA for load issues. will have to de-energize line on pole 23-D-77 to make repairs.bad 50 KVA CSP tr
6291 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-11-28 07:30 | 2010-11-28 08:12 | 54 | 42 | H60215-1 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL BE DISPATCHED AFTER DAYLIGHT/OPENED 224-145 AT 0730 HRS TO MAKE REPAIRS./224-145 BACK IN AT 0812 HRS RELEASED BY CREW 078S03 141CUSTOMERS OUT OPENED 54 AT 0730 AND RESTORED ALL AT 0812 VER/ARN IDC XXXX
6292 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2016-03-29 08:47 | 2016-03-29 15:18 | 9 | 391 | 4001361 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WHILE SWITCHING SOS 3183 REV 39// OCR @ 620-D3-325 WAS FOUND TO HAVE C PHASE RISER BURNT - RESULTING IN OUTAGING 157 CUSTOMER - FROM THIS POLE TO 549-97 (TEMP NO)// BYPASSES CLOSED AT 1016 - RESTORING UP TO 573-102
6293 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-10-26 22:03 | 2010-10-26 23:24 | 28 | 81 | 65275-1 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS OPEN LINE AT 2303 AND CLOSED AT 2324 VER/ARN IDC XXXX
6294 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2020-05-28 08:04 | 2020-05-28 09:07 | 36 | 63 | 4918761 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | jumper against pole, problem fixed and back in at 09:07
6295 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2013-10-16 13:44 | 2013-10-16 14:12 | 81 | 28 | 4940531 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078S11//BLOWN ARRESTER VER/CRB L/3 CRB IDC XXXX
6296 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-04-08 16:21 | 2011-04-08 20:33 | 9 | 252 | 51877-1 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 39501163 // NEED CREW TRY 30T FUSE ON POLE 163-31 BLOW FUSE AGAIN RELEASED BY CREW 078S08/CREW ON SITE/BAD LA 163-131/CLEARED/FETR2100/VEM/POWER RESTORED TO ALL CUST 2033/PLEASE CLOSE TICKET/THANKS/VEM COD-9 ISO LF 38830163000031 VER/HFP L3/HFP IDC XXXX
6297 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-04-19 10:52 | 2008-04-19 16:16 | 7 | 324 | 52280-1 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308503//REMOVED CLAMP ON FUSE POLE 268-15 POLE268-18 IS FAULT POLE RELEASED BY CREW 077H15 REPLACED POLE AND RESTORED POWER ------------ JEFF COMBS//VER/CRB AJB
6298 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2010-08-13 13:18 | 2010-08-13 17:30 | 9 | 252 | 54252-1 | 2268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA BAD 7200 HUNDERED == NEED LINE CREW ALSO NEED A 100 KVA TRANSF ==POWER OK VER/HFP L3/HFP IDCC PN89 XXXX
6299 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-03-02 18:17 | 2014-03-03 13:09 | 2 | 1132 | 4444471 | 2264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN AM HOURS WHEN ROADS ARE SAFE // STS BROKE CUTOUT ON TRANSFORMER, CALL FOR HELP VER/SEF
6300 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-12-04 12:07 | 2014-12-04 13:05 | 39 | 58 | 4833211 | 2262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, FOUND BAD CUTOUT ON POLE 181-173, REPLACED CUTOUT, ALL POWER RESTORED/// ISO 37830181C00299/ COD 39/ VER/BOW L3/HFP AJB
6301 | Pikeville | 3421001 | BREAKS | CITY | 2022-07-14 09:23 | 2022-07-14 15:40 | 6 | 377 | 4487241 | 2262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | All 3 line fuses open on 197-94 will patrol///Top of pole 37820197000041 is burnt off @ the braces will need line crew might can lower Released by crew 074S02//restored @15:40
6302 | Whitesburg | 3401301 | FLEMING | NEON | 2008-07-14 23:56 | 2008-07-15 00:13 | 133 | 17 | 52735-1 | 2261 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401301//SERVICER OPENED RECLOSER TO CHANGE OUT SOLID BLADE CUTOUT//SEE ORDER 52714-1//COD 133// IDC XXXX
6303 | Hazard | 3311103 | STINNETT | WENDOVER | 2020-07-31 07:52 | 2020-07-31 11:38 | 10 | 226 | 4262221 | 2260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Repaired blown arrester on pole 37830461000085 Power restored @ 11:38
6304 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2016-06-12 09:29 | 2016-06-12 13:15 | 10 | 226 | 4337991 | 2260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 67 B 28 BAD 12 KV CUT OUT, CREW REQD. STATION ZONE /// PLEASE DON`T FORGET THE FETRPOLE 67 B 28 BAD 12 KV CUT OUT, CREW REQD. STATION ZONE /// PLEASE DONT FORGET THE FETR.CREW ON SITE,,REPLACED CUTOUT AND ADDED NEW CUTOUT SO BOTH TAPS ARE NOW FUSED INDIVIDUAL..PLEASE MAKE MAP DISCR,,,ALL POWER RESTORED COD-10 ISO LF 38830067B00028 VER/HFP L3/HFP
6305 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2015-06-08 18:39 | 2015-06-08 22:25 | 10 | 226 | 4535311 | 2260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ 254C-130 REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT// VER/ ADH AJB
6306 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-06-19 16:42 | 2009-06-19 17:02 | 113 | 20 | 58104-1 | 2260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW OPENING RECLOSER IN ORDER TO REPAIR BROKEN FUSE ON FUSE POLE 375-43 ON ORDER 59086 COD-113 ISO 37830374D00119 L3/HFP IDC XXXX
6307 | Hazard | 3302703 | HAZARD | HAZARD | 2012-04-27 13:12 | 2012-04-27 15:05 | 20 | 113 | 4717251 | 2260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830296A30776--- POWER RESTORED. COD-20 ISO TF 37830296A30776 VER/HFP L3/HFP IDC XXXX
6308 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-01-17 02:34 | 2022-01-17 06:45 | 9 | 251 | 4359261 | 2259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830165C00226 pri and neu sagged touching-resagged-and also found branch hanging on pri and tran pole 38830165C00289--38830165c00226 15t lat in at 06:45-all good-ds011722
6309 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2021-07-03 06:46 | 2021-07-03 08:20 | 24 | 94 | 4852651 | 2256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | replaced cutout door. time on 08:20
6310 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-06-02 18:11 | 2009-06-02 19:45 | 24 | 94 | 61021-1 | 2256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS OUT ON POLE 168-6. I AM PATROLLING LINE NOW. CUTOUT IS BROKEN ON POLE 168-25. I AM GOING TO CHANGE CUTOUT WHILE POWER IS OFF. I HAVE TO CLIMB POLE AND IT IS VERY CLOSE TO PRI. CONDUCTOR. I CHANGED CUTOUT AND CLOSED LINE FUSE IN AT 19:45. VER/KEP L3/KEP
6311 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-02-19 22:50 | 2015-02-20 02:15 | 11 | 205 | 4045601 | 2255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 38830068A00039 6A PRI DOWN TO38830068A00037 TRUCK TO POLE CAN WAIT TO DAYLIGHT NEED FLAGGERS// POLE38830068A00531 20T SEND TO MAPPING RELEASED BY CREW 078S08//POWER RESTORED @ 0215//MADE MDC// RELEASED BY CREW 078Q12 VER/HFP L3/HFP
6312 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-11-03 03:08 | 2014-11-03 10:39 | 5 | 451 | 4694671 | 2255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE OUT LOOK LIKE FUSE BROKE INTO// ISO 37830004C00014/ COD 5
6313 | Hazard | 3420001 | SOFT SHELL | VEST | 2013-03-25 00:25 | 2013-03-25 03:06 | 14 | 161 | H4953241 | 2254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE ON GROUND POLE 108-36 // OPENED RECL POLE 108-116 @ 0025 //RELEASED BY CREW 077S08 // //VER/GAH IDCC DUP TO OPEN RECLOSER XXXX
6314 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-02-24 20:48 | 2021-02-26 10:20 | 1 | 2252 | 4246881 | 2252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Pole was broken and replaced and riser for underground service was moved tpo new pole and thinks may be an issue with the riser. had a bad spot in underground service, made repairs
6315 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-01-23 04:05 | 2016-01-23 10:20 | 6 | 375 | 4643251 | 2250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF LINE FUSE ON POLE 49-72/MD MADE/ADH 6 CUSTOMER OUT TOTAL.// VER/ ADH
6316 | Hazard | 3310502 | HADDIX | CANOE | 2012-12-08 18:55 | 2012-12-08 22:40 | 10 | 225 | 4452351 | 2250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830169C00170 OPEN LINE FUSE ON AT 18:55 NEED BIG BUCKET AND CUTOUT CLOSED AND RESTORED AT 2240 // VER/TOM L3/TOM IDC XXXX
6317 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2021-06-12 11:35 | 2021-06-12 15:45 | 9 | 250 | 4723521 | 2250 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad ug in sec pedestal/neut bar corroded on each leg/will need to bring new buss work for each leg open xfmer & replace all Released by crew 078S04 on site to make repairs opened xfm at 15:00 closed at 15:45 connections were not the problem attempting to locate bad urd may have to put add a phase on repaired bad urd T LEWIS LR- The 1st Part Out Call came in at 11:35
6318 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2012-04-25 22:39 | 2012-04-26 11:09 | 3 | 750 | 4708161 | 2250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BURNT OFF ON POLE 37830224D00065, POLE LEANING,PRIMARY CONTACTING NEUTRAL, NEED TO REMOVE UNUSED PRI. EXT. AND POLE 37830224D40501. NEED 3 MAN CREW, BIG BUCKET AND FLAGGERS. RELEASED BY CREW 077S04//WILL WORK IN THE AM REMOVED TAP AND REWORKED POLE FUSE BLOWN OFF P# 224 / 62 RESTORED POWER AT 1109 JKC VER/KEP
6319 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2012-03-14 13:25 | 2012-03-14 15:30 | 18 | 125 | 4578681 | 2250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PHASE "C" LEAD BURNT OFF AT SECTIONALLIZER//COD 18//OPENED RECLOSER ON POLE 517-85 AT 15:10 TO TAKE LOAD OFF (SEE H4578681)//COD +51//OPENED OTHER TWO PHASES ON SECTIONALLIZER POLE @ 1512//COD +10//, I CLOSED BACK ON RECLOSER @ IN AT 15:30// RESTORED 51//. TIM SMITH MADE REPAIRS ON SWITCH POLE 539-77 DURING THIS TIME//RESTORED LAST 28 @ 1530// IDC XXXX
6320 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2021-11-19 02:40 | 2021-11-19 10:10 | 5 | 450 | 4107401 | 2250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | call originally came in as all out // was later updated to pole fire, calling servicer //line fuse open on pole 820-c-89//pole top burnt off on pole 820-275//can frame down//crew enroute//crew on site making repairs//repairs made//restored at 10:10//complete//em////Opened TR at 0943 and restored at 1010
6321 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2009-05-05 13:15 | 2009-05-05 14:45 | 25 | 90 | H55204-1 | 2250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | ON SITE, TWO RECLOSERS OUT ("A" &"C" PHASE OUT ONLY TILL 1315 OPENED GOAB POLE#868-205), PATROLLING LINE, XARM BROKE AT POLE# 868-D-74, CALLED R MARCUM FOR HELP CLOSED RECLOSER AT 1323ON SITE, TWO RECLOSERS OUT ( A & C PHASE OUT ONLY TILL 1315 OPENED GOAB POLE#868-205), PATROLLING LINE, XARM BROKE AT POLE# 868-D-74, CALLED R MARCUM FOR HELP CLOSED RECLOSER AT 1323. POWER ON AT 14:45 VER/KEP L3/KEP IDC CNT32 XXXX
6322 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-07-05 10:13 | 2013-07-05 19:35 | 4 | 562 | 4469161 | 2248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 45-4 POLE 292-363 BURNED OFF AT CUTOUT.. DOUBLE DEADEND TWO GUY WIRES 25 KVA ALL SHOULD TRANSFER.. FIELDVIEW SHOWS AEP OWNS POLE.. PROBABLY CANNOT LOWER BECAUSE OF CLEARANCE ISSUES.. TRUCKS TO POLE RIGHT BESIDE ROAD.. FUSE ON PL 292-11 BLOWN TAG AT THAT POLE TO DDC GROUND PLACED PL 292-362 CREW ON SITE/VEM // REPLACED DDC HOLD TAG WITH VERNON MULLINS`S TAG// VER/KEP IDC XXXX
6323 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2018-04-23 23:09 | 2018-04-24 04:30 | 7 | 321 | 4269481 | 2247 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Called customer: phone not in service Bad 50 kva 19.9 transformer can use bucket truck. Released by crew 079S02 Replaced transformer and cutout. replaced lead wires
6324 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-03-10 14:09 | 2017-03-10 23:35 | 22 | 566 | 4546131 | 2246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE ON 38830208000020 IS OPEN. POLE HAS BURNED OFF ON 38830208000076. LIFTED HOT TAP ON 38830208000067 TO ISOLATE. FD ON SCENE,,CREW REQUIRED, NEED,40-5 AEP POLE,25 KVA XFR CUTOUT AND BRACKET ,,NO TRUCKS TRACK EQUIPMENT ONLY.,,LINE FUSE 208-20 BACK IN @ 15:29,LEAVING OFF 1 CUSTOMER RELEASED BY CREW 078S05 RELEASED BY CREW 078Q04//COD 22// VER/DBM AJBC TOF1337 CCF
6325 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-04-28 09:25 | 2022-04-28 16:54 | 5 | 449 | 4811181 | 2245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | looks like crack cutout on line fuse, need 2 19,9 cutouts and big bucket and flagers Released by crew 077S05..replaced c/os..opened@16:40 closed @16:54 Released by crew 077H13
6326 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-01 22:40 | 2010-12-02 11:08 | 3 | 748 | 62291-1 | 2244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 37957183 // TRANSFORMER IS ENERGIZED, BUT NO SECONDARY VOLTAGE, CREW REQUIRED, CUST.SAID OK TO BACK TRUCK THROUGH YARD AND BEHIND HOUSE .//GOT BUCKET STUCK.. WILL NEED YARD DOG AND MORE HELP TO CHANGEDCHANGE TRANSFORMER..... DUTY SUP. WAIT TIL IN MORNING RELEASED BY CREW 077H04 CHANGED XFMR RESTORED POWER AT 1108 CREW 077H01 VER/KEP L3/KEP IDC XXXX
6327 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-01-15 15:01 | 2016-01-15 18:08 | 12 | 187 | 4623121 | 2244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "B" PHASE ONLY COD-12/BAD CUTOUT ON 1062-B-163 FUSE OUT ON 1062-B-205 CREW IS EN ROUTE TO MAKE REPAIRSBAD CUTOUT ON 1062-B-163 FUSE OUT ON 1062-B-255 CREW IS EN ROUTE TO MAKE REPAIRS REPLACED CUTOUT RESTORED POWER AT 18:08 VER/KEP
6328 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-02-26 02:12 | 2011-02-26 04:24 | 17 | 132 | 63099-1 | 2244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLING LINE A-PH FUSE WAS AN BROKEN FUSE LINK CC= 17 ALL CUST SHOWED ON B PH VER/SDB IDC XXXX
6329 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-10-03 11:34 | 2020-10-03 14:41 | 12 | 187 | 4522941 | 2244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | George resaged some low conductor
6330 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-08-26 08:26 | 2019-08-26 11:30 | 22 | 184 | 4946101 | 2243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line crew with manual tree crew cutout cleared up on 175-56/line fuse on at 955 hrs send to tackett Released by crew 078S03,repairs made 1130 please close ticket thanks.bt L3/HFP
6331 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2015-01-21 11:50 | 2015-01-21 12:09 | 118 | 19 | H4948931 | 2242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED LOOSE AT POLE38831121D30415 ,MIDDLE PHASE RECLOSER OPEN FROM BEGINNING OF OUTAGE//HOT LINE CLAMP BURNED LOOSE AT POLE 415 , A PHASE ( CENTER PHASE AT POLE 415 ) . OPENED 2 OUTSIDE PHASES AT 11:50 AND REENERGIZED ALL 3 PHASES AT 12:09 , ALL WORK COMPLETE // GXJ RELEASED BY CREW 074S03 VER/CRB // PER VOICE REC - TROUBLE @ CENTER PHASE RECL `A` PHASE PER SERVICER - COULD NOT VERIFY WITH BUS OBJ OR SCADA/// L3/HFP XXX AJB
6332 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-12-02 18:09 | 2008-12-02 20:07 | 19 | 118 | 54029-1 | 2242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3202201//ARRESTER BAD ON POLE 698-188//COD 19// VER/DBM L3/KEP IDC XXXX
6333 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-04-20 03:09 | 2009-04-20 12:06 | 8 | 537 | 59309-1 | 2241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302 - CUTOUT WENT BAD BURNED TOP OF POLE OFF 175- 198 == WILL BNEED TO REPLACE == OPEN LINE ON POLE 175 - 196 3CUST STILL OUT == PUT MAIN LINE BACK ON AT 05:15 == WILL NEED ALINE CREW == RELEASED BY CREW 077S03//0900 LINE CREW ON SITE////VER/CRB IDC XXXX
6334 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-06-12 03:32 | 2015-06-12 04:55 | 27 | 83 | 4557601 | 2241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACE HOT TAP @ 44-4609//COD 27// VER/DBM AJB
6335 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2013-02-15 23:00 | 2013-02-16 01:20 | 16 | 140 | 4823101 | 2240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW REQUIRED BROKEN 8 FT ARM NEED BRACES CUTOUT AND ARRESTOR GOT TO OPEN WHOLE LINE UP 4X4 BUCKET TRUCK REQUIRED /POLE 251-139 LINE FUSE /OPEN AT 2300 HRS RELEASED BY CREW 078S03//OTHER TICKET IS 4823101 WITH COD OF 15 // RESTORED AT 0120// VER/TOM L3/TOM IDC XXXX
6336 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-03-29 08:05 | 2018-03-29 10:55 | 21 | 170 | 4145521 | 2240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 352-58, bad cutout on pole 352-65, isolated cutout closed line fuse in at 09:45..made repairs restored power at 10:55 Released by crew 077S11
6337 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2011-06-07 14:46 | 2011-06-07 17:06 | 16 | 140 | 4247571 | 2240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LATERAL FUSE OUT ON 1137D17....PATROLLED LINE...ALL UP & OK.....WILL RE-FUSE...//LATERAL FUSE OUT ON 1137D17....PATROLLED LINE...ALL UP & OK....BROKEN CUTOUT...NEED CREW & BUCKET...CALLED J REED...PLEASE SEND TICKET TO HIM..// RELEASED BY CREW 080S01 //COD 16// VER/DBM IDC DCMT XXXX
6338 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2008-01-30 06:40 | 2008-01-30 07:50 | 32 | 70 | 60947-1H | 2240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402204// HOT TAP BURNED OPEN ON STEP-DOWN BANK, NEED HOTTAP, STIRRUP, AND 2-3 MEN, NO TRUCK ACCESS, WILL NEED TO ISOLATE BANK / GXJ RELEASED BY CREW 074S03 ///ONLY ONE PHASE WAS OUT, HAD TO OPEN THE OTHER TWO PHASES AT 0640 ON 1-30-08// CLOSED @ 0750// VER/TOM IDC APPEARS PH A WAS INITIAL PHASE XXXX
6339 | Hazard | 3309003 | JEFF | VIPER | 2018-05-07 06:21 | 2018-05-07 08:55 | 25 | 154 | 4318491 | 2240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/// RESTORED POWER @0745 EXCEPT XFMR ON 393-40, RESTORED POWER TO LAST CUST @ 0855/ ISO 37830393D00037/ ISO 37830393D00040 L3/HFP
6340 | Hazard | 3310502 | HADDIX | CANOE | 2009-04-09 09:15 | 2009-04-09 13:55 | 8 | 280 | 50667-1 | 2240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502//ISO 37840240000068//COD 8//SERVICER OPENED FUSE IN ORDER TO ISOLATE POLE FIRE//CREW ENROUTE TO MAKE REPAIRS//RELEASED BY CREW 077S10// VER/DBM IDCC TOF0703 XXXX
6341 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-02-20 16:56 | 2018-02-21 11:35 | 2 | 1119 | 4866221 | 2238 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | fuse came back out. very difficult location will need 4 or 5 men. 25 kva . Released by crew 074S07 // will hold for daylight per duty supervisor, not safe to work cliffside at night// Pole is hollow need to change out send to CLIFF FREEMAN./ ISO 38831124D00043/ COD 2
6342 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-07-04 08:23 | 2015-07-04 11:15 | 13 | 172 | 4719151 | 2236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | JOEY FOUND LEFT HAND PHASE WITH BACK TO STATION BURNT DOWN LOOKS LIKE BAD COPPER TP ALUM CONNECTION HES GOIN TO RECLOSER WILL CALLWITH POLE # A PHASE COD 13// OPENED OTHER PHASES @ 1007// COD 106//JOEY FOUND LEFT HAND PHASE WITH BACK TO STATION BURNT DOWN LOOKS LIKE BAD COPPER TP ALUM CONNECTION HES GOIN TO RECLOSER WILL CALLWITH POLE # REPAIRED CONDUCTOR ON POLE1038B141 VER/CRB
6343 | Hazard | 3303902 | LESLIE | WOOTON | 2011-05-25 16:27 | 2011-05-25 18:12 | 43 | 105 | 4168611 | 2235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 439-35 RESTORED POWER UP 2 POLE 439-32 AT 1715 REPLACED CUTOUT AND RESTORED POWER 2 REST OF CUSTOMERS AT 1812 VER/KEP AJB
6344 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2013-09-14 08:09 | 2013-09-14 20:34 | 3 | 745 | 4853581 | 2235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG CABLE BAD,CREW ENROUTE TO REPAIR RELEASED BY CREW 074S06 REPAIRS MADE ON AT 20:34 D SAMMONS VER/KEP L3/HFP HFPC CDC83 IDCC XXXX
6345 | South Williamson | 3411401 | DEWEY | INEZ | 2013-01-15 16:51 | 2013-01-15 21:10 | 20 | 259 | 4607861 | 2235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE BLOWN ON 768-125//PATROLING NOW // TIM MILLER & TIM THOMASFUSE BLOWN ON 768-125//PATROLING NOW//SAW FLASH ON POLE 768-219//LIFTED HOT TAP ON POLE 768-49 AND GROUNDED SIDE TAP//BAD INS. OR CUTOUT BACK ON HILL//CREW ENROUTE//CLOSED FUSE ON 125 AT 18:35 RESTORING ALL BUT ONE CUST. COD-20 ISO LF 38830768C00125 VER/HFP L3/HFP IDC XXXX
6346 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-05-30 14:27 | 2014-05-30 17:42 | 20 | 195 | 4954511 | 2234 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 37830343D00242 === TOOK CUTOUT AND ARRESTER OFF TILL CREW GETS HERE TO CHANGE OUT === MADE MAIN LINE HOT 16:04 === JEFF COMBS TO CHANGE ==== RELEASED BY CREW 077S03 REPAIRS MADE AND RESTORED POWER AT 1742 VER/CRB IDC XXXX
6347 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-08-09 19:49 | 2014-08-09 21:06 | 29 | 77 | 4348841 | 2233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L/F OPEN AT POLE 497-13, LIGHTNING BLOWED ARRESTOR AT POLE 497-83 WILL BE MAKING REPAIRS. REPAIRED ARRESTOR CLOSED L/F AT 21:06. AJB
6348 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2012-10-19 11:30 | 2012-10-19 11:42 | 186 | 12 | H4155631 | 2232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATED FEEDER OUTAGE - SERVICER DISPATCHED AND ON SITE AT 0328 ISOLATING FAULT *POLE FIRE AT POLE 954-1138. CALLING OUT CREW. LOOPS OPEN AND TAGGED AT POLE 954-B4-194 VER/DKG MADE THIS OUTAGE FOR OPENING SWITCH TO MAKE UP LOOPS IDC XXXX
6349 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2011-05-01 11:40 | 2011-05-01 12:42 | 36 | 62 | 53151-1 | 2232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 076S02 BAD CUTOUT ON DEADEND XFMR POLE ALSO DAMAGED DEADEND INSULATOR. OPEND FUSE ON 954-487 TO ISOLATE @ 11:40. REPLACING HARDWARE. REPLACED CUTOUT, ARRESTER AND DEADEND INS. POLE IS BURNT ABOUT ONE-THIRD IN TWO. WILL SEND JOB TO ENGINEERING TO SEE IF THEY WANT TO CHANGE IT. ITS OUT AND APPEARS TO BE OK FOR NOW. SH//COD 36 IDC CHANGED TIME OFF FROM 1034 PER COMMENTS XXXX
6350 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2012-10-19 11:30 | 2012-10-19 11:42 | 186 | 12 | H4155631 | 2232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATED FEEDER OUTAGE - SERVICER DISPATCHED AND ON SITE AT 0328 ISOLATING FAULT *POLE FIRE AT POLE 954-1138. CALLING OUT CREW. LOOPS OPEN AND TAGGED AT POLE 954-B4-194 VER/DKG CHANGED TIME OFF FROM 0313 AND CLR DEV TO PRIMARY OPEN FOR SWITCH OPENED TO MAKE UP LOOPS IDC DUP TO MAKE UP LOOPES XXXX
6351 | South Williamson | 3411401 | DEWEY | INEZ | 2010-03-22 04:51 | 2010-03-22 11:03 | 6 | 372 | 52488-1 | 2232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE. NEED CREW RELEASED BY CREW 079S01 ///CREW WILL NEED TO REPLACE CUTOUT// ON SITE STARTING REPAIRS TCM// LINE FEEDS FROM 768-24 WITH A 30T LINE FUSE PROTECTING TAP//COD -6 ENTERED MD ---HFP VER/HFP L3/HFP IDCC CDC92 XXXX
6352 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-11-30 11:12 | 2009-11-30 12:45 | 24 | 93 | 51385-1 | 2232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND ANOTHER HOT TAP LEAD, BURNTED OFF OF LINE FUSE, HAVE REPAIRS MADED AND POWER IS RESTORED AT THIS LOC IDC XXXX
6353 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-10-23 14:59 | 2009-10-23 17:03 | 18 | 124 | 50127-1 | 2232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 32349227 ENTERED MD..HFP 18 CUST ISO LF 38830020D26566 30T LINE FUSE ON HOODS CK. BY THE FALLS BAD CUTOUT 20-6032 ALL THE WAY TO END OF CAROLINE RD NEED BIG BUCKET RELEASED BY CREW 078S08/CREW ON SITE/FETR1745/VEM RESTORED 1703 COD-18 VER/KEP L3/KEP IDCC FPNULL XXXX
6354 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2020-07-16 19:42 | 2020-07-16 23:25 | 10 | 223 | 4172431 | 2230 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad xfm on pole 38830954A21123 25 KVA 7200. Needs larger xfm Released by crew 074S11//changed xfmr out///power restored at 23:25
6355 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2022-11-24 18:37 | 2022-11-24 22:20 | 10 | 223 | 4178671 | 2230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | bad 75 kva padmount 1123B48034 crew req. DR //opened line fuse 39831123B48032 @ 2200 (7 addtl cust) and closed @ 2220 // cod 3 (+7) //
6356 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-03-04 15:52 | 2008-03-04 19:35 | 10 | 223 | 52770-1 | 2230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3400303// LINE FUSE OUT ON POLE 1101D365 25T. BAD ARRESTER ON POLE 1101D363//COD 10 IDC XXXX
6357 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-10-09 10:10 | 2009-10-09 11:39 | 25 | 89 | 66507-1 | 2225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | WORK REQUEST 32130718 // CUSTOMER REPORTED TROUBLE 10/9 AM// MAY BE BAD INSULATOR OR PROBLEM WITH HENDRIX// WILL HAVE TO OPEN TO ISOLATE - NC 600 AMP SWS ON 46-1075 / FAULT POE 46-181 // CREW ON SITE//---PLAN OFF AT 10:00, ON 11:30---REPLACE HENDRIX SPACER STAR AND SPLICE WIRE--OFF 10:10 ON AT 11:39 // VER/TOM IDC XXXX
6358 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-04-30 19:38 | 2013-04-30 21:07 | 25 | 89 | H4060601 | 2225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE OUT AGAIN 159 CUSTCOND OFF INSULATOR,NEED 2 MEN,CUTOUT,ARRESTOR,TIEWIRE /// SEE ASSIGN TAB - INSTRUCTIONS TAB FOR MORE DETAILS. VER/HFP L3/HFP IDC XXXX
6359 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-08-04 21:35 | 2022-08-05 16:07 | 2 | 1112 | 4677661 | 2224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout on pole 302-D-82, manual due to bridge damage. Two customers are fed from this pole, I cut one in the clear due to flood damage to their home but the other customer can be restored once this cutout has been replaced. Crew required. Released by crew 077S04/Broke manuel cutout//crew required.
6360 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-10-15 21:07 | 2018-10-16 15:39 | 2 | 1112 | 4257051 | 2224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT WILL NEED BIG BUCKET TO MAKE REPAIRS AND REMOVE VINES Released by crew 077S01 L3/HFP
6361 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-05-30 11:52 | 2019-05-30 16:30 | 8 | 278 | 4386771 | 2224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Repairs made back to normal.
6362 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2017-10-23 09:53 | 2017-10-23 10:50 | 39 | 57 | 4478461 | 2223 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 21-67 65T OUT POLE 21-3009 BAD CUTOUT FUSE IN 10:50 SEND TO RON /IDC ADDED ONE CUSTOMER BECAUSE NONE LISTED ON OUTAGED TRANSFORMER.RELEASED BY CREW 078S08--CHANGED BAD CUTOUT ON 21-3009--BACK ON AT 11:33--TBL TKT COMP---RMV REL // NO CUST ON FAULT XFMR VER/AWD L3/HFP XXXHFP ACB
6363 | Hazard | 3310502 | HADDIX | CANOE | 2018-02-07 06:11 | 2018-02-07 09:33 | 11 | 202 | 4810571 | 2222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | on pole 37840240000077 have broke cutout and took clamp off line that didnt serv anyone//on pole 37840240000077 have broke cutout and took clamp off line that didnt serv anyone had line fuse out on pole37840216B40156
6364 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-07-14 13:04 | 2012-07-14 14:45 | 22 | 101 | 4723191 | 2222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | C PHASE RECLOSER HERE SEEMS DAMAGED//CAN IS SWOLLEN AND BUSHINGS BURNT//SERVICER PUT BYPASS IN AND RESTORED CUSTOMERS//ISO 39831072C45705//ONLY C PHASE CUSTOMERS OUT//COD 22//MD FILED//AED ENTRY CREATED// IDC XXXX
6365 | Hazard | 3302703 | HAZARD | HAZARD | 2009-01-17 11:13 | 2009-01-17 14:35 | 11 | 202 | 57429-1 | 2222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CONNECTIONS FAILED ON XFMR SECONDARY RISER CALLING FOR CREW TO ASSIST RELEASED BY CREW 077S04 L3/HFP
6366 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-08-20 16:45 | 2016-08-21 11:15 | 2 | 1110 | 4818441 | 2220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BROKE 25T ON POLE 37830482A00040,NEED LINE CREW AND R/W CREW TO FLAG RELEASED BY CREW 077H07REPAIRS MADE AND POWER RESTORED AT 1115/ ISO 37830482A00040/ COD 2/ MD DONE/ VER/BOW
6367 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-02-20 13:59 | 2014-02-20 14:59 | 37 | 60 | 4405701 | 2220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SWITCHING TO REPLACE CUTOUT AT 45-B2-2759 AND TRANSFER LOAD TO REDUCE OUTAGE VER/KEP
6368 | Whitesburg | 3401301 | FLEMING | NEON | 2015-02-20 08:05 | 2015-02-20 14:15 | 6 | 370 | 4052061 | 2220 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE#355-155 TRANSFORMER HOT LEAD PULLED OUT CAN PULL BESIDE OF POLE TO REPAIR RELEASED BY CREW 077F02 I REPLACED XFMR LEAD AND CONNECTIONS VER/HFP L3/HFP
6369 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-04-17 08:23 | 2020-04-17 12:05 | 10 | 222 | 4709141 | 2220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 40t line fuse out due to riser wire broken out of top of cutout. replaced bad cutout riser wire closed 40t fuse in on pole 833-b-542 @ 12:05
6370 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-08-06 08:48 | 2022-08-06 16:12 | 5 | 444 | 4689931 | 2220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830244000060 lat c/o broke--crew req Released by crew 078S01. crew on site
6371 | Hazard | 3303902 | LESLIE | WOOTON | 2012-08-14 11:45 | 2012-08-14 13:36 | 20 | 111 | 4935681 | 2220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OFF @ 1145 RESTORED @ 1336 IDCC CNT21 XXXX
6372 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-12-01 04:06 | 2019-12-01 13:20 | 4 | 554 | 4108861 | 2216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NC SERVICER REQ/ Dispatched in accordance with KYPCo Late Night Callout Guidelines.LINEF IS OUT,WILL PTRLLINEF IS OUT,WILL PTRL///////////NOTHING EVIDENT,WILL TRY FUSE///////FUSE BLEW,LOOKING SOME MORE
6373 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-03-08 09:37 | 2008-03-08 14:14 | 8 | 277 | 54951-1 | 2216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//DUPED DUE TO AREA CROSSOVER//CUTOUT OPEN ON POLE 1115-D-68 (NOT ON MAP, WILL SEND NOTE TO MAPPING)//COD 10//, POLETOP BURNT OFF, POLE#1115-77, CALLEDR MARCUM, HELP ON WAY, CREW ARRIVEDAT 1325//POWER RESTORED 1414// VER/DBM IDC CHANGDED MCC FROM NO INTERRUPTION DUPLICATE XXXX
6374 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-07-05 11:58 | 2009-07-05 19:21 | 5 | 443 | 65900-1 | 2215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND BAD ARRESTER ON POLE 309-38.//COD 5//BAD CUTOUT AND BAD ARRESTER ON POLE 309-38. MADE ALL REPAIRS.// IDC XXXX
6375 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2009-01-16 22:25 | 2009-01-17 02:31 | 9 | 246 | 56488-1 | 2214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3311701//EXISTING 25 KVA 19.9 BAD NEEDS REPLACED WITH 50 KVA RELEASED BY CREW 077S04 ..... REPLACED XFMR RESTORED POWER AT 02:31 VER/TOM L3/TOM
6376 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-02-08 09:53 | 2009-02-08 13:59 | 9 | 246 | 56670-1 | 2214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SLEEVE FAILED ON PRIMARY WIRE, PRIMARY DOWN AT 38830161000017, CREW REQUIRED, TRUCK OK RELEASED BY CREW 078S05/REPAIRS COMPLETE/ALL CUST RESTORED 1359/PLEASE CLOSE TICKET/THANKS/VEM// VER/TOM L3/TOM IDC XXXX
6377 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-09-09 14:18 | 2014-09-09 16:21 | 18 | 123 | 4483341 | 2214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE OPENED UP LINE AT 1418 AND RESTORED POWER AT 1621 VER/CRB
6378 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-05-15 05:58 | 2010-05-15 08:01 | 18 | 123 | 62570-1 | 2214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308001 STS STURRIP BURNED OFF , GOING TO PUT NEW ONE ON IDCC CCO XXXX
6379 | Hazard | 3303902 | LESLIE | WOOTON | 2014-09-11 22:47 | 2014-09-12 11:05 | 3 | 738 | 4492101 | 2214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//// 25KVA 19.9 BAD. PROBABLY CAN USE MATERIAL HANDLER, CREW REQUIRED RELEASED BY CREW 077S08 REPLACED AND RESTORED POWER AT 1105 VER/CRB
6380 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-12-05 05:54 | 2020-12-05 07:16 | 27 | 82 | 4746621 | 2214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut out on pole 394-A-61 has broken down and burned the top of the pole off. Primary is still energized and everything is hanging in the clear. Going to leave as is until a crew and come to make repairs. Need a 12KV cutout and a pole top extension. Released by crew 077H20 Off @ 0554 On @ 0716
6381 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-08-29 08:41 | 2014-08-29 10:00 | 28 | 79 | 4435291 | 2212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELATED TO 4435021//CALLED CUSTOMERS AFTER OTHER OUTAGE RESTORED AND CUST STILL W/O POWER// POLE 1147-5141 BAD UNDERGROUND TAGGED POLE AND TRAN, 1148-5182 POLE 1147-5032 65T SEND NOTE TO RAYBURN TO CK. UNDERGROUND NEXT WEEK//COD 28// VER/DBM AJB
6382 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2012-11-27 16:27 | 2012-11-27 16:53 | 85 | 26 | H4426341 | 2210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF ORDER 4424191 - OUTAGE NECESSARY TO RESTORE OPEN LOOPS ON CKT. 1 HR OR LESS VER/PDP IDCC DUP TO TRANSFER CUSTOMER BACK TO NORMAL XXXX
6383 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-10-11 15:40 | 2011-10-11 16:45 | 34 | 65 | 4965821 | 2210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER PHASE CUTOUT DOOR IS BURNED OUT ON 37830048D30147//PATROLLING//CHANGED CUTOUT DOOR// POWER IS RESTORED//COD 36// VER/DBM IDC PH A ONLY 34 CUSTOMERS XXXX
6384 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2021-12-22 10:34 | 2021-12-22 12:44 | 17 | 130 | 4219711 | 2210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | B-phase out on pole 917C-383..had riser on B-phase cutout burned into on pole 383..made reparis and got linefuse back in at 12:44
6385 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-05-21 04:25 | 2020-05-21 07:15 | 13 | 170 | 4875741 | 2210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o @ 69-4196, line crew, no trucks. restored 07:15
6386 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-03-03 23:11 | 2015-03-04 02:15 | 12 | 184 | 4095751 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A & B PHASE OUT COD-12 2 OF 3 LINE FS OUT,WILL PTRL//////////BROKEN PIN-TYPE INSULATORS ON POLE 1058-81,NEED INSULATORS,2 MEN,BIG BUCKET/////OPND OTHER F AT 01:51,MADE REPAIRS,CLOSED ALL AT 02:15 VER/KEP --- COULD NOT VERIFY VIA SCADA OR VOICE RECORDER (VOICE RECORDER HAS ISSUES) MADE DUP FOR C PHASE OUTAGE L3/HFP HFPC DUP
6387 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-07-26 19:23 | 2008-07-26 23:59 | 8 | 276 | 60614-1 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3410601// 25KVA XFMR BAD. DUTY SUPERVISOR NOTIFIED. CREW ENROUTE. REPLACED XFMR. SH IDC XXXX
6388 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-07-08 09:26 | 2015-07-08 12:30 | 12 | 184 | 4744401 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD TRANFORMER CUT-OUT AT POLE269-B-364, PATROLED LINE BEST I COULD,FOUND BAD TRANFORMER CUT-OUT AT POLE269-B- CLEARED UP INATIVE PATROLED LINE BEST I COULD, POWER RESTORED KWB. VER/CRB
6389 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-07-25 10:12 | 2019-07-25 10:36 | 92 | 24 | 4790781 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | failed crossarm at pole 120-175/ crew opened Sw at 120-D-243 at 1012 to safely isolate cod-92/ Closed at 1036
6390 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2012-04-18 08:04 | 2012-04-18 20:20 | 3 | 736 | 4682701 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE FROM BAD CUTOUT..POLE 968D8..B PHASE FUSE BLOWN ON 992C443..OPENED A & C PHASES @ 14:55..FIRE DEPT ENROUTE TO TRY & EXTINGUISH & SAVE POLE.WILL NEED CREW.NON TRUCK ACCESS.//.FIRE EXTINGUISHED.POLE TOP STILL INTACT..// CREW WILL RETURN TOMORROW TO MAKE REPAIRS TO POLE - NO TRUCK ACCESS & TO0 DANGEROUSE TO WORK TONIGHT. 4/19 OFF AT 13:30 ON AT 17:25 ON DIFFERENT TIX ///VER/CRB IDC XXXX
6391 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-10-08 11:34 | 2017-10-08 16:10 | 8 | 276 | 4421251 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 38830185000108 PRI OFF INSULATOR--TIED IN-- TREE CREW FLAGGED--38830185000107 LAT 15T IN AT 16:10-ALLGOOD-DS100817/ TIE WIRE BROKE ALLOWING CONDUCTOR TO COME OFF PIN/ ISO 38830185000107/ COD 8/ VER/BOW ACB
6392 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-10-06 17:31 | 2009-10-06 18:40 | 32 | 69 | 56462-1 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 37830204000093 WE HAVE ARRESTOR GONE BAD/// CUT ARRESTOR IN CLEAR, REFUSED XFMR AND CLOSED B-PHASE RECLOSER. POWER RESTORED. COD-32 ADDED CUSTOMERS FROM "A" AND "C" PHASES MD FILED VER/KEP L3/KEP IDC XXXX
6393 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-12-02 16:34 | 2009-12-03 04:50 | 3 | 736 | 58640-1 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD AND POLE IS MANUAL REPLACED CUTOUT VER/KEP L3/KEP IDC XXXX
6394 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2009-05-24 11:37 | 2009-05-24 13:55 | 16 | 138 | 62842-1 | 2208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON TRANSF POLE BAD ON SECONDARY SIDE == REPAIRED == POWER OK VER/TOM
6395 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-09-26 03:12 | 2022-09-26 12:57 | 7 | 585 | 4922781 | 2205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.To foggy at the moment to see anthing going to wait till the fog goes down some. Top of Pole 448C1-641 is burnt off. Tech and crew required. Lifting clamp at pole 448C1-522 and tagged to Jeff Caudill to isolate trouble. LF restored at 07:42. // restored @1257
6396 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-10-31 04:14 | 2022-10-31 11:35 | 5 | 441 | 4079771 | 2205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks pole burnt off 222-10 isolated at 222-12 towad 222-10/ line fuse 222-12 back on at 0630 hrs 1 customer still off no tags no grounds/ only 1 line fuse on 222-12 that feeds both side taps md done/crew on site FETR 12:00 LRM all pwr restored 11:35 please closeticket LRM
6397 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2016-06-27 16:18 | 2016-06-27 17:16 | 38 | 58 | 4486771 | 2204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPEN RECLOSER @ 280-62 @ 1626,PRIMARY DOWN @ 280-78 ,BAD ARESTER @ 280-179 RECLOSER IN @ 1716 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT//MADE AED/ADH// VER/ ADH
6398 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-01-29 15:14 | 2008-01-29 16:30 | 29 | 76 | 60711-1 | 2204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3411802//HI SIDE FUSE OF STEPDOWN XFR IS OUT,MIGHT HAVE BEEN LIGHTNING ARRESTOR AS IT IS BLOWN AND CLEARED ITSELF.WILL RE-FUSE.ON POLE 1082-93APPEARED THAT HI-SIDE ARRESTOR FAULTED,TOOK FUSE OUT.CLEARED ARRESTOR,RE-FUSED AND RESTORED// ISO/FLT 38821082000093 COD 29// VER/TOM IDCC CDC92 XXXX
6399 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-12-10 09:39 | 2009-12-10 10:17 | 58 | 38 | 58916-1 | 2204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | VER/HFP TOP OF POLE 597/32 BURNING, TIE WIRE SLIPPED PULLING STIRRUP AND CUTOUT RISER INTO TOP OF POLE; OPENED RECLOSER @ 0939 12/10; PUT OUT FIRE, CUT OFF OLD STIRRUP AND INSTALLED NEW STIRRUP; TOP OF POLE BOWLED OUT , CAN SEE TOP BOLT ON POLE TOP PIN BUT STILL STRONG; RECOMMEND LINE CREW MOVE POLETOP PIN DOWN WHEN POSSIBLE; RECLOSURE BACK IN AT 1017HRS. ; PWR RESTORED; CLOSE TICKET L3/HFP IDC XXXX
6400 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-06-02 03:59 | 2021-06-02 13:10 | 4 | 551 | 4657191 | 2204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva, 7200-120-240 xfmer..trk to pole. flaggers. // Ticket complete closed xfmr on 69-D1-6017 at 13:10.
6401 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2016-07-14 17:40 | 2016-07-14 21:00 | 11 | 200 | 4635001 | 2200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT WAS CHANGED ON THIS POLE EARLIER TODAY
6402 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2019-10-26 08:08 | 2019-10-26 09:58 | 20 | 110 | 4197771 | 2200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed on 808-80. Crew enroute to assist. Replaced and restored @ 9:58 sh
6403 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-03-16 22:02 | 2015-03-17 10:15 | 3 | 733 | 4201941 | 2199 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 ON POLE 1137-220/CREW REQUIRED/2 MEN & MATERIAL HANDLER WITH BIG BUCKET/COD 3/ PER LATE NIGHT CALLOUT WILL DISPATCH IN A.M. REPLACED TRANSFORMER HJ COD-3 ISO TF 38821137B00220 VER/HFP L3/HFP
6404 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2018-05-05 16:13 | 2018-05-05 20:35 | 28 | 259 | 4311011 | 2198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Call Bob Tackett if crew req . CREW REQUIRED : 19.9 kv pin type insulator failed, conductor is floating underneath arm, NEED 19.9 pin type insulator and pin, truck access . 3.8 miles past Bill Hall Br on Frasures Crk on the left/ opened 116-94 at 1938 to isolate for repairs/
6405 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-04-18 14:26 | 2016-04-18 17:15 | 13 | 169 | 4100671 | 2197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4/0 -350MCM CONNECTION BURNED UP.NEED BIG PRESS..350 COPPER AND 2 350/4/0 CONNECTIONS..OPENED XFMR @ 16:23 TO MAKE REPAIRS. VER/CRB
6406 | Hazard | 3302704 | HAZARD | KENMONT | 2011-01-18 13:35 | 2011-01-18 16:38 | 12 | 183 | 62273-1 | 2196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HIGH SIDE FUSE OUT ON STEPDOWN == MAY HAVE BAD STEPDOWN == BAD ARRESTER ON STEPDOWN == CALLED FOR CREW AND FLAGERS TOO == CHANGED ARRESTER == REFUSED STEPDOWN == POWER OK COD-12 ISO LF 37830321A00515 VER/HFP L3/HFP IDC XXXX
6407 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-10-03 12:02 | 2014-10-03 14:04 | 18 | 122 | 4547541 | 2196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD TRANSFORMER CUTOUT ON POLE 1114-B-2. REPLACED 30 T FUSE ON POLE 38821114A00005, POWER IS BACK ON.//MADE MD TO SHOW 30T VER/CRB VER/DKG L3/DKGXXXX
6408 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-06-08 21:37 | 2014-06-08 21:49 | 183 | 12 | 4996791 | 2196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT ON RECLOSER POLE AJB
6409 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2017-12-08 19:50 | 2017-12-09 03:09 | 5 | 439 | 4631551 | 2195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | #4 cu secondary burned dn at pole 188-20 need one man and big bucket. Wire repaired, need 25 kva 7.2kv transformer.
6410 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-08-16 03:46 | 2021-08-16 11:05 | 5 | 439 | 4075391 | 2195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout of 38830286000037 not by truck in this rain more then likely, wont be able to reach it with a squirt boom. one span #2 neutral down on same pole. Released by crew 078S12//arrived RM 25T fuse in @ 11:05 please close tic RM
6411 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-10-26 18:04 | 2010-10-27 12:21 | 2 | 1097 | 64898-1 | 2194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER ON POLE 223A-412 NEEDS TO BE REFUSED, FOUND NO OTHER PROBLEMS RELEASED BY CREW 077E07 BAD10 KVA TRANSFORMER CAN CHANGE WITH MATERIAL HANDLER RELEASED BY CREW 077S04//CUSTOMER MAST IS DAMAGED AT METER 533753961, UNHOOKED CUSTOMER AND LEFT NOTE EXPLAINING THAT THEY NEED TO MAKE REPAIRS//REPLACED TRANSFORMER AND RESTORED REMAINING CUST @ 1221 //COD 1// VER/DBM IDC XXXX
6412 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2012-07-16 15:54 | 2012-07-16 21:43 | 11 | 349 | 4740861 | 2192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 20T ON POLE 138-185 OPEN. RESTORED 18:40 BAD 7200 50 KVA CSP XFMER POLE 138-187 CUT OUT, LA &STANDOFF // MULLINS, VERNON & MORGAN, RICKY & MCCOY, LUCASNO TRUCKS RELEASED BY CREW 078H12/CREW ON SITE/FETR2315/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2143/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
6413 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2022-09-27 09:01 | 2022-09-27 11:27 | 15 | 146 | 4928711 | 2190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | A phase out on pole 38821065D20318--cc15--l/f 1065d2-318 was blown found where primary and nutral had touched at pole 1065d1-75 took slack out power on at 11:27
6414 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-06-15 10:51 | 2016-06-15 14:30 | 10 | 219 | 4349931 | 2190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 7200 CUTOUT IN VERY DIFFICULT LOCATION, UP ON HILL BEHIND MANIS DISTRIBUTING..ROW CREW CUTTING PATH TO POLE. // DONT FORGET FETR REPLACED CUTOUTS AND RESTORED POWER AT 1430 POLE IS BAD NEEDS TO BE REPLACED SEND TICKET ONTO DOUG CHRISTAIN POLE 248-493 VER/HFP L3/HFP AJB
6415 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2020-04-10 10:21 | 2020-04-10 13:40 | 11 | 199 | 4616161 | 2189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | stirrup burned into on take off pole//i installed screw on stirrup//restored at 13:40//complete//em
6416 | Paintsville | 3401101 | FALCON | FALC-OILS | 2012-10-11 07:21 | 2012-10-11 10:40 | 11 | 199 | 4130571 | 2189 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4CU PRIMARY CONDUCTOR PULLED OUT OF SLEEVE. REPAIRS COMPLETE. RE-FUSED 20T ON 878-38 @ 10:40. SH VER/KEP IDC XXXX
6417 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-12-14 08:07 | 2022-12-14 12:10 | 9 | 243 | 4258011 | 2187 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke manual cutout on 37840336000130. Will make repairs once help arrives. Power restored @ 12:10
6418 | Pikeville | 3421001 | BREAKS | CITY | 2020-11-26 17:26 | 2020-11-26 18:18 | 42 | 52 | 4724881 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on dip fuse @ pole220-513 will replace/// Replaced bad cutout and restored service @ 18:18
6419 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-01-17 12:18 | 2010-01-17 17:30 | 7 | 312 | 55426-1 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | I CHECKED VOLTAGE AT U.G. SECONDARY JUCTION 120/ PHASE TO GROUND ON BOTH LEGS AND NO PHASE TO PHASE VOLTAGE THERE IS A PROBLEM IN THE SECONDARY I CHECKED AT XFRM POLE 38821081D00180 120/240 WE HAVE A SECONDARY RISER COMING OFF THIS POLE TO A SECODARY JUCTION BOX ABOUT 15 FROM POLE WILL NEED CREW 3 MEN AND BUCKET. 350 WITH 4/0 NEUTRAL.TIM MCCOY RELEASED BY CREW 074H10 REPLACED 4/0 SEC URD. THAT WAS BAD OPEN AT 18 12 CLOSED AT 17;30 IDC XXXX
6420 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-12-28 14:44 | 2008-12-28 16:08 | 26 | 84 | 64702-1 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410501//VER/CRB CHANGED ISO POLE L3/KEP IDC XXXX
6421 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2019-08-11 15:10 | 2019-08-11 18:12 | 12 | 182 | 4871981 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop open at 93-12, 300a solid blade, corner of boy scout & greenfield. access to field @ green farm gates on greenfield. Released by crew 078S07///making repairs///closed on pole 93-12 @ 18:12///complete BR L3/HFP
6422 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-01-02 10:43 | 2016-01-02 13:19 | 14 | 156 | 4581161 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN LINE CUTOUT AT POLE 39/ BROKEN LINE CUTOUT AT POLE 39, OPENED XFMR POLE 39 AT 12:40 AND CLOSED AT 13:08 . LINE CUTOUT CLOSED AT 13:19, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03/ ISO 38831076000039/ COD 14/ VER/BOW
6423 | Hazard | 3310502 | HADDIX | CANOE | 2013-12-17 03:40 | 2013-12-17 06:28 | 13 | 168 | 4167061 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BROKE ON POLE 169-C-66 AND IS DOWN IN LASH // OPENED LINE FUSE AT POLE 169-C-276 AT 0606, MADE REPAIRS AND CLOSED AT 0628 BAD LINE FUSE CUTOUT ON POLE 37830169C00066 OPEN LINE FUSE ON POLE 169-276 AT 0606 AND CLOSED AT 0628 SEE H4167061 VER/HFP L3/HFP IDC XXXX
6424 | Pikeville | 3401001 | ELWOOD | DORTON | 2017-08-07 13:40 | 2017-08-07 15:04 | 26 | 84 | H4233241 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE ONLY 4 CUST FAILED CUTOUT BURNED CROSSARM IN TWO POLE 287-108. C PHASE LINE FUSE OUT. CREW ARRIVED AND WE OPENED THE OTHER TWO PHASES AT 1340. (31 CUST). CLOSED AT 1504. /// PER B.O. INITAL CALLS ON `A` PHASE 9 CUST VER/HFP L3/HFP SJG
6425 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-05-08 12:12 | 2010-05-08 13:43 | 24 | 91 | 57835-1 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASES ARE OPEN ON POLE 375-79, BAD CUTOUT ON POLE 375-255 NOT SERVING ANYTHING.. TOOK CUTOUT OFF LINE RESTORED POWER AT 13:43//VER/CRB IDC NOT A & B MUST BE PH A AND C, CHANGED COUNT FROM 16 XXXX
6426 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-06-24 16:27 | 2010-06-24 21:00 | 8 | 273 | 56739-1 | 2184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE ON STEPDOWN WILL BE CHANGING OUT OTHER 2 OPEN 3 SINGLE RECL. ON POLE 69-143 AT 19:20 HAVE A STEPDOWN BUSHING BROKE GOING TO CHANGE STEPDOWN HAVE SD CHANGEDCLOSED IN AT 21:00 IDCC CDC92, CNT43 XXXX IDC XXXX
6427 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-08-01 14:21 | 2017-08-01 15:20 | 37 | 59 | 4213541 | 2183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FORESTRY REPORTED PRIMARY OFF OF INSULATOR ON 38830259000022.--NEED RIDGE PIN AND INS -- NBT -- OPEN AND ISOLATE (STILL ENERGIZED) AT 83-235/68--CREW REQ-DS080117 RELEASED BY CREW 078S01/CREW ON SITE/WILL NEED TO OPEN LINE FOR REPAIRS/APROX ONE HOUR OUTAGE/VEM 38830235000068 VER/AWD SJGC FEC40, TOF10:49
6428 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-11-17 07:07 | 2014-11-17 12:30 | 14 | 323 | 4733861 | 2182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE L/F BLOWN ON 37820075000002//WILL PATROL//CUTOUT BROKE ON 75-229 // I ISOLATED CUTOUT // POWER RESTORED @ 9:30 //ALL ON EXCEPT 75-229 // COD 19+1// ON @ 12:30 (B PHASE & AB CUST TOTAL 14) ALL CALLS ON B PHASE PER B.O. ) VER/HFP L3/HFP
6429 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-02-09 20:25 | 2010-02-10 05:30 | 4 | 545 | 54634-1 | 2180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3110902 FOUND POLE ON FIRE WHEN I ARRIVED, OPEN UP LINE FUSE ON POLE 1073-2079 AND GROUNDED LINE AT THIS POINT, POLE 1073-2094 WHICH IS A 355, NEED TO GO BACK WITH A 405, NEED NEW CUTOUT AND ARRESTOR, EVEYTHING THING ELSE SHOULD GO BACK, CREW REQUIRED //CREW ARRIVED, BEGINNING WORK VER/TOM L3/TOM IDCC TOF1939 CHANGED FAILED EQUIPMENT FROM POLE XXXX
6430 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-09-09 03:10 | 2018-09-09 12:15 | 4 | 545 | 4061791 | 2180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva xfmr.bad 37.5 kva xfmr.can go back with a 15 kva.no truck access.bad 37.5 kva xfmr.can go back with a 15 kva.no truck access. Released by crew 076S01
6431 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-02-01 10:43 | 2008-02-01 11:03 | 109 | 20 | 63915-1 | 2180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401101// HAD TO OPEN RECLOSER TO ALLOW FIRE DEPARTMENT TO PUT OUT POLE FIRE//VER/ARN IDC XXXX
6432 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-01-13 08:47 | 2017-01-13 12:05 | 11 | 198 | 4294351 | 2178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T FUSE OUT DUE TO BAD CUT OUT BURNT POLE 1125 B 848 OFF. REPAIRS MADE EVERYTHING LOWERED DOWN./ ISO 38831125B00182/ COD 11/ VER/BOW L3/HFP HFP
6433 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-07-27 12:10 | 2015-07-27 14:11 | 18 | 121 | 4946861 | 2178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 40T FUSE OUT DUE TO BAD ARRESTER ON POLE 140-165. CHANGED ARRESTER FUSE UP EVERYTHING OK// VER/ ADH
6434 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-06-10 09:13 | 2019-06-10 13:15 | 9 | 242 | 4472811 | 2178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole.38831125C30012. line fuse out on pole1125C30135. isolated cutout on 135 & fused line up @ 13:15 replaced cut out & closed xfmr on 135 @ 14:03
6435 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-11-05 16:12 | 2012-11-05 18:20 | 17 | 128 | 4364171 | 2176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 116-18--50T BROKE REPLACED WITH 25T POLE 116-746 WRONG FUSE ON POLE 30T REPLACED WITH 40T//SENT TO GREG BELL //VER/CRB L/3 CRB IDC XXXX
6436 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2021-08-11 13:43 | 2021-08-11 14:47 | 34 | 64 | 4036581 | 2176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | high side step down fuse had rotted out. fuse replaced,power restored
6437 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-03-24 16:40 | 2016-03-24 16:48 | 272 | 8 | 4878441 | 2176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | BAD BYPASS SWITCH IN SECTIONALIZER 16-D-280, WILL HAVE TO OPEN SWTICH 40-C-169 . OPENED AT POLE 169 AT 16:40 AND CLOSED AT 16:48, CLEARED FAILED BYPASS SWITCH, ALL WORK COMPLETE / GXJ// VER/ ADH AJB
6438 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-03-27 18:52 | 2017-03-27 20:19 | 25 | 87 | 4589641 | 2175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O RELEASED BY CREW 078S07 CLOSED AT 20:19 TICKET COMPLETE VER/CRB AJB
6439 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-19 10:10 | 2016-01-19 12:35 | 15 | 145 | 4631271 | 2175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | X ARM IS BROKE ON POLE #38831027D005751 PRIMARY PHASE & NETURAL DOWN BROKE IN THE CLEAR (151 CUT)/ WILL ISOLATE @38831027D30635 (15 CUST) .WALL NEED FLAGGERS FOR 4 LANE HWY, 2 8FT. ARMS 2 MATERIAL HANDLERS 2 LINE CREWS . OPENED ON POLE # 635 @ 10:10/ ALL POWER RESTORED 1235/ ISO 38831027D00575/ COD 151 AJB CCU
6440 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2020-08-16 00:48 | 2020-08-16 09:51 | 4 | 543 | 4333921 | 2172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans cutout failed on 1111c42.replaced cutout,restored at 09:51.
6441 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2019-08-27 03:36 | 2019-08-27 09:40 | 14 | 364 | 4949751 | 2171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAG AND GROUNDED AT POLE 1146-376////fuse on 1146-3 open/ patrolling line/ pole fire @ 1146-377/ #2 primary & neutral/ need pole top ext/ truck ok/ lifted hot tap @ 1146-376/ tagged & grounded to DDC/ Fuse on 1146-3 in @0555/ line crew required/ b tackett took control of grnds and tags//
6442 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2018-12-12 16:38 | 2018-12-12 17:48 | 31 | 70 | 4559391 | 2170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 326-2 hot line clamp came off stirrup,,,repairs made all customers restored @17:48 complete L3/HFP
6443 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-07-30 20:02 | 2019-07-30 23:39 | 10 | 217 | 4812661 | 2170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse out, cutout is broke on pole 203-16, will need to open line fuse on 227-45 long enough to replace cutout 2339
6444 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-05-31 13:21 | 2010-05-31 17:22 | 9 | 241 | 54284-1 | 2169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JACKIE MAGGARD REPORTS BURNTUP CUTOUT ON XFMR POLE// CHANGED OUT CUT OUT AND RESTORED POWER M.D.I.//VER/CRB IDC XXXX
6445 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-10-20 23:57 | 2018-10-22 12:05 | 1 | 2168 | 4290741 | 2168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | power is hot to #67B-450- fuse on xfmr is good, but no power to meter, may be bad xfmr of loose conection , no truck no right of way Released by crew 078E09 L3/HFP
6446 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-05-11 18:23 | 2008-05-11 21:40 | 11 | 197 | 61819-1 | 2167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SAME AS 61476 OPENED TO MAKE REPAIRS.....CREW REMOVED BROKEN POLE AND RESAGED OPEN WIRE SECONDARY LOOKS THAT ALL CUSTOMERS ARE BACK ON...............CPS VER/KEP IDC XXXX
6447 | South Williamson | 3200302 | BELFRY | TOLER | 2016-03-14 18:31 | 2016-03-14 21:48 | 11 | 197 | 4846531 | 2167 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON 1062-C-401 GOING TO MAKE REPAIRS REPLACED CUTOUT ON 1062-C-401 RESTORED POWER AT 21:48 ISO38821062C00401 COD 11
6448 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-11-08 07:58 | 2008-11-08 08:55 | 38 | 57 | 63215-1 | 2166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3400303//LOW SIDE FUSE IS OUT ON STEP DOWN TRANS. AT POLE 1101-126. I AM PATROLLING LINE NOW. LIGHTENING ARRESTER ON CSP TRANS. AT POLE 1101-130 HAD SHORTED OUT. I CUT IT IN THE CLEAR AND REFUSED STEPDOWN TRANS. AND IT STAYED.// VER/TOM IDCC FP126, CDC88 XXXX
6449 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-07-03 21:14 | 2012-07-05 09:17 | 1 | 2163 | 4294781 | 2163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200, TRUCK OK. CREW REQUIRED RELEASED BY CREW 078S11--TRANSFORMER REPLACED 7-4, POWER ON PLEASE CLOSE TICKET. WDC RELEASED BY CREW 077E04
6450 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-08-19 12:50 | 2021-08-19 14:33 | 21 | 103 | 4119781 | 2163 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | copper out of the bottom of the line fuse was touching deadend insulator, i pulled copper away from deadend insulator, refused and restored
6451 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-01-23 09:45 | 2016-01-23 10:45 | 36 | 60 | H4642991 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4642991***** FOUND BAD CUTOUT @ POLE 151-86 ( ONLY 2 CUSTOMERS EFFECTED BEFORE OPENING LINE FUSE)..WILL HAVE TO OPEN UP @ POLE 151-45 TO SAFELY MAKE REPAIRS...OPENED LINE FUSE UP @ 09:45 (36 ADD CUST).CLOSED BACK IN @ 10:45 RESTORING ALL CUSTOMERS// DUPLICATE IN HOIS/ ISO 37820151000045/ COD 38/ VER/BOW AJB
6452 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-11-21 21:40 | 2015-11-22 01:40 | 9 | 240 | 4477461 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 67-486 OPENED LINE FUSE 2140 POLE 67-515 BAD CUTOUT POLE FIRE RELEASED BY CREW 078S08.CREW ON SITE,,INSTALLED POLE TOP EXTENSION.. ALL POWER RESTORED VER/KEP
6453 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-05-29 18:30 | 2010-05-29 20:00 | 24 | 90 | 53452-1 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OPENED DUE TO A BROKEN CUTOUT ON ORDER# VER/KEP L3/KEP IDC XXXX
6454 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-06-17 20:09 | 2013-06-18 14:09 | 2 | 1080 | 4359591 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SEC. POLE 37830047D00080// OPENED XFMR ON 37830047D00002 // 35-5// BROKE// WILL NEED POLE // SMALL PIECE 4/3 // 100 HPS LIGHT / / 3 ARM// ROAD CROSSING // TRUCK APPROACH//2 CUST OUT RELEASED BY CREW 074S05 CREW ONSITE REPAIRS COMPLETE COD-2 ISO TF 37830047D00002 VER/HFP L3/HFP IDC XXXX
6455 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-03-03 16:10 | 2016-03-04 10:10 | 2 | 1080 | 4807701 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR/ ISO 38830188C00182/ COD 2/ VER/BOW
6456 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2010-12-17 16:30 | 2010-12-17 21:00 | 8 | 270 | 53664-1 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD RISER CONNECTION--SEND TO P TOLLIVER RELEASED BY CREW 078S07//OPENED TRANSFORMER POLE 69-4208 @ 2000 TO MAKE REPAIRS OUTAGE APPROX 1 HR. PT//REPAIRED CONNECTION ON HOT LEG AND DEADENDED NEUTRAL POWER RESTORED AT 21:00 PR TOLLIVER//COD 8 IDC XXXX
6457 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-01-06 10:59 | 2014-01-06 11:26 | 80 | 27 | 4236661 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | LOST SECTIONALIZER WHEN RECLOSER OPERATED ON 4232111 WHILE TRYING TO CLOSE//COD 80// VER/DBM IDC XXXX
6458 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-06-01 21:59 | 2008-06-01 22:07 | 270 | 8 | 54211-1 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3308401/ CREW OPENED TO SAFELY MAKE REPAIRS ON 53767 VER/KEP IDCC CCSCO XXXX
6459 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2012-06-19 20:01 | 2012-06-19 20:37 | 60 | 36 | H4932771 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE 327 CUST // RISER BURNT OFF OF TWO HOLE PAD CONNECTOR ON GOAB SWITCH ON 7-C-5..NEED CREW.WILL HAVE TO DROP STATION BREAKER TO REPAIR...//..JUSTICE, HOMER & MATNEY, EDWARD OPENED CB @ 2001 INTERUPTING AN ADDITIONAL 260 CUSTOMERS. // CLOSED CB @ 2037 RESTORING ALL CUSTOMERS. THIS IS FOR THE 60 CUST IN AREA 1275 DURRING THE FEEDER OUTAGE // VER/HFP L3/HFP IDC XXXX
6460 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2021-06-06 22:05 | 2021-06-07 00:20 | 16 | 135 | 4677251 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse open @ 265-A-56..(ASSESSING CONDITION)..Fuse was broke in Cutout,Refused and Restored service @ 12:20
6461 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-10-10 17:30 | 2015-10-10 20:30 | 12 | 180 | 4336861 | 2160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE HAS BROKE OUT OF DEAD-END SHOE AND DROPPED DOWN ENOUGH TO BURN NEUTRAL DOWN, POLE # 967-2, ONLY THING HOLDING PRIMARY IS LINE FUSE ON THIS POLE, WILL HAVE TO OPEN LINE AT NEXT FUSE BACK TO MAKE REPAIRS , OPENED LINE FUSE ON 991-9 AT 17:30, CLOSED AT 20:30, ALL POWER RESTORED/ ISO 38830991000009/ COD 12/ VER/BOW L3/HFP XXXHFP
6462 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-02-27 08:24 | 2009-02-27 11:10 | 13 | 166 | 52130-1 | 2158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | VER/HFP SAME AS 52022, THEY HAVE POWER CALLED CUST GOT A ANSWERING MACHING L3/HFP IDCC NOT A DUPLICATE MCCNI XXXX
6463 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2022-08-04 15:53 | 2022-08-05 09:52 | 2 | 1079 | 4675211 | 2158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOPS BURNT AT POLE 37830254B00074Held overnight per Jeff Baker. Clamp burnt off on pole 254-B-74, repairs made and power restored at 9:42.
6464 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-06-26 08:37 | 2022-06-26 23:48 | 3 | 911 | 4320961 | 2157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lat cutout broke @ 38830900000090.//Should be able to replace with big bucket if some brush is cut.// Released by crew 074S11
6465 | Pikeville | 3407103 | TOPMOST | KITE | 2012-05-18 13:41 | 2012-05-18 20:35 | 14 | 414 | 4807231 | 2156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINE FUSE BLOWN ON POLE 37830233000014 /// PATROLING /// FOUND POLE 37830233000047 ROTTED AND FELL OVER /// WILL NEED 45/5, 8FT ARM, PINS/INS, 4WD LINE TRUCK & PADS OR HAMTRACK /// CUT INLINE DEADEND JUST ABOVE 37830233000044 TO ISOLATE TROUBLE /// GOING TO ENERGIZE UP TO 233-44 /// HOT TO POLE 233-44 @ 15:55 /// FINAL CUSTOMER RESTORED @ 20:35 RELEASED BY CREW 074H18 ///VER/CRB L/3 CRB IDC 90 MIN TRAVEL TIME XXXX
6466 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-10-27 14:28 | 2015-10-27 18:13 | 15 | 225 | 4380951 | 2154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE#287-78//////CUTOUT BURNT TOP OF POLE287-271 OFF NEED LINE CREW //// FIBERGLASS EXTENSION,CUTOUT AND BRACKET//// NO TRUCK//// ISOLATED TROUBLE ON POLE#287-91 LIFTED HOT TAP/// CLOSED LINE FUSE IN @ 16:22 AND RESTORED UP TO 287-91//MADE MDC TO SHOW THE L/F AS A 20T// ENERGIZED LINE ON POLE#287-91 @ 18:13 AND RESTORED REST OF CUSTOMERS RELEASED BY CREW 074H17 L3/DKG VER/CRB AJB
6467 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-01-31 11:01 | 2011-01-31 17:00 | 6 | 359 | 52476-1 | 2154 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELEASED BY CREW 078S01 COMP 1700 // BAD SECONDARY UNDERGROUND // REPAIRED BAD UG //COD 6// VER/DBM IDCC FEC57 XXXX
6468 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-12-03 07:39 | 2008-12-04 01:35 | 2 | 1076 | 54115-1 | 2152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | STS WR# 27520941 /// GOING TO OPEN PAD MOUNT TO CHECK// WAITING ON FUSE FOR PAD MOUNT PADMOUNT TRANSFORMER IS BAD WILL HAVE TO REPLACE WAITING ON A TRUCK TO HANDLE THE WEIGHT RELEASE TO PAUL HICKMAN AND UG CREW . VER/KEP L3/KEP IDC XXXX
6469 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-08-02 07:54 | 2021-08-02 19:51 | 3 | 717 | 4992411 | 2151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG hot leg, cut loose at pole, and bad leg marked in meterbase. Send to Rick Morgan. Possibly put power temp on, or repair. Released by crew 078S02//Arrived RM trouble shooting/replaced underground and installed new pedestal volatge good please close tic RM
6470 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2017-04-29 18:00 | 2017-04-30 01:10 | 5 | 430 | 4695791 | 2150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HIGH SIDE STEPDOWN OUT @ 37830517000085 (48 TOTAL CUSTOMERS : 5 SLEMP DEFEATED CREEK, 43 DAISY LEATHERWOOD) STEPDOWN FUSE BLOWN ON POLE 517-85, REFUSED AND IT BLOWED AGAIN, WILL NEED 500KVA STEPDOWN,//CREW ON SITE - FETR 0400//TOM POWER RESTORED AT 13:10 RELEASED BY CREW 075H03
6471 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-11-03 00:02 | 2011-11-03 00:27 | 86 | 25 | 4046021 | 2150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SDB / 1202 / OPENED RECLOSER AT POLE 620-A1-342 TO REPAIR PRIMARY RISER BURNT OFF AT POLE 38830619000032. ASSOCIATED WITH ORDER 4045811. CC = 86. --- SDB /1227 / RECLOSER AT POLE 342 CLOSED. IDC XXXX
6472 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-02-20 20:06 | 2015-02-21 14:01 | 2 | 1075 | 4059291 | 2150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 19900/120/240 BAD. CAN USE TRUCK. VER/SEF
6473 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-03-17 17:02 | 2014-03-17 17:45 | 50 | 43 | 4503211 | 2150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SERVICER FOUND POLE 37830447000063 BROKEN // WILL NEED TO TAKE AN OUTAGE ON RECL ON POLE 37830447000121 TO MAKE POLE SAFE // OPENED RECL @ 17:02 CLOSED @ 17:45 /// 50 CUST.. GUYED POLE OFF TEMP .& MADE SAFE WILL REQUIRE YARDDOG TO REPLACE POLE COD-50 ISO OCR 37830447000121 VER/HFP L3/HFP IDCC CHANGED FROM UNKNOWN CAUSE XXXX
6474 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-07-05 23:20 | 2017-07-06 02:19 | 12 | 179 | 4078811 | 2148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 118 C 4102 BAD 7200 - 50 KVA 120/240, TRK OK OPENED CAN @ 23:20./FETR0300/VEM/REPAIRS MADE AND ALL CUST RESTORED 0219/PLEASE CLOSE TICKET/THANKS/VEM //COD 12// VER/DBM
6475 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-03-24 12:58 | 2017-03-24 13:10 | 179 | 12 | 4582531 | 2148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OUTAGE NECESSARY TO REPLACE BURNT UP CONNECTION ON TAP--CREW ON SITE--OPENED RECLOSURE DUE TO HOT LINE CLAMP FAILURE--MAKING REPAIRS---APPX 30-45MIN OUTAGE--OPENED OCR ON PL 44-665 AT 12:59--MADE REPAIRS AND CLOSED OCR 44-A-665 AT 13:10---TBL TKT COMP /// COD-179 ISO OCR 38830044A00665 = HOT LINE CLAMP ON LOAD SIDE OF RECL = VER/HFP L3/HFP AJB
6476 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-04-14 07:22 | 2014-04-14 09:15 | 19 | 113 | 4601411 | 2147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER WENT BAD ON POLE 37830223B00263 === BOTTOM OF ARRESTER BLOWN OFF == REFUSED LINE POWER OK//MADE AED VER/CRB IDC XXXX
6477 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2016-12-27 10:48 | 2016-12-27 11:07 | 113 | 19 | 4242251 | 2147 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED BAD DEAD END INSL. AND RESTORED POWER. OFF AT 10:48 BACK ON AT 11:07 TIM MCCOY RELEASED BY CREW 074H10 VER/CRB AJB
6478 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2020-05-24 17:22 | 2020-05-25 10:40 | 3 | 1038 | 4897851 | 2146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 xfm on pole 37830091D00081 2ccReleased by crew 074S11. CREW ON SITE, OPENED LINE FUSE ON PL#37830091D00180 AT 09:30 1cc TO CHANGE 25kva. BACK ON AT 10:40
6479 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-09-16 19:49 | 2011-09-17 13:42 | 2 | 1073 | 4878251 | 2146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD BURNT TOP OF POLE OFF 45/4 POLE DEADEND POLE CUST SAID OK TO TAKE SMALL TRUCK ACROSS BRIDGE WILL WORK TOMORROW 09/17/11 CALLED JEFF COMBS WILL GET MEN AND MATERIAL AND START ABOUT 07:30 AM RELEASED BY CREW 077H01 //VER/CRB IDC DOES FUSE FEED BOTH TAPS, CHANGED FROM 1 CUSTOMER XXXX
6480 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2021-07-11 05:22 | 2021-07-11 16:50 | 4 | 688 | 4889331 | 2146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke @ 37830140C00052.// Will open line fuse on same pole to safely replace cutout.// Opened tap cutout and it is broke also.//Need big bucket to replace cutouts.// Opened tap @ 10:25.// Flaggers required//Restored @ 16:50 Released by crew 074S11
6481 | Paintsville | 3410602 | E.PRESTON | LANCER | 2017-04-08 09:08 | 2017-04-08 13:40 | 10 | 272 | 4630141 | 2145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 38830955B00208 BURNT OFFF/NEED POLE EXT. 2 FIBERGLASS T BRACKETS, 2 15 KV CUTOUTS, 1 ARRESTOR, PRIMARY DEADEND HARDWARE & INSULATOR, & 3 SHIELD BLOCKSNEED POLE EXT. 2 FIBERGLASS T BRACKETS, 2 15 KV CUTOUTS, 1 ARRESTOR, PRIMARY DEADEND HARDWARE & INSULATOR, & 3 SHIELD BLOCKS.CUL LOOP ON 38830955B00200 & CLOSED IN ON POLE38830955B00532 AT 11:45/ FUSE 38830955B00200 ON @ 1340 MD DONE/ VER/BOW L3/HFP XXXHFP
6482 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2017-09-01 08:45 | 2017-09-01 12:00 | 11 | 195 | 4315661 | 2145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CENTER PHASE `B` PHASE OUT 11 CUSTCENTER PHASE B PHASE OUT 11 CUST. BAD CUT-OUT ON POLE 449-990 FEEDING OPEN X-FMR BANK FOR WATER PLANT. THIS CUT-OUT IS OFF THE B PHASE WHICH IS FED FROM 449-77. BAD CUT-OUT TOOK OUT LINE CUT-OUT ON POLE 449-77. WATER PLANT CALLED IN ALSO (TICKET 4315561) IS CUASE OF THIS OUTAGE.CENTER PHASE B PHASE OUT 11 CUST. VER/HFP L3/HFP SJG (SOUTH FUSE)
6483 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-11-27 19:33 | 2020-11-27 20:38 | 33 | 65 | 4726181 | 2145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | High side riser burnt off in the clear on recloser pole 129-B-17. Repairs made and power restored at 20:38.//cod 33
6484 | Whitesburg | 3401301 | FLEMING | NEON | 2012-12-06 00:54 | 2012-12-06 09:50 | 4 | 536 | 4446091 | 2144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | THE PRIMARY IS DOWN BETWEEN POLE 355-299 AND 355-321, I NEED TWO LINEMEN AND A BIG BUCKET. WE WILL FIX FIRST THING IN THE MORNING. 0714 - CALLED BRUCE LINDON LEFT VOICE MAIL TO ARRANGE CREW. VER/KEP IDC CHANGED FROM UNKNOWN XXXX
6485 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2014-07-09 14:22 | 2014-07-09 18:50 | 8 | 268 | 4220921 | 2144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE ONLY OPEN AT THIS TIME . WILL NEED TO OPEN C PHASE WHEN CREW ARRIVES, FAILED TRANSFORMER CUTOUT AT POLE 220 HAS CROSSARM BURNED APART, D. MASSEY HAS ROW AND KYPCO CREWS ENROUTE / GXJ . OPENED C PHASE AND TRANSFORMER ON POLE 1145-20 AT 16:20. ALL CUSTOMERS RESTORED AT 18:50 / GXJ RELEASED BY CREW 074S03//COD 8 + 16// AJBC CNT32 INTL PH A OUT W/8. @16:20 OP PH C W/24 SEE H4220921. TON19:00, PER COMM.
6486 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-07-30 20:45 | 2011-07-31 01:51 | 7 | 306 | 4645041 | 2142 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 92-276 BAD 37,5 TRANS TRUCK OK RELEASED BY CREW 078S08 // 0145 RESTORED IDCC PN510 XXXX
6487 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-01-11 18:40 | 2009-01-11 21:13 | 14 | 153 | 54308-1 | 2142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000102// POLE 46-2136 BAD 50KVA WR 28015351//CREW ON SITE/FETR2147/VEM/XFMR CHANGED AND POWER RESTORED TO ALL CUST/PLEASE CLOSE TICKET/VEM VER/JHM ADDED 3 COD FROM MISMAPPED CUSTOMERS L3/KEP IDC XXXX
6488 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-04-26 15:40 | 2010-04-26 17:39 | 18 | 119 | 51506-1 | 2142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ONE PHASE OUT....DAH RELEASED BY CREW 074S08 CUTOUT REPLACED ON AT 17:39 D SAMMONS//VER/CRB IDC XXXX
6489 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2022-08-11 06:36 | 2022-08-11 18:30 | 3 | 714 | 4724881 | 2142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Replaced broken fuse in cutout door and restored @18:30
6490 | Hazard | 3309302 | VICCO | JEFF | 2019-11-30 21:02 | 2019-12-01 01:00 | 9 | 238 | 4108161 | 2142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad dead end insulator 19.9 need to change both insulators pole 323b-72 truck acess Released by crew 077H14/ ISO 37830323B00072/ COD 9
6491 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2012-02-13 01:21 | 2012-02-13 03:20 | 18 | 119 | 4343801 | 2142 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY CABLE BURNED INTO. I OPENED XFMR AND MADE REPAIRS AND MADE HOT IDCC PN78 XXXX
6492 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2018-06-08 11:01 | 2018-06-08 13:07 | 17 | 126 | 4568381 | 2142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse open on pole 444-3, bad arrester on 37830444000065//line fuse open on pole 444-3, bad arrester on 444-65, made repairs restored power at 13:07
6493 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-02-28 00:25 | 2017-02-28 09:20 | 4 | 535 | 4427181 | 2140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CALLED CUST/ FOUND BAD ARRESTER ON XFMR 833-449. CLEARED AND RESTORED @ 9:20. SH VER/CRB L3/HFP XXXHFP
6494 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-10-31 04:05 | 2022-10-31 11:13 | 5 | 428 | 4079721 | 2140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout broke manual, need a 19.9 cutout already on fiber glass bracket/ line fuse feeds transformer on pole 37830182A00092
6495 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-11-17 09:36 | 2019-11-17 16:44 | 5 | 428 | 4041951 | 2140 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 Kva xfm 7200/// Putting out 60 volts on one leg///will need xfm and 1 man/// I got all meters pulled to keep caution lights on @ intersection// Opened xfm @ 15:07 to make repairs
6496 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-12-31 10:40 | 2009-12-31 17:48 | 5 | 428 | 52493-1 | 2140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED TO REPLACE 25 KVA TRANSFORMER WITH LIKE KIND, WILL NEED CUTOUT AND ARRESTER, TRCK ACCESS BUT MAY NEED PADS, D. MASSEY TO SEND CREW RELEASED BY CREW 074S03 VER/KEP L3/KEP IDC XXXX
6497 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-03-26 13:36 | 2008-03-26 14:45 | 31 | 69 | 60874-1 | 2139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | 3310501// CREW OPENED B PHASE RECLOSER TO REPLACE DEFIECTIVE REGULATOR ON POLE 37830104000118 -- 31 CUSTOMERS OUT// SECOND OUTAGE RELATED TO ORDER 60870-1//BYPASS SWITCH DID NOT CLOSE CORRECTLY AND NEEDED TO OPEN RECLOSER AGAIN TO REPAIR BYPASS SWITCH/ IDC CHANGED COUNT FROM 148 XXXX
6498 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-01-28 19:39 | 2015-01-28 21:08 | 24 | 89 | 4971271 | 2136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RECLOSER IS OPEN ON 38830524000189//COD 24// PATROLLING LINE, PLEASE HAVE NEUTAL ADDED TO ABNORMALS AT 524-101TO 548-2. FOUND BROKEN TIEWIRE AT 38830548000007 REPAIRES MADE APR AT 2108 CLOSE TICKET//MADE AED// VER/CRB L3/HFP XXX AJB
6499 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-09-12 09:40 | 2016-09-12 10:15 | 61 | 35 | H4886441 | 2135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CROSSARM BRACE BROKEON POLE 473-122 CAUSING PHASE TO LAY ON ARM, LOOP BURNT INTO ON POLE 473-105,OPENED SOLID BLADES ON POLE 473-103 AT 09:40 TO ISOLATE..MADE REPAIRS RESTORED POWER AT 10:15. RELEASED BY CREW 077S11//A PHASE OPEN FROM START MADE MDC VER/CRB// BUS OBJ INDICATES INITAL `A` PHASE OUTAGE L3/HFP HFPC FEC44 CNT71 AJB
6500 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-08-24 12:22 | 2015-08-24 13:59 | 22 | 97 | 4168181 | 2134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | NOW FUSES NOT CUTOUTS NEED TO DO AN MD/ B PHASE ONLY (22 CUST), ARRESTER BLOWN AT POLE 365, REFUSED LINE CUTOUT WITH 50T, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03/ ISO 37820025B00391/ COD 22/ VER/BOW // MD ENTERED L3/HFP XXXHFP AJB
6501 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-07-17 22:48 | 2008-07-18 02:45 | 9 | 237 | 53820-1 | 2133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000902// BAD 25KVA CSP TRANSFORMER-LEAKING OIL-CALLING CREW/ NEED 50KVA-CUTOUT-AN 4/0 RISERS-B REYNOLDS TO WORKTRUCK ACCESSABLE COD-9 VER/KEP IDC XXXX
6502 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-02-25 13:41 | 2014-02-25 15:00 | 27 | 79 | 4433661 | 2133 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | COD-27 ISO LF 37830400B00020 ENTERED 3 MD`S ON THIS VER/HFP L3/HFP
6503 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-01-30 05:10 | 2008-01-30 17:00 | 3 | 710 | 61652-1 | 2130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR WAS IN TWO PIECES, PRIMARY AND NEUTRAL WERE REAL CLOSE, RESAGGED PRIMARY AND REPLACED FUSE DOOR//COD 3// VER/DBM IDC XXXX
6504 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-03-09 16:22 | 2022-03-09 20:46 | 34 | 264 | 4594691 | 2128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire @ 38830207002016 ,,can lower ,truck to pole ,,,cut loop and let primary down @ 207-2008 ,,so fire dept could put out ,,,line fuse 207-91 back in @pole fire @ 207-2016
6505 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2021-10-24 17:29 | 2021-10-24 22:33 | 7 | 304 | 4008371 | 2128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | defective transformer 38830268D00034/ restored 2233
6506 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-07-21 21:17 | 2018-07-22 15:00 | 2 | 1063 | 4831021 | 2126 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva 19.9 manuel can replace with 25 just 2 houses about 125 feet to pole 4 men manuel right of way crew.all power restored @ 15:00 hrs.p.hicks
6507 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-04-10 03:20 | 2020-04-10 12:00 | 5 | 520 | 4614871 | 2125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. line fuse cutout broke need two 7200 cutouts on transformer and line fuse need two men and big bucket Released by crew 077S05/ Maps are wrong/ Map Discrepancies made/ line fuse on pole 37830104000125 feeding xfmrs on poles 37830104000104, 37830104000078, 37830104000125 off originally 4 customers/ opened l/f on pole 37830104000125 feeding toward 37830104000114 at 1115 1 customer/ all power restored 1200
6508 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-11-20 15:41 | 2011-11-20 18:33 | 27 | 172 | 4095071 | 2124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--BAD CUTOUT ON POLE 38830069D37132 NEEDS REPLACED--NO TRUCK--ISOLATED TRANSFORMER ON POLE 38830069D37132--LINE FUSE BACK IN AT 16:27 RELEASED BY CREW 078S07------ POWER ON @ 18:33 /// VER/CRB IDC XXXX
6509 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-07-29 22:52 | 2015-07-30 01:49 | 12 | 177 | 4958081 | 2124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-154 BAD CUTOUT NO TRUCK RELEASED BY CREW 078S08/CREW ON SITE/FETR0300/VEM/REPAIRS MADE AND ALL CUST RESTORED 0149/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP AJBC TOF22:40 INTL CUST CALL WAS TO REPORT TROUBLE ONLY.
6510 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-03-15 20:14 | 2012-03-16 05:05 | 4 | 531 | 4586381 | 2124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 37830129A00086 RELEASED BY CREW 077S04BROKEN CUTOUT ON POLE 37830129A00086 --- REPLACED CUTOUT. VER/ARN IDC XXXX
6511 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-06-03 00:53 | 2011-06-03 12:41 | 3 | 708 | 4226451 | 2124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7.2 KV 25KVA TRANSFORMER ON MANUAL POLE, ALSO NEED TO CHANGE CUTOUT AND ARRESTOR AND TEE BRACKET. RELEASED BY CREW 077S04//VER/CRB IDC XXXX
6512 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-09-28 16:28 | 2008-09-28 19:25 | 12 | 177 | 51704-1 | 2124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP PATROLING LINE-REPLACED BAD ARRESTOR ON POLE 38830020B43558 PATROLING LINE-REPLACED BAD ARRESTOR ON POLE 20-3558// BAD LINE FUSE CUTOUT-CALLED CREW TO HELP REPLACE IDC XXXX
6513 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-11-18 14:53 | 2013-11-18 18:06 | 11 | 193 | 4054091 | 2123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE IS BLOWN ON POLE 53-38. DEAD END INSULATOR IS BAD AND GOING TO GROUND ON THE GUY WIRE. DENNIS MASSEY IS ON THE WAY TO ME WITH THE MATERIAL. VER/CRB L3/HFP IDC XXXX
6514 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2010-05-02 16:33 | 2010-05-02 19:46 | 11 | 193 | 54236-1 | 2123 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#34926444 RELEASED BY CREW 078S08// XFR FUSE OPEN ON 69-1083/ TREES ALL OVER OPEN WIRE/ BAD 25 KVA / WE WILL TRY TO TRIM OUT OPENWIRE THE BEST WE CAN//VER/CRB IDC XXXX
6515 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-07-25 19:09 | 2009-07-26 12:50 | 2 | 1061 | 58675-1 | 2122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP IS BURNED INTO ON POLE 189-102. WE ARE GOING TO HAVE TO OPEN LINE FUSE ON POLE 189-51 LONG ENOUGH TO MAKE UP LOOP. WE HAVE TO WAIT UNTIL STORM MOVES ON. RELEASED BY CREW 074S01//COMPLETED @ 1250 PER TIM HALL// IDC XXXX
6516 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-02-27 10:30 | 2009-02-27 17:52 | 13 | 442 | 52114-1 | 2122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PATROLING LINE--ALL -CUSTOMERS 0N EXCEPT TRANSFORMER 67-451--LINE FUSE IN AT 12:50 RELEASED BY CREW 078S07//REPLACED 25KVA ALL CUST. RESTORED AT 17:52 P TOLLIVER//COD 13// VER/DBM IDC XXXX
6517 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-04-12 15:17 | 2008-04-12 20:20 | 7 | 303 | 50547-1 | 2121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S02 BAD 19.9 50 KVA TRANSFORMER. 120/240. PAUL HAS CONTRACTOR CREW IN ROUTE TO REPAIR. VER/HFP IDCC CNT1 XXXX
6518 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-09-29 17:22 | 2014-09-30 02:35 | 7 | 553 | 4537191 | 2121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT ON POLE 529-18 , CLOSED LINE FUSE OUT ON POLE 529-18 @ 20:45 POWER BACK ON . FOUND BAD XFMR ON POLE 529-73 , NEED LINE CREW & 25KVA XFMR & CUTOUT / BRACKET . ALL POWER BACK ON BUT 2 CUST. VER/SEF L3/IDC XXXX
6519 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-12-05 03:49 | 2011-12-05 08:14 | 8 | 265 | 4140691 | 2120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3000301/ PER SET GUIDELINES, WILL HAVECHECKED AT REGULAR WORKTIME //--BROKEN FUSE LINK VER/KEP IDC XXXX
6520 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2009-02-07 07:52 | 2009-02-07 13:45 | 6 | 353 | 56365-1 | 2118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3400701// #2 AA DOWN, MAP INDICATES 1/0 ... REPLACED WITH 150 4/0 TRIPLEX ... ALL WORK COMPLETE / GXJ VER/LDA IDCC CCO XXXX
6521 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-07-29 00:26 | 2017-07-29 09:15 | 4 | 529 | 4200481 | 2116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER/NOT P CUSTOMER. HOLD NORMAL SHIFT START ON 07/29 POLE 38830067A00325 BAD CUTOUT 8T FUSE VER/CRB
6522 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-09-10 15:30 | 2017-09-10 19:25 | 9 | 235 | H4343941 | 2115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINE FUSE OPEN @37830071C30923, FAULT INDICATOR TRIPPED AT FIRST TRANS. AFTER L/F, WILL NEED A LINE CREW TO HELP LOCATE FAULT, 3 PADMOUNT TRANS. ARE AFFECTED. ISOLATED BAD SPAN OF CABLE BETWEEN TRANS. 71-165 AND 166, CLOSED L/F @71-C3-923 AND PICKED UP CUSTOMRS ON 165 @1232. OPENED THAT L/F BACK UP @1530 TO SPLICE CABLE, MADE ALL REPAIRS AND CLOSED L/F BACK IN @1925. RELEASED BY CREW 074S05 37830071000165 VER/AWD SJG
6523 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-10-10 19:05 | 2014-10-10 23:00 | 9 | 235 | 4603921 | 2115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BROKE AT POLE 519-55, WILL NEED 1 MAN TO HELP CHANGE. CHANGED C/O CLOSED BACK IN AT 2300./// ISO 37830519B00055// COD 9 CCC********// VER/BOW L3/HFP
6524 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-04-26 17:18 | 2022-04-26 22:20 | 7 | 302 | 4803841 | 2114 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required can lower burnt off material handler no grounds or tags/223-182 Released by crew 078S03,repairs made all cust restored @ 2220 please close ticket thanks.bt
6525 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-01-06 10:00 | 2018-01-06 14:24 | 8 | 264 | 4712441 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer no reading on meter Bad CSP 25 KVA transformer on 851-460. Need a 50 KVA xfmr and arm mount bracket with cutout. Sec risers should work back - can truck. Released by crew 076S02// transformer replaced, restored at 14:24/ ISO 38830851C00460/ COD 8
6526 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-04-11 16:54 | 2008-04-11 19:06 | 16 | 132 | 66288-1 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINEFUSE OUT,NOTHING VISIBLY WRONG,PRESUME THAT WIND MAY HAVE BLOWN TREE INTO LINE.WILL RE-FUSE LINELINEFUSE OUT,FOUND BAD ARRESTOR,CLEARED IT UP.WILL RE-FUSE CUTOUT/LINECLEARED 3 BAD LOOKING ARRESTORS,1 WAS REALLY BAD.RE-FUSED LINE,ALL OK AFTERWARDS VER/HFP IDC XXXX
6527 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2014-11-18 14:04 | 2014-11-18 17:00 | 12 | 176 | 4742461 | 2112 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE BLOWN IN XFMR BANK CAUSING THREE PHASE CUSTOMERS TO SINGLE PHASE. BAD 50KVA XFMR (120/208). LINE CREW AND FLAGGERS ENROUTE. REPLACED AND RESTORED @ 17:00. SH COD-12 ISO TF 38830954B41138 VER/HFP L3/HFP
6528 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-10-06 21:14 | 2014-10-06 22:50 | 209 | 96 | 4560211 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | POLE 1098-536 ON FIRE SENT TO BILL RELEASED BY CREW 078S08-----POLE FIRE ON 1098-4001---- HOT TAP LIFTED ON 1098-533/// OPENED RECLOSER ON POLE 39831099B10161 TO LIFT HOT TAP ON POLE 39831098C00533 TO REPAIR POLE ON POLE 39831098C04001 AJB TOF19:23 DELTETED REST STEP LCD 39831098C00536 CCO FEC57 CDC83
6529 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2021-07-02 05:38 | 2021-07-02 11:30 | 6 | 352 | 4844611 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | line fuse out on pole 917D-73..top of pole burned into on pole 941C-541.i have an elliot crew on the way.made repairs and got the fuse on pole 917D-73 back in @ 11:30
6530 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2016-08-21 20:15 | 2016-08-22 00:39 | 8 | 264 | 4823061 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TAGGED & GROUNDED TO KYDDC/CREW REQUIRED 40/5 WINDSTREAM POLE INLINE TRUCKS OK 231-58 ISOLATED AND GROUND AT 231-56 TAGGED TO DDC RELEASED BY CREW 078S03/CREW ON SITE/FETR 0100/VEM/REPAIRS MADE AND ALL CUST RESTORED 0039/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP L3/HFP HFPC FP38830231000056
6531 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-04-05 23:01 | 2009-04-06 10:45 | 3 | 704 | 65568-1 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAD A BAD 25 KVA SINGLE BUSHING 7200 VOLT 120/240, CAN USE TRUCKS, RIGHT BESIDE OF ROAD, HAS 3 CUST ON THIS NEED CREW TO CHANGE THIS OUT RELEASED BY CREW 078S06---CREW ON SITE//VER/CRB IDC XXXX
6532 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2013-01-05 15:29 | 2013-01-05 19:53 | 8 | 264 | 4571891 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CHECKING ///J BAKER & G. WHITAKER & R AMBURGEYCHECKING.PHASE DOWN HOT ON HILLSIDE AT POLE 448-133, OPENED BOTH L/F AT POLE 448-130 TO ISOLATE, CREW COMING TO MAKE REPAIRS.CHECKING.PHASE DOWN HOT ON HILLSIDE AT POLE 448-133, OPENED BOTH L/F AT POLE 448-130 TO ISOLATE AT 1705, CREW COMING TO MAKE REPAIRS.MADE REPAIRS CLOSED BOTH L/F AT POLE 448-130 AT 19:53. COD-41 ISO LF 37830448B00130 THIS FOR B PHASE INITALLY OUT DUP FOR C IS H4571891 VER/HFP L3/HFP IDC XXXX
6533 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-06-28 20:47 | 2008-06-29 14:23 | 2 | 1056 | 58306-1 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA XFORMER MAY GET SMALL BUCKET TO POLE RELEASED BY CREW 078S11 VER/KEP
6534 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2012-11-27 16:21 | 2012-11-27 16:53 | 66 | 32 | 4426341 | 2112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF ORDER 4424191 - OUTAGE NECESSARY TO RESTORE OPEN LOOPS ON CKT. 1 HR OR LESS VER/PDP IDC XXXX
6535 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-06 22:43 | 2014-01-07 05:45 | 5 | 422 | 4242861 | 2110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER NEED 50 19,9 KVA TRANSFORMER AND MAT BUCKET VER/SEF IDC XXXX
6536 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-12-20 13:09 | 2012-12-20 13:40 | 68 | 31 | 4487371 | 2108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE 524-95 // OPENED RECL POLE 524-189 @ 1309 //REPLACED BAD CUTOUT ON 624-95, POLE IS SAFE FOR NOW BUT DOES NEED CHANGED AT LATER DATE. PLEASE SEND TO JOHN S TH HAVE JOB WRITTEN. APR AT 1340 CLOSE TICKET. DWEST VER/KEP
6537 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-03-29 07:36 | 2020-03-29 09:40 | 17 | 124 | 4521401 | 2108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse out on pole #38831125C40532 will refuse.fuse went back out .will patrol again.isolated arrestor on pole 38831125C30683 closed in @ 09:40
6538 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-11-13 18:13 | 2011-11-14 03:00 | 4 | 527 | 4072661 | 2108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND OUT POLE 93-246 30T CALL PRC. CREW RELEASED BY CREW 078S08//FOUND BAD CABLE NEAR 93-251 CALLED FOR BACKHOE.PTOLLIVER//POWER RESTORED AT 03:00 PRTOLLIVER IDCC CDC83 XXXX
6539 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-10-29 18:39 | 2008-10-29 22:33 | 9 | 234 | 60672-1 | 2106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED LINE FUSE TO ALLOW THEM TO ISOLATE POLE TOP THAT IS ON FIRE...FETR TO FOLLOW WHEN CREW HAS POLE ISOLATED AND SAFE. RELATED TO ORDER 60656-1 WHICH REPORTED THE POLE FIRE & NO OUTAGE.//COD 9// VER/DBM IDC XXXX
6540 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2020-02-12 21:40 | 2020-02-13 01:34 | 9 | 234 | 4398411 | 2106 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed on poe 1003-347. will replace. complted power restored
6541 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-12-21 19:42 | 2018-12-21 22:58 | 84 | 196 | 4588431 | 2105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfr cutout 206-2291,crew required,no trucks Released by crew 078S05///opened recl 206-D-2051 to change cutout at 2235 - closed at 2258//broke xfr cutout 206-2291,crew required,no trucks Released by crew 078S05/arrived RM opening rec 206-2051 Released by crew 078H20 L3/HFP
6542 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2018-07-25 09:27 | 2018-07-25 16:28 | 5 | 421 | 4853561 | 2105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad neutral made temporary fix will come back tomorrow to make decision on permanet fix // WAS THIS A SERVICE OR SECONDARY PROBLEM ??? HFP
6543 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-11-30 04:50 | 2019-11-30 12:55 | 7 | 485 | 4104121 | 2105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Broken cutout on pole 1147-925, Crew required, no trucks. line fuse on 1147-273 closed back in at 09:50 Released by crew 078H04 opened line fuse 1147-273 at 12-30 back on at 12:55
6544 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-07-06 23:00 | 2019-07-07 02:47 | 25 | 227 | 4671191 | 2103 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | off @ 0208 on @ 0241 related to 4670051 ¦¦¦ COMMENTS FROM ORDER 4670051 ine fuse open on pole 375-89, wire pulled out of splice at pole 375-89, manual pole #2 all . wire, opened line fuse on pole 375-98 to isolate at 02:08 made repairs restored power at 02:41.. L3/HFP
6545 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-12-09 05:06 | 2022-12-09 13:51 | 4 | 525 | 4244491 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines.line fuse 496-25 open ,,496-25 pole burnt off ,,,no trucks ,,can lower Released by crew 078S05 complete R Green
6546 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-01-25 12:00 | 2010-01-25 14:30 | 14 | 150 | 59461-1 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33582169 // STEPDOWN CUTOUT FAILED AND CAUGHT POLE ON FIRE THERE IS ONLY 1/3 OF POLE LEFT THE BURN IS ABOVE THE XFMR HOWEVER WE WILL NEED TO REPAIR OR REPLACE POLE TO CLEAR UP I HAVE SENG BRANCH OFF THIS FEEDS THIS HOLLOW. YOU WILL NEED A 50 2 POLE 2 OR A XARM TO REPAIR IT. TIM MCCOY RELEASED BY CREW 074H10 IDCC TOF1036 XXXX
6547 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-03-29 13:45 | 2013-03-29 16:15 | 14 | 150 | 4966651 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLING LINE. FOUND BLOWN ARRESTER ON 852-125. CLEARED ARRESTER AND RESTORED @ 16:15. SH COD-14 ISO LF 38830852000031 VER/HFP L3/HFP IDC XXXX
6548 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-01-09 03:23 | 2020-01-09 04:05 | 50 | 42 | 4226471 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Broken fuse, 65t back in at 04:05
6549 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-01-07 17:30 | 2014-01-08 02:15 | 4 | 525 | 4254521 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 076S02 BAD 25 KVA XFMR ON 858-302. CREW WILL REPLACE ASAP. CREW ON SITE. RESTORED @ 2:15. SH VER/TOM L3/TOM IDC XXXX
6550 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-12-27 08:30 | 2008-12-27 15:30 | 5 | 420 | 64280-1 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT ON POLE 16C163. I HAVE CALLED DENNIS. HE IS GOING TO GET TWO MAN CREW. HEADED THIS WAY. RELEASED BY CREW 074S11//3413401BAD LINE FUSE CUTOUT ON POLE 16C163. I HAVE CALLED DENNIS. HE IS GOING TO GET TWO MAN CREW. HEADED THIS WAY. //3413401 WE HAVE GOT COUTOUT REPLACED 30T FUSE BACK IN EVERYTHING OK//VER/CRB L3/KEP IDC XXXX
6551 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-10-25 11:16 | 2012-10-25 12:40 | 25 | 84 | 4170851 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-58 BAD CUTOUT 50T FUSE VER/KEP IDC XXXX
6552 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-05-07 07:10 | 2009-05-07 10:40 | 10 | 210 | H62162-1 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001203 -OPENED TRANSFORMMER AT 07:10--HIGH VOLTAGE ON TRANSFORMER--132/275 CALLING CREW RELEASED BY CREW 078S07 IDCC DUP TO OPEN TRANSFORMER XXXX
6553 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-06-20 04:48 | 2012-06-20 14:30 | 5 | 582 | 4935161 | 2100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER WILL BE DISPATCHED AT REG WK TIME. BAD ENCLOSED WESTING HOUSE CUTOUT ON 903-28, WELL NEED CREW TO CHANGE THIS ON HILLSIDE, NO TRUCKS TO POLE, CREW REQ 39830903000028 HAVE POWER RESTORED AT THIS TIME TO ALL CUST BUT ONE, TIME ON WAS 1000 RELEASED BY CREW 078S06..OPENED FUSE ON 903-2 @ 13:25 TO SAFELY MAKE REPAIRS.OPENED FUSE ON 903-2 @ 13:25 TO SAFELY MAKE REPAIRS.POLE 903-28 IS ROTTEN AT THE TOP AND THE BOTTOM.NEEDS ATTN VERY SOON..BLR RELE ///VER/CRB IDC XXXX
6554 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-11-18 22:40 | 2017-11-19 16:09 | 2 | 1049 | 4572881 | 2098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole69-201 NBT Released by crew 078H01/repairs made and all cust restored 1609/please close ticket/thanks/vem
6555 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2021-02-22 11:12 | 2021-02-22 19:56 | 4 | 524 | 4217211 | 2096 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | coating had wore of hot legs and was getting together. replaced wire and restored power
6556 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2017-07-09 21:36 | 2017-07-10 01:58 | 8 | 262 | 4100301 | 2096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE45-4692 PRI. DOWN ON HILL THIRD POLE FROM FUSE NO TRUCKS POLE 45-4689 30T OUT RELEASED BY CREW 078S08,REPAIRS MADE ALL CUST RESTORED @ 0158 PLEASE CLOSE TICKET THANKS.BT//VER/ADH SJG
6557 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-07-10 12:49 | 2015-07-10 14:20 | 23 | 91 | 4763921 | 2093 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT IS BROKEN, NEED LINE CREW TO MAKE REPAIRS, WILL NEED AWP, TO DO TRAFFIC CONTROL, CAN USE TRUCK RELEASED BY CREW 078S06,REPLACED CUTOUT ALL CUST RESTORED @ 1420 PLEASE CLOSE TICKET THANKS.BT AJB
6558 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-11-03 16:35 | 2016-11-03 21:15 | 18 | 280 | 4073161 | 2091 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEPDOWN 92-187 B PHASE ONLY (18 CUST) RESTORED 80T @ 17:40 (12 CUST). BAD 25KVA @ 92-193 WHICH SHOWS ON A PHASE BUT IS B PHASE, INSTALL NEW C/O & ARRESTOR @ 92-143, 144/ 38830092B00144 ON @ 1900(1 CUST)/ 38830092B00143 ON @ 1918 (2CUST)/ REPLACE 25 KVA 38830092B00193 CUST RESTORED @ 2115 (3CUST)/ PLEASE CLOSE TICKET THANKS.BT/ MD DONE/ VER/BOW
6559 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-12-12 14:18 | 2011-12-12 14:40 | 95 | 22 | 4172131 | 2090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPENED STEPDOWN IN ORDER TO MAKE REPAIRS TO DOWNED NEUTRAL//COD 95 // OPENED 1418 CLOSED 1440 CU TOO ALUM SPLICE FAILED VER/KEP IDC XXXX
6560 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-09-01 17:46 | 2021-09-01 21:15 | 10 | 209 | 4198711 | 2090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Bad dead-end insulator on pole 193-69 //Steve Ray has crew enroute to assist///Repairs made closed line fuse in @ 21:15 and restored service
6561 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-12-25 22:44 | 2022-12-26 01:54 | 11 | 190 | 4358771 | 2090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | servicer ETA 2359 //. crew required burnt up 4/3 service drop. needs upgraded to 2/3 drop. need 130ft of 2/3 service wire. Released by crew 078H33. crew on site. repairs made transformer restored @ 1:54 complete LG
6562 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-08-19 07:02 | 2014-08-19 14:00 | 5 | 418 | 4382931 | 2090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | RELEASED BY CREW 078S11.UNDERGROUND SECONDARY BAD..INSTALLED POWER TEMP ON TWO HOUSES
6563 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-10-16 13:42 | 2014-10-16 17:34 | 9 | 232 | 4637441 | 2088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON POLE 38831108D00333 LINE FUSE CUTOUT GATE IS BURNED INTO, THIS IS A PHASE OR LEFT HAND PHASE BACK TOWARD STATION, GREG SHOUSE IS GOING TO HELP ON THIS//COD 9 MAP SHOW THIS TO BE "C" PHASE VER/CRB L3/HFP AJB PH C PER CUST CALL.
6564 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-02 19:20 | 2009-06-03 12:44 | 2 | 1044 | 61492-1 | 2088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S01 COULD BE BAD XFORMER OR CURRENT LIMETT FUSE. NEED TREE CREW TO REMOVE VINES. RELEASED BY CREW 078S01//COD 2// VER/DBM IDC XXXX
6565 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-11-07 13:21 | 2018-11-07 17:13 | 9 | 232 | 4376671 | 2088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | HOLD ORDER DOL 868434/ Crew opening SWS 3783-0379-C0-0158 to repair pole 3783-0020-00-0009/ ISO 37830020000009/ COD 10
6566 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-11-24 07:38 | 2008-11-24 07:50 | 174 | 12 | H51451-1 | 2088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// PHASE C RECLOSER OPEN 182C-257// COD-114//, CROSSARM BURNT OFF ON POLE 158-6// //VER/CRB IDCC DUP TO OPEN RECLOSERS AND CUT LOOPS XXXX
6567 | Hazard | 3420001 | SOFT SHELL | VEST | 2011-07-06 12:48 | 2011-07-06 19:45 | 5 | 417 | 4475151 | 2085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 107-13, POLE107-68 BURNED OFF BAD CUTOUT RELEASED BY CREW 077S11POWER RESTORED AT 19..45//VER/CRB IDC XXXX
6568 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2010-09-17 01:03 | 2010-09-17 06:01 | 36 | 298 | 50864-1 | 2082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAULT POLE 1072-189 ISO LATED AT POLE 1072-33 REC LOCK OUT 1072 -27 ,PARTIAL ALL CUST BUT ONE CREW LIST 40-5 NEW CUT-OUT AND ARRESTOR ,AND BRACKET TRUCK OK RELEASED BY CREW 078S09/CREW ON SITE/DIFF JOB/UG INVOLVED/FETR0630/VEM/REPAIRS MADE/SINGLE CUST RESTORED 0601/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 IDC CHANGED START TIME PER TICKETS XXXX
6569 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-04-01 18:23 | 2010-04-02 00:10 | 6 | 347 | 57213-1 | 2082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA 19.9 NEEDS REPLACED WILL REQUIRE YARD DOG MACHINE AND 3 MEN RELEASED BY CREW 077S04 REPLACED XFMR RESTORED POWER AT 0010 077H01 //VER/GAH IDC XXXX
6570 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-09-23 16:40 | 2013-09-23 17:06 | 80 | 26 | 4880031 | 2080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | TIE WIREOKED ON PRIMARY CREW REQUIRED PRIMARY JUST SITTING ON INSULATOR 293-80/ ON 293-78 6A NEUTRAL DOWN THIS B 2ND WINTER /SEND TO JENTS CREW RELEASED BY CREW 078S03 INSTALLED NEW NEUTRALAT POLE 293-78 TIME OFF 1640//COD 80// VER/DBM L3/HFP IDCC PN80 XXXX
6571 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-07-18 12:35 | 2022-07-18 21:15 | 4 | 520 | 4512941 | 2080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | wire off insulator at 991-72 at 2nd house, behind barn across creek, need 7200 pin and ins and tie wire, 3 man crew, manual pole, no row, no flag GRF Released by crew 077E10
6572 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-06-23 20:47 | 2015-06-24 02:30 | 10 | 343 | 4647711 | 2080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON P-851-651.50 KVA.TRUCK ACCESSIBLE.BLEW XFMR FUSE ON 851- 651 AND LINE FUSE ON 851-8.RE FUSED LINE FUSE ON 851-8 AT .22.45,,,,BACK ON AT 230 VER/KEP
6573 | Whitesburg | 3401301 | FLEMING | NEON | 2014-11-19 07:46 | 2014-11-19 09:30 | 20 | 104 | 4744721 | 2080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AT THE FUSE POLE 37830331C00108//COD 20// VER/CRB L3/HFP AJB
6574 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2016-10-07 13:25 | 2016-10-07 14:45 | 26 | 80 | H4966991 | 2080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | C PHASE REC. OPEN ON POLE 73-644//COD 86..WILL PATROL..FOUND C PHASE LAYING AND BURNT INTO ARM ON POLE 121-223 WILL NEED LINE CREW AND WILL HAVE TO OPEN THE OTHER TWO REC. ON POLE 73-644 TO MAKE REPAIRS..OPENED UNDERSLUNG SWITCHES ON POLE 121-284 @ 13:25 TO MAKE REPAIRS AND CLOSED BACK IN @ 14:45.. VER/CRB L3/HFP HFPC DUP AJB
6575 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-07-12 06:33 | 2009-07-12 13:29 | 5 | 416 | 61962-1 | 2080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP NEED CREW TO CHANGE POLE. RELEASED BY CREW 078S04 FUSE OPEN ON POLE 67-47/CREW ON SITE/DIFF LOCATION/VEM/POLE REPLACED AND POWER RESTORED 1329/PLEASE CLOSE TICKET/THANKS/VEM COD-4 ISO LF 38830067C00047 ROTTEN POLE.... L3/HFP IDC XXXX
6576 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-05-01 16:15 | 2011-05-01 16:42 | 77 | 27 | 53271-1 | 2079 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO 53179-1//LOOP BURNT OPEN ON POLE 1062-30//CREWS OPNED SWITCHES ON THIS POLE IN ORDER TO MAKE SAFE REPAIRS//COD 77// VER/DBM IDC XXXX
6577 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2009-03-26 12:43 | 2009-03-26 14:00 | 27 | 77 | 61750-1 | 2079 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3116701// SEND NOTE TO RAYBURN CUTOUT AND LA NEEDS CHGED POLE 1147-554//COD 27// VER/DBM IDC XXXX
6578 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-02-15 21:17 | 2018-02-16 03:03 | 6 | 346 | 4846311 | 2076 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva, 7200, 120/240, tkk to pole. Released by crew 078S07///opened @ 2300//replaced bad 25 kva///cust restored at 03:03///complete BR//cod 06
6579 | Paintsville | 3401101 | FALCON | FALC-OILS | 2009-04-25 11:27 | 2009-04-25 14:20 | 12 | 173 | 59920-1 | 2076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN ARRESTER//COD 12// VER/DBM IDC XXXX
6580 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-07-29 20:47 | 2012-07-29 21:48 | 34 | 61 | 4862491 | 2074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE FAILED. AJB
6581 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2016-08-23 18:35 | 2016-08-24 11:51 | 2 | 1036 | 4829971 | 2072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK 08/24 BAD 37.5 KVA- NEED TRANSFORMER AND CUTOUT. CREW ON SITE FETR 12:15 ALL PWR RESTORED @ 11:51 VER/HFP L3/HFP
6582 | Pikeville | 3421001 | BREAKS | CITY | 2011-10-05 11:11 | 2011-10-05 15:30 | 8 | 259 | 4948901 | 2072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER FAILED BLOWING THE TRANSFORMER FUSE. VER/KEP IDC XXXX
6583 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-07-31 06:44 | 2009-07-31 11:40 | 7 | 296 | 60703-1 | 2072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT CREW WILL REPLACE,,,POWER RESTORED IDC XXXX
6584 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-02-16 09:14 | 2017-02-16 10:00 | 45 | 46 | 4401541 | 2070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WHILE INSTALLING COVER-UP #4 CU. PRI. CAME OUT OF FARGO LEAD FROM RECL. HELD COND. MAKING REPAIRS NOW//SPLICE HAD GONE BAD//OPENED @ 0914 CLOSED 1000 VER/CRB L3/HFP XXXHFP AJB
6585 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2015-05-19 13:21 | 2015-05-19 14:06 | 46 | 45 | 4445721 | 2070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | EMERGENCY OUTAGE TO REPAIR CONDUCTOR WITH STRANDS BROKEN AND ABOUT TO FALL // COD - 46 ISO OCR 38830429C00364 OFF 1321 ON @ 1406 VER/HFP L3/HFP AJB
6586 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-10-31 08:00 | 2012-10-31 19:30 | 3 | 690 | 4284331 | 2070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 077S12,,FUSE TAIL BROKE, POWER RESTORED @ 19:30.RGP. - CAN CLOSE TICKET RESTORED AT 1930 MWL ///VER/CRB L/3 CRB IDC XXXX
6587 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-04-24 13:35 | 2008-04-24 15:30 | 18 | 115 | 53859-1 | 2070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3410602//REPLACING BUSTED CROSSARM//VER/CRB IDC XXXX
6588 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2010-08-22 15:48 | 2010-08-22 18:56 | 11 | 188 | 59326-1 | 2068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP BURNT OPEN ON 954-86 - XFMRS UP TO AND INCLUDING 86 HAVE NOT BEEN OUT. OPENED FUSE ON 954-83 @ 18:39 TO MAKE REPAIRS. REPAIRS COMPLETE. CLOSED FUSE ON 954-83 @ 18:56 RESTORING ALL CUSTOMERS. SH//VER/CRB IDCC CNT20, TON1906 XXXX
6589 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-11-16 16:15 | 2017-11-17 03:44 | 3 | 689 | 4561651 | 2067 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required with yard dog water and sewer behind trailor no trucks 4 men/chg from 10 kva to a 25 kva Released by crew 078S03 Repairs made, voltage good, Ticket complete
6590 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-04-14 01:40 | 2016-04-14 08:33 | 5 | 413 | 4089771 | 2065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT// VER/ ADH
6591 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-06-12 18:20 | 2008-06-12 23:15 | 7 | 295 | 63406-1 | 2065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TREES GROWN UP AROUND XFMR POLE..FUSE BLOWN...CURRENT LIMITING FUSE BAD...D LEWIS 061208 RELEASED BY CREW 074H08 IDCC CCCF, MCCDS, CNT1 XXXX
6592 | Hazard | 3303902 | LESLIE | WOOTON | 2015-05-17 11:26 | 2015-05-17 14:18 | 12 | 172 | 4438261 | 2064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 341-28 . FOUND BAD ARRESTER ON POLE 341-45 , REPLACED ARRESTER .CLOSED FUSE ON POLE 341-28 @ 14:18/ ISO 37830341000028/ COD 12/ VER/BOW
6593 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-01-03 11:00 | 2017-01-03 11:48 | 43 | 48 | 4264411 | 2064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE FUSES ON 38830761000265 TO SAFELY REMOVE A SWITCH CUTOUT (NOT ON MAP & THEY WERE ALL REMOVED) ON POLE 38830761000082. 1100-1148 VER/AWD L3/HFP XXXHFP AJB
6594 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-03-20 09:46 | 2017-03-20 11:55 | 16 | 129 | 4571651 | 2064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LREPLACED CUTOUT//RESTORED ALL CUSTOMERS AT 11:55//COMPLETE//INE CUTOUT BROKE ON POLE 890-3//OPENED SWITCH ON POLE 866-84 TO SAFELY MAKE REPAIRS//OPENED AT 11:30//REPAIRS MADE//RESTORED ALL CUSTOMERS AT 11:55//COMPLETE//EM DUP ******* SEE H4571651 FOR SW OUTAGE = VER/HFP L3/HFP
6595 | South Williamson | 3200302 | BELFRY | TOLER | 2012-12-29 16:47 | 2012-12-29 17:35 | 43 | 48 | 4552981 | 2064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BRAD HATFILED REPORTED HOTLINE CLAMP BURNT OFF AT POLE 990-D-152. REPLACED HOT LINE CLAMP. VER/TOM L3/TOM IDC XXXX
6596 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-02-21 20:55 | 2015-02-21 21:15 | 103 | 20 | 4067761 | 2060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OPEN RECLOSER TO CLOSE LOOPS ON 450C-162 IN ORDER 4060911/// ISO 37830426D00043/ COD 103//// VER/BOW L3/HFP AJB
6597 | Pikeville | 3403001 | PIKEVILLE | CITY | 2009-04-08 07:35 | 2009-04-08 16:10 | 4 | 515 | 50401-1 | 2060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSES OUT, TRANSFER THIS TICKET TO TIM HALL HE WILL ASSIGN A CREW TO WORK THIS TOMORROW. RELEASED BY CREW 074S05// RESTORED AT 1610. VER/PDP IDC XXXX
6598 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-06-20 20:06 | 2011-06-21 01:00 | 7 | 294 | 4358701 | 2058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE OPEN POLE 212-11, POLE FIRE POLE 212-66 CREW REQD. COMP. 12:55 M.PHELPS IDCC CDC96 XXXX
6599 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-12-06 19:51 | 2010-12-07 00:45 | 7 | 294 | 63790-1 | 2058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED MAP SAYS 292-12 IN FIELD POLE NO. IS 292-131 BAD 25KVA NO TRUCKS MIGHT GET WITH BIG MATERIAL HANDLER/SEND TO JOE HEMLEPPS CREW/RIBBONS TIED AROUND MAILBOX WHERE YOU TURN ADDRESS 6960 US 60 RELEASED BY CREW 078S03//// XFMER REPLACED POWER RESTORED@ 00:45 J. HEMLEPP & CREW 078H05 //VER/GAH IDC XXXX
6600 | Whitesburg | 3309302 | VICCO | JEFF | 2014-01-08 17:11 | 2014-01-09 10:20 | 2 | 1029 | 4262251 | 2058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA NEED TO REPLACE WITH 25 KVA .MANUAL POLE OK BY BRUCE TO HOLD TILL TOMORROW MORNING OK WITH CUSTOMER ALSO RELEASED BY CREW 075H03 VER/CRB IDC XXXX
6601 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-12-05 17:06 | 2013-12-05 22:00 | 7 | 294 | 4102471 | 2058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLED LINE, SHOT LINE FUSE, IT CAME BACK OUT, CALLING FOR HELP VER/CRB L3/HFP
6602 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-07-24 20:35 | 2014-07-24 21:17 | 49 | 42 | 4285251 | 2058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKE WILL REPLACE//LINE FUSE WENT OUT WHEN CUTOUT FAILED ON TRYING IT ON TIX 4285571/// REPLACED BROKEN CUT OUT AND CLOSED LINE FUSE IN @ 21:17 //// RESTORED SERVICE VER/CRB AJB
6603 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-02-21 09:50 | 2016-02-21 14:13 | 9 | 263 | 4742101 | 2058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED 911 WITH AN ETA OF 0945//NO OUTAGE TILL RECLOSER 336-80 OPENED @ TIE WIRE BROKEN PRIMARY LAID ON POLE BURNT 2/3 THRU OPEN OCR@0950 RETIED PRIMARY AND E WIRE BROKEN PRIMARY LAID ON POLE BURNT 2/3 THRU OPEN OCR@0950 RETIED PRIMARY RELEASED BY CREW 077S01//LIFTED HOT TAP ON POLE 312-16 @ 1225 CLOSED REC @ 1230 VER/CRB
6604 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-12-22 04:00 | 2018-12-22 12:57 | 5 | 537 | 4589911 | 2057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | . 40t fuse out due to pole burnt into due to bad insulator pole 760-289. i opened hot line clamp on pole 760-90 to iso truuble. closed 40t fuse in at 10:20 should have cust back on. 1 still out on tap that is iso Released by crew 074S11//CLOSED LOOP @ 1257 L3/HFP
6605 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-12-08 15:56 | 2016-12-08 19:03 | 11 | 187 | 4178341 | 2057 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | INSTALLED POWER TEMP. TICKET COMPLETE//ENTERED AED/AWD VER/AWD
6606 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2012-06-22 15:42 | 2012-06-22 19:50 | 13 | 248 | 4947451 | 2056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE OPENED UP AT 334-B-12 POWER RESTORED TO ALL EXCEPT COUGAR LN, CUT ARRESTOR IN CLEAR ON POLE 334-140 ,2 FUSE RESTORED AT 1950 KWB COD-13 ISO LF @ 38830334B00012 VER/HFP L3/HFP IDC XXXX
6607 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-11-27 11:39 | 2019-11-27 20:13 | 4 | 514 | 4075331 | 2056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | wire down pole 139831147D30904 to 39831147D30921 bad 50kva non truck accessible line fuse open 1147-162 Released by crew 078H25,repairs made all cust restored @ 2013 please close ticket thanks.bt/ ISO 39831147D30162/ cOD 4
6608 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-06-10 07:02 | 2021-06-10 11:19 | 8 | 257 | 4702321 | 2056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lat cutout broke on pole 38831099000011// Will be making repairsLat cutout broke on pole 38831099000011//Need big bucket to replace.// Crew required Released by crew 074S11
6609 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-21 07:38 | 2008-07-21 14:29 | 5 | 411 | 55523-1 | 2055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3008701//REPLACING HOTTAP//COD 4// VER/DBM IDCC PN1, CNT4 XXXX
6610 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2022-03-24 14:05 | 2022-03-24 16:22 | 15 | 137 | 4669891 | 2055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Damaged UG secondary feeding a meter base. I have helping coming to assist with repairs.
6611 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-07-20 13:08 | 2015-07-20 15:25 | 15 | 137 | 4917341 | 2055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND LOOP BURNED INTO ON POLE 882-141//MAKING REPAIRS//REPAIRS MADE//RESTORED AT 15:25//COMPLETE//EM VER/CRB
6612 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2012-06-28 21:50 | 2012-06-29 09:15 | 3 | 685 | 4973731 | 2055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR, WILL NEED CREW TO CHANGE RELEASED BY CREW 077S12//OKD BY DUTY SUPER MIKE LEWIS TO HOLD TIL AM//* C.SEXTON WILL WORK THIS JOB TODAY.COD-3 ISO 37830356D00144 AJB
6613 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-07-14 16:29 | 2013-07-14 23:20 | 5 | 411 | 4522671 | 2055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 270-2018 LINE FUSE OPEN AND GROUNDED AND TAGGED CREW REQUIRED/NO TRUCKS/270-144 LOCATION FAULT RELEASED BY CREW 078S03 IDC XXXX
6614 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-11-09 18:20 | 2011-11-09 20:37 | 15 | 137 | 4063051 | 2055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-8388 BAD CUTOUT BURNT CROSSARM OFF POLE 45-2042 OPENED 3-50T FUSES AT 18;20 NEED 3-CUTOUT AND LA AND 8FT. CROSSARM RELEASED BY CREW 078S08/CREW LOADING MATERIAL/FETR2215/VEM ///VER/CRB IDC XXXX
6615 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2012-10-29 10:08 | 2012-10-29 11:02 | 38 | 54 | H4180461 | 2052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / "WILL CHECK AT REGULAR TIME" SDB / WILL CHECK AT REGULAR TIME FAILED CUTOUT. WILL NEED OUTAGE. CREW ENROUTE.SDB / WILL CHECK AT REGULAR TIME FAILED CUTOUT. WILL NEED OUTAGE ON POLE 37820148000049. CREW ENROUTE.// OPENED FUSE @ 1008 (38 CUST) // COD-39 ISO LF @ 37820148000049 DUPLICATING FOR 38 CUST FROM ORDER 4180461 VER/HFP L3/HFP IDCC PN143 XXXX
6616 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-11-28 22:56 | 2013-11-29 10:20 | 3 | 684 | 4086771 | 2052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE, WILL NEED 1 MAN (ASSIST ONLY). BETTER TO WAIT UNTILL MORNING SINCE 2 MANUEL POLES WILL NEED WORKED. TROUBLE ON POLE 254A-53. ONLY 1 CUST OUT // K. NAPIER WILL CALL FOR TICKET AROUND 0700 HRS. ARCOS 1 MAN AT 0700 TO ASSIST // VER/CRB L3/HFP IDC XXXX
6617 | Hazard | 3302703 | HAZARD | HAZARD | 2009-12-17 15:39 | 2009-12-17 18:30 | 12 | 171 | 54441-1 | 2052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POSSIBLE BAD TRANSFORMER AND ARM BURNT IN HALF POWER RESTORED AT 1830 COD-12 VER/HFP L3/HFP
6618 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2016-07-27 17:24 | 2016-07-27 18:00 | 57 | 36 | 4692561 | 2052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I BELIEVE CUTOUT GOING BAD ON RIGHT NOW VER/CRB AJB
6619 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-09-08 16:35 | 2010-09-08 17:00 | 82 | 25 | H64658-1 | 2050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "B" PHASE ON RECLOSER OPEN PHASES ROLL ON OUT THE LINE CALLING IT COD-83/OPENED 2ND RECLOSER AT 1635 TO MAKE REPAIR ON CLAMPI REPLACED A HOT LINE CLAMP THAT HAD FAILED. VER/KEP L3/KEP IDC XXXX
6620 | Pikeville | 3414501 | CONSOLIDATE COAL | COAL COMPANY | 2008-06-29 00:14 | 2008-06-29 04:30 | 8 | 256 | 58871-1 | 2048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REMOVED RISER FROM BYPASS SWITCH, AND INSTALLED TEMPORARY JUMPER WIRE BURNED LOOSE FROM TOP OF BYPASS SWITCH AT POLE 88-196, NEED 2 MAN CREW , 2/0 COPPER WIRE AND BYPASS SWITCH / GXJ... OPENED, ISOLATED AND TAGGED OCR ON POLE 88-194 AT 00:25, 06-29-08 GXJ RELEASED BY CREW 074S03 IDC XXXX
6621 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-04-21 05:39 | 2010-04-21 11:20 | 6 | 341 | 65820-1 | 2046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34766312//CREW ENROUTE RELEASED BY CREW 074S02----REPLACED CUTOUT ALSO REPLACED XFMR--074H14//VER/CRB//MADE A MD IDCC CNT1 XXXX
6622 | Pikeville | 3421001 | BREAKS | CITY | 2014-02-24 08:51 | 2014-02-24 10:04 | 28 | 73 | 4429841 | 2044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074S02 CLOSED @ 1004// BUSTED HOT TAO - CLOSED IN @ 1004// VER/TOMN L3/TOM
6623 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-04-01 02:30 | 2016-04-01 19:32 | 2 | 1022 | 4013401 | 2044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 37830150000039 HAS TRANSFORMER THAT SERV LIGHTS ON STEEL TOWER ON HIGHT LINE, LID BLOWN OFF AND BURNING OIL IN CAN , TRANSFORMER NOT ON MAP BUT HAS OPEN SEC TO TOWER, ALSO GOT 35 FOOT POLE BURNED./RESTORED 1932 ALL CUSTOMERS RESTORED. VER/AWD//L3/TAR
6624 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-11-10 14:45 | 2020-11-10 16:10 | 24 | 85 | 4657781 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 1147- 5195 40t needs added to fieldview
6625 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-06-19 18:34 | 2015-06-20 01:22 | 5 | 408 | 4613451 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-6079 BAD 50KVA TRANS NEED BAG 1/0 SERVICE DOWN 1/0 LASE CABLE DOWN TRUCK TO POLE NEED LINE CREW MIT BRING TREE CREW RELEASED BY CREW 078S08///REPAIRED SEC AND SERV///REPLACED XFMR///TBL TKT COMP///BACK ON @ 01:22///RMV//COD 5// VER/DBM
6626 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-01-29 19:14 | 2008-01-29 20:22 | 30 | 68 | 60784-1 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311401// RECLOSER ON STEPDOWN IS OPEN. PATROLLING LINE. FOUND BAD CUTOUT ON POLE 328-300//COD 30// VER/DBM IDC XXXX
6627 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2022-10-30 16:07 | 2022-10-30 17:15 | 30 | 68 | 4079011 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hotline clamp burnt up had to replace
6628 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-12-25 11:40 | 2015-12-25 17:20 | 6 | 340 | 4558761 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT ON POLE 1061D-179 , BAD 50 KVA XFMR , WILL NEED LINE CREW & 50 KVA XFMR . 19.9V . MANUEL.// VER/ ADH
6629 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-10-01 10:29 | 2020-10-01 18:59 | 4 | 510 | 4517351 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Fuse is open on 453-97. Tie wire broken and primary is off the insulator @ 453-247. No tags or ground placed. Linecrew required. Please send copy to forestry this tap needs cutout bad.SENT TO R/W ////arivved RM repairs made line fuse in @18:59 please close tic RM
6630 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-10-20 20:00 | 2011-10-21 04:30 | 4 | 510 | H4005171 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE BROKE IN FIELD NEED TECH AND LINE CREW POLE 269-C-214 BROKE,MAP SHOWS 35-6 ,WILL HAVE TO OPEN UP LINE AT POLE 269-C-163 TALK TO ALL CUST RELEASED BY CREW 078S09 IDCC DUP TO OPEN FUSE XXXX
6631 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-10-27 14:50 | 2009-10-27 15:50 | 34 | 60 | H56903-1 | 2040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE FUSE OPEN AT POLE 1098-284, A & C PHASES OK, DE-ENERGIZED TAP FROM POLE 38831098C00384 TO POLE 495, NO CUSTOMERS ON 495 ... WILL NEED TO REPLACE CUTOUTS AT POLE 284 ... OPENED A & C PHASES AT 14:50 AND CLOSED ALL PHASES AT 15:50 ... ALL WORK COMPLETE / GXJ VER/KEP L3/KEP IDC XXXX
6632 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-01-30 06:01 | 2011-01-30 14:30 | 4 | 509 | 52196-1 | 2036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 37830295D00044 -- PATROLLING LINE --- FUSED LINE AT08:20, CAME BACK OUT- NOTIFIED DUTY SUPERVISOR, HELP TO PATROL LINE IS ENROUTE.//CHANGED INSULATOR 295-82LINE FUSE OUT ON POLE 37830295D00044 -- PATROLLING LINE --- FUSED LINE AT08:20, CAME BACK OUT- NOTIFIED DUTY SUPERVISOR, HELP TO PATROL LINE IS ENROUTE. BAD INSULATOR ON POLE 37830295D00046 //BAD ARRESTOR ON 295-208 //VER/CRB IDC DCMT XXXX
6633 | Hazard | 3303902 | LESLIE | WOOTON | 2008-08-27 12:31 | 2008-08-27 21:00 | 4 | 509 | 56225-1 | 2036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3303902//BAD 7.2 PIN INSULATOR ON POLE# 488-27/// ALSO CLEAR UP POLE GROUNDS THAT GOT PULLED OVER CLOSE TO TRANSFORMERS DUE TO COPPER THEIVES STEALING POLE GROUNDS.//REPLACED ARRESTOR ON POLE #487-144//VER/CRB IDC XXXX
6634 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-03-03 01:30 | 2010-03-03 03:23 | 18 | 113 | 62404-1 | 2034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ASSCIOATED WITH ORDER 62401-1 CREW OPENED LFS ON POLE 50-29 TO MAKE REPAIRS ***CUTOUT BROKE DOWN AND CAUGHT POLE 50-76 ON FIRE. I OPENED TRANS. AND LIFTED HOTTAP AT 00:25. WE WILL HAVE TO OPEN ALL 3 LINE FUSES ON POLE 50-29 WHEN CREW GETS HERE TO LOWER CROSSARM AND NEW CUTOUT. THERE IS JUST 1 CUST. OUT FOR NOW. VER/PDP IDC XXXX
6635 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-08-06 06:47 | 2011-08-06 10:33 | 9 | 226 | 4670611 | 2034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR PL. # 236-107 MAKING REPAIRS/ J. HEMLEPP/ REPLACED C/O & L/A POWER RESTORED @ 10:33//VER/CRB IDC XXXX
6636 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2020-01-13 01:40 | 2020-01-13 18:37 | 2 | 1017 | 4295251 | 2034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Slemp/Defeated cr. breaker out waiting on side by side to patrol line bad cutout on 538C/207
6637 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-02-17 17:15 | 2022-02-18 10:10 | 2 | 1015 | 4494861 | 2030 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | talked to cust said we need to wait until tomorrow they would be able to help us get to pole Released by crew 077S07. Loose connections at transformer, repaired.
6638 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-11-11 01:32 | 2018-11-11 08:18 | 5 | 406 | 4388261 | 2030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | /Fuse link appears to have broke. Restored @ 8:18. sh L3/HFP
6639 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-05-13 20:00 | 2014-05-14 02:20 | 7 | 380 | 4693721 | 2030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SAMMONS & LEWIS & MCKINNEY & MCCOWN // MATERIAL: 40/ 4 POLE, 10KVA 120/240 7.2KV TRANSFORMER, CUTOUT, ARRESTER . TRUCK ACCESSMATERIAL: . TRUCK ACCESS . OPENED POLE 259-29 AT 20:00 , INSTALLED SOLID SWITCH AT POLE 259-30 OPENED AND TAGGED FOR G. JUSTICE, CLOSED 259-20 AT 21:05 ENERGIZING TO POLE 259-46, INSTALLED SOLI //VER/GAH IDC XXXX
6640 | Pikeville | 3421002 | BREAKS | GRASSY | 2011-04-12 15:27 | 2011-04-12 18:50 | 10 | 203 | 55937-1 | 2030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 39541783 // RECLOSER ON POLE 197-98 IS OPENED. WITH BACK TO STATION THE LEFT HAND RECLOSER IS OUT. THE OTHER 2 IS IN. INSULATOR ON POLE 197-17 LOOKS LIKE IT HAS BROKEN DOWN AND POLE AND CROSSARM IS SMOKING AT TIMES. DENNIS IS BRINGING HELP TO CHANGE INSULATORS. WE WILL HAVE TO OPEN RECLOSERS AT POLE 197-98 WHEN CREW ARRIVES FOR ABOUT 45 MINUTES. I OPENED THE OTHER 2 RECLOSERS AT 18:25 SO WORK COULD BE DONE. WE FIXED PROBLEM AND CLOSED ALL 3 RECLOSERS IN AT 1850 SEE H55937-1 VER/HFP L3/HFP
6641 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-07-12 08:31 | 2011-07-13 18:20 | 1 | 2029 | 4526981 | 2029 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKEN AND HANGING IN THE CLEAR ON POLE 37830042C00066 RELEASED BY CREW 074M01 COD-1 ISO TF 37830042C00448 VER/HFP L3/HFP IDC XXXX
6642 | Hazard | 3302704 | HAZARD | KENMONT | 2012-09-18 02:18 | 2012-09-18 10:45 | 4 | 507 | 4056731 | 2028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM . BAD CUTOUT (MANUEL) 19.9 POLE HAS 2 CUTOUTS ON IT MAY WANT TO CHANGE BOTH , WILL TAKE CREW. POLE IS BEHIND SERVICE PUMP AT JEFF. RELEASED BY CREW 075H04 REPLACED CUTOUTS AND RESTORED POWER AT 1045 COD-4 ISO TF 37830321D00348 VER/HFP L3/HFP IDC XXXX
6643 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-07-06 15:44 | 2022-07-06 21:22 | 6 | 338 | 4400881 | 2028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke line fuse crew requird big buckett Released by crew 078S03
6644 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2008-01-29 17:16 | 2008-01-29 18:34 | 26 | 78 | 60763-1 | 2028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3311401//LINE FUSE BLOWN ON POLE 328-55. PATROLLING LINE. WE PUT A 65T FUSE IN THIS CUTOUT. THIS WAS INSTALLED AS AN ISOLATING POINT ONLY. FOUND BAD LTNG ARRESTER ON POLE 328-129// SENT REPORT TO MAPPING ON MISSING FUSE DBM// COD 26//ISO 37830328C00055// VER/DBM IDC XXXX
6645 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-03-07 20:56 | 2008-03-07 23:45 | 12 | 169 | 54770-1 | 2028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802//FOUND POLE BURNED IN TWO,WILL CLEAR IT UP POLE 28-158 ,IS A DEAD-END POLE THAT DOESNT SERVE ANYTHING.CUT WIRE GOING TO THIS POLE IN CLEAR AT POLE 28-114,THEN CLOSED FUSE AND RESTORED POWER TO ALL VER/LDA IDC CHANGED CNT FROM 6 XXXX
6646 | Whitesburg | 3312902 | JENKINS | JENKINS | 2013-11-02 12:23 | 2013-11-02 13:08 | 45 | 45 | 4003751 | 2025 | DISTRIBUTION STATION | EQUIPMENT FAILURE | SWITCH, OH | CB B LINE DISC FAILED OUTAGE TO REPLACE VER/KEP L3/HFP
6647 | Hazard | 3311103 | STINNETT | WENDOVER | 2013-11-23 07:33 | 2013-11-23 11:18 | 9 | 225 | 4066851 | 2025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CALL SEVICE AFTER DAYLIGHT.//BAD CUTOUT ON 461-110. VER/CRB L3/HFP
6648 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2010-04-02 18:30 | 2010-04-03 01:15 | 5 | 405 | 57693-1 | 2025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3P XFR BANK BLEW UP,XFRS/POLE ON FIRE.FIRE DEPT ON SITE TO HOPEFULLY EXTINGUISH FIRE.AFTER OUT,WILL ISOLATE BANK AND RE-ENERGIZE LINE.ISOLATED BANK,CLOSED BACK BY DDC/SCADA.PROBLEM ON 67-83 RELEASED BY CREW 074S06//CREW WORKING ON TRBL, SHOULD COMPLETE BY ER TIME. //VER/GAH IDC XXXX
6649 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-07-29 18:44 | 2011-07-29 22:57 | 8 | 253 | 4639681 | 2024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED---BAD 25KVA NEEDS REPLACED WITH A 50KVA RELEASED BY CREW 078S07/CREW ON SITE/XFMR ENROUTE/VEM/XFMR CHANGED AND POWER RESTORED TO ALL CUST 2257/PLEASE CLOSE TICKET/THANKS/VEM/VER/CRB IDC XXXX
6650 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-12-28 13:47 | 2014-12-28 15:15 | 23 | 88 | 4888281 | 2024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESTORED 40T @ 15:15 BAD CUTOUT ON POLE 38830020C24542 VER/CRB AJBC CDC92
6651 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-12-17 14:57 | 2015-12-18 13:50 | 8 | 1373 | 4540381 | 2024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | @ 1554 PATROLLING CKTLOW SIDE FUSE BLOWN ON STEP-DOWN POLE 37830310A20181..WILL PATROL../// OPENED LINE FUSE ON POLE 310-86 AND TAGGED TO DDC AND CLOSED LOAD SIDE BACK AND STAYED.TALKED TO TIM HALL AND SAID WILL WORK IN THE A.M. WILL NEED PUG..FEEDS OIL WELL. // DDC HOLD TAGS PLACED//0936 GAVE TIM MCCOY PERMISSION TO REMOVE KYDDC TAGS AND REPLACE WITH HIS //BAD INSULATOR ON POLE 37830310000116// VER/CRB
6652 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-01-16 06:08 | 2009-01-16 11:45 | 6 | 337 | 55520-1 | 2022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP XFMR OUTAGE ONLY AT POLE 37830272A40392 WITH 6 CUSTOMERS FED FROM THIS XFMR NEED A NOTE SENT TO TECH TO CHECK LOAD ON EXISTING 25 KVA COD- 6 PER SERVICER.. ENTERED 2 MD`S AND ADJUSTED CUSTOMER COUNT..SENT EMAIL TO DOUG CHRISTIAN...HFP//3300601 RESTORED AT 1145 COD-6 PER SERVICER L3/HFP
6653 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-02-13 01:39 | 2014-02-13 18:30 | 2 | 1011 | 4377731 | 2022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER WILL CHECK ONCE THE ROAD CONDITIONS IMPROVE//, LINE FUSE BLOWN, GATE BURNED UP, BAD CUTOUT ON POLE 180, REPLACED. POWER RESTORED VER/KEP
6654 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2008-10-16 21:33 | 2008-10-17 04:58 | 15 | 445 | 56367-1 | 2021 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 26827897 ///CREW REQUIRED BURNT OFF POLE/40/5/ISOLATED ON 270-57 2 CUSTOMER WILL BE OFF/270-16 CLOSE IN AT 2300 HRS 2 CUSTOMERS STILL OFF RELEASED BY CREW 078S03/// LAST 2 CUSTOMERS ON @ 04:58 VER/ARN IDC XXXX
6655 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-09-22 10:36 | 2018-09-22 11:30 | 38 | 54 | 4140871 | 2018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | / riser burnt out of cutout on source side and welded shut on load side/ ISO 39831148A00131/ COD 37/ Had to open xfmr 39831148A00131/ ISO 39831148A00131/ cOD 1 1110 - 1130 L3/HFP
6656 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-07-09 08:36 | 2012-07-09 12:12 | 18 | 216 | 4636671 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 876-2 LINE FUSE BLOWN..TOP OF POLE 876-311 BURNED OFF DUE TO BAD CUTOUT..ISOLATED ON P-876-298 RELEASED BY CREW 076S01// CLOSED CUTOUT IN AT 10:15 ON 876-2, REPLACING POLE TOP NOW TCM// ONLY TWO CUSTOMERS OUT AFTER ISOLATION ON POLE 876-298, AND FUSE BACK IN ON 876-2, RELEASED BY CREW 076H01//COD 22 IDC CHANGED TIME OFF FROM 0701 FIRST CALL WAS FULL POWER, ALSO LOOKS LIKE PHASE B ONLY CHANGED COUNT FROM 22 XXXX
6657 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-01-07 17:16 | 2015-01-07 21:00 | 9 | 224 | 4914401 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 227-65 FUSE STILL IN, GOING UP TO WERE WE HAVE WIRE DOWN////// PRIMARY DOWN AT POLE 37830227D00087//, 6ACU, BUCKET ACCESSABLE. LIFTED CLAMP ON POLE37830227D00087//, CREW MAY WANT TO OPEN FUSE ON POLE 227-65 ON THEIR WAY UP HERE. CREW REQUIRED. RDS SLICK UP HOLLOW! RELEASED BY CREW 077S08//SLEEVE FAILED PER JEFF COMBS VER/CRB L3/HFP XXX AJB CUST R BEHIND TEMP PT.
6658 | Whitesburg | 3401301 | FLEMING | NEON | 2008-07-24 12:03 | 2008-07-24 16:15 | 8 | 252 | 59816-1 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401301// WILL NEED A CREW AND MATERIAL HANDLER AND A 50 KVA RELEASED BY CREW 074S07//VER/CRB IDC XXXX
6659 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2021-07-21 19:24 | 2021-07-21 21:00 | 21 | 96 | 4943891 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | had one leg of the open wire secondary broke at pole 1111-31 to 111..i opened the line fuse on pole 1111B-32 at 20:30 to make repairs and got it back in at 21:00
6660 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2022-02-17 23:37 | 2022-02-18 10:49 | 3 | 672 | 4500281 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25 kva trucks ok Released by crew 078S03,repairs made all cust restored @ 1049 please close ticket thanks.bt
6661 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-10-28 08:45 | 2015-10-28 12:29 | 9 | 224 | 4385811 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON POLE 134-35 AT 08:45, POLE 134-83 IS BURNT OFF. CAN LOWER EVERTHING, TIM SMITH CREW COMING TO MAKE REPAIRS. ALL POWER RESTORED//3420002// VER/ ADH L3/HFP XXXHFP
6662 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-01-31 11:09 | 2011-01-31 16:45 | 6 | 336 | 52480-1 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, COURTHOUSE GOING TO CLOSE, CREW ON WAY STS 38632426. ACTUAL POLE # IS 181/6.//COD 6//ISO// VER/DBM IDC XXXX
6663 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-09-21 08:04 | 2011-09-21 08:52 | 42 | 48 | 4891671 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER BURNT OFF AT RECLOSER COD-42 "C" PHASE ONLY RISER BURNT OFF AT RECLOSER COD-42 C PHASE ONLY . RESTORED C PHASE AT 08:52 , ALL WORK COMPLETE / GXJ VER/KEP IDC XXXX
6664 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2022-06-02 20:06 | 2022-06-02 21:30 | 24 | 84 | 4008101 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broke. Restored @ 21:30. sh
6665 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-01-29 15:17 | 2011-01-29 20:05 | 7 | 288 | 52036-1 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEND TO LINKOUS RELEASED BY CREW 078S07//WR#38621859 ALL POWER RESTORED AT 20:05//VER/CRB IDC XXXX
6666 | Pikeville | 3408103 | SALISBURY | MARTIN | 2017-02-06 19:51 | 2017-02-06 21:03 | 28 | 72 | 4362521 | 2016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | (A) PHASE FUSE OPENED ON 38831098D00111 (COD 6) WHEN FUSE WAS ATTEMPTED TO BE CLOSED ON 38831098D00172. RELATED TO ORDER 4362281. OPENED ABOUT 1951. FAULT 38831099000084. RESTORED 2103. VER/AWD /// BUS OBJECTS INDICATES `A` PHASE OUTAGE = L3/HFP HFPC CNT34 AJB
6667 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-08-23 13:15 | 2017-08-23 14:20 | 31 | 65 | 4293251 | 2015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO SAFELY REPLACE BROKEN CUTOUT.TIME OFF WAS 13:15, TIME ON WAS 14:20,, VER/KEP SJG
6668 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2021-04-14 07:49 | 2021-04-14 10:52 | 11 | 183 | 4449801 | 2013 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | crew reqd. behind applebees/broke cutout, all 3 needs changed truck ok. Released by crew 078S04///complete///back in @ 10:52///BR
6669 | Whitesburg | 3314401 | MAYKING | ERMINE | 2016-10-21 10:09 | 2016-10-21 13:30 | 10 | 201 | 4037621 | 2010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 497-181, BAD CUTOUT ON POLE 473-156 BURNT POLE OFF, ISOLATED & GROUNDED & TAG ON POLE 497-181..MADE REPAIRS RESTORED POWER AT 13:30../ ISO 37830497C10181/ COD 10/ 15T ON POLE 497-181 MD DONE/ VER/BOW L3/HFP XXXHFP
6670 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-07-03 11:25 | 2012-07-03 17:00 | 6 | 335 | 4265221 | 2010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | OK //VER/GAH
6671 | Pikeville | 3402002 | KEYSER | STONECOAL | 2013-10-26 07:59 | 2013-10-26 11:20 | 10 | 201 | 4964251 | 2010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE PULLED OUT OF SLEEVE AT POLE 38821129B00101 /// NEED 3 MEN #4 SOLID CU & SLEEVES AND BIG BUCKET MASSEY, MCKINNEY & MCCOWN //VER/GAH L3/HFP IDC XXXX
6672 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-04-28 19:15 | 2016-04-28 23:26 | 8 | 251 | 4139831 | 2008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 1014A23 I CAN REPLACE CUTOUT RESTORED POWER AT 23:26/ ISO 38821014A00023/ COD 8/ VER/BOW
6673 | Hazard | 3303901 | LESLIE | HYDEN | 2021-09-03 01:06 | 2021-09-03 04:33 | 12 | 207 | 4204971 | 2007 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | defective cutout on pole 37830291C20208/ opened recl de-energized on pole 37830291C20207/ had to open line fuse one pole 37830291000127 at 0330/ closed line fuse 37830291000127 0418/ closed recl 0433
6674 | Paintsville | 3401802 | INDEX | HOSPITAL | 2015-01-20 12:14 | 2015-01-20 18:55 | 5 | 401 | 4946911 | 2005 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, UG | BAD CONNECTION ON U/G SEC.350.NEED WIRE /PRESS/.TOOK XFMR OFF AT 17.08..BACK ON AT 18.55..HAD TO REMOVE 1 SEC OF CONDUIT..CHG SPLICES INSIDE CONDUIT..2 SPLICES WERE BAD.REPLACED CONDUIT../ ISO 38830654B00408/ COD 12/// PER B BOWERSOCK CUST FROM PED 433 INITALLY HAD PART POWER (5 CUST) & 7 CUST INTERRUPTED WHEN TR OPENED // SEE DUP H4946911 FOR TR OUTAGE OF 7 CUST // VER/HFP L3/HFP
6675 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-08-19 12:06 | 2011-08-19 14:40 | 13 | 154 | 4730741 | 2002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | BROKE GUY WIRE ON PRIMARY--NEED TO REPLACE GUY COD-13 ISO LF 37830155000118 VER/HFP L3/HFP IDC CHANGED CAUSE FROM FOREIGHN OBJECT XXXX
6676 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2011-01-01 05:14 | 2011-01-01 10:00 | 7 | 286 | 57482-1 | 2002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38258393 // BAD CUTOUT ON 37830419B00289 == CALLED FOR BIG BUCKET AND 1 MAN AND FLAGGERSBAD CUTOUT ON 37830419B00289 == CALLED FOR BIG BUCKET AND 1 MAN AND FLAGGERS == CHANGED CUTOUT == POWER OK BAD CUTOUT TOOK LINE FUSE OUT TOO == COD-7 ISO LF 37830419B00289 VER/HFP L3/HFP IDC DCMT XXXX
6677 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-12-13 09:08 | 2017-12-13 10:17 | 29 | 69 | 4645141 | 2001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Line fuse out @47-D-31, checking. Fuse melted out closed back in @ 1017.
6678 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-06-24 06:41 | 2011-06-24 17:48 | 3 | 667 | 4407241 | 2001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WIRE LOOSE FROM INSULATOR AND LAYING ON CROSSARM RELEASED BY CREW 074S03///CREWS IN PROCESS OF SWITCHING LOAD TO MINIMIZE OUTAGE TO MAKE REPAIRS. WILL NEED AT LEAST 2 HR OUTAGE.//COD 3// VER/DBM IDC XXXX
6679 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2013-09-11 15:40 | 2013-09-11 17:45 | 16 | 125 | 4838931 | 2000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF AT RECLOSER REPAIRED TIME ON 17:45 COD-16 ISO OCR 38830114000251 VER/HFP L3/HFP IDC XXXX
6680 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-09-26 19:00 | 2009-09-26 19:25 | 80 | 25 | H64242-1 | 2000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED FUSE POLE#1123-166 COD-26 TO ISOLATE BURNING POLE OPENED RECLOSER AT 1900 TO MAKE REPAIRS RESTORED ALL POWER AT 1925 CALL ON ORDER 64152 MADE DUP VER/KEP L3/KEP IDCC CCERF XXXX
6681 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-09-20 13:08 | 2009-09-20 14:28 | 25 | 80 | 55423-1 | 2000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP RELATED TO ORDER 55251-1 CREW OPENED SWITCHES ON POLE 46-1075 TO ISOLATE INSULATOR THAT IS BREAKING DOWN AND CAUSING FLICKERING LIGHTS FROM CB OPERATIONS. L3/HFP IDC XXXX
6682 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2015-02-20 09:22 | 2015-02-20 20:28 | 3 | 666 | 4053801 | 1998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KV CSP XFMR BURNT UP, NEEDS CHANGED/ MANUAL, 12KV. // OPENED RECL 63 CUST @ _1752___ TO FIX BROKEN INSULATOR // CLOSED @ __2010______ XFMR 3 CUST BACK ON @ 2028 SEE H4053801 FOR RECL OUTAGE - VER/HFP L3/HFP
6683 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2009-03-11 10:20 | 2009-03-11 14:02 | 9 | 222 | 57185-1 | 1998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-9 WR # 28881416 // 45` 4 POLE BURNT INTO CAN GET TRUCK TO IT NEED FLAGGERS L3/HFP IDC XXXX
6684 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-03-07 00:09 | 2008-03-07 04:54 | 7 | 285 | 54445-1 | 1995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3000102// 600 AMP LINE SW BURNING - TOOK OUTAGE IN ORDER TO REPLACE SWITCH // COD-7 VER/LDA IDC XXXX
6685 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2015-03-20 04:23 | 2015-03-20 12:48 | 5 | 505 | 4211891 | 1993 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF///////869-226////40CLASS 5,XFR APPEARS OK,MAY BE ABLE TO TRANSFER EVERYTHING//////FUSE BLOWN AT 869-204 RELEASED BY CREW 074S06.. REPLACED POLE AND ALL HARDWARE. /// VER/HFP L3/HFP
6686 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-03-14 20:47 | 2009-03-15 01:17 | 15 | 270 | 58634-1 | 1993 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD-15 // PATROLING LINE-- BAD CUTOUT BURNT OFF TOP OF POLE -- CALLING CREW/// LIFTED HOTTAP ON POLE 38830092B00094---INSTALLED TAG AN GROUND--CLOSED LINE FUSE IN AT 20:10 COD-11// WR#28926727 // REPLACED POLE AND RESTORED LAST 4 CUSTOMERS AT 0117// VER/LDA IDC XXXX
6687 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-07-15 05:38 | 2014-07-15 11:10 | 6 | 332 | 4246611 | 1992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 37830154000012, PATROLLING LINE. BAD ARRESTER ON POLE 37830154000144, REPLACED ARRESTER. POWER RESTORED.COD 6// VER/ADH AJB LF 37830154000012, DOES NOT SHOW TO FEED XFR 37830154000131. LCD 37830154000131
6688 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2010-05-23 09:21 | 2010-05-23 13:30 | 8 | 249 | 66470-1 | 1992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 35237286 // BAD TRANSFORMER RISER BURNT INTO--CALLING CREW RELEASED BY CREW 078S07----------------------POWER OFF @ 12:45 ON @ 13:30 COD-8 VER/HFP L3/HFP IDCC TOF1245, PN129 XXXX
6689 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-08-01 16:44 | 2012-08-01 19:45 | 11 | 181 | 4879441 | 1991 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 38831149000061 ALSO XFMR FUSE BLOWN ON POLE 38831149000223 FOUND CRACKED CUTOUT OUT ON POLE 38831149000223, GOING TO REPLACE ALL POWER RESTORED @ 19:45 COD-11 ISO LF 38831149000061 VER/HFP L3/HFP IDC XXXX
6690 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-08-17 14:01 | 2011-08-17 20:39 | 5 | 398 | 4720961 | 1990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRYED LINE FUSE IT CAME OUT HARD. NEED LINE CREW. // COD 5 ///BAD LA POLE#164-219/DIFF LOCATION/FETR 2030/VEM/BAD CUTOUT ALSO/FETR2045/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2039/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
6691 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2021-06-08 12:54 | 2021-06-08 16:13 | 10 | 199 | 4688711 | 1990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF on 999-4 open/ patrolling line/ broke cut out on 999-4/ making repairs/repairs made LF in @ 1613/ Please close ticket/ MLH
6692 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-05-14 22:36 | 2013-05-15 09:39 | 3 | 663 | 4114791 | 1989 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XMF FUSE OUT. BAD 25KVA. 7200, TRUCK OK. LINECREW REQUIRED RELEASED BY CREW 078S11//PER AFTER HOURS CREW CALLOUT GUIDELINES, HOLDING ORDER FOR CREW TO REPAIR DURING REGULAR WORK HOURS// IDC XXXX
6693 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2016-07-29 17:19 | 2016-07-29 18:10 | 39 | 51 | 4709891 | 1989 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | POLE 38830021B30057 65T LINE FUSE MELTED OUT CUTOUTS NEEDS CHGED SEND NOTE TO RAYBURN CUTOUTS NEED CHGED AND LARGER FUSE INSTALLED/ ISO 38830021B30057/ COD 39/ VER/BOW AJB
6694 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-11-19 06:55 | 2014-11-19 10:36 | 9 | 221 | 4744531 | 1989 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP,CLOSE CLEARANCES.NEED CREW W COVER-UP AND CUTOUT////////CREW REPLACED CUTOUT,CLOSED AND RESTORED///////SEND TO TECH,POLE IS ROTTEN HERE 37830024A30970 VER/CRB L3/HFP
6695 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-10-09 07:17 | 2015-10-09 11:15 | 17 | 238 | 4330411 | 1988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT ON POLE 375-34, BAD CSP XFMR ON POLE 375-110.ISOLATED XFMR , CLOSED LINE FUSE IN AT 08:48.. RELEASED BY CREW 077S11 POWER RESTORED AT 11:15/ ISO 37830375B00034/ COD 17/ VER/BOW L3/HFP XXXHFP
6696 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2018-06-05 04:16 | 2018-06-05 09:00 | 7 | 284 | 4556641 | 1988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines.// Fuse did break
6697 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-04-16 11:54 | 2013-04-16 13:05 | 28 | 71 | 4013251 | 1988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLNG LINE--BROKEN FUSE-- /// A PHASE 28 CUSTOMERS ISO LF 39831123D37060 VER/HFP L3/HFP IDC CALLS ON BOTH PHASE MORE ON C BUT THE NUMBER OF CALLS LEADS TO SMALLER LOADED PHASE LEFT COUNT AS IS XXXX
6698 | South Williamson | 3411401 | DEWEY | INEZ | 2017-12-23 01:17 | 2017-12-23 03:49 | 14 | 152 | 4665231 | 1987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout changed, power on
6699 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-01-17 18:57 | 2019-01-18 11:30 | 2 | 993 | 4683261 | 1986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 37830249A00014,manual,72kv,line fuse up on hillside,need path cut//MADE MD TO SHOW MIS-MAPPED CUST//broke cutout on pole 37830249A00014,manual,72kv,line fuse up on hillside,need path cut,hold till morning per Hold till morning per duty PHIL HICKS//COULD NOT MAKE OPS UNABLE TO CONTACT CUSTOMERS// power restored at 11:30
6700 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2014-07-14 02:15 | 2014-07-14 10:31 | 4 | 496 | 4237191 | 1984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT @ POLE 207A-203 NEED LINE CREW TO REPLACE RELEASED BY CREW 078S05/CREW ON SITE/LIFTING HT ON 207-196 TO CHG CUTOUT/FETR1130/VEM/REPAIRS MADE AND ALL CUST RESTORED 1031/PLEASE CLOSE TICKET/THANKS/VEM
6701 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-05-12 20:20 | 2011-05-13 00:28 | 8 | 248 | 4079141 | 1984 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BURNT NEUTRALS UP ON THE SECONDARY SIDE//COD 8// VER/DBM
6702 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-04-15 10:35 | 2013-04-15 11:06 | 64 | 31 | 4010031 | 1984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED REC TO SAFELY MAKE REPAIRS ON PO#4008981 VER/KEP IDC XXXX
6703 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-02-05 02:39 | 2018-02-05 06:53 | 20 | 254 | 4805161 | 1983 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30t lf @ 91-384 open, pole fire # 91-2002, loop cut & ground @ 91-412. lf restored @ 04:10 Released by crew 078S07/crew on site/room to lower/FETR 0730/vem/repairs complete and power restored to all cust 0653/please close ticket/thanks/vem 38830091D00384
6704 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-25 15:00 | 2009-06-25 19:43 | 7 | 283 | 59653-1 | 1981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP THERE ARE 3 LINE FUSES ON POLE 1148-24. ONLY THE CENTER PHASE FUSE IS BLOWN. I AM PATROLLING LINE NOW. LIGHTENING ARRESTER BLEW ON POLE 1148-62 AND TOOK OUT LINE FUSE. I CLEARED ARRESTER AND CLOSED LINE FUSE IN AT 19:43. THERE WAS ONLY 2 CUSTOMERS OUT. ENTERED MD L3/HFP
6705 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-02-05 17:12 | 2010-02-05 21:55 | 7 | 283 | 64627-1 | 1981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | POLE LEANING 10 FT. WILL BE DROPPING STA. OUT FOR 30 MIN. (OPENED IN NEW ORDER) OR LESS NEED TO SEND COPY TO RON RYE FOR TECH. COME OUT AND DO JOB FOR NEW ANCHOR. WE HAD 2 PRI. COND. DOWN AND A NEUT. DOWN ALL CUST. ON AT 21:55//COD 7// VER/DBM IDC XXXX
6706 | South Williamson | 3411401 | DEWEY | INEZ | 2010-04-21 01:50 | 2010-04-21 04:50 | 11 | 180 | 65800-1 | 1980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLED LINE - WHAT I COULD SEE OF IT LOOKED OK. WILL TRY LINE FUSE. FUSE CAME BACK OUT. FOUND BAD ARRESTER ON 720-85. ISOLATING. ARRESTER ISOLATED. RESTORED @ 4:50. SH VER/KEP L3/KEP IDC XXXX
6707 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-04-28 03:24 | 2016-04-28 10:00 | 5 | 396 | 4135791 | 1980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME 4-28-16 BROKE 19.9 KV CUTOUT// VER/ ADH
6708 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-08-15 00:38 | 2008-08-15 11:38 | 3 | 660 | 52143-1 | 1980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3404302//, FIRST POLE UP HILL FROM FUSE POLE BURNT OFF AT TOP, POLE#1013-A-248/CREW TO MAKE REPAIRS IN THE MORNING ON THE 8-15-08 DUE TO BAD LOCATION // VER/TOM IDC XXXX
6709 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2017-09-04 12:30 | 2017-09-04 15:15 | 12 | 165 | 4328591 | 1980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BAD,, 954-589 CHANGING 38830954A30589 VER/AWD
6710 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-05-15 07:39 | 2019-05-15 09:05 | 23 | 86 | 4270861 | 1978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER BACK AND SHE REPORTED APT BUILDING OUT,,cut out burnt up
6711 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-12-26 09:29 | 2010-12-26 10:55 | 23 | 86 | 55775-1 | 1978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKEN ... COLD LOAD PEAKED AT 23.2 AMP THEN DROPPED TO 17, ALL WORK COMPLETE / GXJ// EMAILED TO ENGINEERING TO GET PROPER FUSE SIZE FOR MAP DISCREPANCY // COD 23// VER/DBM IDC XXXX
6712 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-04-07 00:31 | 2017-04-07 10:50 | 8 | 619 | 4625591 | 1977 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KY DDC TAGS///TR 900-230 WAS NEVER OPEN///TOP OF POLE BURNED OFF ON 900-254.LINE FUSE BLOWN ON 900-170.ISOLATED TAGGED AND GRD ON 900-170 FOT THE DDC..LINE FUSE 38830900000170 BACK IN AT 345 (7 CUST).. RELEASED BY CREW 076S01/ CREW ON SITE REPAIRING POLE NOW TCM/ HOT TAP 38830900000210 BACK ON @ 1050 (1 CUST)/ VER/BOW L3/HFP XXXHFP
6713 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-08-08 18:23 | 2009-08-08 22:30 | 8 | 247 | 64428-1 | 1976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER BAD NEED TWO MEN AND A BUCKET TRUCK REPLACED TRANSFORMER IDC XXXX
6714 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-02-06 15:47 | 2008-02-07 08:15 | 2 | 988 | 51618-1 | 1976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | /// RELEASED BY CREW 078H02, 7.2KV,25KVA120/240 BACKYARD, NEED YARDDOG CAN OPEN PRI TAP ON FUSE TOP OF POLE IN BAD SHAPE 4MEN RELEASED BY CREW 078H08//3003701//VER/CRB IDC XXXX
6715 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-03-27 18:50 | 2018-03-28 01:25 | 5 | 395 | 4133411 | 1975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ETA 1930// //bad 7200 10 kva, no trks, yrd dog, xfmer bag /pole38830070B43584 :bad 7200 10 kva, no trks, yrd dog, xfmer bagETR 1930/pole 70 b4 3584 :bad 7200 10 kva, no trks, yrd dog, xfmer bag Released by crew 078S07,repairs made all cust restored @ 0125 please close ticket thanks.bt
6716 | Pikeville | 3421001 | BREAKS | CITY | 2009-01-16 10:18 | 2009-01-16 15:00 | 7 | 282 | 55850-1 | 1974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD TRANSFORMER CREW ENROUTE. RELEASED BY CREW 074S02XFMR CHNGED POWER BACK ON ADDED 1 CUSOTMER THAT WAS MISS MAPPED FROM ORDER 56187-1 MD-ENTERED TOTAL COD - 7 L3/HFP
6717 | Hazard | 3302704 | HAZARD | KENMONT | 2013-04-12 07:13 | 2013-04-12 14:06 | 9 | 413 | 4002301 | 1973 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REM FROM MAIN LINE == GOT MAIN LINE ON AT 10:28 === 2 CUST STILL OFF === NEED LINE CREW AND 25 KVA 19.9 TRANSF AND CUTOUT AND T BRACKET === MANUAL POLE RELEASED BY CREW 077S03//COD 9// VER/DBM IDC XXXX
6718 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-06-12 20:12 | 2022-06-13 04:25 | 4 | 493 | 4062071 | 1972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO TAGS NO GROUNDS,, line fuse open on 92-433,, burnt off dead end transformer pole at 38830092A00438,, 45 foot pole,, wire is still in air,, truck access,, crew required Released by crew 078H10 Repairs made closed on 92-A-433 at 04:25. Ticket complete
6719 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-06-10 10:18 | 2013-06-10 10:52 | 58 | 34 | 4249711 | 1972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE AN TAGED ON POLE 39831124B33073 AT 10:18//COD 58//OPENED LINE FUSE AN TAGED ON POLE 39831124B33073 AT 10:18--OPENED LINE FUSE AN TAGED ON POLE 39831124B33073 AT 10:18-FIRE DEPT PUT POLE OUT--MADE TEMP REPAIRS--SEND TO TECHS FOR POLE REPLACEMENT//COD 58// VER/DBM IDC XXXX
6720 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-06-10 09:26 | 2008-06-10 13:30 | 13 | 244 | 61424-1 | 1972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401001//FUSE OUT ON POLE 263-331 STEP DOWN TRANSFORMER, NEED TO CHANGE OUT CSP 25 KVA TRANSFORMER TO CONVENTIONAL TRANSFORMER 12KVA POLE 263-137. ON AT 11:30 //COD 13// VER/DBM IDCC FP XXXX
6721 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-02-20 17:01 | 2015-02-21 09:27 | 2 | 986 | 4058201 | 1972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15KV 19.9 XFMR BAD, CAN REACH WITH SMALL BUCKET BUT SLICK NARROW RD./// CREW REQUIRED RELEASED BY CREW 077S08//COD 2// VER/DBM
6722 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-03-28 13:01 | 2022-03-28 16:00 | 11 | 179 | 4683801 | 1969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Span of Neutral down from pole 120-A-373 to 120-A-87,spoke with Rick Ray and is on the way to help get it put back up..Will be opening Line fuse at 120-A-84 will keep up with Time.Open @ 15:30/ Closed @ 16:00.
6723 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-08-02 00:43 | 2019-08-02 08:55 | 4 | 492 | 4829401 | 1968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | //6t fuse out looks like fuse broke installed new fuse eveything ok
6724 | Hazard | 3309002 | JEFF | JEFF | 2019-08-10 14:04 | 2019-08-10 18:12 | 9 | 248 | 4869521 | 1968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | low side riser burnt out of step down/ open point on pole 321-92 to cut out 1 span primary, closed stepdown at 18:45, grounded and tagged to tim smith Released by crew 077H14 all power restored at 18:12 Released by crew 077H02
6725 | Hazard | 3310502 | HADDIX | CANOE | 2013-02-19 09:18 | 2013-02-19 09:25 | 281 | 7 | H4828341 | 1967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKE CROSSARM ON POLE 121-40 GOT CREW COMMING TO REPLACE RELEASED BY CREW 077S05 //VER/GAH IDC XXXX
6726 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-06-22 20:29 | 2014-06-22 22:40 | 15 | 131 | 4139031 | 1965 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | SEND NOTE TO RAYBURN TRANS, VERY HOT 1/0 RISER MELTING OFF POLE NEEDS ANOTHER TRANS INSTALLED DOWN LINE OR CHG. POT TO 75 KVA 350 RISERS VER/SEF
6727 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-10-20 00:27 | 2011-10-20 11:22 | 3 | 655 | 4001711 | 1965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED--SLEEVE PULLED LOOSE--PRIMARY DOWN--TRUCK TO POLE RELEASED BY CREW 078S07//COD 3// VER/DBM IDC XXXX
6728 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-04-22 01:13 | 2021-04-22 12:08 | 3 | 655 | 4469691 | 1965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Temp 33 /CREW REQUIRED BAD 25 kva xfr ,,big bucket 2 pole Released by crew 078S05///Complete BR
6729 | Whitesburg | 3401301 | FLEMING | NEON | 2008-11-30 00:29 | 2008-11-30 02:40 | 15 | 131 | 53058-1 | 1965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401301 - RELEASED BY CREW 074S073401301 - CUTOUT IS BROKE ON POLE 355-75 WILL NEED ONE MAN AND A CUTOUT //VER/GAH IDC XXXX
6730 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-08-04 19:38 | 2009-08-05 12:00 | 2 | 982 | 59786-1 | 1964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FOR XFMR BROKEN, 19.9 KV NEED CUTOUT, TRUCK ACCESSABLE, CUSTOMER IS GOING ON VACATION IN THE MORNING AND WOULD LIKE TO BE RESTORED TON IGHT IF POSSIBLE. WATCH DOG, MAY BITE RELEASED BY CREW 077M02 VER/KEP L3/KEP IDC XXXX
6731 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-11-04 06:09 | 2018-11-04 09:25 | 10 | 196 | 4361191 | 1960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Line fuse cutout failed. Replaced and restored @ 9:25. sh L3/HFP
6732 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-05-22 08:05 | 2010-05-22 12:45 | 7 | 280 | 66236-1 | 1960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35235219 //TRANSFORMER IS BAD WILL NEED ONE MAN BIG BUCKETT AND 50 KVA TRANSFORMER IS BAD WILL NEED ONE MAN BIG BUCKETT AND 50 KVA TRANSFORMER REPLACED TRANSFORMER // COD-7 VER/HFP L3/HFP IDC XXXX
6733 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-07-12 11:40 | 2009-07-12 14:00 | 14 | 140 | 62828-1 | 1960 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | VER/HFP XFMR FUSE OUT, PART POWER TO SEVERAL BUSINESSES, XFMR FUSE HAD BROKE COD-14 ISO TF 37830206B00163 L3/HFP IDCC MCCDL, CCO XXXX
6734 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2017-06-07 00:35 | 2017-06-07 11:28 | 3 | 653 | 4918171 | 1959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 6A PRIMARY DN. NEED LINE CREW CAN USE TRUCK LINE FUSE OUT ON POLE 174-12 NO GROUNDS PLACED. RELEASED BY CREW 074S02/// REPAIRS MADE WIRE PULLED OUT OF COPPER FARGO SLEEVE,BACK ON AT 11:28 37820174000012 VER/AWD
6735 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-01-08 18:36 | 2019-01-08 20:05 | 22 | 89 | 4643481 | 1958 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Riser burnt off cutout at pole 69-5585, repairs made and all power restored at 20:05 L3/HFP
6736 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-06-04 21:17 | 2014-06-04 23:00 | 19 | 103 | 4978571 | 1957 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1147-4544 40T LINE FUSE CUTOUT BURNT UP COD-19 ISO LF 39831147C24544 VER/HFP L3/HFP
6737 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-02-20 08:59 | 2015-02-20 19:51 | 3 | 652 | 4053351 | 1956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE/////////BAD 25 KVA,REPLACE W SAME,IS 19.9/CANT GET TO POLE XCEPT W HAMTRAK////////////NEED CREW,CAN USE WINCH IF NECESSARY,IS IN BACK YARD RELEASED BY CREW 074S06 VER/TOM L3/TOM
6738 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-04-15 00:14 | 2013-04-15 11:06 | 3 | 652 | 4008981 | 1956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER NOT OUT ** SERVICER FOUND BAD CUTOUT ON POLE 272-D-862 *** NOT BY TRUCK. *** CREW WILL BE DISPATCHED AT REG WORK TIME TO REPLACE.RECLOSER NOT OUT SERVICER FOUND BAD CUTOUT ON POLE 272-D-862 NOT BY TRUCK. CREW WILL BE DISPATCHED AT REG WORK TIME TO REPLACE. OPENED LINE UP AT 10.35 CLOSED AT 11.06 REPLACED BAD CUTOUTS VER/KEP IDC XXXX
6739 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-05-28 08:49 | 2021-05-28 14:15 | 6 | 326 | 4635051 | 1956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | needs trees cut back at this tran--38830186000048 50t blown--replaced suspect c/o 38830186000149--50t line fuse in at 14:15--allgood-ds052821//SENT TO R/W
6740 | Hazard | 3302703 | HAZARD | HAZARD | 2014-07-06 16:44 | 2014-07-06 18:39 | 17 | 115 | 4197241 | 1955 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 075H04 XFMR LEAD BAD . OPENED XFMR ON POLE 296A-700 @ 18:25 CLOSED BACK @ 18:39 , ALL POWER OK ./// COD 17//// ISO 37830296A30700 VER/HFP L3/HFP
6741 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-09-13 22:15 | 2013-09-14 00:10 | 17 | 115 | H4852681 | 1955 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 596-88 NO TRUCKS TO POLE, LINECREW REQUIRED RELEASED BY CREW 078S11//SWITCH AT 2215 17 COD//BROKEN CUTOUT ON 596-88 NO TRUCKS TO POLE, LINECREW REQUIRED RELEASED BY CREW 078S11 (BAD POLE HAD TO GUY IT OFF TO MAKE IN SAFE TO CLIMB ;SEND TROUBLE TICKET TO TECH TO BE CHANGED OUT AT LATER: ; DATE TRACK EQUIPTMENT REQUIRED // DUP OF 4852681 TO REPLACE CUTOUT VER/HFP L3/HFP IDC XXXX
6742 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2008-12-12 08:35 | 2008-12-12 10:30 | 17 | 115 | 57509-1 | 1955 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | 3312201//REGULATOR INSIDE STATION FAILED VER/KEP L3/KEP IDCC XXXX
6743 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-02-03 12:39 | 2010-02-03 14:12 | 21 | 93 | 62651-1 | 1953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OUT AT POLE 37830247A00307 DUE TO BAD XFMR AND CUTOUT AT POLE 247-382//VER/CRB IDC XXXX
6744 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-01-14 06:08 | 2009-01-14 09:45 | 9 | 217 | 54831-1 | 1953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001003// ISO 38830231000108//PRIMARY FELL IN CLEAR AT POLE 231-108//COD 9// REC AT POLE 230-228 OPENED AT 09:15, CLOSED AT 09:45(NEW OUTAGED CUSTS ION 54861Z)// VER/DBM L3/KEP
6745 | Pikeville | 3408103 | SALISBURY | MARTIN | 2017-02-06 17:33 | 2017-02-06 21:10 | 9 | 217 | 4362281 | 1953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON 38831099000084 TOOK OUT FUSE ON 1098D172 REPLACED ARRESTOR ON 1099-84 RESTORED POWER AT 21:10 VER/AWD L3/HFP
6746 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-03-04 10:21 | 2015-03-04 14:25 | 8 | 244 | 4097811 | 1952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | TIE WIRE BROKEN AN PHASE LAYING AGINST IN PIN @ POLE 38830427000040PRIMARY OFF PIN INSULATOR ON POLE 427-40 MAY GET TRUCKS TO POLE ( TIE WIRE BROKE ) NEED LINE CREW.PRIMARY OFF PIN INSULATOR ON POLE 427-40 MAY GET TRUCKS TO POLE ( TIE WIRE BROKE )RETIED PHASE AND CHANGED BAD CUTOUT TIME ON 2;25 PLEASE CLOSE TICKET DWW VER/CRB L3/DKGXXXX
6747 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2015-11-12 12:30 | 2015-11-12 13:45 | 26 | 75 | 4431251 | 1950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LUKE REPORTED OUTAGE// CREW REQD. CONNECTION @ HOT TAP AND LINE FUSE 45 C2 4698 RELEASED BY CREW 078S07 RELEASED BY CREW 078H22,REPAIRS MADE ALL CUST RESTORED @ 1345 PLEASE CLOSE TICKET THANKS.BT VER/CRB AJBC TOF10:21
6748 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2015-04-14 08:02 | 2015-04-14 10:32 | 13 | 150 | 4315181 | 1950 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 21 B3 3095 B PHASE CUTOUT BROKE 65T/CREW ONSITE TO REPAIR// COD 13 PART POWER// VER/ ADH
6749 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-08-20 18:33 | 2011-08-20 23:57 | 6 | 324 | 4734251 | 1944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA///REPLACE WITH 37.5 AND ALSO NEW SEC RISERS////2 CUST OUT/// TRUCK TO POLE OK/// RELEASED BY CREW 078H16//PT ON SITE//REPLACED TRANSFORMER POWER RESTORED AT 11:57 CLOSE TKT. PR TOLLIVER IDC XXXX
6750 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-09-09 01:07 | 2017-09-09 05:10 | 8 | 243 | 4342511 | 1944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALL CENTER REPORTS GAS LEAK IN AREA AND EMERGENCY PERSONAL ON SITE,,LINE FUSE OUT ON 858-14..PATROLLING BAD CUTOUT DOOR ON 858-14..CHANGING SJGC TON04:53 PER PO
6751 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-11-29 10:26 | 2016-11-29 18:32 | 4 | 486 | 4142551 | 1944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT LOOP ON 182 -3748 POLE AT 182-3749 IS BURNT OFF 45-2 SIDE ARD TRUCK OK /CAN LOWER NO GROUND INSTALLLED RELEASED BY CREW 078S03,REPAIRS MADE ALL CUST RESTORED @ 1832 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830182B43748/ COD 4/ VER/BOW
6752 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-12-14 17:36 | 2008-12-14 23:00 | 6 | 324 | 58360-1 | 1944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3300601// TRANSFORMER LEAD BURNT INTO VER/PDP IDC XXXX
6753 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-02-25 07:09 | 2011-02-25 10:45 | 9 | 216 | 61180-1 | 1944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 FUSES BLOWN,1 BAD CUTOUT, ON TRANSFORMER BANK ON POLE 37830271A10477, CENTER PHASE FUSE BLOWN ON POLE 37830271A00184---ALL POWER RESTORED AT 10:45//COD 13//ISO 37830271A00184// VER/DBM IDC LOOKS LIKE MAYBE PHASE A WAS OUT NOT B, THE ONLY CALL WAS ON PH A, CHANGED COUNT FROM 13 XXXX
6754 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-05-05 16:50 | 2015-05-05 20:04 | 10 | 194 | 4393381 | 1940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ARRIVED AT CALL, FOUND BAD 50 KVA, SINGLE BUSHING, 7200V 120/240, CREW REQ, CAN USE TRUCK HAVE TRANSFORMER OPEN UP RIGHT ACROSS STREETT FROM 1032 WINFRED, RELEASED BY CREW 078S06/ ISO 39831073B12099/ COD 10 VER/HFP L3/HFP
6755 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-08-06 08:51 | 2010-08-06 19:37 | 3 | 646 | 50153-1 | 1938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT GATE BURNED UO. NEIGHBORS REPORT LAST NIGHT STARTED SMOKING AND THIS MORNING COULD SEE FIRE.CUT OUT FUSE HOLDER APPEARS CHARRED. RELEASED BY CREW 077F01
6756 | Hazard | 3301401 | COMBS | COMBS | 2015-03-07 22:36 | 2015-03-08 14:45 | 2 | 969 | 4165191 | 1938 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK IN THE MORNING CREWS AND SERVICER TO REPORT @ 0700 FOR ANOTHER OUTAGE. SERVICE BURNT IN TWO AT TRANSFORMER... ONE SIDE OF TRANSFORMER HAS NO VOLTAGE, POWER RESTORED. VER/KEP
6757 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2017-08-26 09:59 | 2017-08-26 15:22 | 6 | 323 | 4300591 | 1938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WIRE PULLED OUT OF SLEEVE AT POLE 37830225D00308WIRE PULLED OUT OF SLEEVE AT POLE 225D-308 RELEASED BY CREW 077H14 OPENED RECLOSERS 4300591.WIRE PULLED OUT OF SLEEVE AT POLE 225D-308 RELEASED BY CREW 077H14 ALL POWER RESTORED AT 15:22 RELEASED BY CREW 077H02 VER/AWD L3/HFP HFPC CNT1 SJG
6758 | Hazard | 3310502 | HADDIX | CANOE | 2008-01-25 12:41 | 2008-01-25 12:54 | 149 | 13 | 59575-1H | 1937 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3310502// COD-1235 // TOP OF POLE BROKE OFF // WILL LOWER LINE ON POLE & REPLACE CROSSARM//3310502 RELEASED BY CREW 077S05 VER/LDA DEBBIE/149 CUST OFF AGAIN ON ORDER 59575-1H...245 CUST OFF AGAIN ON ORDER 59575-1HA IDC XXXX
6759 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-10-28 01:51 | 2016-10-28 09:55 | 4 | 484 | 4059201 | 1936 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 2 CONNECTIONS BURNDT INTO ON A SECONDARY, WILL BE MAKING REPAIRS. REPAIRED 4 SECONDARY CONNECTIONS, RESTORED @1000. /// REPLACED CONNECTIONS ON SECONDARY & TRANSFORMER POLE // COD-4 ISO SO 37830095000092
6760 | Hazard | 3302704 | HAZARD | KENMONT | 2013-11-09 13:53 | 2013-11-09 17:55 | 8 | 242 | 4024411 | 1936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ISO 37830297000087//COD 8// LOOP INTO ON POLE 297-87. WIRE FELL OUT OF HOT LINE CLAMP// VER/DBM L3/HFP IDC XXXX
6761 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2021-06-29 05:55 | 2021-06-29 09:30 | 9 | 215 | 4820421 | 1935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Dispatched in accordance with KYPCo Late Night Callout Guideline. I cut a damaged arrestor in the clear on pole 175-3 and replaced a broken cut out. I also repaired several damaged secondary connections. Power restored at 9:30.
6762 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2017-10-07 20:15 | 2017-10-07 21:00 | 43 | 45 | 4418611 | 1935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4417711/ CREW OPENING SWITCH TO REPAIR CUTOUT CONNECTION ON 38830954C20683/ ISO 38830954A40908/ COD 43/ OPENED @ 2015 CLOSED @ 2100/ VER/BOW L3/HFP XXXHFP ACB
6763 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-08-18 17:35 | 2010-08-18 21:10 | 9 | 215 | 57829-1 | 1935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLEW BUT GATE DID NOT OPEN BURNT GATE UP REPLACED GATE RESTORED POWER AND CUT ARRESTER IN CLEAR ON POLE 387-259 VER/KEP L3/KEP IDC XXXX
6764 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-03-04 19:53 | 2016-03-05 12:00 | 2 | 967 | 4818391 | 1934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFMER. MUST BLOCK 1 LANE US 23 FLAGGERS REQD. NOTIFY CSX @ TRACKS. ACROSS FROM TRI-STATE PAWN @ 43 ST. RELEASED BY CREW 078S07/ RAILROAD HAS BEEN NOTIFIED RR REP SHAWN/ HAD TO OPEN LINE FUSE ON POLE 38830070A45181 TO REPAIR TRANSFORMER 38830070A41553/ ISO 38830070A45181/ COD 2/ MD DONE/ OPENED LINE FUSE 38830070A45181 @ 1140/ CLOSED LINE FUSE 38830070A45181 @ 1200// VER/ ADH
6765 | Paintsville | 3401802 | INDEX | HOSPITAL | 2019-08-17 15:17 | 2019-08-17 22:35 | 8 | 438 | 4900221 | 1932 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | Bad 50 Kva padmount transformer (single phase feed thru 7200). Crew will be enroute as soon as they get in and get equipment loaded. No truck access. Opened pri on 654-457 @ 21:50 (De-energized xfmrs 654-463 & 464). Restored all customers @ 22:35. sh Released by crew 076S02
6766 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-09-13 23:27 | 2008-09-14 00:51 | 23 | 84 | 62282-1 | 1932 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401102/WR # 26253686 //3401102/CHECKING NOW3401102/CHECKING NOWLEAD COME OUT OF TOP OF XFMER CUTOUT VER/KEP MLR OK
6767 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-12-22 10:29 | 2015-12-22 13:10 | 12 | 161 | 4550071 | 1932 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 398-155, MANUEL POLE ON HILLSIDE..REPLACED CUTOUT , RESTORED POWER AT 13:10./ ISO 37830398D00091/ COD 12/ VER/BOW
6768 | Paintsville | 3401802 | INDEX | HOSPITAL | 2008-03-07 16:01 | 2008-03-07 17:25 | 23 | 84 | 54698-1 | 1932 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | 3401802// CENTER PHASE - B PHASE SECTIONALIZER CUTOUT BURNT UP - 23 CUST EFFECTED/ VER/HFP IDCC CNT23 XXXX
6769 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-07-13 07:09 | 2017-07-13 13:35 | 5 | 386 | 4112781 | 1930 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | BAD LA ON XFR POLE,WILL CLEAR IT UP AND RE-FUSE OUT AT POLE 1058-321////////CLEARED ARRESTOR,RE-FUSED&RESTORED /// B PHASE FUSE OUT COD 5 ISO LF 38821058B00321 VER/HFP L3/HFP
6770 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2020-02-24 15:30 | 2020-02-24 18:43 | 10 | 193 | 4428281 | 1930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | no outage, pole has rotted off at ground level 37830304000053 , DHE is going to replace pole.. OPENED L/F 37830328A00064 @ NO CUSTS OUT TILL THEN // OFF @ 1530 // ON @1843 L3/HFP
6771 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-22 11:10 | 2021-06-22 16:30 | 17 | 320 | 4791561 | 1930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on 770-a-36//opened fuse on 770-275 at 15:40//repairs made//restored at 16:30//complete//em
6772 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-04-21 07:14 | 2018-04-21 10:27 | 10 | 193 | 4260371 | 1930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Riser burnt out of line fuse cutout on 60 ft pole. Additional personel enroute to assist. Replaced cutout and restored @ 10:27. sh/ ISO 38830833D00227/ COD 10
6773 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2022-01-06 23:50 | 2022-01-07 15:53 | 2 | 963 | 4317621 | 1926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse open on pole 859-A-36, top of pole brunt off at pole 859-A-54 do to bad cutout, will be crew crew required will need pole top pin, cutout lighting arrester, pole top ext or 8ft arm,roads are still bad shape may need chains on trucks.//// all 7200. Released by crew 074S03
6774 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-03-15 03:18 | 2009-03-15 05:05 | 18 | 107 | 58679-1 | 1926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401702// COD-18 // HIGH SIDE CUTOUT ON STEPDOWN TRANSFORMER IS BROKEN. I AM GOING TO CHANGE CUTOUT.3401702// COD-5 // HIGH SIDE CUTOUT ON STEPDOWN TRANSFORMER IS BROKEN. I AM GOING TO CHANGE CUTOUT. I CHANGED THE CUTOUT AND RESTORED POWER AT 05:05 VER/LDA IDCC CDC92 XXXX
6775 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-10-24 13:41 | 2016-10-24 17:15 | 9 | 214 | 4049211 | 1926 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CUSTOMER HAD LOW VOLTAGE ON ONE LEG OF SECONDARIES FOUND BAD CONNECTION AT SERVICE POLE REPLACED CONNECTION RESTORED POWER AT 17:15 CONNECTION HAD GOTTEN HOT AND MELTED TAPE AND ALLOWED WIRE TO CORRODE VER/AWD
6776 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2022-06-20 08:45 | 2022-06-20 15:10 | 5 | 385 | 4259131 | 1925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Secondary hot leg has got against main line neutral and burndt 2 hot legs and the main line neutral down off pole #1151-D-102, will need another man to help put neutral back up and repair sec. No truck access. Will have to open trans. to make repairs. Only 2 customers with part power currently. Opened trans. @1442 made repairs and closed back in @1510.
6777 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-03-31 17:30 | 2015-03-31 18:25 | 35 | 55 | H4249511 | 1925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BACK TO STATION C & B RECLOSERS ARE OPEN ( 61 CUSTOMERS)///WIRE DOWN BETWEEN POLE 852-48 AND 852-49///OPENED A PHASE REC @ 17:30 AND OPENED ALL 3 LOAD SIDE DISCONNECTS SWITCHES AND PLACED TAG FOR ROBIE BLAIR///CLOSED RECLOSURES ON 852-409 @ 18:25///COMPLETE BR COD-96 DUP OF 4249511 FOR A PHASE OUTAGE 35 CUST VER/HFP L3/HFP AJB CCTOR PER TROUBLEMAN
6778 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-08-22 16:03 | 2014-08-22 17:20 | 25 | 77 | 4403891 | 1925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT GATE FUSE BROKE MAKING UP THRU GATE CAUSED FIRE/// REFUSED XFMR POWER RESTORED//ISO//COD 6 AJB
6779 | Pikeville | 3421001 | BREAKS | CITY | 2008-06-22 08:25 | 2008-06-22 11:20 | 11 | 175 | 51725-1 | 1925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400901/// 2 LINE CUTOUTS ARE BLOWN ON POLE 220-6. BOTH CUTOUTS ARE BROKE DOWN THE MIDDLE OF THEM. I THINK LIGHTENING MAY HAVE HIT POLE. PIKEVILLE IS SENDING HELP TO CHANGE THEM. IT TAKES A BIG BUCKET. . WE HAVE CUTOUTS REFUSED NOW. // VER/TOM
6780 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-04-25 12:57 | 2015-04-25 14:11 | 26 | 74 | 4364651 | 1924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /FUSE OPEN ON 501-325 PATROLLING LINE/ FUSE OPEN ON 501-325 PATROLLING LINE, FOUND AND REPLACED BAD CUTOUT ON 501-91 APR AT 1411 CLOSE TICKET/ ISO 38830501000325/ COD 26/ VER/BOW L3/HFP XXX AJB
6781 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2016-02-20 04:20 | 2016-02-20 06:48 | 13 | 148 | 4739631 | 1924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STEPDOWN F IS OUT,WILL PTRL////////////BAD ARRESTER POLE 7-45,WILL CLEAR IT UP////////CLEARED ARRESTOR,WILL RE-FUSE LINE///////RE-FUSED AND RESTORED//COD 13//AED ENTRY CREATED//
6782 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-03-05 14:44 | 2012-03-05 15:58 | 26 | 74 | H4549011 | 1924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER IS OPEN AT 169-230. CUTOUT FAILED ON POLE 169-238 AND BURNED TOP OF POLE OFF. WE LIFTED HOTTAP ON POLE 169-77 TO ISOLATE FAULT. I AM GOING TO CLOSE RECLOSER AT 169-230 BACK IN. WE WILL LOWER EQUIP. ON 169-238 TO GET THIS TAP BACK ON. I CLOSED RECLOSER AT 169-230 IN AT 15:58. THIS LEAVES 2 CUSTOMERS OUT UNTIL WE FIX PROBLEM. WE PUT HOT TAP AT 169-77 ON LINE AT 17:30//COD 27// VER/DBM IDC XXXX
6783 | Hazard | 3309002 | JEFF | JEFF | 2010-07-27 19:55 | 2010-07-27 20:32 | 52 | 37 | 58204-1 | 1924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREWS OPENED FEEDER BREAKER IN ORDER TO MAKE REPAIRS TO BROKEN INSULATOR IN ORDER 58152-1//COD 52// VER/DBM IDC XXXX
6784 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-08-07 13:11 | 2008-08-07 14:30 | 44 | 79 | 66492-1 | 1922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3301402// CUTOUT BROKE DOWN AND POLE ON FIRE OPENED OCR ON POLE # 250 - 8 . ///RELATED TO ORDER 66461-1. VER/HFP IDC XXXX
6785 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-11-04 10:32 | 2019-11-04 17:01 | 8 | 389 | 4289581 | 1922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RISER FUSE OUT ON POLE 38830785C21142//COD 3//MADE MD TO SHOW MISMAPPED CUSTOMER //COD SHOULD BE 3//tried riser and it blew l/f on pole 38830785C20813 @ 1430//cod 3 from beginning of outage//RISER FUSE OUT ON POLE 38830785C21142//COD 3//MADE MD TO SHOW MISMAPPED CUSTOMER //COD SHOULD BE 3//tried riser and it blew l/f on pole 38830785C20813 @ 1430 Crew enroute.RISER FUSE OUT ON POLE 38830785C21142//COD 3//MADE MD TO SHOW MISMAPPED CUSTOMER //COD SHOULD BE 3//tried riser and it blew l/f on pole 3 L3/HFP
6786 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-07-26 08:58 | 2014-07-26 09:15 | 113 | 17 | 4289581 | 1921 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECL TO SAFELY REPLACE CUTOUT ON PO#4288651 IDC XXXX AJB
6787 | Hazard | 3301101 | CHAVIES | CHAVIES | 2018-04-28 09:31 | 2018-04-28 15:55 | 5 | 384 | 4286271 | 1920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout 7200 e bad cutout 7200 Released by crew 077H14 L3/HFP
6788 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2013-03-31 08:45 | 2013-03-31 10:05 | 24 | 80 | 4969181 | 1920 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | `A` PHASE FUSE OUT 24 CUST TOTAL //A PHASE FUSE OUT 24 CUST TOTAL // CHGED TWO CUTOUTS ON POLE 45-6661 50T LINE FUSE OUT 69-1003 COD-24 ISO LF 38830069A31003 VER/HFP L3/HFP IDC XXXX
6789 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-05-17 10:50 | 2009-05-17 11:50 | 32 | 60 | 60563-1 | 1920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT...POLE FIRE ON 37820032A00139.....CAN REACH FROM CREW BUCKET TRUCK & MAKE REPAIRS....POLE BURNT COMPLETELY OFF AT TOP, BUT POWER NOT OFF.....POLE TOP & CUTOUT ARE FLOATING.....CALLED CREW, (JOEY REED) THEY ARE ENROUTE....WILL OPEN LATERAL FUSE ON 37820032A00138 WHEN THEY ARRIVE...//...OPENED TAP @ 10:50...REPLACED CUTOUT, EXTINGUISHED POLE FIRE, RE WORKED POLE-TOP, RE-ENERGIZED TAP @ 11:50.....JRV...05/17/09 VER/PDP
6790 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-09-29 14:55 | 2008-09-29 16:55 | 16 | 120 | 51920-1 | 1920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3413401//OPENED A PHASE OCR AT POLE 65-162 B AT 14:55//ISO 37830065D00162//COD 16//,OPENED B & C PHASE AT 16:20, REPACED 8 ARM, BRACES AND INSULATORS, ON AT 16:55, ALL WORK COMPLETE / GXJ IDC XXXX
6791 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2021-08-07 14:44 | 2021-08-07 17:50 | 16 | 186 | 4015641 | 1919 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN IN THE CLEAR AT POLE 38821110C00163 COD 9//OPENING B PHASE RECLOSER TO MAKE REPAIRS THIS WILL OUTAGE 7 MORE CUSTS//OPENED OCR @ 1715 //CONDUCTOR PULLED OUT OF SLEEVE/CLOSED RECLOSERWIRE DOWN IN THE CLEAR AT POLE 38821110C00163 COD 9//OPENING B PHASE RECLOSER TO MAKE REPAIRS THIS WILL OUTAGE 7 MORE CUSTS//OPENED OCR @ //CONDUCTOR PULLED OUT OF SLEEVE// Released by crew 079S03
6792 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-07-25 17:16 | 2014-07-26 09:15 | 2 | 959 | 4288651 | 1918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE OUT UP ON BAD POLE, CALLED CUST, THEY SAID WAIT UNTILL IN MORNING RELEASED BY CREW 078S09/CREW ON SITE/FETR 10:15/ REC. PL# 262-227 OPENED @ 08:55/ TO SAFELY ISOLATE & MAKE REPAIRS@262-106/ REC. IN SERVICE @ 9:15/ ALL CUST. RESTORED@ 09:15/ PLEASE CLOSE TICKET. JEH VER/KEP
6793 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-01-12 10:56 | 2012-01-12 15:30 | 7 | 274 | 4251311 | 1918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 424-1 WASHED OUT AND LEANING, PRIMARY ON GROUND, YARD DOG JOB, NEED MANUAL TREE CREW FOR ROW, EXISTING POLE IS 45 BUT COULD GET BY WITH 40, NO PHONE OR CABLE.,, TEMP ANCHOR INSTALLED TO PULL POLE BACK, SEND COPY TO TECH TO WRITE JOB FOR CHANGING POLE, ALL POWER RESTORED//COD 7// VER/DBM IDC XXXX
6794 | South Williamson | 3411401 | DEWEY | INEZ | 2008-04-27 22:58 | 2008-04-28 01:15 | 14 | 137 | 54716-1 | 1918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401//ONSITE @ 0024....FUSE OUT ON LATERAL....POLE 768-D-39....PATROLLING.....JRVENTURINO....04/28/08....FOUND PROBLEM....BRKN XFRMR CUTOUT....LAST POLE...768D224....DUZNT FEED ANY METERS ANYMORE....WILL CLEAR UP AND RESTORE REMAINING CUSTS.....JRV 00:55 // COD-14 //3411401//ONSITE @ 0024....FUSE OUT ON LATERAL....POLE 768-D-39....PATROLLING.....JRVENTURINO....04/28/08....FOUND PROBLEM.... VER/LDA IDC XXXX
6795 | Pikeville | 3407103 | TOPMOST | KITE | 2015-05-01 11:27 | 2015-05-01 15:00 | 9 | 213 | 4381361 | 1917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T LINE FUSE OUT DUE TO POLE 37830233000040 BEING BURNT OFF. POLE37830233000040 HAS 15KVA TRANSFORMER ON IT ALSO. TIM HALL ON THE WAY WITH MATERIAL TO MAKE REPAIR//MDC MADE AND NOTE ADDED TO MAPS//. WE ADDED CROSS ARM TO TOP OF POLE. SEND COPY TO ENG AND SEND COPY TO ROW ALSO. EVERYTHING NEEDS CUT FROM FUSE POLE. 37830234000053 VER/CRB L3/HFP XXX AJB
6796 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-06-05 00:51 | 2011-06-05 11:30 | 3 | 639 | 4233091 | 1917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-431 BAD 37.5 NO TRUCK NEED TRECK MAN. TAKE TO CUST SAIDS ROAD OUT BACKSEND TO CREWS RELEASED BY CREW 078S08 RELEASED BY CREW 078H01PRT ON SITE NO TRUCKS //REPLACED TRANSFORMER AND CUT-OUT POWER RESTORED AT 11:30 PRT //VER/GAH IDC XXXX
6797 | South Williamson | 3411401 | DEWEY | INEZ | 2017-11-19 00:01 | 2017-11-19 10:40 | 3 | 639 | 4576841 | 1917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke on pole 769-79//making repairs////cutout replaced//restored at 10:40//complete//em
6798 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-05-16 14:31 | 2009-05-16 20:54 | 5 | 383 | 58603-1 | 1915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF WILL HAVE TO REPLACE POLE @ 1525 - CONTACTED JEFF COMBS D/S FOR HELP.POLE TOP BURNT OFF WILL HAVE TO REPLACE POLE RELEASED BY CREW 077H14 REPLACED POLE AND RESTORED POWER AT 2054 JKC//VER/CRB IDC XXXX
6799 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-11-05 13:01 | 2021-11-05 15:55 | 11 | 174 | 4060371 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 line fuse cutout on pole 126-c4-252. G. shouse crew going to make repaires Released by crew 077S10
6800 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-07-12 14:00 | 2010-07-12 14:22 | 87 | 22 | 65470-1 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 35945882 // PRI BROKE AT BASKET ON POLE 44-B-256,GOING TO OPEN UP REC, ON POLE 44-A-158 TO MAKE REPAIRS WILL OFF AND ON TIMES FOR TICKET ,OFF TIME WAS 14;00HRS, ON TIME BACK ON 14;22HRS38820771B30063 IDC XXXX
6801 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2017-04-05 15:36 | 2017-04-05 17:03 | 22 | 87 | 4617441 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON 38831101D30365 TO SAFELY REPLACE EQUIPMENT ON POLE 38831101D30363. ASSOCIATED WITH OUTAGE 4617141. OPENED 1536.1703. VER/AWD L3/HFP XXXHFP AJB
6802 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-01-06 17:08 | 2022-01-07 09:05 | 2 | 957 | 4314161 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 39830879D00037 WILL NEED BIG BUCKET AND CUTOUT // DUE TO HAZARDOUS ROAD CONDITION HOLDING UNTIL TOMORROW
6803 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2017-12-11 10:16 | 2017-12-11 13:10 | 11 | 174 | 4638731 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 KVA transformer. Line crew enroute to replace. Crew working to replace. Replaced xfmr & restored @ 13:10. sh COD-11 IS TF 38830809000846
6804 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-03-14 17:37 | 2009-03-15 04:15 | 3 | 638 | 58565-1 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S06POLE 1011-129 IS BURNED OFF,3 FUSES OUT DOWN THE HILL.DALE HAM IS ROUNDING UP CREW/MATERIALS,WILL BE HERE SHORTLY// WR# 28926547 //MADE REPAIRS AND RESTORED,ALL OK AFTERWARDS // COD-3 VER/LDA IDC XXXX
6805 | Pikeville | 3408103 | SALISBURY | MARTIN | 2013-01-23 11:26 | 2013-01-23 14:20 | 11 | 174 | 4732921 | 1914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLED LINE AND FOUND ONLY BAD ARRESTER AT POLE 22 ( IN CLEAR ) MAY OR MAY NOT HAVE BEEN PROBLEM .REFUSED LINE CUTOUT, ALL WORK COMPLETE / GXJ//COD 11//AED ENTRY FOR ARRESTER CREATED// VER/DBM IDC XXXX
6806 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-03-13 15:59 | 2009-03-13 20:32 | 7 | 273 | 58229-1 | 1911 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308503//ISO 37830246D00049//LINE BROKE IN THE CLEAR AT POLE 246-49//WILL HAVE TO OPEN STEPDOWN XFRMR LATER TO MAKE REPAIRS//COD 7//CONDUCTOR BURNT DOWN ON POLE 246-49// VER/DBM IDC XXXX
6807 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2013-01-13 06:15 | 2013-01-13 11:40 | 14 | 325 | 4599281 | 1910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRC CREW REQUIRED--BAD CUTOUT BURNT TOP OFF 40CL 5 TRANSFOMER POLE TRUCK TO POLE--LIFTED HOT TAP AND INSTALLED GROUND ON POLE 38830068A00106-BURNT OFF POLE ON FRYER CT OFF KEATON DR ON HILL CLOSED FUSE IN ON POLE 38830068A00088 AT 0800 - HOIS CC 14 ON FUSE FROM 0615 TO 0800 12CC REST 0800 . ALL ON AT _1140____ RELEASED BY CREW 078H02 ///VER/CRB L/3 CRB IDC XXXX
6808 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-04-15 07:19 | 2014-04-15 10:30 | 10 | 191 | 4605581 | 1910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 570-13 DUE TO POLE FIRE AT 594-35 PLEASE SEND COPY TO WES B SO HE CAN LOOK AND SEE IF HE WANTS TO CHANGE POLE LATER, WAS ABLE TO LOWER AND RESTORE POWER. APR AT 1030 CLOSE TICKET VER/CRB IDC XXXX
6809 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-17 12:07 | 2009-06-17 15:20 | 12 | 193 | 59511-1 | 1909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-11 ISO 37830021000027 FUSE DOOR BURNT UP.FUSE DOOR BURNT UP. RESTORED ALL CUSTOMERS EXCEPT XFMR ON POLE 21-27 AT 14:58. WILL HAVE MATERIAL TO RESTORE LAST CUSTOMER IN ABOUT 20 MINUTES. COD-11 ISO 37830021000027 L3/HFP
6810 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-06-22 07:55 | 2011-06-22 09:41 | 18 | 106 | 4386591 | 1908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THERE IS A LINE FUSE CUTOUT BURNT UP ON POLE 38831102000070 WE WILL HAVE TO REPLACE. I WILL CALL CREW. REPLACED BAD CUTOUT AND RESTORED POWER AT 09:41 TIM MCCOY VER/HFP L3/HFP
6811 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-06-15 14:54 | 2011-06-15 17:33 | 12 | 159 | 4322571 | 1908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE 1131-8 IS OUT,GOING TO ADD ANOTHER FUSE ON UP STREAM FRM THIS ONE,CREW ENROUTE TO DO WORK//////FOUND A BAD CUTOUT WHICH WE ISOLATED//////RE-FUSED AND RESTORED//COD 12// VER/DBM
6812 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2014-11-12 12:03 | 2014-11-12 15:35 | 9 | 212 | 4722681 | 1908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER RESTORED/ BROKE FUSE/ ISO 38830069A31259/ COD 9// VER/BOW L3/HFP AJB
6813 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-02-20 13:38 | 2019-02-20 14:31 | 36 | 53 | 4816621 | 1908 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | stirrup burnt in half on pole 39831147C14007. making repairs.
6814 | Pikeville | 3402002 | KEYSER | STONECOAL | 2012-04-05 04:27 | 2012-04-05 10:48 | 5 | 381 | 4649071 | 1905 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AFTER REGULAR WORKTIME AS PER SET GUIDELINES//POLE 1104_183 TOP BURNT OFF//COD ?? //CUTOUT FAILED CAUSING POLE FIRE, AND ALSO RIDEWAY NEED TO BE CUT. DAMAGE POLE 1104_183//MAP WRONG FO RTHIS SECTION OF LINE, UNSURE OF ACTUAL CUST COUNT, SERVICER TO GET UP WITH MAPPING// VER/DBM IDC XXXX
6815 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-02-05 01:30 | 2014-02-06 09:15 | 1 | 1905 | 4351581 | 1905 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED // MAY HAVE A BAD 15 KVA 12 KV TRANSFORMER AT POLE 162-D0-280 WILL NEED TO SET UP IN ROAD TO CHANGE RELEASED BY CREW 108E02, CREW LOADING XFMR,,ALL POWER RESTORED//COD 1// VER/DBM
6816 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-01-14 11:23 | 2020-01-14 13:00 | 40 | 97 | 4303491 | 1904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO OUTAGE TILL RECLOSER 37830227A00007//COD 40//OFF @ 1123 ON @ 1144 UP TO 37830227B00031//Bad dead end insulators on pole 251-45.Bad dead end insulators on pole 251-45. Recloser on pole 227A-7 opened from 11:23 to 11:44. All power restored from open point 227-31 restored at 13:00. Released by crew 077H20
6817 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2008-03-27 15:10 | 2008-03-28 00:02 | 44 | 532 | 61263-1 | 1904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001202// FUSE OUT ON POLE 69-4042//COD 44//POLETOP BURNT OFF//ISOLATED AT FAULT POLE AND RESTORED ALL BUT 2 CUST @ 1530//CREWS TO REWORK POLE//CHANGING OUT 40/5 POLE. WATER HOLE//TIME ON AT 00:02 VER/PDP IDCC PN4022 XXXX
6818 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-07-18 00:39 | 2015-07-18 02:55 | 14 | 136 | 4904761 | 1904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LINE FUSE OPEN ON POLE 472-20, SPLICE PULLED OUT OF PRIMARY AT POLE 472-61, MADE REPAIRS RESTORED POWER AT 02:55. VER/CRB
6819 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-10-01 08:36 | 2022-10-01 10:35 | 16 | 119 | 4954411 | 1904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | A phase Lat open @ 16C-5.//Bad CSP xfm on pole 16C-5.//Isolated xfm and restored @ 10:35.// No customers on bad xfm.
6820 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-08-10 04:14 | 2016-08-10 12:10 | 4 | 476 | 4756381 | 1904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK IN THE AM AT START OF REGULAR SHIFT PER CALLOUT GUIDELINES, XFORM FUSE OUT ON 69-5064,XFORM BAD OIL ON SIDE OF CAN OLD CSP 25KVA SINGLE BUSH,HAS A XFORM CUTOUT ON POLE NEED CREW TR OK SEND TO B. TACKETT RELEASED BY CREW 078S04,,CREW ON SITE,,,,ALL POWER RESTORED// VER/ ADH
6821 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-09-16 20:30 | 2013-09-17 00:28 | 8 | 238 | 4859101 | 1904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER STEVE BREWER: -NEED 3 MAN CREW--50KVA TRANSFORMER--TRUCK TO POLE--NEED NEW 4/0 RISERS TO SPLIT LOAD ON SECONDARY RELEASED BY CREW 078S07/ FETR 01:00 JEH/ POWER REST.@ 00:28//JEH/CLOSE TICKET IDC XXXX
6822 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-03-06 11:50 | 2013-03-06 15:00 | 10 | 190 | 4881021 | 1900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE BUT DUE TO POLE FIRE I OPENED LINE FUSE ON POLE 117-53 AT 11:50 POLE FIRE DUE TO BAD CUTOUT. LINE CREW ON THE WAY. SHOULD BE BACK ON BY 15:30 LINE FUSE CLOSED BACK IN AT 15:00 EVERYTHING OK. VER/KEP IDC XXXX
6823 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2018-10-20 15:09 | 2018-10-20 23:04 | 4 | 475 | 4273731 | 1900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE MD TO SHOW L/F ON POLE 37820054000020//COD 4//Line fuse is open at pole 37820054000020. Primary dead end pole 37820054000119 is burned off. Need 40/5 pole, dead end material for #2AAA, 15 kva 7200, cutout and bracket. Can use bucket truck. 811 locate #1810200109 Released by crew 079S02
6824 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-11-12 10:39 | 2014-11-12 16:51 | 17 | 372 | 4722241 | 1900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1055 PATROLLING LINE //POLE 117-482 BURNT OFF, LIFTED HOT TAP POLE 117-304. RESTORED 117-175 W/ 30T @11:35, 117-178W/25TPOLE/ 117-482 GROUNDED AND TAGGED TO DDC/CREW ON SITE/V MULLINS CHG TAGS/FETR1730/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1651/PLEASE CLOSE TICKET/THANKS/VEM TRANSFORMER ON 117-304 WAS STILL ON// VER/BOW L3/HFP AJB
6825 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-05-07 16:40 | 2017-05-07 19:50 | 10 | 190 | 4765481 | 1900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL L/F OPENED ON POLE 38830834D00350 @ 1640// FRAMED DOWN ON POLE38830834D00354 AND RESTORED @ 19:50. SH VER/CRB
6826 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-03-15 19:10 | 2021-03-16 01:30 | 5 | 380 | 4338461 | 1900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke no trucks// crew required// luke mccoy
6827 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-04-05 02:05 | 2011-04-05 02:30 | 76 | 25 | 64947-1 | 1900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 64719-1 CREW OPENED RECLOSER TO ALLOW THEM TO SAFELY REPLACE DEFECTIVE CUTOUT COD-76 VER/HFP L3/HFP IDCC TOF INCORRECT DATE 4/5 XXXX
6828 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-08-30 10:30 | 2021-08-30 14:01 | 9 | 211 | 4175431 | 1899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad dead end instulator on pole 1149-148, need 19.9 dead end insulator and 19.9 cutout and arrester, Beuford Napier is coming to assist with repairs, and ROW crew
6829 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-02-06 08:41 | 2008-02-07 16:20 | 1 | 1899 | 52382-1 | 1899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3007904// DONNIE JENT - 3007904// BAD 19.9 XFORMER , COULD BE DAMNAGE TO CUST EQUIPMENT. NEEDS LINE CREW ,THEY HAVE BEEN OUT FROM YESTERDAY AT 3AM ( 2-6-08)3007904// BAD 19.9 XFORMER , COULD BE DAMNAGE TO CUST EQUIPMENT. NEEDS LINE CREW ,THEY HAVE BEEN OUT FROM YESTERDAY AT 3AM ( 2-6-08) RELEASED BY CREW 078S01// BACK ON 1620//// VER/TOM IDC CHANGED START TIME FROM THE 7TH XXXX
6830 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-06-04 19:00 | 2008-06-06 02:39 | 1 | 1899 | 58342-1 | 1899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ASSIGNED TO MIKE COLEMAN AND WES BARKER BAD XFMER VER/KEP
6831 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-07-10 15:19 | 2013-07-10 17:45 | 13 | 146 | 4498061 | 1898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 38821060D00076, PATROLLING LINE. FUSE SIZE IS A 20T.//COD 13// VER/DBM IDC XXXX
6832 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-11-15 06:42 | 2022-11-15 09:20 | 12 | 158 | 4143321 | 1896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored @ 9:20. sh
6833 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-11-04 02:03 | 2021-11-04 12:35 | 3 | 632 | 4055371 | 1896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830332000018 15t lat blown.38830332000089 wire down, #2 pri--crew req-ds110421 Released by crew 078S01 crew on site FETR 13:00 LRM all pwr restored 12:35 LRM
6834 | Pikeville | 3421001 | BREAKS | CITY | 2022-08-20 09:41 | 2022-08-20 16:00 | 5 | 379 | 4767301 | 1895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @220-C2-138, checking. Cutout went bad and burndt the top of the pole off @220-C2-623, this will take a line crew and a manual tree crew, no truck access. The Line fuse cutout @220-C2-623 is also busted. Released by crew 074S05. REPAIRS COMPLETE, ON AT 16:00
6835 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-02-20 04:02 | 2015-02-20 10:21 | 5 | 379 | 4047371 | 1895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA @ POLE 206-1066 NEED LINE CREW TO REPAIR TRUCK OK RELEASED BY CREW 078S05/CREW ENROUTE/VEM/CREW ON SITE/FETR1045/VEM/ONLY 5 CUST ON THIS XFMR/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1021/PLEASE CLOSE TICKET/THANKS/VEM VER/HFP L3/HFP
6836 | Hazard | 3303903 | LESLIE | HALSFORK | 2021-06-11 03:52 | 2021-06-11 11:45 | 4 | 473 | 4712241 | 1892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout GuidelinesReplaced broken cut-out on 37830363000040. Power restored @ 11:45
6837 | Hazard | 3308001 | JACKSON | S.JACKSON | 2019-03-22 16:52 | 2019-03-22 17:36 | 43 | 44 | 4010951 | 1892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | got pole 38831107000040 rotted off . need 40 foot pole pt pin and clevis and spool and three man crew opened line fuse on 38831107000001 /// cod 43 /// off @ 1652 on @ 1736 got pole 38831107000040 rotted off . need 40 foot pole pt pin and clevis and spool and three man crew L3/HFP
6838 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-11-20 19:21 | 2016-11-20 20:47 | 22 | 86 | 4120171 | 1892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | B PHASE LINE FUSE OUT ON POLE 278A-2649( COD-22) . PATROLLED LINE , WAS CLEAR . CLOSED LINE FUSE BACK @ 20:47 . FUSE WAS BROKE . /// VER VIA BUSINESS OBJECTS B PHASE OUTAGE = VER/HFP L3/HFP AJB
6839 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2012-07-12 19:54 | 2012-07-12 23:17 | 17 | 203 | 4702001 | 1891 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT 1137D306..BAD XFMR CUTOUT ON 1137C20 ON HILLSIDE.LIFTED HOT LINE CLAMP W LONG STICK.TROUBLE ISOLATED.//.RE-FUSED LATERAL.PARTIAL RESTORE @ 21:17..SEND TO J REED.THANX..JRV RELEASED BY CREW 080S01 COD-17 ISO LF 38821137D00306 IDC XXXX
6840 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2017-02-04 21:13 | 2017-02-04 22:43 | 21 | 90 | 4358951 | 1890 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPEN TRANSFORMER AT 22:25 AND CLOSE AT 22:43, TRANSFORMER LEAD FAILED CUT BAB AND REMADE CONNECTIONS/// VER/DKM L3/HFP XXXHFP AJB
6841 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2009-02-27 16:30 | 2009-02-27 18:45 | 14 | 135 | 52352-1 | 1890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE 940-65 IS OUT,WILL PATROLBELIEVE ARRESTOR ON POLE 13 FAULTED,TOOK LINE FUSE OUT.RE-FUSED,ALL OK AFTERWARDS//VER/CRB IDC XXXX
6842 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-03-07 15:15 | 2008-03-07 19:45 | 7 | 270 | 54678-1 | 1890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 3403003//PRI. UNDER GROUND OUT.///25 KVA PAD MOUNT TRANSFORMER BAD. PAD 37830024A21527. VER/HFP IDC XXXX
6843 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-05-04 12:58 | 2014-05-04 15:13 | 14 | 135 | 4661451 | 1890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ 185-149 NEED LINE CREW TO REPLACE RELEASED BY CREW 078S05/ FETR 15:45/ JEH/ REPAIRS COMPLETE POWER REST. @ 15:13//JEH// PLEASE CLOSE TICKET VER/SEF L3/HFP IDC XXXX
6844 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2012-06-19 17:36 | 2012-06-19 20:45 | 10 | 189 | 4932881 | 1890 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1099-85 SEC. RISER MELTED OFF TRANS SEND NOTE TO TEC. TRANS NEEDS TO BE CUT IN LINE BECAUSE OF LOAD IN FRONT OF 312 7TH. AVE RELEASED BY CREW 078S08 COD-10 ISO TF 39831099A20085 IDC XXXX
6845 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-07-22 12:54 | 2011-07-22 16:50 | 8 | 236 | 4579001 | 1888 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PART POWER ON UNDERGROUND TRANS. 1148-650 4-CUST OUT RELEASED BY CREW 078S08//CREW ON SITE FETR 23:30// PRTOLLIVER//REPAIRED 350 UG POWER RESTORED AT 16:50 PR TOLLIVER RELEASED BY CREW 078H03 VER/DKG L3/DKG
6846 | Hazard | 3303902 | LESLIE | WOOTON | 2016-12-25 15:12 | 2016-12-25 17:10 | 16 | 118 | 4236791 | 1888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830364000145/ ISO 37830389A00085/ COD 16/ VER/BOW
6847 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2018-08-31 20:23 | 2018-08-31 22:14 | 17 | 111 | 4025961 | 1887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found a bad cutout on pole 321-424 and replaced it. Power restored at step down pole 321-568 @ 22:14
6848 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2017-11-19 00:22 | 2017-11-19 16:05 | 2 | 943 | 4577371 | 1886 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o g shouse
6849 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-05-17 13:38 | 2009-05-17 19:55 | 5 | 377 | 61131-1 | 1885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409303//FEEDER OUTAGE IS ON ANOTHER TICKET// DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. REPAIR IN PROGRESS. REPAIRS COMPLETE. RESTORED AT 19:55. SH//VER/CRB IDCC TON1958 XXXX
6850 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-07-12 08:54 | 2011-07-12 16:45 | 4 | 471 | 4527311 | 1884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR IS BURNED UP. I AM GOING TO CHANGE DOOR.//COD 4// VER/DBM
6851 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-07-12 06:38 | 2010-07-12 09:15 | 12 | 157 | 65185-1 | 1884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLING LINE, BAD LIGHT LIGHTNING ARRESTOR ON POLE 158-23 COD-12 VER/HFP L3/HFP IDC XXXX
6852 | Whitesburg | 3312902 | JENKINS | JENKINS | 2017-04-25 15:46 | 2017-04-25 21:00 | 6 | 314 | 4682131 | 1884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, NEED TWO MEN ONE A , ONE ASSIST. 25 KVA 7200//SERVICER SAYS COD IS 6// VER/CRB L3/HFP HFPC CNT3
6853 | Whitesburg | 3409503 | BURDINE | JENKINS | 2017-04-25 15:46 | 2017-04-25 21:00 | 6 | 314 | 4682131 | 1884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, NEED TWO MEN ONE A , ONE ASSIST. 25 KVA 7200//SERVICER SAYS COD IS 6// VER/CRB L3/HFP HFPC CNT3
6854 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-06-24 19:43 | 2011-06-24 22:20 | 12 | 157 | 4411951 | 1884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE BLOWN ON POLE 102-5.. PATROLLING LINES.. RESAGGED PRIMARY THAT WAS LOW FROM PL 102-46 TO 102-47.. CLOSED 10T FUSE BACK IN AT 22:20 RESTORED//COD 12// VER/DBM IDC XXXX
6855 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-05-20 06:08 | 2009-05-20 06:41 | 57 | 33 | H50920-1 | 1881 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN POLE 1058-401,SAMMONS IS GETTING HELP.// COD-77 // OPENED RECL 1058-370 @ 06:08 // COD-57 //IN ORDER TO PUT WIRE UP.MADE REPAIRS AND RESTORED AT 06:41.HAD BURNED IN TWO AT CONNECTION OF SWITCHES LETTING 1 PHASE FALL TO GROUND// ALSO SEE OUTAGE #50920-1 VER/LDA IDCC PN68, CDC88 XXXX
6856 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-03-12 07:39 | 2014-03-12 10:30 | 11 | 171 | 4469751 | 1881 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 19.9 KV CUTOUT COD-11 ISO LF 37830387D00285 VER/HFP L3/HFP IDC XXXX
6857 | Hazard | 3301401 | COMBS | COMBS | 2013-08-12 19:24 | 2013-08-12 22:15 | 11 | 171 | 4656861 | 1881 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT OPEN AT POLE 37830271C00057 OPENED TRANSFORMER ON 271-57 AT 21:55 CLOSED AT 22:15. CLOSED FUSE ON POLE 271-57 AT 22:15... POWER RESTORED. VER/SEF
6858 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-04-22 06:10 | 2021-04-22 12:30 | 10 | 380 | 4469921 | 1880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA on pole 129-D-67, manual CSP. Released by crew 077S04, open tap on 129-67 to get safe spacing to change xfmr @11:30 ALL CUST RESTORED @ 1230
6859 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-06-05 07:22 | 2017-06-05 08:56 | 20 | 94 | 4906531 | 1880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A BAD TRANSFORMER CUTOUT AT POLE 38821137D00566/ ISO38821137D00307 / COD 20/ SJG
6860 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-06-17 01:09 | 2019-06-17 16:49 | 2 | 940 | 4519691 | 1880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kVA xfmrbad 7.2 kv 25kva 120/240 volt transformer / four man crew , no truck to pole , will require yard dog, swampy Released by crew 078M06
6861 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2009-06-13 08:46 | 2009-06-13 16:36 | 4 | 470 | 60964-1 | 1880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW ON SITE REPAIRIN UDERGROUND CABLE . URD POWER ON MAPS OR INCORRECT ONLY 4 CC OUT FROM A NEW INSTALLED 50 KVA PM. TR IN PLACE OF PED # 937 FEEDING FROM J BOX 785-C-2-9001 MAPS VERY MESSED UP HERE NEED ENIGINEER TO CORRECT VER/KEP L3/KEP TRS 785-893 AND 785-898 ARE OUT BAD CABLE BETWEEN JB 9001 AND NEW P.M IN SERVICE IN PLACED WHERE PED SAME AS 60117-1 COD-11
6862 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-05-24 14:13 | 2020-05-24 17:21 | 10 | 188 | 4896791 | 1880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout .changing
6863 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2008-01-29 08:40 | 2008-01-29 11:12 | 17 | 152 | 60581-1 | 1879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117602//RECLOSER 38830114000251 OPEN INSTEAD OF STEP-DOWN / SERVICER PATROLING/3117602//FOUND BAD CUT-OUT ON POLE114-74 CLOSED RECLOSER AT 1025/COMPLETED REPAIRS AND CLOSED TRANS AT 1112 VER/KEP IDC XXXX
6864 | Pikeville | 3421001 | BREAKS | CITY | 2016-04-09 05:11 | 2016-04-09 07:48 | 24 | 157 | 4073511 | 1878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 220D-389...PATROLLED LINE AND FOUND TOP OF POLE 220-871 BURNT OFF..REPAIRS MADE PUT HOTLINE CLAMP BACK ON @ 07:48.. RELEASED BY CREW 074S01//COD 24 AJB
6865 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-02-07 05:52 | 2016-02-07 10:20 | 7 | 268 | 4681551 | 1876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 12 KV C/O & ARRESTOR. TRK ACC. BETWEN 4442 & 4432 SHERWOOD RELEASED BY CREW 078S07 VER/KEP L3/HFP XXXHFP
6866 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2010-11-26 02:30 | 2010-11-26 03:37 | 28 | 67 | 59703-1 | 1876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1122D-99 (SEE ORDER 59694-1)//COD 28 // VER/DBM IDC XXXX
6867 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2008-05-28 19:36 | 2008-05-28 20:43 | 28 | 67 | 52397-1 | 1876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE #417-254 TOP POLE BURNED OFF... ISOLATE ON POLE 417-38 RESTORED POWER AT 2043 WILL LEAVE TAP OFF UNTIL TOMORROW TO CHANGE POLE /// PAUL PRATT & RICK MAGGARD TALKED TO CUSTOMER A ND THEY SAID IT WOULD BE OK TO REPLACE POLE TOMORROW 05/29. OPS ORDER CREATED BY PAUL AND POWERON ORDER CLOSED OUT. VER/HFP IDC XXXX
6868 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-09-02 12:08 | 2014-09-02 13:15 | 28 | 67 | 4448301 | 1876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 30T RESTORED VER/ARN L3/HFP AJB
6869 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-10-11 09:02 | 2013-10-11 13:30 | 7 | 268 | 4929621 | 1876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD ON POLE 97-144. TIM HALL IS SENDING CREW TO HELP.//TRANSFORMER IS BAD ON POLE 97-144. TIM HALL IS SENDING CREW TO HELP. WE CHANGED TRANS. VER/CRB L/3 CRB
6870 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2018-08-09 16:30 | 2018-08-09 18:35 | 15 | 125 | 4934521 | 1875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Broken neutral at pole, Fixed. All power restored/ ISO 38830045B12068/ COD 15
6871 | Hazard | 3310502 | HADDIX | CANOE | 2008-11-17 09:05 | 2008-11-17 15:20 | 5 | 375 | 65874-1 | 1875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502// COD-5 // STS WR # 27313718 // TOP OF POLE BURNT OFF AT POLE 37830051000041CALLED BRUCE WITH INFO--POLE BURNT OFF- RELEASED BY CREW 077S06 REPLACED POLE AND RESTORED POWER AT 1520 JEFF COMBS VER/LDA IDC XXXX
6872 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-01-12 08:17 | 2009-01-12 11:45 | 9 | 208 | 54370-1 | 1872 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3401302//CUTOUT IS BROKE ON TRANSFORMER BANK I WILL NEED ONE MAN CUTOUT AND FLAGGERS RELEASED BY CREW 074S07 COD-9 VER/KEP L3/KEP IDCC CNT1 XXXX
6873 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2021-06-30 12:03 | 2021-06-30 14:00 | 16 | 117 | 4826821 | 1872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Broken fuse, restored @ 14:00
6874 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2021-12-31 16:43 | 2021-12-31 17:55 | 26 | 72 | 4242361 | 1872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ht and basket burnt off at pole 1122-109 repairs made lf in at 17:55 complete
6875 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-12-28 08:03 | 2021-12-28 11:31 | 9 | 208 | 4231231 | 1872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | in front of 2002 washington st at pole 1147--5096 bad 50kva crew required truck ok Released by crew 078S09//arrived RM xfm replaced volatge check good please close tic RM
6876 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2022-03-26 11:38 | 2022-03-26 14:45 | 10 | 187 | 4676701 | 1870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 35-5 making repairs.
6877 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-03-29 14:40 | 2020-03-29 16:05 | 22 | 85 | 4522781 | 1870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | crew required, pole needs to be changed out, pole was still on fire due to house fire last night. have got fire out . please send this to paul layne. he has info Released by crew 074S04//power restored at 16:05, opened L/F at 14:40
6878 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-08-09 01:00 | 2008-08-09 02:50 | 17 | 110 | H50425-1 | 1870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3403003// HAD TO OPEN LINE FUSE TO REPLACE TRANSFORMER. WILL HAVE OFF FOR ABOUT ONE AND A HALF HOURS // COD-17 // SEE OUTAGE 50410-1 // VER/LDA IDCC TOF2102 XXXX
6879 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-09-09 00:18 | 2014-09-09 04:45 | 7 | 267 | 4481701 | 1869 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL DISPATCH DURING NORMAL HOURSPOLE 69-4699 6T TRANS FUSE BROKE REPAIRED VER/ARN AJB
6880 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2022-08-12 16:38 | 2022-08-13 01:40 | 4 | 542 | 4734531 | 1868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | dip pole open at38830045D16184 crew required needs 7200 parking stands Released by crew 078S09//CLOSED DIP FUSE IN @ 2040// Repairs made, closed at 01:40. Ticket complete.
6881 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2014-11-24 19:21 | 2014-11-25 10:55 | 2 | 934 | 4777271 | 1868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE 35-5 FOREIGN ROTTED OFF -- NEED TO GO BACK WITH 40-5 ---- POLE255-81 TAGED TO DDC--- POLE 255-107 GROUND INSTALLED--CREW REQ. COD-2 ISO LF 38830255000081 VER/HFP L3/HFP
6882 | Hazard | 3303902 | LESLIE | WOOTON | 2011-09-29 02:52 | 2011-09-29 09:05 | 5 | 373 | 4930231 | 1865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH AT REG WK TIME./WILL DISPATCH AT REG WK TIME.REPLACED BAD CUTOUT VER/KEP IDC XXXX
6883 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-11-25 04:13 | 2013-11-25 07:40 | 9 | 207 | 4071661 | 1863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 68-757 BAD LA POLE 68-498 40T INSTALLED LINE FUSE ON 68-756 25T POLE 68-759 15T//COD 9//MD FILED ON NEW LINE FUSES//NO AED ENTRY REQUIRED, ARRESTER WAS REPLACED VER/HFP L3/HFP
6884 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-03-22 02:41 | 2010-03-22 06:08 | 9 | 207 | 52449-1 | 1863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE RECLOSER OPEN ONLY ... TRANSFORMER CUTOUT FAILED ... REPLACED CUOUT, ALL WORK COMPLETE / GXJ 9 CUSTOMERS IDCC CNT67 XXXX
6885 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2010-11-23 07:12 | 2010-11-23 09:25 | 14 | 133 | 58873-1 | 1862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 795-92 TAKING OUT LATERAL FUSE/CUTOUT CHANGED //REFUSED LATERAL AT 9:25//COMPLETE//EM,//VER/CRB IDC XXXX
6886 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-02-16 07:40 | 2018-02-16 23:11 | 2 | 931 | 4848281 | 1862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no truck in yard ,,454-7597 BROKE 7200 xfr cutout Released by crew 078S05 replaced cut out xfmr back in at 23:11 Released by crew 078Q09
6887 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-12 11:42 | 2015-02-12 13:20 | 19 | 98 | 4010381 | 1862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LOW SIDE FUSE ON STEPDOWN IS BLOWN ON POLE 38830791C00148//PATROLING//CUTOUT BROKE ON POLE 38830791A00044////REPAIRS MADE//RESTORED AT 13:20//COMPLETE//EM VER/CRB L3/HFP XXX
6888 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-04-03 08:44 | 2016-04-03 11:50 | 10 | 186 | 4040201 | 1860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAVE A HOTTAP LEADE BURNED OFF @ POLE # 38830760B00201 .WILL OPEN LINE FUSE ON POLE #38830760B00200 & MAKE REPAIRS. OPENED ON 200 @ 11:30 MADE REPAIRS & CLOSED @ 11:50 /// SEE H4040201 FOR FUSE OUTAGE FOR 4 CUST VER/HFP L3/HFP
6889 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-05-16 20:49 | 2010-05-16 21:20 | 60 | 31 | H63175-2 | 1860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PART OF 63175-1, HAD TO RE-OPEN N.O. SWS 572-94 IN ORDER TO MAKE LOOPS BACK. THIS RE-OUTAGED 60 CUSTOMERS WHICH HAD PREVIOUSLY BEEN RESTORED BY BACKFEEDING THROUGH THESE SWITCHES//COD 60// VER/DBM IDC XXXX
6890 | Cannonsburg | 3001401 | LOUISA | CITY | 2010-02-09 08:58 | 2010-02-09 10:00 | 30 | 62 | 54177-1 | 1860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN ARRESTOR,,,,,,BACK ON POWER RESTORED //A PHASE ONLY.//VER/CRB IDC XXXX
6891 | Hazard | 3310502 | HADDIX | CANOE | 2016-08-17 19:10 | 2016-08-18 10:40 | 2 | 930 | 4806601 | 1860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9KV TRANSFORMER,TRUCK ACCESSIBLE,NEED TO WAIT TIL TOMORROW RELEASED BY CREW 077H07 REPLACED TRANSFORMER POWER RESTORED AT 10:40 VER/AWD
6892 | Hazard | 3309302 | VICCO | JEFF | 2009-06-03 04:00 | 2009-06-03 09:10 | 6 | 310 | 63680-1 | 1860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 346C-411== ARRESTER BAD ON POLE 346C-470 == REFUSED ==POWER OK // COD 6 IDCC PN470, CNT4 XXXX
6893 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2008-12-13 12:09 | 2008-12-13 14:58 | 11 | 169 | 57982-1 | 1859 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3401302// LINE LAYING TREES THAT ARE GROWN UNDER LINE TRIMED TREES ALSO FOUND BAD ARRESTOR ON POLE 380-93 REPLACED 30 AMP FUSE ON POLE 380-20//COD 11// VER/DBM L3/KEP IDC XXXX
6894 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-11-18 20:31 | 2017-11-19 12:00 | 2 | 929 | 4571091 | 1858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answer voicemail..cutout broken ..line fuse blown.. Released by crew 076S01.REPLACED CUTOUT power back on!!!!
6895 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-03-12 21:41 | 2022-03-13 13:10 | 2 | 929 | 4617691 | 1858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | broken de insulator 19.9. need big bucket and could possibly use small bucket// only line fuse 37830214A00074 toward pole 37830214A00075/ power restored 1310
6896 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-04-06 19:50 | 2018-04-07 10:49 | 4 | 899 | 4197431 | 1858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answer line fuse door burn up 246-52 need big bucket maybe bad cutout ,xform fuse blew on 246-102 never found any wire down Released by crew 078S04--burnt up door--bad location on pole--having to relocate CO--open xfmr @ 10:19---all repairs made--closed LF & xfmr @ 10:49---tbl tkt comp
6897 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-05-31 21:16 | 2015-06-01 12:44 | 2 | 928 | 4490921 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS AND GROUNDED/BAD CUTOUT ON POLE265-67 , NO POWER OUT @ THIS TIME . POLE IS SMOKING . CUT LOOP ON POLE 265-66 TO CLEAR BAD CUTOUT .IN CASE POLE 265-67 FALLS . ONLY 1 CUST OUT . CUT LOOP @ 12:30AM . GOING TO HOLD UNTIL DAYLIGHT . WILL TAKE LINE CREW ,CUTOUT & TBRACKET LIGHTNING ARRESTER . DEADEND POLE TOP EXT. POLE IS MANUEL RELEASED BY CREW 075H04
6898 | Pikeville | 3408401 | KIMPER | LONGFORK | 2009-08-14 17:36 | 2009-08-15 09:04 | 2 | 928 | 58439-1 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP CREW WILL WORK IN THE AM ON 8-15-09 DUE TO UNSAFE CONDITIONS. WE RAN A PRIMARY TAP TO SERVE METER 533745411 WE LEFT ONE METER OUT UNTIL ROUTE TO THE POLE IS CLEARED ,TO SAFELY CHANGE XFMR. ON AT 9:04 /// COD-2 ISO TF 37820005000112 L3/HFP IDC XXXX
6899 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-06-02 12:53 | 2013-06-02 13:22 | 64 | 29 | 4209361 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO ORDER 4207791, FIELLDS OPENED LINE FUSE TO CHANGE INSULATORS COD-64 ISO LF 38830984000048 VER/HFP L3/HFP IDC XXXX
6900 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2017-01-31 01:16 | 2017-01-31 09:00 | 4 | 464 | 4343231 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 449-55, DIDNT TAKE RECLOSER OUT . REPLACED BROKEN CUTOUT POWER RESTORED AT 9:00/ ISO 37830449A40055/ COD 4 ***CCC MD DONE/ VER/BOW L3/HFP XXXHFP
6901 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2016-03-02 19:36 | 2016-03-03 11:04 | 2 | 928 | 4804601 | 1856 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS ON 148-48 NO VOLTAGE ON ONE LEG NON TRK APP NEED TWO MAN MANUAL TREE CREW CUSTOMERS SAID IT WAS OK TO WAIT TILL MORNING TIM HALL WILL SEND CREW IN MORNING RELEASED BY CREW 079H03// CREWS ON SITE /// REPLACED TRANSFORMER AND RESTORED POWER AT 11:04TIM MCCOY// VER/ ADH// VER/ ADH
6902 | Pikeville | 3413402 | GARRETT | LACKEY | 2016-06-24 18:49 | 2016-06-25 10:17 | 2 | 928 | 4467081 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPAIRS MADE ORDER COMPLETE.HAD TAPS OFF FROM 10:07- 10:12// VER/ ADH
6903 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2019-11-10 13:12 | 2019-11-10 20:56 | 4 | 464 | 4017001 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER
6904 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-08-18 14:08 | 2013-08-18 18:00 | 8 | 232 | 4676871 | 1856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 117-45 NUMBER 4 ACSR BURNT DOWN ACROSS SHOPS CK. NEED 4-MAN CREW AND FLAGGERS POLE 117-45 40T OPENED TRANS ON POLE 117-45 1 CUST. OUT RELEASED BY CREW 078S08//COD 8 (+ 1 SEE ORDER H4676871)// VER/DBM IDC XXXX
6905 | Hazard | 3303902 | LESLIE | WOOTON | 2015-01-09 07:12 | 2015-01-09 11:37 | 7 | 265 | 4922851 | 1855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN 1 SPAN 230 ==== NEED LINE CREW AND SOME 2 WIRE AND BIG BUCKET ROW OK === REPAIRED LINE ==== REFUSED LINE ==== POWER OK/ WIRE WAS ROTTEN/ ISO 37830462000025/ COD 7 VER/CRB -- MD ENTERED - L3/HFP XXX AJB
6906 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2012-07-13 08:04 | 2012-07-13 11:30 | 9 | 206 | 4706741 | 1854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND BAD RIGHT OF WAY, ROW CREW ENROUTE. ---- TRIMMED TREE, REPLACED CUTOUT AND ARRESTOR, POWER RESTORED.//COD 9 IDC XXXX
6907 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2020-12-28 14:07 | 2020-12-28 15:56 | 17 | 109 | 4831181 | 1853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | wire pulled loose from sleeve went back and opened switch at 501-3 @ 1518 to make repairs closed @1556 Released by crew 078S11. LR-The 1st all out call came in at 14:07
6908 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-06-14 11:41 | 2008-06-14 16:45 | 7 | 304 | 64589-1 | 1853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000701//LIFTED HOT TAP ON POLE#1072-68 CLOSED IN FUSE#1048-3// HAVE FIRE PUT OUT, AND NEED 404 POLE, AND CUTOUT AND ARRESTOR, EVERYTHING ELSE WILL WORK BACK, HAVE HOT TAP LIFTED ON POLE 1072-68, CREW REQUIRED, AND CAN USE TRUCKS ON THIS RELEASED BY CREW 078S06-----------------------------POWER ON @ 16:42//VER/CRB
6909 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-07-26 15:05 | 2021-07-26 16:19 | 25 | 74 | 4959151 | 1850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cutout on 429-359//// apr at 1619 close ticket
6910 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2009-01-16 07:25 | 2009-01-16 10:30 | 10 | 185 | 55578-1 | 1850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28092337 // THIS THE SECOND TIME FUSE HAS BLOWN WITH IN 3 HRS COD-10 L3/HFP
6911 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-12-17 17:07 | 2019-12-17 17:17 | 185 | 10 | 4161661 | 1850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 37830579D00151//NO OUTAGE TILL//OPENED RECLOSER 37830531A30160 @ 1707 //COD 185 CLOSED @ 1717
6912 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2019-10-17 08:38 | 2019-10-17 11:15 | 17 | 157 | 4158681 | 1849 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Only middle phase is open. open other 2 solid blades on pole 448-517 at 10:00 bad solid blade cutout L3/HFP
6913 | Pikeville | 3413401 | GARRETT | GARRETT | 2008-12-21 22:39 | 2008-12-22 02:30 | 8 | 231 | 62030-1 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | COD- 8 CCC 20T FUSE OUT ON POLE 170-6. I FOUND A POLE DOWN POLE 1145-110. DONT SERVE ENYTHING. I ISO LINE AT POLE 1145-24. FUSED UP EVERYTHING OK. POLE 1145-110 HAS TRANSFORMER ON IT. SEND COPY OF THIS TO RON RYE ENG PIKVILLE. TO REMOVE POLE AND OLD SECTION OF LINE OR SET NEW POLE. VER/HFP L3/KEP IDCC CNT15 XXXX
6914 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-10-28 23:08 | 2010-10-29 00:25 | 24 | 77 | 66430-1 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#37541313 7200 PRI. BURNT OFF TOP OF CUTOUT ( REPLACED CUTOUT) ON STEPDOWN VER/PDP IDC XXXX
6915 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-11-12 16:18 | 2013-11-12 20:09 | 8 | 231 | 4033051 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE 1031-115 IS OUT,WILL PTRL///////NEED CREW,MAT HANDLER,POLE EXTENSION OR X ARMS FOR A DEAD-END POLE.AND A CUTOUT/ARRESTOR COMBO/////MADE NECESSARY REPAIRS AND RESTORED VER/CRB L3/HFP
6916 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-06-07 23:44 | 2008-06-08 10:00 | 3 | 616 | 59996-1 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR CHANGE OUT IN THE MORNING RELEASED BY CREW 075H01 VER/HFP IDCC CNT1 XXXX
6917 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-01-12 21:47 | 2018-01-13 02:55 | 6 | 308 | 4740361 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad trans on 32C2 25 KVA 19.9 trk app send ticket to Joey Reed Released by crew 079H03.Replaced transformer
6918 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2014-10-29 15:11 | 2014-10-29 19:35 | 7 | 264 | 4671931 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | TRANSFORMER 80-86/ UNDERGROUND PEDESTAL/ 1 LEG-PHASE OUT/ CREW REQUIREDPART POWER OFF XFMR OR PEDESTAL, ONE HOT LEG IS OFF. CANT GET INTO U G XFMR, LOCK CLOGGED WITH MUD. NEED LINE CREW. 178-A-374, 8980 IS PADMOUNTPART POWER OFF XFMR OR PEDESTAL, ONE HOT LEG IS OFF. CANT GET INTO U G XFMR, LOCK CLOGGED WITH MUD. NEED LINE CREW./ ISO 37830178A00368/ COD 7// VER/BOW
6919 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-07-13 12:40 | 2010-07-13 13:57 | 24 | 77 | 66033-1 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S09// LEAD OUT OF CUTOUT-WILL HAVEE TO OPEN OTHER FUSE ON POLE TO MAKE REPAIRS (SEE 66108-1 FOR OTHER OUTAGE) COD-24 VER/HFP L3/HFP IDC XXXX
6920 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-28 19:48 | 2011-06-28 20:12 | 77 | 24 | H4431661-1 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 142-144 B PHASE IS OPEN COD-144//POLE 142-17 IN FRONT OF FIRE DEPT, BASKET ON C PHASE, BROKE///PL. 142-17 #2 SOLID CU. FAILED @ BASKET( AL BASKET ON CU. THIS IS NOT ACCEPTABLE PRACTICE) TOOK OUTAGE ON A&C PHASE RECLOSER@ 19:48 COD-77 TO MAKE REPAIRS/ REPAIRS COMPLETE ALL POWER RESTORED @ 20:12 J. HEMLEPP & CREW 078H05 VER/KEP IDC XXXX
6921 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-04-03 10:24 | 2015-04-03 14:15 | 8 | 231 | 4263631 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, BAD CUTOUT ON POLE 205-444, WILL NEED 1 MAN, MANUEL RELEASED BY CREW 077S02PATROLLING LINE, BAD CUTOUT ON POLE 205-444, WILL NEED 1 MAN, MANUEL . ALL POWER RESTORED//COD 8// VER/DBM L3/DKGXXX
6922 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-11-10 13:44 | 2009-11-10 14:50 | 28 | 66 | 55703-1 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 32616890 POLE 1123-1518 50T LINE FUSE BROKE IDC XXXX
6923 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-07-28 05:57 | 2017-07-28 08:45 | 11 | 168 | 4191981 | 1848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE CUTOUT BROKE ON BANK POLE 47-D-466, WILL HAVE TO OPEN OTHER 2 TRANS. TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. C PHASE C/O WAS ALSO BROKE, OPENED UP BANK @0818, PUT BACK IN @0845.//LF C PHASE WAS ALSO OPEN 37830047D00166 //TOTAL COD 11// VER/CRB L3/HFP XXXHFP
6924 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-08-22 22:57 | 2014-08-23 01:19 | 13 | 142 | 4409371 | 1846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F BLOWN ON 37830072A00278// CUTOUT BROKE ON 37830072A00099//WILL CHANGE CUTOUT // POWER RESTORED @ 01:19// 8-23// COD 13// VER/ ADH
6925 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-05-01 23:30 | 2011-05-02 00:41 | 26 | 71 | 53360-1 | 1846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND OLD HOT TAP JUMPER INSTALLED ON TOP OF B PHASE LINE FUSE, THAT WAS ARCHING, I OPEN UP LINE FUSE AT 2330, AND THIS WILL REQUIRE CREW TO MAKE REPAIRS, WILL NEED HOT TAP AND COPPER WIRE, RELEASED BY CREW 078S06/CREW ON SITE/FETR0100/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0041/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDC LOOKS LIKE PH B ONLY CHANGED COUNT FROM 31 XXXX
6926 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-06-05 22:25 | 2020-06-06 13:48 | 2 | 923 | 4967601 | 1846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA transformer need 4 man line crew and row crew to cut path manual 7200V Released by crew 077S03 Released by crew 077H09// TODD DAY ON SITE // REPAIRED AND RESTORED @1348
6927 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-11-29 12:58 | 2010-11-29 15:20 | 13 | 142 | 60627-1 | 1846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEED PRIMARY AND PRIMARY NEUTRAL RESAGED FROM POLE 186-192 TO 186-195, TRUCKS TO POLE 186-192. NEED LINE CREW. RELEASED BY CREW 078S01//COD 13// VER/DBM IDC XXXX
6928 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-02-11 05:32 | 2012-02-11 07:35 | 15 | 123 | 4333471 | 1845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IDCC CDC83 XXXX
6929 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-10-06 16:51 | 2014-10-06 20:00 | 25 | 189 | 4559491 | 1845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE ON 429-27 IS OPEN PATROLLING LINE, FOUND POLE 429-2013 BURNT OFF, ISOLATED TAGGED AND GROUNDED TO BILL F ON 429-303. REFUSED 429-27 AT 1800 ONE CUSTOMER OFF/// ISO 38830429B00027/// COD 25 IDCC TON2000 STEP ONE XXXX AJB
6930 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-03-22 14:43 | 2011-03-22 16:46 | 15 | 123 | 56763-1 | 1845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 25T LINE FUSE OUT ON POLE 38830094D16016-PATROLING LINE--REPLACED BAD ARRESTOR ON POLE 38830094D1601 -- SEND TO ENGINEERING -- CLEARANCE VIOLATION ON POLE 38830094D16013 ENTERED MD...HFP COD-15 ISO LF 38830094D16016 VER/HFP L3/HFP IDCC PN6007 XXXX
6931 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-05-19 02:05 | 2015-05-19 09:46 | 4 | 461 | 4443891 | 1844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK DURING NORMAL WORK HOURS ACCORDING TO CALLOUT GUIDE LINES,XFORM FUSE BROKE REFUSE POWER RESTORED 09;26,ON POLE 140-212 COD-4 ISO TF 38830140B00212 DELETE LAST REST STEP IN HOIS - HAD TO OPEN FUSE TO CLEAR STRANDED CALLS ON MAP VER/HFP L3/HFP
6932 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-06-21 06:54 | 2011-06-21 14:35 | 4 | 461 | 4359701 | 1844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACED TRANS. IDCC PN26, CNT27 XXXX
6933 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-05-03 10:51 | 2011-05-03 12:20 | 36 | 89 | 4000831 | 1844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR 3 9803284 // CUTOUT BROKEN ON POLE 175-140, REENERGIZED REC. ON POLE 37830151000054 AT 1140CUTOUT BROKEN ON POLE 175-140, REENERGIZED REC. ON POLE 37830151000054 AT 1140 ---ALL POWER RESTORED AT 1220. RELEASED BY CREW 077S04 COD-36 ISO OCR 37830151000054 VER/HFP L3/HFP IDC DCMT XXXX
6934 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-12-21 19:12 | 2015-12-22 01:20 | 5 | 368 | 4549131 | 1840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT FAILED ON 1138-B-33 BURNT TOP OF POLE OFF POLE TOP HANGING BY GRD WIRE NTA UP ON BANK CAN ISOLATE TRANS AND JUST MAKE REPAIRS ON PRIMARY CONDUCTOR RESTORED POWER @01:20//COD 5// VER/DBM
6935 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-12-15 10:06 | 2018-12-15 13:10 | 10 | 184 | 4567841 | 1840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Line fuse open @210-27, checking. Dead end insulator bad on pole 210-112, will be changing out. Changed out dead end and refused @1310. ¦¦¦¦¦ L3/HFP
6936 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-03-29 13:45 | 2020-03-29 21:25 | 4 | 460 | 4526031 | 1840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Open wire secondary neutral down from 38830044C14013, to 38830044C14099. Trucks to pole, crew required. Transformer opened at 14:45. #2acsr, Wire up, transformer fuse back in at 21:25 Released by crew 078S02
6937 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-01-12 13:56 | 2008-01-12 17:00 | 10 | 184 | 56277-1 | 1840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2206403//FOUND BAD ARRESTER ON POLE 189-23//COD 10// VER/DBM IDC XXXX
6938 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2008-04-21 14:45 | 2008-04-21 15:39 | 34 | 54 | H1100513-1 | 1836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE RECLOSER LOCKED OUT - 31 CUST ON SITE, XARM BURNT OFF, ONE PHASE DOWN, CALLED R MARCUM FOR HELP// JOEY REED ALSO LOGGED ON TROUBLE ORDER//, PULLED OTHER TWO PHASES OFF AT 1445// A PHASE OUT ENTIRE TIME B/C OUT FROM 1445 UNTIL CLOSED // A (AC/ABC)=34 // B= 14 // C=9 TOTAL COD = 57 - OTHER 23 CUTOMER OUTAGED ON DUPLICATE ORDER H1100513-1 // VER/TOM IDC XXXX
6939 | Hazard | 3302703 | HAZARD | HAZARD | 2011-01-09 08:51 | 2011-01-09 12:15 | 9 | 204 | 60078-1 | 1836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT.---BAD 25 KVA TRANSFORMER.//VER/CRB IDC XXXX
6940 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-04-19 13:03 | 2014-04-19 20:42 | 4 | 459 | 4618561 | 1836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST. HAS 92V ON EACH HOT LEG AND 187V ACROSS, FUSE BLOWN ON XFMR BANK. 4TH TIME ITS BLOWN, NEED TO CHANGE OUT 50KV 7200, MANUAL NEED POLE JIB. GATE AT SCHOOL HAS COMPANY LOCK ON IT, GO IN GATE ON STRONGS BR. NEED R/W CREW MANUAL, NEED 4 MAN LINE CREW. FORMAN, 2 AS, 1 COR D. BEHIND SCHOOL ON HILL! // ARCOS @ 0800 - P.HICKMAN, R.RICE, M.EMBERTON, B. CLEMONS// OUT - 1100 TO 1355 ON 4-20-14 //VER/GAH
6941 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2014-09-01 23:07 | 2014-09-01 23:41 | 54 | 34 | 4446531 | 1836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | EDDIE OPENING RECLOSER TO SAFELY REPLACE CUTOUT RELATED TO TICKET 4446211 OFF 2307 ON 2341 VER/SEF L3/HFP AJB
6942 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2021-12-08 15:17 | 2021-12-08 15:23 | 306 | 6 | 4162751 | 1836 | TRANSMISSION LINE | EQUIPMENT FAILURE | CAPACITOR | DOL 1168245 Temporary Coalton Station Outage to Isolate failed 69kV CAP Bank AA at Coalton
6943 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2018-03-19 02:55 | 2018-03-19 09:02 | 5 | 367 | 4025391 | 1835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | will work at start time 3-19-18/. 50 kva had a 6t fuse melted. replaced with correct size.
6944 | Hazard | 3310502 | HADDIX | CANOE | 2021-09-28 13:44 | 2021-09-28 18:06 | 7 | 262 | 4299801 | 1834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | on pole 192-22 wire came off insulator, got tim smith crew coming to help . pole up on side of mountian On @ 1806
6945 | Hazard | 3309302 | VICCO | JEFF | 2021-10-03 09:11 | 2021-10-03 11:32 | 13 | 141 | 4311751 | 1833 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 346D/196 guy wire wsa on top of transformer cutout blowing line fuse re/ pulled guy and moved cutout power on
6946 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-11-29 05:57 | 2016-11-29 13:35 | 4 | 458 | 4139851 | 1832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1013-211,ISOLATED,TRUCK APPROACH, POWER ON @ 08:27,10AMP FUSE BLEW ON TAP POLE 38821013C00206 @ 0827 (3 CUST) . 38821013C00211 POWER RESTORED AT 13:35 ( 1 CUST)
6947 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-11-18 07:17 | 2011-11-18 11:06 | 8 | 229 | 4089291 | 1832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 SPAN OF WIRE DOWN RELEASED BY CREW 077S10 PUT WIRE UP AND RESTORED POWER AT 1106 JKC ///VER/CRB IDC XXXX
6948 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-05-01 05:25 | 2016-05-01 05:55 | 61 | 30 | 4146761 | 1830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT 49-74,WILL HAVE TO OPEN RECLR 49-75,THEN ISOLATE AT 49-73 IN ORDER TO SAFELY REPAIR CUTOUT,NEED 1 MAN,BUCKET TO HOLD OUTAGE TIME TO A MINIMUM////OPND RECLR 05:25,REPLACED CUTOUT,CLOSED RECLR @05:55 RELEASED BY CREW 074S06 VER/AWD /// DUPLICATING AND EST TIMES FOR WHEN HOT TAP WAS LIFTED 6 CUST TO COMP WORK SAFELY /// L3/HFP HFPC DUP CDC92 FP37820049000074 PN37820049000074 TOF CNT67 AJB
6949 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-10-28 09:26 | 2014-10-28 09:47 | 87 | 21 | H4666351 | 1827 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 37830222D00226, LEAD ALMOST TOUCHING TEE BRACKET, TRANSFORMER FUSE BLOWN ALSO, WILL NEED TO OPEN RECLOSER ON 37830246C00439 TO CLEAR ARRESTER. NEED 1 MAN TO HELP./SERVICER OPENING RECLOSER 246-439 FOR 30 MIN TO SAFELY MAKE REPAIRS//FIX IT IN HOIS// COD 87+1 FROM DUPLICATE OUTAGE// TIME OFF 9:26 ON 9:47//VER/ ADH VER/DKG L3/DKGXXXX THIS IS THE OUTAGE FOR OPENING RECLOSER AJB
6950 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-04-08 23:31 | 2021-04-09 09:40 | 3 | 609 | 4433391 | 1827 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines. xfm fuse pulled into. power restored 9:40
6951 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-04-27 10:13 | 2016-04-27 15:20 | 8 | 307 | 4131871 | 1826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T LF OPEN @ 116-295, BAD CO @ 115D227 SEND TO D.JENT LF RESTORED @ 13:50. 1 XFMER OFF RELEASED BY CREW 078S07 CLIMB POLE AND REPLACE CUTOUT AND BKT TRANSFORMER RESTORED AT 15:20 VER/HFP L3/HFP
6952 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-12-16 20:27 | 2008-12-16 21:50 | 22 | 83 | 59266-1 | 1826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3410501 -FUSE BLOWN------FUSE APPEAERD TO JUST BREAK //VER/GAH L3/KEP IDC XXXX
6953 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-06-01 18:42 | 2015-06-01 19:55 | 25 | 73 | 4495901 | 1825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL SERVICER OPENED L/F OPENED LINE FUSE ON 801-24 AT 18.42.OPENED LINE FUSE ON 801-24 AT 18.42.CUTOUT CHG ..BACK ON AT 19.55 VER/CRB L3/DKG
6954 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-04 16:02 | 2008-06-04 17:56 | 16 | 114 | 56549-1 | 1824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POSSIBLE BAD ARRESTOR ON FUSE POLE//3008702//VER/CRB
6955 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2019-01-08 19:08 | 2019-01-09 02:44 | 4 | 456 | 4644071 | 1824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | high side came out of xfr cutout,manual work on hill,tyler lewis coming to help,,fetr,03:00,,opened line fuse 185-57 @01:30 closed @ 02:44(see 4648231),,all customers restored complete//cod 4
6956 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2022-10-20 15:37 | 2022-10-20 17:13 | 19 | 96 | 4048821 | 1824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse had broken
6957 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-04-15 15:50 | 2018-04-15 16:18 | 65 | 28 | 4228351 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 2150502; opened sws 941-C4-16 @ 1550 interrupting 275cc (65cc APCo & 210cc KPCo); 210cc restored by Kentucky DDC at 1559 (transferred to their order); due to POR issue, showed 65cc restored via new order 4229681;//// transferred 210 customers to outage 4226171
6958 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-07-12 11:25 | 2015-07-12 11:35 | 182 | 10 | 4780361 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOBBY TACKETT REPORTS CREEK SIDE PHASE BURNING ON STEP DOWN 287-277/ CUTOUT DOOR WAS BURNED UP. WE OPENED RECLOSERS AT 11:25 , CHANGED DOOR, AND CLOSED RECLOSERS AT 287-286 BACK IN AT 11:35. RELEASED BY CREW 074S01// VER/ ADH
6959 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-01-04 14:05 | 2020-01-04 16:25 | 13 | 140 | 4211441 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | p-926-51 top burned off due to bad cutout.contacted rick ray to bring ext for pole top.grd and tagged p-926-30 L3/HFP
6960 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-07-11 06:23 | 2013-07-11 09:25 | 10 | 182 | 4505171 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE ,, STIRUP BURNED OFF A PHASE CHECKING LINE FOR POSSIBLE FAULT//COD 10 + 6// REPAIRED STIRUP AND RESTORED POWER AT 09:25// IDCC CNT16 XXXX
6961 | Hazard | 3309002 | JEFF | JEFF | 2010-07-28 09:27 | 2010-07-28 15:31 | 5 | 364 | 58358-1 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSF == NEED LINE CREW == AND 100KVA TRANSF 120 V 240BAD TRANSF == = ERIC PRATT TO CHANGE TRANSFBAD TRANSF === ERIC PRATT TO CHANGE TRANSF RELEASED BY CREW 077S03 COD-5 VER/HFP L3/HFP IDC DCMT XXXX
6962 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-07-23 08:10 | 2009-07-23 12:30 | 7 | 260 | 64523-1 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP "A" AND "B" PHASE OPEN BUSTED OPEN "C" PHASE AT 0927, BAD CUTOUT ON "B" PHASEFOUND BAD CUTOUT ON POLE 902-485, ON B PHASE, ALSO HAVE BAD CUTOUT ON 902-20, WHICH IS THE LINE FUSE POLE, HAVE CALLED FOR CREW TO BRING 6 CUTOUTS AND CHANGE THEM FOR ME, JOE H. IS ON HIS WAY, DUPLICATING FOR C PHASE OUTAGE L3/HFP IDC XXXX
6963 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-11-14 15:58 | 2022-11-14 18:08 | 14 | 130 | 4142281 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bad lightening arrester on csp xfmr, cleared up. Power restored.
6964 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-01-01 10:45 | 2011-01-01 18:20 | 4 | 455 | 57638-1 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED. TOP OF POLE#-190-135 IS BURNED ALMOST IN TWO. CUTOUT BROKE DOWN. I OPENED TRANS. ON THIS POLE. WE HAVE 2 PEOPLE OUT NOW. WE WILL HAVE TO HAVE SINGLE TAP OPENED UP AT POLE 190-49 WHEN CREW ARRIVES. I CALLED DAVE SAMMONS AND HE SAID HE WOULD HEAD THIS WAY WHEN THEY GOT CLEARED UP ON JOB THEY WERE WORKING ON. I LIFTED HOTTAP ON POLE 190-49 AT 17:45 AND CLOSED IT IN AT 18:20. WE PUT A BRACE ON POLE. COD-5 THIS IS FOR THE TR OUTAGE SEE H57638-1 FOR ADD CUST VER/HFP L3/HFP IDC XXXX
6965 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2019-08-04 12:59 | 2019-08-04 14:30 | 20 | 91 | 4839151 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout L3/HFP
6966 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-11-19 08:11 | 2008-11-19 14:15 | 5 | 364 | 66540-1 | 1820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I THINK BECAUSE OF OVERLOAD. I AM GOING TO REFUSE TRANS. 25 KVA HAS GONE BAD UNDER LOAD. TIM HALL IS GOING TO SEND A CREW AS SOON AS POSSIBLE TO CHANGE IT TO A 50 KVA. POLE 193-169. RELEASED BY CREW 074S01 CREW ON SITE WILL TAKE APROX. 1 HOUR R RAY VER/KEP IDC XXXX
6967 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-10-28 09:00 | 2009-10-28 15:52 | 19 | 412 | H60884-1A | 1819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | VER/HFP B PHASE RECL OPEN 23 CUSTOMERS // OPENED A&C PHASE RECL - 19 CUSTOMERS @ 0900 // ORDER 64103-1 CREATED FOR RECL OUTAGE TO RETURN THIS TO NORMAL. DUPLICATING THIS ORDER FOR THE 30 CUSTOMERS INTERRUPTED TO RETURN THE N.O. SWITCH TO NORMAL L3/HFP IDCC CNT 42 XXXX
6968 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-11-06 15:13 | 2014-11-06 17:00 | 17 | 107 | 4706341 | 1819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONDUCTOR CAME OUT OF DEAD-END CLAMP ON 810-216 AND BLEW LINE FUSE ON 810-33. REPLACED CLAMP, INSULATOR AND RESAGGED PRIMARY. CLOSED 30T LINE FUSE ON 810-33 @ 17:00. SH ENTERED MD // VER/HFP L3/HFP
6969 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-03-13 07:55 | 2019-03-13 11:17 | 9 | 202 | 4976031 | 1818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 19.9 cutout on pole 188-344, Line crew & flaggers required.---crew on site---repaired cutout--pwr restored at 11:17--tbl tkt comp L3/HFP
6970 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-09-08 07:53 | 2012-09-08 11:15 | 9 | 202 | 4029211 | 1818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 967-7 ///VER/CRB L/3 CRB IDC XXXX
6971 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2012-01-02 07:01 | 2012-01-02 08:42 | 18 | 101 | 4224141 | 1818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/PDP IDC XXXX
6972 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2013-03-06 07:38 | 2013-03-06 15:12 | 4 | 454 | 4878631 | 1816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLED FROM OPEN POINT AT POLE 37830258A20158 TO POLE 37830257D30103 . NO TROUBLE FOUND / GXJ RELEASED BY CREW 074S03.. RECLOSER OPEN ON POLE 306-211, DEADEND BELLS ON B PHASE HAS BROKE ON POLE 306-270 WILL NEED BIG BUCKET.. REPLACED DEADEND BELLS RESTORED POWER AT 15:12. VER/KEP IDC XXXX
6973 | Hazard | 3309002 | JEFF | JEFF | 2010-07-27 17:47 | 2010-07-27 20:32 | 11 | 165 | 58152-1 | 1815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 077S08// 345-7 WE HAVE 7200 DEADEND INSU. BLOWN UP, C/O BURNT BAD AND ARRESTOR. JEFF COMBS, VIRGIL AND TIM HEADING TO THIS OUTAGE. LOOKING WERE TO ISOLATE TO CHANGE INSU./// OPEN JEFF OCB B AT 19:55 WORK SOMPLETED AND CLOSED JEFF OCB B AT 20:32. POWER RESTORED.//COD 11// VER/DBM IDC XXXX
6974 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2013-09-30 19:05 | 2013-09-30 21:50 | 11 | 165 | 4900281 | 1815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT DOOR BURNT UP ON XFMR BANK POLE. TYPE IS OBSELETE SO IM CHANGING CUTOUT AND THEN TESTING XFMR. REPLACED BOTH XFMR CUTOUTS AND REFUSED @ 21:50. SH VER/CRB L/3 CRB IDC XXXX
6975 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-03-01 02:57 | 2008-03-01 09:00 | 5 | 363 | 51636-1 | 1815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD BURNT TOP OF POLE OFF NEED 2 MEN ALL MAMUAL ** @ 0415 CONTACTED GREG SHOUSE D/S FOR CREW. VER/LDA IDC XXXX
6976 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2008-03-19 21:55 | 2008-03-20 00:40 | 11 | 165 | 59111-1 | 1815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3403002// HOT TAP BURNT OFF SEVR IN AIR REPAIRING.3403002// HOT TAP LEAD TO CUTOUT BROKE VER/KEP IDC XXXX
6977 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2016-07-18 07:01 | 2016-07-18 11:20 | 7 | 259 | 4651261 | 1813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 1099-6027 10T TRANS, FUSE OUT BAD LA ON TANK CHGED LA VER/AWD
6978 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-07-19 13:51 | 2014-07-19 20:15 | 8 | 384 | 4263771 | 1812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-4015 40/5 POLE BURNT OFF HOT TAP OFF 91-360 91-89 40T BACK ON 15:00 TRUCK TO POLE RELEASED BY CREW 078S08, CREW ON SITE, POLE HAS BEEN REPLACED, ALL POWER RESTORED AT 20:15 RELEASED BY CREW 078H03//COD 8// VER/DBM AJB
6979 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2013-07-16 18:51 | 2013-07-17 09:57 | 2 | 906 | 4532461 | 1812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5 TRUCK MAYBE SEND TO JOE RELEASED BY CREW 078S08...CUST REQ THAT WE REMOVE LARGE TRUCK FROM HER DRIVEWAY, AGREED TO WAIT UNTILL THE A.M. TO HAVE POWER RESTORED.CAN BE CHANGED WTIH SERVICE BUCKET AND BACK YARD MACHINE.BLR RELEASED BY CREW 078H07/CREW ON SITE/FETR1030/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0957/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDC XXXX
6980 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-04 18:16 | 2008-07-05 00:18 | 5 | 362 | 62334-1 | 1810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL NEED TO REPLACE TOP OF POLE WITH FIBERGLASS PIN AND INSULATOR VER/ARN IDC XXXX
6981 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2012-05-07 13:33 | 2012-05-07 18:15 | 12 | 282 | 4755531 | 1809 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3 PHASE DELTA BANK BURNT UP--NEED 3 CUTOUTS --1 75 KVA AND 2 25 KVA TRANSFORMERS--OIL SPILL & PROPERTY DAMAGE// NEED LOAD CHECK TO SEE IF TRANSFORMERS NEED UPGRADED C PHASE FUSE ON POLE 38830021B43609 BACK IN AT 14:30 RELEASED BY CREW 078S07 COD- C PHASE 12 ISO LF 38830021B43609 VER/HFP L3/HFP IDCC CDC92 XXXX
6982 | Paintsville | 3401102 | FALCON | SALYERSVI | 2009-01-18 09:26 | 2009-01-18 13:45 | 15 | 259 | 57993-1 | 1809 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD- 15 WR # 28107249 //..TOP OF POLE BURNED OFF..BB..CUT DEADEND ON POLE.875-720.ONLY XFMR ON POLE 38830875A00721 IS OFF..EVERYONE ELSE IS BACK ON. AT 10 52..(12) .875-222...BB ALL RESTORED @ 1345 (3) L3/HFP
6983 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-05-14 20:11 | 2018-05-15 11:15 | 2 | 904 | 4349631 | 1808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need 25 kva transformer and cutout and arrestor for 19.9 tranformer up n side of hill and cust said wait til in morning Released by crew 077S05
6984 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-03-04 18:37 | 2013-03-04 20:30 | 16 | 113 | 4870321 | 1808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CHECKED ALL FUSES OK, AS BEST I COULD TELL.CUST WOULD LIKE TO HAVE GREG BELL TO LOOK AT THIS . THEY ARE HAVING TROUBLE WITH IN BALANCE ON THE PRI. SIDE.CONTACT ROGER WATKINS AT 465-8000//CONTACT MIKE HURLEY//CUST AGREED TO HOLD TIL MORNING//SEND OLLIE AND STATION SERVICER TO THIS PLEASE// BASKET BURNT OFF ON LOAD SIDE OF RECLOSER AT POLE 190-146// SEE OUTAGE 4871161 FOR OUTAGE DETAILS AND OUTAGE MINUTES// VER/TOM L3/TOM IDC LOOKS LIKE ONE PHASE WAS OUT FROM BEGINNG CHANGED FROM NO INTERRUPTION XXXX
6985 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-05-30 13:39 | 2011-05-30 15:32 | 16 | 113 | 4209711 | 1808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-7064 BAD CUTOUT REPAIRED//VER/CRB IDC XXXX
6986 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-07-07 18:30 | 2011-07-07 18:51 | 86 | 21 | 4482551 | 1806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE YET..BAD CUTOUT.ON 1138C57.SOLID BLADE.FEEDS TOWARDS THE SINGLE PHASE RECLOSER ON 1138C67.WILL HAVE TO REPLACE.WILL HAVE HAVE OUTAGE ON THE SINGLE PHASE LATERAL GOING UP WIDOWS BR ROAD.HAVE CALLED CREW.PLEASE SEND TO JOEY REED.// RELEASED BY CREW 080S01.OPENED AT 18:30 ON AT 18:51//VER/CRB//MDC MADE IDCC PN178 XXXX
6987 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-11-29 14:00 | 2016-11-29 15:26 | 21 | 86 | 4144631 | 1806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED 25T LINE FUSE ON 38830954A20349 @ 14:00 TO ISOLATE BURNT OFF XFMR POLE 954-1123. NO OUTAGE PRIOR RDM ENROUTE TO BRING MATERIAL TO REPAIR. COMPLETED REPAIRS AND CLOSED LINE FUSE 954-349 @ 15:26 RESTORING OUTAGED CUSTOMERS. SH/ MD DONE/ ISO 38830954A20349/ COD 21/ VER/BOW L3/HFP XXXHFP AJB
6988 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-07-26 12:24 | 2017-07-26 16:42 | 7 | 258 | 4181811 | 1806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-2262 BAD 75KVA TRANS TRUCK TO POLE RELEASED BY CREW 078S08///REPLACED BAD 75 XFMER///ALL CUST RESTORED @ 16:42///COMPLETE BR/ ISO 38830045B12262/ COD 7/ VER/BOW SJG
6989 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-08-14 02:23 | 2018-08-14 17:25 | 2 | 902 | 4951081 | 1804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad cutout on pole 424-209 burnt dead end bells into loop holding phase up.. Released by crew 077S11 power restored at 17:25 Released by crew 075H03 L3/HFP
6990 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2016-08-07 13:13 | 2016-08-07 17:00 | 9 | 227 | 4746611 | 1803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE RECLOSER OPEN //COD 9//CLOSED RECLOSER @ 15:00. XFMR CUTOUT FAILED ON 1047-25 AND IS ISOLATED. REPLACING CUTOUT. REPLACED XFMR CUTOUT AND CLOSED @ 17:00 RESTORING REMAINING CUSTOMERS. SH RELEASED BY CREW 076S02 VER/CRB
6991 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-05-27 23:50 | 2014-05-28 09:51 | 3 | 601 | 4941161 | 1803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON PRIMARY TAP TAKE OFF POLE. WILL NEED FLAGGERS AND BIG BUCKET TO SET TOOLS AND MATERIAL UP ON A ROCK CLIFF. NO TRUCK TO POLE. THIS IS JUST PAST CAMP CREEK GOING TOWARDS VIRGINIA. RELEASED BY CREW 079S02 VER/KEP
6992 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-09-10 21:28 | 2018-09-11 00:48 | 9 | 200 | 4080421 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed and burnt off pole 760-349. Only one customer out until I opened line fuse 760-24 to isolate @ 22:45. Crew enroute to repair. Made repairs and restored line fuse 760-24 @ 00:48. sh Released by crew 076S02
6993 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-05-06 12:15 | 2013-05-06 14:45 | 12 | 150 | 4074131 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NO POWER OFF UNTIL 1215 -05/06 - 5 CUST & 1234 - 12 CUST // NEED TECH---POLE 39831147C24553 IS ROTTED OFF AN LEANING --TRUCK TO POLE--CLEARENCE PROBLEM--PHONE AT 13 FEET ACROSS RD--CITY TO BLOCK RD--JOHN SODA CONTACTED WINDSTREAM TO CHANGE POLE RELEASED BY CREW 078S07/ WINDSTREAM TO SET PL. FETR 16:00 JEH DUPLICATING FOR 5 CUST OFF @ 1215 SEE DUP H4074131 VER/HFP L3/HFP IDCC CCO XXXX
6994 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-02-19 07:05 | 2015-02-19 10:50 | 8 | 225 | 4041331 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY BURNT IN THE CLEAR ON POLE 38830905000048//ISO//COD 8// CREW ENROUTE TO ASSIST. (SEE RELATED ORDER 4042471 FOR RECL OUTAGE TO MAKE REPAIRS)//CREW ENROUTE TO ASSIST. OPENED LINE FUSE 905-36 @ 10:14 TO MAKE REPAIRS//CLOSED LINE FUSE 905-36 @ 10:50 RESTORING ALL OUTAGED CUSTOMERS. SH// VER/HFP L3/HFP
6995 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-08-23 10:45 | 2017-08-23 13:15 | 12 | 150 | 4292311 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE37830247D01015,PUT OUT POLE FIRE AND LIFTED CLAMP 37830247D00920 AT 10:45 TO TRANSFORMER,NEED LINE CREW AND BIG BUCKET AND 19.9 KV CUTOUT AND ARRESTER AND BRACKET,ABOUT HALF OF POLE IS BURNT INTO, RELEASED BY CREW 077S04/ ISO 37830247D00920/ COD 12/ 3308502 BONNYMAN HAZARD/ VER/BOW
6996 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2008-12-21 21:31 | 2008-12-22 00:51 | 9 | 200 | 61918-1 | 1800 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 27771349 ///LEAD NEARLY BURNED INTO AT XFR,WILL OPEN XFR TO MAKE REPAIRSMADE NECESSARY REPAIRS,ALL OK AFTERWARDS COD-9 VER/KEP L3/KEP IDC XXXX
6997 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-11-25 02:10 | 2014-11-25 05:10 | 10 | 180 | 4778591 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELATED TO ORDER 4767541//HAD TO OPEN FUSES IN ORDER TO SAFELY REPLACE TRANSFORMER ON POLE 925-43//COD 10// VER/DBM AJB
6998 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-07-20 09:18 | 2014-07-20 09:43 | 72 | 25 | 4265521 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SERVICER LOAD BUSTED B PHASE HERE TO MAKE REPAIRS RELATED TO ORDER 4265341//COD 72// VER/DBM AJB
6999 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-09-05 13:03 | 2014-09-05 14:43 | 18 | 100 | 4468581 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REPLACING POLE// LOOP 37830269D00044// RECLOSER 37830293000169/// COD 18// VER/BOW
7000 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2012-08-06 14:54 | 2012-08-06 15:14 | 90 | 20 | 4904141 | 1800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREW FOUND LOOP LAYING ON AN ARM (TIE WIRE BROKE) ON A BUCK ARM POLE. CREW OPENED RECLOSERS TO ALLOW THEM TO SAFELY RETIE LOOP TO INSULATOR... NO TRUCK ACCESS //OFF 1454 ON @ COD-90 ISO OCR 37820265B00107 VER/HFP L3/HFP IDC 5 CUSTOMERS ALREADY OUT ON ANOTHER ORDER XXXX
7001 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2019-07-26 17:24 | 2019-07-26 21:41 | 7 | 257 | 4796921 | 1799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse blown will check and refuse///Fuse link in cutout door had broke.I refused and restored power @ 21:41
7002 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-02-04 13:27 | 2012-02-04 14:29 | 29 | 62 | 4319721 | 1798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT BROKEN, BLEW LINE FUSE AT MOUTH. FAULT POLE 201-68..CAN CHANGE MYSELF.FOUND CABLE TV LINE DOWN ACROSS HOUSES AND DRIVEWAYS.WHAT EVER CAUSED TV TO FALL JARD OUR POLE ENOUGH TO CAUSE CUTOUT TO FALL APPART.. CUSTOMER SAYS CUTOUT HAS BEEN FRYING FOR A YEAR.P.HICKS/POSSIBLE VEHCLE ACCIDENT HOOKING THE TV CABLE AND PULLING IT DOWN NO VERIFICATION THOUGH VER/KEP IDC XXXX
7003 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-01-20 12:21 | 2022-01-20 18:20 | 5 | 359 | 4391221 | 1795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 45/4 pole 7200 dead end complete truck fuse out on pole 11 in church parking lot no grounds or tags;;cutout bad burned pole off Released by crew 077H0245/4 pole 7200 dead end complete truck fuse out on pole 11 in church parking lot no grounds or tags;;cutout bad burned pole off power restored at 18: 20
7004 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-12-14 05:41 | 2019-12-14 10:40 | 6 | 299 | 4152641 | 1794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines bad door, replaced and back in at 10:40
7005 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-04-08 14:26 | 2022-04-08 17:09 | 11 | 163 | 4741771 | 1793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 794C-6.broke cutout on pole 38820794C00301.i will be climbing to make repairs..i made my repairs and got line fuse on pole 794C-6 back in at 17:09
7006 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-05-13 14:43 | 2008-05-13 16:20 | 54 | 97 | 63603-1 | 1793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000903//POLE FIRE AT POLE #1123-288//SERVICER OPENED FUSE @1123-2019 AND THEN ISOLATED FAULT POLE//CREW ENROUTE////WILL MAKE TEMP. REPAIRS NEED TO SEND COPY OF TICKET TO TECH TO WRITE WO FOR POLE REPLACEMENT P R TOLLIVER// NEED 5 TALLER POLE AND NEW 25KVA TRANSFORMER WHEN TECH WRITES JOB//SERVICE BACK ON AT 16:20/// RELEASED BY CREW 078H03//VER/CRB IDCC TON1624 XXXX
7007 | South Williamson | 3411401 | DEWEY | INEZ | 2015-04-10 08:07 | 2015-04-10 10:50 | 11 | 163 | 4302231 | 1793 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEFUSE BLOWN ON POLE 768-30//FOUND BROKE CUTOUT ON POLE 768-205//REPLACED CUTOUT//RESTORED AT 10:50//COMPLETE//EM COD-11 ISO LF 38830768D00030
7008 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-07-23 11:43 | 2019-07-23 15:27 | 8 | 224 | 4780441 | 1792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 37830248A00914 BURNT OFFbad cutout burnt top of pole37830248A00914,need 40c4 pole,2 dead ends,3 clevis,2 guys,25kva transformer,cutout complete,some 2/3 service wire,all 72kv,need r/w crew,all manualbad cutout burnt top of pole37830248A00914,need 40c4 pole,2 dead ends,3 clevis,2 guys,25kva transformer,cutout complete,some 2/3 service wire,all 72kv,need r/w crew,all manual Released by crew 077S04 L3/HFP
7009 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-06-24 15:44 | 2019-06-24 20:00 | 7 | 256 | 4575271 | 1792 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B TACKETT///4/0 risers burnt up and bad connections @ 69-4528. crew reqd. no trks4/0 risers burnt up and bad connections @ 69-4528. crew reqd. no trks open neut& bad hot leg.open can @ 14:35 Released by crew 078S07,repairs made please close ticket thanks.bt L3/HFP
7010 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-06-06 13:16 | 2010-06-06 17:00 | 8 | 224 | 57681-1 | 1792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | BAD INSULATOR FAULTED BURNING LINE DOWN..CALLED TIM MILLER, HES SENDING CREW.. VER/ARN IDC XXXX
7011 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-08-03 22:29 | 2016-08-03 22:45 | 112 | 16 | 4731021 | 1792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | RELATED TO 4726741//SEE DOL 676836//OPENED N.O. RECLOSER IN ORDER TO RETURN CKT TO NORMAL//COD 112// VER/ARN L3/HFP XXXHFP AJB
7012 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-11-01 01:30 | 2009-11-01 01:58 | 64 | 28 | H53870-1 | 1792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED; TOP 18 OF POLE BURNT OFF ANGLE POLE 524/107 ; CAN LOWER EVERYTHING ON POLE--NEW POLE NOT REQUIRED; NEED NEW 7200 CUTOUT AND BRACKET AND 15 FT OF # 2; 4 WHEEL DRIVE TRUCK ACCESSABLE BUT VERY STEEP GRAVEL DRIVEWAY; CLEARED UP AND GROUNDED ISOLATION POLE 524/189 RELEASED BY CREW 078S12 ISOAT 524-77 CLOSED TIE SWITCH 572-94 AT 2050 PICKED UP ALL BUT 8 CUST//CREW ON SITE WILL LOWER ATTACHMENTS//COMPLETE AT 01:58 ALL CUST. RESTORED.P R TOLLIVER RELEASED BY CREW 078H03 //VER/GAH IDC XXXX
7013 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2019-04-08 10:44 | 2019-04-08 13:10 | 18 | 146 | 4069111 | 1791 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burnt up on pole 450-245 causing line fuse to blow on pole 450-243 ON @ 1310
7014 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2021-03-02 20:25 | 2021-03-03 11:20 | 2 | 895 | 4294131 | 1790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA 19.9 truck may reach will be real close if it does please move cutout around pole Released by crew 077S03 replaced xfmr power back on @ 11:20
7015 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2018-03-21 14:41 | 2018-03-21 20:39 | 5 | 358 | 4039011 | 1790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open on 1147-820, pole fire at 39831123B00655. This at the end of Fawn ln, off of foxhunters. Can lower everything, no trucksLine fuse open on 1147-820, pole fire at 39831123B00655. pole 1147-820 is tagged and grounded to vernon mullins./crew on site/FETR2045/vem/all cust restored 2039/please close ticket/thanks/vem/ ISO 39831147A00820/ COD 5
7016 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-01-08 07:30 | 2015-01-08 10:29 | 10 | 179 | 4918161 | 1790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY DOWN @ 303-51 NEED LINE CREW TO REPAIR,PLACE GROUNDS & TAG TO VERNON MULLINS @ 303-51 RELEASED BY CREW 078S05/CREW ON SITE/FETR 1115/VEM/ON 10:29/COD10// VER/ ADH L3/HFP XXX
7017 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-05-24 07:49 | 2018-05-24 13:25 | 13 | 336 | 4405961 | 1788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200 50 kva 120/240. no truck, yard dog Released by crew 078S07,open line fuse @ 1124b22529 @ 1207//COD 3 FROM BEGINNING OF OUTAGEbad 7200 50 kva 120/240. no truck, yard dog Released by crew 078S07,open line fuse @ 1124b22529 @ 1207,line fuse in @ 1325,all cust restored please close ticket thanks.bt Released by crew 078H02 // L3/HFP
7018 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-12-27 23:50 | 2018-12-28 09:46 | 3 | 596 | 4603701 | 1788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on riser pole 38830020D16058, Crew required, can reach with big bucket. Access from sarah rd. Released by crew 078H04 L3/HFP
7019 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-06-01 | 2012-06-01 09:56 | 3 | 596 | 4857411 | 1788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT FUSE OUT//COD 3// VER/DBM IDC XXXX
7020 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-07-23 09:07 | 2008-07-23 11:36 | 12 | 149 | 58553-1 | 1788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE OUT FAULT POLE TREE ON HENDRIX CABLE . SERVICER WILL OPEN ALL FUSES AND CHANGE SIZE FROM 80 T TO 60 T POLE 70-605 TREE ON POLE 70-675 LOOP BURNTING POLE 70-605 3-65T POLE 70-605 - 1-40T RELEASED BY CREW 078S08 VER/KEP IDCC PN637 XXXX
7021 | Pikeville | 3421002 | BREAKS | GRASSY | 2008-01-18 06:09 | 2008-01-18 11:07 | 6 | 298 | 57509-1 | 1788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF AT 221-40 AND LINE FUSE BLOWN POLE AT 37820221C40177 WILL REQUIRE CREW FETR 11:00// (CHECK CC AFTER LINE IS RESTORED) CC=6// RELEASED BY CREW 100S01// GRUNDY OUTAGE//VER/RRH IDCC PN27 XXXX
7022 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-08-28 12:41 | 2012-08-28 14:15 | 19 | 94 | 4980501 | 1786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 1123-6631 CHGED LA 1123-6632 BAD LA POLE 1123-6630 25T LINE FUSE COD-19 ISO LF 39831123D26630 VER/HFP L3/HFP IDC XXXX
7023 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-05-17 06:41 | 2016-05-17 12:38 | 5 | 357 | 4224531 | 1785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD EPOXILATOR ON POLE 194-109 NO TRUCK ACCESS NEED 3 MEN RELEASED BY CREW 074S02 REPAIRS MADE ON AT 12:38 VER/AWD
7024 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-11-30 09:45 | 2018-11-30 14:00 | 7 | 255 | 4493381 | 1785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad insulators on pole 38831086000005, need two de insulator for 19.9this is were two tone trailer yellow and brown on left Released by crew 077S05 repairs made and power restored at 1400
7025 | Hazard | 3303902 | LESLIE | WOOTON | 2009-09-07 15:01 | 2009-09-07 17:00 | 15 | 119 | 52744-1 | 1785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A//COD 15// VER/DBM IDC XXXX
7026 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-08-20 17:15 | 2009-08-20 23:12 | 5 | 357 | 56960-1 | 1785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | C PHASE FUSE OUT ON POLE--TRUCK OK--NEED CROSSARM AN NEW PINS -INSULATORS AN BRACES--L MCCARTY TO WORK-TAGED BLOWN FUSE FOR CREW RELEASED BY CREW 078S07 // WILL HAVE 2 HR OUTAGE STARTING @ 22:30- 2312 VER/PDP IDCC TOF2230 XXXX
7027 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-06-04 21:38 | 2011-06-05 12:30 | 2 | 892 | 4232351 | 1784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REPLACING POLE - WILL WORK THIS AS SOON AS POLE IS REPLACED// BAD 25 KVA CSP XFMR..NEED 1 MAN TRANSFORMER AND MATERIAL HANDLER..CUTOUT AND ARRESTOR... RELEASED BY CREW 076S01CREW REPLACING POLE - WILL WORK THIS AS SOON AS POLE IS REPLACED// BAD 25 KVA CSP XFMR..NEED 1 MAN TRANSFORMER AND MATERIAL HANDLER..CUTOUT AND ARRESTOR...TOMMY GOBLE BRINGING TRANSFORMER//VER/CRB IDC DCMT XXXX
7028 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-04-30 18:16 | 2010-04-30 20:33 | 13 | 137 | 53266-1 | 1781 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT 30T 44-5521 RELEASED BY CREW 078S08//MADE A MD//LINE FUSE OUT 30T 44-5521 RELEASED BY CREW 078S08// BAD L/A ON POLE 44 -7122 //VER/CRB IDC XXXX
7029 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2021-08-17 19:15 | 2021-08-18 10:05 | 2 | 890 | 4090111 | 1780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuses keep pulling into
7030 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-07-03 02:42 | 2017-07-03 12:35 | 3 | 593 | 4068271 | 1779 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 60 AMP CUTOUT// VER/CRB
7031 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-12-14 10:55 | 2010-12-14 15:09 | 7 | 254 | 66573-1 | 1778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA NEEDS CHANGED TO 37.5 OR 50 KVA CHGD LAST TIME WITH TRUCK RELEASED BY CREW 078S03/CREW ON SITE/FETR1545/VEM/XFMR CHANGED AND POWER RESTORED TO ALL CUST AT 1509/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
7032 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-10-10 10:25 | 2016-10-10 11:13 | 37 | 48 | 4982181 | 1776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED LINE FUSES ON 37830351B00002 TO SAFELY REPAIR DOWNED LINE. ASSOCIATED WITH 4981821. VER/AWD L3/HFP XXXHFP AJB
7033 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2021-12-11 05:51 | 2021-12-11 20:39 | 2 | 888 | 4170631 | 1776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | jumper on pole 135 has come out of the top of the xfmr cutout. thy will need to isolate at 38830213000052 so they can climb pole 135 and make repairs Released by crew 078S12
7034 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-06-07 20:25 | 2022-06-07 22:00 | 49 | 95 | 4035141 | 1775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 423-A-129. this bad transformer opened recloser on pole 423-B-255. got recloser back in @ 21:00. transformer replaced. power restored Released by crew 077S11
7035 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-06-11 16:09 | 2008-06-11 18:50 | 11 | 161 | 62757-1 | 1771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410502// CUTOUT DOOR BURN-UP // VER/TOM IDC XXXX
7036 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-06-11 00:31 | 2021-06-11 06:12 | 14 | 341 | 4711941 | 1771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Fuse open at 38821057D00006 crews found bad TR 25kva 19.9 on pole 38821057D00304 will change later this AM Released by crew 074H04 line fuse restored at 0139 TR fuse restored at 0612
7037 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-01-16 08:19 | 2009-01-16 11:00 | 11 | 161 | 55677-1 | 1771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-11 WR # 28092824 BAD 25KVA NEED 50 KVA 4/0 RISERS TRUCK TO POLESEND TO JIM LINKOUS RELEASED BY CREW 078S08 REPLACED 25 KVA WITH 50 KVA , UPGRADED RISER WIRE,REPLACED CUTOUT,ALL POWER RESTORED AT 11:00 L3/HFP
7038 | Pikeville | 3410602 | E.PRESTON | LANCER | 2015-12-26 10:36 | 2015-12-26 14:10 | 13 | 214 | 4561711 | 1770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 955-103. CLOSED LINE FUSE 955-95 @ 12:38 RESTORING ALL BUT XFMR 955-103. REPLACING CUTOUT. REPLACED CUTOUT AND CLOSED XFMR 955-103 @ 14:10 RESTORING REMAINING OUTAGED CUSTOMERS. SH RELEASED BY CREW 076S02// VER/ ADH
7039 | Hazard | 3308002 | JACKSON | PANBOWL | 2020-05-24 11:30 | 2020-05-24 16:25 | 6 | 295 | 4896011 | 1770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | red to red burnt out at 38831084A00173. repaired 16:25
7040 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-06-11 16:10 | 2008-06-11 16:25 | 118 | 15 | 62755-1 | 1770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602// RELATED TO ORDER 62727-1 CREW OPENED RECLOSER TO ALLOW THEM TO REPLACE CUTOUT THAT BROKE AND WAS HANGING ON THE POLE ARCING.37830458000195 MLR OK IDC REDUCED BY 20 CUSTOMERS AND CREATED ORDER FOR ORIGINAL CUSTOMERS XXXX
7041 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2008-11-10 23:30 | 2008-11-11 02:35 | 10 | 185 | 63776-1 | 1770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3409001// BAD SECTION OF U/G OUT // COD-10 / 0155 RESTORED 2 CUST // 0235 RESTORED 8 CUST // VER/LDA IDCC STP XXXX
7042 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-03-01 02:28 | 2009-03-01 03:20 | 34 | 52 | 52664-1 | 1768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STEPDOWN FUSE MELTED OUT OR BROKE ON POLE 8-36 WHILE SWITCHING TO P.U. CUSTOMERS FROM THE HADDIX/QUICKSAND CKT. B PHASE 33 CC. VER/PDP IDCC CDC92, XXXX
7043 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-02-01 09:09 | 2008-02-01 12:50 | 8 | 221 | 63539-1 | 1768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001203// RELEASED BY CREW 078S08 RELEASED BY CREW 078S07CLOSED RECLOSER @ 1215 IDC XXXX
7044 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-11-17 14:00 | 2009-11-17 14:52 | 34 | 52 | 65182-1 | 1768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BYPASS CUTOUT BROKEN ON RECLOSER POLE CREW HAD TO OPEN RECLOSER TO SAFELY REPLACE VER/KEP L3/KEP IDC XXXX
7045 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-03-11 07:04 | 2011-03-11 14:26 | 4 | 442 | 53330-1 | 1768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERV CROSSES ROAD HERE,HAS BEEN TORN DOWN BY TREE,WILL TRY TO GET SOME HELP.GOING TO REPLACE LEAKING XFR,T HALL ARRANGING THIS.NOTE NEW FETR//////REPLACED DAMAGED XFR AND RESTORED,ALL OK AFTERWARDS//VER/CRB IDC MAY HAVE BEEN REST TIME INVOLVED XXXX
7046 | Whitesburg | 3312902 | JENKINS | JENKINS | 2017-09-14 14:43 | 2017-09-14 15:00 | 104 | 17 | 4363031 | 1768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | DOL 771556//CREW OPENED SWS IN ORDER TO SAFELY MAKE UP LOOPS ON POLE 382-44//COD 104//SEE ALSO 4361341// VER/DBM VER/HFP L3/HFP SJG
7047 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-09-26 22:12 | 2010-09-26 23:45 | 19 | 93 | 53896-1 | 1767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED ISOLATED CUTOUT IDC XXXX
7048 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2012-07-25 07:31 | 2012-07-25 17:20 | 3 | 589 | 4821811 | 1767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | LINE FUSE & XFMR FUSE ON POLE# 542-163 ARE BOTH OPEN TREE IN LINE BETWEEN #542-135 & #542-328. MAP DISCR. THERE IS NO TRANSF. ON POLE# 542-135, JUST 1/0 LASH SEC. NEED TO REPLACE 2-FUSES AND TRIM TREE, MANUAL TREE CREW. RELEASED BY CREW 078E09/BRKN CUTOUT 524-163 (XFMER) WHICH FAULTED LINE FUSE 40T, SAME 542-163 /FETR 18:00/JEH// REPAIRS COMP. POWER RESTORED @ 17:20 JEH ( 3 CUST.)// VER/DBM
7049 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2010-01-05 05:56 | 2010-01-05 07:29 | 19 | 93 | H60687-1 | 1767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SPLICE FAILED CREW ON SITE REPAIRING; OPEN OCR ON POLE 428-453 AT 05:56 CLOSED IN AT 07:29 VER/KEP L3/KEP IDC XXXX
7050 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-05-11 18:49 | 2011-05-11 19:20 | 57 | 31 | 4066131 | 1767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 2206403 / CC-450 / CB OPENED FOR REPAIRS TO DAMAGED SWITCH ON PRIM MET. POLE /
7051 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-12-20 05:37 | 2019-12-20 11:30 | 5 | 353 | 4171721 | 1765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | spoke with customer, neighbors out//temps below freezing// 19.9 cutout big bucket and flaggers Released by crew 077H14 repairs made and power restored at 1130
7052 | Hazard | 3302703 | HAZARD | HAZARD | 2016-12-19 20:05 | 2016-12-19 23:21 | 9 | 196 | 4222021 | 1764 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFMR . NEED 50KVA XFMR 7200 & BIG BUCKET . NEED 2 MEN & BIG BUCKET . THIS SHELL MART IN TOWN ACROSS FROM PIZZA HUT . RELEASED BY CREW 075H04 VER/CRB
7053 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-02-04 13:48 | 2012-02-04 18:00 | 7 | 252 | 4319791 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 37830247B00104, HAVE WIRE DOWN OFF POLE 37830247B00131 #4 CU. PRIMARY, ALSO HAVE BAD XFMR CUTOUT ON POLE 37830247B00131, 34KV. 3 MAN CREW NEEDED, BIG BUCKET. RELEASED BY CREW 077S08 VER/KEP IDC XXXX
7054 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-12-24 16:31 | 2008-12-24 17:55 | 21 | 84 | 63559-1 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE RECLOSER OUT ON POLE 66C61 END OF CROSS ARM B URNT OFF POLE 66D213. DUE TO BAD CUT OUT. I REPLACED CUTOUT AND ARRESTER. MOVED WIRE IN ON ARM. CLOSED IN A PHASE RECLOSER EVERYTHING OK. SEND COPY OF THIS TO ENG PIKEVILLE RON RYE TO GET ORDER TO REPLACE CROSS ARM.//PHASE A RECLOSER WAS OPEN ONLY//COD 21// VER/DBM L3/KEP IDC CHANGED START TIME FROM 1558 XXXX
7055 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-11-14 15:15 | 2011-11-14 19:27 | 7 | 252 | 4075451 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1108-283 BURNED NEARLY INTO,NEEDS REPLACED.PVILLE IS NOTIFIED.CREW ENRT SHORTLY WITH MATERIALS,OPENED LINE FUSE AT 1108-276//////REPLACED POLE AND RESTORED,CUTOUT HAD BROKEN DOWN//COD 7//MD FILED//ISO 38821108000276// VER/DBM IDCC TOF1438, ESTIMATED TIME OFF XXXX
7056 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-12-29 07:06 | 2009-12-29 08:30 | 21 | 84 | 62854-1 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND BASKET BURNTED INTO ON POLE 902-144, MADE TEMP REPAIRS ON THIS, TO GET POWER BACK ON, WELL NEED TO SEND CREW TO REPLACE THIS BASKET, PRI IS 4/0 PRI IDC XXXX
7057 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2017-11-19 13:40 | 2017-11-19 14:22 | 42 | 42 | 4582431 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | pole 37830188B00085 has broken croissarm 8 ft arm (2) pins (2) 1301 (1) set 60in. braces //open three switches to isolate trouble on pole 37830188B00093 at 13:40 closed at 14:22/ ISO 37830188B00093/ COD 42
7058 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-02-20 03:06 | 2015-02-20 08:00 | 6 | 294 | 4046991 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN WILL REFUSE/// BAD 25 KVA 19.9 TRANSFORMER/// CAN USE TRUCK RELEASED BY CREW 074H17 CREW ON SITE RESTORED AT 08:00AM VER/HFP L3/HFP
7059 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-06-27 14:41 | 2013-06-27 15:30 | 36 | 49 | 4416521 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR IN LINE FUSE. COD-36 ISO LF 38830211000047 IDC XXXX
7060 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2008-03-28 12:50 | 2008-03-28 13:39 | 36 | 49 | 61548-1 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001002// 1AND 3/4 MILE OUT RT. 5 FROM US 60 YELLOW TRL. ON RIGHT JUST PASS WILLIAMS CK. CHURCH POLE ON HILL ON LEFT 114-12 2- CUST RELEASED BY CREW 078S08// HAD TO OPEN SOLID BLADE @ POLE 90-357 TO SAFELY CHAGE CUTOUT// OPENED SOLID BLADE @ 1250 AND CLOSED BACK IN @ 1339 //// VER/TOM IDCC CNT38 SEE DUPLICATE OUTAGE XXXX
7061 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-07-16 16:43 | 2013-07-16 19:10 | 12 | 147 | 4531041 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED 50 KVA TRUCK TO POLE RELEASED BY CREW 078S08 //NEED A TRANSFORMER BAG LEAKING/ FETR 19:30 JEH/REPAIRS COMP. POWER REST. @ 19:10//JEH//COD 12// VER/DBM IDCC FP NULL XXXX
7062 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2017-04-30 12:09 | 2017-04-30 15:25 | 9 | 196 | 4697291 | 1764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PUT IN ABNORMAL 254B255 TO 254B256#4 COPPER NEUTRAL TRUCKS OK NEEDS RIGHT OF WAY CUT/ BAD PLACE IN THE CONDUCTOR/ CONDUCTOR BROKE INTO/ ISO 38830254B00255/ COD 9/ VER/BOW L3/HFP XXXHFP AJB
7063 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-08-30 15:11 | 2021-08-31 00:51 | 9 | 580 | 4178371 | 1762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | attempted to contact customer, no response //. bad padmount 4774. line crew required. will need to isolate. will need new padmount and material to terminate new elbow. will possibly need DT Bonzo. Released by crew 078H33 Opened LF @ 2325 and Restored all @ 0051
7064 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-06-19 10:18 | 2009-06-20 15:40 | 1 | 1762 | 53808-1 | 1762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DC ADDED AN UNRELATED WIRE DOWN CALL IN THE GENERAL AREA. PLEASE CHECK WHEN DOING THIS ORDER. BAD UNDER GROUND SERVICE GOING TO GO OVERHEAD SERVICE IDC XXXX
7065 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-11-09 00:39 | 2013-11-09 03:35 | 10 | 176 | 4023251 | 1760 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | BAD SEC RISERREPLACED SEC. RISER VER/KEP
7066 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-09-01 01:09 | 2022-09-01 02:37 | 20 | 88 | 4824181 | 1760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 1023 -45 phone company pole rotted off can tie off/send to kevin griffith Released by crew 078S03 Opened line fuse on 1023-43 at 01:10 Closed at 02:37. Ticket complete//cod 20
7067 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-09-04 14:55 | 2012-09-04 17:35 | 11 | 160 | 4004991 | 1760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE ON HIGH SIDE OF STEP-DOWN TRANSFORMER- CHANGED BOTH HIGH-SIDE AND LOW- SIDE CUT-OUTS AND POWER RESTORED//COD 11// VER/DBM IDCC CDC96 XXXX
7068 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-04-07 22:27 | 2015-04-08 13:07 | 2 | 880 | 4286101 | 1760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT BURNT OFF POLE NEED LINE CREW TO REPAIR @ POLE 326-171 NO TRUCK LINE FUSE OPEN & TAG TO DDC RELEASED BY CREW 078S05YARD DOG WORK, DO NOT TAKE ANYTHING BIGGER THAN PICKUP IN THE DRIVEWAY, NO PLACE TO TURN, SHOULD B ABLE TO LOWER RELEASED BY CREW 078H07//CREW ON SITE///POLE REPAIRED///TBL TKT COMP///PWR RESTORED @ 13:07 VER/SEF
7069 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-12-02 16:14 | 2014-12-02 19:10 | 10 | 176 | 4827191 | 1760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 67-275 HOT TAP BURNT OFF NO TRUCK WILL HAVE TO OPEN LINE FUSE ON POLE 67-272 NEED CREW,,CREW ON SITE MAKING REPAIRS COD-10 ISO PO @ 38830067D00275 VER/HFP L3/HFP
7070 | South Williamson | 3411401 | DEWEY | INEZ | 2018-09-16 20:45 | 2018-09-16 23:35 | 16 | 170 | 4108731 | 1760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | failed cutout pole 38/opened fuse 275 at 2205 to make repairs closedt 2335 L3/HFP
7071 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-11-02 10:10 | 2015-11-02 13:50 | 8 | 220 | 4402731 | 1760 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | MADE MDC TO SHOW CORRECT CUST PREMISE WITH CORRECT TRANS//COD 8//BAD 7200-50 KVA 2 PRI. BUSHING 120/208BAD 7200-50 KVA 2 PRI. BUSHING 120/208 RELEASED BY CREW 078S07.. CREW ON SITE TO REPLACE BAD XFMR ON POLE 1123-6662 WILL HAVE TO OPEN XFMR BANK.. TRIED TO LET BUSINSSES KNOW BUT NO ONE WOULD ANSWER ETR 14:00.. OPENED BANK AT 13:20 BACK IN AT 13:50 AND COMPLETE//PART OUT FROM BEGINNING VER/CRB L3/HFP HFPC MCCDL
7072 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2019-07-30 19:53 | 2019-07-31 10:32 | 2 | 879 | 4815601 | 1758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arr. on pole laying on brkt took station breaker out/// circuit was out starting at 19:53
7073 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-11-27 11:58 | 2022-11-27 21:44 | 3 | 586 | 4184701 | 1758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke XCO on 22-130broke XCO on 22-130
7074 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2011-10-19 15:26 | 2011-10-19 19:37 | 7 | 251 | 4999641 | 1757 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD HOTTAP ///VER/CRB IDC XXXX
7075 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-12-27 22:52 | 2011-12-28 13:30 | 2 | 878 | 4208991 | 1756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE THE TOP OF A 405 POLE BURNTED OFF, CAUSE WAS A BAD CUTOUT, LINE FUSE IS OPEN ON POLE 901-5038, LINE IS GROUNDED AT THIS POLE, FIRE IS OUT, JUST FEEDS TWO CUST, WELL NEED LINE CREW, YARD DOG, MANUEL TREE CREW TO MAKE REPAIRS, EVERYTHING WILL GO BACK, BUT NEED A NEW CUTOUT RELEASED BY CREW 078S06//CREW ON SITE//POWER RESTORED AT 13:30 SEND COPY TO TREE CREWS TO TRIM PINE TREES PRT// VER/KEP IDC XXXX
7076 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-06-13 08:31 | 2011-06-13 15:50 | 4 | 439 | 4309001 | 1756 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STW WR # 40357303 // ONE OF THE 120 VOLT LEGS IN THIS UNDERGROUND SERVICE HAS CORRODED APART. I CALLED TIM HALL WHO IS CALLING A CREW AND A TECH TO BRING AN UNDERGROUND FAULT FINDER. RELEASED BY CREW 074S02/MADE REPAIRS AND CLOSED IN AT 1550 COD-4 ISO TF 37830143A00221 VER/HFP L3/HFP IDCC CCUG XXXX
7077 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-14 17:59 | 2008-12-14 23:50 | 5 | 351 | 58363-1 | 1755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3308401//CALLED THIS CUSTOMER AND THEY ARE STILL OUT//NEEDS CHECKED FUSE BROKE. VER/PDP L3/KEP IDC XXXX
7078 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2022-11-18 21:40 | 2022-11-19 00:55 | 9 | 195 | 4160741 | 1755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 xfmr///lid blew off//need line crew and big bucket//truck approach//please send to ToMMy Goble/ opened @ 835-251 @ 12:15 closed @ 12:55//cod 2
7079 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2013-04-28 08:21 | 2013-04-28 08:36 | 117 | 15 | 4053181 | 1755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER @ 0825 TO ALLOW CREWS TO MAKE UP LOOPS AT POLE 225-290// SHOULD TAKE LESS THAN 30 MINUTES AND WILL RESTORE ENTIRE LINE// CLOSED RECLOSER @ 0836 RESTORING ALL//ASSOCIATED WITH OUTAGE 4052851// IDC XXXX
7080 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-03-29 19:55 | 2018-03-29 20:08 | 135 | 13 | 4151711 | 1755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER 37820098D00149 TO TAKE LOAD OFF STEP-DOWN 37820098D20148B TO REPAIR SPUR//NO OUTAGE TILL RECLOSER OPENED//Hot tap arcing on pole#98-D2-148B /// Opened recloser on pole#98-149 @ 19:55 to make repairsHot tap arcing on pole#98-D2-148B /// Opened recloser on pole#98-149 @ 19:55 to make repairs/// Tightened hot tap up and closed recloser in @ 20:08
7081 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2021-08-27 08:55 | 2021-08-27 11:10 | 13 | 135 | 4160501 | 1755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | multile customers part powering found bad squeezes on pole 70-531 made repairs. complete
7082 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-05-13 20:10 | 2012-05-13 23:25 | 9 | 195 | 4786581 | 1755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE-TOP INSULATOR FAILED. REPAIRS COMPLETE BUT FUSE IS IN A DIFFICULT LOCATION. WILL HAVE TO FIND A BRIDGE AND WALK BACK TO FUSE. RESTORED @ 23:25. SH IDC XXXX
7083 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-02-13 07:02 | 2009-02-14 12:15 | 1 | 1753 | 59275-1 | 1753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9KV 23637 HWY421 ROCKHOUSE JUST PAST WESTEND MARKET ON LEFT RELEASED BY CREW 077S01 COMPLETED BY J. GILLY 12:15 2/14/2005 //VER/GAH IDC XXXX
7084 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-12-08 20:46 | 2008-12-09 00:25 | 8 | 219 | 55566-1 | 1752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 27597105 // RELEASED BY CREW 078S08//REPLACE BAD 50KVA AND CUTOUT AND ARRESTOR.//P R TOLLIVER/// VER/LDA L3/KEP IDC XXXX
7085 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-02-17 13:10 | 2022-02-17 14:53 | 17 | 103 | 4492001 | 1751 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 102-30. Not truck accessable. Cutout repaired closed at 14:53.
7086 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-01-07 09:30 | 2010-01-08 14:40 | 1 | 1750 | 65478-1 | 1750 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | GOING BACK WITH A CREW IN THE MORNING TALKED WITH CUST ABOUT THIS REPAIRED NEUTRAL LEADS BUT STILL HAVING PROBLEM RELEASED BY CREW 077S01 // THIS ORDER REPLACED ORDER 65037-1 THAT WAS CLOSED BY MISTAKE...(ADJUSTED TIME OFF TO TIME OF THAT ORDER). COD-1 IDCC CNT4 XXXX
7087 | Pikeville | 3407101 | TOPMOST | DEMA | 2014-09-02 13:50 | 2014-09-02 18:00 | 7 | 250 | 4447101 | 1750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 113-47 POLE DOWN/ CREW REQUIRED/ GOING TO OPEN LINE FUSE OPEN UP AT 113-44POLE 113-47 HAS ROTTED OFF AT THE GROUND LINE AND LAID OVER. 40-6 POLE. OPENED 15T LINE FUSE ON POLE 113-44 AT 13:50 EST SHOULD HAVE BACK ON BY 18:30. CREW ON THE WAYPOLE 113-47 HAS ROTTED OFF AT THE GROUND LINE AND LAID OVER. 40-6 POLE. OPENED 15T LINE FUSE ON POLE 113-44 AT 13:50 EST SHOULD HAVE BACK ON BY 18:30. CREW ON THE WAY FUSE CLOSED BACK IN AT 18:00 EVERYTHING OK/// COD 7 VER/DKG L3/DKG
7088 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-01-24 10:15 | 2016-01-24 16:05 | 5 | 350 | 4646651 | 1750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA TRANSFORMER FAILED ON 978-209. MAY NEED TO WINCH XFMR FROM SMALL TRUCK DUE TO NARROW ALLEY AND DEEP SNOW. CAN ACCESS WITH SERVICE BUCKET WITH NO PROBLEMS. CREW ENROUTE TO REPLACE. REPLACED AND RESTORED @ 16:05. SH/ ISO 38830978C10209/ COD 5/ VER/BOW
7089 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-08-13 13:52 | 2019-08-13 19:42 | 5 | 350 | 4883191 | 1750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on three phase bank pole. Crew enroute to assist. bReplaced three cutouts and restored @ 19:42. sh L3/HFP
7090 | Hazard | 3309003 | JEFF | VIPER | 2018-06-22 19:20 | 2018-06-23 09:55 | 2 | 875 | 4649321 | 1750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 7.2kv cutout on pole 415c3-37 Released by crew 077E04/ ISO 37830415C30037/ COD 2
7091 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-04-19 11:29 | 2008-04-19 21:12 | 3 | 583 | 52328-1 | 1749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308503//RELEASED BY CREW 077H15 REPLACED POLE AND RESTORED POWER ---- JEFF COMBS VER/ARN AJB
7092 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-03-23 23:32 | 2016-03-24 09:15 | 3 | 583 | 4875871 | 1749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRIED TO CALL CUSTOMER, NO ANSWER, WILL WORK DURING NORMAL WORK HOURS. BAD CONN. ON TRANS. REPAIRED // IDC OFF 8:45 BACK ON 9:15 TRANS POLE 38830069D28155
7093 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-08-20 08:56 | 2015-08-20 11:35 | 11 | 159 | 4156511 | 1749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 448-476 BURNT CROSSARM INTO, OPENED LINE FUSES AT 08:56 ON POLE 448-122 TO ISOLATE. RELEASED BY CREW 077S11 POWER RESTORED AT 11:35 /// COD-11 ISO LF @ 37830448B00122 VER/HFP L3/HFP
7094 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-05-05 23:00 | 2017-05-06 00:16 | 23 | 76 | 4758761 | 1748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE @ 181-64,LIFTED HOT TAP @ 181-63 & GROUNDED AND TAGGED TO VERNON MULLINS, 181-156 LINE FUSE BACK IN @ 00:16,POLE BURNT OFF @ CUTOUT SHOULD BE ABLE TO LOWER XFR AND CONDUCTER,,FIRE DEPT, SPRAYED POLE AND FIRE IS OUT RELEASED BY CREW 078S05/CREW ON SITE/FETR 0730/VEM/REPAIRS MADE AND ALL CUST RESTORED /PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/ARN AJB
7095 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-11-16 14:59 | 2008-11-16 15:45 | 38 | 46 | H65702-1 | 1748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3411902// TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. 50 KVA ON POLE 97-254. I WILL CALL DUTY SUPER. WE CHANGED TRANSFORMER. LOST FUSE WHEN TRIED TRANSFORMER VER/KEP MLR OK IDC XXXX
7096 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-07-23 14:04 | 2008-07-23 21:21 | 4 | 437 | 58932-1 | 1748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED 37.5 YARD DOG NEEDED SEND TO LLOYD M. RELEASED BY CREW 078S08// GETTING HELP TO RELOCATE XFR TO NEXT POLE/ POWER ON @ 21:21LOADING YARD DOG AND PICKING UP TOOLS//3001203//VER/CRB
7097 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-02-13 06:00 | 2016-02-13 13:17 | 4 | 437 | 4692471 | 1748 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, UG | BAD SEC. U.G...REPAIRED BAD SPLICE IN U.G.SERVICE, POWER RESTORED AT 13:17,,,,, THIS SERVICE NEEDS TO BE REBUILT ASAP, FOR MORE INFO SEE T SMITH. . DAIRY QUEEN ONLY CUST. WITH OUTAGE. VER/TOM L3/TOM
7098 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-08-23 20:46 | 2012-08-24 11:20 | 2 | 874 | 4966951 | 1748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKING.BAD 25 KVA, 19.9 TRANS. WILL NEED 1 MAN, BIG BUCKET AND A NEW TRANS. TO MAKE REPAIRS. RELEASED BY CREW 075H01//REPAIRS COMPLETE//COD 2// VER/DBM IDC XXXX
7099 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-05-17 13:46 | 2011-05-17 15:02 | 23 | 76 | 4105531 | 1748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FUSE OPEN ON POLE 38830501000319 PATROLLING LINE. FOUND BAD POLE TOP PIN INSULATER ON 501-231 MADE REPAIRES ALSO VERY SMALL LIMB ON LINE UNDER INSULATER. ALL POWER RESTORED AT 1502 CLOSE TICKET//COD 23
7100 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2016-04-29 00:16 | 2016-04-29 14:50 | 2 | 874 | 4140251 | 1748 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL WORK ACCORDING TO AFTER HOURS GUIDELINE..NEED TO STRAIGHTEN POLE AND REPLACE SECONDARY. RELEASED BY CREW 077S04 FOUND BAD SECONDARY CONNECTION MADE REPAIRS COMPLTED AT 1450 CREW 077H01 VER/AWD
7101 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-04-26 16:45 | 2010-04-26 18:17 | 19 | 92 | 51535-1 | 1748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE FUSE ON POLE 47-249 AT 16:45 RELEASED BY CREW 074S05/// CUTOUT HAD FAILED REPLACED BAD CUTOUT AND ARRESTOR AND RESTORED POWER AT 18:17 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC XXXX
7102 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-10-12 09:31 | 2020-10-12 15:20 | 5 | 349 | 4547721 | 1745 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | C phase riser fuse out on 38831077D00434 will refuse and try. bad ug conductor will need a crew//MADE MD TO SHOW RISER FUSES//COD 1//
7103 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-08-06 19:01 | 2016-08-06 20:50 | 16 | 109 | 4743891 | 1744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED 911 WITH AN ETA OF 1950//BASD 12 KV C/O
7104 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-07-06 13:22 | 2011-07-06 17:00 | 8 | 218 | 4475501 | 1744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//VER/CRB IDC XXXX
7105 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-02-25 08:42 | 2010-02-25 12:20 | 8 | 218 | 60800-1 | 1744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHANGE BAD CUTOUT//COD 8// VER/DBM IDC XXXX
7106 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-11-21 08:21 | 2021-11-21 12:30 | 7 | 249 | 4112121 | 1743 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Theres a bad UG secondary conductor in a pedestal at this location. This will require help to dig up this pedestal and splice this UG. The pedestal is located directly behind this customers meter base. 1/0 UG. Restored 1230/awaiting order to release in system.
7107 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-09-23 11:39 | 2010-09-23 13:53 | 13 | 134 | 52790-1 | 1742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-OUT ON 3-PH ALREADY CALLED P,R,C CREW CHANGE OUT BAD CUT-OUT //VER/CRB IDC XXXX
7108 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2014-11-01 06:29 | 2014-11-01 21:14 | 2 | 885 | 4679571 | 1741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED 40/5 POLE DEADEND WITH TRANSFORMER BURNT OFF/LINE FUSE ON 329-1 BLOWN BACK IN AT 0819 HRS ISOLATED ON 329-10 1 CUSTOMER STILL OFF /FAULT ON 329-138 RELEASED BY CREW 078S03 RELEASED BY CREW 078H03CREW REQUIRED 40/5 POLE DEADEND WITH TRANSFORMER BURNT OFF/LINE FUSE ON 329-1 BLOWN BACK IN AT 0819 HRS ISOLATED ON 329-10 1 CUSTOMER STILL OFF /FAULT ON 329-138 RELEASED BY CREW 078S03,,CREW ON SITE
7109 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-07-03 09:59 | 2012-07-04 15:00 | 1 | 1741 | 4266221 | 1741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED B PHASE XFORMER BAD 50KVA TRUCKS TO POLE. XFORMER BANK ON PLATFORM. WILL NEED NEW RISER WIRE FOR XFORMERS AND 3 NEW CUTOUTS. RELEASED BY CREW 078M03CREW REQUIRED B PHASE XFORMER BAD 50KVA TRUCKS TO POLE. XFORMER BANK ON PLATFORM. WILL NEED NEW RISER WIRE FOR XFORMERS AND 3 NEW CUTOUTS. POWER RESTORED AT THIS LOCATION AT 15:00 ON 7/4/2012 IDC XXXX
7110 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2017-04-23 11:17 | 2017-04-23 12:17 | 29 | 60 | 4670971 | 1740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED RECLOSERS ON 37830234000137 (COD 29) TO SAFELY MAKE REPAIRS TO DOWNED WIRE ON ORDER 4670491. OPENED AT 1120. ISOLATED AND TAGGED TO D SAMMONS. OPENED 1117-1217. VER/AWD L3/HFP XXXHFP AJB
7111 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-02-22 16:57 | 2014-02-22 22:45 | 5 | 348 | 4426931 | 1740 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL HAS PULLED LOOSE IN SPLICE IN SPAN OF 2/3 SECONDARY CONDUCTOR. I AM CALLING FOR HELP TO REPLACE WIRE. I AM GOING TO RUN NEW SERVICE FROM ANOTHER TRANSFORMER POLE. RELEASED BY CREW 074S01SEND TO ENG. DEPT. WE NEED TO CHANGE TRANS. TO A 25KVA ON POLE 37820103B00191. IT IS ONLY A 15 KVA NEUTRAL HAS PULLED LOOSE IN SPLICE IN SPAN OF 2/3 SECONDARY CONDUCTOR. I AM CALLING FOR HELP TO REPLACE WIRE. I AM GOING TO RUN NEW SERVICE FROM ANOTHER TRANSFORMER POLE. WE RELOCATED SERVICE TO POLE 378 //VER/GAH
7112 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-07-19 19:50 | 2012-07-19 22:44 | 10 | 174 | 4778111 | 1740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE VER/KEP IDC XXXX
7113 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-05-13 21:26 | 2019-05-13 23:51 | 12 | 145 | 4266041 | 1740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer, states entire hollow is out//line fuse out on 1099-31. patrolled line saw no hazards. looks like line fuse on 1099-31 failed. restored power at 23:51//cod 12// L3/HFP
7114 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-01-19 12:28 | 2011-01-19 13:55 | 20 | 87 | 62717-1 | 1740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 37830345B40420 1 SPAN WIRE DOWN == WIRE BROKE AT SPLICE == REPAIRED LINE == REFUSED POWER OK VER/KEP L3/KEP IDC XXXX
7115 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2015-12-13 14:37 | 2015-12-13 17:50 | 9 | 193 | 4528991 | 1737 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER LUG CONNECTION FAILED. ATTEMPTING TO CLEAN UP LUG AND REPLACE RISER. REPLACED #4 CU RISERS WITH 2/0 COPPER AND REPAIRED LUG. RESTORED @ 17:50. SH COD-9 ISO TF 38830834A00127 VER/HFP L3/HFP AJB
7116 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2017-12-27 03:41 | 2017-12-27 05:45 | 14 | 124 | 4680711 | 1736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer // lights are very dim // large appliances wont run, no heat // meter is flashing all zeros // recommened customer turn off main breaker until servicer arrives // Repaired. Had xfmr open frpm 5:20 to 5:45. sh //originally affecting 3 custoemrs per servicer//opened xfmr to make repairs//cod 3 + 11//
7117 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-06-29 14:28 | 2008-06-29 18:05 | 8 | 217 | 59441-1 | 1736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-4309 HOT TAP BROKE OFF VER/KEP IDC XXXX
7118 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-10-22 09:32 | 2009-10-22 13:09 | 8 | 217 | 64236-1 | 1736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 32325968 POLE 1123-6612 BAD CUTOUT AND LA ALSO RUBBER CAP AND ANIMAL GUARD CALLED RAYBURN TO GET CREW//LINES COVERED UP NEED R/W CUT SEND TO O.C TO HAVE CUT// VER/DBM IDC XXXX
7119 | Whitesburg | 3409503 | BURDINE | JENKINS | 2014-01-24 09:37 | 2014-01-24 13:45 | 7 | 248 | 4307841 | 1736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KPOOVA XFMR, WE NEED MATERIAL HANDLER BUCKET AND XFMR AND CUT OUT RELEASED BY CREW 077S12 RESTORED @13:45POWER COD-7 ISO TF 37830382C10039 VER/HFP L3/HFP IDC XXXX
7120 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-07-16 14:07 | 2021-07-16 19:54 | 5 | 347 | 4920851 | 1735 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a Hot Leg into at Trans,Going to pull Meter and Resqueeze Conductor..Made repairs and restored at 19:54,Checked Voltage and its good Now.
7121 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2015-05-26 09:27 | 2015-05-26 15:14 | 5 | 347 | 4464141 | 1735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA TRANS. IS BAD IN A BANK OF TRANSFORMERS ON POLE 24B-224. TIM HALL IS SENDING CREW TO CHANGE TRANS. RELEASED BY CREW 074S01/// REPAIRS MADE ON AT 15:14 R RAY/COD 5// VER/ ADH
7122 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-02-13 15:47 | 2009-02-13 16:38 | 34 | 51 | 60316-1 | 1734 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302//CREWS OPENED LINE IN ORDER TO MAKE REPAIRS ON ANOTHER OUTAGE 58315-1//CUTOUT BROKEN ON POLE 175-11//COD 34 MLR OK IDC XXXX
7123 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-11-18 04:46 | 2020-11-18 09:35 | 6 | 289 | 4703941 | 1734 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Line fuse out on pole 329-15. wire down from pole 329-90 to pole 329-85.. primary conductor is only conductor down.. 6A wire//hold for normal start per duty/no tags or groundsLine fuse out on pole 329-15. wire down from pole 329-90 to pole 329-85.. primary conductor is only conductor down.. 6A wire Released by crew 077S11 power restored at 09:35
7124 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2022-01-20 14:01 | 2022-01-20 16:50 | 28 | 169 | 4391551 | 1732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | top broke off on dead end pole fire at pole 44-4587 crew required no trucks needs pole top extension. hot tap lifted at 44f4501 no tags no grounds Released by crew 078S09top broke off on dead end pole fire at pole 44-4587 crew required no trucks needs pole top extension. Tap lifted at 44C2-4501 fuse at 44C1-4028 closed at ___16:50. Ticket
7125 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2017-05-06 01:44 | 2017-05-06 07:30 | 5 | 346 | 4759101 | 1730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFM. CUTOUT BROKE DOWN AND BURNT TOP OF POLE 266-275 OFF WILL BE ABLE TO FRAME DOWN ON POLE.WILL NEED 19.9 CUTOUT AND BRACKET 19.9 DEADEND INSULATOR AND ONE MAN WITH BIG BUCKET TO MAKE REPAIRS.. VER/ARN
7126 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2015-08-25 00:07 | 2015-08-25 04:14 | 7 | 247 | 4169681 | 1729 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD ARRESTOR ON POLE 37830294000257 TRUCK ACCESS IF DRY..LINE CUTOUT BROKE ON POLE 37830294000202. POWER RESTORED.//COD 7//AED ENTRY CREATED// VER/HFP L3/HFP
7127 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2009-12-02 16:11 | 2009-12-02 17:23 | 24 | 72 | 58167-1 | 1728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQUEST 32908319 // POLE 45-3034 BURNT OFF POLE 45-3034 SEND TO VERNON M..//COD 24//OPENED FUSE ON POLE 38830045C24698 @ 1611//ISO//CREW ON SITE/MAKING POLE SAFE/FETR1845/VEM/ALL CUST RESTORED 1723/PLEASE CLOSE TICKET/THANKS/VEM IDCC TOF1552, PN3035, CNT30 XXXX
7128 | Hazard | 3303902 | LESLIE | WOOTON | 2015-08-05 11:18 | 2015-08-05 12:30 | 24 | 72 | H4979111 | 1728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD 6DISC ON FUSE POLE WILL NEED LINE CREW IN THE AM TO MAKE REPAIRS RELEASED BY CREW 077S01 OPENED STEPDOWN AT 11:18 CLOSED AT 12:30// VER/ ADH /// VER TIMES PER VOICE REC - DUP OF 4979111 FOR STEPDOWN OUTAGE OF 14 CUST L3/HFP HFPC DUP AJB
7129 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-06-17 18:06 | 2015-06-17 21:42 | 8 | 216 | 4589151 | 1728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTNING ARRESTER/ PUT IT IN ABNORMAL NEEDS REPLACED/ ISO 37840384000028/ COD 8/ VER/BOW
7130 | South Williamson | 3200302 | BELFRY | TOLER | 2014-07-02 07:32 | 2014-07-02 12:20 | 6 | 288 | 4181931 | 1728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079S02 BAD TRANSFORMER CUTOUT. REPLACED CUTOUT, POWER IS BACK ON.//COD 6// VER/DBM
7131 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-06-02 19:37 | 2009-06-03 10:00 | 2 | 863 | 61577-1 | 1726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 140-422 BAD 25KVA NOTRUCKS PLEASE CHG.. CUTOUT OUT TYPE RELEASED BY CREW 078S08 // BACK ON @ 1000 VER/TOM L3/TOM IDC XXXX
7132 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-07-31 00:55 | 2013-07-31 02:50 | 15 | 115 | 4608721 | 1725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 70-3009 20T POLE70-3032 BAD LA POLE 70-3040 10T TRANS FUSE IDC XXXX
7133 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-04-17 18:24 | 2018-04-18 00:09 | 5 | 345 | 4247641 | 1725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 50 kva trucks ok/ ISO 38830269D00071/ COD 5/crew on site/FETR0045/vem/repairs complete and all cust restored 0009/please close ticket/thanks/vem
7134 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2020-05-19 14:20 | 2020-05-19 17:05 | 41 | 165 | 4857501 | 1725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO OUTAGE TILL TRANSFORMERAND L/F OPENED ON POLE 37830449A20045//COD 41//REPAIRING CONNECTIONS. Found cracked cutout on pole 449A-45 and need to open tap fuse feeding across river to make repairs safely. opened xfer and tap @ 1626 made rapairs and restored all customers @ 1705
7135 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-08-15 17:49 | 2021-08-15 19:44 | 15 | 115 | 4072881 | 1725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout 38831061A00191broke cutout
7136 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-05-06 05:55 | 2018-05-06 15:30 | 3 | 575 | 4313811 | 1725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Crew reqd. broke cutout on pole 188-201. Possibly use small bucket with mopad. Cust on corner says ok if need to use truck.. Released by crew 078H17
7137 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-03-09 16:15 | 2011-03-10 02:14 | 10 | 599 | 52383-1 | 1724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT BURNT OFF TOP OF POLE 161-101, NO TRUCKS TO POLE ,CAN GET YARD DOG. LIFTED HOT TAP ON POLE 161-24. POLE 161-101 IS 35/5, NEED TO GO BACK WITH 40/5. RELEASED BY CREW 078S01//TRACK BUCKET JOB PRT//T-BUCKET ON SITE PRT//REPLACED CUTOUT/ARRESTOR AND LOWERED ATTACH. ALL POWER RESTORED AT 02:14 PRT// IDC XXXX
7138 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-08-20 08:30 | 2010-08-20 09:52 | 21 | 82 | 58560-1 | 1722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE OUT FROM POLE 72-171, TWO PHASE WRAP TOGETHER BETWEEN POLES 72-7 AND 72-8//COD 21// VER/DBM IDC XXXX
7139 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-03-03 16:53 | 2019-03-03 21:40 | 6 | 287 | 4947341 | 1722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | need power temp, bad neutral,installed power temp all cust restored please close ticket thanks.bt
7140 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-10-29 18:09 | 2017-10-29 22:15 | 7 | 246 | 4510251 | 1722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 247-976, BAD CUTOUT ON POLE 247-1093, MAN COMING TO HELP. POWER RESTORED/// VER/DKM L3/HFP XXXHFP ACB
7141 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-06-05 20:26 | 2017-06-05 22:29 | 14 | 123 | 4913191 | 1722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED BAD DEADEND INS ON38830499000040 APR AT 2229 CLOSE TICKET VER/CRB
7142 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-10-23 13:38 | 2009-10-23 16:13 | 19 | 155 | 66523-1 | 1721 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 32348BIRD AT FUSE POLE.GOT ALL CUSTOMERS BACK ON EXCEPT 1 CUSTOMER BAD CUTOUT.F REPLACED CUTOUT.FIRSR 18 CUSTOMERS BACK ON AT 15:05. L3/HFP IDC XXXX
7143 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-07-09 15:53 | 2010-07-09 18:45 | 10 | 172 | 64162-1 | 1720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD DEAD END INSULATOR, WILL CHANGE OUT,..ALL POWER RESTORED @ 18:45HRS COD-10 VER/HFP L3/HFP IDC XXXX
7144 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2016-07-03 21:55 | 2016-07-04 01:30 | 8 | 215 | 4519501 | 1720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | BAD 50 KVA, 19.9 TRANSFORMER, NEED 2 MEN AND A BIG BUCKET .GUY GOT INTO PRIMARY BUSHING ON TRANSFORMER, REPULLED GUY, POWER RESTORED @ 01:30 VER/KEP
7145 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-07-17 20:19 | 2014-07-17 20:28 | 191 | 9 | 4257831 | 1719 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | AJB
7146 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-08-18 12:23 | 2010-08-18 15:30 | 16 | 187 | 57625-1 | 1717 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CENTER PHASE FUSE ONLY BLOWN ON 901-21. PATROLLING LINE. FOUND BAD DEADEND INSULATOR ON 925-33 ON LATTERAL TO 925-243. ISOLATED AND RESTORED ALL CUSTOMERS EXCEPT ONES ON AFFECTED TAP. XFMR ON 33 IS ON UNTIL CREW RETURNS WITH BUCKET AND MATERIAL TO MAKE REPAIRS. CREW ENROUTE. CLOSED FUSE ON 21 @ 14:05. REPLACED INSULATOR AND RESTORED REMAINING CUSTOMERS @ 15:30. SH//VER/CRB IDC XXXX
7147 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-03-04 06:54 | 2015-03-04 09:30 | 11 | 156 | 4096551 | 1716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN, PATROLLING THE LINE. BAD TRANSFORMER CUTOUT ON POLE 38821137D00388. ILL REPLACE THE CUTOUT. VER/CRB L3/DKGXXXX
7148 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-06-05 19:06 | 2008-06-06 02:15 | 4 | 429 | 58596-1 | 1716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000701//BAD 50KVA VER/KEP
7149 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-08-04 12:14 | 2009-08-04 17:00 | 6 | 286 | 55205-1 | 1716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP RELEASED BY CREW 074S02 REPLACED CUTOUT. COD-6 ISO TF L3/HFP IDC XXXX
7150 | South Williamson | 3411401 | DEWEY | INEZ | 2011-05-01 07:59 | 2011-05-01 12:45 | 6 | 286 | 53098-1 | 1716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 19.9 /XFMR ON POLE 743-121//NO TRUCK//CREW REQUIRED//CHANGING NOW//RESTORED AT 12:45//COMPLETE/EM //COD 6// VER/DBM IDC XXXX
7151 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-02-15 13:55 | 2010-02-15 19:13 | 38 | 318 | 57970-1 | 1716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830182D00314, ISOLATED AT 38830182D00307, CLOSED FUSE AT 14:25 RELEASED BY CREW 078S05 POWER ON @ 19:13 VER/KEP L3/KEP IDC XXXX
7152 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2015-04-20 07:50 | 2015-04-20 11:55 | 7 | 245 | 4338811 | 1715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ROW CREW ENROUTE TO CUT TREE AT POLE 92, LOWERED PRIMARY AND GUY AND INSTALLED NEW CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ/ ISO 37830234000192/ COD 7 VER/HFP L3/HFP
7153 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-11-07 10:16 | 2017-11-07 11:05 | 35 | 49 | 4537241 | 1715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout need line crew === manual pole replaced cutout and arrester === pen line at 10:16 closed at 11:05 power ok L3/HFP XXXHFP
7154 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2014-10-04 07:25 | 2014-10-04 11:24 | 15 | 239 | 4551161 | 1713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 469-1, BAD CUTOUT ON POLE 445-63 BURNT POLE OFF, ALSO BAD 50 KVA XFMR, REPAIRED POLE ISOLATED XFMR CLOSED LINE FUSE IN AT 09:00 .REPLACED XFMR RESTORED POWER AT 11:24 RELEASED BY CREW 077S11 VER/CRB IDCC TOF0631 ESTIMATED TIME OFF XXXX
7155 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-05-30 23:04 | 2008-05-31 13:20 | 2 | 856 | 53068-1 | 1712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3008701// BAD UNDERGROUND /CREW WILL WORK 5-31-08/CONTACT DAN HUFF IN AM UNDERGROUND SECONDARY FEEDER WILL NEED REPLACED AT LATER DATE...INSTALLED 2 POWER TEMPS TO RESTORE SERVICE TO 2 MOBILE HOMES BLR RESTORED AT 1320 VER/ARN IDC XXXX
7156 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-05-09 21:24 | 2014-05-10 04:32 | 4 | 428 | 4679911 | 1712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL REPLACE XFMR . CREW IS IN ROUTE VER/ARN
7157 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2021-12-28 17:11 | 2021-12-28 20:45 | 8 | 214 | 4233311 | 1712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew require flaggers also truck ok Released by crew 078S03//arrived RM &levi grayson
7158 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2013-01-29 23:44 | 2013-01-30 14:00 | 2 | 856 | 4752641 | 1712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AS PER AFTER HOURS DISPATCH GUIDELINES, WILL CHECK THIS DURING REGULAR WORK HOURS//.. BAD XFMR ON POLE 494-117 THIS A 25 KVA 19.9 CAN USE TRUCK RELEASED BY CREW 077S11.CHANGED TRANS. CLOSED BACK IN AT 1400 ///VER/CRB L/3 CRB IDC XXXX
7159 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-09-21 20:03 | 2017-09-21 21:33 | 19 | 90 | 4380251 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREWS WILL OPEN THE LINE FUSE ON POLE 38830045B22688 AFFECTING CUSTOMERS ON BOTH EDGEWOOD AVE. & HIGHLAND AVE. FROM 7:30PM UNTIL 11:00PM ON 9/21/2017. THIS OUTAGE IS NECESSARY TO MAKE EMERGENCY REPAIRS TO AEP FACILITIES. WE APOLOGIZE FOR ANY INCONVENIENCE THIS MAY CAUSE.--CREW ON SITE--OPEN LF 45-2688 @ 20:03---ALL REPAIRS MADE--CLOSED LF 45-2688 @ 21:33---TBL TKT COMP---RMV//19 COD/// VER/DKM L3/HFP XXXHFP
7160 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-07-06 21:10 | 2016-07-07 11:25 | 2 | 855 | 4551211 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05,,CREW ON SITE,,REPLACED XFMR, CUTOUT AND ARRESTER,,ALL POWER RESTORED COD-2 ISO TF 38830184B00240 VER/HFP L3/HFP
7161 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2019-06-18 10:55 | 2019-06-18 15:20 | 8 | 265 | 4537981 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | T LEWISbad secondary connections @ 1148-41, sec between 41 and 40. to tyler lewis Released by crew 078S07 ????????????????????????????????????
7162 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-01-08 07:06 | 2021-01-08 09:00 | 15 | 114 | 4855651 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broke. ooMAP DESCoo Primary ug from padmount 809-1066 is parked in 809-1067. 30T fuse on 809-1064 thats marked N.O. is in use and feeds padmount xfmrs 1065 & 1066. This is the 30T that was broke. Restored @ 9:00. sh//COD ACTUALLY 15
7163 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-10-07 07:22 | 2015-10-07 08:57 | 18 | 95 | 4324401 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BLOWN ON POLE 41 CHECKING NOW!! FUSE LOOK TO BE BROKE INSTEAD OF BLOWN.. J/// COD-18 ISO LF 38830850000041 VER/HFP L3/HFP
7164 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-02-07 16:51 | 2017-02-07 17:21 | 57 | 30 | 4367901 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE ON 39831123D16032 TO SAFELY REPLACE CUTOUT ON POLE 39831123D16089. RELATED TO 4365061. OPENED 1651-1721. COD 57 (MINUS 2 ON TRANSFORMER) VER/AWD L3/HFP XXXHFP AJB
7165 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2008-12-11 17:44 | 2008-12-11 18:02 | 95 | 18 | 56818-1 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400601/ HARVEY FOUND SOLID BLADES ON POLE 211B-421 IN TROUBLE // WILL NEED TO OPEN 187A-362 B PHASE 95 COD//- WATCHING UNTIL CREW GETS THERE/// WORK REQUEST 27649767 // +1 MISMAPPED CUSTOMER// L3/IDC IDC XXXX
7166 | Hazard | 3303902 | LESLIE | WOOTON | 2014-12-06 06:48 | 2014-12-06 12:30 | 5 | 342 | 4838961 | 1710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 CUTOUT WENT BAD TOP OF POLE BURNT OF 37830510000164 VER/CRB
7167 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-06-27 14:38 | 2012-06-27 22:03 | 5 | 445 | 4968441 | 1709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | PRIMARY U.G. SERVICE RELEASED BY CREW 074S05. ISOLATED XFMR 24-1099. CLOSED FUSE AT 24-659 ENERGIZING XFMR 24-1097 AT 17:45. WILL TRY TO FIND FAULT. FAULT FOUND, HAVE ADDNL DIGGING TO DO TO SPLICE. RELEASED BY CREW 074H03 //VER/CRB L/3 CRB
7168 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-03-26 14:29 | 2017-03-26 15:30 | 28 | 61 | 4585901 | 1708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLED NOTHING FOUND/ CHANGED LINE FUSE CUTOUT AND CLOSED BACK IN 38830069D16067/ ISO 38830069D16067/ COD 28/ VER/BOW AJB
7169 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-10-05 03:31 | 2018-10-05 10:38 | 4 | 427 | 4199461 | 1708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines.line fuse out on 1057C00041 & xfmr fuse out on 38821057C00042 .have a bad 19.9 epoxalator on pole 38821057C00204. will need dead end insulator.fiberglass t bracket cutout & arrestor. & material handler.
7170 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2018-03-19 08:20 | 2018-03-19 12:24 | 7 | 244 | 4025591 | 1708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY RISER BURNED OUT AT XFR LUG,WILL REPAIR IF POSSIBLE 38820967A00085SECONDARY RISER BURNED OUT AT XFR LUG,WILL REPAIR IF POSSIBLE////////MADE NECESSARY REPAIRS&RESTORED.XFR OFF 12:15,ON 12:24
7171 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-03-29 22:39 | 2014-03-30 06:17 | 6 | 458 | 4537611 | 1707 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 92-6004 BURNT OFF LINE FUSE OUT 92-253 40T POLE 92-4001 REMOVED HOT TAP GROUNDED LINE FOR VERNON CLOSED FUSE ON POLE 92-253 AT 12:30 3- CUST OUT RELEASED BY CREW 078S08/CREW ON SITE/FETR0600/VEM/GETTING EQUIP OFF OF HILL/NEW FETR 0630/VEM/REPAIRS MADE AND POWER RESTORED TO 3 CUST @0617/PLEASE CLOSE TICKET/THAKS/VEM RELEASED BY CREW 078H14 VER/KEP IDC SIX TOTAL CUSTOMERS XXXX
7172 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-06-14 22:24 | 2014-06-15 12:37 | 2 | 853 | 4092311 | 1706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE TREES REMOVED NEED LINE CREW BAD CUTOUT NO TRUCK HAVE MAIN LINE FUSE OPEN LINE GROUNDED 67-116 // VIRGIN & GOBLE & RUGGLES & SIMMONS /// TAGS PLACED FOR KY DDC - CONTACT DDC UPON ARRIVAL///RETAGD TO R VIRGIN(CREW)///CHANGED CUTOUT AND LA///PWR ON @ 12:37///TBL TKT COMP COD-2 ISO LF 38830067D00116 VER/HFP L3/HFP
7173 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-06-23 21:47 | 2015-06-24 10:42 | 4 | 775 | 4647931 | 1705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | L/F BLOWN ON 38831127A00385//WILL PATROL/BAD CSP 1127-402/L/F BLOWN ON 38831127A00385//WILL PATROL// BAD CSP XFMR ON POLE 38831127A00402// WILL NEED 25 KVA / CUTOUT / FIBER. BRACKET / TRUCK OK // VERY TIGHT LOCATION FOR TRUCK RELEASED BY CREW 074S05..REPLACED XFMR SERVICE RESTORED.D LEWIS// VER/ ADH
7174 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2019-05-07 08:36 | 2019-05-07 10:58 | 12 | 142 | 4234891 | 1704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 380-A-20. cutout on pole 380-A-93 looks bad.. looks like its been smoked.. cuout changed.. power restored @ 10:58 L3/HFP
7175 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-07-23 08:38 | 2009-07-23 12:11 | 8 | 213 | 64687-1 | 1704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP DUPLICATING FOR FUSE OUTAGE // OPENED LINE FUSE ON POLE 39831147A00172 AT 09:15--BAD CUTOUT BURNT POLE OFF-NEED CREW--V MULLINS TO WORK /// 8 CUSTOM OFF @ 0838 & 7 MORE @ 0915/CREW LOADING MATERIAL/FOREMAN ON SITE/FETR1315/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1211/PLEASE CLOSE TICKET/THANKS/VEM L3/HFP IDC XXXX
7176 | South Williamson | 3200302 | BELFRY | TOLER | 2010-04-02 16:29 | 2010-04-02 16:53 | 71 | 24 | 57621-1 | 1704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPEN RECLOSER TO SAFELY REPLACE CUTOUTS ON ORDER 57440 VER/KEP AJBC INLT ONLY C PH ON SW 40A-3 WERE OUT. OP ALL PH ON OCR 15D-81 IDCC XXXX
7177 | Hazard | 3309302 | VICCO | JEFF | 2010-03-01 01:48 | 2010-03-01 04:10 | 12 | 142 | 61775-1 | 1704 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3309302///, CUST SAYS THEY HAVE PART POWER, CHECKING PROBLEM, FOUND SEC LEAD ON XFMR BURNT INTO, REPAIRED IDC XXXX
7178 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2016-01-07 09:39 | 2016-01-07 16:45 | 4 | 426 | 4591981 | 1704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE. REPLACED AND RESTORED @ 16:45. SH/ ISO 38830834B00302/ COD 4/ VER/BOW
7179 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-12-01 20:25 | 2009-12-01 22:47 | 12 | 142 | 54441-1 | 1704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 224-386 BURNT IN TWO PER RUSSELL AKEMON // POWER STILL ON BUT POLE IS BURNT INTO, POSSIBLY CAN USE POLE EXT. AND NOT HAVE TO CHANGE OUT POLE. TOLD JEFF COMBS WHAT WE HAVE HERE. NO POWER OFF RIGHT NOW //OPENED FUSE ON POLE 37830224B00370 IN ORDER TO MAKE REPAIRS//ISO//COD 12// VER/DBM IDC XXXX
7180 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2016-11-28 18:28 | 2016-11-28 19:42 | 23 | 74 | 4135091 | 1702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD HOT TAP VER/CRB AJB
7181 | Pikeville | 3402003 | KEYSER | MULLINS | 2015-06-21 05:28 | 2015-06-21 12:33 | 4 | 425 | 4626181 | 1700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINEF IS OUT,WILL PTRL/////POLE 1127-392 HAS 2 REALLY BAD EPOXILATOR DEAD-END INSULATORS,NEED CREW,2 INSULATORS,NO APPROACH,ALSO MAY CHANGE CUTOUT ON 386 ALSO //////NOTE NEW FETR//////CREW ON-SITE10:35/////////REPAIRS COMPLETED,RESTORED// VER/ ADH
7182 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-06-11 15:00 | 2008-06-11 16:25 | 20 | 85 | H62755-1 | 1700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308602// RELATED TO ORDER 62727-1 CREW OPENED RECLOSER TO ALLOW THEM TO REPLACE CUTOUT THAT BROKE AND WAS HANGING ON THE POLE ARCING.37830458000195 IDC CREATED ORDER FOR ORIGINAL CUSTOMERS XXXX
7183 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2009-03-04 18:35 | 2009-03-04 19:00 | 68 | 25 | 55083-1 | 1700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW HAD TO OPEN RECLOSER TO ALLOW THEM TO SAFELY REPLACE A DEFECTIVE CUTOUT....RELATED TO ORDER 55016-1. L3/HFP IDCC CNT67 XXXX
7184 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-04-04 18:23 | 2010-04-04 19:31 | 25 | 68 | 58515-1 | 1700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW OPENED FUSE TO SAFELY REPLACE POLE249-230 VER/KEP L3/KEP AJB
7185 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-04-28 18:55 | 2017-04-28 20:41 | 16 | 106 | 4692631 | 1696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE37830254B00004//FOUND TRANSFORMER FUSE BLOWNON POLE37830254D00131, PULL VINES OFF CLOSE TRANFORMER,,BAD ARRESTER ON POLE 254-131,CUT IN CLEAR//MADE AED //NO CUSTS ON TRANS 37830254D00131 VER/CRB L3/HFP XXXHFP
7186 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2018-01-02 09:00 | 2018-01-02 14:39 | 5 | 339 | 4696631 | 1695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 182-3560,csp 25 kva xfr leaking oil,,,RESET xfr and customers back on @ 11:36 ,,,,CREW REQUIRED trucks to pole,,NEED to go back with 37.5 kva Released by crew 078S05 crew on site fetr 15:45 all pwr resored @ 14:39 please close ticket lrm/ ISO 38830182B43560/ COD 5
7187 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2020-08-25 21:39 | 2020-08-25 23:48 | 19 | 129 | 4378671 | 1695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | no crew required recloser back in at 2245 hrs to 272-73 back on at 2348 hrs Released by crew 078S03
7188 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-12-24 10:23 | 2022-12-24 15:30 | 20 | 307 | 4343351 | 1694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | L/F ON POLE 38831027C00196//MD MADE//COD 20//BAD TRANSFORMER ON POLE 38831003D20337//OPEN L/F ON POLE 38831027C00196//MD MADE//COD 20// crew required crew wil need a 25KVA 7200 xformer and a 7200 cutout///// can get a bucket truck to pole 1003-337 to chage xformer out. Released by crew 074S03 Released by crew 074H11
7189 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-12-28 21:15 | 2017-12-28 23:36 | 12 | 141 | 4686601 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out, fuse broke/ ISO 37830277000022/ COD 12xfmr fuse out, fuse broke. xfmr on pole 277-20. power restored
7190 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-08-31 17:17 | 2021-08-31 20:25 | 9 | 188 | 4186711 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found bad cutout on pole 20-3055 made repairs. line fuse on pole 20-3028 back in @ 20:25. complete
7191 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-02-27 09:48 | 2008-02-27 14:30 | 6 | 282 | 50861-1 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CSP TRANSFORMER BREAKER/ CALLED CREW//BAD CONNECTION AT SECONDARY/ NEED NEW 1/0 RISER WIRE-1/0 TWIST AN NEW PRIMARY RISER AN NEW HOTTAP RELEASED BY CREW 078S07//3116703 IDC XXXX
7192 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2008-07-29 21:30 | 2008-07-30 02:12 | 6 | 282 | 61977-1 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000301//BAD 25 KVA CSP TRANSFORMER-NEED 37.5 NEW RISER WIRE AN CUTOUT-CALLED CREW- SEND TO V MULLINS RELEASED BY CREW 078S07//WR#25498399/ COD-6 // //WR#25498399/CREW ON SITE/FETR0145 PER SVCR VER/LDA IDC XXXX
7193 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-08-02 09:37 | 2018-08-02 10:24 | 36 | 47 | 4894481 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Conductor has broke out of Deadend shoe and sagged down close to primary neutral and service drop. Pole 1105-C-18 and the Neutral is caught under and D.D. Light head at 1105-c-288 Both will require outages to repair/// Repairs made and resored at 10:24 Off at 9:37. Tim McCoy L3/HFP
7194 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-11-15 21:39 | 2018-11-16 11:45 | 2 | 846 | 4431071 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 7200 trans. on pole 25-C-116, this will need a line crew and a tree crew to cut a path, manual pole 300 ft. up on mtn. line crew needs to look at this first and see which way they want to winch in trans. This needs to be done during daylight hours. Released by crew 074S05 repairs made on at 11:45 d sammons
7195 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-03-09 05:50 | 2022-03-09 08:58 | 9 | 188 | 4591631 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Fuse is open on 525-76 patrolling line////// Replacing broken cutout on 525-131//// All repaires made & apr @ 0858 close ticket. dwest
7196 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-03-04 12:04 | 2009-03-04 14:25 | 12 | 141 | 54959-1 | 1692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001201// BAD 50KVA WR/ 28781989 RELEASED BY CREW 078S08//CREW ON SITE WILL REPLACE XFORMER//COMPLETE AT 14:25 ALL CUST. RESTORED PR TOLLIVER//COD 12//STARTED AS PART OUT BUT OPENED TRANSFORMER FUSE TO REPLACE// VER/DBM IDC XXXX
7197 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-12-31 17:47 | 2011-12-31 23:25 | 5 | 338 | 4218951 | 1690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3311401/ BAD 25 KVA TRANS. WILL NEED 2 MEN AND MATERIAL HANDLER, MANUAL POLE.BAD 25 KVA TRANS. WILL NEED 2 MEN AND MATERIAL HANDLER, MANUAL POLE.CHANGED TRANS. CLOSED BACK IN AT 23:25 //VER/GAH IDC XXXX
7198 | Hazard | 3303901 | LESLIE | HYDEN | 2009-09-14 21:25 | 2009-09-15 11:30 | 2 | 845 | 56932-1 | 1690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQUEST # 31717029 /// BAD 10KVA 7200 120/240 CUSTOMER SAID THAT OK TO CHANGE IN THE AM ON 9-15-09 COD-2 ISO TF 37830363000060 L3/HFP IDC XXXX
7199 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2022-02-10 14:32 | 2022-02-10 14:58 | 65 | 26 | 4465031 | 1690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout on pole 966A-128 is buzzing really loud..i will be changing cutout..i opened line fuse on pole 966A-128 at 14:32 and back in at 14:58
7200 | South Williamson | 3411401 | DEWEY | INEZ | 2014-08-10 23:52 | 2014-08-11 09:15 | 3 | 563 | 4351701 | 1689 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON 38830720C00077/ LINE FUSE BLOWN ON 38830720C00026// CUTOUT REPLACED//RESTORED AT 09:15// ISO 38830720C00026/// COD 3
7201 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2019-11-27 14:46 | 2019-11-28 00:09 | 3 | 563 | 4088181 | 1689 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | line fuse open 91-d/85; pri came out of sleeve at 115/112; truck ok; line crew req; ebp Released by crew 078E02,repairs made all cust restored please close ticket thanks.bt
7202 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-12-06 18:26 | 2016-12-06 23:10 | 10 | 284 | 4172291 | 1688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN 185-146 PATROLLING..// 161-111 BURNT OFF ..LOWERING EVERYTHING CREW REQUIRED..LIFTED HOT TAP @ 161-15 3 //..LIFTED HOT TAP @ 161-15..LINE FUSE BACK IN @ 20:11//LEAVING OFF 1 CUSTOMER VER/AWD L3/HFP XXXHFP
7203 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-01-03 10:32 | 2019-01-03 14:33 | 7 | 241 | 4625221 | 1687 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERV DROP CONNECTIONS NEED RE-WORKED.RISER TOO SHORT,NEED LONGER RISER.MASSEY SENDING MATERIAL.OPENED XFR-14:03,CLOSED-14-30////////REPAIRS COMPLETED &RESTORED POWER,ALL OK AFTERWARDS
7204 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-01-26 06:03 | 2010-01-26 15:25 | 3 | 562 | 59885-1 | 1686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | STS WR # 33597607 // WIRE HAS BURNT DOWN, ALSO HAVE BAD ARMS ON THIS POLE, WILL HAVE OUTAGE STARTING AT 13:00 HRS AND REPLACE ARMS PER SERVICER COD-2 VER/HFP L3/HFP IDC XXXX
7205 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-10-09 12:11 | 2017-10-09 16:52 | 6 | 281 | 4435921 | 1686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON 1014A370 CUTOUT IS IN PRIMARY ZONE I THINK I CAN REMOVE HOT LINE CLAMP ON 1014A367 TO DE-ENERGIZE TAP NO ADDITIONAL CUSTOMERS AFFECTED TO MAKE REPAIRS/MD FILED FOR MIS-MAPPED CUSTS COD-3/TRANS RESTORED POWER AT 16 52 VER/AWD L3/HFP XXXHFP ACB
7206 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-07-21 13:46 | 2012-07-21 18:27 | 6 | 281 | 4791661 | 1686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED TRANSFORMER ON POLE 39831147A00330 AT 15:21--CREW REQUIRED--BAD 25KVA TRANSFORMER--CAN USE SMALL MATERIAL HANDLER AND GET OFF RD--NEED NEW CUTOUT RELEASED BY CREW 078S07 LINKOUS & MCCOY & MCCANN(ALL POWER RESTORED AT 18:27 SEVERAL CUSTOMERS REPORTED DAMAGE DUE TO HIGH VOLTAGE CH VOLTAGE AT SEVERAL HOUSES NEW XFMER 125/250 OLD XFMER 300 VOLTS PER LEG REPORTED BY ELECTRICAN PER CUSTOMER) COD-6 ISO TF 39831147A00330 VER/HFP L3/HFP IDC XXXX
7207 | Pikeville | 3421002 | BREAKS | GRASSY | 2009-06-11 14:29 | 2009-06-12 18:35 | 1 | 1686 | 58222-1 | 1686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN, WILL REPLACE AND REFUSE//POWER RESTORED @ 18:35//COD 1// VER/DBM IDC MOVED START TIME FROM THE 12TH XXXX
7208 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2022-08-07 10:03 | 2022-08-07 15:40 | 5 | 337 | 4698381 | 1685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse link appears to have broken. Restored @ 15:40. sh
7209 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-06-12 00:59 | 2010-06-12 15:01 | 2 | 842 | 60521-1 | 1684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TO TACKLE IN DAYLIGHT RELEASED BY CREW 078S02 RELEASED BY CREW 078H05/SEND AFTER 0800//CORRECT ISO 38830546000041 // MISSING FUSE //COD 2// VER/DBM
7210 | Hazard | 3310502 | HADDIX | CANOE | 2008-09-12 00:59 | 2008-09-12 08:00 | 4 | 421 | 61729-1 | 1684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310502 -WIRE DOWN POSSIBLE POLE BURNED UP // VER/TOM IDC XXXX
7211 | Pikeville | 3407101 | TOPMOST | DEMA | 2014-02-04 14:47 | 2014-02-04 21:48 | 4 | 421 | 4348221 | 1684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 138-24 NEED : 1MAN AND MATERIAL HANDLER, 25 KVA ( 7.2 KV / 120/240 ), FLAGGING CREW . ALL WORK COMPLETE / GXJ VER/CRB
7212 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2010-10-26 16:00 | 2010-10-26 23:01 | 4 | 421 | 63985-1 | 1684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 71-134 ROTTED OFF AT GROUND LINE AND FELL OVER. I HAVE CUTOUTS OPENED AT POLE 71-134 AND HOT LINE CLAMPS OFF. LINE TAGED. CREW WILL NEED TO GROUND LINE. I CALLED TIM HALL HE WILL HEAD CREW THIS WAY . I OPENED LINE UP AT 16:00. RELEASED BY CREW 074S11 //VER/CRB IDC XXXX
7213 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2017-05-05 13:03 | 2017-05-05 19:03 | 10 | 360 | 4755881 | 1683 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 425-021 FUSE OPEN, POLE 425-145 BURNT OFF AT CUT-OUT, CREW REQUIRED, TRUCK ACCESS CAN LOWER CONDUCTORS, CUT PRIM LOOP ON POLE 425-144 TAGGED AND GROUNDED TO VERNON MULLINS. CLOSED FUSE 425-021 AT 15:30 RELEASED BY CREW 078H11/CREW ON SITE/FETR 2000/VEM RELEASED BY CREW 078H14//COD 10// VER/DBM
7214 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-12-31 03:23 | 2017-12-31 05:56 | 11 | 153 | 4689721 | 1683 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse melted out,,,line fuse back in @ 05:56 complete//cod 11
7215 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-12-02 16:47 | 2009-12-02 19:20 | 11 | 153 | 58802-1 | 1683 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SEC. POLE 263-219 ROTTED OFF AND FELL ON CHURCH. WE ARE GOING TO REMOVE POLE AND CUSTOMER SAID NO NEED TO PUT POLE BACK IN. IT TOOK LINE FUSE OUT ON POLE 263-93. I CLOSED FUSE IN AT 19:20//COD 9// VER/DBM IDC XXXX
7216 | Pikeville | 3413402 | GARRETT | LACKEY | 2017-07-14 21:50 | 2017-07-15 11:51 | 2 | 841 | 4125341 | 1682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED: 15 KVA 120/240 7.2 KV , TRUCK ACCESS RELEASED BY CREW 074S03 CREW ARRIVED WORKING ON XFMR//COD 2// VER/DBM
7217 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2019-01-16 17:17 | 2019-01-16 19:12 | 17 | 115 | 4679601 | 1682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on 9-C-9001.patrolled line saw no hazards.restored line fuse at 18:51.custommer flagged me down.found trans fuse broken at 9-C-50.replaced trans cutout,restored power at 9-C-50 at 19:12 Released by crew 079H03 L3/HFP
7218 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-08-04 07:01 | 2014-08-04 16:21 | 3 | 560 | 4329681 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 294-3 LOOP OPEN NO CREW REQUIRED ISOLATION POLE 38830294000003 COD 3// VER/ ADH
7219 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-01-18 17:35 | 2009-01-19 00:35 | 4 | 420 | 58105-1 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 28107855 // RELATED TO ORDER 58104-1 & 58148-1 (SAME CUST)ADDING 1 CUSTOMER FROM THAT ORDER COD-4 .XFMR TESTED GOOD WITH TESTER, FUSE BLEW WITH LEADS REMOVED, PHIL TOLLIVER IS ON THE WAY WITH 50KVA XFMR. RELEASED BY CREW 078S05///REPLACED 25KVA WITH 50KVA DUE TO LOAD ALSO REPLACED BAD CUTOUT/// COMPLETE AT 00:35 P R TOLLIVER/// COD-4 VER/LDA L3/KEP
7220 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-02-24 11:57 | 2009-02-24 13:21 | 20 | 84 | 51067-1 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BROKEN FUSE LINK--E MAIL TO RAYBURN--BAD ARRESTOR AN CUTOUT NEEDS REPLACED--4/0 TRANSFORMER RISERS MEALTING AN NEEDS REPLACED ASAP--TRUCK OK NEED FLAGMAN//VER/CRB IDC XXXX
7221 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-03-03 21:10 | 2009-03-03 21:30 | 84 | 20 | 54752-1 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CREW HAD TO OPEN RECLOSER TO ALLOW THEM TO SAFELY MAKE REPAIRS TO LOOP THAT IS BURNT OPEN ON ORDER 54747-1 L3/HFP IDC XXXX
7222 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-04-06 03:06 | 2009-04-06 07:06 | 7 | 240 | 66126-1 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | XFR TO RE-FUSEMOLDING FELL ONTO RISER.REMD MOLDING,RE-FUSED AND RESTORED VER/KEP L3/KEP IDC XXXX
7223 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-07-06 14:20 | 2011-07-06 15:30 | 24 | 70 | 4474811 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT//VER/CRB IDCC TOF1155 ESTIMATED TIME OFF XXXX
7224 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2016-05-04 16:02 | 2016-05-04 16:50 | 35 | 48 | 4174281 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 45-6523 BAD CUTOUT POLE 45-6776 B AND C FUSE 50T LINE FUSE OUT VER/AWD AJB
7225 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2008-04-07 15:50 | 2008-04-07 19:20 | 8 | 210 | 64922-1 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA CSP BAD.//340300350 KVA CSP BAD. RELEASED BY CREW 074S08 8 CUSTOMERS OUT// VER/HFP IDC XXXX
7226 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-04-30 18:35 | 2013-04-30 19:55 | 21 | 80 | 4060761 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 38830351000137, REPAIRS MADE, ALL POWER RESTORED COD-21 ISO LF 38830351000044 VER/HFP L3/HFP IDC XXXX
7227 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-09-02 10:20 | 2015-09-02 15:00 | 6 | 280 | 4190681 | 1680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP XFMER. TRUCK ACCESS. 7200-25KVA RELEASED BY CREW 078S07/1500BAD 25 KVA CSP XFMER. TRUCK ACCESS. 7200-25KVA RELEASED BY CREW 078S07,REPAIRS MADE PLEASE CLOSE TICKET THANKS.BT/ ISO 38830044C24525/ COD 6/ VER/BOW L3/DKG VERIFIED TIMES WITH VOICE RECORDER
7228 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2016-03-05 02:41 | 2016-03-05 12:00 | 3 | 559 | 4818771 | 1677 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED 251-148 TO 251-149 #4 COPPER DOWN PRIMARY TRUCKS OK/LINE FUSE 251-143 OPEN 15T TAGGED TO DDC/AND ISOLATED NO GROUNDS RELEASED BY CREW 078S03 . POWER RESTORED AT 12:00 ISO 38830251000143 COD 3
7229 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2017-03-02 20:17 | 2017-03-03 10:15 | 2 | 838 | 4508081 | 1676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMB BURNED OUT OF RISER ON P-978-307.REPLACINGHOT TAP BROKEN OUT OF RISER.CHANGING VER/CRB
7230 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-11-29 09:59 | 2015-11-29 19:00 | 8 | 541 | 4491521 | 1676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC HOLD TAG// FUSE WAS OPEN ON 473-40, PL 473-131 BURNT OFF, ISOLATED BY LIFTING HT ON 473-130. TAGGED TO DDC AT 1130. NO GROUND PLACED.TRUCK OK POLE CAN BE REPAIRED WITH WOODEN POLETOP, FUSE 473-40 BACK IN AT 1138, LINECREW REQUIRED RELEASED BY CREW 078S11.. CREW ON SITE TO MAKE REPAIRS ETR 19:00.. REPAIRS MADE AND CUSTOMERS RESTORED AT 19:00.. RELEASED BY CREW 078H22 VER/CRB
7231 | Hazard | 3310502 | HADDIX | CANOE | 2014-01-24 02:06 | 2014-01-24 09:05 | 4 | 419 | 4305371 | 1676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR , NEED 1 MAN & BUCKET TRUCK , THE 177 BUCKET WOULD WORK BETER HERE, TIGHT PLACE. //V. HURT TO ASSIST //BAD 25 KVA XFMR , NEED 1 MAN & BUCKET TRUCK , THE 177 BUCKET WOULD WORK BETER HERE, TIGHT PLACE. REPLACED WITH 50 KVA. POWER BACK ON @ 09:05 RELEASED BY CREW 075H04 VER/HFP L3/HFP
7232 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-04-23 16:36 | 2008-04-23 16:54 | 93 | 18 | 53626-1 | 1674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3000102//CREW OPENED SWITCHES ON POLE#46-165 TO MAKE REPAIRS ON SWITCHES ON POLE 46-1075/VER/CRB IDC XXXX
7233 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2016-07-22 15:53 | 2016-07-22 18:59 | 9 | 186 | 4668171 | 1674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA, 7200, 120/240. 2 BUSHING, TRK OK IN ALLEYWAY RELEASED BY CREW 078S07---CREW ON SITE--REPLACED BAD 50KVA--CUTOUT AND ARRESTOR---CK VOLT GOOD---CLOSED AT 18:59---TBL TKT COMP/ ISO 38830045C14497/ COD 9/ VER/BOW
7234 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-04-11 14:24 | 2009-04-11 17:30 | 9 | 186 | 51509-1 | 1674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001//REPLACING POLE 1127-514//VER/CRB IDC XXXX
7235 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2022-04-05 05:48 | 2022-04-05 09:47 | 7 | 239 | 4722651 | 1673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Recloser locked out. Crew onsite patrolling ckt with UTV.//changed cutout on pole 38830113D30137
7236 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-04-09 03:41 | 2016-04-09 07:40 | 7 | 239 | 4073461 | 1673 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | DPOLE 20-3031 LOOP ON BOTTOM OF CUTOUT BURNT OFF REPAIRED//COD 7 VER/HFP L3/HFP AJB
7237 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2012-06-19 17:08 | 2012-06-19 20:37 | 8 | 209 | 4932771 | 1672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE B PHASE 327 CUST // RISER BURNT OFF OF TWO HOLE PAD CONNECTOR ON GOAB SWITCH ON 7-C-5..NEED CREW.WILL HAVE TO DROP STATION BREAKER TO REPAIR...//..JUSTICE, HOMER & MATNEY, EDWARD OPENED CB @ 2001 INTERUPTING AN ADDITIONAL 260 CUSTOMERS. // CLOSED CB @ 2037 RESTORING ALL CUSTOMERS. VER/HFP L3/HFP IDC XXXX
7238 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-08-22 14:49 | 2019-08-22 18:32 | 16 | 223 | 4929491 | 1672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr on pole 37830205D00106, 19.9 kv, 25 kva, evening crew on the way to replace restored @ 1832
7239 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-04-29 02:27 | 2011-04-29 09:25 | 4 | 418 | 52131-1 | 1672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE CHECKED AT REGULAR WORKTIME AS PER CALLOUT GUIDELINES REPLACED CUTOUT//COD 4// VER/DBM
7240 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-10-01 14:46 | 2008-10-01 18:15 | 8 | 209 | 52654-1 | 1672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-8 STS WR # 26564270 /// POLE 45-7054 BAD 50 KVA TRUCK TO POLE TRANS ON HERMAN AVE IN CHURCH PARKING LOTPOLE 45-7054 BAD 50 KVA TRUCK TO POLE TRANS ON HERMAN AVE IN CHURCH //PARKING LOT RELEASED BY CREW 078S08//CHANGED XFMR VOLTAGE CHECKED GOOD ALL RESTORED AT 16:15 IDC XXXX
7241 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2014-09-19 18:37 | 2014-09-20 00:11 | 5 | 334 | 4512461 | 1670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 250KVA STEPDOWN TR // CALLING CREW // TRUCK ACCESSABLE // MULLINS & MORGAN & GOBLE & HOWARDBAD 250 KVA STEPDOWN XFORMER, NEED LINE CREW , TRUCKS TO POLE. NEED OIL SPILL SMALL TO CLEAN UP. COME DOWN PATRICK SPUR RD. TAGED TO VERN. REMOVED SOURCE AND LOAD SIDE HOT TAPS./CREW ON SITE/FETR0130/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0011/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN
7242 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-08-21 19:35 | 2011-08-22 09:30 | 2 | 835 | 4737581 | 1670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA . TRUCK TO POLE LAST TWO HOUSES ON LEFT PULL DOWN DRIVE ON LEFT SEND TO CREWS RELEASED BY CREW 078S08//WORK IN AM NEED SMALL BUCKET NEW CONCRETE DR. NEED PERMISSION TO PUT TRUCK ON// RELEASED BY CREW 078H03//VER/CRB IDC XXXX
7243 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-01-25 10:08 | 2010-01-25 19:24 | 3 | 556 | 59358-1 | 1668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 077S04, LEAD OFF SERVICE AT XFMR POLE, SECONDARY BAD, WILL TAKE COUPLE MEN TO WORK THIS, NEED ABOUT 100FT 2/3. BRUCE SAID FIRST CREW TO CLEAR UP TO CATCH THIS. LEFT XFMR OPEN RELEASED BY CREW 077S08 VER/KEP L3/KEP IDC XXXX
7244 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2012-03-05 13:00 | 2012-03-05 21:00 | 5 | 480 | 4552091 | 1668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 265-341 ABT 2.5 FT BURNED OFF,WILL NEED REPRD.NEED CREW.40C4POLE & DEADEND MATERIALTO MAKE OK.WILL CUT LOOP AT POLE 265-340 AND GET ALL ON XCEPT POLE 341/CLOSED FUSE @ 17:57 ON POLE 49 RELEASED BY CREW 074S06 // COD-5 ISO LF 37820265D00049 VER/HFP L3/HFP IDC XXXX
7245 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-12-01 18:29 | 2020-12-01 20:48 | 12 | 139 | 4737401 | 1668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 xfmer sec. riser burnt off. to l.mccoy Released by crew 078S07 transformer off at 20:40 back on at 20:48 LR- The 1st customer All Out call came in at 18:29.
7246 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2016-03-14 10:08 | 2016-03-14 17:05 | 4 | 417 | 4842521 | 1668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 404-66 10 T LINE FUSE. NEED LINE CREW , TRUCKS TO POLE. RELEASED BY CREW 078S01/ ISO 38830404000066/ COD 4/ VER/BOW
7247 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-03-28 11:37 | 2010-03-28 16:15 | 6 | 278 | 55204-1 | 1668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT AND ARRESTOR ON POLE 181-291, CALLING FOR HELP COD-6 VER/HFP L3/HFP IDC XXXX
7248 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-05-12 16:36 | 2009-05-12 18:35 | 14 | 119 | 66020-1 | 1666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 189-116//3008702//VER/CRB
7249 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-10-14 18:30 | 2008-10-14 20:29 | 14 | 119 | 55773-1 | 1666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP RELATED TO ORDER 55759-1 CREW OPENED RECLOSER ON POLE 37830426C00641 TO ALLOW THEM TO REPAIR DOWNED CONDUCTOR /// RECL SIZE NOT DETERMINED BUT ENTERED MD & SENT EMAIL TO ENGINEERING TO CORRECT..HFP COD-14 IDC XXXX
7250 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2010-10-11 11:26 | 2010-10-11 13:17 | 15 | 111 | 58625-1 | 1665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING TRANSFORMER//VER/CRB IDC XXXX
7251 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-03-25 18:57 | 2013-03-25 22:25 | 8 | 208 | 4958401 | 1664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN..I FUSED IT UP AND IT STAYED FOR A FEW MINUTESAND DROPPED BACK OUT.BRING A 75 KVA IF WE HAVE ONE..IF NOT A 50 KVA 19900 120-240.CAN USE MATERIAL HANDLER..2 MEN. RELEASED BY CREW 074H08 CHANGED TRANSFORMER ALL OK VER/KEP IDC XXXX
7252 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2013-08-11 07:42 | 2013-08-11 09:50 | 13 | 128 | 4649181 | 1664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 37830343C00144 === CHANGED INSULATER === REFUSED POWER OK CC = 13. VER/SDB
7253 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-01-14 00:14 | 2014-01-14 02:22 | 13 | 128 | 4279611 | 1664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACING BROKEN CUTOUT //VER/GAH L3/HFP IDC XXXX
7254 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-05-27 07:35 | 2019-05-27 11:03 | 8 | 208 | 4347841 | 1664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Pole 38830526000060 has 15t fuse not on the maps. please have fuse added to maps. Also customer at 2721 is on txmf 526-98. Please have maps corrected. Fuse 526-60 in @ 1103. apr close ticket
7255 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-06-24 06:38 | 2012-06-24 11:15 | 6 | 277 | 4956361 | 1662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEVICER WILL BE DISPATCHED AT 0730 BAD 50KVA 19.9 NEED 75KVA 19.9 TRUCK TO POLE RELEASED BY CREW 078S08 (REPLACED WITH 75 KVA) ENTERED MD COD-6 ISO TF 38830116B02504 VER/HFP L3/HFP
7256 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2013-03-19 06:16 | 2013-03-19 15:30 | 3 | 554 | 4918061 | 1662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORKTIME // XFMR CUTOUT FAILED ON 522-221 AND BURNT TOP OF ANGLE POLE OFF. NOT TRUCK ACCESSIBLE. CREW WORKING TO MAKE REPAIRS. RELEASED BY CREW 076S02 //COD 3// VER/DBM IDC XXXX
7257 | South Williamson | 3200302 | BELFRY | TOLER | 2017-10-04 08:50 | 2017-10-05 12:32 | 1 | 1662 | 4408761 | 1662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK 09/05 NO TRUCK ACCESS, LOOKS LIKE TRANSFORMER FUSE BLOWN BACK ON MOUNTAIN. CREW EN-ROUTE WITH ATV. RELEASED BY CREW 079S02/ BAD TRANS MANUAL REPLACEMENT ON HILL PER CUST OK TO WAIT TILL 10-5/ XFMR CHANGED ON 10/5 AT 12:32 D SAMMONS COD-1 ISO TF 38821015A20281 VER/AWD L3/HFP XXXHFP
7258 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-05-18 08:37 | 2009-05-18 11:08 | 11 | 151 | 61841-1 | 1661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP CREW ON SITE REPLACING TRANSFORMER. COD-11 L3/HFP IDC XXXX
7259 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-11-30 14:26 | 2016-11-30 16:57 | 11 | 151 | 4150711 | 1661 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 318-30, REPLACED CUTOUTS RESTORED POWER AT 16:57.. 37830180000030 VER/AWD L3/HFP XXXHFP
7260 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-06-28 16:20 | 2019-06-28 23:15 | 4 | 415 | 4613871 | 1660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19900 cutout broke. Jason is gonna bring cutout//cod 4//iso//
7261 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2019-07-05 10:36 | 2019-07-05 13:22 | 10 | 166 | 4659711 | 1660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | /bad 50 kva xfr 182-2522,,,,2 bushing ,,,truck to pole///replaced bad 50 kva///complete BR L3/HFP
7262 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-01-15 21:37 | 2009-01-16 03:09 | 5 | 332 | 55348-1 | 1660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3312202// THIS IS A BURNT OF TRANSFORMER - WILL NEED TO COME BACK WITH A 25 KVA, 3-4 MEN, MANUAL// ADVISED DUTY SUPERVISOR - GETTING CREW TOGETHER// RICK, RON, WOO AND JEFF WORKING ON THIS// WR# 28091405 // REPLACED WITH 25 KVA , RESTORED POWER TO CUSTOMERS AT 0309 JEFF COMBS VER/LDA L3/KEP
7263 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-11-10 16:18 | 2009-11-10 20:15 | 7 | 237 | 56380-1 | 1659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303//, ON SITEFUSE OUT, POLE#1138-B-32, PATROLLING LINE, 15T FUSE//COD 7// VER/DBM IDC XXXX
7264 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2017-03-11 09:03 | 2017-03-11 13:00 | 7 | 237 | 4548051 | 1659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-7583 BAD CUTOUT NO TRUCK NEED LINE GREW RELEASED BY CREW 078S08,REPLACED CUTOUT ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT 38830069D47583 VER/AWD
7265 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-01-26 14:03 | 2009-01-26 14:10 | 237 | 7 | 59948-1 | 1659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308603//PHILIP GABBARDS CREW WAS REPLACING CUTOUT ON POLE 470-105 THE BRACKET BROKE AS THEY WERE RESTORING AND FELL ACROSS LINE LOCKING OUT RECLOSER ON POLE 470-46 THEY REPAIRED BRACKET AND RESTORED AT 1410 MLR OK IDC XXXX
7266 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-10-16 09:57 | 2012-10-16 19:10 | 3 | 553 | 4145201 | 1659 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | SEND TO B REYNOLDS--BAD 4/0 UG TO APTS 212-213-214 RELEASED BY CREW 078S07 RELEASED BY CREW 078H07//REPAIRED BAD HOT LEG POWER RESTORED AT 19:10 VOLTAGE CHECKED GOOD CLOSE TKT PRT// VER/DBM IDCC PN7146, CNT7 XXXX
7267 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2013-12-25 06:03 | 2013-12-25 10:00 | 7 | 237 | 4200051 | 1659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 522-71 PATROLLING LINE, LINE WAS TRACKING THROUGH OLD DOOR ON 522-80 FUSE WAS BLOWN BUT DOOR WAS STILL UP. ISOLATED TAP ON 522-80. APR AT 1000 CLOSE TICKET. DEW MD FILED ON POLE#80 VER/KEP L3/HFP IDCC FEC49 XXXX
7268 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-02-10 07:12 | 2010-02-10 11:48 | 6 | 276 | 54884-1 | 1656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RISER BURNED UP ON TRANSRORMER BANK..HAVE TO DROP OUT TRANSFORMER BANK TO FIX..REPLACED RISER RE HOOKED XFMR..BB//VER/CRB IDC CHANGED COUNT FROM 11, CLEARING POLE FROM 106 AND FAULT POLE FROM 106 XXXX
7269 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2010-12-29 18:47 | 2010-12-29 21:05 | 12 | 138 | 56885-1 | 1656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED AT WEATHERHEAD CAUSING NEUTRAL CONDUCTOR TO BURN IN TWO. REPLACED ENTIRE #2 THREE CONDUCTOR SERVICE WITH SAME SIZE. PLEASE FORWARD TO PEGGY WYSONG AS THIS IS POSSIBLE DAMAGE CLAIM. (PROVIDED CUSTOMER WITH NAME AND TROUBLE TICKET # AT HER REQUEST) SH // FORWARDED INFO TO PEGGY WYSONG IDC XXXX
7270 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-02-20 13:22 | 2014-02-20 15:40 | 12 | 138 | 4405641 | 1656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | TIE WIRE BROKE ON 811-72 AND LET PRIMARY FALL TO POLE-TOP PIN. TIE WIRE IS ALSO BROKE ON 811-59 AND WILL NEED TO BE REPAIRED. CREW ENROUTE TO ASSIST. REPAIRS COMPLETE. RESTORED @ 15:40. SH VER/SEF
7271 | Whitesburg | 3409503 | BURDINE | JENKINS | 2015-09-20 01:38 | 2015-09-20 03:56 | 12 | 138 | 4251931 | 1656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/ARN L3/HFP XXXHFP
7272 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-09-05 08:17 | 2021-09-05 10:35 | 12 | 138 | 4210821 | 1656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad line fuse cut-out. Power restored.
7273 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2020-02-06 03:58 | 2020-02-06 10:05 | 5 | 367 | 4367181 | 1655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0358/D A phase (RIGHT HAND PHASE 5 CUST)) L/ F open @37830048D20107, checking.0358. A phase L/ F open @37830048D20107, checking. Cutout failed @48-D2-682, gonna isolate trouble with 3 clamps @48-D2-992.0358/ ALL ON @ 1005
7274 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-07-25 16:26 | 2009-07-25 17:23 | 29 | 57 | 57710-1 | 1653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309001// / FOUND HOT LIN CLAMP OFF ON POLE 37830393D00037, FUSE NOT BLOWN BUT CLAMP OFF. REPLACED STIRRIP, CLOSED FUSE, POWER RESTORED//COD 29// VER/DBM IDCC CNT36 XXXX
7275 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-06-11 08:03 | 2009-06-11 09:30 | 19 | 87 | 57460-1 | 1653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND 2 40 T FUSES POWER ON COD-19 ISO 38830182B22506 IDC XXXX
7276 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-07-31 12:15 | 2009-07-31 13:30 | 169 | 75 | 66524-1 | 1653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | HAD TO OPEN RECLSOER TO SAFELY REPLACE BROKEN CUTOUT IDC XXXX
7277 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2019-04-22 12:07 | 2019-04-22 15:04 | 19 | 177 | 4147061 | 1653 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO ISOLATE FAULT AT POLE 38821137D00318 - POLE FIRE I opened recloser on pole 38821137A00331 at 12:07, source side riser removed and tagged to Matney. Released by crew 079S02
7278 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-09-26 12:35 | 2012-09-26 16:31 | 7 | 236 | 4089371 | 1652 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TRANSMISSION LINE FELL ACROSS DISTRIBUTION/SERVICERS PATROLLING. CUSTOMER LIVES RIGHT WHERE STATIC IS DOWN ON DISTRIBUTION, LINE FUSE IS BLOWED RELEASED BY CREW 077S02 // COD-7 ISO LF 37830230B00027 VER/HFP L3/HFP IDC XXXX
7279 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-10-23 10:39 | 2017-10-23 14:35 | 7 | 236 | 4478711 | 1652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKE ON POLE 228-65, (MANUEL POLE) LINE FUSE BLOWN ON POLE 228-1, CALLING FOR HELP ON @ 1435 COD-7 ISO LF 37830228000001 VER/HFP L3/HFP ACBC TON 1448
7280 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-04-23 08:09 | 2011-04-23 12:05 | 7 | 236 | 62381-1 | 1652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-526 BAD CUT AND LA LIGHTING POLE 45-525 30T IDC XXXX
7281 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-12-22 07:24 | 2008-12-22 11:20 | 7 | 236 | 62291-1 | 1652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401001TRANS. FUSE IS BLOWN FROM OVERLOAD. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. TIM HALL IS SENDING A CREW TO CHANGE IT.COD-7 REPLACED BAD 25KVA TRANS. WITH A 50KVA TRANS. ROBBIE WORRIX//VER/CRB L3/KEP IDC XXXX
7282 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2015-03-14 10:47 | 2015-03-14 17:40 | 4 | 413 | 4192981 | 1652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 343-D-57 XFMR C/O BROKEN. 19.9 KV C/O AND ARRESTOR AND BRKT NEEDED, MANUAL CREW REQ. RELEASED BY CREW 077S08/ ISO 37830343D00057/ COD 4/ VER/BOW
7283 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-02-23 02:22 | 2016-02-23 09:15 | 4 | 413 | 4749681 | 1652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK DURING NORMAL WORK HOURS BAD CUTOUT.CHANGING ISO 38830875A00036 COD 4 VER/AWD
7284 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2017-11-14 12:59 | 2017-11-14 16:55 | 7 | 236 | 4555811 | 1652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO OUTAGE UNTIL XFMR OPENED @ 1259 COD-7 ISO TF 38830069D37101wire burnt out of hot line clamp on pole 38830069D37101 needs new cutout Released by crew 078H01/ ISO 38830069D37101/ COD 7
7285 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-06-02 18:48 | 2017-06-02 21:33 | 10 | 165 | 4899771 | 1650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER LOUD NOISE NEIGHBOR OUT/ DISABLED UNABLE TO CHECK METER SQUIRREL IN XFMR RISER BLEW XFMR FUSE. TRANSFORMER CUTOUT BROKE. REPLACED CUTOUT AND RESTORED LINE FUSE 833-534 @ 21:33. SH/ ISO 38830833D00534/ COD 10/ VER/BOW
7286 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-03-27 06:55 | 2013-03-27 07:50 | 30 | 55 | H4960931 | 1650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND ONE PHASE HENDRIX BURNT IN CLEAR// CREW TO MAKE REPAIRS// 556 CONDUCTOR IS BURNED DOWN BEHIND SOUTH SIDE MALL. WHEN READY TO MAKE REPAIRS WE WILL NEED TO OPEN AT POLE 966-629. & TAG FOR EDDIE MATNEY556 CONDUCTOR IS BURNED DOWN BEHIND SOUTH SIDE MALL. WHEN READY TO MAKE REPAIRS WE WILL NEED TO OPEN AT POLE 966-629...OPENED LINE AT 06:55..NOT ON MAP ..CLOSED BACK IN AT 07:50. VER/PDP IDCC DUP TO OPEN SWITCH XXXX
7287 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-12-30 09:00 | 2013-12-30 09:55 | 30 | 55 | 4211831 | 1650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 1123-5006 WIRE FELL OUT OF BOTTOM OF CUTOUT REPAIRED VER/CRB IDC XXXX
7288 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2022-04-08 09:25 | 2022-04-08 10:40 | 22 | 75 | 4740481 | 1650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse bad on pole 942B-70.bad cutout..replace cutout and got line fuse on pole 942B-70 back in at 10:40
7289 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-08-24 07:20 | 2021-08-24 09:50 | 11 | 150 | 4142281 | 1650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LF blown on 1149-282// patroling// found bad arrester on pole 1149-250 and cleared it up, will try 65t on 1149-282
7290 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-09-19 17:20 | 2011-09-19 18:15 | 30 | 55 | 4885181 | 1650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 206-251,,, BAD CUTOUT ON POLE 38830206C02516, REPLACED CUTOUT, ALL POWER RESTORED COD-30 ISO OCR 38830206C02515 VER/HFP L3/HFP IDC XXXX
7291 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-01-11 13:38 | 2013-01-11 15:15 | 17 | 97 | 4596261 | 1649 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S01----POLE BURNT OFF AT CUTOUT , WILL LOWER PRIMARY AND CUTOUT ///VER/CRB L/3 CRB IDC XXXX
7292 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-07-31 07:44 | 2020-07-31 18:03 | 7 | 619 | 4262821 | 1648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout hanging in the clear on pole 184A-36 and a line fuse open on pole 184A-35. Line fuse closed back in at 9:06, crew required on the cutout.restored power at 18:03
7293 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2011-04-06 14:08 | 2011-04-06 21:00 | 4 | 412 | 51056-1 | 1648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 39469989 //FOUND ARRESTER BLOWN ON 904-17 AND CLEARED UP. WILL TRY FUSE.FOUND ARRESTER BLOWN ON 904-17 AND CLEARED UP. WILL TRY FUSE. RESTORED @ 21:00. SH COD-4 ISO LF 38830904000015 VER/HFP L3/HFP IDC XXXX
7294 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-12-31 19:44 | 2010-12-31 21:27 | 16 | 103 | 57442-1 | 1648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | A PHASE STEP DOWN FUSE OUT - 16 CUSTOMERS--BAD ARRESTOR ON STEPDOWN BANK NEEDS REPLACED VER/ARN IDCC CNT25 XXXX
7295 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-12-15 22:42 | 2011-12-16 13:41 | 12 | 899 | 4181311 | 1647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 164-319 POLE TOP BURNT OFF POLE 164-37 40T NO TRUCKS 1-CUST OFF MIT WANT FOR DAY LIGHT 40T BACK IN 11;50 PM RELEASED BY CREW 078S08/CREW ON SITE/DIFF LOCATION/TRACK EQUIP/FETR1400/VEM/REPAIRS MADE AND POWER RESTORED AT 1341/PLEASE CLOSE TICKET/THANKS/VEM // COD 12// VER/DBM IDC XXXX
7296 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-05-16 21:47 | 2011-05-17 00:50 | 9 | 183 | 4102891 | 1647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STS WR # 39991294 // PATROLLED. FUSE LINK BROKE. RE-FUSED @ 00:50. SH
7297 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2019-02-12 20:32 | 2019-02-13 05:40 | 3 | 548 | 4784081 | 1644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 50 KVA transformer on 38830978C10159 serves three meters: 534086651, 533610262 & 533757599. Primary riser broke at xfmr bushing. Replaced riser and restored @ 5:40. sh////map discrepancy submitted
7298 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-09-24 18:38 | 2009-09-25 01:29 | 4 | 411 | 61687-1 | 1644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/ARN IDC XXXX
7299 | Pikeville | 3402003 | KEYSER | MULLINS | 2021-12-20 20:43 | 2021-12-21 01:28 | 19 | 285 | 4215351 | 1641 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | loop burned in 2 on pole 1127-B-9, need line crew #2 acsr// will have to open on 1127-B-11 to safely make repairs// opened LF @ 00:25// closed @ 01:28
7300 | Pikeville | 3421001 | BREAKS | CITY | 2009-04-03 05:20 | 2009-04-03 08:45 | 8 | 205 | 64390-1 | 1640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3400901//CUTOUT FAILED//COD 8// VER/DBM IDC XXXX
7301 | Hazard | 3309002 | JEFF | JEFF | 2011-05-31 16:07 | 2011-05-31 21:35 | 5 | 328 | 4215051 | 1640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 167 KVA 7200 XFMR..REPLACED XFMR RESTORED POWER AT 21:35 VER/KEP IDC XXXX
7302 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-04-28 08:32 | 2017-04-28 14:00 | 5 | 328 | 4689571 | 1640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 336-64 IS BROKE WILL NEED 4 MAN CREW CALLED OUT AT 6 IN THE MORNING AND MANUEL R/W CREW// NEED 40FT POLE RUNNING CORNER AND CLEVIS AND GUY NO POWER OFF RELEASED BY CREW 077S01//NEED YARDDOG// OPEN LINE @ 832 AM 077H04/ RESTORED 1400/ ISO 37840336000055/ COD 5/ VER/BOW L3/HFP HFPC TOF04/27/2017 CDC83
7303 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-06-25 17:56 | 2009-06-25 20:25 | 11 | 149 | 60454-1 | 1639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP HAD 2 BAD LINE CUTOUT BAD ON 247C- 881 == CHANGED CUTOUTS OUT == REFUSED == POWER OK L3/HFP
7304 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-05-04 08:29 | 2011-05-04 13:02 | 6 | 273 | 4006041 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE ON POLE 1135-15 AT 0829. GOT POLE # 1135-38 BURNED OFF . NEED 40 FOOT POLE PT PIN AND CUTOUT AND ARRESTOR AND EVERTHING ELSE WILL TRANSFER RELEASED BY CREW 077S05 REPLACED POLE AND RESTORED POWER AT 1302 CREW 077H01//ISO//COD 6// VER/DBM IDC XXXX
7305 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-02-06 16:49 | 2010-02-06 19:51 | 9 | 182 | 50815-1 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLETOP BURNT OFF, CALLED FOR CREW, 12T LINE FUSE OUT AT POLE#1064-B-235, POLE BURNT OFF AT # 1064-272 LINE FUSE AND 1 SPAN TAP AND 15T TRANS ON 272 NOT ON MAP IDC XXXX
7306 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-02-10 10:37 | 2020-02-10 12:43 | 13 | 126 | 4387511 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 1057-304, will replace. power restored at 12:43 L3/HFP
7307 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-03-12 12:28 | 2008-03-12 15:30 | 9 | 182 | 56529-1 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001203- PART OF OUTAGE 56529-1 CONTR OPENED TR TO DE-ENERGIZE SECONDARY FEEDING BACK TO FAULT POLE 25-B-2783 VER/PDP IDC XXXX
7308 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-02-04 08:53 | 2009-02-04 11:55 | 9 | 182 | 55416-1 | 1638 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308001// STS I GOT SEC LEADS BURNED IN TO GOING TO OPEN 1083-433 TO MAKE REPAIRS OPEN TRANSFORMER AT 1129 AND CLOSED AT 1155//VER/CRB
7309 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2018-07-02 12:40 | 2018-07-02 14:46 | 13 | 126 | 4705751 | 1638 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 21-3095 line fuse cutout broke door still in, fuse blown need line crew big bucket,send to l. mccoy Released by crew 078S04 COD-13 ISO LF 38830021B33095
7310 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-06-10 19:53 | 2013-06-10 22:55 | 9 | 182 | 4255341 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37840336000037 == REPLACED === POWER OK ///VER/CRB L/3 CRB
7311 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2008-11-25 08:02 | 2008-11-25 12:35 | 6 | 273 | 52034-1 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402802//..LINE FUSE BLOWN...TOP OF POLE BURNED OFF 786-371....ROBEY BLAIRS CREW TO WORK JOB..BB RELEASED BY CREW 076S01//VER/CRB IDC XXXX
7312 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2022-08-04 10:24 | 2022-08-04 12:30 | 13 | 126 | 4673441 | 1638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole
7313 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2021-04-10 21:00 | 2021-04-10 23:36 | 21 | 156 | 4439511 | 1636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm cutout broke and is on crossarm @ 37830018B20569// no truck access// Opened fuses @ 37830018000139 @ 22:22// Repairs made & restored @ 23:36
7314 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-10-10 08:02 | 2014-10-10 13:30 | 7 | 328 | 4601141 | 1636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | @ 1030 PATROLLING LINE //1015-31 --15 T 0N 1140---POLE 1015-32 HAS BAD CUTOUT HELP ENROUTE1015-31 --15 T 0N AT 1140---POLE 1015-32 HAS BAD CUTOUT------- HELP ENROUTE---32 ON AT 1330 RELEASED BY CREW 077S06// COD 7 AJB
7315 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-01-05 13:48 | 2010-01-05 19:15 | 5 | 327 | 61609-1 | 1635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. 25 KVA TRANS. ON POLE 335-46 IS BAD. WE NEED TO INSTALL A 50 KVA 12KV. I THINK WE CAN REACH WITH A TRUCK. NEED TO BRING ONE OF THE 4/8 SHEETS OF COVER UP TO LAY OVER WATER METER. RELEASED BY CREW 074S01VER/TOM IDC XXXX
7316 | South Williamson | 3411401 | DEWEY | INEZ | 2020-07-25 08:03 | 2020-07-25 13:30 | 5 | 327 | 4230431 | 1635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 769D110 due tofailed cutout on 769D165.i can make repairs.made repairs restored power at 13:30
7317 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2016-07-16 11:17 | 2016-07-17 11:33 | 2 | 1456 | 4646471 | 1634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT OFF POLE @ 248-208 NEED LINE CREW LIFTED HOT TAP @ 248-195 LINE FUSE 248-41IN @ 1415 RELEASED BY CREW 078S05 VER/CRB
7318 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-02-25 08:39 | 2011-02-25 09:03 | 68 | 24 | 61325-1 | 1632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CREWS OPENED RECLOSER IN ORDER TO MAKE REPAIRS TO HOTTAP AND BASKET FOR ORDER 61162-1//COD 68//CLOSED IN @ 0903 // VER/DBM IDC XXXX
7319 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-09-21 08:19 | 2011-09-21 10:35 | 12 | 136 | 4891681 | 1632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "B" PHASE ONLY COD-12 B PHASE RECLOSER OUT ON POLE 329-288, BAD ARRESTER ON POLE 305-11.. REMOVED ARRESTER RESTORED POWER AT 10:35 RELEASED BY CREW 077S11 VER/KEP IDCC PN214 XXXX
7320 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2020-06-23 18:24 | 2020-06-23 20:40 | 12 | 136 | 4066251 | 1632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | will replace xfmr riser.repairs have been made & power restored @ 20:40
7321 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2011-09-21 14:57 | 2011-09-21 21:45 | 4 | 408 | 4893641 | 1632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OPEN AT POLE 38830271000142, PATROLED LINE AND FOUND NO HAZARDS,,,, POSSIBLE BAD INSULATOR ON POLE 271-225, NO TRUCK, CREW REQUIRED, PORC. BELL ON DOUBLE DEAD END. ACCESS FROM END OF RASTORFER RD. RELEASED BY CREW 078S05/POWER REST. @ 21:45 J. HEMLEPP COD-4 ISO LF 38830271000142 VER/HFP L3/HFP IDC XXXX
7322 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-08-04 20:12 | 2014-08-04 21:20 | 24 | 68 | 4331191 | 1632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 44-384 BAD HOT TAP POLE 44-107 65T/// ISO 38830044A00107/// COD 24 VER/DKG L3/DKG AJB
7323 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-03-23 18:14 | 2011-03-23 19:05 | 32 | 51 | 57575-1 | 1632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ALL OF FROG POND OUT//OPEN AT POLE 818-74//LEAD HAS COME OUT OF HOT TAP ON THIS POLE//PATROLED REST OF LINE FOUND NOTHING/GOING TO REPAIR//REPAIRS MADE//RESTORED AT 19:05//COD 32 // SENT TO FORESTRY// ISO// VER/DBM IDC XXXX
7324 | Pikeville | 3311401 | REEDY STATION | DEANE | 2017-05-21 09:08 | 2017-05-22 12:19 | 1 | 1631 | 4833341 | 1631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WE HAVE A BAD STRING OF INSULATORS AND A ARM PIN AND INS. ON POLE 306-261 , NEED CREW WITH KOBOTA AND ROW CREW TO CUT PATH TO POLE. WE WILL WORK TOMMOROW/ ISO 37830306000211/ COD 4. RESTORED POWER ATY 12:19 5/22/2017 RELEASED BY CREW 077H17 VER/CRB
7325 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2014-01-30 11:17 | 2014-01-30 15:10 | 7 | 233 | 4329681 | 1631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309104 // REMOVED JUMPER ON WRONG ORDER MADE ORDER DUP // BAD 25 KVA XFMR ON POLE 401-13, WILL NEED FLAGGERS TOOK 2 POLE TAP OFF @ 1425 ON @ 1510 1 CUST // 7 CUST ON THIS TR ON POLE 37830401C00013 DUP IN HOIS VER/HFP L3/HFP
7326 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-03-08 17:22 | 2015-03-08 20:05 | 10 | 163 | 4168911 | 1630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 511-2 . FOUND BAD ARRESTER ON POLE 488-42 , CUT IN CLEAR. . DIDNT HAVE ARRESTER ON TRUCK TO REPLACE . CLOSED FUSE @ 20:05// VER/ ADH L3/HFP XXX
7327 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2017-05-06 09:37 | 2017-05-06 12:00 | 19 | 143 | 4760871 | 1629 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OCR IS OPENED 37830211B00100//POLE TOP BURNT @ POLE 37830211B00412//LIFTED HT @ POLE 37830211B00001//CLOSED RECLOSER @ 1056 VER/CRB
7328 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-12-26 12:08 | 2020-12-26 15:09 | 9 | 181 | 4824421 | 1629 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | patrolled walked to every pole, found a bad pri deadend ins, on1047-46 chg it, cls in lf at 1509, power restored so far at this loc//MD HAS ALREADY BEEN MADE
7329 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-09-19 23:42 | 2011-09-20 08:45 | 3 | 543 | 4886421 | 1629 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE CHECKED IN THE MORNING 6T FUSE OUT DUE TO BAD CUTOUT. WILL BE CHANGING. I HAVE CUTOUT FUSED UP EVERYTHING OK//COD 3 IDC XXXX
7330 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-02-05 09:03 | 2013-02-05 15:50 | 4 | 407 | 4792071 | 1628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR HAD BLOWN INSIDE INEZ TRANSMISSION STATION//STATION HAS REPAIRS MADE AND IM GOING TO REFUSE AT POLE 841-3 6//1550//COMPLETE//EM//COD 4// VER/DBM IDC XXXX
7331 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-07-28 17:03 | 2017-07-28 17:25 | 74 | 22 | 4197081 | 1628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | RELATED TO 4196291//OPENED TO SAFELY OPEN BROKEN SWITCHES 38830068B00123//COD 295//RESTOERD 74 CUST, REMAINING 221 CUST TRANSFERRED TO 4196291// SJG (RELATED TO 4196241)
7332 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-04-08 14:52 | 2013-04-08 17:20 | 11 | 148 | 4988711 | 1628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP BURNT UP AND CAUSED XFMR FUSE TO MELT OUT. REPLACED CLAMP AND RE-FUSED CUTOUT. RESTORED @ 17:20. SH//COD 11// VER/DBM IDC XXXX
7333 | Whitesburg | 3309301 | VICCO | REDFOX | 2008-05-05 08:35 | 2008-05-05 09:12 | 44 | 37 | 57052-1 | 1628 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | 3309301//STATION SERVICER ISOLATING EQUIPMENT THAT FAILED NOW, POTENTIAL TRANSFORMER FAILED. VER/HFP IDC XXXX
7334 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-02-12 20:24 | 2019-02-13 00:55 | 6 | 271 | 4783691 | 1626 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | serve-in pulled apart , we replaced it
7335 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-10-17 10:28 | 2011-10-17 19:30 | 3 | 542 | 4990541 | 1626 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY CONDUCTOR HAS MELTED AND SHORTED OUT AT TRANS. POLE. I AM GOING TO SPLICE WIRE. I REWORKED TRANS. LEADS. ///VER/CRB IDCC PN107 XXXX
7336 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2008-07-28 16:31 | 2008-07-28 19:54 | 8 | 203 | 61272-1 | 1624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309101// FOUND BROKEN CUTOUT ON POLE 449-33 WHICH ALSO HAS A LINE FUSE BLOWN ON IT//VER/CRB IDC XXXX
7337 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-05-03 12:19 | 2020-05-03 14:15 | 14 | 116 | 4790161 | 1624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 37830182D00161
7338 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-03-02 11:18 | 2010-03-02 13:14 | 14 | 116 | 62182-1 | 1624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, LINE FUSE OUT, BAD CUTOUT, MAKING REPAIRS, SEND COPY TO R MARCUM, XARM BURNT INTO , NEEDS REPLACED//COD 14//// VER/DBM IDC XXXX
7339 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-12-01 07:23 | 2008-12-01 11:15 | 7 | 232 | 53406-1 | 1624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3402001//XFR IS OUT,WILL RE-FUSE IF NOTHING VISIBLY WRONG IS FOUNDOIL COMING OUT OF BUSHINGS,DID NOT RE-FUSE.CALLED FOR BIGGER XFR AND CREW.NOTE FETR CHANGE RELEASED BY CREW 074S06-----------------CHANGED 25 KVA TO A 50 KVA------ L3/KEP IDC XXXX
7340 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-12-31 08:24 | 2011-12-31 09:54 | 18 | 90 | 4218141 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLLING. FUSE APPEARS TO HAVE MELTED OUT OR BROKE. RE-FUSED 30T @ 9:54. SH VER/PDP IDC XXXX
7341 | Hazard | 3302703 | HAZARD | HAZARD | 2010-04-16 13:35 | 2010-04-16 16:35 | 9 | 180 | 63827-1 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSF == NEED LINE CREW CALLED BRUCE CHANGED TRANSF == POWER OK//COD 9// VER/DBM IDCC PN317 XXXX
7342 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-06-12 13:56 | 2011-06-12 14:50 | 30 | 54 | 4301911 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED RECLOSERS IN ORDER TO SAFELY REPAIR DAMAGED CROSSARMS//SEE ORDER 4300961//COD 30// VER/DBM IDC XXXX
7343 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-06-05 18:00 | 2009-06-05 20:15 | 12 | 135 | 66081-1 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER ON POLE 164-56 VER/KEP L3/KEP IDC XXXX
7344 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-07-02 07:30 | 2011-07-02 12:00 | 6 | 270 | 4447811 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN//CALLING CREW FOR HELP, BIG BUCKET NEEDED // COD 6// VER/DBM IDC XXXX
7345 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2018-05-10 15:33 | 2018-05-10 18:15 | 10 | 162 | 4332691 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | pole38830046B11069 # 2 al primary down to 46-2008. crew reqd. ashland fabricating//L/F 38830046B11069 IS OPEN//pole 46-1069 # 2 al primary down to 46-2008. crew reqd. ashland fabricating Released by crew 078S07
7346 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2014-09-27 07:45 | 2014-09-27 14:30 | 4 | 405 | 4532101 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50KV XFMR 7200, BAD, NEED CREW, BUCKET ACCESSABLE. OIL ON PAVEMENT, NEED TO CLEAN. RELEASED BY CREW 077S08 CREW ON SITE WORKING CHANGED BAD TRANSFORMER ;;POWER RESTORED AT 14;30//COD 4 VER/DKG L3/DKG
7347 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2019-05-28 21:28 | 2019-05-29 02:52 | 5 | 324 | 4357551 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm fuse blown //// Lid has blown off of 25KVA // Changed xfm and restored service @ 02:52/ ISO 38821065D20145/ COD 5*** (1cc premise #039100503 mismapped MD DONE)
7348 | Cannonsburg | 3001401 | LOUISA | CITY | 2009-12-05 11:40 | 2009-12-05 13:55 | 12 | 135 | 56174-1 | 1620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED; TRUCK ACCESSABLE; NEED 7200 CUTOUT; TRANSFORMER FEEDING 4 RESIDENCES RELEASED BY CREW 078S12ALL CUSTOMERS ON @ 13:55 VER/KEP L3/KEP IDC XXXX
7349 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2014-12-06 08:11 | 2014-12-07 11:10 | 1 | 1619 | 4839261 | 1619 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | KYDDC TAGS PLACED ON POLE 38830021B10036//POLE 38830021A20532 BAD LA AND CUTOUT B PHASE OUT TOO POLE 38830021B10036 2-80T LINE FUSE OUT OPENED OTHER FUSE 15:00 NEED BIG BUCKET FOR POLE 21-532 TAGGED LINE FUSE POLE DDC RELEASED BY CREW 078S08..TOO LATE TO HAVE GATE OPENED TONIGHT,,WILL WORK IN AM. CUSTOMER DOES NOT NEED ON TONIGHT ,,CREW ON SITE,ALL REPAIRS MADE, ALL POWER RESTORED VER/CRB
7350 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-01-22 20:33 | 2009-01-22 20:54 | 77 | 21 | 59270-1 | 1617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3010601// HAD TO OPEN @ 39831148A00235 DUE TO TOP OF CUTOUT DOOR BURNING// THIS OUTAGED 77 CUSTOMERS// BAD CUTOUT// BACK ON @ 2054// ONLY 77 OUT ON THIS OUTAGE THE OTHER 13 WERE OUTAGED SEPERATELY/ VER/TOM L3/TOM MLR OK
7351 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-01-07 02:37 | 2014-01-07 11:36 | 3 | 539 | 4244251 | 1617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ENERGIZED PRIMARY LAYING ON GROUND// OPENING RECLOSER TO ISOLATE//OPENED AT 03:48// INSTALLED PRIMARY DEADEND AT 881-79// 2 SPANS OF 6A COPPER DOWN // NEED LINE CREW AND BUCKET TREE CREW, 6A WIRE AND 1 PRIMARY DEADEND ASSEMBLY // CLOSED RECLOSER ON 882-564 AT 04:50 ENERGIZING UP TO 881-79 RELEASED BY CREW 076H02//???? IDCC CNT21 CREATED OUTAGE TO OPEN RECLOSER XXXX
7352 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-07-26 08:41 | 2009-07-26 12:32 | 7 | 231 | 64341-1 | 1617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830278000093 NOT ON MAP, 8T FUSE, CREW REQUIRED AND HAVE BEEN NOTIFIED. PLEASE SEND TO BILL FRALEY RELEASED BY CREW 078S05 MD FILED VER/KEP L3/KEP IDC XXXX
7353 | Pikeville | 3408103 | SALISBURY | MARTIN | 2020-05-27 21:27 | 2020-05-28 02:50 | 5 | 323 | 4915891 | 1615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva trasformer . changed bad transformer everything ok back on at 02:50
7354 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-10-16 06:08 | 2019-10-16 11:25 | 6 | 317 | 4144061 | 1615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cust checked meter and is blank //Cutout broke on pole 98-240 Eric Mckinney has crew enroute to assist/// opened line fuse 98-102 @ 10:55 changed bad cutout closed line fuse in @ 11:25 and restored service L3/HFP
7355 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2018-07-16 14:57 | 2018-07-16 20:20 | 5 | 323 | 4781661 | 1615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200-25kva, no trks. pack in. Released by crew 078S07/on site RM Restored @ 2020bad 7200-25kva, no trks. pack in. Released by crew 078S07/on site RM power on at 20:20 opened line fuse at 18:45 please close tic RM
7356 | Hazard | 3311103 | STINNETT | WENDOVER | 2018-07-23 11:30 | 2018-07-23 12:55 | 19 | 85 | 4839661 | 1615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT OPEN LINE FUSE ON 435-57 @ 1130 AND CLOSED @ 1255 Released by crew 077S01 // no customers out until line fuse was open
7357 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-02-05 10:47 | 2009-02-05 16:10 | 5 | 323 | 55889-1 | 1615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR-28381897 BAD 25KVA NEED 37.5 TRUCK TO POLE 3-CUST RELEASED BY CREW 078S08 REMOVED 25 KVA INSTALLED 37.5 KVA; UPGRADED RISERS; ALL POWER RESTORED AT 1610 VER/KEP L3/KEP
7358 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-11-23 07:54 | 2017-11-23 16:52 | 3 | 538 | 4597451 | 1614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr lid blew off and oil in xfmr is on fire, pole is across crk on hillside, will need line crew to replace xfmr , cutout and arrestor. having to replace pole
7359 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-04-13 19:33 | 2008-04-14 00:02 | 6 | 269 | 50882-1 | 1614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501// FUSE POLE 38831040000093 RELEASED BY CREW 077S05 STS BAD CUTOUT AND BURN TOP OF POLE OFF, GOING TO LOWER EQUIPMENT ON POLE FAULT POLE FUSE POLE 38831040000093 ??RELEASED BY CREW 077S05 STS BAD CUTOUT AND BURN TOP OF POLE OFF, GOING TO LOWER EQUIPMENT ON POLE VER/JHM IDC XXXX
7360 | Whitesburg | 3314401 | MAYKING | ERMINE | 2021-08-03 15:54 | 2021-08-03 20:23 | 6 | 269 | 4998481 | 1614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Lightening arrester bad at pole#497-121, replaced.
7361 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-02-12 14:52 | 2009-02-13 17:45 | 1 | 1613 | 54354-1 | 1613 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP GATE LOCKED, TALKED TO CUSTOMER, SHE WILL OPEN GATE TOMMORROW, 2-13-09 RELEASED BY CREW 078S05PLEASE SEND TO V MULLINS RELEASED BY CREW 078S05/CREW ON SITE MAKING REPAIRS J. HEMLEPP L3/HFP
7362 | Hazard | 3303902 | LESLIE | WOOTON | 2016-04-12 10:08 | 2016-04-13 13:00 | 1 | 1612 | 4084511 | 1612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PAUL PRATT REPORTS HE GOT CALL REPORTING LINE FUSE OUT. BAD CUTOUT BURNT TOP OF POLE OFF WILL HAVE TO GET LINE CREW IN THE MORNING WITH PICKUP, NO ACCESS AS OF NOW// VER/ ADH AJB
7363 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-02-15 07:40 | 2010-02-15 10:39 | 9 | 179 | 57695-1 | 1611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BLOWED UP CUTOUT ON 1130-172 TOOK FUSE OUT ON 1130-168,WILL HAVE TO REPLACE CUTOUT AND RE-FUSE LINE AFT THIS IS DONE//COD 9// VER/DBM IDC XXXX
7364 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2016-05-27 14:08 | 2016-05-27 19:30 | 5 | 322 | 4265141 | 1610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REC. OPEN ON 991-266/// CUTOUT BROKE ON38820991D10303//REC. OPEN ON 991-266/// CUTOUT BROKE ON 991-303// REPAIRS MADE // POWER RESTORED @ 19:30
7365 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-06-07 21:20 | 2016-06-08 10:45 | 2 | 805 | 4322241 | 1610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA 7200 TRANSFORMER BAD ON 16-D-171 NTA CUSTOMER SAID THEY CAN WAIT UNTILL THE MORNING FOR REPAIRS TO BE MADE SPOKE TO TIM HALL HE SAID HE WOULD SEND CREW DOWN FIRST THING IN MORNING NEED MANUAL ROW CREW TO CLEAR PATH RELEASED BY CREW 079H03.REPLACED TRANSFORMER. VER/CRB
7366 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-07-02 19:21 | 2017-07-03 00:43 | 5 | 322 | 4067941 | 1610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | --38830478D10277 BAD 50 KVA 19,9 TRAN--TRK ACCESS THOUGH YARD PER CUST ON B STREET--CREW REQ-DS070217 RELEASED BY CREW 078S01/CREW ON SIE/FETR 0200/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0043/PLEASE CLOSE TICKET/THANKS/VEM // COD 5
7367 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2017-10-28 12:13 | 2017-10-28 14:54 | 10 | 161 | 4505161 | 1610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINEF IS OUT,WILL PTRL////////POLE 1108-123,CUTOUT BROKEN,WILL REPLACE//////CUTOUT REPLACED,WILL RE-FUSE VER/AWD L3/HFP XXXHFP
7368 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-11-30 15:25 | 2008-11-30 20:47 | 5 | 322 | 53243-1 | 1610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303// RELEASED BY CREW 080S013408303// , BAD CUTOUT, REPLACING IT, POLE#1137-A-368, ABOUT 5 CUST, ON AT 2047//VER/CRB IDC XXXX
7369 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-03-14 02:03 | 2015-03-14 15:27 | 2 | 804 | 4192091 | 1608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 265-B-359 FAILED CUTOUT CALL CAME IN ON 4191971/ 265-B-359 FAILED CUTOUT 40-4 POLE #2 AL WIRE DOUBLE DEADEND CUTOUT AND FIBERGLASS BRACKET. CAN USE TRUCK. NEED 3 MAN CREW WITH LINE TRUCK AND BUCKET TRUCK./ ISO 37820265B00060/ COD 2/ VER/BOW
7370 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-06-20 11:34 | 2014-06-20 20:30 | 3 | 536 | 4121891 | 1608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY LOOP BURNT OPEN POLE 20/7548; NEED SERVICER; MAY NEED FLAGGERS; RELEASE TO LINE; EBP RELEASED BY CREW 078E02 CREW ON SIGHT WAITING FOR AWP CREW/ FETR 23:15..REPLACED SPAN 1/0 SECONDARY, RESTORED POWER 20:30 VER/KEP
7371 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2017-05-13 22:42 | 2017-05-15 01:30 | 1 | 1608 | 4796771 | 1608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200 - 10 KVA,BETWEEN SLAG & ASHPHALT PLANT. TRUCKS OK. 138 OVERBUILD RELEASED BY CREW 078S07,,CREW ON SITE,,XFMR REPLACED ,,ALL POWER RESTORED
7372 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-05-29 17:33 | 2015-05-29 19:47 | 12 | 134 | 4481781 | 1608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 076H07///LINE FUSE BLOWN AT 901-177///BAD CUTOUT ON POLE 901-162///MAKING REPAIRS///REPAIRS MAD///CLOSED LINE FUSE ON POLE 901-177 @ 19:47///COMPLETE BR/ ISO 38830901000177/ COD 12/ VER/BOW
7373 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2011-01-09 09:05 | 2011-01-09 15:47 | 4 | 402 | 60084-1 | 1608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 449-729 RELEASED BY CREW 077S11BAD XFMR ON POLE 49-729 .. REPLACED BANK OF XFMRS & CLEANED OIL SPILL UP RESTORED POWER AT 15:47, ONLY 4 CUSTOMERS AFFECTED IN THIS OUTAGE//VER/CRB IDC XXXX
7374 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-02-28 10:47 | 2017-02-28 15:15 | 6 | 268 | 4428051 | 1608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S06 BAD 50 KVA, CREW REQ, CAN USE TRUCKS AT THE CORNER OF TRAM RD AND KEYS LANE RELEASED BY CREW 078S06 // REPLACED VER/CRB
7375 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-09-24 20:05 | 2014-09-24 20:27 | 73 | 22 | 4526451 | 1606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR ON POLE #188-151 IS BROKE AND CONDUCTOR IS LAYING ON ARM/// WILL OPEN RECLOSERS ON POLE #211-A-305 AND CHANGE INSULATOR// OPENED RECLOSERS @20:05 AND CLOSED BACK IN @ 20:27 /// RESTORED SERVICE NO OUTAGE TIL RECLOSER WAS OPENED VER/CRB AJB
7376 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-11-01 05:22 | 2013-11-01 10:43 | 5 | 321 | 4989551 | 1605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PIECE OF 2/3 SEC CABLE BROKEN DOWN,WILL REPAIR////////MADE NECESSARY REPAIRS,ALL OK AFTERWARDS. VER/CRB L/3 CRB
7377 | Pikeville | 3401001 | ELWOOD | DORTON | 2021-06-09 23:41 | 2021-06-10 08:35 | 3 | 534 | 4700521 | 1602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout GuidelinesWe have a broke Cutout on Pole 262-52,Going to make repairs..We have a broke Cutout on Pole 262-52,Going to make repairs..Restored service @ 08:35.
7378 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2021-05-21 21:29 | 2021-05-22 10:50 | 2 | 801 | 4609071 | 1602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | current limiting fuse bad/Refused transformer c/o and closed, still no power, will need to replace current limiting fuse and try again. I opened door back up before leaving c/o has been refused. By Truck blacktop driveway no flagging needed. Released by crew 078E06. power restoed at 1050
7379 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-08-23 10:56 | 2014-08-24 13:38 | 1 | 1602 | 4412861 | 1602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CREW REQ 15 KVA CABIN CAN WAIT RELEASED BY CREW 078S09 CHANKGED BAD KVA ON PN:333-143 OLD KVA HOWARD IND 3815005201 15KVA NEW KVA POWER PARTNER SS# 14A300063 15 KVA REFUSED CUTOUT ON PN 333=140 AT 13:38 POWER RESTORED PLEASE CLOSE TICKET THANKS DWW VER/CRB
7380 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-07-10 09:01 | 2014-07-10 10:30 | 18 | 89 | 4224631 | 1602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 1147-4532 40T POLE 1147-4615 BAD LA REMOVED OFF CSP TRANS,
7381 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-11-27 15:25 | 2019-11-27 21:09 | 13 | 344 | 4090341 | 1601 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQD///////PRIM CND BROKE LOOSE,SQUEEZON IS HOLDING IT UP.DID GET CUSTS POWER BACK ON.NEEDS TO BE FIXED SOON THOUGH.MAY WANT TO LET CREW REPAIR THIS AFTER ALL ELSE IS DONE.ABT A FOOT APART MIDSPAN. Released by crew 074S06//OPENED L/F 38831027B00032 TO MAKE REPAIRS @ 2020 all repairs made @ 2109
7382 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2016-02-29 04:25 | 2016-02-29 07:45 | 8 | 200 | 4785381 | 1600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 38830045C45781/ POWER RESTORED 0745/ ISO 38830045C45781/ COD 8/ VER/BOW L3/HFP XXXHFP
7383 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-10-03 10:01 | 2016-10-03 15:21 | 5 | 320 | 4955811 | 1600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO REPLACE WITH 25 KVA 19.9 PER MIKE LEWIS RELEASED BY CREW 077S04 REPAIRS MADE AND POWER RESTORED 1521 VER/CRB L3/HFP XXXHFP
7384 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2011-10-20 14:29 | 2011-10-20 21:09 | 4 | 400 | 4004481 | 1600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 879-290, BURNING TOP OF POLE OUT, 3 WAY PRI DEADEND POLE, SHOULD BE ABLE TO USE EVERYTHING BACK, WELL NEED NEW CUTOUT, MAPS SHOWS TO BE A 355, SHOULD GO BACK WITH A 405, PASS HARDIN GREENHOUSE, CROSS HIGHWAY, TURN AT HILLSIDE DRIVE. CREW REQ, LINE IS NOT GROUNDED, DO HAVE PERMISSION TO BACK TRUCKS IN YARD RELEASED BY CREW 078S06/TECH TO WRITE JOB/WINDSTREAM POLE/POWER RESTORED 2109/PLEASECLOSE TICKET/THANKS/VEM ///VER/CRB IDC XXXX
7385 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-02-28 13:03 | 2017-02-28 13:37 | 47 | 34 | 4428271 | 1598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BYPASS C/O GOING BAD ON POLE 37830095000227, DAVE SAMMONS IS ON THE WAY TO HELP CHANGE OUT.//NO OUTAGE TILL RECLOSER OPENED//NO OUTAGE TILL RECLOSER OPENED ON POLE 37830095000227 @ BYPASS C/O GOING BAD ON POLE 37830095000227, DAVE SAMMONS IS ON THE WAY TO HELP CHANGE OUT. OPENED ALL 3 RECLOSERS @1303 AND PUT BACK ON @1337. VER/CRB AJB
7386 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-02-09 04:46 | 2021-02-09 06:20 | 17 | 94 | 4950571 | 1598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | called customer and customer is unable to check meter Fuse link broke in temporary line fuse installed on 785-201 (Installed for construction purposes) Restored @ 6:20. No map desc needed. sh///All customers termporarily fed from B phase till construction work is complete (17 COD)
7387 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-12-27 21:49 | 2010-12-28 11:08 | 2 | 799 | 56370-1 | 1598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE/////////XFR IS BAD,WILL CHANGE IN MORNING.IT IS A 15 19.9,NEED TO GO BACK WITH A 25.HOLD TICKET PER D SAMMONS,WILL CALL FOR IT IN MORNING WR# 38216972/// REPLACED BAD XFMR AND RESTORED POWER. TIM MCCOY RELEASED BY CREW 074H10 COD-2 ISO TF 38821010000057 VER/HFP L3/HFP IDC XXXX
7388 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-10-01 03:36 | 2016-10-01 10:15 | 4 | 399 | 4951811 | 1596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 91-D-292 BAD 12KV CUT OUT. TRK OK . IN BLIND CURVE RELEASED BY CREW 078S07,,CREW ON SITE..CUTOUT REPLACED,,ALL POWER RESTORED/ ISO 38830091D00292/ COD 4/ VER/BOW L3/HFP XXXHFP
7389 | Pikeville | 3421001 | BREAKS | CITY | 2016-04-30 23:50 | 2016-05-01 04:16 | 6 | 266 | 4146271 | 1596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40T LINE FUSE OUT DUE TO BAD CUTOUT ON POLE 243-D-109 WILL BE CHANGING OUT. CHANGED BAD TRANSFORMER CUTOUT CLOSED IN 40T LINE FUSE EVERYTHING OK VER/ARN
7390 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2010-06-02 22:19 | 2010-06-03 11:37 | 2 | 798 | 55616-1 | 1596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07 BAD CSP TRANSFORMER 25 KVA, NO TRUCK IVE ALREADY GOT PERMISSION FROM OWNER TO USE YARD DOG, NEED CUT-OUT AND STAND-OFF CREW REQ WHEN CREW FINISHS WITH JOB CALL 465-2099, CUST WANTS CALLED RELEASED BY CREW 078S09/CREW GETTING TRACK EQUIP IN PLACE/DIFF LOCATION/FETR 1300/VEM VER/KEP L3/KEP IDC XXXX
7391 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-12-07 09:35 | 2010-12-07 12:00 | 11 | 145 | 63991-1 | 1595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TWO OUTSIDE FUSES BLOWN ON POLE 38831027C00604...FOUND TWO CRACKED CUTOUTS ON POLE 38831027C00604...ROGER MAYNARD HAS A CREW IN ROUTE TO CHANGE...WILL HAVE TO OPEN CENTER PHASE WHEN CREW ARRIVES...POWER RESTORED @ 12:00 COD-20 ????? VER/HFP L3/HFP IDC XXXX
7392 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-02-08 10:38 | 2014-02-08 15:57 | 5 | 319 | 4367731 | 1595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL NEED SOME HELP, XFMR LEADS BURNT UP WILL HAVE TO CHANGE TO BIGGER LEADS AND REMAKE CONNECTS.///// VER/SEF
7393 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-06-10 01:41 | 2008-06-10 07:00 | 5 | 319 | 61194-1 | 1595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000202//...BAD TRANSFORMER ON POLE 286-150,,, TRANSFORMER NEEDS TO BE UPGRADED TO 25KVA,,, YOU CAN REACH IT WITH A TRUCK,, I ASK OWNERS IF IT WOULD BE ALRIGHT TO GO DOWN BESIDE GARAGE THEY SAID OK RELEASED BY CREW 078S02/CREW ON SITE J. HEMLEPP 078H05//COD 5// VER/DBM IDCC TOF0301 XXXX
7394 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-08-25 20:13 | 2010-08-26 09:30 | 2 | 797 | 60592-1 | 1594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | MARK SWIFT PH 232 0446 VERITY MIDDLE SCHOOL--METER# 428783432 --BAD CONECTION AT CT --DAMAGED CT--WILL REPAIR 8/26/10 RELEASED BY CREW 078S07MARK SWIFT PH 232 0446 VERITY MIDDLE SCHOOL--METER# 428783432 --BAD CONECTION AT CT --DAMAGED CT--WILL REPAIR 8/26/10 -O ADKINS MADE REPAIRS--10:30 VER/KEP L3/KEP IDC DCMT CHANGED TIME OFF FROM 1030 PER CONF CALL, CUSTOMER WAS OK WITH WAITING TILL MORNINIG XXXX
7395 | Hazard | 3310502 | HADDIX | CANOE | 2009-12-30 10:34 | 2009-12-31 13:07 | 1 | 1593 | 66232-1 | 1593 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS NEED 10 KVA TRANSFORMER AND SERVICE WIIRE RELEASED BY CREW 077S05 STEVE REPORTS JIM MULLINS WILL HAVE CREW REPAIR THIS ON 12/31/09. REPLACED XFMR AND RESTORED POWER AT 1245 JKC IDC XXXX
7396 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-11-30 09:56 | 2009-11-30 10:55 | 27 | 59 | 51184-1 | 1593 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND HOT TAP LEAD BURNTED OFF OF LINE FUSE, HAVE REPAIRS MADE AND POWER IS RESTORED AT THIS LOC IDC XXXX
7397 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-12-16 01:34 | 2016-12-16 10:25 | 3 | 531 | 4199241 | 1593 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEED 2 MEN AND BIG BUCKET, AND 7200 CUTOUT AND ARR. AND TEE BRACKET. RELEASED BY CREW 077S04.CHANGED BAD CUT OUT, ALL POWER RESTORED @ 10:25 HRS// VER/ ADH
7398 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2012-01-03 23:37 | 2012-01-04 06:15 | 4 | 398 | 4230981 | 1592 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAS TO BE A BAD CON SOMEWHERE,3 POLES TO CHECK,2 ARE CLIMBERS///BAD SPLICES AT POLE 232,CANT REACH SAFELY IN DARK DUE TO A BROKEN UG CONDUIT ON POLE.NEED HELP TO MAKE REPAIRS////////NOTE NEW FETR/////MADE NECESSARY REPAIRS AND RESTORED VER/ARN IDC XXXX
7399 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-12-13 23:21 | 2019-12-14 12:37 | 2 | 796 | 4152021 | 1592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines broke 19,9 cutout, need flagers and crew Released by crew 077S05..replaced cutout, all power restored @ 12:37..p.hicks
7400 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-04-03 09:10 | 2015-04-03 10:56 | 15 | 106 | 4263131 | 1590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | RELATED TO 4261731// OPENING LINE FUSE 38830901000161 TO SAFELY REPLACE SWITCH ON POLE 38830925000088 L3/DKGXXX
7401 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-01-25 07:30 | 2009-01-25 10:09 | 10 | 159 | H59704-1 | 1590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND RECLOSER TO STILL BE IN WHEN I ARRIVED, THEN FOUND A SPAN OF #4 CU, PRIMARY DOWN ON POLE 1024-88, OPEN RECLOSER AND ISOLATED AND GROUNDED IT, AND THEN CLEARED PRIMARY OUT OF THE ROAD, HAVE CALLED FOR CREW TO BUT THIS BACK, ALSO CAN USE TRUCKS, LOOKS LIKE IT PULLED OUT OF SLEEVE RELEASED BY CREW 078S06//COD 166 VER/KEP L3/KEP
7402 | Hazard | 3310502 | HADDIX | CANOE | 2021-11-05 06:37 | 2021-11-05 11:55 | 5 | 318 | 4058991 | 1590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 75 kva 19,9 ,call gilley and getting crew together Released by crew 077S05
7403 | Paintsville | 3409302 | KENWOOD | AUXIER | 2012-02-11 07:33 | 2012-02-11 12:51 | 5 | 318 | 4333711 | 1590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 T FUSE BLOWN ON 858-244..DUE TO CSP TRANSFORMER BAD ON POLE. 858-267..CHANGED OUT 25 KVA TRANSFORMER. ///VER/CRB IDC XXXX
7404 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-02-22 00:45 | 2020-02-23 03:15 | 1 | 1590 | 4425111 | 1590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad neutral in UG service, Need power temp. Meter on left side of home in corner by fence. Released by crew 078S02/ removed meter interrupting power at 0045/ loading pwr temp now LRM pwr restored @ 3:15 please close ticket LRM/ ISO 39831148B20375/ COD 1 L3/HFP
7405 | Pikeville | 3407101 | TOPMOST | DEMA | 2017-02-22 07:23 | 2017-02-22 14:00 | 4 | 397 | 4413351 | 1588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED . REPLACED CUTOUT AND ARRESTER, ALL WORK COMPLEE / GXJ 37830138000027 VER/AWD L3/HFP XXXHFP
7406 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-06-21 08:49 | 2018-06-21 17:38 | 3 | 529 | 4632871 | 1587 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broke on pole 189-233 and broke clamp off the pri. bushing of xfm...will need 1 man with bucket to replace 19.9 15kv. single bushing xfm..restored @ 1738
7407 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-11-19 08:28 | 2008-11-19 09:29 | 26 | 61 | H66411-1 | 1586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | WR 27354496 ** SERVICE FOUND WIRE DOWN WILL ISOLATE- CREW CALLED OUT TO MAKE REPAIRS.WIRE PULLED OUT OF SLEEVE AT 38830351000103, SLID THROUGH NEXT POLE, 2 SPANS PRIMARY DOWN, REC STILL CLOSED, PRI HANGING IN CLEAR AT FAULT POLE.. TRUCK OK RECLS NOT OUT .. OPENED BOTH RECL AT POLE 351-72 AT ____ CLOSED AT _____WR 27354496 SERVICE FOUND WIRE D VER/KEP IDC XXXX
7408 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-07-11 08:03 | 2018-07-11 10:05 | 13 | 122 | 4760521 | 1586 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | pole 138-490 10 t xfmer fuse restored
7409 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2017-07-21 22:02 | 2017-07-22 11:15 | 2 | 793 | 4153491 | 1586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER ON 1114C115 NTA 4 MEN AND FOREMAN 25 KVA 7200 AND CUTOUT AND BRACKET DO CALL OUT ABOUT 5:30 AM PER DENNIS MASSEY RESTORED AT 11:15//VER/ADH. L3/HFP XXXHFP
7410 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-05-24 11:18 | 2011-05-24 16:35 | 5 | 317 | 4157361 | 1585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S10---NEED SMALL TRUCK TO PATROLL LINE VER/HFP L3/HFP
7411 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-06-21 21:06 | 2021-06-22 01:30 | 6 | 264 | 4786631 | 1584 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | no outage.single cust prb..cust had a hot lead on service about burned into.cut didnt have any 240voltage.tracked it down and replaced the splice.
7412 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2010-07-23 12:14 | 2010-07-23 16:16 | 15 | 242 | 55950-1 | 1584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 91-100 BAD 50KVA TRANS TRUCK OK NEED T-BRECKET AND CUTOUT LINE FUSE ON 91-299 30T BACK ON 01;10 5- CUST STILL OUT RELEASED BY CREW 078S08// ALL BACK ON AT 16:16 VER/KEP L3/KEP IDC XXXX
7413 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2013-04-08 10:09 | 2013-04-08 13:05 | 9 | 176 | 4987311 | 1584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SEHD TO B FRALEY RELEASED BY CREW 078S07//BAD XFMR//COD 9// VER/DBM IDC XXXX
7414 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-10-29 11:08 | 2020-10-29 11:44 | 44 | 36 | 4595131 | 1584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER 37830319000034 TO REPLACE CUTOT ON POLE 37830319000041//NO OUTAGE TILL RECLOSER OPENED ATCracked cutout on pole 319-41, isolated at 9:55. Will be opening recloser on pole 319-34 to safely replace this equipment.Cracked cutout on pole 319-41, isolated at 9:55. Will be opening recloser on pole 319-34 to safely replace this equipment. Recloser on 319-34 was opened at 11:08 and closed at 11:44.
7415 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2011-05-17 18:42 | 2011-05-17 22:00 | 8 | 198 | 4106611 | 1584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 40004927 //BAD 19.9 CUTOUT WAS ABLE TO LIFT HOTTAP; LINE CREW IN ROUTE TIME OFF WAS 1913 RELEASED BY CREW 078S11//CREW ON SITE///078H05/ REPAIRS COMPLETE POWER RESTORED @ 22:00 J. HEMLEPP & CREW COD-8 ISO LF 38830478A40284 VER/HFP L3/HFP
7416 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-02-15 11:10 | 2016-02-15 11:43 | 48 | 33 | 4696981 | 1584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN THE AM 2-15-16 DUE TO SLICK ROADS, BAD CUTOUT ON POLE 231-82, CALLED FOR HELP, WILL NEED TO OPEN LINE WHEN HELP GETS HERE//NO OUTAGE TILL STEP-DOWN OPENED ON POLE 37830207D00067 @1110 VER/CRB L/3 CRB AJB
7417 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-02-12 08:07 | 2009-02-13 10:30 | 1 | 1583 | 66349-1 | 1583 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SERVE END ON WIRE ON POLE, HAVE RESQUEEZED AND EVERYTHING IS OK AT THIS LOC.
7418 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-06-19 20:13 | 2014-06-19 22:06 | 14 | 113 | 4117251 | 1582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE OPEN AT POLE 379-172, STIRRUP BURNDT INTO AT POLE 379-241, WILL BE MAKING REPAIRS.MADE REPAIRS CLOSED L/F BACK IN AT 22:06//COD 14// VER/DBM
7419 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2010-12-07 11:32 | 2010-12-07 13:05 | 17 | 93 | 64046-1 | 1581 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT-UP ON 808-80. FUSE NOT ON MAP. CUTOUT APPEARS TO BE OK - REPLACING DOOR. DOOR REPLACED. RE-FUSED @ 13:05. PLEASE ADD 30T FUSE ON 808-80 TO MAP. THANKS, SH ENTERED MD .... HFP COD-17 ISO LF 38830808000080 VER/HFP L3/HFP IDC XXXX
7420 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-10-05 08:16 | 2018-10-05 13:32 | 5 | 316 | 4200001 | 1580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad 19.9 insulator on pole 38821058D00252 have called for line crew. complted COD-5 ISO LF 38821058D00274
7421 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2016-09-03 14:03 | 2016-09-03 19:19 | 5 | 316 | 4866331 | 1580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 TRANS. ON POLE 24-B4-224, GOING TO OPEN OTHER 2 FUSES ON BANK, WILL NEED 2 MEN, AN A LINEMAN AND A LOWER CLASS WITH A MATERIAL HANDLING BUCKET TO HELP CHANGE. CUTTING 1/0 IN CLEAR FROM POLE 24-224 TOWARD 24-223. BAD 50 KVA 7200 TRANS. ON POLE 24-B4-224, GOING TO OPEN OTHER 2 FUSES ON BANK, WILL NEED 2 MEN, AN A LINEMAN AND A LOWER CLASS WITH A MATERIAL HANDLING BUCKET TO HELP CHANGE. GOT TRANS CHANGED OUT AND CLOSED THE BANK BACK IN @ 1919. ALSO GOT THE 1 CUST. ON POLE 223 PUT B VER/AWD
7422 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-05-16 17:30 | 2010-05-17 19:50 | 1 | 1580 | 63329-1 | 1580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | STS WR # 35137146 // CLOSED RECLOSER IN AND IT DID NOT STAY LINE IS ALL BACK IN THE MTN AND THIS WILL BE BETTER TO HOLD THIS UNTILL TOMMOROW MORNING TOP OF POLE BROKEN OFF ALL MANUAL2 BR VER/KEP L3/KEP IDC XXXX
7423 | South Williamson | 3411401 | DEWEY | INEZ | 2014-08-27 08:00 | 2014-08-27 14:35 | 4 | 395 | 4427071 | 1580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 CU PRIMARY PULLED OUT OF SLEEVE AND BLEW LINE FUSE ON 38830766B00044. NEED BUCKET ROW CREW, THREE MEN, #4 CU WIRE AND BIG BUCKET. NO TEMP GROUNDS OR TAGS PLACED. RELEASED BY CREW 076S02/ OPENED FUSE ON SIDE TAP AT 12:06 CLOSED BACK AT 13:06 TO PUT WIRE UP SAFELY , SEND COPY TP PEGGY WYSONG, TCM// VER/KEP
7424 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2021-08-17 20:50 | 2021-08-18 10:00 | 2 | 790 | 4092341 | 1580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 197-164///NO TRUCK///Customer said would be ok till in the morning///will need 1 man to assist/// Released by crew 074S02
7425 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-03-08 20:05 | 2009-03-08 22:43 | 10 | 158 | 56332-1 | 1580 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3103101//RECLOSER WAS NEVER OUT//COD 10//MADE MDC//PRIMARY FELL OFF POLE. BAD INSULATOR ON POLE126-26. RE TIED WIRE ON SIDE OF INSULATOR, SHOULD HOLD TILL TOMORROW. IDC XXXX
7426 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-12-07 11:37 | 2009-12-07 16:00 | 6 | 263 | 50301-1 | 1578 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD 4/0 UG CALLING CREW--IKES CREW TO WORK RELEASED BY CREW 078S07//COD 6// VER/DBM IDC XXXX
7427 | Hazard | 3309003 | JEFF | VIPER | 2018-11-15 18:15 | 2018-11-15 19:38 | 19 | 83 | 4427661 | 1577 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened line fuse on pole 440-3 at 18:15 closed line fuse at 19:38 lowered attachments 1815-1938 L3/HFP
7428 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2020-11-03 09:26 | 2020-11-03 16:00 | 4 | 394 | 4638101 | 1576 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Reported Bright/Dim // This house and the brothers home next door is having the same issues // customer Mable Hunt contact number 502-208-2827REWORKED ALL CONNECTIONS,XFR STILL SURGING OCCASIONALLY////////BRINGING ME ONE FRM PVILLEREWORKED ALL CONNECTIONS,XFR STILL SURGING OCCASIONALLY////////BRINGING ME ONE FRM PVILLE///////REPLACED XFR&RESTORED,ALL OK
7429 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-10-30 21:45 | 2016-10-30 23:30 | 15 | 105 | 4064251 | 1575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE ON 39831147C24555 AT 2145 TO ISOLATE FAULT POLE 39831147C24557 - DUE TO POLE FIRE// CREW CALLED TO MAKE REPAIRS// WILL UPDATE WHEN MORE INFO AVAILABLE//TOM,REPLACE CUTOUT LINE FUSE IN @ 2330 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/TOM L3/TOM
7430 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2012-12-20 09:25 | 2012-12-20 10:40 | 21 | 75 | 4484611 | 1575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 375-265 WILL HAVE TO POLE LINE FUSE ON POLE 375-464 TO ISOLATE.. REPLACED CUTOUT RESTORED POWER AT 10:40 VER/KEP
7431 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2015-11-12 12:10 | 2015-11-12 15:05 | 9 | 175 | 4432991 | 1575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED LINE FUSE ON POLE 38820771B10065 AT 12:10 TO ISOLATE POLE 38820771B10185 THAT IS ON FIRE DUE TO A BAD TRANSFORMER CUTOUT. FIRE DEPT IS EN-ROUTE TO PUT THE FIRE OUT.// POLE BURNT - CREW ENROUTE// RELEASED BY CREW 079S02 RELEASED BY CREW 079H07 VER/CRB
7432 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-05-22 06:53 | 2010-05-22 09:18 | 23 | 145 | 66226-1 | 1575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 168-12. I AM PATROLLING LINE NOW. CUTOUT IS BROKEN DOWN ON POLE 168-15. I HAVE IT ISOLATED FROM MAIN LINE. I AM GOING DOWN AND CLOSE LINE FUSE IN AT POLE 168-12. THIS WILL LEACE 3 CUSTOMERS OUT. I CLOSED LINE FUSE IN AT 07:50 AND IT STAYED. ONLY 3 CUSTOMERS ARE STILL OUT. WILLIE IS BRINGING CUTOUT TO CHANGE IT. RELEASED BY CREW 074S01 // COD-23 VER/HFP L3/HFP IDC XXXX
7433 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-08-14 13:30 | 2010-08-14 16:25 | 9 | 175 | 54631-1 | 1575 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36442292 // 15 KVA TRANSFORMER FEEDING 8-CUST NEEDS UPGRADED TO AN 25 KVA SINGLE BUSHING 7200 120/240 TRANSFORMER .NEED NEW CUT-OUT AND OIL SPILL KIT TO CLEAN UP BLACK TOP NEAR ST, TRUCKS O.K, CREW REQ, RELEASED BY CREW 078S09---TREE CREW TO CUT OUT SEC.---OUTAGE 13:30 TO 16:25 VER/HFP L3/HFP
7434 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-07-02 04:08 | 2012-07-02 17:15 | 2 | 787 | 4199551 | 1574 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACE BAD ARRESTOR. PLEASE CLOSE THIS TICKET
7435 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2021-05-09 19:26 | 2021-05-09 23:48 | 6 | 262 | 4565611 | 1572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Line fuse cutout riser connection failed. Repaired and restored @ 23:48. sh/ ISO 38830810B00023/ COD 6
7436 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-06-01 21:50 | 2009-06-02 04:23 | 4 | 393 | 58245-1 | 1572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLING CREW /BAD TRANSFORMER//WR#30084441//CREW HAS BEEN ON SITE FOR AWHILE GETTING YARD DOG TO POLE/FETR0530/VEM/ALL CUST RESTORED 0423/PLEASE CLOSE TICKET/THANKS/VEM VER/LDA IDC XXXX
7437 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-09-22 14:33 | 2022-09-22 18:55 | 6 | 262 | 4909821 | 1572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | xfmer pole broke 18-52 loop cut @ 18-50 isolating broke pole. line crew reqd. Released by crew 078S07. complete time on 18:55
7438 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2017-05-11 20:54 | 2017-05-12 10:00 | 2 | 786 | 4783651 | 1572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 2 MEN.LINE FUSE OUT ON 752-22..PATROLLING. LINE FUSE CUTOUT BROKEN HANGING DOWN BETWEEN PHASES ON CROSS ARM..NEED COVER UP AND OBSERVER..CLIMBER DIFF LOCATION..WATER IN BOTTOM..HAVE TO WADE SMALL CREEK..NEED TO WAIT UNTIL TOMORROW.. RELEASED BY CREW 076S01/// VER/DKM
7439 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-04-07 13:04 | 2013-04-07 17:26 | 6 | 262 | 4985571 | 1572 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT// POWER IS RESTORED ///VER/CRB L/3 CRB IDC XXXX
7440 | Hazard | 3309302 | VICCO | JEFF | 2009-12-10 06:44 | 2009-12-11 08:55 | 1 | 1571 | 57313-1 | 1571 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OPEN @ POLE 346-A0-0419. NEEDS RE-FUSED. CWB RELEASED BY CREW 078E10 === CUTOUT GATE BURNED UP REPLACED & REFUSED ==POWEROK
7441 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-07-03 14:35 | 2012-07-03 17:12 | 10 | 157 | H4274681 | 1570 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED INTO AT 153-9, OPEN RECLOSER AT POLE 153-273 AT AROUND 15:50 TO WORK ON LOOPS.LOOP BURNT OPEN ON POLE 37830153D00009 OPENED REC. ON POLE 37830153D00253 AT 15:50 REPAIRED LOOP, CLOSED REC. AT 16:35. POWER RESTORED. ///VER/CRB L/3 CRB AJB
7442 | Hazard | 3302704 | HAZARD | KENMONT | 2014-02-13 09:01 | 2014-02-13 22:05 | 2 | 784 | 4379771 | 1568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S04 - REPLACE CUTOUT BUCKET TRUCK ACCESSABLE CANTACT G. FUGATE IF MORE INFO IS NEEDED MWL----- CUTOUT REPLACED, POWER RESTORED. VER/TOM L3/TOM
7443 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2014-01-07 10:19 | 2014-01-07 13:35 | 8 | 196 | 4249461 | 1568 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED 25 KVA XFMR FAILED AND BLEW XFMR FUSE. NEED A 50 KVA XFMR, THREE MEN, MATERIAL HANDLER. CAN BLOCK SIDE STREET AND TRUCK. CREW ENROUTE. RELEASED BY CREW 076S02// CREW ON SITE TCM//COD 8// VER/DBM L3/HFP
7444 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-09-29 17:02 | 2010-09-29 20:18 | 8 | 196 | 55258-1 | 1568 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | RISER AT TRANSFORMER LUG BURN-IN TWO // VER/CRB IDC XXXX
7445 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2019-11-24 02:10 | 2019-11-24 09:00 | 15 | 410 | 4061421 | 1566 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened line fuse on pole 37830182D00117 @ 0210 due to pole fire.opened solid blade on pole 182-121,pole #182-283 burnt off at ground CLOSED FUSE @ 0230 UP TO SB ON POLE 37830182D00121 //MADE MD TO SHOW SB ON THIS POLE//NO OUTAGE TILL L/F OPENED
7446 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-06-19 18:35 | 2022-06-20 20:40 | 1 | 1565 | 4255921 | 1565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Per G Shenefield, only 1 customer out of power. Transformer fuse is still in. One service coming off the transformer has the neutral and 1 hot leg burned in two, will be making repairs with Todd McCoy later tonight. 6/20/22.
7447 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2018-11-21 18:42 | 2018-11-21 23:55 | 5 | 313 | 4468251 | 1565 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | xfr open @ 254-9,,,,,1 span open wire burnt down 254-9 to 254-10,,,crew required and a role of 1/0 service drop pole to pole Released by crew 078S05//cod 5 L3/HFP
7448 | South Williamson | 3202201 | LOVELY | LOVELY | 2017-07-05 22:03 | 2017-07-06 11:05 | 2 | 782 | 4078481 | 1564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9. CAN USE BUCKET TRUCK. I TALKED TO THE CUSTOMER AND HE SAID WE CAN WAIT TILL DAYLIGHT TO WORK//PER STEVE RAY, HOLD UNTIL REGULAR WORK HOURS//POWER RESTORED // ISO 38820770C00051/ COD 2/ VER/BOW
7449 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-09-17 23:19 | 2012-09-18 12:21 | 2 | 782 | 4055971 | 1564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | TREES IN LINE WHERE IT CROSSES THE RIVER NEED ROW CREW , AND COULD BE BAD DEAD END INSULATOR ON POLE # 1062-51 MIGHT BRING ON JUST IN CASE . 19.9 RELEASED BY CREW 075H04//WILL WORK IN THE AM STS BAD INSULATOR ON POLE 1062-51 COD-2 ISO LF 38831062000045 VER/HFP L3/HFP IDC XXXX
7450 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-10-28 02:27 | 2009-10-28 03:35 | 23 | 68 | 59942-1 | 1564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 20-1591 BAD LA REPLACED //VER/GAH IDC XXXX
7451 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-01-17 13:49 | 2012-01-17 15:21 | 17 | 92 | 4268521 | 1564 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 269-169 LINE FUSE BLOWN CREW REQUIRED POLE ON FIRE NO TRUCKS HILLSIDE/ISOLATED 269-171 B PHASE ONLY HOT/269-169 BACK ON AT 1521 HRS. ////VER/CRB IDC XXXX
7452 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-10-07 13:11 | 2021-10-07 16:30 | 12 | 199 | 4327771 | 1563 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | C phase fuse open on arrival (12 COD)C Phase Line fuse open on 144-A-62,(ASSESSING CONDITION)..C Phase Line fuse open on 144-A-62,We have a Blown Arrester on Tran Bank pole 144-A-421,Have trouble isolated and Paul Layne is coming to change all 3 Cutouts and Arrester..
7453 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-04-25 10:54 | 2018-04-25 13:58 | 14 | 184 | 4277271 | 1562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @38831148000253, checking.pole fire on 38831148000299. lifted hot tap on 38831148000082. will refuse at 38831148000253.have material on way to make repairs on 229.this coustomer will be out till aprox 14:30, closed line fuse back in @12:40. last coustomer on @13:58. Released by crew 074S05
7454 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2010-03-09 14:18 | 2010-03-09 16:40 | 11 | 142 | 64322-1 | 1562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SEND TO B LYNCH RELEASED BY CREW 078S07//VER/CRB IDC XXXX
7455 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-07-16 13:43 | 2016-07-17 15:45 | 1 | 1562 | 4646961 | 1562 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | A & C TRANS, FUSES OUT TRYED A PHASE FUSE BLOWN DID NOT TRY OTHER ONE TRUCK TO POLE IF DRY BRING 2-25KVA TRANS. RELEASED BY CREW 078S08//CALL MAINT AFTER COMPLETE TO CHECK THEIR EQUIP// VER/CRB
7456 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-05-21 21:47 | 2022-05-22 01:30 | 7 | 223 | 4924051 | 1561 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | rest 0130
7457 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-06-26 18:54 | 2009-06-26 21:30 | 10 | 156 | 63793-1 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNED UP// VER/DBM
7458 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-06-26 06:42 | 2021-06-26 09:18 | 10 | 156 | 4808531 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | load side fuse out on step down pole 146-194// patroling// found bad arrester on pole 146-125, cut in the clear// will try step down fuse//DAE MADE
7459 | Pikeville | 3407103 | TOPMOST | KITE | 2014-04-01 15:51 | 2014-04-01 17:35 | 15 | 104 | 4552671 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED ARRESTER AND REFUSED LINE / GXJ /// COD-15 ISO LF 37830209000058 VER/HFP L3/HFP IDC XXXX
7460 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2016-03-15 10:45 | 2016-03-15 12:45 | 13 | 120 | 4850491 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CUST HAD BROKEN NEUTRAL IN SERVICE DROP WAS BROKEN AT THE POINT WHERE NEUTRAL IS SERVED THROUGH HOUSE KNOB AND ATTACHED TO HOUSE. THIS WAS 2/3 DROP 100AMP METER BASE. SEND COPY TO PEGGY IN DAMAGE CLAIMS CUST COULD POSSIBLY CALL IN. HE DID SAY THE DISPLAY LIGHTS WAS NOT WORKING ON GAS STOVE OVEN.BUT THE BURNNERS WOULD COME ON. AFTER I MADE NEUTAL REPAIRS VOLTAGE OK/EMAILED PEGGY/ADH// VER/ ADH
7461 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-07-16 18:39 | 2008-07-16 19:44 | 24 | 65 | 53403-1 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409302//FUSE OPEN ON 882-52 CHECKING LINE NOW//COD 24//FUSE BROKE// VER/DBM IDC XXXX
7462 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-01-04 15:36 | 2015-01-04 18:51 | 8 | 195 | 4904111 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-5076 BAD CUTOUT BRING 3-CUTOUTS AND LA MARKED POLE RED RIBBON RELEASED BY CREW 078S08/CREW ON SITE/FETR 1930/VEM/B PHASE XFMR ONLY ON ORIG CALL/OPENED BANK FOR REPAIRS 1759/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1851/PLEASE CLOSE TICKET/THANKS/VEM/ORIGNAL CALL 15:36/COD 8// VER/ ADH // ONLY 3 PHASE CUST ON BANK -- L3/HFP XXX
7463 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-05-28 12:15 | 2019-05-28 14:15 | 13 | 120 | 4353381 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | wire has jumped off insulator, re-sagging middle phase. isolating pole is 184-438. opened recloser at 12:15, closed back in at 14:15 L3/HFP
7464 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-11-19 10:01 | 2014-11-19 15:40 | 5 | 339 | 4745501 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE FUSE OPEN AT POLE 1003-91, GUY WIR BROKEN AT POLE 1003-52, ISOLATED TRANSFORMER POLE 52 TO CLEAR GUY AFTER RESTORING MAIN LINE . CUTOUT BAD POLE 78//ARRESTER BAD ON POLE 93//L/F BACK IN AT 1349//3 TRANS STILL OUT93,52 AND 79//POLE 52 CLOSED AT 1405//POLE 93 CLOSED AT 1500//MADE MD ON POLE 92 TO SHOW 15T L/F TOWARDS POLE 93//POLE 79 @ 1540 VER/CRB
7465 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2012-07-09 15:06 | 2012-07-09 16:24 | 20 | 78 | 4648591 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE HAD PULLED LOOSE ON HIGH SIDE OF STEPDOWN, APR AT 1624. CLOSE TICKET. DWEST VER/HFP L3/HFP IDC XXXX
7466 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-03-21 10:52 | 2018-03-21 12:10 | 20 | 78 | 4036571 | 1560 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew opening SW 56-C-147 to change broken cutout foundat pole56-36/1 hr outage//opened at 1117 and closed at 1210
7467 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-07-20 19:14 | 2008-07-21 21:13 | 1 | 1559 | 54465-1 | 1559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE ON FIRE BURNING SECONDARY HAY WAGON BURNT BENEATH PUT OUT BY FIRE DEPT IF LINES BURN DOWN WILL FALL ONTO BARN. SECONDARY DOWN AND TRANSFORMER FUSE OPEN. NEED CREW.ALSO ROLL OF 1/0 SEC. LMR. VER/KEP IDC XXXX
7468 | South Williamson | 3411401 | DEWEY | INEZ | 2008-08-31 07:20 | 2008-08-31 15:21 | 8 | 481 | 57959-1 | 1559 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | VER/HFP LIGHTING ARRESTER BAD ON POLE 861-C2-89. CLOSED 40T FUSE ON POLE 861-C2-88 AT 09:54 STS WR# 26040254 RELEASED BY CREW 079S01 THINK WE HAVE BAD POT HEAD GOING TO REPLACE AND TRY PUT 25TS IN ON POLE 861-C2-89 TO KEEP FROM TAKING MAIN LINE OUT ENTERED MD & SENT EMAIL TO PERRY FARMER, BOB SHURTLEFF, TIM HALL, DENNIS MASSEY, RANDAL MARCUM & DDC STAFF. IDCC CNT2 LINE FUSE IS CORRECT XXXX
7469 | Hazard | 3308502 | BONNYMAN | HAZARD | 2017-10-25 11:34 | 2017-10-25 11:53 | 82 | 19 | 4497261 | 1558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENING RECLOSER TO REPLACE BROKEN STRANDS OF WIRE/ ISO 37830223A10576/ COD 82/ 1134-1153/ VER/BOW L3/HFP XXXHFP ACB
7470 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-06-20 12:58 | 2017-06-20 18:00 | 9 | 302 | 4007341 | 1558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR ON POLE 171C-53 . CLOSED FUSE 37830171000051 BACK @ 15:35 . ALL POWER BACK ON EXCEPT XFMR ON POLE 171C-53 . . NEED 2 MEN WITH BUCKET TO CHANGE XFMR . 15KVA 7200 & CUTOUT , TBRACKET . RELEASED BY CREW 075H04..P.HICKS..CHANGED XFMR, 37830171000053 ALL POWER RESTORED @ 18:00 (1 CUST)/ VER/BOW SJG
7471 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-05-11 18:17 | 2016-05-11 18:58 | 38 | 41 | 4202871 | 1558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4201411*** OPENING LINE FUSE TO CHANGE CUTOUT ON POLE 37820151000075/ ISO 37820151000045/ COD 38//OPENED 1817 CLOSED 1858// VER/ ADH AJB
7472 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-08-11 00:10 | 2009-08-11 00:51 | 38 | 41 | 63681-1 | 1558 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED CUTOUT TO SAFELY ISOLATE A BURNING POLE ON ORDER 63147 VER/KEP L3/KEP IDC XXXX
7473 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-12-16 09:01 | 2016-12-16 17:40 | 3 | 519 | 4200141 | 1557 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ***SEE H4200141*** ONE BAD SECONDARY UNDERGROUND LEG, SIZE OF COND IS 350. CREW REQUIRED/ ONLY 3 CUSTOMERS AFFECTED WITH PART POWER 38830478C20582 ORIGINALLY/ OPENED 38830478C20577 (2 CUST ADD.) @ 1441 TO MOVE CONDUCTOR CLOSED @ 1503 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD) @ 1531 TO DO SOME CONNECTIONS CLOSED @ 1543 (REST. 2 CUST)/ OPENED 478-577 (2 CUST. ADD.) @ 1722 TO FINISH WORK CLOSED @ 1740 (REST. ALL 5 CUST)/ VER/BOW
7474 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-04-05 23:02 | 2009-04-06 12:00 | 2 | 778 | 65573-1 | 1556 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1099-118 BAD 15KVA NEED 25KVA TRUCK OK RELEASED BY CREW 078S08----CREW ON SITE//3000902//VER/CRB IDC XXXX
7475 | Hazard | 3303903 | LESLIE | HALSFORK | 2020-12-26 14:27 | 2020-12-27 16:22 | 1 | 1555 | 4825071 | 1555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | customer called saying they have no power, bad xfmr 25 kva 7200 truck acess Released by crew 077S07. Same as 4826201. power restored can close mwl
7476 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2019-05-02 19:56 | 2019-05-03 01:07 | 5 | 311 | 4203241 | 1555 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke 38820771A40221 checking now..//MADE MD TO SHOW MIS-MAPPED CUST// L3/HFP
7477 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-26 18:27 | 2009-09-26 22:09 | 7 | 222 | 64475-1 | 1554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE IS OUT ON POLE1081-17. I HAVE PATROLLED LINE. I AM GOING TO REFUSE LINE FUSE. LIGHTENING ARRESTER ON POLE 1081-93 WAS BAD. WE CLEARED IT UP AND CLOSED LINE FUSE IN AT 22:09.
7478 | Hazard | 3302704 | HAZARD | KENMONT | 2010-06-20 22:04 | 2010-06-20 23:55 | 14 | 111 | 51925-1 | 1554 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3302704/ ONE HOT LEG ON TRANSF BURNED OFF == REPAIRED == POWER OK IDC XXXX
7479 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-10-24 14:25 | 2017-10-24 18:44 | 6 | 259 | 4493591 | 1554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT ON 38830621000087 AND INSULATORS THROUGHOUT HILLSIDE. TRYING FUSE ON 38830621C40226 VER/AWD L3/HFP XXXHFP ACB
7480 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-04-12 11:33 | 2016-04-12 12:15 | 37 | 42 | 4084891 | 1554 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE AND TIE IN CONDUCTOR ON POLE 37830505000026/ ISO 37830505000003/ COD 37 REPLACED BAD POLE AND RESTORED POWER AT 1215 , OPENED OCR AT 1133/ VER/BOW AJB
7481 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2012-08-04 10:56 | 2012-08-04 14:10 | 8 | 194 | 4895671 | 1552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 45-4693 BAD LA POLE 45-4689 30T//COD 8// VER/DBM IDC XXXX
7482 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-08-08 08:06 | 2014-08-08 11:20 | 8 | 194 | 4341421 | 1552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FOUND BAD DEADEND PRI BELL INSULATOR BAD, CREW REQ, CAN USE TRUCK, NEED TO REPLACE INS RELEASED BY CREW 078S06 COD 8// VER/ ADH
7483 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-05-11 11:02 | 2009-05-11 17:30 | 4 | 388 | 59784-1 | 1552 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3301701 THIS FUSE WAS OPENED FOR SERVICER REQUEST/THIS IS FOR A GAS WELL AND THE CUST CALLED THE SERVICER
7484 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-06-10 02:51 | 2012-06-10 07:42 | 7 | 291 | 4897211 | 1551 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE OPEN ON POLE 37830247D00823, TRANSFORMER FUSE OPEN ON POLE 37830247D00864===LINE FUSE RESTORED AT 0500, BAD TRANSFORMER ON POLE 37830247D00864, 4 CUST. STILL OUT.- NEED 2 MEN,19.9- 25 KVA, AND MATERIAL HANDLER.== ALL POWER RESTORED AT 0742. // VER/TOM L3/TOM IDC XXXX
7485 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2016-06-27 16:26 | 2016-06-27 17:16 | 31 | 50 | H4486771 | 1550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPEN RECLOSER @ 280-62 @ 1626,PRIMARY DOWN @ 280-78 ,BAD ARESTER @ 280-179 RECLOSER IN @ 1716 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT//MADE AED/ADH// VER/ ADH
7486 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-02-05 11:19 | 2009-02-05 12:09 | 31 | 50 | H1115361-1 | 1550 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE. ISOLATE ON POLE 47-32. ON AT 08:00AM RELEASED BY CREW 074S05 REPLACE C/O AND ARRESTOR ON 155 ON AT 12:09 COMPLETE D SAMMONS OPENED FUSE 47-31 @ 1119, CLOSED BACK @1209 //VER/GAH AJB
7487 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-05-03 14:05 | 2021-05-03 20:04 | 18 | 359 | 4516721 | 1549 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout @ pole 38830140C05512/isolating @ pole 38830140D07004/possibly get truck to pole need mopads but cust doesnt know where septic tank is. crew reqd. line fuse back in @ 15:15 ///Released by crew 078S04///complete BR
7488 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-12-09 07:40 | 2013-12-09 11:58 | 6 | 258 | 4131321 | 1548 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-2015 40/4 PRI. POLE BURNT OFF NEED POLE CUTOUT TRANS. CAN TRANSFER RELEASED BY CREW 078S08//UPPED 10 T TO 25T MADE MDC// VER/CRB L3/HFP
7489 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2017-03-26 17:33 | 2017-03-26 22:42 | 5 | 309 | 4586281 | 1545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE BAD CUTOUT ON POLE 37830072A00311. WILL NEED 1 8FT XARM ,2- 7200 CUTOUTS ,MATERIAL HANDLER & 2 MEN. PULLED OFF ON POLE 37830072A00142 @19:15 BACK ON @ 22:42//VER/ADH
7490 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-12-06 09:36 | 2016-12-06 11:19 | 15 | 103 | 4169281 | 1545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED A BAD TRANSFORMER CUTOUT AT POLE 38821114A00083. ALL POWER RESTORED AT 11:19. VER/CRB L3/HFP XXXHFP
7491 | South Williamson | 3200302 | BELFRY | TOLER | 2022-09-05 14:55 | 2022-09-05 23:30 | 3 | 515 | 4840541 | 1545 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FAULT POLE 38820966D00654//ENROUTE TO GET CREW//GOING TO TRY AND ISOLATE AT SWITCHES 38820966D00027 THIS WILL OUT 3- 3 PHASE CUSTOMERS//opened at 1455 at pole 38820966D00027 // closed at 2330 //
7492 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2021-02-26 04:41 | 2021-02-26 11:07 | 4 | 386 | 4253481 | 1544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout GuidelinesFuse is open at 188-C-152(LOOKING IT OVER)..Fuse is open at 188-C-152(LOOKING IT OVER)..The fuse had broke changed it out and restored at 11:07.../// ISO 37830188C00152/ COD 4
7493 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-07-14 15:34 | 2013-07-14 22:00 | 4 | 386 | 4522311 | 1544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN ON 297-15 TO 14 PRIMARY ONLY #2 ALUM. UP ON HILL AT SKAGGS TAXIDERMY/TRUCK OK SMALL SERVICE BUCKET /12T LINE FUSE // REYNOLDS, CANTRELL, & STONE & MORGAN VER./PDP IDC XXXX
7494 | Hazard | 3303902 | LESLIE | WOOTON | 2013-01-16 07:27 | 2013-01-16 09:39 | 12 | 132 | 4610061 | 1544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ 486-180 ///VER/CRB L/3 CRB ID XXXX
7495 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2009-01-17 00:04 | 2009-01-17 06:30 | 4 | 386 | 56520-1 | 1544 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3403201//BAD 15KVA TRANSFORMER ON POLE 141-38. CALLED WILLIE HE IS GOING TO GET CREW HEADED THIS WAY. WE HAVE NEW 25KVA INSTALLED EVERYTHING OK. L3/HFP MD FILED L3/KEP
7496 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-08-30 15:25 | 2011-08-30 19:42 | 6 | 257 | 4776011 | 1542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFR FUSE OUT,WILL RE-FUSELINE FUSE OUT,WILL RE-FUSE,POLE 95-19,APPEARS TO BE "B" PHASE COD-6//FUSE CAME BACK OUT,MAY NEED TREE CREW TO CUT SOME /// CUTOUT OR ARRESTER BAD ON 37830095000209// INACTIVE XFMR NEEDS REMOVED //WILL HAVE ENG. WRITE A JOB TO REMOVE ALL// ALSO R/W NEEDS CUT VERY BAD// REFUSED // POWER IS RESTOR VER/KEP IDC XXXX
7497 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2018-05-19 16:43 | 2018-05-20 01:17 | 3 | 514 | 4378521 | 1542 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50kva 7200 transformer on pole 38830067D00302, cutout also burnt up, No trucks to pole. six wheeler or track machine access from 417 greenhill rd. Released by crew 078H04---crew on site---changed 50kva--pwr restored at 01:17---tbl tkt comp Released by crew 078H16
7498 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-09-05 12:33 | 2013-09-05 15:07 | 10 | 154 | 4822381 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 6/A NEUTRAL BROKE IN 3 SPANS POLE 37830042C00420 IS THE FIRST POLE TO WORK. 271,272, 319 WILL BE WORKED AS WELL. REMOVE ARMS AND REPLACE WITH POLE TOP PINS. OFF AT 12:33 ON AT 15:07 TIM MCCOY VER/CRB L/3 CRB IDC XXXX
7499 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2010-10-31 07:35 | 2010-10-31 08:45 | 22 | 70 | 50379-1 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WR 37558027 //PRI LOOP BURNT OPEN // COD-22 ENTERED MD...HFP PRI LOOP BURNT OPEN ON POLE 1147-5012 INSTALLED 30T LINE FUSE ON POLE VER/HFP L3/HFP IDC XXXX
7500 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2019-01-25 14:55 | 2019-01-25 16:45 | 14 | 110 | 4722581 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp burned off underswung switch on pole 356-89. I replaced the riser and clamp L3/HFP
7501 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-11-26 11:02 | 2008-11-26 14:42 | 7 | 220 | 52457-1 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-7 CREW REQUIRED BAD 25 KVA NO TRUCKS CONTACTED MCCARTY RELEASED BY CREW 078S03 IDC XXXX
7502 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-04-24 19:25 | 2011-04-24 21:45 | 11 | 140 | 63795-1 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRIX CONDUCTOR BROKE AT SPACER AND IS HANGING DOWN ON SIDEWALK. BLOCKED AREA OFF AND CALLED DUTY SUPERVISOR FOR CREW. CREW ENROUTE. OPENED THREE SWITCHES ON 954-641 TO ISOLATE @ 19:25. REPAIRS COMPLETE. REMOVING GROUNDS. CLOSED SW ON 954-641 @ 21:45. SH RELEASED BY CREW 076S02 //VER/GAH IDC XXXX
7503 | South Williamson | 3411401 | DEWEY | INEZ | 2009-11-14 12:16 | 2009-11-14 14:50 | 10 | 154 | 57067-1 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | JRV ON SITE @ 13:33....BROKEN SURGE ARRESTER ON 34.5 KV WYE-DELTA XFRMR BANK ON POLE 744-A2-57...ALL 3 FUSES BLOWN ON BANK.....WILL CLEAR ARRESTER & RE-FUSE XFRMERS .....//....CLEARED BROKEN ARRESTER....RE-FUSED XFRMR BANK...POWER RESTORED....JRV....11/14/09 /// VER/TOM L3/TOM IDCC PN NULL XXXX
7504 | Pikeville | 3403001 | PIKEVILLE | CITY | 2021-01-18 06:50 | 2021-01-18 09:24 | 10 | 154 | 4874491 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. fuse open @24-D2-429, checking. Trans. cutout busted here, will be changing. Got cutout replaced and power restored @0924.
7505 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-04-15 03:44 | 2021-04-15 10:09 | 4 | 385 | 4452281 | 1540 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.Line fuse open @ 214-B-93(ASSESSING CONDITION)..Line fuse open @ 214-B-93(ASSESSING CONDITION)..We have a broke cutout on 214-B-346,Going to get it changed out ..Line fuse open @ 214-B-93(ASSESSING CONDITION)..We have a broke cutout on 214-B-346,Going to get it changed out ..Restored service at 10:09.
7506 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-03-04 03:28 | 2016-03-04 12:00 | 3 | 512 | 4813471 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 CUTOUT RESTORED 1200 ISO 38830117B00371 COD 3 VER/AWD
7507 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-12-07 12:22 | 2015-12-07 13:10 | 32 | 48 | 4515921 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO 4514991 - SERVICER OPENED RECLOSER TO ALLOW HIM TO SAFELY REPAIR LOOP THAT IS BURNT OPEN /// COD-31 ISO OCR 37830311000151 OPENED @ 1222 CLOSED @ 1310 VER/HFP L3/HFP AJB
7508 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2008-02-13 14:01 | 2008-02-13 14:33 | 48 | 32 | 62536-1 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200204//, ON SITE, POLETOP BURNT OFF AT XFORMER, CALLED CREW FOR HELP//OPENED FUSE @ 1400 TO SAFELY CHANGE POLE//COD48//, ON SITE, POLETOP BURNT OFF AT XFORMER, CALLED CREW FOR HELP, POLE# 1016-D-250, 50T FUSE, OFF AT 1401, BACK ON AT 1433// VER/DBM IDCC PN61 XXXX
7509 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2014-09-20 07:52 | 2014-09-20 08:40 | 32 | 48 | 4513001 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 38830045D26639 NEEDS NEW BASKET INSTALLED ON #6 CU. PRI. , SCREW ON BSKT. TEMP. INSTALLED VER/KEP L3/HFP AJB
7510 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-12-11 21:19 | 2010-12-11 23:58 | 28 | 159 | 65426-1 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR 38077062 // POLE 92-405 PRI TAP BROKE ON CUTOUT SEND TO BILL RELEASED BY CREW 078S08 // AED CREATED AND NOTE PLACED ON MAP VER/TOM IDC XXXX
7511 | Pikeville | 3421001 | BREAKS | CITY | 2011-03-18 12:12 | 2011-03-18 14:20 | 12 | 128 | 55461-1 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW CHANGING POLE THAT IS BURNT//COD 12// VER/DBM IDC XXXX
7512 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-09-09 05:21 | 2021-09-09 11:45 | 4 | 384 | 4224471 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | hot line clamp has burnt up for the xfmr cutout on pole 38830118B00096. not by truck Released by crew 078S12
7513 | Hazard | 3309301 | VICCO | REDFOX | 2009-05-16 23:56 | 2009-05-17 12:44 | 2 | 768 | 59945-1 | 1536 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTENING ARRESTOR BAD ON CREEK SIDE PHASE. WILL TAKE BIG BUCKET. CREW NEEDED RELEASED BY CREW 077S08//VER/CRB IDC XXXX
7514 | Hazard | 3312201 | ENGLE | INDUSTRIAL PARK | 2012-01-02 14:47 | 2012-01-02 19:54 | 5 | 307 | 4225721 | 1535 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | ROADS HAVE BLACK ICE ON MAIN 4 LANES. AND VEHICLE ACCIDENTS WILL DELAY RESTORATION EFFORTS.BAD PRIMARY METERING 150KVA CENTER PHASE,,,,BY PASSED METERING AS PER MIKE LASSLO.WILL CHANGE AT LATER DATE.POWER RESTORED @ 19:54 HRS // COD 6// VER/DBM IDC XXXX
7515 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-03-26 16:44 | 2008-03-26 18:42 | 13 | 118 | 60952-1 | 1534 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3116102//REPLACING/ FUSE20T//COD 13// VER/DBM IDC XXXX
7516 | Pikeville | 3421001 | BREAKS | CITY | 2018-01-23 04:26 | 2018-01-23 08:05 | 7 | 219 | 4764481 | 1533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke here @ pole#243-230 on center phase// will have to open other two fuses up to change bad cutout/ Opened other 2 phases @07:40/ Changed bad cutout and closed all 3 phases 0805/ ISO 37820243D00230/ COD 7/ no customers on b&C A phase has 4 and 3phase 3 7 were all out originally L3/HFP
7517 | Hazard | 3310502 | HADDIX | CANOE | 2011-05-26 07:59 | 2011-05-26 16:30 | 3 | 511 | 4171541 | 1533 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LOOP BURNT INTO--3 TR---144-13-HAS BAD 6 IN DISK-HELP ON THE WAY-FETR 1600--THIS WAS WHAT TOOK MAIN LINE OUT 2 TIMES LAST 24 HOURS- VER/KEP
7518 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-12-10 04:37 | 2015-12-10 08:52 | 6 | 255 | 4522121 | 1530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK ACCORDING TO AFTER HOURS GUIDELINE FUSE LINK APPEARS TO HAVE BROKE. RESTORED @ 8:52. SH// VER/ ADH AJB
7519 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-08-10 15:24 | 2015-08-10 16:15 | 30 | 51 | 4118001 | 1530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | B PHASE REC. NEEDS NEW BASKET INSTALLED. #2 AL. PRI./COD 30/EMAILED RAYBURN/ADH// VER/ ADH L3/HFP XXXHFP AJB
7520 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-05-18 08:49 | 2011-05-18 13:55 | 5 | 306 | 4107721 | 1530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 245-293 BURNED OFF BAD CUTOUT TOOK CLAMP OFF OF POLE 245-81 AT 0849, GOT CREW COMMING TO CHANGE POLE OUT///REPLACE 40C4 POLE ,RIDGE PIN INSULATOR , CUTOUT ARRESTER, 2 CLEVIS, TRANSFER TRANSFORMER AN GUY AND LIGHT. VER/KEP IDCC TOF0710, PN82 XXXX
7521 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-11-16 00:25 | 2018-11-16 13:10 | 2 | 765 | 4434211 | 1530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 246-262, burnt top of pole off can lower, isolated on pole 246-27 not grounded, truck acess, need 7200 cutout arr t bracket Released by crew 077H14 L3/HFP
7522 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-09-22 17:24 | 2010-09-22 22:30 | 5 | 306 | 52282-1 | 1530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830385000148, POLE BURNT IN TWO. 40/4. ISOLATED ON POLE 385-26, TOOK CLAMP OFF, TIME 17:24. NEED CREW AND R/W CREW//// POLE REPLACED, POWER RESTORED//COD 5//ISO// VER/DBM IDCC TOF1625 XXXX
7523 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2012-06-08 13:24 | 2012-06-08 17:39 | 6 | 255 | 4894251 | 1530 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100KVA TRANS. TRUCK TO POLE HOLD FOR VERNON M. CREW RELEASED BY CREW 078S08/FETR 1745/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1739/PLEASE CLOSE TICKET/THANKS/VEM COD-6 ISO TF 38830045C24511 VER/HFP L3/HFP IDC XXXX
7524 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-09-20 00:17 | 2017-09-20 01:42 | 18 | 85 | 4374771 | 1530 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BURNT UP SECONDARY CONNECTION COMPLETE,,ONLY 1 CUSTOMER PART POWER ACBC CCU
7525 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-03-29 13:18 | 2014-03-29 18:17 | 16 | 299 | 4533981 | 1529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW REQUIRED NO TRUCKS 295-16 DEADEND BELL BACK WIRE DOWN ACROSS ROAD ISOLATED ON 296-16/POLE 295-1 BACK IN AT 1440 HRS 1 CUSTOMER STILL OFF RELEASED BY CREW 078S03/CREW ON SITE/FETR1830/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1817/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB IDC XXXX
7526 | Hazard | 3309301 | VICCO | REDFOX | 2020-01-10 11:35 | 2020-01-10 13:54 | 11 | 139 | 4230571 | 1529 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | recloser out on pole 325-280, lights are bouncing back and forth between closed and open, contacted J Holliday, hes on his way to re-program controls. recloser back in at 13;54
7527 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2009-10-15 18:04 | 2009-10-15 21:15 | 8 | 191 | 50205-1 | 1528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O ON XFMER POLE. WILL REPLACE. P.HICKS................ALL POWER RESTORED P.HICKS 21:15HRS//VER/CRB IDC XXXX
7528 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2011-05-22 10:48 | 2011-05-22 17:10 | 4 | 382 | 4121641 | 1528 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CUSTOMER GETTING 120 VOLTS TO METER. UG SERVICE. DUTY SUPERVISOR ENROUTE TO ASSIST IN LOCATING UG JCT. BOX. UG CABLE HAS ONE HOT LEG OPEN BETWEEN XFMR 785-228 AND JCT BOX 785-896. MEAN DOGS IN YARD WHERE XFMR IS LOCATED - TRYING TO REACH CUST AS NO ONE IS HOME TO PUT THEM UP. ALSO TRYING TO LOCATE AUTO XFMR FOR TEMP. INSTALLED TEMP OVERHEAD FROM 38830785C20828. RESTORED @ 17:10. SH VER/ARN IDC XXXX
7529 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-07-18 08:01 | 2017-07-18 16:30 | 3 | 509 | 4136311 | 1527 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | THIS IS A 120-240 BANK, NOT A 480. POLE 247-151, BAD 10KVA 7200 TRANSFORMER, AND THREE CRACKED CUTOUTS. CAN GET TRUCK IN BACK YARD. SIDE YARD HAS SEPTIC SYSTEM. RELEASED BY CREW 078H04/POWER RESTORED AT 16:30, CUTOUTS & ARRESTORES REPLACED,/ TWO PHASES OPEN (2-3 PHASE CUST) ONE PHASE STILL ON (1 SINGLE PHASE CUST)/ OENED OTHER PHASE AT ______??? (1 ADD CUT)/ ISO 38830247000151/ COD 3*** PER SERVICER 1 CUSTROMER NOT SHOWN ON MAP MD DONE/ DUPLICATE IN HOIS
7530 | South Williamson | 3411401 | DEWEY | INEZ | 2012-09-26 05:12 | 2012-09-26 10:27 | 9 | 315 | 4087881 | 1526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 792-130 BURNT OFF DUE TO CUTOUT FAILURE///CUT LOOP ON POLE 792-128 TO ISOLATE//REFUSED LATERAL ON 792-11 AT 7:20 TO PARTIAL RESTORE /CREW ON SITE//REPAIRS MADE//AL RESTORED AT 10:27//COMPLETE//EM RELEASED BY CREW 079S01 COD-9 ISO LF 38830792C00011 VER/HFP L3/HFP IDC XXXX
7531 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-01-05 13:41 | 2008-01-05 17:19 | 7 | 218 | 54046-1 | 1526 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601// PATROLING LINE/ CALLING CREW/ P TOLLIVER TO WORK RELEASED BY CREW 078S07// BAD CUT OUT WILL HAVE TO BE REPLACED//// VER/TOM IDC XXXX
7532 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-12-21 09:40 | 2012-12-21 14:45 | 5 | 305 | 4499161 | 1525 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WIRE IN TWO ON SEC //VER/GAH
7533 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-06-26 18:50 | 2008-06-27 03:18 | 3 | 508 | 55308-1 | 1524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 7200 XFMR AND ARRESTER ON POLE 38830184A00331 BESIDE BARN ON BACK OF PROPERTY, TRUCK OK RELEASED BY CREW 078S05/ VERY MUDDY & SLICK VER/HFP IDCC CNT1 XXXX
7534 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-09-24 18:56 | 2011-09-25 01:17 | 4 | 381 | 4912701 | 1524 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/VEM/ORIGINAL CALL 4 CUST PART POWER/OPEN XFMR 1148-650 AT 2347 TO ISOLATE BAD UG/XFMR BACK IN AT 0019/ 4 CUST OUT FOR REPAIRS/REPAIRS MADE AND POWER RESTORED TO 4 CUST AT 0117/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
7535 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-06-21 16:47 | 2011-06-22 18:10 | 1 | 1523 | 4365421 | 1523 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE OF 3 XFMR FUSES BLOWN ON BANK.BAD XFMR..CREW REQUIRED, 19.9 KV, 25KVA, 120-240, 2 BUSHING.CALLED DAVE SAMMOMS.WAITING TO SEE WHAT THIS NEXT STORM DOES.WILL PROB WORK 1ST THING IN AM OF 06/22/11..JRV RELEASED BY CREW 080S01// VER/DBM IDC XXXX
7536 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-02-13 09:03 | 2014-02-14 10:25 | 1 | 1522 | 4379811 | 1522 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | TRANSFORMER LEAD BURNED OFF AT PL#304C2-177; REPAIRS MADE - CAN CLOSE TICKET MWL VER/HFP L3/HFP
7537 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-06-17 21:13 | 2012-06-17 23:45 | 10 | 152 | 4924411 | 1520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERV CHECKING LINE.FOUND BAD CUT OUT SERV TO FIX.ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/TOM L3/TOM IDC XXXX
7538 | Whitesburg | 3314401 | MAYKING | ERMINE | 2018-04-05 15:56 | 2018-04-05 21:00 | 5 | 304 | 4193091 | 1520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ON HOUSE//37830450A00048//NEED A LINE TRUCK TO REMOVE//CALLED CUST//pole rotten and fell on house.. cut service down on pole 450A-54 to make safe. pole 450A-152 needs replaced Released by crew 077H21POLE ON HOUSE//37830450A00048//NEED A LINE TRUCK TO REMOVE//CALLED CUST//pole rotten and fell on house.. cut service down on pole 450A-54 to make safe. pole 450A-152 needs replaced .. repairs made.. open transformer @ 20:45 closed @ 21:00//can close mwl
7539 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2010-06-06 15:31 | 2010-06-06 20:35 | 5 | 304 | 57841-1 | 1520 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFMR. DUTY SUP NOTIFIED - CREW TO COME AND CHANGE AS SOON AS THEY FINISH @ W LIBERTY. RELEASED BY CREW 076S02BAD 50KVA XFMR. DUTY SUP NOTIFIED - CREW TO COME AND CHANGE AS SOON AS THEY FINISH @ W LIBERTY. ENROUTE.BAD 50KVA XFMR. DUTY SUP NOTIFIED - CREW TO COME AND CHANGE AS SOON AS THEY FINISH @ W LIBERTY. ENROUTE. WORKING TO REPLACE XFMR. REPAIRS COMPLETE. RESTORED @ 20:35. SH//VER/CRB IDC XXXX
7540 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-01-11 11:47 | 2021-01-11 18:13 | 5 | 386 | 4861301 | 1518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG @ 1148-b3-650, 350 Ug, Both sides of apartments showing bad neutral, but checks good @ transformer. Opened transformer 1148-650 @ 13:30 Released by crew 078S02/on site RM repairs made power on @ 18:13 pleaseclose tic RM
7541 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-07-06 11:37 | 2018-07-06 15:50 | 6 | 253 | 4737101 | 1518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Found bad arrester on 669-10, apr at 1550 close ticket
7542 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2008-10-25 11:47 | 2008-10-25 12:10 | 66 | 23 | 58939-1 | 1518 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW HAD TO OPEN RECLOSER TO ALLOW THEM TO REPLACE A DEFECTIVE SWITCH ON POLE 38830285000020 IDC XXXX
7543 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2021-03-18 18:37 | 2021-03-19 17:25 | 7 | 1368 | 4349651 | 1517 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | DOL 1100232 // will work on tomorrow per v.mullins/bad potheads/cable tests good/crews making repairs/FETR1730/vem/repairs and all customers restored 1725/please close ticket/thanks/vem
7544 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-07-04 23:52 | 2013-07-05 12:30 | 2 | 758 | 4467271 | 1516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA NO TRUCK TO POLE YARD MAC. OR TRUCK PADS RELEASED BY CREW 078S08 VER/SEF IDC XXXX
7545 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-02-02 12:32 | 2009-02-03 13:48 | 1 | 1516 | 54643-1 | 1516 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED SERVICE COMPLETE JXM VER/KEP L3/KEP
7546 | Hazard | 3310502 | HADDIX | CANOE | 2011-10-18 13:50 | 2011-10-19 15:05 | 1 | 1515 | 4994811 | 1515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER--LEANING POLE RELEASED BY CREW 077S10//ROW TOO BAD TO FINISH TONITE//WILL FINISH CUTTING AND CHANGE TRANSFORMER IN THE AM//COD 1//REPAIRED 1505// VER/DBM IDC XXXX
7547 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-04-20 01:38 | 2020-04-20 10:03 | 3 | 505 | 4721291 | 1515 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.---broke c/o-crew req-ds042020 Released by crew 078S01//on site RM power on at 10:03 please close tic RM
7548 | Pikeville | 3408103 | SALISBURY | MARTIN | 2014-10-16 07:37 | 2014-10-16 09:25 | 14 | 108 | 4636101 | 1512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AT POLE 1098-441, WILL ISOLATE 3 PHASE UG TAP AND 1 PHASE LAT AT POLE 441 TO REPAIR . OPENED ALL LATERAL CUTOUTS AT POLE 441 AT 08:45 AND REPLACED CUTOUT . CLOSED ALL CUTOUTS AT POLE 441 AT 09:10, CLOSED C PHASE AT POLE 302 AT 09:25 , ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03// FIX IT IN HOIS// VER/DKG L3/DKG DKGXXXX OUTAGE CAN STAND AS IS SINCE NO CUSTOMERS WERE ACTUALLY RESTORED UNTIL C PHASE WAS CLOSED ON POLE 302
7549 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-03-10 08:18 | 2010-03-10 09:30 | 21 | 72 | 64517-1 | 1512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34193530 //NO CREW REQUIRED CALLED FOR 3346 TO ASSIST VER/HFP L3/HFP IDCC PN37 XXXX
7550 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-10-23 17:58 | 2009-10-23 18:40 | 36 | 42 | 50405-1 | 1512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-6777 PRI BURNT OFF BOTTOM OF CUTOUT REPAIRED 50T LINE FUSE ALSO 3-65T FEEDING TOWARD 29TH. ST. ON SAME POLE IDCC PN1099 XXXX
7551 | Whitesburg | 3312901 | JENKINS | KONA | 2013-02-04 23:30 | 2013-02-04 23:54 | 63 | 24 | 4791611 | 1512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED RECLOSER AT 2330 TO ALLOW HIM TO SAFELY REPLACE FAILED CUTOUT IN ORDER 4791601 /// COD-63 ISO OCR 37830403C00284 VER/HFP L3/HFP IDCC CNT65 2 CUSTOMERS INITIALLY OUT XXXX
7552 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-01-29 14:35 | 2011-01-29 15:59 | 18 | 84 | 52014-1 | 1512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE--BAD ARRESTOR NEEDS REPLACED--NO TRUCK // CREATED AED//VER/CRB IDC XXXX
7553 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2012-02-11 14:36 | 2012-02-11 15:48 | 21 | 72 | 4335691 | 1512 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED HOT TAP///VER/CRB IDC XXXX
7554 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2014-06-24 21:51 | 2014-06-25 00:22 | 10 | 151 | 4150941 | 1510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE ON POLE #24-A-1582 AND IT TOOK OUT THE LINE FUSE ON POLE#24-B-1 //// I GOT TIM MCCOY COMING WITH BIG BUCKET TO CHANGE CUT-OUT RELEASED BY CREW 074H17//// CHANGED BAD CUT OUTS AND RESTORED POWER AT 00:22 TIM MCCOY RELEASED BY CREW 074H10 VER/KEP
7555 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-06-24 17:29 | 2019-06-24 20:00 | 10 | 151 | 4577331 | 1510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 30t fuse out due to bad arrester. made repairs everything rest of line looked to be good. closed 30t fuse at 20:00 everything ok
7556 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-05-16 12:55 | 2009-05-17 01:30 | 2 | 755 | 58503-1 | 1510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED A CREW, HAVE A BAD 25 KVA, CAN USE TRUCK, RIGHT BESIDE OF ROAD JUST BEHIND GREENHOUSE, ON LEFT RELEASED BY CREW 078S06 RELEASED BY CREW 078S10 VER/KEP L3/KEP IDC XXXX
7557 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-06-10 08:50 | 2008-06-11 10:00 | 1 | 1510 | 61386-1 | 1510 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3404302//ON SITE, XFORMER FUSE BLOWN, REFUSING IT, BAD XFORMER//SERVES ONLY A CAUTION LIGHT//CREWS MIGHT NOT GET THIS UNTIL TOMORROW MORNING PER R MARCUM//FLAGGERS NEEDED// L3/DKG IDC XXXX
7558 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2019-04-23 21:47 | 2019-04-23 22:45 | 26 | 58 | 4151921 | 1508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20t restored @ 90-69. bad co door @ 22:45 L3/HFP
7559 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-11-18 08:12 | 2010-11-18 10:48 | 11 | 156 | 57767-1 | 1508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3 LINE FUSES NOT ON MAP ON 785-967 (FEEDS 3 PHASE LATTERAL TOWARD 785-994). PHASE C IS BLOWN AFFECTING 11 CUSTOMERS. PATROLLING. FOUND THREE BLOWN ARRESTERS ON XFMR BANK. ISOLATING BANK. CLOSED LINE FUSE @ 9:56 RESTORING ALL BUT XFMR BANK 785-1086 - REPLACING ARRESTERS. REPAIRS COMPLETE. RESTORED REMAINING CUSTOMERS @ 10:48. SH//COD 11//MD FILED//ISO 38830785A40967// VER/DBM IDC XXXX
7560 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-12-15 08:39 | 2016-12-15 10:35 | 13 | 116 | 4195831 | 1508 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , I CHANGED IT OUT VER/CRB L3/HFP XXXHFP
7561 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-06-15 17:59 | 2016-06-15 20:16 | 11 | 137 | 4355071 | 1507 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP FAILED LETTING HOT LINE CLAMP LOSE CONNECTION AND FAL IN THE CLEAR WILL TRY TO REPLACE STIRRUP AND REATTACH HOT LINE CLAMP REPLACED STIRRUP ON 1077-D-93 RESTORED POWER AT 20:16 VER/CRB
7562 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-09-15 | 2009-09-15 04:11 | 6 | 251 | 56984-1 | 1506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR/ 31718760 BAD PRI. UNDERGROUND SEND TO VERNON RELEASED BY CREW 078S08/CREW ON SITE/TESTING CABLE/FETR0700/VEM/ISOLATED BAD CABLE AND RESTORED TWO CUST 0411/HAD CABLE PLACED IN ABNORMAL AND COPY TICKET TO D.HUFF FOR NEW RIVER REPAIR/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/ARN IDCC PN3713, CNT2, CDC83 XXXX
7563 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-05-27 16:19 | 2014-05-27 20:30 | 6 | 251 | 4936781 | 1506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE IS OPEN ON 38830454D26573 COD-6/ PATROLLING LINE PLEASE HAVE FUSE ADDED TO MAPS 15T ON38830454D26573 & PLACE ARRESTERS 454D275 & 76 IN ABNORMAL DB ARRESTERS WERE CUT IN THE CLEAR APR AT 2030/ MD FILED FOR CUSTOMER AND FUSE/ VER/KEP IDC XXXX
7564 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-02-17 15:01 | 2015-02-17 23:23 | 3 | 502 | 4036961 | 1506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CREW REQUIRED TRUCKS OK 6A PRIMARY AND NEUTRAL NEEDS RESAGGED ON38830292B00120 LINE FUSE OPEN ON 38830292B00092 /TAGGED TO REYNOLDS RELEASED BY CREW 078S03/ MD DONE//MADE AED ON TRANS POLES 38830292B00118,38830316000001,AND 38830316000002 THEY CUT THE ARRESTORS IN CLEAR//THIS L/F IS BETWEEN POLE 92 ANSD 117 VER/CRB L3/HFP XXX
7565 | Paintsville | 3401802 | INDEX | HOSPITAL | 2012-03-30 09:42 | 2012-03-30 14:45 | 12 | 303 | 4633701 | 1506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA CSP TRANSFORMER.BAD.ON POLE 655-266..BLEW LINE FUSE..ON 655-18. RELEASED BY CREW 076S01// CREW ON SITE STARTING REPAIRS TCM// POT CHANGED OUT BACK ON AT 14:45 TCM// //COD 12// VER/DBM IDC XXXX
7566 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-07-20 10:04 | 2010-07-20 14:15 | 6 | 251 | 53715-1 | 1506 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE////////////XFR IS BAD,WILL BE REPLCING IT,CREW HAS BEEN ADVISED.SEND TICKET TO DALE HAMILTON RELEASED BY CREW 074S06 RELEASED BY CREW 074H03 VER/KEP L3/KEP IDC XXXX
7567 | Hazard | 3310502 | HADDIX | CANOE | 2014-02-05 16:47 | 2014-02-05 21:48 | 5 | 301 | 4359491 | 1505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 19.9 TRANSFORMER, CALL TIM SMITH AND HE IS SENDING TWO MEN TO HELP CHANGE OUT VER/CRB
7568 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2013-02-02 20:42 | 2013-02-02 20:49 | 215 | 7 | 4786711 | 1505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRIMARY TAP CUTOUT FAILED, AND BURNED POLE TOP OFF. RELEASED BY CREW 079H06 RELEASED BY CREW 079H07 VER/KEP IDC XXXX
7569 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2013-02-12 04:37 | 2013-02-12 09:38 | 5 | 301 | H4812071 | 1505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 COPPER PRIMARY PULLED OUT OF SLEEVE ON POLE 38830069B28059 56 CC. NEED THREE MAM PRC CREW--TRUCK TO POLE--WILL NEED FLAGGERS--OPENED LINE FUSE AN INSTALLED TAG FOR DDC ON POLE 38830069B28022 AT 04:37 5 CC. 0724 GAVE RON VIRGIN PERMISSION TO REMOVE DDC TAG AND INSTALL TAG FOR HIS SELF. RESTORED 65T LF @ 08:15//BAD 25KVA XFMR ON PL. 69-8059///REPLACED XFMR BACK ON @ 09:38///VOLT CK OK VER/KEP IDC XXXX
7570 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-10-28 09:20 | 2011-10-28 14:21 | 5 | 301 | 4029511 | 1505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PART POWER// CHECKING// BAD 25 KVA// ONLY GETTING 45 VOLTS ON ONE SIDE AT THE XFMR//CALLED T. HALL AND HE IS GETTING A CREW ROUNDED UP// NO TRUCK APP. RELEASED BY CREW 074H14.HAD ///VER/CRB IDCC PN7 XXXX
7571 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-02-02 19:52 | 2014-02-03 00:53 | 5 | 301 | 4338711 | 1505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | PRIMARY HAS PULLED OUT OF A SLEVE AT POLE 38821084A00010, AND IS HOT UP TO THIS POLE. ONLY ONE SPAN DOWN, NO TRUCK. // J REED, R THORNBURY, R THOMAS & H JUSTICE VER/HFP L3/HFP IDC XXXX
7572 | Pikeville | 3413402 | GARRETT | LACKEY | 2008-08-06 18:04 | 2008-08-06 23:05 | 5 | 301 | 66160-1 | 1505 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3413402//12T FUSE OUT ON POLE 112-88. BAD 10KVA TRANSFORMER ON POLE 112-88. NEED MATERIAL HANDLER BUCKET TWO MEN. 15KVA TRANSFORMER. RELEASED BY CREW 074S11// 5 COD ON LINE FUSE// UPDATED MAP DISC SENT IDCC PN118, CNT1 XXXX
7573 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2022-07-24 16:58 | 2022-07-24 20:06 | 8 | 188 | 4568911 | 1504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2 way lf @ 1098-206. copper burnt out of bottom of cutout feeding towards 1098-700. no trks Released by crew 078S07
7574 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-09-22 09:26 | 2010-09-22 15:42 | 4 | 376 | 52099-1 | 1504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLING LINE NOW--BAD 100 KVA 19.9 120-240 WITH CT METERING,NEED CUTOUT AND ARRESTER,NEED GUY REPULLED OR REPLACED LOCATED AT LAB AT OLD RIVER PROCESSING ON POLE 221-150 RELEASED BY CREW 077S10//TRANS TOOK A SHOT OF LIGHTNING REPLACED ANCHOR AND IN PROCESS OF REPLACING TRANSFORMER , CUTOUT .//VER/CRB IDC XXXX
7575 | Pikeville | 3408101 | SALISBURY | PRINTER | 2016-03-08 12:21 | 2016-03-08 13:55 | 16 | 94 | 4827241 | 1504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | @ 1309 PATROLLING LINE// FOUND BAD ARERESTER 40T FUSE OUT POLE 1146-23 CLEARED ARRESTER UP DIFICULT LOCATION NO TRUCK. // ENTERED AED COD-16 ISO LF 38831146D00023 VER/HFP L3/HFP
7576 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-06-19 13:44 | 2021-06-19 20:00 | 4 | 376 | 4772241 | 1504 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | bad secondary connection on pole, repaires made all power restored @20:00
7577 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2020-04-26 23:49 | 2020-04-27 01:08 | 19 | 79 | 4755301 | 1501 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 2349/pole fire opened fuse at 38830092C00620 affecting 19 CC to put fire out. Lowered everything on pole 38830092D00963, pole burned in two. Line fuse back in @ 01:08
7578 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-07-28 16:20 | 2017-07-28 16:40 | 75 | 20 | H4195651 | 1500 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE RECLOSURE OPEN @ 833-438 COD 11 ,CUTOUTS BROKE @833-211 GOING TO ISULATE CUTOUTS. GOING TO OPEN OTHER RECLOSURES TO MAKE SAFE REPAIRES.@ 1620 CLOSED @ CLOSED 1640 . OPENED RECOLSURES @ 14:20 CLOSED @ 14:40 38830833C00438 VER/AWD SJGC DUP
7579 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2009-04-08 13:27 | 2009-04-09 14:25 | 1 | 1498 | 50508-1 | 1498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | PER LINE CREW SUPERVISOR, RANDALL MARCUM : TALKED WITH CUSTOMER AND ITS OK TO LEAVE POWER OFF UNTIL WE SET POLE// LINKED TO ORDER 65828-1 & SW ORDER 66544-1 ALL CUSTOMERS NOW RESTORED. *DO NOT CLOSE ORDER ** SW DISP CLOSE NOW PART OF SOS 1165-78 VER/PDP IDC XXXX
7580 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-07-03 12:41 | 2015-07-03 16:15 | 7 | 214 | 4714381 | 1498 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND PRIMARY AND NEUTRAL WRAPPED TOGETHER BTWEEN 291 AND 787, UNWRAPPED WIRE. POWER RESTORED VER/CRB
7581 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-12-08 09:31 | 2013-12-08 17:50 | 3 | 499 | 4115071 | 1497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF BLOWN ON 37820266000045// WILL PATROL// POWER IS RESTORED VER/SEF L3/HFP
7582 | Pikeville | 3408103 | SALISBURY | MARTIN | 2018-03-24 19:10 | 2018-03-25 19:19 | 3 | 1449 | 4056311 | 1497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Assessor Required , 4 WD pickup required , will need to patol line from open fuse pole 1074-510 to cell tower / GXJ 3/25: Patroled line. Found no problems. Can fuse line cutout. ENY Released by crew 074E06 . opened at pole 1074C-208 @ 18:55 and closed @ 19:19 to replace cutout on pole 1074-510 / ALL WORK COMPLETE / GXJ Released by crew 074S03 38831074C00208
7583 | Hazard | 3303901 | LESLIE | HYDEN | 2008-06-10 06:01 | 2008-06-10 14:20 | 3 | 499 | 61263-1 | 1497 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303901//--SEND TO SAM W.-19.9 CUTOUT-TRACKING-EASY SQ. BUCKET JOB-OUT 2 TIMES-BUGS OR POLLON-EASIER TO REPLACE-GRAVEL DRIVE-SEE FROM ROAD-JIM RELEASED BY CREW 077S06//COD 3 IDC XXXX
7584 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-07-31 12:14 | 2018-07-31 14:30 | 11 | 136 | 4877241 | 1496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout at barntalked to caretaker going to get with so can get the gates open this week
7585 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2009-01-23 06:06 | 2009-01-23 12:20 | 4 | 374 | 59314-1 | 1496 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3403801//BAD TRANSFORMER CREW ENROUTE.//COD 3//BAD TRANSFORMER CREW ENROUTE. RELEASED BY CREW 074S023C//CREW ON SITE WILL CHNG X-FMR AND CUT-OUT R RAY// VER/DBM ADDED 1 CUST FROM MISMAPPPED L3/KEP
7586 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2009-07-06 06:06 | 2009-07-06 11:05 | 5 | 299 | 51301-1 | 1495 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3200201// THIS WELL BE DISPATCHED THIS MORNING, XFORMER FUSE BLOWN, REFUSING IT, DOOR BURNT UP AT XFORMER FUSE COD-5 ISO TF 38821089B00028 L3/HFP IDC XXXX
7587 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-12-08 08:04 | 2010-12-08 10:50 | 9 | 166 | 64281-1 | 1494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY LEAD ON TRANS. HAS BURNED INTO. I AM GOING TO OPEN TRANS. AND SPLICE WIRE. I SPLICED LEAD ON TRANSFORMER.//COD 9// VER/DBM IDC XXXX
7588 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-03-14 09:59 | 2009-03-14 12:45 | 9 | 166 | 58428-1 | 1494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 38821130000084-----20 T BLOWN--- BROKEN C/O ISOLATED ON POLE #38821130000269 //VER/GAH
7589 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-07-27 22:09 | 2014-07-28 10:36 | 2 | 747 | 4297171 | 1494 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA XFMR BAD// CAN USE MATERIAL HANDLING BUCKET TO CHANGE// ADVISED CUSTOMER THAT CREW WOULD BE OUT AFTER 7:30 A.M.// RELEASED BY CREW 076S02/ CREW ON SITE TCM// ISO 38830882A00425// COD 2
7590 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-12-06 07:15 | 2009-12-06 13:08 | 7 | 353 | 61604-1 | 1493 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP STS WR # 32953302 // 6A CW PRIMARY NEUTRAL DOWN FROM POLE 3783-19B-40 TO POLE 3783-19B-41, INSTALLED SECONDARY BREAKERS AT POLE 37830019B00041 AND REENERGIZED TRANSFORMER AT 10:25, ONE CUSTOMER STILL OUT ... AT METER # 190229567 ( RECORDS INDICATE SERVED FROM POLE 106 BUT IS SERVED FROM POLE 41 ) OPENED TRANSFORMER AT 12:54 AND CLOSED AT 13:08 / ALL WORK COMPLETE / GXJ CREATED ORDER 62845-1 FOR TR OUTAGE TO MAKE REPAIRS. L3/HFP IDC XXXX
7591 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2019-04-08 14:26 | 2019-04-08 14:47 | 71 | 21 | 4070551 | 1491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | EMERGENCY OUTAGE TO REPLACE SWITCH ON POLE 37830045000092 ¦¦ COD-70 ON RECL (TOOK LOAD OFF WITH RECL) OFF@ 1426 ON@ 1447 ¦¦ OPENED TAPS ON SW POLE 37830045000092 - 1 CUST TO REPLACE SW OFF@ 1426 ON@ 1447 L3/HFP sjg
7592 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-01-23 19:42 | 2016-01-23 23:15 | 7 | 213 | 4645631 | 1491 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED 6T XFMR FUSE - BROKE
7593 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-12-27 20:31 | 2018-12-27 23:00 | 10 | 149 | 4603271 | 1490 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on p-900-225.. blew line fuse on 900-5. changing cutout--restored 2300 L3/HFP
7594 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-02-26 08:26 | 2019-02-26 09:28 | 24 | 62 | 4923471 | 1488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | High side fuse out on step down 147-500 will refuse/// Cutout door burnt up //// changed bad door and refused step down @ 09:24 and restored service
7595 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-09-12 10:37 | 2013-09-12 14:45 | 6 | 248 | 4841791 | 1488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | THE TOP OF POLE 427-266 IS BURNED OFF . GEORGE WHITAKER IS COMMING TO MAKE REPAIRS RELEASED BY CREW 077S12 REPAIRS MADE POWER RESTORED@14:45 COD-6 ISO LF 37830427A00054 VER/HFP L3/HFP IDC XXXX
7596 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-04-17 17:18 | 2016-04-17 23:30 | 4 | 372 | 4098151 | 1488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA, 7200 120/240, CHANGE C/O & ARRESTOR. TALK TO PROP. OWNER ABOUT TRK IN DRIVEWAY.XFMER @ 119 NH DRIVE RELEASED BY CREW 078S07
7597 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-11-19 17:09 | 2016-11-19 21:17 | 6 | 248 | 4115761 | 1488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | FUSE OPEN ON POLE 382-206. THIS FUSE WAS INSTALLED ABOUT A WEEK AGO. PRIMARY IS OFF PIN ON POLE 406-1. WILL NEED ONE MAN. THIS IS MANUAL GOING DOWN THE SIDE OF PINE MOUNTAIN. POWER RESTORED AT 21:17 VER/HFP L3/HFP
7598 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2018-07-02 06:53 | 2018-07-02 15:09 | 3 | 496 | 4703141 | 1488 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | secondary pole 328-209 rotted off at ground level & fell over, opened xfmr at 11:42 so crew can replace pole.. Released by crew 077S11
7599 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2021-09-21 22:18 | 2021-09-22 01:03 | 9 | 165 | 4266201 | 1485 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 38830045A20666 bad con at tran riser-repaired-allgood-ds092221/ Part Power when arrived/ opened transformer to make repairs at 1245am closed 0103am
7600 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2017-02-18 21:03 | 2017-02-19 02:00 | 5 | 297 | 4406681 | 1485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRUCKS OK RELEASED BY CREW 078S03/// VER/DKM L3/HFP XXXHFP
7601 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-01-31 15:18 | 2020-01-31 16:13 | 27 | 55 | 4351841 | 1485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse, back in at 16:13
7602 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-02-10 19:50 | 2009-02-10 20:45 | 27 | 55 | 57536-1 | 1485 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP BAD ARRESTER AT 38830206A31197 COD-27 L3/HFP MLR OK
7603 | South Williamson | 3200302 | BELFRY | TOLER | 2017-05-13 12:00 | 2017-05-13 12:14 | 106 | 14 | H4794581 | 1484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SEE DOL CASE 741489///BELFRY - BELFRY ISOALTION FOR BUS DISCS REPLACEMENT///RECORD FOR RESTORATION OF PORTION OF CKT BY CLOSING BELFRY - TOLER 12KV CB B/// VER/DKM AJB
7604 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-04-03 03:27 | 2015-04-03 11:15 | 4 | 468 | 4261671 | 1484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER ON SITE/LINE FUSE OUT 92-329/LINE LOOKS CLEAR/SERVICER TO TRY FUSE/FETR0500/VEM/FUSE @92-329 IN AT 0447/XFMR FUSE @92-422 BLEW/APPEARS TO BE BAD CUTOUT/NEW FETR0630/VEM/CUTOUT CHANGED /25 KVA XFMR IS BAD/TRUCK OK/19.9 25KVA/VEM RELEASED BY CREW 078H14 VER/KEP L3/DKGXXXX
7605 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-01-25 09:45 | 2010-01-25 17:14 | 10 | 449 | 59335-1 | 1484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF == POLE 37830369D00321 == OPEWN PRIMARY ON POLE 37830369D00256 == LINE FUSE OPEN ON POLE 37830369D00239 20 T == PUT LINE FUSE IN AT 11:10 AM == 1CUST STILL OUT == J COMBS TO REPLACE POLE RELEASED BY CREW 077S03 REPLACED POLE AND RESTORED POWER TO LAST CUSTOMER AT 1709 JKC IDC XXXX
7606 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-04-19 09:24 | 2009-04-19 11:10 | 14 | 106 | 58645-1 | 1484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE SIDE FUSE ON STEPDOWN OUT--PATROLING LINE FOUND BAD ARRESTOR ON 117-297 // SENT TO RAYBURN VER/TOM L3/TOM IDCC FP NULL XXXX
7607 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-01-01 13:25 | 2009-01-01 13:39 | 106 | 14 | 50589-1 | 1484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3312202//OPENED TO ALLOW SERVICER TO WORK ON ORDER #50519-1//VER/CRB L3/KEP IDC XXXX
7608 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-04-12 16:26 | 2013-04-13 00:51 | 8 | 505 | 4005391 | 1484 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1121-192 TOP BURNTED OFF, CUTOUT CAUSED IT, ISOLATED ON POLE 1121-82, LIFTED HTSP, GROUNDED AND TAGGED LINE FOR DDC, CREW REQ, 404 POLE MAYBE ABLE TO USE EXTENDEN ON THIS HAS UNDERGROUND SERVICE ON POLE., DIRECTION ARE, FROM 23 OUT RT 1, TO 14 MILE MARKER, ROAD ON LEFT MARKED SIKES PRIVATE RD, FIRST DRIVE WAY TO THE RIGHT BRICK HOUSE ON LITTLE HILL, CAN USE TRUCK. GO AROUND BACK SEPTIC TANK IN THE FRONT, RELEASED BY CREW 078S06/CREW ON SITE/FETR 0045/VEM/PR 0051 VER/PDP IDCC CNT6, STP MISSING XXXX
7609 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-02-22 07:11 | 2021-02-22 09:05 | 13 | 114 | 4214561 | 1482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester at pole 293-79. made repairs and restored power at 9:05
7610 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-11-25 06:04 | 2008-11-25 06:23 | 78 | 19 | H51808-1A | 1482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3010602//POLE FIRE ON POLE 1124-8018 CREW REQ, ALL CUST RESTORED BUT 5 RELEASED BY CREW 078S09/CREW ON SITE/FETR 11-25-08/0730/VEM/WORK COMPLETE0623/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN IDCC DUP TO OPEN CIRCUIT TIE XXXX
7611 | Pikeville | 3403001 | PIKEVILLE | CITY | 2014-08-18 19:45 | 2014-08-18 20:24 | 38 | 39 | 4381381 | 1482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CONDUCTOR IS LAYING ON THE ARM /// WILL OPEN RECLOSERS ON POLE#25-B-391 WHEN STEVE RAY IS IN POSITION/// OPENED RECLOSERS @ 19:45 FOR CREW TO DUE WORK/// REPAIRS MADE CLOSED RECLOSERS IN @ 20:24 AND RESTORED SERVICE// COD 38//VER/ ADH AJB
7612 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-11-28 00:49 | 2021-11-28 13:10 | 2 | 741 | 4129211 | 1482 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse out, bad 19.9 , 15 kva xfmr, need crew, power restored
7613 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2010-06-15 21:07 | 2010-06-15 23:35 | 10 | 148 | 65698-1 | 1480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "C" PHASE OPEN COD-10LIGHTNING ARRESTER BLOWN ON 954-160.LIGHTNING ARRESTER BLOWN ON 954-160. TRIED FUSE AND IT CAME BACK OUT. FOUND ANOTHER BLOWN ARRESTER ON 38830954B41212 ON AN UNUSED XFMR. WILL ISOLATE AND TRY AGAIN.. RESTORED @ 11:35. SH VER/KEP L3/KEP
7614 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2022-11-16 04:30 | 2022-11-16 16:50 | 2 | 740 | 4146891 | 1480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines/// FUSE OPEN POLE 321-D3-640 /// CUT OUT WENT BAD BURNING OFF TOP OF POLE 321-D-543 /// GILLEY HAS MATERIAL LIST // NEED LINE CREW Released by crew 077H12
7615 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-07-26 22:10 | 2009-07-27 10:30 | 2 | 740 | 56191-1 | 1480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSED HAD ROTTED REPLACED IT IDC XXXX
7616 | South Williamson | 3411401 | DEWEY | INEZ | 2019-04-26 21:00 | 2019-04-26 21:20 | 74 | 20 | 4176661 | 1480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | found broke by pass cutout on pole 672-133///opened recloser and step down on next pole back to repair//repairs made//opened at 21:00//closed at 21:20//complete//em
7617 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-07-02 08:45 | 2015-07-02 13:41 | 5 | 296 | 4708051 | 1480 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | /RELEASED BY CREW 078S01/CREW PATROLLING LINE/VEM/BAD DEAD END BELL @571-67/FETR1430/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1341/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830571000005/ COD 5
7618 | Hazard | 3303902 | LESLIE | WOOTON | 2020-02-07 08:17 | 2020-02-07 16:30 | 3 | 493 | 4375951 | 1479 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 19.9 manuel, also replace cutout if possible Released by crew 077S07, changing now, p.hicks
7619 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-08-13 19:27 | 2021-08-13 19:56 | 51 | 29 | 4057901 | 1479 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced xfr cutout @ 206-2423,,line fuse restored @ 19:56 complete
7620 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-01-06 10:49 | 2014-01-06 14:55 | 17 | 246 | 4236461 | 1478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED TAP ON 374-69 TO ISOLATE BURNT OFF POLE//COD 17// CLOSED IN MAIN LINE AT 1206 LOWERED ATTACHMENTS ENERGIZED HOT TAP ON POLE 374-69 AT 1455 RELEASED BY CREW 078Q08 VER/KEP IDC XXXX
7621 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-12-25 07:57 | 2008-12-25 14:50 | 6 | 413 | 63856-1 | 1478 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT BROKE DOWN AND HAS TOP OF POLE 98-495 BURNED OFF. DENNIS IS GETTING HELP. I LIFTED A HOT TAP ON POLE 98-143 TO ISOLATE TROUBLE AND CLOSED RECLOSER IN ON POLE 98-39 { CENTER RECLOSER IS THE ONLY ONE OPEN } AT 11:30. THIS LEAVES ONLY 2 CUSTOMERS OUT UNTIL TROUBLE IS FIXED. FAULT POLE 37820098C00495 L3/HFP IDC XXXX
7622 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-12-12 06:57 | 2022-12-12 09:41 | 9 | 164 | 4250861 | 1476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot tap burnt off basket on 556, cutout on arm. crew required. Send to Babe morgan. pole 20-b4-3538 Released by crew 078S02 complete R.Green time on 9:41
7623 | South Williamson | 3411401 | DEWEY | INEZ | 2020-11-11 13:49 | 2020-11-11 16:33 | 9 | 164 | 4662591 | 1476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F blown on 769-A-25 will check// Cutout has failed on 769-A-142 will be replacing// Replaced cutout and closed L/F @ 16:33
7624 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2022-06-14 18:12 | 2022-06-14 20:15 | 12 | 123 | 4116441 | 1476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 1146-35, bad 12kv c/o. line crew reqd. set up on uhlen branch Released by crew 078S07,repairs made all cust restored @ 2015 please close ticket thanks.bt
7625 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-02-10 03:27 | 2011-02-10 05:30 | 12 | 123 | 55808-1 | 1476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN----FUSE LINK APPEARED TO HAVE BROKE VER/PDP IDC XXXX
7626 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-08-31 05:12 | 2015-08-31 11:21 | 4 | 369 | 4184311 | 1476 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME/NO CREW REQUIRED BAD CUTOUT CHANGING ARRESTOR ALSO VER/CRB
7627 | Hazard | 3303901 | LESLIE | HYDEN | 2010-05-13 23:59 | 2010-05-14 04:54 | 5 | 295 | 61789-1 | 1475 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW MAKING REPAIRS NOW, PHASE B CAME OFF INSULATOR ON ANGLE POLEB PHASE INSULATOR JUMPED OFF OF POLE TOP PIN...OPEN GOAB ON POLE 388A-307 @ 03:44 HRS, MADE REPAIRS AND CLOSED GOAB @ 04:54 HRS....ALL POWER RESTORED P.HICKS IDCC DUP TO OPEN GOAB, LOOKS LIKE POLE 37830388A00028 WAS OUT INITIALLY XXXX
7628 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-06-27 23:10 | 2016-06-27 23:21 | 134 | 11 | H3311103 | 1474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD INSULATOR RELEASED BY CREW 077S01 VER/KEP
7629 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-06-02 10:31 | 2009-06-02 12:45 | 11 | 134 | 58961-1 | 1474 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP COD11//MADE A MD //CHG OUT CUT OUT CUT ARRESTOR IN CLEAR REPLACED 30-T LINE FUSE L3/HFP IDC XXXX
7630 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-04-15 14:57 | 2020-04-16 15:30 | 1 | 1473 | 4700231 | 1473 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in service drop at service pole. SERVICER REQUIRED..Pole number is actually 49-304 Released by crew 074X05,repairedbroken nuetral in service drop at service pole..cc1..on 1530
7631 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2009-01-13 17:47 | 2009-01-13 18:51 | 23 | 64 | 54775-1 | 1472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | WR # 28051934 ///HOT -TAP LEAD BROKEN OFF TOP OF CUT-OUT ON ATALL POLE CAN REACH RELEASE AND GIVE TO VERNON MULLINS RELEASED BY CREW 078S09/CREW ON SITE/FETR1932/VEM/REPAIRS MADE AND ALL CUST RESTORED AT 1851/PLEASE CLOSE TICKET /THANKS/VEM VER/TOM L3/TOM IDCC TOF1732 ESTIMATED TIME OFF XXXX
7632 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2021-05-28 13:45 | 2021-05-28 16:49 | 8 | 184 | 4637171 | 1472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20t lf open @ 1148-871. no tags or grounds. bad c/o 1148-902. no trks. access from 116 or 108 pheasant ct. off bluebird Released by crew 078S07///making repairs///Complete BR
7633 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2008-08-05 14:52 | 2008-08-05 21:00 | 4 | 368 | 65536-1 | 1472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3402202// 25T FUSE OUT ON POLE 66D15. I HAVE LINE GROUNDED AND TAGED AT THIS LOCATION. GREG JUSTICE THANKS HE HAS FOUND A BAD INSULATOR. LOOKS LIKE TYE WIRE BROKE. PRIMARY OFF INSULATOR AT POLE 66D172. FROM 66D172 TO POLE 66D171 PRIMARY WIRE IS ABOUT 10 FOOT BELOW NEUTRAL. FUSED UP EVERYTHANG OK/// VER/TOM IDC XXXX
7634 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2014-10-07 10:31 | 2014-10-07 13:35 | 8 | 184 | 4564421 | 1472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE POLE (NO DAVOX SENT) COD-8 ISO PO @ 37830423C00134 VER/HFP L3/HFP AJB CCO FEC57
7635 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2010-11-30 09:58 | 2010-11-30 11:30 | 16 | 92 | 61006-1 | 1472 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD,POLE BURNT OFF. POWER OFF.XFMR ON POLE 34 IS OFF ALSO.//COD 16// VER/DBM IDC XXXX
7636 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-10-01 13:52 | 2013-10-02 14:22 | 1 | 1470 | 4902511 | 1470 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED--BAD 4/0 UG SERVICE TO POND PUMP--CAN WORK TOMORROW RELEASED BY CREW 078S07 RELEASED BY CREW 078H01//THE OPS ORDER NUMBER IS 030546401.//CUSTOMER IS AWARE THIS WILL WAIT UNTIL OUR UNDERGROUND CREWS CAN WORK ON THIS// VER/DBM L3/HFP IDC XXXX
7637 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2008-06-05 10:51 | 2008-06-05 15:45 | 5 | 294 | 58143-1 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BLOWN TRANSFORMER FUSE,,,,,,BACK ON AT 15:45 VER/HFP
7638 | Hazard | 3310502 | HADDIX | CANOE | 2009-03-04 13:15 | 2009-03-04 13:50 | 42 | 35 | 54984-1 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310502//CREWS OPENED RECLOSER TO PUT WIRE BACK UP SAFELY//RELATED TO ORDER 54819-1//COD 42// VER/DBM IDC XXXX
7639 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-05-25 14:06 | 2019-05-25 19:00 | 5 | 294 | 4331731 | 1470 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 2 xfmr fuses blown, 2 cutout gates burnt up, also buss bar in meterbase burnt up, electrican on site , working to restore.all power restored @ 19:00 p.hicks
7640 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-07-13 13:38 | 2012-07-13 15:07 | 40 | 89 | 4712171 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED -BAD CUTOUT ON POLE 38830093B00313///HELPED FIRE DEPT PUT OUT FIRE--OPENED RECLOSER AT 13:38--RECLOSER BACK IN AT 14:12-- RELEASED BY CREW 078S07,,, COOMPLETE//COD 40 IDCC TOF1252 XXXX
7641 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2008-07-29 14:50 | 2008-07-29 15:05 | 98 | 15 | H61624-1 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202203 -POLE TOP BURNED OFFPOLE TOP BURNED OFF POLE 771-497 BAD CUTOUT RELEASED BY CREW 079S01//CREW ON SITE STARTING REPAIRS TCMILLER //SAM CLOSED BREAKER IN AT 12:43 //VER/GAH IDC XXXX
7642 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2014-08-14 17:52 | 2014-08-14 19:30 | 15 | 98 | 4370591 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BROKE CUTOUT @1091-6 LIFTED HOT TAP ,FEEDS OLD XFMER THAT IS NOT IN SERVICE ,, MADE HOT @ POLE 1092-3 @19:30//COD 15// VER/DBM
7643 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-11-26 13:20 | 2010-11-26 21:30 | 3 | 490 | 59788-1 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONLY GETTING 70 VOLTS ON ONE SIDE OF SEC CALLED FOR R/W CREW TO CUT PINE TREES THAT HAS GROWN INTO SEC BEFORE THIS CAN BE LOCATED--ALSO HAD TO CHANGE 25KVA WAS LEAKING OIL AND BAD CUTOUT VER/PDP IDC XXXX
7644 | Whitesburg | 3401301 | FLEMING | NEON | 2008-02-13 11:39 | 2008-02-13 14:45 | 13 | 186 | 62482-1 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401301// POLE 355-475 TOP OF POLE IS BURNED IS BURNED OFF DUE TO BAD CUTOUT WILL NEED A CREW I WILL GET UP WITH BRUCE LIND0N RELEASED BY CREW 074S07//LAST CUST ON @ 1445// VER/DBM IDC XXXX
7645 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-10-28 08:23 | 2009-10-28 10:08 | 14 | 105 | 60761-1 | 1470 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP CONNECTION APPEARS BURNT-UP AT XFMR. NO TRUCK ACCESS - WILL HAVE TO OPEN XFMR TO CHECK. OPENED XFMR AT 09:45, RE-WORKED XFMR CONNECTIONS AND CLOSED XFMR AT 10:08 RESTORING ALL CUSTOMERS. SH L3/HFP IDC XXXX
7646 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-07-21 17:56 | 2016-07-21 18:02 | 245 | 6 | 4664481 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | MOAB | N.O. TIE RECL AT POLE 37830178B00008 AND N.C. GOAB SW AT POLE 177-D4 37830177D40583 RELEASED BY CREW 077H07/// VER/DKM AJB
7647 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-01-10 11:55 | 2008-01-10 15:25 | 7 | 210 | 55454-1 | 1470 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3402801// BAD 25KVA XFMR. R. MAYNARD WILL COME CHANGE IT WHEN HE FINISHES TROUBLE AT SALYERSVILLE. RELEASED BY CREW 076S02//COD 7// REMOVED BAD XFMR FROM 785-98 AND INSTALLED NEW XFMR ON POLE 785-97.ON AT 15:25// VER/TOM IDC XXXX
7648 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2016-07-22 17:56 | 2016-07-22 18:02 | 245 | 6 | 4667841 | 1470 | TRANSMISSION LINE | EQUIPMENT FAILURE | INSULATOR | SWITCHING BETWEEN BULAN STATION AJAX-DWAR CKT. AND BECKAM STATION HINDMAN CKT,,REC. POLE37830178B00008 AND GOAB POLE37830177D40583 RELEASED BY CREW 077H07 VER/ARN AJB
7649 | Pikeville | 3407103 | TOPMOST | KITE | 2019-02-06 11:13 | 2019-02-07 11:40 | 1 | 1467 | 4758511 | 1467 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse blown..Bad 25 KVA XFMR truck approach no one currently living at either residence// called Joey Reed he said to email copy of ticket to PR and crew will change tomorrow 2/7/19// I did notify property owner Released by crew 074H06/ CREW ON-SITE/ BACK ON AT 11:40 RICK RAY L3/HFP
7650 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-05-10 17:07 | 2009-05-10 22:00 | 5 | 293 | 57043-1 | 1465 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANSFORMER-IN PARKING LOT BEHIND APTS-SEND TO BOB RELEASED BY CREW 078S07//VER/CRB IDCC PN6521 XXXX
7651 | Hazard | 3309003 | JEFF | VIPER | 2018-06-18 10:18 | 2018-06-19 10:42 | 1 | 1464 | 4618491 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST VOLTAGE WAS FINE, BUT THIS IS THE 2ND TIME HE HAS HAD PROBLEMS IN 3 WEEKS. WILL NEED SOMEONE TO REWORK CONNECTIONS IN THE DAY LIGHTS TO MAKE SURE OUR SIDE IS OK. Released by crew 077S01/ 1018 to 1042CUST VOLTAGE WAS FINE, BUT THIS IS THE 2ND TIME HE HAS HAD PROBLEMS IN 3 WEEKS. WILL NEED SOMEONE TO REWORK CONNECTIONS IN THE DAY LIGHTS TO MAKE SURE OUR SIDE IS OK. Released by crew 077S01 conn.went bad open at 10:18 on 10:42/ ISO 37830393D00032/ COD 1
7652 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-10-02 15:57 | 2015-10-02 19:00 | 8 | 183 | 4303911 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT/ 1900/ ISO 37830554000065/ COD 8/ VER/BOW L3/HFP XXXHFP
7653 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2019-05-05 01:42 | 2019-05-05 07:48 | 4 | 366 | 4222261 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout broke, no trucks to pole. Crew required Released by crew 078H04 Crew on site, Repairs made, ticket complete.//cod 4
7654 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-03-15 15:13 | 2020-03-15 17:15 | 12 | 122 | 4480221 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A and C riser fuse cutouts busted @24-D2-1679, will have to open B phase to change them all out, will keep track of times. Opened B phase riser @1548. Changed all 3 riser fuse cutouts and closed them back in @1715.
7655 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-07-29 18:49 | 2015-07-29 22:25 | 9 | 216 | 4957351 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PUT 15KVA TRANSFORMER BACK @ 38830760D00330/ COD 9/ MD DONE ISO 38830760D00024/ VER/BOW L3/HFP XXXHFP AJB
7656 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2008-06-29 19:08 | 2008-06-29 21:10 | 12 | 122 | 59688-1 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | ON SITE, XFORMER FUSE BLOWN, REFUSING IT VER/KEP IDC XXXX
7657 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-03-15 13:32 | 2020-03-15 21:40 | 3 | 488 | 4480021 | 1464 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | All connections look good at secondary pole behind the houses where the service splits,Going to have to walk up on hill and check at pole 145-2 XFM pole. Bad 25 KVA XFM 7200 will need line crew to help make repairs,and manual RAC ..Restored service at 9:40.
7658 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2016-08-09 12:59 | 2016-08-09 16:28 | 7 | 209 | 4753831 | 1463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 15T FUSE LINK ON LINE FUSE 1091-24 APPEARS TO HAVE BROKEN. RESTORED @ 16:28. SH VER/AWD AJB
7659 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-01-08 11:27 | 2013-01-08 13:40 | 11 | 133 | 4577581 | 1463 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLING LINE, FOUND BAD ARRESTOR ON 203-87. POWER RESTORED IDC XXXX
7660 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-06-14 09:58 | 2013-06-15 10:20 | 1 | 1462 | 4339621 | 1462 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | **** ARCOS NEEDED****INSULATION ON 4/3 SERVICE DETERIORATED, NEED TO REPLACE WITH 2/3 IN A.M. NEED 1 MAN AND BIG BUCKET. CUST. REQUESTED WE WAIT UNTIL MORNING. ARCOS AT 0800. ---- SDB / 1 CC INTERRUPTED FROM 0958-1020. VER/SDB IDC XXXX
7661 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-08-30 01:28 | 2014-08-30 09:35 | 3 | 487 | 4437851 | 1461 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM 8-30-14 NEED 1 A LINEMAN ,MATERIALHANDLER 4 LINE HOSES, & 7200 CUTOUT//COD 3// VER/DBM
7662 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-05-20 10:02 | 2017-05-20 18:09 | 3 | 487 | 4827081 | 1461 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT GATE BURNED UP OLD TYPE NEED TO REPLACE CUTOUT AND ARRESTER TRUCK ACCESSIBLE WILL NEED FLAGGERS RELEASED BY CREW 077E02 REPAIRS MADE AND POWER RESTORED AT 1809/ ISO 37830244000094/ COD 3 VER/KEP
7663 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-12-26 17:52 | 2009-12-27 18:13 | 1 | 1461 | 52219-1 | 1461 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER SAYS SVC MAN REPAIRED LOOSE CONNECTED EARLIER TODAY. WE CAN CLOSE THIS TICKET. RELEASED BY CREW 074E08
7664 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-01-11 07:26 | 2014-01-11 09:24 | 17 | 118 | 4270911 | 1460 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON ARM BROKEN,ISOLATED IT.CLOSED RECLR ON 1080-53 AT 08:45.ALL ON XCEPT AT BROKEN CUTOUT XFR//////P LAYNE ENROUTE W BUCKET//////REPLACED CUTOUT AND RESTORED AT 09:24 RELEASED BY CREW 074S06 VER/TOM L3/TOM L3/HFP IDCC CNT56 PH B ONLY XXXX
7665 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2010-05-08 08:02 | 2010-05-08 12:05 | 6 | 243 | 57543-1 | 1458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 235-127.//VER/CRB IDC XXXX
7666 | South Williamson | 3411401 | DEWEY | INEZ | 2020-10-22 09:21 | 2020-10-22 13:12 | 7 | 231 | 4575361 | 1458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Stirrup burnt off on line fuse. Crew enroute to assist. Opened latteral to transformer 742-66 @ 12:00, made repairs and closed line fuse 742-5 @ 13:12 restoring both latterals. (Map Desc - Both latterals are now protected by 15T line fuse on 742-5) sh//MD MADE
7667 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2008-01-30 07:51 | 2008-01-30 11:54 | 6 | 243 | 61849-1 | 1458 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000105//BAD HOT -TAP VER/ARN IDC XXXX
7668 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-01-13 23:12 | 2016-01-14 03:15 | 6 | 243 | 4618621 | 1458 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD JUNCTION BOX ON POLE--4/0 UG CONNCTIONS BAD IN BOX ON POLE -1 MAN 1 STOREROOM-TRANSFORMER OPEN 1 HOUR JIM AJB.
7669 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-05-28 22:51 | 2017-05-29 00:43 | 13 | 112 | H4877461 | 1456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BAD CUTOUT/WITH ARMS/DETAILS IN ACESSMENTS RELEASED BY CREW 078S03--C PHASE OPEN UPON ARRIVAL--OPENED A & B PHASE APPX 22:51--MADE REPAIRS TO X ARMS---CLOSED ON 206-1100 AT 00:43---TBL TKT COMP--RMV/// RECRD FOR OPENING LINE FUSES A & B/// VER/DKM
7670 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-03-09 13:44 | 2012-03-10 14:00 | 1 | 1456 | 4567031 | 1456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL NEED TO LOWER 1/0 TRIPLEX SECONDARY TO GROUND AND SPLICE, CREW REQUIRED , WILL COMPLETE ON 03-10-12 / GXJ RELEASED BY CREW 074S03WILL NEED TO LOWER 1/0 TRIPLEX SECONDARY TO GROUND AND SPLICE, CREW REQUIRED , WILL COMPLETE ON 03-10-12 / GXJ . REPLACED 75 FT 1/0 / 3 SD, ALL WORK COMPLETE / GXJ//COD 1// VER/DBM IDC XXXX
7671 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2013-01-30 12:33 | 2013-01-30 14:04 | 16 | 91 | 4755021 | 1456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 079H06. BAD CUTOUT ON POLE 1036-232. NTA I HAVE HELP IN ROUTE. COD-16 ISO LF 38821036C00036 VER/HFP L3/HFP IDCC TOF0923 LINB ON FULL POWER INITIAL CALL XXXX
7672 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-02-05 16:46 | 2015-02-05 17:12 | 56 | 26 | 4993721 | 1456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED 4993531/ OPENING RECLOSER ON POLE 37830179C00232 TO SAFELY CHANGE CUTOUT ON POLE 37830179C00082/ OPENED RECLOSER AT 1646 VER/BOW L3/DKGXXXX SEE 4993531 FOR TRANSFORMER OUTAGE TOTAL NUMBER OF CUST 60 ON RECLOSER....56 ON THIS OUTAGE AND 4 ON 4993531 AJB
7673 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2010-08-23 13:44 | 2010-08-23 17:12 | 7 | 208 | 59636-1 | 1456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36556350 //RELEASED BY CREW 074S04 BAD 25KVA.RELEASED BY CREW 074S04 BAD 25KVA. VCHANGED OUT TO 37.5 KVA COD-8 MISMAPPED CUSTOMER MD FILED VER/KEP L3/KEP IDC XXXX
7674 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-03-02 22:19 | 2016-03-03 00:11 | 13 | 112 | 4804791 | 1456 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON HOTLINE CLAMP // COD 13 HOT LINE CLAMP ON LINE FUSE RISER ON POLE 405-291 CONNECTER BURNED UP. I REPLACED IT VER/KEP
7675 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-07-01 10:15 | 2015-07-01 10:30 | 97 | 15 | 4704081 | 1455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | CHANGING RECLOSER ON POLE 37830424B42216/ THE BYPASS WAS CRACKED SO HAD TO OPEN RECLOSER/ ISO 37830424B42216/ COD 97 AJB
7676 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-06-20 12:24 | 2011-06-20 17:15 | 5 | 291 | 4352561 | 1455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CUTOUT//COD 5// VER/DBM IDC XXXX
7677 | Hazard | 3308001 | JACKSON | S.JACKSON | 2012-10-10 02:24 | 2012-10-10 10:29 | 3 | 485 | 4127531 | 1455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED AT REG WK TIME TODAY. STS POLE COMPLTED COVERED IN VINES AND LINE FUSE CUTOUT IS BROKE ,CALL JIM MULLINS AND HE IS GETTING ME ONE MAN TO HELP CHANGE CUTOUT OPEN LINE FUSE AT 0945 AND CLOSED AT1029 VER/KEP IDC XXXX
7678 | Hazard | 3308001 | JACKSON | S.JACKSON | 2013-04-11 21:39 | 2013-04-12 02:30 | 5 | 291 | 4000821 | 1455 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT ON 55 FOOT POLE ON SIDE OF HILL. GOT RUSELL COMMING TO HELP ON THIS TRANSFORMER FUSE OUT ON POLE 1083 D1 0003 BAD CUTOUT, RELEASED BY CREW 077S05 POWER BACK ON @ 2:30 COD-5 ISO PO @ 38831083D10003 VER/HFP L3/HFP IDC XXXX
7679 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-01-11 01:59 | 2017-01-11 13:22 | 6 | 683 | 4285621 | 1453 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE 924-75 GNDS @ 924-60 TAGGED TO DDC CREW REQ. YARD DOG BEST WAY IN IS THREW RED GATE POST. NEED TECH 45-4 DEAD END WITH XFMR #2 ACSR 7200 LINE FUSE IN @ 04:33 ON P 924-30 STILL LEAVES ONE CUST OFF PERMISSION GIVEN AT 0929 TO V MULLINS TO REMOVE TAGS/KYDDC TAGS/GNDS IN PLACE @ 7200 LINE FUSE IN @1325 39830924000060 @1322 VER/AWD /// VER TIMES PER VOICE RECORDER = L3/HFP HFPC FP39830924000062 TON1321
7680 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2015-02-24 20:03 | 2015-02-25 00:05 | 6 | 242 | 4079211 | 1452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFER,TRUCK ACCESSIBLE, NEED MATERIAL HANLDER AND CREW/10T FUSE OUT DUE TO BAD 50KVA TRANSFORMER. CAN USE TRUCK NEED 50KVA 7200. RISER WIRE.10T FUSE OUT DUE TO BAD 50KVA TRANSFORMER. CAN USE TRUCK NEED 50KVA 7200. RISER WIRE. TRANSFORMER CHANGED EVERYTHING OK. AJB
7681 | South Williamson | 3200302 | BELFRY | TOLER | 2012-04-07 03:57 | 2012-04-07 10:00 | 4 | 363 | 4653341 | 1452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL HOLD TIL REGULAR WORK TIME AS PER SET GUIDELINES //XFMR OUTAGE ONLY..POLE 1063A1...NO FAULT..FUSE LINK JUST BROKE..//.REPLACED FUSE..POWER ON COD-4 ISO TF 38821063A00001 ENTERED MD VER/HFP L3/HFP IDC XXXX
7682 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2015-08-31 13:26 | 2015-08-31 13:48 | 66 | 22 | H418251 | 1452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ORIGINAL COD 106//STIRRUP BURNT OPEN ON PHASE B RECLOSER.STIRRUP BURNT OPEN ON PHASE B RECLOSER. OPENED ALL THREE RECLOSERS ON 954-579 @ 13:26, REPLACED STIRRUP AND CLOSED ALL THREE REC @ 13:48. SH RELEASED BY CREW 076S02 VER/CRB L3/DKG THIS OUTAGE FOR OPENING A AND C PHASES SEE 418251 FOR ORIGINAL OUTAGE ON B PHASE AT RECLOSER AJB
7683 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-12-08 09:32 | 2010-12-08 15:35 | 4 | 363 | 64323-1 | 1452 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR IS OPEN, BAD XFMR, CALLING FOR HELP //COD 4 // WR# 38032812 // VER/DBM IDC XXXX
7684 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-05-01 09:08 | 2009-05-01 11:31 | 13 | 143 | 61742-1 | 1451 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP LINE FUSE OUT ON POLE # 458-73,.....BAD CUTOUT ON POLE 482-248 ISOLATED CUTOUT...CLOSED LINE FUSE AT 10:57 RESTORING POWER TO ALL BUT ONE CUSTOMER...REPLACED CUTOUT RESTORED POWER AT 11:31 COD-13 L3/HFP IDCC PN73, TON1131, TON1137 XXXX
7685 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-12-07 09:18 | 2021-12-07 14:08 | 5 | 290 | 4157731 | 1450 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required cutout on3 phase pole no trucks/sent mullins a message to let no Released by crew 078S03 back on at 1408
7686 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-11-01 10:32 | 2013-11-02 10:42 | 1 | 1450 | 4995091 | 1450 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000202 - BAD 7200 100KVA VOLTAGE 277-480, TRUCKS OK. TWO FUSES OUT ON 358-51 SECONDARY BUSHING BURNT UP. CUSTOMERS NAME IS JEFF KINSER, LINECREW REQUIRED. RELEASED BY CREW 078S11. VER/CRB L/3 CRB
7687 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-04-23 13:11 | 2014-04-23 14:14 | 23 | 63 | 4627661 | 1449 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON POLE 37830128000189, CUT IN CLEAR, POWER RESTORED.//MADE AED VER/CRB
7688 | Hazard | 3308401 | BECKHAM | HINDMAN | 2013-05-23 14:49 | 2013-05-23 17:30 | 9 | 161 | 4173071 | 1449 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGING BURNT UP C/O - CAN CLOSE TICKET POWER RESTORED AT 1730 MWL //VER/GAH IDCC CCO XXXX
7689 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2018-07-28 06:08 | 2018-07-28 12:10 | 4 | 362 | 4865731 | 1448 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | gate burnt up
7690 | South Williamson | 3200302 | BELFRY | TOLER | 2015-06-27 06:59 | 2015-06-27 11:00 | 6 | 241 | 4672941 | 1446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | SECONDARY POLE #1039-C-153 ROTTEN AND FELL OVER ONTO CUSTOMERS HOUSE BREAKING NUETRAL JOEY IS GOING TO REPLACE POLE RELEASED BY CREW 079H03... REPLACED 35-5 POLE AND 1/0 SECONDARY VER/KEP
7691 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-10-25 10:32 | 2009-10-25 14:33 | 6 | 241 | 52862-1 | 1446 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQ # 32360230 //HAD THIS OUT THIS MORNING AT 7, WHEN BACK OUT AT 10:30, HAVE A BAD 25 KVA, SINGLE BUSHING, 7200 120/24, CAN USE TRUCK ON THIS, TRANSFORMER IS BEHIND CHURCH ON SPRUCE ALLY, NEED CREW TO REPLACE TRANSFORMERHAD THIS OUT THIS MORNING AT 7, WHEN BACK OUT AT 10:30, HAVE A BAD 25 KVA, SINGLE BUSHING COD-6 ISO TF 39830900C14038 L3/HFP IDC XXXX
7692 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-02-04 05:48 | 2022-02-04 10:37 | 5 | 289 | 4437981 | 1445 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | lf open @ 901-314. broke cross arm @ 39830901A20502//lf open @ 901-314. broke cross arm @ 901-502.tree on primary @ 901-504. send to b.ramey Released by crew 078S07
7693 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-06-29 14:35 | 2014-06-29 16:26 | 13 | 111 | 4167901 | 1443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 38821139C30206, PATROLLING THE LINEI FOUND BAD TRANSFORMER CUTOUT, WILL REPLACE IT. CUTOUT REPLACED AND POWER IS BACK ON.//COD 13// VER/DBM
7694 | Hazard | 3303901 | LESLIE | HYDEN | 2015-02-10 03:59 | 2015-02-10 12:00 | 3 | 481 | 4004511 | 1443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR/ISO POLE37830388B00040/CLOSED 1200/.FIX IT IN HOIS// VER/ ADH L3/HFP XXX
7695 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2011-10-14 14:49 | 2011-10-14 16:40 | 13 | 111 | 4981161 | 1443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LEAD WAS LOOSE ON BOTTOM OF LINE FUSE CUTOUT.. CAUSING ARCING. REPLACED CUTOUT AND ARRESTER.. RESTORED POWER AT 1640..R.RICE... COD-13 ISO LF 37830296A20352 VER/HFP L3/HFP IDC XXXX
7696 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-05-16 11:05 | 2020-05-16 12:56 | 13 | 111 | 4842031 | 1443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Cphase line fuse blown on 1152-B2-353.no haardsseen,restored power at 12:56
7697 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2014-10-06 17:45 | 2014-10-06 18:24 | 37 | 39 | 4559451 | 1443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED RECL @ 1745 TO ALLOW HIM TO CLEAR UP POLE FIREXFMR CUTOUT FAILED ON 954-542 AND CAUSED POLE TO CATCH FIRE. OPENED RECLOSER 38830954B40413 @ 17:45 TO ISOLATE.XFMR CUTOUT FAILED ON 954-542 AND CAUSED POLE TO CATCH FIRE. OPENED RECLOSER 38830954B40413 @ 17:45 TO ISOLATE. REPLACED CUTOUT AND PUT POLE FIRE OUT. CLOSED RECLOSER @ 18:24 RESTORING ALL OUTAGED CUSTOMERS. SH COD-37 ISO OCR 38830954B40413 VER/HFP L3/HFP AJB
7698 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-04-25 09:57 | 2016-04-25 17:58 | 3 | 481 | 4122681 | 1443 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, WILL NEED BIG BUCKET, PLEASE SEND TO P. HICKS. CUTOUT IS BAD ON POLE 156-236, ONLY FEEDS LIGHTS AND A ENTRANCE GATE RELEASED BY CREW 077S02..WILL WORK AFTER ASPLUNDH EMP. FUNERAL TODAY.REPLACED CUTOUT, ALL POWER RESTORED @17:58 P.HICKS VER/AWD
7699 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2011-07-04 01:05 | 2011-07-04 01:19 | 103 | 14 | 4452501 | 1442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HAD TO OPEN OCR TO MAKE REPAIRS/BAD HOTTAP/SERVICER TO REPAIR/FETR 0130/VEM/REPLACED HOTTAP AND BASKET/ALL CUST RESTORED 0119/PLEASE CLOSE TICKET/THANKS/VEM VER/DKG L3/DKG IDC XXXX
7700 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2011-06-09 17:14 | 2011-06-09 20:30 | 8 | 196 | 4277951 | 1442 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 240-156. I AM PATROLLING LINE NOW. CUTOUT WAS BROKEN ON POLE 240-96. I ISOLATED CUTOUT AND CLOSED LINE FUSE AT 240-156 IN AT 20:12 AND IT STAYED. I AM GOING TO GO CHANGE CUTOUT NOW. I CHANGED CUTOUT AND RESTORED POWER TO LAST CUSTOMER AT 20:30 // COD-8 ISO LF 37830240000156 VER/HFP L3/HFP IDC XXXX
7701 | Hazard | 3303902 | LESLIE | WOOTON | 2008-08-04 09:49 | 2008-08-04 12:00 | 11 | 131 | 64914-1 | 1441 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT BLOWED L/A IN THE CLEAR//3303902/VER/CRB IDC XXXX
7702 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-01-28 18:17 | 2020-01-28 19:53 | 15 | 96 | 4345331 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on xfmr riser. Opened xfmr, reworked sec connections, replaced old xfmr cutout and restored @ 19:53. sh L3/HFP
7703 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-07-15 18:20 | 2015-07-15 19:50 | 16 | 90 | 4884321 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REMOVED HOT LINE CLAMP FROM LINE FOR XFMR ON POLE 182-118 REFUSED LINE CUTOUT TO RESTORE POWER TO REST OF CUSTOMERS 1 CUSTOMER LEFT OFF; ALL POWER ON AT ABOUT 1950 BUT TRANSFORMER AT 182-118 (4888351) CAN CLOSE MWL
7704 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-04-10 09:57 | 2015-04-10 14:45 | 5 | 288 | 4303121 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | OPEN WIRE SEC HOT LEG BURN DOWN MIDSPAN,BAD IN MIDDLE OF SPAN1 STRAND HOLDING OTHER LEG,PULLED METER AT HS,LINE CREW & FLAG NEEDED NO 2 AL,( REPAIRS MADE, SERVICE RESTORED, INSTALLED METER) COD-5 ISO TF 38830092B00369
7705 | Hazard | 3309302 | VICCO | JEFF | 2018-01-30 15:18 | 2018-01-30 15:50 | 45 | 32 | 4784591 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BAD CROSSARM ON POLE 37830348B00307//OPENED STEP-DOWN ON POLE 37830348B00329//COD 88//OPENED 1518 CLOSED 1550
7706 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-08-28 19:42 | 2008-08-28 20:12 | 48 | 30 | 57097-1 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401002// PRI. CONDUCTOR BROKE AT STIRRUP AND LET PRI. FALL BELOW NEUTRAL. HOT TAP IS ALL THAT IS HOLDING IT UP. I AM GOING TO OPEN LINE FUSE ON POLE 284-91 LONG ENOUGH TO REPAIR CONDUCTOR. I OPENED LINE FUSE AT 19:42, REPAIRED CONDUCTOR, AND CLOSED IT BACK IN AT 20:12.//VER/CRB IDC ADDED ORDER FOR ORIGINAL CUSTOMERS OUT XXXX
7707 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2017-06-05 16:56 | 2017-06-05 17:06 | 144 | 10 | 4911291 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER BYPASS CUTOUT BBREAKING DOWN HAD TO OPEN LINE 1062-451 TO MAKE REPAIIRS OPENES AT 16:56 MADE REPPAIRS RESTOORED POWER AT 17:06/ ISO 38821062D00451/ COD 144/ VER/BOW SJG
7708 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-01-23 22:01 | 2019-01-23 22:17 | 90 | 16 | 4712801 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 300 amp solid blade cutout broke on pole37830102000057 will have recloser on pole 37830102000149 when johnny get here to change cutout // 2201-2217 L3/HFP
7709 | Hazard | 3303902 | LESLIE | WOOTON | 2017-02-10 17:35 | 2017-02-10 17:55 | 72 | 20 | 4384431 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE TO REPLACE BAD CUTOUTS ON STEPDOWN POLE 37830415000017//WAITING ON FLAGGERS TO TAKE OUTAGE.//OPENED STEP-DOWN @ OPEN LINE TO REPLACE BAD CUTOUTS ON STEPDOWN POLE,.OPEN STEPDOWN FUSES @17:35 HRS, CLOSED BACK IN @ 17:55 ALL POWER RESTORED.P.HICKS//CUTOUTS HAD BEEN ARCING PER D CHRISTIAN CHANGED BEFORE THEY COULD START A FIRE VER/CRB L3/HFP XXXHFP AJB
7710 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-07-06 10:59 | 2013-07-06 12:19 | 18 | 80 | 4474061 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C PHASE FUSE ONLY//COD 18//BROKE CUT-OUT ON POLE 375-309. LINE FUSE BLOWN ON POLE 375-79. REPLACED CUT-OUT.BROKE CUT-OUT ON POLE 375-309. LINE FUSE BLOWN ON POLE 375-79. REPLACED CUT-OUT. POWER RESTORED AT 12:19 7/6/2013.//COD 18// VER/DBM IDCC PN309 XXXX
7711 | South Williamson | 3411401 | DEWEY | INEZ | 2008-03-26 13:55 | 2008-03-26 14:05 | 144 | 10 | 60881-1 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3411401// PAUL MUNCY & CREW ON SITE NEEDED TO OPEN LINE FUSE TO SAFELY REPLACE INSULATOR THAT IS BROKEN ALL CUSTOMERS BACK ON AT 1405 VER/HFP IDC XXXX
7712 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-07-12 06:14 | 2011-07-12 10:14 | 6 | 240 | 4524531 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CUT OUT REPLACED ON POLE 448-582 LINE FUSE OUT ON POLE 448C3-69 7.2 KVNEED CUT OUT REPLACED ON POLE 448-582 LINE FUSE OUT ON POLE 448C3-69 RELEASED BY CREW 077F08/ REPLACED BAD C/O. VER/KEP
7713 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-05-25 08:24 | 2021-05-25 13:12 | 5 | 288 | 4618851 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse blown on pole 1125-C4-90 and line fuse blown on pole 1125-C4-406// patroling/// line fuse on pole 406 back in at 11:45, bad dead end insulator on pole 1125-C4-406,
7714 | South Williamson | 3411401 | DEWEY | INEZ | 2019-10-31 12:53 | 2019-10-31 17:41 | 5 | 288 | 4227481 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke on xfmer fuse. Repairs made, back to normal.
7715 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-11-02 14:30 | 2015-11-02 16:30 | 12 | 120 | 4402911 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER NOC, VOLTAGE AT THIS TOWER SITE ONLY 109 ON EACH LEG. WHEN A/C KICKS ON, IT CAUSES GENERATOR TO KICK ON AS WELL // POLE NUMBER IS EITHER 809-338 OR 809-D2-871, NOC REPRESENTATIVE SHOWED 2 POLE NUMBERS. SAME LOCATION BUT DIFFERENT CKTS//NO OUTAGE TILL L/F OPENED OPENED 14:30 - CLOSED @ 16:30. SH // COD-12 ISO LF 38830809000687 VER/HFP L3/HFP
7716 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-02-10 10:18 | 2011-02-10 15:06 | 5 | 288 | 55867-1 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 XFORMER, NO TRUCKS TO POLE , MAY GET YARD DOG IN.. NEED TO COME IN OFF PONDEROSA DR. 16033 ADDRESS. //NEED TO GET TRACK MACHINE TO CHANGE XFMR///FETR SHOULD BE OK @ 15:30//CHANGED BAD XFMR///VOLT CHECKED OK///COD 5? PER SERVICER IDC XXXX
7717 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-04-03 16:30 | 2014-04-03 18:00 | 16 | 90 | 4560721 | 1440 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 45-43 HOT TAP BROKE REPAIRED VER/CRB IDC XXXX
7718 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-12-15 09:23 | 2022-12-15 21:27 | 2 | 724 | 4263141 | 1439 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | replacrd ug service
7719 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-06-21 20:31 | 2011-06-22 20:30 | 1 | 1439 | 4375531 | 1439 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | WE HAD BAD 4/0 UNDERGROUND AT THIS LOC, HAVE 121 VOLTAGE ON ONE SIDE, AND 37 ON THE OTHER, ACROSS THE TWO HOT ONES, WE HAD 94 VOLT, CREW REQ, NEED TO LOC BAD CABLE AND MAKE REPAIRS, CUST DID NOT WANT HIS POWER SHUT OFF, TILL THEY COME TO FIX THIS, MATERIAL SPLICE FOR UNDERGROUND SEC. AND 4/0 WIRE RELEASED BY CREW 078S06//ONLY ONE CUSTOMER HAS PARTIAL POWER.//GAB// VER/DBM IDC XXXX
7720 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2008-05-11 12:48 | 2008-05-11 18:47 | 4 | 359 | 60987-1 | 1436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF NEEDS CREW RELEASED BY CREW 078S08------REPAIRED HOT TAP POWER ON @ 18:47 VER/KEP IDCC CNT1 XXXX
7721 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-09-16 17:25 | 2010-09-17 01:21 | 13 | 476 | 50778-1 | 1436 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT 38830303000232, ISOLATED AT 38830303000206, 40-5 POLE WITH 4/0 URD SERVICE, 2 1/2 CONDUIT, TRUCK OK, CREW CONTACTED, FUSE CLOSED AT 18:45 RELEASED BY CREW 078S05/CREW ON SITE/DIFF JOB/U/G COMPLICATIONS/FETR0100-9/17/10//VEM/NEW FETR 0130/VEMREPAIRS MADE AND CUST RESTORED 0121/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 IDC XXXX
7722 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-01-14 08:48 | 2012-01-14 13:35 | 5 | 287 | 4260541 | 1435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | ALL 3 RECLOSERS SEEM TO BE IN ON POLE 263-377. I AM GOING BACK ON MOUNTAIN AND MAKE SURE THE TRANS. SERVING THE AEP TOWER IS ENERGIZED. OPENED "A" PHASE SWITCH AT POLE 264-49 TO ISOLATE BROKEN INSULATOR ON POLE#264-50 . WE OPENED THE OTHER 2 PHASES ON POLE 264-49 AT 12:30, CHANGED INSU VER/KEP IDCC PN377 XXXX
7723 | Hazard | 3309302 | VICCO | JEFF | 2015-03-19 16:52 | 2015-03-19 20:17 | 7 | 205 | 4210551 | 1435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BROKEN, NEED 1-8FT CROSSARMAND BRACES, 2- STRAIGHTLINE ARM PINS AND INSULATORS, C/O AND ARRESTOR AND ARM BRKT. 3-MAN LINE CREW, FLAGGERS./// OPENED REC ON POLE 323-D-790 AT 18:06 AND OPENED LOWSIDE C/O TO GET VISIBLE OPENING AND TAGGED IN GREG SHOUSE NAME. RELEASED BY CREW 077S08 AJBC CDC86
7724 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-06-18 20:07 | 2008-06-18 20:42 | 41 | 35 | 50556-1 | 1435 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3008701//SERVICER OPENED LINE IN ORDER TO MAKE REPAIRS TO A PIN INSULATOR AND RESAG PRIMARY//SEE ORDER 50503-1//COD 41// VER/DBM AJB
7725 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-07-22 21:48 | 2011-07-23 09:45 | 2 | 717 | 4592211 | 1434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 19.9 ONE MAN BIG BUCKET CALLED DUTY SUV. HOLD TILL MORNING RELEASED BY CREW 075H01BAD 15 KVA 19.9 ONE MAN BIG BUCKET CALLED DUTY SUV. HOLD TILL MORNING REPLACED BAD TRANSFORMER POWER RESTORED @09:45 IDC XXXX
7726 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2014-02-04 19:26 | 2014-02-04 23:25 | 6 | 239 | 4348821 | 1434 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | .BAD CUTOUT ON POLE 392-63. POLE IS MANUEL NEED 1 MAN TO HELP. CLOSED CUTOUT @ 23:25
7727 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2022-02-20 16:12 | 2022-02-20 19:11 | 8 | 179 | 4520261 | 1432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole:1184020 3 phase pole 8ft arm straight line 40-5 windstream has owner ship of pole 75 kva on pole open wire and 3 service drops on pole Released by crew 078S09 Opened xfmr on 118-c1-4020 at 16:12. Closed at 19:11. Ticket complete
7728 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-08-31 13:29 | 2013-09-01 13:21 | 1 | 1432 | 4805571 | 1432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON 37830072C00626// WILL REFUSE// BAD 50KVA//120/208 VOLTAGE//CENTER XFMR//TRUCK APP.// THIS IS AT GLAM SALON RELEASED BY CREW 074S05. VER/CRB L/3 CRB IDC XXXX
7729 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-12-23 10:58 | 2009-12-24 10:50 | 1 | 1432 | 60197-1 | 1432 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE MELTED OUT..REFUSED TRANSFORMER...BB
7730 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-02-02 13:52 | 2009-02-03 13:43 | 1 | 1431 | 54706-1 | 1431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALLED CUSTOMER AND THEY ARE STILL EXPERIENCING THIS PROBLEM AS OF 2022 2-2-09// SSERVICEMAN SPLICED OUT SERVICE ,LOOSE CONNECTION.AND SPLICED IN NEW SER. POWER BACK ON. RELEASED BY CREW 078E09
7731 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2022-10-30 20:12 | 2022-10-30 22:51 | 9 | 159 | 4079391 | 1431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required 65t
7732 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2017-06-19 00:08 | 2017-06-19 08:05 | 3 | 477 | 4994581 | 1431 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 1123-4525/CLOSED IN @0805/PLEASE CLOSE TICKET/MLH
7733 | Hazard | 3309302 | VICCO | JEFF | 2014-02-15 12:52 | 2014-02-15 13:05 | 110 | 13 | 4389581 | 1430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEUTRAL DOWN BETWEEN STEPDOWN AND REC. CALLED TIM SMITH TOLD HIM WHAT I GOT HE WILL COME AND PUT IT BACK UP WHEN HE CLEARS ON HIS TROUBLE. RELEASED BY CREW 077S08 OPENED RECL;S ON POLE 347 16 AT 12;52 CLOSED BACK AT 13;05 POWER RESTORED // CONDUCTOR PULLED OUT OF SLEEVE /// COD-108 ISO OCR @ 37830347A00316 VER/HFP L3/HFP AJB
7734 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-12-31 11:44 | 2018-12-31 11:55 | 130 | 11 | 4614741 | 1430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT 37820050000155,HAVE TO REPLACE IT.CANT CLIMB POLE AS IS.WILL HAVE TO OPEN LINE,AT LEAST THAT PHASE,POSSIBLY ALL.CREW ENROUTE TO HELP.// NO OUTAGE TILL GOAB OPENDED SWITCH 37820026000148 OPEN @ 1144 CLOSED @ 1155 BAD CUTOUT 50-155,HAVE TO REPLACE IT.CANT CLIMB POLE AS IS.WILL HAVE TO OPEN LINE,AT LEAST THAT PHASE,POSSIBLY ALL.CREW ENROUTE TO HELP.OPENED 26-148@11:44,CLOSED@11:54///////////MADE ALL REPAIRS&RESTORED
7735 | South Williamson | 3411401 | DEWEY | INEZ | 2017-03-02 17:05 | 2017-03-03 16:55 | 1 | 1430 | 4505431 | 1430 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BUENED UP AT XFMR ///REPAIRED CONNECTIONS//RESTORED AT 16:55//COMPLETE//EM
7736 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-02-15 15:00 | 2013-02-15 15:38 | 133 | 38 | 4822251 | 1429 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I OPENED A SINGLE PHASE RECLOSER ON POLE 426-685 AT 15:00 TO ISOLATE A BAD CUTOUT ON POLE 426-35 AND CLOSED BACK IN AT 15:09. WE CHANGED CUTOUT ON POLE 426-35 AND CLOSED IT BACK AT 15:38 CUSTOMERS ON THIS RECLOSER SHOULD BE ON 426-685 OUTAGE 4822251 HAS CUSTOMER OUTAGES ON IT MD FILED, ALSO SENT NOTE TO MIKE LEWIS VER/KEP IDC XXXX
7737 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-12-08 21:38 | 2015-12-08 22:46 | 21 | 68 | H4519331 | 1428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD 77//LOOP ON38830020A41539 BURNT OPEN// RELEASED BY CREW 078S07---BURNT LOOP--CREW TO JOB SITE TO MAKE REPAIRS//MADE MDC ON POLE 20-A4-1537 TO SHOW 3 L/F INSTEAD OF 2//COD 77//LOOP ON38830020A41539 BURNT OPEN// RELEASED BY CREW 078S07---BURNT LOOP--CREW TO JOB SITE TO MAKE REPAIRS---OPENED OTHER 2 OCR A& C ON PL 20-3024 AT 21:38 A& C COD 21 CLOSED 2246 VER/CRB AJB
7738 | Pikeville | 3408101 | SALISBURY | PRINTER | 2020-01-12 12:27 | 2020-01-12 16:25 | 6 | 238 | 4288271 | 1428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot-line clamp burnt off on 1123-57. Installed new 300 amp switch on 1123-57 and closed @ 16:25. sh//cod 6
7739 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-11-07 07:30 | 2013-11-07 11:28 | 6 | 238 | 4017671 | 1428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ,FIRE IS NOW OUT ,OPENED LINE FUSE AT PL, 91-D-122 AT 7;30 FAULT POLE IS 91-D-197 TRUCK O,K POLE IS READY TO FALL 50-2 RELEASED BY CREW 078S09,,CREW ON SITEREPAIRS MADE, LOWERED FACILITIES, ALL POWER RESTORED VER/CRB L3/HFP
7740 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-07-17 06:24 | 2011-07-17 14:20 | 3 | 476 | 4554911 | 1428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD 25 KVA SINGLE BUSHING, 7200 120/240 NEED L/C, BUCKET CAN BE USE, HAVE 3 CUST WITHOUT POWER AT THIS TIME DIRECTION, TURN AT CAR WASH GO STRAIGHT TO WRIGHT LANE, FIRST POLE RELEASED BY CREW 078S06/ XFMER REPLACED ALL POWER RESTORED @ 14:20 J. HEMLEPP 078H05//VER/CRB
7741 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-04-10 17:18 | 2015-04-10 23:15 | 4 | 357 | 4306141 | 1428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMER ON POLE 851-368///NEED 7200 25KVA XFMER, CUTOUT AND ARM MOUNT BRACKET///TALKED TO ROGER MAYNARD HE IS SEND A COUPLE MEN TO HELP///CHANGED XFMER///CLOSED @ 23:15///COMPLETE BR VER/KEP
7742 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-06-17 11:55 | 2009-06-17 12:12 | 84 | 17 | 59080-1 | 1428 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP EMERGENCY OUTAGE TO REPLACE DEFECTIVE CUTOUT COD-84 ISO 38830502000209 OFF 1155 ON 1212 L3/HFP
7743 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-05-25 16:07 | 2020-05-26 04:00 | 2 | 713 | 4904481 | 1426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout will require a big bucket to change or hooks, be close n reaching with squirt boom, cutout only thing needed Released by crew 078M06 // cod 2
7744 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-11-11 17:42 | 2020-11-12 05:35 | 2 | 713 | 4664271 | 1426 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cracked c/o top to bottom--nbt--crew req--ds111120 Released by crew 078S01 changed cut out t lewis
7745 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2012-11-09 09:20 | 2012-11-09 10:35 | 19 | 75 | H4376041 | 1425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY CONDUCTOR BROKE AT STIRRUP. WORKING TO ISOLATE - CREW ENROUTE TO MAKE REPAIRS. OPENED SWITCH ON 38830786A00110 @ 9:20 TO ISOLATE. REPAIRS COMPLETE. CLOSED SWITCH ON 786-110 @ 10:35. CLOSED RECLOSER ON 785-1266 @ 10:40 RESTORING REMAINING OUTAGED CUSTOMERS. SH ///VER/CRB L/3 CRB IDCC DUP TO OPEN SWITCH XXXX
7746 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-11-30 11:49 | 2010-11-30 13:14 | 21 | 85 | 61062-1 | 1425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RECLOSER OPEN ON POLE 38830453000308 PATOLING LINE 1234PM FOUND BAD CUTOUT ON POLE 430-12 ISOLATED CUTOUT MADE RECLOSER ON POLE 453-308 HOT AT 1256PM BAD CUTOUT CHANGED AND POWER RESTORED AT 1314 RELEASED BY CREW 078S11//COD 21// VER/DBM IDC XXXX
7747 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-05-17 19:58 | 2022-05-18 00:43 | 5 | 285 | 4904981 | 1425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | The line fuse on pole 555-18 is open with a bad pole top insulator on pole 555-B-42, calling for a big bucket. No grounds or tags placed. Released by crew 077S04
7748 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2010-05-02 19:10 | 2010-05-02 20:45 | 15 | 95 | 54338-1 | 1425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34926684 POLE 1147-410 BAD CUTOUT//MADE MD//VER/CRB IDC XXXX
7749 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-12-14 01:30 | 2010-12-14 06:15 | 5 | 285 | 66354-1 | 1425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. I THINK WE JUST HAVE 3 CUSTOMERS OUT. TRANSFORMER IS BURNED UP. TIM HALL IS SENDING HELP. WE CHANGED TRANS. AND CLOSED IT IN AT 06:15 VER/ARN IDC XXXX
7750 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2022-06-13 21:52 | 2022-06-14 05:47 | 3 | 475 | 4078941 | 1425 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 115B-2006,,, crew required. Released by crew 078H12///Replaced bad 50KVA///Complete BR
7751 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-06-25 20:18 | 2018-06-26 08:10 | 2 | 712 | 4666511 | 1424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Hold for tomorrow sts transformer fuse pull into
7752 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-08-04 12:51 | 2022-08-05 12:35 | 1 | 1424 | 4674231 | 1424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 135-C4-238 is washed out on creek bank and laying on house//// cut 1/0 lash loss on pole 135-155//// going to be crew required///// and send a copy to DAN MUSIC///// customers phone number 946-2292... 477-9306 Released by crew 074S03
7753 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-03-12 13:28 | 2014-03-12 17:30 | 7 | 242 | 4471811 | 1424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BURNT POLE OFF 14 ABOVE XFMR. CREW ENROUTE TO REPAIR. INSTALLED NEW 25T LINE FUSE TO PROTECT TAP TO XFMR 859-25 AND LEFT ISOLATED. CLOSED 25T LINE FUSE TO XFMR 835-213 @ 16:00 RESTORING THAT XFMR. RELEASED BY CREW 076S02// CREW STARTING REPAIRS// CLOSED NEW CUTOUT ON 835-35 AT 17:30 RESTORING THE REST OF CUSTOMERS. ENTERED MD VER/HFP L3/HFP
7754 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-08-22 03:08 | 2011-08-22 15:00 | 2 | 712 | 4740511 | 1424 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL BE CHECKED FIRST THING IN THE MORNING--BAD TRANSFORMER-NEED BUCKET--15 KVA 7200 RELEASED BY CREW 077S10 REPLACED BAD TRANSFORMER //VER/CRB IDC XXXX
7755 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2011-04-25 10:07 | 2011-04-25 13:05 | 8 | 178 | 64048-1 | 1424 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 FUSE OUT INTRANSFORMER BANK-- BAD 25 KVA TRANSFORMER IN BANK/ 2 TRANSFORMER DELTA BANK 120/240 208 HIGH LEG--CREW REQUIRED--SEND TO B FRALEY RELEASED BY CREW 078S07//COD 8// VER/DBM IDC XXXX
7756 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-05-31 15:13 | 2011-06-01 14:56 | 1 | 1423 | 4214761 | 1423 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | STS WR # 40180205 // UNDERGROUND NOT MAPPED CORRECTLY PER SERVICER CREW WILL HAVE TO THUMP OUT LINE AND TRACK IT DOWN, TEC NEEDS TO GET THIS PLOTTED CORRECTLY AND GET CORRECTIONS TO MAPPING----WILL HAVE TOO REPLACE UG CABLE RELEASED BY CREW 078H01 VER/HFP L3/HFP IDC XXXX
7757 | Pikeville | 3421001 | BREAKS | CITY | 2010-02-19 13:18 | 2010-02-20 13:00 | 1 | 1422 | 59163-1 | 1422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICE KNOB BROKEN.GATE LOCKED. CANNOT GET IN. SERVICE IS ABOUT TEN FEET FROM THE GROUND. THE GATES MAYBE OPEN IF THEY ARE WORKING HERE TOMORROW. THIS CAN HOLD TO MONDAY IF NEED BE.....DAH RELEASED BY CREW 074S08I HAVE A BAD CUTOUT ON POLE 37820220B00604 AND THIS IS ALSO WHERE THE HOUSE KNOB IS BROKEN I WILL REPLACE BOTH CUTOUTS ON THIS POLE AND REPAIR THE HOUSE KNOB. TIM MCCOY//ISO 37820220B00604//COD 1// VER/DBM IDC XXXX
7758 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-04-03 05:59 | 2015-04-03 09:56 | 6 | 237 | 4262221 | 1422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE IS OPEN ON 1146B0-150 PATROLLING LINE, CLEARED 2 ARRESTERS ONE ON 38830018000163 & 39831146B00191, APR AT 0956 CLOSE TICKET//COD 6//AED CREATED// VER/DBM L3/DKGXXX
7759 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-07-09 16:03 | 2017-07-09 20:00 | 6 | 237 | 4099651 | 1422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER//NO ANSWER// CREW REQ, BAD 25 KVA, SINGLE BUSHING, 7200/120/240, CAN USE TRUCK FIRST TRANSFORMER AFTER CROSSING RAILROAD TRACKS RELEASED BY CREW 078S06..CREW ON SITE,,REPLACED CUTOUT AND XFMR,,ALL POWER RESTORED VER/CRB SJG
7760 | Pikeville | 3409502 | BURDINE | LEVISA | 2014-07-15 02:43 | 2014-07-15 10:37 | 3 | 474 | 4246411 | 1422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WILL WORK DURING NORMAL WORK HOURS BAD ARRESTER ON POLE 336-13.
7761 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-09-08 18:12 | 2011-09-08 20:15 | 44 | 123 | 4849601 | 1422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED FUSE TO SAFELY ISOLATE A BURNING POLE 45-3673 BURNT OFF TEP REPAIRED SEND TO TEC INSTALLED 20T LINE FUSE ON 45-3502 MD FILED VER/KEP IDC XXXX
7762 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-07-27 22:18 | 2012-07-28 02:15 | 6 | 237 | 4854011 | 1422 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F BLOWN,BAD CUTOUT,WILL REPLACE,HAD TO PICK UP CUTOUT//////REPLACED AND RESTORED,ACTUALLY RESTOREDE AT 02:15,COMPUTER PROBLEMS//COD 6// VER/DBM
7763 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-10-04 20:59 | 2010-10-04 23:21 | 10 | 142 | 56876-1 | 1420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR# 37176730 //NO CREW REQUIRED PLACE ARRESTOR IN ABNORMAL //VER/CRB IDC XXXX
7764 | South Williamson | 3411401 | DEWEY | INEZ | 2022-04-03 01:10 | 2022-04-03 13:00 | 2 | 710 | 4717171 | 1420 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Failed 19.9 TR crew will need to replace it
7765 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-07-09 07:24 | 2008-07-09 15:17 | 3 | 473 | 65438-1 | 1419 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA RELEASED BY CREW 077S01 COD-3/// CHANGED XFMR POWER RESTORED VER/HFP IDC XXXX
7766 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-02-20 09:00 | 2020-02-20 11:09 | 11 | 129 | 4419941 | 1419 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Opened xfmr at 9:00 to replace cutout and discovered that xfmr is bad. Crew enroute to replace. Replaced 50kva xfmr, cutout bracket, cutout & arrester. Restored @ 11:09. sh L3/HFP
7767 | Pikeville | 3411801 | JOHNSCREEK | META | 2013-07-07 08:32 | 2013-07-07 14:26 | 4 | 354 | 4478611 | 1416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW REQD(3MEN),#2 ACSR P&N DOWN,CAN POSSIBLY USE TRUCK ALTHO GRND MAY BE TOO SOFT RELEASED BY CREW 074S06 BAD EPOXILATOR INSULATOR ON ANGLE POLE ON AT 14:26//COD 4// VER/DBM IDC XXXX
7768 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2019-01-04 13:46 | 2019-01-04 19:40 | 4 | 354 | 4628291 | 1416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C phase line fuse blown on pole 449-29, bad cutout on pole 449-109 Released by crew 077S11 bad 25 kva manual power restored at 19:40
7769 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2020-11-26 01:27 | 2020-11-26 07:00 | 17 | 333 | 4723981 | 1416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TR open at 39831148B10852 due to failed cutout pole burnt off back yard crew required/send to reynolds Released by crew 078S03 opened line fuse at 39831148B10724 from 0610-0700 (additional 15 CC) all restored at 0700
7770 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-07-08 01:44 | 2022-07-08 13:32 | 2 | 708 | 4426311 | 1416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout/crew reqd/truck ok/send to K Griffith Released by crew 078S04 Closed at 13:32 Ticket complete.
7771 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-03-31 17:32 | 2016-03-31 21:28 | 6 | 236 | 4011861 | 1416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 126-127, TRUCK ACCESSABLE,19.9KV RELEASED BY CREW 077M02
7772 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-07-20 16:38 | 2010-07-20 19:35 | 8 | 177 | 54131-1 | 1416 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BARREL BURNED UP, WILL REPLACE CUTOUT AND TRY TO REFUSE TRANSFORMER.//VER/CRB IDC NOT SURE WHEN POWER ACTUALLY WENT OUT XXXX
7773 | Cannonsburg | 3001401 | LOUISA | CITY | 2014-08-25 08:30 | 2014-08-25 13:13 | 5 | 283 | 4420491 | 1415 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | FUSE TAIL BROKEN, CUTOUTS AND ARRESTERS NEED REPLACED, D WHEELER IS I CHANGED ALL CUTOUTS AND ARRESTERS IVE GOT A BAD 50 KVA STOREROOM IN ROUTE WITH NEW KVA CHANGED KVA POWER RESTORED AT 13;13 PLEASE CLOSE TICKET THANKS DWW// COD 5// VER/ ADH
7774 | South Williamson | 3411401 | DEWEY | INEZ | 2013-09-23 18:52 | 2013-09-23 23:35 | 5 | 283 | 4880681 | 1415 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 19.9 XFMR 0N POLE 649-300//NEED COUPLE MEN AND BIG BUCKET // RELEASED BY CREW 079S01BAD 50 KVA 19.9 XFMR 0N POLE 649-300//NEED COUPLE MEN AND BIG BUCKET // REPAIRS MADE RESTORED AT 23:35 VER/PDP IDC XXXX
7775 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-12-22 18:17 | 2008-12-22 21:39 | 7 | 202 | 62774-1 | 1414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001401//,,,,BLOWN TRANSFORMER OIL ALL OVER POLE STEAM COMING OUT OF TOP OF TRANSFORMER,,,TRANSFORMER IS A 15KVA NEEDS TO BE 25KVA POLE IS TRUCK ACCESSIBLE YOU WILL END UP BLOCKING OFF ONE END OF STREET RELEASED BY CREW 078S02/CREW ON SITE/FETR2159/POWER RESTORED 2139/PLEASECLOSETICKET/THANKS/VEM//COD 7// VER/DBM L3/KEP IDC XXXX
7776 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-11-24 09:37 | 2008-11-24 09:44 | 202 | 7 | 51527-1 | 1414 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401//OPENED RECLOSER TO MAKE UP LOOPS ON ORDER 51451-1 VER/KEP MLR OK IDC XXXX
7777 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-05-29 14:32 | 2019-05-30 14:05 | 1 | 1413 | 4362911 | 1413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | guy wire rusted loose and laying on xfmr riser//guy has no breaker in it//i cleared it up and stapled dwn secure to pole//please send to technician group to have new anchor and breaker installed//restored at 14:05//complete//em
7778 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-07-26 11:05 | 2009-07-27 10:38 | 1 | 1413 | 65941-1 | 1413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEUTRAL BROKEN AND LYING ACROSS JD VANCE ROAD ,CUSTOMER AFRAID TO CROSS,I WILL STAND BY UNTILL SOMEONE COMES TO CLEAR UP AND MAKE SAFE,,,MATERIAL NEEDED CUTOUT AND ARRESTER(19.9) 18 FIBERGLAASS T BRKT,, RELEASED BY CREW 077E01 VER/DKG L3/DKG IDC XXXX
7779 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-06-19 11:45 | 2016-06-20 11:18 | 1 | 1413 | 4388281 | 1413 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE OUT ON TRANSFORMER POLE// TRANSFORMER BAD FEEDS OIL WELL CUSTOMER SAID WE CAN CHANGE IT MONDAY ON REGULAR TIME// ISO 38830852000083/ COD 2// REPAIRS COMPLETE// RESTORED AT 11:18 RDM// ONLY 1 CUSTOMER OFF TRANSFORMER VER/CRB
7780 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-12-23 11:28 | 2017-12-23 17:21 | 4 | 353 | 4667531 | 1412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout to side tap at pole 37820009D00241. I can make repairs. Also found two spans of #2 AAA primary down, pole top is broke out at 37820009D00243, possibly can lower the primary. Can use bucket truck, need three man line crew and manual tree crew. Released by crew 079S02 on at 17:21
7781 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-07-26 14:08 | 2009-07-26 20:01 | 4 | 353 | 51881-1 | 1412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUT OUT VER/KEP L3/KEP IDC XXXX
7782 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2011-03-23 16:08 | 2011-03-23 21:12 | 14 | 304 | 57171-1 | 1412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE 655-320 BURNED OFF DUE TO BAD CUTOUT..ISOLATED ON 655-146..RE FUSED 655-107 (CENTER PHASE ONLY) AT 17.15..EVERYONE BACK ON EXCEPT 2 CUSTOMERS.CATHLOTIC CH AND PARSONAGE..BACK ON 21.12//VER/CRB IDC XXXX
7783 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-09-29 04:22 | 2020-09-29 10:15 | 4 | 353 | 4505461 | 1412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.line fuseout on 771-A3-6 due to failed trans cutout on 771-A3-429 that is not serving anyone.isolated cutout.restored poer at 10:15
7784 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-06-13 05:04 | 2018-06-13 10:57 | 4 | 353 | 4594761 | 1412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | called customer, neighbor is out as well as a couple of streetlights///customer has checked breaker//Dispatched in accordance with KYPCo Late Night Callout Guidelines//TRANS NEVER OFF //COD 4// te Night . tree fell @ 37830020000153 have at least 2 spans of peimary & netural down .need line crew tree crew# 2 aul ,sleeves pole top pin 7200 ins//
7785 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2013-10-18 13:37 | 2013-10-18 19:30 | 4 | 353 | 4946651 | 1412 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED 40/6 POLE BACK YARD NO TRUCKS YARD DOG /DEAD END POLE WITH TRANSFORMER 15KV LINE FUSE OPEN ON 174-51/ISOLATED TAGGED AND GROUNDED FOR DDC RELEASED BY CREW 078S03 VER/SEF
7786 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-06-11 17:29 | 2012-06-11 23:45 | 6 | 376 | 4901901 | 1410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED CAN CUT POLE OFF /TRUCKS OK/ISOLATED ON 171-33/GOING TO LINE FUSE THAT IS OUT/20T LINE FUSE 171-30 BACK ON AT 1903 HRS RELEASED BY CREW 078S03 REPAIRS MADE.LAST CUSTOMERS ON AT 23:45..BLR //VER/GAH IDCC PN74 XXXX
7787 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-04-13 20:08 | 2009-04-14 00:50 | 5 | 282 | 52039-1 | 1410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS. ON POLE 41-51 NEED CREW WITH NEW TRANS. CAN USE TRUCK I THINK WE SHOULD UP-GRADE TO A 37.5 OR A 50 KVA 7200/120-240 OVER LOAD CONDITION LIKELY./COD 5// CREW HAS ARRIVED BEGINING WORK TRANS. CHANGED RE-ENERGIZED AT 00:50 VER/PDP IDC XXXX
7788 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-07-29 12:07 | 2009-07-29 14:28 | 10 | 141 | 61685-1 | 1410 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 078S07 RELEASED BY CREW 078S09RELEASED BY CREW 078S07 CUT L/A IN CLEAR ON POLE 1123-560 BACK TO FUSE POLE 1123-254 REPLACING FUSE ADDED 2 MISMAPPED CUSTOMERS AND FILED MD VER/KEP L3/KEP IDC XXXX
7789 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2011-04-11 23:17 | 2011-04-12 00:45 | 16 | 88 | 55431-1 | 1408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 771-510//BAD CUTOUT ON POLE 771-409//REPLACED CUTOUT//RESTORED AT 00:45///20T FUSE//COMPLETE//EM//VER/CRB IDC XXXX
7790 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2021-08-18 09:23 | 2021-08-18 11:31 | 11 | 128 | 4104601 | 1408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened xfmer @ pole 38830044D47508/span of open wire down from pole 38830044D47559 to pole 38830044D47583 1/0. also cutout broke/repairs made. pls close. tre
7791 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-12-01 16:14 | 2014-12-01 22:06 | 4 | 352 | 4822641 | 1408 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | VINES ON POLE 149B-17 , REMOVED VINES . FOUND LOOP INTO ON POLE 149B-16 . GATE LOCKED CUST. LIVES IN TOWN GOING TO COME UNLOCK WILL TAKE ABOUT 30 MIN. TO GET HERE . CLOSED FUSE ON POLE 149B-79 @ 22:06 COD-4 ISO LF 37830149B00079 VER/HFP L3/HFP
7792 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-02-25 23:32 | 2022-02-26 13:15 | 9 | 823 | 4547471 | 1407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr manuel on hill, need 15 kva 19.9, also need to change cutout and t-bracket, need flaggers, no ROW needed, on hill just past Mason Hollow on 406 opened line fuse at 12:02 power restored at 13:15 Released by crew 077H02
7793 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-11-15 14:10 | 2019-11-15 20:11 | 134 | 21 | 4037941 | 1407 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | DOL 971262/ Load Transfer/ 12kV Bus regulators at Breaks have failed//voltage is floating high, need to add load from other sources to bring voltage down//cod 67
7794 | Pikeville | 3409502 | BURDINE | LEVISA | 2016-12-24 04:13 | 2016-12-24 05:27 | 19 | 74 | 4231901 | 1406 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE#33-138 WILL PATROL/// BAD CUTOUT ON POLE # 335-208 WILL CHANGE/// CHANGED BAD CUTOUT AND CLOSED LINE FUSE IN @ 05:27 AND RESTORED SERVICE VER/TOM L3/TOM
7795 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-12-08 12:50 | 2013-12-08 17:31 | 5 | 281 | 4116271 | 1405 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAB 7200 CUTOUT ON POLE 186-197, NO TRUCKS TO POLE . NEED LINE CREW. FIRST XFORMER UP PAST LINE FUSE ON THE LEFT. RELEASED BY CREW 078S01/ FETR / 18:30 JEH/ REPAIRS COMP. POWER RESTORED @ 17:31// JEH VER/SEF L3/HFP
7796 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-09-08 22:15 | 2009-09-08 22:33 | 78 | 18 | 57080-1 | 1404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW HAD TO OPEN RECLOSERS TO ALLOW THEM TO SAFELY REPLACE A DEFECTIVE CUTOUT THAT HAS NO TRUCK ACCESS (CLIMB JOB). RELATED TO ORDER 56625-1 // /OPENED RECLOSERS AT POLE 153-273 AT 22:15 AND RESTORED AT 22:33 L3/HFP IDCC CNT80 XXXX
7797 | Hazard | 3302704 | HAZARD | KENMONT | 2018-01-03 01:46 | 2018-01-03 03:43 | 12 | 117 | 4700751 | 1404 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | lead burnt off csp xfmr
7798 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2009-06-10 00:04 | 2009-06-10 05:55 | 4 | 351 | 63761-1 | 1404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR. DUTY SUPERVISOR NOTIFIED- CREW ENROUTE TO CHANGE. CREW ON SITE - REPAIR IN PROGRESS. RESTORED AT 05:55. SH VER/PDP IDC XXXX
7799 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-05-22 22:13 | 2010-05-23 00:10 | 12 | 117 | 66426-1 | 1404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116703/// STS 35237043 BROKEN CUTOUT IDCC CCU XXXX
7800 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-01-07 06:01 | 2020-01-07 10:17 | 24 | 256 | 4219321 | 1404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines////.Cutout broke on xfm/// This is about 100 up on side of hill ///will need some help Paul Layne is getting some help headed this way// Opened line fuse 195-16 @ 09:58 to change bad cutout/// restored @ 1017
7801 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-10-22 08:30 | 2011-10-22 14:21 | 4 | 351 | 4009651 | 1404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR C/O BURNT UP, WILL NEED HELP TO CHANGE THIS OUT.//// CHANGED OUT XFMR C/O, POWER RESTORED COD-4 ISO TF 38831059D00047 VER/HFP L3/HFP IDC XXXX
7802 | Hazard | 3308002 | JACKSON | PANBOWL | 2009-08-09 17:23 | 2009-08-09 19:11 | 13 | 108 | 50800-1 | 1404 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3308002//FUSE BROKE//COD 13// VER/DBM IDC XXXX
7803 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2016-07-14 17:04 | 2016-07-15 16:26 | 1 | 1402 | 4634241 | 1402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER. LINE CREW AND FLAGGERS; REPLACE XFMR; PWR RESTORED AT 1600HRS; EBP RELEASED BY CREW 078E02 VER/CRB
7804 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2015-08-13 14:20 | 2015-08-14 13:42 | 1 | 1402 | 4132151 | 1402 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINE FUSE OUT ON POLE 942B41444 TRIED FUSE CAME BACK OUT GOING TO ISOLATE PRIMARY UNDERGROUND TO DETERMINE WHERE TROUBLE IS FOUND BAD UNDERGROUND CABLE NO TRK ACCESS GOING TO LEAVE OUT TILL TOMORROW WHEN CREW CAN GET SOME EQUIPMENT TO DO JOB RELEASED BY CREW 079H03..REPLACED THREE PHASE UNDERGROUND CABLE
7805 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2012-01-16 03:41 | 2012-01-16 11:28 | 3 | 467 | 4263511 | 1401 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 318C-228 BAD CUTOUT HAS BURNT XFMER POLE INTO, WILL GET CREW. CAN WRK WITH TRUCK, 40/4 POLE, PTP, INS, C/O, ARR, T-BRK..19.9KV..SEND TO PAUL HICKMANS CREW.. RELEASED BY CREW 077H09 REPLACED POLE AND CUTOUT RESTORED POWER AT 1128 CREW 077H01 ///VER/CRB IDC XXXX
7806 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2022-03-24 16:48 | 2022-03-24 20:12 | 10 | 204 | 4670701 | 1401 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 38830237000143 c/o broke -- crew req -ds032422 // Repairs made closed at 20:12. Ticket complete. // cod 1//maps are not correct.. note send to techs to get mapping field checked//take off pole 237-143 hs one pole tap on it with 1 customer//
7807 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-07-08 16:18 | 2015-07-09 02:50 | 7 | 632 | 4746891 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE 185-151 BACK IN @18:26 ////BAD 50 KVA CSP ON POLE 185-87 ISOLATED //// NO TRUCKS 4-MAN LINE CREW UP ON THE SIDE OF HILL RELEASED BY CREW 078S05,REPLACED XFMR ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT RELEASED BY CREW 078H19 VER/SEF
7808 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2010-08-16 10:40 | 2010-08-16 11:20 | 35 | 40 | 56362-1 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BASKETT BURNT OFF SOURCE SIDE PRIMARY, REPLACED BASKETT.//COD 35// VER/DBM IDC XXXX
7809 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2017-10-23 09:15 | 2017-10-23 12:10 | 8 | 175 | 4478201 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT.REPLACED BAD CUTOUT& RESTORED POWER 38831052C00213 VER/AWD L3/HFP XXXHFP
7810 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-12-11 08:54 | 2021-12-11 11:49 | 8 | 175 | 4172801 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on transformer pole 174-332
7811 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-07-31 12:31 | 2013-07-31 16:23 | 10 | 232 | 4610131 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKED LIKE FUSE HAD PULLED LOOSE, ALL POWER RESTORED AT 1428. ONE CUSTOMER OUT RELEASED BY CREW 078S11/CREW ON SITE/FETR1700/VEM/SECURED UG FOR EXCAV/POWER RESTORED 1623/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDC XXXX
7812 | Hazard | 3310502 | HADDIX | CANOE | 2014-08-15 13:37 | 2014-08-15 14:12 | 40 | 35 | 4372441 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | CHANGING OUT RECLOSER/// MANUAL SO NEED TO OPEN IT// APPROX. 30 MIN// VER/BOW AJB
7813 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-07-20 16:15 | 2016-07-20 18:35 | 10 | 140 | 4661871 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION , REPAIRED OFF @ 16:15, ON @ 16:35/ ISO 38830044C35052/ COD 10/ VER/BOW
7814 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-12-18 02:30 | 2018-12-18 07:10 | 5 | 280 | 4575871 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks cutout broke on top of pole need observer /199-114 Released by crew 078S03. L3/HFP
7815 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2019-05-12 02:45 | 2019-05-12 08:35 | 4 | 350 | 4255191 | 1400 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 597-1. Changing cutout, All repaires made and apr at 0835 close tuicket. dwest
7816 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-02-23 11:22 | 2015-02-23 15:15 | 6 | 233 | 4074941 | 1398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUSE BLOWN ON POLE # 37830312000003WILL PATROLL//// #4 COPPER PRIMARY DOWN @ POLE # 37830312000005///// NEED 3 MAN LINE CREW /// NO TRUCK TIM HALL IS GETTING CREW TOGETHER//LINE FUSE BLOWN ON POLE # 312-3 WILL PATROLL//// #6A COPPER PRIMARY DOWN @ POLE # 312-5///// NEED 3 MAN LINE CREW /// NO TRUCK TIM HALL IS GETTING CREW TOGETHERLINE FUSE BLOWN ON POLE # 312-3 WILL PATROLL//// #6A COPPER PRIMARY DOWN @ POLE # 312-5///// VER/CRB L3/HFP XXX AJB
7817 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2014-06-11 15:39 | 2014-06-12 14:57 | 1 | 1398 | 4055431 | 1398 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKE 35-5 POLE #195-48 NEED POLE TOP PIN%26INS,CLEVIS%26SPOOL 1 MANUEL TREE CREW %26 6 MAN LINE CREW === 300 TO 400 FT. ON HILL ALL MANUEL WORK. CAN NOT USE TRACK MACHINE RELEASED BY CREW 074H15//SERVICE HAS BEEN RESTORED BOBBY TACKETT VER/ARN
7818 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-03-09 16:10 | 2009-03-10 15:26 | 1 | 1396 | 56669-1 | 1396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | VER/HFP 3001101// MTR: 533515045 JUDD F HUNDLE NEW ACCOUNT ACTIVE AS OF MARCH 2 // NO PENDING DISCONNECT REQUESTS...// HOLD FOR B FRALEY TO WORK TOMORROW--BAD UG PEDASTAL RELEASED BY CREW 078S07 L3/HFP IDC XXXX
7819 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-07-22 00:22 | 2013-07-22 12:00 | 2 | 698 | 4573471 | 1396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / SPOKE W/ CUST, OK TO CK AT DAYLIGHT. SOMEONE FROM RR MUST BE THERE.//CUTOUT BROKE ON POLE 771-61//NEED BUCKET TRUCK//CREW ENROUTE//REPAIRS MADE//RESTORED AT 12:00//COMPLETE//EM//COD 5// VER/DBM IDCC PN63, CNT5 XXXX
7820 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-10-27 10:01 | 2009-10-27 15:50 | 4 | 349 | 56903-1 | 1396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE FUSE OPEN AT POLE 1098-284, A & C PHASES OK, DE-ENERGIZED TAP FROM POLE 38831098C00384 TO POLE 495, NO CUSTOMERS ON 495 ... WILL NEED TO REPLACE CUTOUTS AT POLE 284 ... OPENED A & C PHASES AT 14:50 AND CLOSED ALL PHASES AT 15:50 ... ALL WORK COMPLETE / GXJ VER/KEP L3/KEP IDC XXXX
7821 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2013-08-10 08:06 | 2013-08-10 13:55 | 4 | 349 | 4643891 | 1396 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD AND BURNED POLE TOP OFF///ENOUGHSPACING ON POLE TO CUT OFF AND PUT LONG RIDGEPIN AND MAKE REPAIRS//REPAIRS MADE REST OF LINE IS GOOD//RESTORED AT 13:55//COMPLETE//EM VER/CRB L/3 CRB
7822 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2012-12-25 07:52 | 2012-12-25 09:25 | 15 | 93 | 4515421 | 1395 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | POLE 69-4016 BAD CONN. REPAIRED //VER/GAH IDC XXXX
7823 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2021-10-04 17:40 | 2021-10-04 18:25 | 31 | 45 | 4316381 | 1395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | hot tap burnt up & riser burnt off/repairs made. pls close. tre
7824 | Pikeville | 3401001 | ELWOOD | DORTON | 2014-02-12 07:15 | 2014-02-12 15:00 | 3 | 465 | 4374871 | 1395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. ON POLE 214-104 IS BAD.I AM CALLING FOR HELP. TIM HALL IS SENDING HELP. RELEASED BY CREW 074S01TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. ON POLE 214-104 IS BAD.I AM CALLING FOR HELP. TIM HALL IS SENDING HELP. WE CHANGED A 15 KVA TO A 25 KVA VER/SEF
7825 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2012-01-02 08:36 | 2012-01-02 13:15 | 5 | 279 | 4224371 | 1395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 FUSE OUT IN TRANSFORMER BANK AT PUMP STATION--BAD B PHASE CUTOUT--NEED PRC CREW--TRUCK TO POLE// PLEASE CALL CUSTOMER BACK WHEN REPAIRED *** MIDDLE TR. D JIM LINKOUS CREW WILL WORK THIS CALL.1 FUSE OUT IN TRANSFORMER BANK AT PUMP STATION--BAD B PHASE CUTOUT--NEED PRC CREW--TRUCK TO POLE RELEASED BY CREW 078S07 PLEASE CALL CUSTOMER BACK WHEN REPAIRED MIDDLE TR. D JIM LINKOUS CREW WILL WORK THIS CALL. ( BROKEN CUTOUT LEAD REPAIRED POWER RESTORED AT 13:15)//ISO// COD 3// VER/DBM IDC XXXX
7826 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-02-08 08:36 | 2009-02-08 13:15 | 5 | 279 | 56656-1 | 1395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "B" PHASE OUT / COD-5 /CONNECTOR BURNED INTO ON XFMR SECONDARY RISERCONNECTOR BURNED INTO ON XFMR SECONDARY RISER RELEASED BY CREW 077S04B PHASE OUT / COD-5 /CONNECTOR BURNED INTO ON XFMR SECONDARY RISERCONNECTOR BURNED INTO ON XFMR SECONDARY RISER RELEASED BY CREW 077S04 == REPAIRED CONNECTION ON NEUT ==// VER/TOM L3/TOM IDC XXXX
7827 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-12-07 06:44 | 2016-12-07 11:23 | 5 | 279 | 4172891 | 1395 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | @ 0800 PATROLLING LINE //ATTEMPTED TO CALL STS GOT POLE 38831060C00090 BURNED OFF CALL BRUCE AND GETTING CREW COMING TO LOWER CONDUCTORS // COD-5 ISO LF 38831060C00068 VER/HFP L3/HFP
7828 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-01-23 07:40 | 2018-01-23 16:15 | 14 | 179 | 4764841 | 1394 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer pole 736-1 (35-5) damaged due to cutout failure. Had xfmr 38830736000001 open from 7:40 to 8:30 to put out fire. Crew to replace today - Emergency Dig # 1801230258 issued @ 8:55./ closecd @ 38830737000133 @ 16:15/ opened fuse 38830761000083 @ 1406 and closed fuse 38830761000083 @ 1424 L3/HFP
7829 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-05-19 09:22 | 2008-05-19 13:40 | 6 | 258 | 65794-1 | 1393 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001002//PRIMARY DOWN AT 38830279000002, ISOLATED AT SAME POLE, REPLACED 100T FUSE ON POLE 38830278000010, SINGLE PHASE 6A COPPER, CREW REQUIRED // 6 CUSTOMERS ORIGINALLY OUT ON B PHASE FUSE// 1 RESTORED AT 1105// CUSTOMERS RESTORED @ 1340 IDC XXXX
7830 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2013-04-12 01:54 | 2013-04-12 09:38 | 3 | 464 | 4001341 | 1392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER AFTER HOURS TROUBLE GUIDE LINES THIS WILL BE CHECKED IN THE A.M. LINE FUSE BLOWN ON POLE 421-17, BAD CUTOUT ON POLE 421-19 & 421-20.. REPLACED CUTOUTS RESTORED POWER AT 09:38//COD 3//MD FILED ON MISMAPPED CUSTS// VER/DBM IDC XXXX
7831 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-07-01 19:34 | 2019-07-01 21:30 | 12 | 116 | 4629721 | 1392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Lead out of hot-line clamp on line fuse pole. Hotline clamp was broken. Replaced and restored @ 21:30. Tree at 38830852000229 needs cut (Address 1991 Mash Fk). Please send ROW a note. Thanks, sh L3/HFP
7832 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2022-06-15 18:58 | 2022-06-15 22:50 | 6 | 232 | 4130711 | 1392 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad xfmr in wye/delta bank. Replaced bad xfmr and restored @ 22:50. sh
7833 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-11-30 15:43 | 2016-11-30 17:30 | 13 | 107 | 4151251 | 1391 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON 795-19//CUTOUT BROKE ON POLE 795-84//MAKING REPAIRS//REPAIRS MADE//RESTORED AT 17:30//COMPLETE//EM VER/CRB
7834 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2022-05-27 14:02 | 2022-05-27 16:21 | 10 | 139 | 4967011 | 1390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Lat fuse out @ 163-66.// Arrester blown @ 37830163B00272.//Will be making repairs.//Restored @ 16:21
7835 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-06-07 18:12 | 2011-06-07 22:50 | 5 | 278 | 4259531 | 1390 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ALL CUSTOMERS FEEDING FROM XFMR POLE 70-3521 ONLY RECEIVING 120V, EVEN CUSTOMER ACROSS FROM XFMR. POSSIBLE BAD CONNECTION @ XFMR POLE. NEED SVC TRUCK TO CHECK CONNECTIONS. TRUCK OK. NO FLAGGING REQUIRED. CWB RELEASED BY CREW 078E10 COD-5 VER/HFP L3/HFP IDC XXXX
7836 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-11-17 19:55 | 2014-11-18 07:30 | 2 | 695 | 4738681 | 1390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BURNED POLE38831083C31099 OFF NEED CREW, POLE, AND YARD DOG TO SET POLE DID DAMAGE TO YARD WHEN SETTING RELEASED BY CREW 077S05 VER/SEF L3/DKGXXXC CDC86 THIS OUTAGE IS FOR THE 2 CUSTOMERS THAT WERE OUT FROM THE BEGINNING WITH THE BURNT CUTOUT...SEE 4739901 FOR OPENING RECLOSERS TO CUT LOOPS
7837 | Hazard | 3309301 | VICCO | REDFOX | 2011-11-23 08:10 | 2011-11-23 12:48 | 5 | 278 | 4106531 | 1390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | C PHASE LINE FUSE OPEN ON POLE 326-174, BAD DEADEND INSULATOR ON POLE 350-50 RELEASED BY CREW 077S11REPLACED INSULATORS AND RESTORED POWER AT 1248 ///VER/CRB IDC FOUND OTHER EPOXILATOR INSULATORS ON OTHER POLES CHANGED THEN ALSO XXXX
7838 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-07-18 13:45 | 2013-07-19 01:20 | 2 | 695 | 4548631 | 1390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | USED THE BEAST SHOWS BAD NEU. POSSIBLE IN THE GR.WHERE A TREE STUMP WAS REMOVED CUST HAS HIGH VOLTAGE LEFT XFORM OPEN RELEASED BY CREW 078S04..BAD NUET AND BAD HOT LEG.INSTALLING NEW UG SERVICE. VER/SDB IDC TOF1215, ESTIMATED TIME OFF FOR REPAIR XXXX
7839 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-12-01 07:47 | 2008-12-01 12:25 | 5 | 278 | 53409-1 | 1390 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3001002//POLE FIRE AT 38830401000059, CREW REQUIRED, NEED 45 POLE AND CUTOUT, TRUCK OK. 9811 ST RT 1, JIM LINKOUS WILL BE WORKING OUTAGE. RELEASED BY CREW 078S05 REPLACED CUTOUT AND ARRESTOR CUT OFF TOP OF POLE PLENTY OF CLEARANCE (NO JOINT USE) COD-5 VER/KEP L3/KEP IDC XXXX
7840 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-09-13 14:07 | 2010-09-13 17:00 | 16 | 173 | 66070-1 | 1388 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FUSE OUT ON 380-27, WIRE DOWN ON 356-27 WILL NEED LINE CREW TO PUT WIRE UP... ISOLATED ON 356-27 ENERGIZED LINE UP TO THIS POLE AT 15:28//RESTORING 15 CUST// RELEASED BY CREW 077S11PUT UP DOWNED WIRE POWER RESTORED #4 SOLID COPPER//LAST CUST ON @ 1700// VER/DBM IDC XXXX
7841 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2020-10-17 09:23 | 2020-10-17 15:10 | 4 | 347 | 4563911 | 1388 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at pole //PART POWER TO ALL CUSTOMERS//OPENED TRANS LATER
7842 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2012-06-08 12:27 | 2012-06-08 13:30 | 22 | 63 | 4894171 | 1386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 67-212 BAD LA POLE 67-169 15T LINE FUSE COD-22 ISO LF 38830067D00169 VER/HFP L3/HFP IDC XXXX
7843 | Paintsville | 3401802 | INDEX | HOSPITAL | 2021-06-29 23:06 | 2021-06-30 00:45 | 14 | 99 | 4824921 | 1386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | grd sec lead shorted out against the primary bushing on csp xfmr, p-655-312 blowing line fuse on 655-18.corrected re-fused line fuse at ..00:45/ ISO 38830655A00018/ COD 14
7844 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-05-06 06:03 | 2013-05-06 13:45 | 3 | 462 | 4075301 | 1386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 39831147A00795--INSTALLED GROUNDS AND TAGED TO DDC---NEED CREW--POLE 39831147A00991 HAS BURNT OFF--TRUCK TO POLE--// HOLD TAG PLACED FOR DDC - CONTACT DDC UPON ARRIVALLINE FUSE OUT ON POLE 39831147A00795--INSTALLED GROUNDS AND TAGED TO DDC---NEED CREW--POLE 39831147A00991 HAS BURNT OFF--TRUCK TO POLE--SEND TO B REYNOLDS RELEASED BY CREW 078S07 // ON AT 1345 COD-3 ISO LF 39831147A00795 // PLEASE CLOSE ORDER IDCC TON939, FP NULL XXXX
7845 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-09-30 00:28 | 2015-09-30 08:10 | 3 | 462 | 4292761 | 1386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL LOOK AT ON REGULAR SHIFT PER LATE NIGHT CALLOUT.. BAD C/O DOOR VER/CRB
7846 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-01-20 09:06 | 2011-01-20 11:40 | 9 | 154 | 62930-1 | 1386 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 426-127 WILL NEED BIG BUCKET TO WORK SAFE..OPENED LINE FUSEON 426-326 AT 11:12 (SEE 62993-1) MADE REPAIRS RESTORED POWER AT 11:40//COD 9// VER/DBM IDC XXXX
7847 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-08-20 09:10 | 2011-08-20 13:47 | 5 | 277 | 4733071 | 1385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR ,MANUAL, GOT HELP COMING. 1 CUST. OUT. ENTERED MD..HFP COD-5 ISO LF 37830225D00277 VER/HFP L3/HFP IDC XXXX
7848 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-06-21 15:15 | 2016-06-21 19:52 | 5 | 277 | 4397811 | 1385 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT,REPLACED CUTOUT ALL CUST RESTORED @ 1952 PLEASE CLOSE TICKET THANKS.BT VER/CRB
7849 | Hazard | 3310502 | HADDIX | CANOE | 2014-04-03 18:24 | 2014-04-04 00:10 | 4 | 346 | 4568081 | 1384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830050000091 OVER ON SIDE OF HILL COD-4 ISO LF 37830050000012 VER/HFP L3/HFP
7850 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-08-10 19:28 | 2009-08-11 07:00 | 2 | 692 | 60722-1 | 1384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP ,,,CREW NEEDED BAD 25KVA 7200V TRANSFORMER,,,, TRUCK ACCESSIBLE TRIED IT TWICE RELEASED BY CREW 078S02 COD-2 ISO TF 38830429A46105 L3/HFP IDC XXXX
7851 | Whitesburg | 3401301 | FLEMING | NEON | 2010-06-26 21:34 | 2010-06-27 03:20 | 4 | 346 | 57936-1 | 1384 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NEED HELP FINDING TROUBLE RELEASED BY CREW 075H01 VER/LDA IDC XXXX
7852 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2015-11-22 23:38 | 2015-11-23 11:09 | 2 | 691 | 4479011 | 1382 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN 1/0 BAD VOLTAGE GOOD AT XFMR BAD AT SEC. POLE SEND TO CREW NO TRUCK AT XFMR POLE ACCESS TO FIELD UP CREEKSIDE ROAD----FOUND BAD SERV-N IN 1/0 SECONDARY---MADE REPAIRS---VOLT CK 123-123-246---TBL TKT COMP VER/CRB
7853 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2010-11-30 23:26 | 2010-12-01 10:57 | 2 | 691 | 61534-1 | 1382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL WORK IN THE MORNING OF 12/01 ... A PHASE OUT, PUT CUSTOMER ON B PHASE RESTORED HIS POWER AT 09:35 WILL BE PATROLLING LINE.. HOT LINE CLAMP BURNT OFF AT 539-77 ON A PHASE.. MADE REPAIRS RESTORED POWER AT10:57 COD-2 VER/KEP L3/KEP IDC XXXX
7854 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2010-04-17 06:56 | 2010-04-17 16:30 | 5 | 574 | 64298-1 | 1382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007906POLE BURNT OFF POLE IS A 40 POLE SINGLE PHASE DEADEND WITH A 15KVA TRANSFORMER THERE COULD BE ENOUGH ROOM TO MOVE DOWN BUT IT IS 19.9 AND ABOUT 2.5 OF THE 40 POLE IS MISSING,,,WIRE SIZE IS#2ALUM AND IT IS ISOLATED ON POLE 478-185 BY CUTTING THE LOOP. THE LINE FUSE IS ON POLE 478-18.//COD 5// IDCC CNT2 STP MISSING, PN186 XXXX
7855 | Pikeville | 3411801 | JOHNSCREEK | META | 2020-10-15 03:41 | 2020-10-15 15:12 | 2 | 691 | 4556881 | 1382 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout GuidelinesXFRF IS OUT.XFR HAS BURNT PLACE ON THE SIDE OF IT,WILL CHECK THAT OUTXFRF IS OUT.XFR HAS BURNT PLACE ON THE SIDE OF IT,WILL CHECK THAT OUT///////INADVISABLE TO RE-FUSE XFR,WILL CALL FOR A REPLACEMENT//////MYLES IS GOING TO TAKE CARE OF THIS Released by crew 074S06 // repairs made @ 15:12
7856 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-07-29 12:27 | 2010-07-30 11:27 | 1 | 1380 | 58894-1 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE 1127-262 NEED TO REPLACE CROSS ARM. SEND THIS TO LINE CREW , STEVE RAY NEED ONE 8 FT CROSS ARM RELEASED BY CREW 074S05/// I AM GOING TO REPLACE XARM THIS MORNING WILL TRY THE FUSE LATER.//REPLACED ARM AND REPLACED CUTOUT AND ARRESTOR. RESTORED POWER AT 11:27. 7/30/10 TIM MCCOY//VER/CRB IDC OIL WELL OUT ENTIRE TIME XXXX
7857 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-01-11 13:30 | 2012-01-11 14:39 | 20 | 69 | 4247201 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | GOT SEC LEADS ABOUT TO BURNING ON POLE 1083 C2 301 GOT PHILILP HICKS COMMING WITH HIGHPRESS TOOL AND WIRE , WILL HAVE TO OPEN TRANS BANK ON POLE 1083- 302 TO MAKE REPAIRS. WILL CALL YOU BEFORE OPENING BANK OPEN BANK AT 1330 AND CLOSED AT 1439 VER/KEP IDC XXXX
7858 | South Williamson | 3411401 | DEWEY | INEZ | 2013-01-18 10:29 | 2013-01-18 10:59 | 46 | 30 | 4666911 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED FUSE IN ORDER TO MAKE LOOPS BACK FOR ORDER 4660441//COD 46// VER/DBM IDC XXXX
7859 | Hazard | 3302704 | HAZARD | KENMONT | 2008-06-30 14:15 | 2008-06-30 21:55 | 3 | 460 | 60277-1 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3302704//RELEASED BY CREW 077S03 INSULATOR == CHANGED INSULATOR == // VER/TOM IDC XXXX
7860 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-08-08 15:29 | 2020-08-08 16:38 | 20 | 69 | 4301971 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Time off 16:33 back on @ 16:38. Bad connection on 46-2105
7861 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-11-30 06:44 | 2015-11-30 11:20 | 5 | 276 | 4493711 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 CUTOUT COD-5 ISO LF 37830481C400089 ADDED 1 CUST FROM ORDER 4493721 & MADE MD FOR THAT CUST // VER/HFP L3/HFP
7862 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-08-13 00:43 | 2014-08-13 08:23 | 3 | 460 | 4364231 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK DURING NORMAL WORK HOURS,, FUSE TAIL HAD BROKE APR AT 0823 CLOSE TICKET
7863 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-05-15 08:35 | 2008-05-15 10:53 | 10 | 138 | 64131-1 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411802//WILL CHECK FOR PROBLEMSBAD XFR,GOING TO REPLACE IT.HAVE CONTACTED PVILLE AND THEY WILL BE ENROUTE SHORTLY RELEASED BY CREW 074S06 1 CUST PP UNTIL TERRY OPENED TR @ 0835 -- ALL 10 CUST BACK ON @ 1053 SEE DUPLICATE H1101945-1 FOR PART POWER CALL ASSOCIATED WITH THIS ORDER. THIS COVERS OUTAGE ON XFMR. VER/HFP IDC XXXX
7864 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-10-07 10:41 | 2013-10-07 15:43 | 23 | 302 | 4917811 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF ON POLE 282-134, CUT LOOP ON POLE 282-133 TO ISOLATE TROUBLE. PUT FIRE OUT , REC.ON POLE 306-137 BACK IN AT 11:30. TRUCKS TO ALL POLES. MAY BE ABLE TO LOWER EQUIPMENT. RELEASED BY CREW 078S01/CREW ON SITE/FETR1600/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1543/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDC XXXX
7865 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-07-25 12:24 | 2021-07-25 17:00 | 5 | 276 | 4953291 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cut out broke on pole 1013B-17.non truck...willl have to climb pole..line fuse feeds one span tap.only cust out is feed from transformer on pole 1013B-35..need a man to climb and a man to ground..pole is on a big hill side..cut out is broke in the clear Released by crew 079S03
7866 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2008-12-14 11:04 | 2008-12-14 16:49 | 4 | 345 | 58185-1 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003702// 138-229 40/5 BURNT OFF // ONLY CUSTOMERS OUT ARE ON POLE 138-229 AND THE FUSE OFF OF POLE 229 (NOT ON MAP, 15T FEEDS TOWARDS POLE 230)//COD 5//CREW ON SITE/LINE FUSE ON POLE#138-196 OPEN AT 1330 TO MAKE REPAIRS, THIS TOOK OUT 20 MORE CUST///FETR1830/POLE CHANGED AND POWER RESTORED AT 1649/NEED TO SEND NOTE TO MAPPING/15T ON POLE 138-229//SENT REPORT TO MAPPING DBM VER/KEP L3/KEP IDC XXXX
7867 | Pikeville | 3408103 | SALISBURY | MARTIN | 2011-09-03 10:27 | 2011-09-03 12:22 | 12 | 115 | 4791051 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REFUSED LINE CUTOUT . ALL WORK COMPLETE / GXJ//COD 12// VER/DBM IDC MAP SHOWS 1099-31 BUT PO SHOWES 1099-4 XXXX
7868 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-04-12 03:30 | 2013-04-12 09:15 | 4 | 345 | 4001311 | 1380 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 292-94 , OPENED LINE FUSE ON POLE 292-12 WAITING ON CREW. OPENED LINE FUSE AROUND 03:30 MAY WAIT UNTIL DAYLIGHT IF CREW WANTS TO RAINING HARD. OR UNTIL THE RAIN STOPS.//WAITING ON LINE TRUCK TO MOVE 75KV XFMR.//COD 4// VER/DBM IDCC TOF0133 XXXX
7869 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-07-06 14:01 | 2015-07-06 15:47 | 13 | 106 | 4732411 | 1378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN ON POLE REPAIRED// VER/ ADH
7870 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2018-09-03 23:46 | 2018-09-04 11:15 | 2 | 689 | 4039851 | 1378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Per George Whitaker; Dispatched in accordance with KYPCo Late Night Callout Guidelines. I changed gate in cutout COD-2 ISO TF 37830493001301
7871 | Hazard | 3302703 | HAZARD | HAZARD | 2020-03-16 15:27 | 2020-03-17 19:21 | 106 | 14 | 4483201 | 1378 | TRANSMISSION STATION | EQUIPMENT FAILURE | MOAB | DOL 1001076 & 1001150/ Failed MOLDLR at Hazard station load transfer for repairs/ Open CB at 1527 Closed N.O. at 1528/
7872 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-10-08 00:41 | 2012-10-08 12:10 | 2 | 689 | 4122211 | 1378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WILL WORK IN THE AM, ONLY 1 LEG OF SECONDARY IS HOT, CALLING FOR HELP. BAD UNDERGROUND SECONDARY COD-2 PER SERVICER SEE 4123211 FOR OUTAGE TO REPAIR THIS . VER/HFP L3/HFP IDC XXXX
7873 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-05-30 19:40 | 2009-05-30 21:26 | 13 | 106 | 51943-1 | 1378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | 3302701//WAS PART OF 51746-1 BUT THESE CUST NEVER CAME BACK ON//FOUND RECLOSER 318-281 OPEN WITH MOST EVERY LIGHT IN THE CONTROL BOX FLASHING// AFTER PATROLLING THE LINE TO CONFIRM NO HAZARDS, PULLED AC POWER AND BATTERY FOR THE REC CONTROL, THEN PUT BATTERY AND AC BACK AND RECLOSER RESET AND CLOSED BACK ON ITS OWN//SENT EMAIL TO MIKE LASSLO ABOUT ABNORMAL BEHAVIOR, NO ABNORMAL ENTRY ADDED TO DATABASE UNTIL KNOWN IF WAS JUST AND ISOLATED INCIDENT AND SEEMS TO BE OK NOW//COD 13// VER/DBM
7874 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2010-08-27 17:21 | 2010-08-27 18:14 | 26 | 53 | 61321-1 | 1378 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEAD BROKE AT CUTOUT--//COD 26// VER/DBM IDC XXXX
7875 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2008-06-06 19:00 | 2008-06-07 02:39 | 3 | 459 | 59376-1 | 1377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07 BAD TRAN. 25KVA//3116702/CREW ON SITE /FETR0315/VEM/XFMR AND CUT OUT CHANGED POWER RESTORED0239 VER/ARN
7876 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-05-31 10:28 | 2010-05-31 22:58 | 2 | 750 | 54169-1 | 1377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN 30CL6 SEC POLE 91-345, CUT SEC LOOPS PL. 91-344. 1 CUST STILL OUT. CREW REQ. 3 MEN. TRUCK OK...AT THE END OF OVERLOOK CIR. ON LEFT GREY TRL.... RELEASED BY CREW 078H16 // ON AT 2055 IDCC PN403, STP XXXX
7877 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-04-15 13:25 | 2009-04-15 14:16 | 27 | 51 | 54261-1 | 1377 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW OPENED FUSE TO SAFELY REPLACE BAD INSULATOR VER/KEP L3/KEP IDC XXXX
7878 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-02-07 06:08 | 2008-02-07 09:00 | 8 | 172 | 52215-1 | 1376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409301//XFMR FUSE BLOWN. FUSE LINK APPEARS TO HAVE BROKE. RE-FUSED XFMR. SH/ - COD 8/ VER/TOM IDC XXXX
7879 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-08-26 02:26 | 2021-08-26 13:54 | 2 | 688 | 4155221 | 1376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Dispatched in accordance with KYPCo Late Night Callout GuidelinesUnable to see pole 166-106,ASSESSING CONDITION.B phase is down at pole 166-2,Willhave to open all 3 Fuses at 166-106,This is Manual pole already have Rick Ray and Tree crew in Route to help make repairs..B phase is down at pole 166-2,Willhave to open all 3 Fuses at 166-106,This is Manual pole already have Paul Layne and Tree crew in Route to help make repairs..Opened fuse at 10:30 made repairs and restored at 13:54.
7880 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-01-30 15:18 | 2018-01-30 15:50 | 43 | 32 | 4784591 | 1376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BAD CROSSARM ON POLE 37830348B00307//OPENED STEP-DOWN ON POLE 37830348B00329//COD 88//OPENED 1518 CLOSED 1550
7881 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-08-03 22:26 | 2011-08-04 04:10 | 4 | 344 | 4661841 | 1376 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT INTO JUST ABOVE TRANSFORMER, 1103-313, ONE SPAN PRIMARY NO. 2 ALUM DOWN, NEED ONE CUTOUT AND ARRESTOR DEAN-END INSULATOR STC, CNT3, PER PHONE CONF
7882 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-07-19 07:05 | 2015-07-20 06:00 | 1 | 1375 | 4910001 | 1375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVE 7200 SHOULD BE TRUCK OK,,, LINECREW REQUIRED RELEASED BY CREW 078S11,REPLACED XFMR ALL CUST RESTORED @ 0600 PLEASE CLOSE TICKET THANKS.BT VER/SEF
7883 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-12-17 05:43 | 2010-12-17 10:18 | 5 | 275 | 53073-1 | 1375 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR# 38144935 // POLE 115-95 50 CLASS 4 BURNT OFF TRUCK TO POLE SEND NOTE TO RAYBURN AND TEC. RELEASED BY CREW 078S08//CAN LOWER ATTACH. TALKED WITH TECH. PT//REPAIRS COMPLETE AT 10:09 POWER RESTORED AT 10:18 REFUSED WITH 30T MAP HAD 20T CUTOUT HAD 40T G.BELL TO CHANGE MAP PT//VER/CRB IDC XXXX
7884 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-10-20 17:03 | 2011-10-21 04:30 | 2 | 687 | 4005171 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE BROKE IN FIELD NEED TECH AND LINE CREW POLE 269-C-214 BROKE,MAP SHOWS 35-6 ,WILL HAVE TO OPEN UP LINE AT POLE 269-C-163 TALK TO ALL CUST RELEASED BY CREW 078S09 IDCC CNT6, PN163 XXXX
7885 | Hazard | 3310502 | HADDIX | CANOE | 2020-06-09 17:12 | 2020-06-10 00:50 | 3 | 458 | 4986601 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 19.9 xfm. need 19.9 cutout and bracket. truck access Released by crew 077S10.. restored power at 00:50 // cod 3
7886 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2020-03-13 01:17 | 2020-03-13 12:44 | 2 | 687 | 4474031 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | spoke with customer, heard loud noise and saw flash when fuse blew but no active pole fire or smoke//will check in daylight //pole 1017-315just abt uprooted.isolated@1041-130@08:45 to de-energize.everett young enroute to asesspole 1017-315just abt uprooted.isolated@1041-130@08:45 to de-energize.everett young enroute to asess Released by crew 074S06// cutout broken on bank of xfmrs @ pole 38821065D29029// will make repairs
7887 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-09-08 18:06 | 2010-09-08 21:55 | 6 | 229 | 64719-1 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLING CREW--CALLED J HEMLEPP--BAD 15KVA--OIL SPILL-BESIDE ROAD RELEASED BY CREW 078S07/078H05 ON SITE @ 19:15//// WAITING FOR CREW TO ARRIVE.REPAIRS COMPLETE CUST. RESTORED @ 21:55/ CLEANED UP OIL/// J. HEMLEPP//VER/CRB IDC XXXX
7888 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-05-23 17:53 | 2011-05-24 01:31 | 3 | 458 | 4148351 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA NO TRUCK RELEASED BY CREW 078S08/CREW WAITING FOR WEATHER TO PASS/FETR 0100 5-24-11/VEM/NEW FETR0200/VEM/REPAIRS MADE AND POWER RESTORED 0131/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP
7889 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-06-08 22:43 | 2022-06-09 02:32 | 6 | 229 | 4043471 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 44-20693,, changed,, complete at 2:32
7890 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-07-07 11:07 | 2019-07-07 18:45 | 3 | 458 | 4672751 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STEVEN RAY///XFR IS BAD,1 DEAD LEG@THE BUSHINGS,NEED CREW,25KVA 7.2.DOUBTFUL THAT TRUCK CAN GET CLOSE ENOUGH/////////REPLACED XFR,RESTORED POWER.ALL OK AFTERWARDS
7891 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-08-12 14:33 | 2015-08-12 18:22 | 6 | 229 | 4128531 | 1374 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSS ARMS BROKE ON POLE 37830223C00156 === CALLED FOR LINE CREW AND ROW CREW/ A PHASE ORIGINALLY OPEN OTHER TWO PHASES @CROSS ARMS BROKE ON POLE 37830223C00156 === CALLED FOR LINE CREW AND ROW CREW ==== OPEN BAND C PHASE AT 16:19 === MADE REPAIRES ALL POWER ON AT/FIX IT IN HOIS/ SEE DUP H4128531 FOR B&C PHASE OUTAGE VER/HFP L3/HFP
7892 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-06-20 12:03 | 2011-06-21 10:56 | 1 | 1373 | 4352361 | 1373 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN; NEEDS REFUSED RELEASED BY CREW 077F07, REFUSED XFMR MADE LOUD ON OFF BUZZING SOUND CHECKED VOLTAGE READ 271 VOLTS ACROSS HOT LEGS NEED TO REPLACE XFMR 25 KVA 7.2 KV TRUCK ACCESSIBLE CRELEASED BY CREW 077E02 CHANGED XFMR RESTORED POWER AT 1056 CREW 077H01//VER/CRB IDC XXXX
7893 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-02-10 11:17 | 2012-02-10 17:00 | 4 | 343 | 4332361 | 1372 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SEND TO CREWS 4-CUSTS PART POWER RELEASED BY CREW 078S08, REPAIRED BAD SECONDARY TO APTS///VER/CRB IDC XXXX
7894 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-09-06 08:47 | 2012-09-06 14:30 | 4 | 343 | 4023131 | 1372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE FUSE ON POLE 37830393B00091 ==OPEN LINE AT 08:47 === NEED LINE CREW AND 45 FT POLE POLE TOP PINE T BRACKET CUTOUT ARRESTER 2 CLIVES == GET TRUCK TO POLE RELEASED BY CREW 077S03 COD-4 ISO LF 37830393B00091 VER/HFP L3/HFP IDC XXXX
7895 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2011-11-25 18:15 | 2011-11-25 23:58 | 4 | 343 | 4114921 | 1372 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO BRING 1/0 CHG. SEC. TRUCK TO TRANS POLE OFF 18;15 RELEASED BY CREW 078S08 // CUTTING R/W REPLACING SEC/ HAD TO CHANGE XFR 15 KVA TO 25 IDC XXXX
7896 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-05-11 19:13 | 2017-05-12 02:50 | 3 | 457 | 4782721 | 1371 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELEASED BY CREW 074S02//REPAIRED FAILED INSULATOR//COD 3// VER/DBM
7897 | Pikeville | 3407103 | TOPMOST | KITE | 2012-01-04 12:53 | 2012-01-04 15:10 | 10 | 137 | 4233231 | 1370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ///VER/CRB IDC XXXX
7898 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2021-04-25 00:56 | 2021-04-25 12:21 | 2 | 685 | 4477781 | 1370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***DDC HOLD TAG***//Fuse open on pole 248-C-66 with a tag placed for DDC and a gronud. Pole 248-C-441 had a broken cutout that burned the pole off about 1 foot about the top XFMR hanger. This pole is manual behind a house and a shed but it appears that a back yard machine could set the pole. Will need a 40 pole, 12KV primary deadend assembly, guy attachment and guy breaker, 2 clevis and spools, 12 KV cutout and a t-bracket. Released by crew 077S04
7899 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2012-12-14 08:11 | 2012-12-14 12:45 | 5 | 274 | 4468831 | 1370 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S05/FETR 13:30 JEH// UPGRADE FROM 50 TO 75 KVA/ REPLACED C/O&L/A / REPAIRS COMPLETE POWER RESTORED @ 12:45 // SENT EMAIL TO ENGINEERING TO HAVE MAP CORRECTED ENTERED MD VER/HFP L3/HFP
7900 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2013-03-28 10:17 | 2013-03-28 14:05 | 6 | 228 | 4964161 | 1368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON 37830048A31604/// WILL REFUSE/// BAD 75KVA// T. HALL IS ROUNDING UP A CREW RELEASED BY CREW 074S05//COD 6//CREW REPLACED XFMR// VER/DBM IDC XXXX
7901 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-03-19 14:53 | 2009-03-19 17:25 | 9 | 152 | 60145-1 | 1368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND ANOTHER POLE BURNTED OFF, POLE NUMBER IS 879-175, WHICH IS A 40` CLASS 5 POLE, THE ONLY THING GOOD ABOUT THIS IS NO ONE IS LIVING IN THIS HOUSE, THE DIRECTION IS GO TO GRAF BRO, ALL THE WAY TO THE RIVER TURN RIGHT, FOLLOW GRAVEL DRIVE TO POLE. HAVE LOOP CUT ON 878-162 & GROUNDED. VER/ARN IDCC CNT10 XXXX
7902 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-05-27 12:28 | 2010-05-27 15:00 | 9 | 152 | 51389-1 | 1368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ONLY PHASE C FUSE BLOWN//COD 9//ARRESTOR WAS BAD ON POLE 351-109 I REMOVED ARRESTOR FROM LINE AND REFUSED LINE//AED CREATED // VER/DBM IDC XXXX
7903 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-05-09 16:29 | 2021-05-09 22:11 | 4 | 342 | 4558451 | 1368 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | arrived--LF Pl# 38830115C46035 open--patrolled found bad LF cutout pL# 115c4-6035--replaced cutout ---re fused 40T LF @ 22:11---tbl tkt comp--rmv Released by crew 078H16
7904 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-11-30 13:45 | 2022-11-30 18:32 | 7 | 287 | 4211881 | 1367 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25KVA 7200 transfomer manual gonna need line crew, send to will jones Released by crew 077H05 //opened line fuse OFF@1719 RESTORED ALL @1832
7905 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2013-11-01 19:00 | 2013-11-01 20:45 | 13 | 105 | 4999811 | 1365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE ROTTON OFF AT GROUND @858-53 CREW IN ROUTE TO CHANGE.OPENED @858-52 @ 19:00REPAIRES COMPLTED ON POLE 53 . MADE LINE HOT @ 20:45 COD-13 ISO LF 38830858C00052 VER/HFP L3/HFP IDC XXXX
7906 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-04-10 03:11 | 2016-04-10 06:26 | 7 | 195 | 4076981 | 1365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY BROKE IN THE CLEAR @ POLE #38831078000037 COD-7 WILL ISOLATE @ 38831078000033 NEED #4 C0PPER SLEVES ,MATERIAL HANDLER & 2 MENPRIMARY BROKE @ POLE #38831078000037 WILL ISOLATE @ 38831078000033 NEED #4 C0PPER SLEVES ,MATERIAL HANDLER & 2 MEN OPCLOSED BACK IN @06:10ENED @ 33 @06:26
7907 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2008-10-25 16:35 | 2008-10-25 19:50 | 7 | 195 | 59058-1 | 1365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP PATROLING LINE// CALLED CREW IDC XXXX
7908 | Hazard | 3302704 | HAZARD | KENMONT | 2009-02-18 11:00 | 2009-02-18 12:45 | 13 | 105 | 63884-1 | 1365 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNED OFF BY CUTOUT , WILL HAVE TO OPEN LINE UP AT P #321 / 2 IN ORDER TO CHANGE POLE DUE TO WEATHER .OPENED LINE CUTOUT AT 1100 HRS WILL RESTORE POWER WHEN FINISHED WITH TRANSFERING TO NEW POLE . JEFF COMBS REPLACED POLE AND RESTORED POWER IDCC PN380 CNT1 TOF0808 XXXX
7909 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-05-17 14:06 | 2014-05-17 16:10 | 11 | 124 | 4719391 | 1364 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON THE TAKE OFF POLE. REPLACED THE LINE CUTOUT, AND POWER IS BACK ON.//COD 11// VER/DBM L3/HFP
7910 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-03-26 10:19 | 2015-03-26 16:00 | 4 | 341 | 4229521 | 1364 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 205-86 NO POWER HERE PER JIM HOLLIDAY 1 PHASE IS HOT BUT OPEN SECONDARY LOOSE AND HANGING DOWN.POWER RESTORED TEMP, STILL NEED TO REPLACE OPEN SECONDARY, PLEASE SEND TO D. CHRISTIAN, OPENED XFMR AT 15:15, CLOSED BACK IN AT 16:00 COD-4 ISO TF 37830205C00087 VER/HFP L3/HFP
7911 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-08-05 10:51 | 2009-08-05 11:20 | 47 | 29 | 62369-1 | 1363 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BAD CUTOUT ON 834-34 ISOLETED CUTOUT IT DOSNT FEED ANYTHING /// CLOSED IN 40T FUSE ON 834-621// COMPLETE TT COD-47 38830834A00011 VER/KEP L3/KEP IDC XXXX
7912 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-01-25 08:11 | 2014-01-25 14:30 | 4 | 379 | 4311641 | 1362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 212-16.BAD 19.9 15KVA XFORMER, TRUCKS TO POLE. ONE CUST (BARN & CUST SAID OK TO FIX LATER) AND REPEATER ON THIS POLE /// XFMR ON POLE 212-16 WAS BAD, THERE IS A SPAN OF 1/0 SECONDARY FROM POLE 212-16 TO 212-100 FEEDING HOUSE. WE REMOVED XFMR AT 212-16 AND HOUSE, BARN, REPEATER, AND SECONDARY ARE ALL ON XFMR AT POLE 212-100, PLEASE DO MAP DISCR. TO ADD SECONDARY SPAN AND REMOVE XFMR FROM MAPS// ENTERED MD COD-4 VER/HFP L3/HFP IDC XXXX
7913 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-01-14 11:24 | 2022-01-14 15:11 | 6 | 227 | 4346131 | 1362 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KATHY LOVELY line fuse on p-900-1 is cracked causing customer at 900-179 to have flickering lights.need to change 2 cutouts on 900-1..brick house white trim on the right at the mo of Barbara ln .606-434-3359 .. before church,on right. Released by crew 076S01 / restored all fuses @1511
7914 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-04-03 10:18 | 2015-04-03 14:50 | 5 | 272 | 4263741 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HENDRICKS BURNED DOWN BETWEEN P-785-263 AND 785-264..OPENED 785-D-331 AT 1356 348CC/..OPENED SWITCHES AT 14.10 BACK ON AT 14.50.. RELEASED BY CREW 076S01 VER/KEP (SEE DUP) L3/HFP XXX
7915 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-03-24 16:39 | 2010-03-24 18:55 | 10 | 136 | 54107-1 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 37830208000026 WE HAVE LINE FUSE OUT, CHECKING LINE//// 37830208000026 FOUND ARRESTOR BROKEN AND HANGING DOWN FROM C/O, CUT IN CLEAR AND CHECKED REST OF LINE. POWER RESTORED VER/KEP L3/KEP IDC XXXX
7916 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2022-06-15 16:18 | 2022-06-15 20:50 | 5 | 272 | 4128231 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Transformer is not putting out voltage on pole 425B-84. Transformer size is 37.5 probably need to go to a 50KVA 7200. Released by crew 077H15
7917 | South Williamson | 3200301 | BELFRY | BELFRY | 2017-04-23 11:09 | 2017-04-23 13:25 | 10 | 136 | 4670961 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TAP FUSE IS BLOWN AT POLE 38820990A00053. POLE TOP IS BURNED OFF AT 990-B-544. I WILL MAKE TEMPORARY REPAIRS TO GET THE POWER BACK ON. PLEASE SEND TO CLIFF FREEMAN TO HAVE THIS POLE REPLACED. CLIFF PLEASE MAKE CONTACT WITH THIS CUSTOMER, HE IS UPSET ABOUT THIS HAPPENING. 38820990B00544 SENT TO FREEMAN/AWD VER/AWD L3/HFP XXXHFP
7918 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-11-15 13:55 | 2020-11-15 16:45 | 8 | 170 | 4683721 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Primary came out of shoe at pole191-D102,Causing wire to let down back towards 191-D-100,Going to get it pulled back up and redeadened.Restored Lines Fuse at 16:45.
7919 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-02-23 00:20 | 2009-02-23 06:00 | 4 | 340 | 50464-1 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 NEED TO GO BACK WITH 50 KVA RELEASED BY CREW 077H14BAD 25 KVA 19.9 NEED TO GO BACK WITH 50 KVA CLOSED XFMR AT 0550 IDC XXXX
7920 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-10-27 16:55 | 2015-10-27 19:45 | 8 | 170 | 4381441 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLEW ON POLE 857-64///BROKE XFMER CUTOUT ON POLE 857-206///NEED 1 LINEMAN AND BIG BUCKET///REPAIRS MADE///CLOSED LINE FUSE IN AT 19:45///COMPLETE BR VER/CRB L3/HFP XXXHFP
7921 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-01-15 17:00 | 2010-01-15 18:20 | 17 | 80 | 54581-1 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TANSFORMER IS LEAKING AND CECIL SEXTON CREW IS GOING TO REPLACE THIS RELEASED BY CREW 074S07OPENED LINE FUSE AT 1700 CLOSED IT AT 1820//COD 17// VER/DBM IDC XXXX
7922 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-04-13 07:55 | 2011-04-13 10:45 | 8 | 170 | 56181-1 | 1360 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN WILL REFUSE//BAD 50 KVA//LINE FUSE OUT ON 37830048A41163 SHOWED FUSE OUT ON SEPERATE ORDER
7923 | Pikeville | 3410602 | E.PRESTON | LANCER | 2014-01-08 20:14 | 2014-01-08 22:45 | 9 | 151 | 4262831 | 1359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | REPAIRED SECONDARY RISERS VER/TOM L3/TOM
7924 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2022-10-12 16:43 | 2022-10-13 00:16 | 3 | 453 | 4020641 | 1359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | /Fuse blown on XFMR pole 248-A-553, closed back in and XFMR made a loud hum and the fuse melted back out. Crew required with a 25KVA 7200, manual. Released by crew 077S04
7925 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2019-11-01 07:27 | 2019-11-01 15:00 | 3 | 453 | 4271551 | 1359 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED/// Bad 25KVA XFM 7200/// Truck accessible Released by crew 074S02//all repairs made power back on at 15:00/ ISO 37820101000181/ COD 3
7926 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-06-10 04:46 | 2008-06-10 08:00 | 7 | 194 | 61253-1 | 1358 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1099-3068 BAD CUTOUT TREES POLE 1099-3019 2-30T LINE FUSES//COD 7// VER/DBM IDCC PN3068 XXXX
7927 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2014-08-11 18:46 | 2014-08-11 19:09 | 59 | 23 | 4355881 | 1357 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1147-275 BAD CUTOUT REPLACED SEND NOTE TO TEC. TO CK. POLE BURNT 1/3 OF POLE OPENED REC. C PHASE 59 CUSTOMERS 18;46 TO 19;09 ISO OCR 39831147A00237 VER/HFP L3/HFP AJB PH C. INTL CUST CALLS WERE TO REPORT TROULBE ONLY.
7928 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-08-22 20:51 | 2014-08-23 02:30 | 4 | 339 | 4408151 | 1356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F OUT,WILL RE-FUSE///////BAD 50 KVA XFR,NEED CREW,MATERIAL BUCKET,WILL HAVE TO CUT CHAIN TO GET TO POLE RELEASED BY CREW 074S06XFR F OUT,WILL RE-FUSE///////BAD 50 KVA XFR,NEED CREW,MATERIAL BUCKET,WILL HAVE TO CUT CHAIN TO GET TO POLE ///////REPLACED XFR AND RESTORED,ALL OK AFTERWARDS// LINE FUSE ON POLE 38821137A00416/ POWER RETORED TO EVERYTHING @ 2:30// TRANSFORMER TOOK OUT LINE FUSE// COD 4// VER/ ADH
7929 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-07-22 05:46 | 2010-07-22 11:25 | 4 | 339 | 55388-1 | 1356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKING NOW XFMER FUSE OPEN.THINK XFMER BAD OIL COMING OUT OF IT AND IT BLACK AROUD SECONDARY BUSHING RELEASED BY CREW 076H06//COD 4// VER/DBM IDC XXXX
7930 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2020-09-23 01:43 | 2020-09-23 09:15 | 3 | 452 | 4487901 | 1356 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Unloc/Held for daylight per KPCO late night callout guidelines. Xfmr fuse link appears to have broken. Restored @ 9:15. sh
7931 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-09-25 05:14 | 2021-09-25 09:45 | 5 | 271 | 4289791 | 1355 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines.fuse broke , replaced
7932 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-11-01 07:19 | 2014-11-01 14:50 | 3 | 451 | 4679871 | 1353 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED 40/5 POLE POLE 268D21 NEED DUMP TRUCK TO SET POLE/OPEN TAG AND GROUND AT 268-27 TO TACKETT/268D27 OPEN AT 1000 HRS RELEASED BY CREW 078S03,,CREW ON SITE,,POLE REPLACED,,ALL POWER RESTORED, WORK ORDER HAS BEEN WRITTEN// CLOSED @ 14:50// COD 3+59 // SEE DUP H4679871 FOR OUTAGE ON SW // VER/HFP L3/HFP
7933 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-09-21 12:42 | 2017-09-21 18:20 | 4 | 338 | 4379261 | 1352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT BURNT UP ON 95-47 CREW REQUIRED 37830095000047/CALLED CUSTOMER-NO ANSWER TRANS CUTOUT BURNT UP ON 95-47 CREW REQUIRED CREW REPLACED CUTOUT RESTORED POWER AT 18:20 37830095000047 VER/AWD VER/ALB
7934 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-12-24 02:52 | 2016-12-24 08:30 | 4 | 338 | 4231811 | 1352 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 19.9 CUTOUT ON POLE 37830220000055 NEED BIG BUCKET AND ONE MAN//COD 4
7935 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-12-06 17:37 | 2013-12-06 20:50 | 7 | 193 | 4109441 | 1351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 318A-115. FOUND BAD INSULATOR ON POLE 318A-283. GOT PHILLIP HICKS COMING TO MELINE FUSE OUT ON POLE 318A-115. BAD INSULATOR ON POLE 318A-283. POWER BACK ON @ 20:50 VER/CRB L3/HFP
7936 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2022-08-13 08:27 | 2022-08-13 11:40 | 7 | 193 | 4735811 | 1351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | line fuse blown on 785-887.. u/g faulted, need line crew.811 dig # 2208130149.11:40.
7937 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-11-25 02:12 | 2008-11-25 10:50 | 7 | 518 | 51961-1 | 1351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003701//POLE FIRE AT 38830185000300, ISOLATED AT 38830185000240, FUSE ON POLE 185-93 CLOSED AT 03:15, CREW REQUIRED, 40-5 POLE FIRE TRUCK OK. 2 CUST OUT. RELEASED BY CREW 078S05//VER/CRB IDC XXXX
7938 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2012-11-27 09:08 | 2012-11-27 12:21 | 7 | 193 | 4424091 | 1351 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BURNED OFF 8 FOOT CROSSARM. NEED CROSSARM, AND CUTOUT FOR 7200. I THINK YOU CAN USE BUCKET IF YOU BACK IN AT DRIVEWAY THAT SAYS STEPHANIES LN..APCO OPENED FUSE ON POLE 821B125 AT 10:40.//NO CUST ON APCO SIDE// ///VER/CRB L/3 CRB IDC CHANGED TIME OFF FROM 1040, CNT10 LOOKS LIKE FROM COMMENTS THE INITIAL TRANSFORMER WOULD HAVE BEEN OUT BEFORE OPENING LINE XXXX
7939 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-09-26 16:10 | 2012-09-26 17:00 | 27 | 50 | 4090021 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BURN OFF AT POLE 38830136000026, PATROLED LINE AND FOUND NO HAZARDS, REPLACED BASKET AND HOT TAP, ALL POWER RESTORED COD-27 ISO PO @ 38830136000026 VER/HFP L3/HFP IDC XXXX
7940 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-02-01 19:54 | 2018-02-01 23:39 | 6 | 225 | 4790881 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT Released by crew 077S01 fuse out 37830387D00309
7941 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-08-22 02:32 | 2009-08-22 05:02 | 9 | 150 | 60313-1 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN ON POLE 266-4 AND TOOK OUT LINE FUSE ON POLE 266-2. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT AND CLOSED LINE FUSE IN AT 05:02. VER/PDP IDCC PN517 XXXX
7942 | Hazard | 3309302 | VICCO | JEFF | 2014-10-03 11:42 | 2014-10-03 14:24 | 12 | 162 | 4547341 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 348-B-113, BAD CUTOUT ON POLE 372-95//LINE FUSE OUT ON POLE 348-113, BAD CUTOUT ON POLE 372-95, ISOLATED CUTOUT, CUTOUT RESTORED POWER AT 14:24.LINE FUSE OUT ON POLE 348-113, BAD CUTOUT ON POLE 372-95, ISOLATED CUTOUT, CLOSED LINE FUSE IN AT 13:30, REPLACED CUTOUT RESTORED POWER AT 14:24. RELEASED BY CREW 077S11 VER/CRB VER/DKG L3/DKGXXXX
7943 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2016-07-27 01:30 | 2016-07-27 09:00 | 3 | 450 | 4687031 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HOLD TILL THE AM PER GUIDELINES// BAD C/O, REPLACED POWER RESTORED AT THIS LOC AT 0900 BY AMG VER/AWD
7944 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2019-11-05 01:54 | 2019-11-05 09:24 | 3 | 450 | 4292201 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held in accordance with KYDDC late night callout guidelines.bad cutout , replaced cutout & arrester restored power at 09:24..
7945 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-01-25 11:55 | 2010-01-25 12:45 | 27 | 50 | 59449-1 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 33581280 // HOT TAP BROKE OFF IN WIND REPAIRED//VER/CRB IDC XXXX
7946 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-09-11 18:20 | 2018-09-11 20:35 | 10 | 135 | 4085421 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o @ 69-6018, curve on terrace @ mindy jane. line crew. restored @ 20:35
7947 | South Williamson | 3411401 | DEWEY | INEZ | 2012-08-20 13:50 | 2012-08-20 17:35 | 6 | 225 | 4955361 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE DOWN AT 697-8//LINE FUSE BLOWN ON 697-8///PULLED OUT OF SLEEVE//#4 COPPER///CREW ENROUTE///REPAIRS MADE//RESTOREDAT 1735//COMPLETE//EM VER/KEP IDC XXXX
7948 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-04-23 15:50 | 2018-04-23 17:20 | 15 | 90 | 4266511 | 1350 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO POWER OFF UNTIL HOT TAP LIFTED ON POLE 37830251000050 COD-15 ISO PO @ 37830251000050 OFF @ ON @ opened line at pole 251-50 at 15:50, trouble pole is 251-52opened line at pole 251-50 at 15:50, trouble pole is 251-52. power restored 1720
7949 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-07-21 04:09 | 2012-07-21 05:20 | 19 | 71 | 4789461 | 1349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/ARN
7950 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-10-09 10:06 | 2012-10-09 14:25 | 11 | 259 | 4125481 | 1349 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37830466000045 == UNKNOWN CAUSE == LINES IN FIELD DOSE NOT MATCH THE MAPS == WILL MAKE JOB FOR ENG. TO LOOK AT THEM == ALSO THE FUSE ON POLE 37830466000079 NOT RIGHT === GOT MAIN LINE ON AT 11:55 === CHANGED CUTOUT OUT THEN GOT THE LAST CUST ON AT 14:25 == RELEASED BY CREW 077S03 MD ENTERED & ENGINEERING NOTIFIED VIA EMAIL FOR HELP ON CORRECTION TO MAP // COD-11 ISO LF 37830466000045 VER/HFP L3/HFP IDC XXXX
7951 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-05-02 15:25 | 2016-05-02 21:02 | 4 | 337 | 4160781 | 1348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLED LINE COULD NOT SEE ANY THING ON LINE,,FUSED LINE STAYED 5 MIN,, FUSE BLEW AGAIN , LOOKS LINE THE PROBLEM MAY BE ON POLE 55B4/289 ARRESTOR OR DEADENDS,,, LIMB IN LINE REMOVED AND REESTORED POWER AT21:02,JDM RA RELEASED BY CREW 077E01 VER/HFP L3/HFP
7952 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-01-22 23:31 | 2016-01-23 10:45 | 2 | 674 | 4642991 | 1348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ****SEE H4642991**** FOUND BAD CUTOUT @ POLE 151-86 ( ONLY 2 CUSTOMERS EFFECTED BEFORE OPENING LINE FUSE)..WILL HAVE TO OPEN UP @ POLE 151-45 TO SAFELY MAKE REPAIRS...OPENED LINE FUSE UP @ 09:45 (36 ADD CUST).CLOSED BACK IN @ 10:45 RESTORING ALL CUSTOMERS// DUPLICATE IN HOIS/ ISO 37820151000045/ COD 38/ VER/BOW
7953 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2013-09-18 18:35 | 2013-09-19 00:12 | 4 | 337 | 4865371 | 1348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | 207-51 LINE FUSE,WIRE SLID THROUGH ON POLE 206-2105 LAYING PRI. BASKET AGAINST RIDGE PIN ,PRI WIRE BURNT IDC XXXX
7954 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-10-05 03:44 | 2018-10-05 09:21 | 4 | 337 | 4199471 | 1348 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.bad cotout L3/HFP
7955 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2015-05-05 05:31 | 2015-05-05 13:00 | 3 | 449 | 4390731 | 1347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | WILL HAVE SERVICER CHECK @ START OF SHIFT//TOM BAD 37.5 KVA TRANSFORMER. ALL THREE METERS PULLED - UG COND TESTS OK. CREW ENROUTE TO REPLACE. RELEASED BY CREW 076S02/ CREW ON SITE TCM/ HAD TO STOP JOB 37.5 TO HEAVY FOR BUCKET, 750 LBS LINE TRUCK IN ROUTE TCM/COD 3// VER/ ADH
7956 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-09-02 02:31 | 2011-09-02 10:00 | 3 | 449 | 4783321 | 1347 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411801 - AS PER PRESET GUIDELINES, WILL HAVE SERVICER CHECKED AT REGULAR WORKTIMEXFR TO RE-FUSEXFR TO RE-FUSE///////25 KVA 19.9,CAN USE MAT HANDLERXFR TO RE-FUSE///(XFR IS BAD)XFR TO RE-FUSE//CREW WILL CALL FOR TICKET RELEASED BY CREW 074S06// CREW IN ROUTE//COD 3// VER/DBM IDC XXXX
7957 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2010-06-12 20:04 | 2010-06-13 18:30 | 1 | 1346 | 61814-1 | 1346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER STAYED IN FOR 1 HR THEN WENT BACK OUT..TRANSFORMER IS BAD...CALLED TIM THOMAS..NEED NEW TRANSFORMER AND CREW..NOONE AVAL.TO CHG XFMR MAY BE SUNDAY..TRANSFORMER STAYED IN FOR 1 HR THEN WENT BACK OUT..TRANSFORMER IS BAD...CALLED TIM THOMAS..NEED NEW TRANSFORMER AND CREW.. RELEASED BY CREW 076S01// TRANSFORMER CHANGED COMPLETE TT//COD 1// VER/DBM
7958 | Hazard | 3301101 | CHAVIES | CHAVIES | 2022-09-23 19:54 | 2022-09-24 18:20 | 1 | 1346 | 4915991 | 1346 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tried to replace old cutout door but door is broke.hold until morning just will need A lineman and a servicer..cutout to close to primary.line will need to be opened to change cutout..cutout is within MAD Released by crew 077H20. Replaced cut out, xfmr is bad. Will need a 7200/15 KVA xfmr, manual. Also Pole# 17-20 has anchor pulled out Released by crew 077H07 power restored at 18:20
7959 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2013-12-23 07:51 | 2013-12-23 12:20 | 5 | 269 | 4195181 | 1345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON HIGH SIDE OF STEPDOWN , WILL NEED BIG BUCKET RELEASED BY CREW 077S11. CHANGED CUTOUT AND RESTORED POWER AT 1220 VER/SEF L3/HFP IDC XXXX
7960 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-07-21 01:41 | 2022-07-21 06:10 | 5 | 269 | 4533141 | 1345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830476D40173 lat c/o broke--replaced-in at 06:10-allgood-ds072122
7961 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-12-15 17:39 | 2008-12-16 00:35 | 5 | 416 | 58725-1 | 1345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE IS OUT ON 334-9. I AM PATROLLING LINE NOW. DEAD END INSULATOR ON POLE 334-22 HAS BROKEN DOWN. WILLIE IS SENDIND HELP. I CLOSED LINE FUSE IN AT POLE 334-9 UP TO AN OPEN POINT AT POLE 334-20 AT 20:30. THIS GOT ALL BUT 2 CUSTOMERS BACK ON. //VER/GAH L3/KEP IDC XXXX
7962 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-05-01 21:01 | 2015-05-02 01:30 | 5 | 269 | 4382951 | 1345 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05.. TRANSFORMER REPLACED AND COMPLETE VER/ARN
7963 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-02-24 06:07 | 2012-02-24 08:55 | 8 | 168 | 4491181 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISP IN THE AM // PATROLLING. STIRRUP BURNT OPEN ON 38830810D00074. <<5 CUSTOMERS AFFECTED>> MADE REPAIRS ON 810-74 BUT FOUND BAD CUTOUT ON 38830810D00254. CHANGED CUTOUT AND RESTORED ALL CUSTOMERS AT 8:55. SH COD-5 ISO PO 38830810D00074 VER/HFP L3/HFP
7964 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-10-17 09:36 | 2008-10-17 10:40 | 21 | 64 | 56481-1 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3314402//OPENED LINE FUSE 331-147 @ 0936 COD 21 TO ISOLATE POLE FIRE// VER/KEP IDC XXXX
7965 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-01-28 00:56 | 2012-01-28 08:24 | 3 | 448 | 4299971 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL HAVE SERVICER CHECK AT REGULAR WORK TIME AS PER PRESET GUIDELINES // FUSE BROKE, REFUSE TRANSFORMER VER/PDP IDC XXXX
7966 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2021-01-25 21:16 | 2021-01-26 01:00 | 6 | 224 | 4892221 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | crew required 6a primary only no trucks tagged to b tackett no grounds Released by crew 078S03,repairs made all cust restored @ 0100 please close ticket thanks.bt
7967 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-11-30 05:14 | 2009-11-30 10:50 | 4 | 336 | 50849-1 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307301// WELL DISPATCH IN THE AM--- BAD CUTOUT NEED BIG BUCKET IDC XXXX
7968 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-01-29 17:52 | 2012-01-29 20:40 | 8 | 168 | 4303251 | 1344 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LEADS BURNT OFF AT TRANSFORMER, NEED 1 MAN, BIG BUCKET, AND 4/0 COPPER FOR TRANSFORMER LEADS. ---OPENED TRANSFORMER AT 1950 CLOSED AT 2040, POWER RESTORED.//COD 8 VER/KEP IDC XXXX
7969 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2009-05-10 08:55 | 2009-05-10 11:43 | 8 | 168 | 54042-1 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 20T FUSE POLE900-4030 MD FILED HAD ALINE FUSE OUT ON POLE 900-4030, 12T, CAUSE FOUND BAD 25 KVA ON POLE 900-4035, HAVE LINE FUSE BACK IN AT 11:00, PRIMARY BUSHING WAS BURNTED, ON TRANSFORMER, CAUSING THIS, THIS TRANSFORMER, JUST FEEDS D TO D LIGHT FOR CHURCH, CAN WAIT TILL TOMMORROW TO CHANGE IT OUT, CAN USE TRUCKS//VER/CRB//MADE A MDC
7970 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-10-21 15:42 | 2010-10-21 18:30 | 8 | 168 | 61806-1 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BAD. I WILL NEED A BIG BUCKET TRUCK AND A CUTOUT. I WILL CALL DUTY SUPERVISOR. JAY CHANGED CUTOUT. COD-8 VER/HFP L3/HFP IDC XXXX
7971 | Hazard | 3310502 | HADDIX | CANOE | 2011-10-19 13:08 | 2011-10-19 15:00 | 12 | 112 | 4998801 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW OPENED LINE AT POLE 37830098000005 IN ORDER TO MAKE REPAIRS FOR ORDER 4994811//COD 12//ISO// VER/DBM IDC XXXX
7972 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2014-10-25 06:00 | 2014-10-25 08:48 | 8 | 168 | 4660401 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SERVICER WILL CHECK AT START TIME 10-25-14. WILL CHECK XFMR & REFUSE.FUSE LINK .WAS BROKE .NOT BLOWN. VER/CRB L3/HFP
7973 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2017-07-28 16:20 | 2017-07-28 23:48 | 3 | 448 | 4196541 | 1344 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 38820965C20597. LIFTED HOT TAP ON 38820965C00182.BROKEN CUTOUT/OPENED TAP AND REPLACED SILVERTOP CO/ REENERGIZED TAP @23:48 3 COD VER/AWD
7974 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-09-20 15:15 | 2012-09-21 02:26 | 2 | 671 | 4072691 | 1342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED TRUCKS OK FOREIGN POLE 40/4 DOUBLE DEAD END WITH TRANSFORMER INSTALLED ISOLATED ON 197-2 AT 1515 HRS 2 CUSTOMERS OFF RELEASED BY CREW 078S03 (HIT VERY HARD ROCK TAKING LONGER TO DIG HOLE) ALL POWER RESTORED AT 02:26 //VER/GAH IDC XXXX
7975 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-04-03 23:18 | 2014-04-04 10:29 | 2 | 671 | 4570971 | 1342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER AFTER HOURS GUIDE LINES THIS TROUBLE WILL BE CHECKED ASAP 04/04/14 . REPLACED CUTOUT AND ARRESTER ON POLE 68 AND REFUSED LINE CUTOUT , ALL WORK COMPLETE / GXJ VER/SEF
7976 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2021-07-10 12:43 | 2021-07-10 14:45 | 11 | 122 | 4881951 | 1342 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection at mast, resqueezed
7977 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-11-03 00:01 | 2015-11-03 11:12 | 2 | 671 | 4404871 | 1342 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL DISPATCH DURING NORMAL WORK HOURS. BAD 25 KVA 7200 TRANDFORMER, NEED TO REPLACE CUTOUT AND ARRESTER ALSO, CAN USE TRUCK. RELEASED BY CREW 077S04 VER/CRB
7978 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-06-06 08:01 | 2013-06-06 10:30 | 9 | 149 | 4227011 | 1341 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | /BAD 50KVA TRANS POLE 1147-4607 TRUCK TO POLEBAD 50KVA TRANS POLE 1147-4607 TRUCK TO POLE RELEASED BY CREW 078S08///CHANGED OUT 50KVA XFMR////PWR CK GOOD///124/124/248V//// COD 9 ISO TF 1147-4607 VER/SEF
7979 | Hazard | 3309003 | JEFF | VIPER | 2015-02-20 11:58 | 2015-02-20 19:25 | 3 | 447 | 4055521 | 1341 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25KVA CSP TRANSFORMER BURNT UP-MANUEL REPLCED XFMR RESTORED POWER AT 19:25 VER/CRB L3/DKGXXXX
7980 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-02-28 12:14 | 2011-02-28 17:49 | 4 | 335 | 64538-1 | 1340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38970839 // CUTOUT BROKEN ON POLE 37830201C00043 NEED 3 MEN AND BIG BUCKET AND FLAGGERS RELEASED BY CREW OFF 1742 ON 1749STS WR # 38970839 // CUTOUT BROKEN ON POLE 37830201C00043 NEED 3 MEN AND BIG BUCKET AND FLAGGERS RELEASED BY CREW 077S04 OPENED C PHASE REC AT 1742 CLOSED IN AT 1749 REPLACED CUTOUT CREW 077H01 DUPLICATING FOR RECL OUTAGE...SEE H64538-1 VER/HFP L3/HFP IDCC CNT1 XXXX
7981 | Paintsville | 3401802 | INDEX | HOSPITAL | 2019-09-03 07:08 | 2019-09-03 11:36 | 5 | 268 | 4974071 | 1340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva xfmr, called Tim Thomas.. he is bringing crew to chg.bad 50 kva xfmr, called Tim Thomas.. he is bringing crew to chg. ON @ 1136bad 50 kva xfmr, called Tim Thomas.. he is bringing crew to chg.bad 50 kva xfmr, called Tim Thomas.. he is bringing crew to chg. Released by crew 076S01.. changed transformer and restored power at 11;36..complete rn L3/HFP
7982 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2015-11-12 11:15 | 2015-11-12 16:50 | 4 | 335 | 4432341 | 1340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT 38830044C24630/ ISO 38830044C24630/ COD 4/ BROKEN XFORM CUTOUT ,REPLACED POWER RESTORED/ VER/BOW
7983 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-09-27 09:25 | 2015-09-27 15:00 | 4 | 335 | 4277851 | 1340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TACKETT & RUGGLES & SIMMONS // POLE BURNT OFF POLE 1123-620 BURNT OFF 15T LINE FUSE OUT 1123-477 RELEASED BY CREW 078S08 ///ENTERED MD COD-4 ISO LF @ 39831123B00477 /// //IT FORCE CLOSED VER/HFP L3/HFP
7984 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-11-04 16:22 | 2015-11-04 20:50 | 5 | 268 | 4410011 | 1340 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H04///BROKE CUTOUT ,NEED 72KV CUT OUT AND BRACKET,MANUAL.20:20 AND CLOSE AT20:50// VER/ ADH /// SEE H4410011 ALSO FOR OUTAGE TO REPAIR FOR 2 CUSTOMERS = L3/HFP XXXHFP
7985 | Pikeville | 3403001 | PIKEVILLE | CITY | 2014-02-13 16:22 | 2014-02-13 19:33 | 7 | 191 | 4384441 | 1337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 074S05// XFMR FUSE// WILL REFUSE// FUSE LINK BROKE// POWER IS RESTORED VER/KEP
7986 | Pikeville | 3402003 | KEYSER | MULLINS | 2014-01-08 13:19 | 2014-01-08 16:30 | 7 | 191 | 4260761 | 1337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | PAD MOUNT XFMR 38831127B00362 FUSE IS BLOWN DUT TO UNG. PED SHORTING OUT// CREW ENROUTE // REPAIRS MADE // POWER IS RESTORED VER/CRB L3/HFP HFP IDC XXXX
7987 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-11-14 18:29 | 2015-11-14 21:40 | 7 | 191 | 4448471 | 1337 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 1 LEG OUT ON UG // CREW ENROUTE TO INSTALL ADD A PHASE // VER/ARN
7988 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-04-11 16:58 | 2008-04-11 18:30 | 21 | 92 | 66305-1 | 1337 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED/ ISOLATED CUTOUT AND CLOSED LINE FUSE AT 17:55 STILL HAVE 4 CUSTOMERS OUT TILL GET CUTOUT CHANGED GOT XFRMER BACK ON 18:30 VER/HFP IDC XXXX
7989 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-09-12 19:46 | 2013-09-13 01:20 | 4 | 334 | 4847881 | 1336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200 LIGHTNING VER/KEP IDC XXXX
7990 | Hazard | 3310502 | HADDIX | CANOE | 2016-03-31 13:30 | 2016-04-01 11:46 | 1 | 1336 | 4009351 | 1336 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 LEG OF SERVICE AND NEUTRAL BURNED INTO,SEC BUSHING BROKEN ON TRANSFORMER, MAY NEED 15KVA 19.9 XFMR.OPENED XFMR FUSE TO MAKE SAFE. ONLY 1 CUST RELEASED BY CREW 077M02/ RIGHT XFRM IS 37830075000157/ CREW REQUIRED
7991 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-01-07 03:45 | 2009-01-07 11:10 | 3 | 445 | 52253-1 | 1335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S04//TRANSFORMER ON POLE 153-30 IS ALSO PROTECTED BY FUSE /COD 3//VER/CRB MD FILED L3/KEP IDC XXXX
7992 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-06-08 15:45 | 2015-06-08 20:12 | 5 | 267 | 4529111 | 1335 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 19.9KV. CAN USE TRUCK RELEASED BY CREW 074S02// ON SITE AND GETTING THE FLAGGERS IN PLACE TO REPLACE TRANSFORMER. CHANGED BAD TRANSFORMER AND RESTORED POWER AT 20:12TIM MCCOY RELEASED BY CREW 074H10 VER/HFP L3/HFP
7993 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-04-15 16:11 | 2014-04-15 23:35 | 3 | 444 | 4608441 | 1332 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TECH AND 3 MAN PRC CREW--LIFTED HOT TAP AND INSTALLED TAG AND GROUND ON POLE 38830019D00005 FOR B REYNOLDS--CALLED FIRE DEPT TO PUT OUT POLE FIRE RELEASED BY CREW 078S07 //VER/GAH
7994 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-07-15 21:16 | 2017-07-16 19:27 | 1 | 1331 | 4129671 | 1331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | GREG HEDRICK REPORTS OK TO WAIT TILL DAYLIGHT RELEASED BY CREW 074S11 FOUND LOOP BURNT OPEN ON POLE 37830115000184 IN PROCESS OF MAKING REPAIRS OPENED CUTOUTS ON POLE 216 AT AT 18:45 ALL RESTORED AT 19:27 D SAMMONS RELEASED BY CREW 074H02 37830115000177 VER/AWD // AEP TOWER SITE OUT & 1 CELL TOWER = L3/HFP HFPC LCD37830115000177 TOF1845 CNT2
7995 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-05-13 15:54 | 2012-05-13 17:55 | 11 | 121 | 4786131 | 1331 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN ON POLE #410-189 LINE FUSE OUT ON POLE #410A-20 //COD 11// VER/DBM IDC XXXX
7996 | South Williamson | 3202201 | LOVELY | LOVELY | 2014-03-28 10:52 | 2014-03-28 13:05 | 10 | 133 | 4531181 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 766-28///CUTOUT BROKE ONJ POLE 766-57//CUTOUT REPLACED//RESTORED AT 13:05//COMPLETE//EM VER/CRB
7997 | Pikeville | 3421001 | BREAKS | CITY | 2022-12-06 10:35 | 2022-12-06 13:45 | 7 | 190 | 4233421 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2 conductor down @ pole 197-154 will be making reoairs///Opened N/Cswitches on pole 197-27 @ 10:35///Closed switches 197-154 in @ 13:45 down to open switches on pole 197-27 and restored service Released by crew 074S02
7998 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2018-06-18 15:02 | 2018-06-18 17:15 | 10 | 133 | 4617081 | 1330 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | sec. riser burnt off of can, open wire sec. ready to fall. xfmer open @ 15:45. Released by crew 078S07Crew on site FETR 17:45. repairs made, transformer back in at 17:15/ ISO 39831147C14124/ COD 10 L3/HFP
7999 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2010-03-31 15:00 | 2010-03-31 16:35 | 14 | 95 | 56578-1 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER POLE 67-379. CLEARED UP FOR NOW. WILL BE CHANGING AFTER CLOSING RECLOSER IN COD-14 CCC VER/HFP L3/HFP AJB PH B.
8000 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-01-07 09:59 | 2014-01-07 14:25 | 5 | 266 | 4249141 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. 25 KVA 19.9 TRANS IS BAD ON POLE 216-7. CREW IS ON THE WAY. WE CHANGED TRANSFORMER.//COD 5// VER/DBM
8001 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-11-06 02:31 | 2011-11-06 06:57 | 5 | 266 | 4054511 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | SDB / 0101 / ALL OUT. CC 5. --- SDB / 0657 / FAILED TR FUSE. ALL RESTORED IDC CORRECTED FOR DST XXXX
8002 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-07-04 10:40 | 2012-07-04 21:45 | 2 | 665 | 4334241 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT.BAD XFMR.THIS IS POLE THAT WAS BROKE & LEANING AT LECKIEVILLE & TEMPORARILY RESET..BEHIND HOUSE 433..NON TRUCK ACCESS.CREW REQUIRED.JRV RELEASED BY CREW 080S01. REPLACED TRANSFORMER . CUSTOMER HAS BAD MTR BASE LEFT OFF . VER/KEP
8003 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2009-03-05 12:37 | 2009-03-05 13:15 | 35 | 38 | 55295-1 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3409401//OPENED THIS FUSE TO SAFELY MAKE REPAIRS FOR ORDER 55187-1//COD 35// VER/DBM IDC XXXX
8004 | Paintsville | 3401102 | FALCON | SALYERSVI | 2016-03-03 18:00 | 2016-03-03 22:05 | 8 | 245 | 4809401 | 1330 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE AT POLE 104 CLOSED AT 20:20, CLOSED TRANSFORMER POLE 137 AT 22:05, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 COD-8 DUP IN HOIS ********************
8005 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2021-08-21 18:00 | 2021-08-21 19:35 | 14 | 95 | 4133551 | 1330 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Secondary burned up @ 20-d4-7562. Opening transformer to make repairs. off @ 19:15 back on @ 19:35.
8006 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2021-04-17 02:47 | 2021-04-17 10:10 | 3 | 443 | 4457721 | 1329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN CUTOUT ON L/F 39831123C14059//COD 3//Broken cutout on 39831123C14059//Broken cutout on 39831123C14059. Change and restored @ 10:10
8007 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2022-03-13 21:34 | 2022-03-14 04:57 | 3 | 443 | 4621551 | 1329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 7200 nbt-crew req-ds031322/manual/ xfmr in @ 0457/ please close ticket/ MLH
8008 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-09-11 15:12 | 2014-09-11 22:35 | 3 | 443 | 4490511 | 1329 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 10 KVA TRANSFORMER IN BANK, C PHASE OR ROADSIDE CAN @ WEAVERTOWN. PAUL COFFEE RELEASED BY CREW 078H12/ CREW ON SITE/ WILL SPLIT WINDINGS ON REPLACEMENT XFMER/BANK VOLTAGE IS 120/208 // REPAIRS COMP. POWER REST. @ 22:35// JEH/// PLEASE CLOSE TICKET// COD 3// VER/ ADH
8009 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-05-06 21:46 | 2022-05-07 08:50 | 2 | 664 | 4855161 | 1328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | traffic rain...bad cutout.changing
8010 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-12-08 17:49 | 2009-12-08 20:35 | 8 | 166 | 57839-1 | 1328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 32992177 POLE 141-74 BAD 19.9 CUTOUT AND LA CHGED //COD 8 IDC XXXX
8011 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-02-02 10:32 | 2014-02-02 13:18 | 8 | 166 | 4336551 | 1328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CHECKING LINE OUT FOUND BROKE FUSE ON POLE 1124-2536 ALL POWER RESTROLED AT 13:18 PLEASE CLOSE TIC RM//COD 8// VER/DBM
8012 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-01-01 12:11 | 2014-01-01 17:43 | 4 | 332 | 4216991 | 1328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLWN// WILL REFUSE// BAD 100 KVA 7,200// NEED CREW// TRUCK APP.// XFMR CHANGED // POWER IS RESTORED VER/SEF IDC XXXX
8013 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-05-31 16:31 | 2018-05-31 17:54 | 16 | 83 | 4530251 | 1328 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 1060-208 will replace
8014 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-06-07 10:19 | 2016-06-07 14:00 | 6 | 221 | 4318351 | 1326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SERVICER INSTALLING U/G SERVICE AND WILL BE DELAYED ABOUT 2 HRS - ADJUSTING ETR BY 2 HOURS //HFP // FUSE OUT ON POLE 38831125A00171 & XFMR ON LOAD SIDE OF THIS FUSE... NEED MD // 40T LINE FUSE OUT ON POLE#38831125A00171. POWER RESTORED @ 14:00 COD-6 ISO LF 38831125A00171 *****ENTERED MD -- VER/HFP L3/HFP
8015 | Hazard | 3310502 | HADDIX | CANOE | 2021-06-19 00:43 | 2021-06-19 08:05 | 3 | 442 | 4769621 | 1326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change cutout on pole 37830051000108/ ISO 37830051000001/ COD 3
8016 | South Williamson | 3411401 | DEWEY | INEZ | 2014-02-13 02:22 | 2014-02-13 13:25 | 2 | 663 | 4377811 | 1326 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER WILL CHECK ONCE THE ROAD CONDITIONS INPROVE //DHE CREW GOING TO CHANGE XFMR RELEASED BY CREW 079S01 VER/HFP L3/HFP
8017 | South Williamson | 3411401 | DEWEY | INEZ | 2008-07-31 09:50 | 2008-07-31 14:15 | 5 | 265 | 62925-1 | 1325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401// CUTOUT BAD//COD 5// VER/DBM IDC XXXX
8018 | South Williamson | 3411401 | DEWEY | INEZ | 2010-09-16 10:39 | 2010-09-16 15:04 | 5 | 265 | 50389-1 | 1325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36911773 /// XFMR FUSE OUT.....NO TREES.....MAY HAVE BEEN BIRD OR SQUIRRELL.....WILL RE-FUSE...//...TOOK DOOR OUT...FUSE NOT BLOWN....SHOOK CUTOUT WITH STICK....TOP OF CUTOUT BROKEN....NEED CREW....CAN REACH WITH BUCKET...PLEASE SEND TO JOEY REED...THANKS....JRV RELEASED BY CREW 079H08 COD-5 VER/HFP L3/HFP IDC XXXX
8019 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-02-07 04:40 | 2018-02-07 09:05 | 5 | 265 | 4810481 | 1325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | customer checked breaker and reports neighbor is out // Dispatched in accordance with KYPCo Late Night Callout Guidelines Transformer fuse appears to have broke. Restored @ 9:05. sh
8020 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-10-08 14:43 | 2015-10-08 15:36 | 25 | 53 | H4327871 | 1325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR // @ 1443 CREW OPENED LINE FUSE TO SAFELY REPLACE BAD TRANSFORMER (25 CUST OUTAGED - 2 INITALLY OUT) ALL ON 1536 DUP OF 4327871 FOR FUSE OUTAGE VER/HFP L3/HFP AJB
8021 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2015-02-21 15:45 | 2015-02-21 20:10 | 5 | 265 | 4065261 | 1325 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER. CREW ON THE WAY RELEASED BY CREW 074S11// REPLACED BAD TRANSFORMER WITH A 37.5 CHECKED VOLTAGE AND RESTORED POWER AT 20:10 TIM MCCOY RELEASED BY CREW 074H10/ ISO 37830211C00315/ COD 5/ VER/BOW
8022 | Whitesburg | 3312902 | JENKINS | JENKINS | 2022-01-23 13:08 | 2022-01-23 15:35 | 9 | 147 | 4398411 | 1323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 382-A2-293. replaced cutout, power restored
8023 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2019-09-12 17:54 | 2019-09-12 20:21 | 9 | 147 | 4011161 | 1323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot clamp loose on 1037D66 nta repaired hot tap.restored power at 20:21. L3/HFP
8024 | Cannonsburg | 3001401 | LOUISA | CITY | 2014-08-30 19:20 | 2014-08-30 20:09 | 27 | 49 | 4439441 | 1323 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OPEN ON 454-1664 PATROLLING LINE, NOTHING FOUND WHILE PATROLLING LINE, FUSE APPEARED TO HAVE PULLED LOOOSE. APR AT 2009 CLOSE TICKET//COD 27// VER/DBM AJB
8025 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-03-26 10:05 | 2010-03-26 12:50 | 8 | 165 | 54617-1 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE AT POLE 37830225B00026 AT 10:05// POLE 37830225B00238 ON FIRE AT CUTOUT CALLING FOR CREW TO ASSIST RELEASED BY CREW 077S04//VER/CRB IDCC FP NULL XXXX
8026 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-04-22 14:37 | 2012-04-22 16:05 | 15 | 88 | 4694241 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE APPEARED TO BE BURNT REPLACED FUSE AND POWER IS RESTORED//COD 15// VER/DBM IDC XXXX
8027 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-10-15 11:03 | 2015-10-15 13:15 | 10 | 132 | 4351061 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD ARRESTER ON 833-387. CLEARED ARRESTER AND CLOSED 30T LINE FUSE ON 833-227 @ 13:15. SH/ ISO 38830833D00227/ COD 10/ VER/BOW L3/HFP XXXHFP
8028 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2018-11-15 03:40 | 2018-11-15 05:40 | 11 | 120 | 4400461 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout on 762-47 (Not on map) failed. L3/HFP
8029 | Pikeville | 2974101 | BIG ROCK STATION | CONAWAY | 2012-12-20 23:04 | 2012-12-21 00:10 | 20 | 66 | 4494991 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2974101// CREW OPENED FUSE 151D10 TO MAKE REPAIRS//CC--20//ALL CUSTOMERS RESTORED AT 0010 VER/TSH
8030 | Hazard | 3308001 | JACKSON | S.JACKSON | 2017-11-06 13:10 | 2017-11-06 16:50 | 6 | 220 | 4535391 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | got bad 25 / 7200 transformer, need transformer and cutout and arrestor and material handler bucket Released by crew 077S05 power restored at16:50
8031 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-02-27 17:21 | 2013-02-27 17:45 | 55 | 24 | 4861341 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4861051 SERVICER HAD TO OPEN RECLOSER TO ALLOW HIM TO SAFELY REPLACE BROKEN CUTOUT ///OFF 1721 ON 1745 // COD-55 ISO OCR 38830271C24005 VER/HFP L3/HFP IDC XXXX
8032 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2017-11-16 15:15 | 2017-11-16 17:27 | 10 | 132 | 4561541 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole fire on 1137A726 opened cutouts on this pole at 15:55 extinguished fire and i think i have enuff material to make repairs--made repairs replaced 2 cutouts and arrestors and 2 arm pins 19.9 opened 1137A64 at 16:33 closed 1137A64 at 17:27 restoring all customers pole is burnt somewhat at cutout brackets plz send copy to Cliff Freeman Released by crew 079H03 38821137A00064 38821137A00726
8033 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-09-13 12:45 | 2016-09-13 15:30 | 8 | 165 | 4889291 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WILL WORK AT START TIME CALLED CUSTOMER HE HAS HIS BREAKERS OFF CREW COMMING TO SET POLE AND AND NEW UNDERGROUND RELEASED BY CREW 077S05 OPENEDTRANSFORMER ON POLE 782 AT 12:45 CLOSED BACK BAT 13:30 POWER RESTORED TO LAST CUSTOMER AT 15:30 VER/CRB L3/HFP XXXHFP
8034 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-04-15 11:46 | 2012-04-15 16:10 | 5 | 264 | 4674041 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED 50 KVA 5 CUST OUT TRUCK TO POLE RELEASED BY CREW 078S08/ FETR 17:00/ JEH/ XFMER CHANGED OUT. UPRADED TO 37.5 ALL POWER REST.@ 16:10////078H05 ///VER/CRB IDC XXXX
8035 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-03-27 15:19 | 2017-03-27 17:09 | 12 | 110 | 4589151 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 95-38///WILL PATROL...FOUND BAD XFM. CUTOUT ON POLE 95-202 THIS IS NON-TRUCK APPROACH WILL MAKE REPAIRS.. REPAIRS MADE..CLOSED BACK IN @ 17:09 VER/CRB L3/HFP HFPC CDC92
8036 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-05-24 00:15 | 2017-05-24 11:15 | 2 | 660 | 4846701 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 19.9 CUTOUT-CLIMB JOB---GIVE TO RUSS,I WILL SEND CLEMONS OR SOMEONE TO HELP-ALL READY ON FIBER BR--JIM COD-2 ISO LF 37830246B00002 VER/HFP L3/HFP
8037 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-04-18 20:30 | 2010-04-18 22:20 | 12 | 110 | 64850-1 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ... REPLACED CUTOUT, TREES WITHIN INCHES OF PRIMARY ON THIS TAP / SEND TO FORESTY // COMPLETE / GXJ VER/LDA IDC XXXX
8038 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-02-11 15:45 | 2013-02-11 18:30 | 8 | 165 | 4810941 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT. ///VER/CRB L/3 CRB IDC XXXX
8039 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-04-23 15:46 | 2010-04-23 20:10 | 5 | 264 | 50037-1 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER, 7200 120/240 SINGLE BUSHING. 3 SERVICES FROM THIS POLE. CANNOT USE TRUCK, CAN USE WINCH.. ..DAH RELEASED BY CREW 074S08 WR. 34812605 VER/KEP L3/KEP IDC XXXX
8040 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-10-25 10:40 | 2008-10-25 16:10 | 4 | 330 | 58915-1 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | VER/HFP STS WR # 26957491 //SERVICER OPENED SOLID BLADE @ POLE 38830208000041 PLACED GROUNDS AND FLAGED POLE; OLD POLE IS 40/5 NEED TO GO BACK WITH 45/5. RELEASED BY CREW 078S01/CREW ON SITE/FETR1730/REPAIRS MADE AND POWER RESTORED TO ALL CUST AT 1609/PLEASE CLOSE TICKET/THANKS/VEM COD-4 ENTERED MD- HFP IDC XXXX
8041 | Hazard | 3311101 | STINNETT | REDBIRD | 2020-04-27 10:00 | 2020-04-27 13:40 | 6 | 220 | 4756811 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bill McCoy - NOC, reports Asher Radio Tower is out of powerChanged bad arrester @ pole 37830531B40175. Power restored @ 13:40
8042 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-01-02 17:20 | 2020-01-02 19:10 | 12 | 110 | 4204931 | 1320 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | replaced arrester on pole 51 and refused line fuse power restored at 19:10 L3/HFP
8043 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-08-23 17:46 | 2014-08-24 15:45 | 1 | 1319 | 4414721 | 1319 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQD. BAD 7200- 25 KVA, NO TRUCK RELEASED BY CREW 078H12//CONTACT M PHELPS TO DISCUSS ACCESS.. 25 KVA REPLACED AND CUSTOMER RESTORED AT 15:45.. COMPLETE CAY VER/CRB
8044 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2012-06-18 06:56 | 2012-06-18 17:55 | 2 | 659 | 4925311 | 1318 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CONTACTED CREW //BAD 10KVA// COD-2 ISO TF 38830376000075 VER/HFP L3/HFP IDC XXXX
8045 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-02-18 03:07 | 2015-02-18 14:05 | 2 | 658 | 4037811 | 1316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 37830177C00013, PATROLING LINE...37830177C00164 BURNT OFF AT CUTOUT, NEED 40 CL 4, CUTOUT AND ARR, TEE BR, 2 GUY COMPLETE, 2 - 19.9 DEADEND INS. MANUAL POLE, MAY BE ABLE TO WORK WITH TRUCK IF CUST. WILL MOVE CARS. RELEASED BY CREW 077S04//COD 2// VER/DBM L3/HFP XXX
8046 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-07-16 06:12 | 2009-07-16 11:41 | 4 | 329 | 64189-1 | 1316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP XFR CUTOUT BURNED UP,NOT EVIDENT UNTIL VERY CLOSE VISUAL,NOTE FETR CHANGE/REPLACED BAD CUTOUT AND RESTORED,ALL OK AFTERWARDS COD-4 ISO REC 37820053000280 L3/HFP IDCC CDC92 XXXX
8047 | South Williamson | 3411401 | DEWEY | INEZ | 2018-07-04 19:44 | 2018-07-05 17:40 | 1 | 1316 | 4725001 | 1316 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke---need one 19.9 kv cutout & arrester for xfrm pole # 769-126--need some to climb pole Released by crew 074M06
8048 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2009-02-05 05:45 | 2009-02-05 08:11 | 9 | 146 | 55774-1 | 1314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE. ISOLATE ON POLE 47-32. ON AT 08:00AM RELEASED BY CREW 074S05 REPLACE C/O AND ARRESTOR ON 155 ON AT 12:09 COMPLETE D SAMMONS //VER/GAH
8049 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2015-04-01 13:48 | 2015-04-01 17:27 | 6 | 219 | 4255731 | 1314 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER. NEED 25KVA ARRESTER CUTOUT. CAN USE TRUCK RELEASED BY CREW 074S11.XFMR HAS BEEN REPLACED AND POWER RESTORED.D LEWIS/COD 6/ CLOSED 1727 L3/GSL// VER/ ADH
8050 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2010-04-16 12:08 | 2010-04-16 13:49 | 13 | 101 | 63780-1 | 1313 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT .. POWER RESTORED AT 13:49//COD 13// VER/DBM IDC XXXX
8051 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2015-08-19 14:54 | 2015-08-19 16:16 | 16 | 82 | 4153751 | 1312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | FUSE IS OPEN ON38830454B43509 LARGE TREE FELL BREAKING ONE SPAN OF #4 ALUM TRUCK OK, LINECREW ONLY REQUIRED RELEASED BY CREW 078S11 WIRE PUT BACK UP CLOSED FUSE ON PN 454-3509 AT 16:16 PLEASE CLOSE TICKET THANKS DWW VER/CRB L3/HFP
8052 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-09-04 13:01 | 2015-09-04 15:45 | 8 | 164 | 4197941 | 1312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75 KVA 2 BUSHING 7200, 150 VOLTS 1 LEG, 80 OTHER LEG. BESIDE ROAD RELEASED BY CREW 078S07---BAD NEUTRAL CONNECTION @ THE NEUTRAL BUSHING ON XFMR(RISER)---MADE REPAIRE---VOLT CK GOOD---126-126-243---TBL TKT COMP VER/CRB L3/DKG CHECKED VOICE RECORDER, TIMES WERE NOT MENTIONED
8053 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-08-28 20:26 | 2008-08-28 20:42 | 82 | 16 | H56954-1 | 1312 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 3000701AT 2026 OPENED N.O. SWS ON POLE 1072-5025 DUE TO PHASING , ALL CUSTOMERS RESTORED AT 2042 VER/PDP IDC XXXX
8054 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-04-12 20:26 | 2017-04-12 21:35 | 19 | 69 | 4641921 | 1311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD FUSELINK IN L/F, PATROLLED FOUND NOTHING WRONG, REPLACED FUSE POWER RESTORED AT THIS LOC AT 2135 BY AMG 39830975000061 VER/AWD L3/HFP HFPC CCU FEC57 FP
8055 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-05-01 15:24 | 2019-05-01 16:33 | 19 | 69 | 4195061 | 1311 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | resaged primary and neutral @ 208-58 and tied up telephone across road ,,line fuse 208-20 back in @ 16:33 complete L3/HFP
8056 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-04-05 13:34 | 2011-04-05 13:51 | 77 | 17 | 62981-1 | 1309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREE ON TAP UP ON CLIFF ACROSS FROM SWAN CT. JUST BEFORE COATES BR. ARY . NEED ROW CREW AND 2 MEN. RELEASED BY CREW 077S04TREE ON TAP UP ON CLIFF ACROSS FROM SWAN CT. JUST BEFORE COATES BR. ARY . NEED ROW CREW AND 2 MEN. POWER RESTORED, SAME AS 65917.//VER/CRB IDC CHANGED START DATE FROM 1808 4/4 CREATED SEPARATE OUTAGE FOR 1 CUSTOMER XXXX
8057 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-03-13 12:20 | 2014-03-13 15:27 | 7 | 187 | 4488941 | 1309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4486601 // CREW REPLACING BURNT OFF 60` POLE // OPENED RECLOSER ON POLE 37820098B00572 @ 1210 4 CUST THEN OPENED NEWLY INSTALLED SWS ON POLE 37820098B00024 @ 1220 7 CUST // DALE HAS KENNY BROOM & DEWEY AKERS CREWS WITH HIM // CLOSED SW @ 1527 & RECL @ 1530 THIS IS SWITCH RECORD VER/HFP L3/HFP
8058 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2019-03-10 12:08 | 2019-03-10 12:15 | 187 | 7 | 4967551 | 1309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OFF @ 1208 ON @ 1215 RESTORING CKTS NORMAL L3/HFP
8059 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-03-05 08:50 | 2008-03-05 10:49 | 11 | 119 | 53698-1 | 1309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3410602//FUSE LINK APPEARS TO HAVE BROKEN. RE-FUSED LINE CUTOUT ON POLE 38831004000008 (25T). SH//VER/CRB IDC XXXX
8060 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-01-13 20:13 | 2019-01-13 21:30 | 17 | 77 | 4669391 | 1309 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | loop open @ 69-1063, restored// cod 17//iso L3/HFP
8061 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-10-11 02:49 | 2014-10-11 10:05 | 3 | 436 | 4604861 | 1308 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BAD CHANGING/// CHANGED OUT C/O, REFUSED LINE FUSE ON POLE 37830387B00063///POWER RESTORED CCC ENTERED MD // COD-3 ISO LF 37830387B00063 VER/HFP L3/HFP
8062 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-02-12 10:20 | 2009-02-13 08:06 | 1 | 1306 | 50564-1 | 1306 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKEN ON 4/3 SERVICE DROP, NOT 9 CUST OUT, JUST ONE, HAVE REPAIRS MADE, EVERYTHING IS OK AT THIS LOC//VER/CRB
8063 | Hazard | 3309302 | VICCO | JEFF | 2008-07-05 09:10 | 2008-07-05 11:35 | 9 | 145 | 62714-1 | 1305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 3348-113...... BAD CUTOUT ON POLE #348-117....REPLACED CUTOUT RESTORED POWER AT 11:35 CUSTOMER COUNT IS INCORRECT COD-9 VER/HFP IDC XXXX
8064 | South Williamson | 3200302 | BELFRY | TOLER | 2019-05-03 06:43 | 2019-05-03 09:08 | 9 | 145 | 4206271 | 1305 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Replaced the line fuse that had broke.
8065 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2011-06-11 23:23 | 2011-06-12 10:15 | 2 | 652 | 4299611 | 1304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRMR FUSE OUT POLE 941B72..WILL RE-FUSE..//..FUSE LINK JUST BROKE..NO FAULT..REPLACED OLD CUTOUT DOOR & RE-FUSED XFMR..POWER ON..JRV..06/12/11//COD 2// VER/DBM IDC XXXX
8066 | Hazard | 3420001 | SOFT SHELL | VEST | 2015-02-21 13:17 | 2015-02-21 16:00 | 8 | 163 | 4063931 | 1304 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 133-148, PATROLLING LINE, FOUND BAD ARRESTER ON POLE 133-52, POWER RESTORED//COD 8// VER/DBM
8067 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-11-23 14:33 | 2019-11-23 17:16 | 35 | 163 | 4059681 | 1303 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 300 amp solid blade cutout failed on sw pole 876-367 - PH A.//COD 4 FROM THE BEGINNING OF OUTAGE//OPENED OTHER 2 PHASES @ 1655// Replaced two 300 amp sw cutouts and restored @ 17:16. sh Released by crew 076S02
8068 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-11-01 16:11 | 2018-11-01 23:25 | 3 | 434 | 4351891 | 1302 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Need 50kva 7200 and new risers, riser is melted out. crew required. Truck ok with 4 mow pads Released by crew 078S11/arrived RM opened xfm@22:24 closed@23:25 please close tic RM L3/HFP
8069 | Hazard | 3303902 | LESLIE | WOOTON | 2009-01-08 06:53 | 2009-01-08 10:30 | 6 | 217 | 53215-1 | 1302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3303902 -REPLACE BAD INSULATOR VER/KEP L3/KEP IDC XXXX
8070 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-08-07 16:53 | 2022-08-07 20:30 | 6 | 217 | 4699871 | 1302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed on transformer bank 875-515 blowing ph C line fuse on 875-237. Opened other two fuses @ 19:05 to make repairs. Replaced cutout and restored @ 20:30. sh//cod 6
8071 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2010-04-01 19:45 | 2010-04-01 23:22 | 6 | 217 | 57243-1 | 1302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 34501363 // BAD 50 KVA TRUCK OK SEND TO LLOYD MC. RELEASED BY CREW 078S08/ MCCARTY AND RUGGLES MAY TAKE SOME EXTRA TIME WITH JUST 2 MEN//COD 6// VER/DBM IDCC MCCDIS XXXX
8072 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2018-07-21 16:32 | 2018-07-21 19:38 | 7 | 186 | 4829091 | 1302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | related to previous outage 4813481; recloser came back out cc118 open SB 1041b209 to isolate closed in rec. 17b443 @???? restorring 30ccrelated to previous outage 4813481; recloser came back out.found phase laying on the arm at pole 1041-c-108..isolated trouble at pole 1041-b-209..closed recloser on pole 1017-b4-443a @ 17:55
8073 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-12-08 16:11 | 2022-12-08 19:48 | 6 | 217 | 4243671 | 1302 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9Line fuse cutout broke on pole 193-207 feeding tap toward pole 193-323///Shawn Goble is coming to assist//Changed cutout and restored service @ 19:48
8074 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-07-28 00:30 | 2013-07-28 02:40 | 10 | 130 | 4599171 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED ARRESTOR ON POLE #38831077B00521. CLOSED A PHASE OCR @ 02:40 WILL CHANGE BAD COTOUT ON POLE #38831077000296 VER/CRB L/3 CRB IDC MOST CALLS WERE ON C BUT I THINK THEY WERE MISSMAPPED BECAUSE OF THE NUMBER OF CALLS. XXXX
8075 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-06-03 16:04 | 2008-06-03 18:14 | 10 | 130 | 55122-1 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401002/// RELATED TO ORDER 55026-1 //ONLY B PHASE RECLOSER OUT 8 CUSTOMERS ON POLE 37830165000021//WE HAVE 3 SINGLE RECLOSERS ON POLE 165-21. JUST 1 RECLOSER IS OPEN. WITH BACK TO THE STATION IT WILL BE LEFT HAND PHASE. SHOULD BE B PHASE ACCORDING TO MAP. I AM GOING TO PATROLL LINE. 6 DEADEND DISK IS BURNED UP ON POLE 165-144. WILLIE IS SENDING HELP. WE CHANGED INSULATOR.//3401002//VER/CRB
8076 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-04-30 13:39 | 2021-05-01 11:19 | 1 | 1300 | 4503841 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew req. bad 25kva truck okay if dry feeds camper nobody here Released by crew 078S06///this feeds a camper will work in AM of 05/01/21 BR Released by crew 078H22crew req. bad 25kva truck okay if dry feeds camper nobody here Released by crew 078S06///this feeds a camper will work in AM of 05/01/21 BR ////Complete @ 11:19 BR
8077 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2008-10-20 07:30 | 2008-10-20 09:40 | 10 | 130 | 57171-1 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP STS WR # 26855395 FOUND A SPAN OF 6A PRIMARY DOWN ON POLE 18-62, NEED CREW TO MAKE REPAIRS, I HAVE LINE GROUNDED ON POLE18-58 CAN USE TRUCKS ON THIS RELEASED BY CREW 078S06 IDC XXXX
8078 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-12-28 02:35 | 2017-12-28 04:45 | 10 | 130 | 4683701 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 hot legs burndt into on pole 24-D2-482, had to open trans. bank on this pole to make repairs, opened @0422, closed back in @0445.
8079 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2013-11-21 18:05 | 2013-11-21 23:30 | 4 | 325 | 4063561 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA// NEED 1 MAN // BUCKET// 50 KVA-7200// XFMR BAG// OIL SPILL ON GRD NEEDS CLEANED// POWER IS RESTORED// SEND TO T. HALL//EMAILED TO T HALL//COD 4// VER/DBM
8080 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-03-26 13:39 | 2009-03-26 14:05 | 50 | 26 | 61777-1 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411901//SERVICER OPENED RECLOSER TO ASFELY REPAIR CUTOUT//COD 50// VER/DBM IDC XXXX
8081 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-12-15 10:40 | 2020-12-15 15:00 | 5 | 260 | 4770981 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replace broke cutout////////had to open to repair 2 services that were damaged by a piece of equipment.cutout fell apart when i opened it.replaced it after getting ddc to create me a ticket
8082 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-06-03 17:40 | 2008-06-04 04:30 | 2 | 650 | 55247-1 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07 POLE 68-628 BAD 25 KVA TRUCK TO POLE WOODBINE AND BYBEE RD RELEASED BY CREW 078S08//3001101 IDCC CNT1 XXXX
8083 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-07-22 17:46 | 2010-07-22 23:11 | 4 | 325 | 55724-1 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS FUSE OUT ON 809-459 GOING TO GIVE IT A SHOT//TRANSFORMER IS BAD CALLED CREW TO CHANGE//TRANSFORMER CHANGED POWER RESTORED AT 2311 COMPLETE TT VER/ARN IDC XXXX
8084 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-12-13 19:23 | 2020-12-14 00:48 | 4 | 325 | 4765211 | 1300 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25KVA XFM need a A lineman with material handler.. opened XFM at 23:50 closed at 00:48
8085 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-02-25 10:26 | 2022-02-25 17:39 | 3 | 433 | 4545081 | 1299 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 19.9 15 kva manual.. Also gonna need a manual row crew 19.9 cutout Released by crew 077H05
8086 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-07-10 08:15 | 2013-07-10 08:37 | 59 | 22 | 4494501 | 1298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | OUTAGE FOR CREW TO SAFELY MAKE REPAIRS. VER/ARN IDC XXXX
8087 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-08-20 08:11 | 2014-08-20 19:00 | 2 | 649 | 4388291 | 1298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 38821139B00037/// NOT SHOWN ON MAP/// JOEY REED CAN WORK THIS ORDER WHEN HE FINISHES UP ON THE ORDER HE ALREADY HAS/// WONT BE ABLE TO GET TO IT UNTIL 1600.BAD CUTOUT HAS BURNED PART THROUGH CROSSAR& FELL IN THE CLEAR. NEED 7200 CUTOUT. NO TRUCK, JOEY REED WILL HEAD THIS WAY WHEN HE CLEARS UP ON A BROKE POLE AROUND 16:00. RELEASED BY CREW 079S02.OP SW (SEE 4391531)AT POLE 1139-109 AT 18:11 CLOSED SWITCHES AT 19:00 RELEASED BY CREW 079H07//MADE MD ADH// VER/ ADH AJBC LCD38821139B0010 CNT280
8088 | South Williamson | 3411401 | DEWEY | INEZ | 2018-03-24 17:02 | 2018-03-25 14:40 | 1 | 1298 | 4051611 | 1298 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout broken,pole 744d-343, will need 19.9 kv cutout,truck access , servicer,,jdm Released by crew 077E01//repairs made//restored at 14:40//complete//em
8089 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-05-05 12:33 | 2021-05-05 15:15 | 8 | 162 | 4539071 | 1296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 174-c2-535. replaced and restored power at 15:15
8090 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2012-12-26 11:15 | 2012-12-26 12:27 | 18 | 72 | 4526001 | 1296 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMERS ENTRANCE CABLE SHORTED OUT CAUSED CONECTOR FAILURE ON SECONDAY CONNECTION AT TRANSFORMER POLE// REMOVED METER# 532280257--MADE REPAIRS--SEND TO MARTIN TO CHECK POLE 38830045D16045 FOR REPLACEMENT //VER/GAH IDC XXXX
8091 | South Williamson | 3202201 | LOVELY | LOVELY | 2019-10-16 07:19 | 2019-10-16 10:55 | 6 | 216 | 4144441 | 1296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 674-344//cutout broke on 674-345//replaced cutout//restored at 10:55//complete//em
8092 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-03-25 00:27 | 2020-03-25 02:15 | 12 | 108 | 4507681 | 1296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | patrolling--38830452000042 30t lat blown--in at 02:15
8093 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-11-27 14:54 | 2012-11-28 12:30 | 1 | 1296 | 4426111 | 1296 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | DANGER OPEN MANHOLE IN STATE RIGHT AWAY AT THIS LOCATION--SERVICE NEUTRAL BROKEN AT SIGN--HOLD TILL MORNING RELEASED BY CREW 078S07DANGER OPEN MANHOLE IN STATE RIGHT AWAY AT THIS LOCATON--SERVICE NEUTRAL BROKEN AT SIGN--HOLD TILL MORNING /// REPAIRED SERVICE VER/HFP L3/HFP IDCC CCO XXXX
8094 | South Williamson | 3411401 | DEWEY | INEZ | 2011-04-28 10:16 | 2011-04-28 15:40 | 4 | 324 | 51240-1 | 1296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PAUL MUNCEY FOUND BAD XFMR- WILL MAKE ARRANGEMENTS TO REPLACE..//VER/CRB IDC XXXX
8095 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-02-11 07:36 | 2008-02-11 09:24 | 12 | 108 | 58832-1 | 1296 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CONNECTION BURNED APART ON XFMR SECONDARY RISER. RE-WORKED SECONDARY SIDE OF XFMR. RESTORED TO SERVICE AT 9:24. SH VER/HFP IDC XXXX
8096 | Pikeville | 3408103 | SALISBURY | MARTIN | 2012-08-05 19:30 | 2012-08-05 20:07 | 35 | 37 | H4899331 | 1295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEFT HAND PHASE WITH BACK TO STATION OUT DUE TO LOOP BURNT INTO. NEED 2 MEN 3 CUTOUTS NOT TRUCK ACCESIBLE. THIS LOOKS LIKE A PHASE. OPENED UP B AND C PHASES AT 19:30 CLOSED BACK IN AT 20:07. REPLACE ALL 3 CUTOUT. EVERYTHING OK. A = 15 CC B/C = 40 CC. VER/SDB IDC XXXX
8097 | Hazard | 3309302 | VICCO | JEFF | 2018-11-15 14:05 | 2018-11-15 18:24 | 5 | 259 | 4422781 | 1295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS @ 3783-0276-00-0115/ pole fire, pole # 276-159. dead-end straight line pole, single phase, can use pole top extension/ ISO 37830276000115/ COD 5 L3/HFP
8098 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-06-26 09:41 | 2015-06-26 14:00 | 5 | 259 | 4661691 | 1295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 1108-45, BAD ARRESTOR ON POLE 1108-77, WILL BE WORKING ON IT./// ARRESTOR CHANGED AND LINE HOT./ ISO 38831108A00045/ COD 5/ VER/BOW
8099 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-03-05 11:35 | 2019-03-05 14:40 | 7 | 185 | 4953211 | 1295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Load side riser burnt off on step down 37820194C00335 will open high side and make repairs//COD 7//Load side riser burnt off on step down 194-335 will open high side and make repairs/// Repaired load side riser and closed load side fuse in @ 14:40 and restored service
8100 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-03-02 21:28 | 2010-03-03 00:33 | 7 | 185 | 62397-1 | 1295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT FAILED POLE 37830247D00864 BURNED INTO CALLING FOR CREW//LOWEREDE PRIMARY WILL CHANGE POLE TOMORROW VER/PDP IDC XXXX
8101 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2016-02-08 06:43 | 2016-02-08 09:48 | 7 | 185 | 4682241 | 1295 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOOR BURNED OUT OF CUTOUT,WILL REPLACE DOOR OR CUTOUT,WHICHEVER IS NECESSARY////////////REPLACED DOOR AND RESTORED,ALL OK AFTERWARDS VER/AWD L3/HFP XXXHFP
8102 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-07-22 11:18 | 2013-07-22 12:45 | 37 | 87 | 4575231 | 1294 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LOW SIDE STEPDOWN FUSE BLOWN ON POLE 38831101D30126 BAD CSP XFMR ON POLE 38831101D30130 ISOLATED XFMR GOING TO RESTORE ALL BUT ONE CUSTOMER STEPDOWN IN @ 11:50 XFMR ON POLE 38831101D30130 RESTORED @ 12:45 RELEASED BY CREW 074H18//COD 37// VER/DBM IDC XXXX
8103 | South Williamson | 3411401 | DEWEY | INEZ | 2020-09-13 14:44 | 2020-09-13 16:00 | 17 | 76 | 4457681 | 1292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 770-a-275///cutout broke on pole 770-c-163//i replaced cutout//restored at 16:00//complete//em
8104 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-06-03 13:17 | 2013-06-03 18:40 | 4 | 323 | 4214921 | 1292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER... POWER RESTORED AT 18:40 //COD 4// VER/DBM
8105 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-11-13 13:27 | 2013-11-13 14:35 | 19 | 68 | 4036171 | 1292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLLING LINE. FOUND NO PROBLEMS. FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 14:35 // COD-19 ISO LF 38830760B00261 VER/HFP L3/HFP IDC XXXX
8106 | Whitesburg | 3309302 | VICCO | JEFF | 2014-11-01 19:44 | 2014-11-01 21:00 | 17 | 76 | 4689421 | 1292 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENING LINE FUSE 397-176 TO ISOLATE POLE FIRE//BAD C/O ON POLE 397-147, OPENED L/F AT POLE 397-176 AT 19:44 TO SAFELY PUT OUT. WILL BE MAKING REPAIRS.BAD C/O ON POLE 397-147, OPENED L/F AT POLE 397-176 AT 19:44 TO SAFELY PUT OUT. WILL BE MAKING REPAIRS.MADE REPAIRS CLOSED L/F AT 2100. VER/DKG L3/DKGXXXC TOF1847 CUST WAS REPORTING POLE FIRE AT 1847/POWER INTERRUPTED AT 1944
8107 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-01-30 06:12 | 2014-01-30 10:30 | 5 | 258 | 4327111 | 1290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830563000018 === NEED LINE CREW AND CUTOUT FOR 34.5 === CHANGED CUTOT ==== OPEN LINE AT 9:54 CLOSED AT 10:30 === ALLPOWER ON 5 INITALLY OFF INTERRUPTED 21 @ 0954 ALL ON @ 1030 ENTERED MD DUP IN HOIS VER/HFP L3/HFP IDC XXXX
8108 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2014-01-30 09:44 | 2014-01-30 14:02 | 5 | 258 | 4328781 | 1290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 TRANSF === CALLED TIM SMITH TO CHANGE OUT TRANSF RELEASED BY CREW 077S03 REPLACED WITH 50KVA POWER RESTORED AT 14:02 COD5 ISO 37830343D00207 VER/HFP L3/HFP
8109 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2015-02-20 14:34 | 2015-02-20 18:09 | 6 | 215 | 4057211 | 1290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED 1/0 SECONDARY WITH 4/0 POWER RESTORED AT 18:09 OPEN XFM ON POLE 449-33 AT 17:05 // 4054011 & THIS ORDER 4057211 ARE RELATED SOME HOW // NEED MORE INFORMATION - VER/HFP
8110 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-06-18 06:39 | 2013-06-18 13:49 | 3 | 430 | 4361821 | 1290 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK IN THE AM ON 6-18-13,,WILL NEED CUTOUT , 7.2 KV,, TRUCK ACCESS,,FLAGGERS NEEDED,,,JDM RELEASED BY CREW 077E01;;; ON SITE WORKING BAD CUTOUT IS ON POLE 151 60 - CAN CLOSE TICKET POWER HAS BEEN RESTORED MWL
8111 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-01-12 10:53 | 2022-01-12 16:15 | 4 | 322 | 4338881 | 1288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke line fuse cutout 7200, truck acess big bucket with flaggers Released by crew 077S07bad 7.2v cutout. crew on site. p.hicksbad 7.2v cutout. crew on site. p.hicks.. all power restored @ 16:15 p.hicks
8112 | Hazard | 3309301 | VICCO | REDFOX | 2010-01-02 00:26 | 2010-01-02 11:10 | 2 | 644 | 56459-1 | 1288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR, NEED 2 MEN AND 25 KVA 7200 , CAN USE BIG BUCKET / DUTY SUPV WILL GET CREW STARTED AT DAYBREAK.XFMR FUSE OUT, BAD XFMR, NEED 2 MEN AND 25 KVA , CAN USE BIG BUCKET RELEASED BY CREW 077S02 COD-2 VER/HFP L3/HFP IDC XXXX
8113 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-02-05 19:48 | 2011-02-05 20:34 | 28 | 46 | 54708-1 | 1288 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREWS OPENED STEPDOWN IN ORDER TO MAKE REPAIRS RELATED TO ORDER 54551-1 //COD 28// VER/DBM IDC XXXX
8114 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-08-06 11:01 | 2022-08-06 21:45 | 2 | 644 | 4691171 | 1288 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | left side hot leg on the 4/0 underground service has gone bad Released by crew 078S12. crew on site. put power temp on for now will come back at a later date for permanent repairs complete
8115 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-07-21 20:43 | 2018-07-21 22:40 | 11 | 117 | 4830771 | 1287 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 1130-184 NTA replaced cutout restored power at 22:40
8116 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2019-11-09 08:17 | 2019-11-09 13:00 | 14 | 283 | 4014331 | 1286 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | cut service drop down comeing from pole 38830045D37237 going to inactive meter532296083. transformer off at 1200 back on at 1300//part power for 2 custs until trans opened L3/HFP
8117 | Pikeville | 3402002 | KEYSER | STONECOAL | 2009-03-31 05:23 | 2009-03-31 09:40 | 5 | 257 | 63260-1 | 1285 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3402002//LEAD BURN OFF ON THE TRANSFORMER ON THE SECONDARY SIDE//OPENED TRANSFORMER @ 0920 TO MAKE REPAIRS//3402002// RISER WIRE AT TRANSFORMER MELTED INTOCOD 5// VER/DBM IDC XXXX
8118 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-12-25 09:51 | 2018-12-25 13:25 | 6 | 214 | 4597621 | 1284 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: neighbor is out also/ neighbor heard loud noise/ Customer cant access meter Transformer cutout failed. Additional personnel enroute to assist. Replaced cutout and bracket. Restored @ 13:25. sh/ ISO 38830882D00157/ COD 6 L3/HFP
8119 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-11-27 00:05 | 2017-11-27 10:46 | 2 | 641 | 4603281 | 1282 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /line fuse cutout on pole 37830147000040 is broke letting fuse fall open. Released by crew 077H11
8120 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-10-15 21:09 | 2017-10-16 04:16 | 3 | 427 | 4460021 | 1281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FUSE IS OPEN ON 38830258000054 NO GROUNDS OR TAGS PLACED. #2 PRIMARY DN @ 258-74 CREW REQUIRED. RELEASED BY CREW 078S11/ON SITE RM POWER ON AT 04:16 PLEASE CLOSE TIC RM//VER/ADH L3/HFP XXXHFP
8121 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-10-19 15:23 | 2020-10-19 16:24 | 21 | 61 | 4568401 | 1281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 65t open @ 20-4507, #2 al pri down between 20-1554 to1553. no trk. access 115 bellefonte dr Released by crew 078S07
8122 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-10-20 19:18 | 2011-10-21 02:25 | 3 | 427 | 4005871 | 1281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5 NEED 37.5 OR 50KVA NO TRUCKS MITE BE ABLE TO GET SMALL MACHINE UP TO POLE USE LEFT GATE LARGER SEND TO CREWS RELEASED BY CREW 078S08 IDC XXXX
8123 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-06-19 20:44 | 2020-06-19 23:47 | 7 | 183 | 4049161 | 1281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva, 120-240 7200. replace w/25. trk to pole Released by crew 078S07///on site replacing xfmr///complete BR
8124 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2019-06-05 21:26 | 2019-06-06 00:29 | 7 | 183 | 4434521 | 1281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed. Cleared vines, replaced bracket and broken cutout. Restored @ 00:29. sh/ ISO 38830954B40078/ COD 7/ ISO 38830954B40078/ COD 7 L3/HFP
8125 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-09-29 11:57 | 2014-09-29 12:58 | 21 | 61 | 4535791 | 1281 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE 850-56//UNABLE TO NOTIFY CUSTS VER/CRB AJB
8126 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-02-23 19:25 | 2014-02-23 21:33 | 10 | 128 | 4429141 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 3 MAN CREW--BAD 19.9 CUTOUT--MAYBE TRUCK TO POLE WITH PADS RELEASED BY CREW 078S07/CREW ON SITE/FETR2215/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2133/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH
8127 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-02-01 21:02 | 2015-02-01 23:42 | 8 | 160 | 4979721 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED ON 786-151 AND BLEW LINE FUSE 786-176. REPLACED CUTOUT AND CLOSED LINE FUSE @ 23:42. SH/ ISO 38830786B00176/ COD 8/ VER/BOW L3/HFP XXX
8128 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-05-15 22:20 | 2010-05-16 00:51 | 10 | 151 | 63013-1 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ON SITE, PATROLLING LINE, CLOSED 20T FUSE ON POLE#32-B-22(MD FILED) AT 0005 , UP TO POLE#32-B-25, BAD ARRESTER ON POLE#56-508, CLOSED AT POLE#32-B-25 AT 0051 VER/KEP L3/KEP IDCC TON 0051 XXXX
8129 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-07-10 06:15 | 2015-07-10 11:35 | 4 | 320 | 4761281 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | 2 LINE FUSES BLOWN ON 1084-307 AND GUY WIRE PULLED LOOSE AND LYING AT POLE--EVERYTHING ELSE LOOKS OK.077M01--BK RELEASED BY CREW 077M01
8130 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-05-03 17:40 | 2016-05-03 23:00 | 4 | 320 | 4171231 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON 795C85 I WILL B CHANGING IT OUT REPLACED CUTOUT RESTORED POWER AT 23:00 COD-4 ISO TF 38820795C00085
8131 | Pikeville | 3407101 | TOPMOST | DEMA | 2010-04-26 20:15 | 2010-04-27 01:35 | 4 | 320 | 51691-1 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILURE, POLE BURNED APART, CREW ENROUTE... ALL WORK COMPLETE / GXJ VER/LDA IDC XXXX
8132 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-11-29 14:35 | 2011-11-29 14:55 | 64 | 20 | 4127311 | 1280 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW HAD TO OPEN RECLOSER TO ALLOW THEM TO SAFELY REPLACE BAD INSULATORS THAT COULD NOT BE REPLACED WITH LINE ENERGIZED COD-64 ISO OCR 38831040000018 VER/HFP L3/HFP IDC XXXX
8133 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2021-07-01 10:27 | 2021-07-01 14:00 | 6 | 213 | 4834351 | 1278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50kva 7200 120/240 by truck @ 1147-c2-4563. Crew required Released by crew 078S02,repairs made all cust restored @ 1400 please close ticket thanks.bt
8134 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-07-12 17:07 | 2016-07-12 20:40 | 6 | 213 | 4618701 | 1278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE ON POLE 37830294000105, NEED 1 MAN AND BIG BUCKET, 2 19.9 CUTOUTS AND BRACKETS AND ARRESTER. ALL POWER RESTORED @ 20:40 VER/AWD
8135 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2011-10-12 11:32 | 2011-10-12 11:50 | 71 | 18 | H4970131 | 1278 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF AT 94-6510 "B" PHASE ONLY COD-30 OPENED RECLOSER AT 94-6503 TO ISOLATE AND REPAIRPOLE 94-6510 HOT TAP BURNT OFF OPENED REC. POLE 94-6503 11;32 TILL 11;50 SEND NOTE TO RAYBURN NUMBER 4 WIRE NEEDS TO BE UPGRADED NUMBER 2 RISER 2-OUTAGE IDCC DUP TO OPEN RECLOSER XXXX
8136 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2008-04-20 10:56 | 2008-04-20 12:52 | 11 | 116 | 52720-1 | 1276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VERIFIED THAT LINE FUSE IS OUT. PATROLLING LINE. I HAVE FOUND A BROKEN CUTOUT AT POLE 474-23//3314402//VER/CRB IDC SEE 52770-1 FOR OTHER 2 CUSTOMERS XXXX
8137 | Paintsville | 3401102 | FALCON | SALYERSVI | 2011-06-07 15:02 | 2011-06-07 16:00 | 22 | 58 | 4248471 | 1276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKEN...RE FUSED TRANSFORMER..//COD 22// VER/DBM IDC XXXX
8138 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-03-09 15:49 | 2010-03-09 17:45 | 11 | 116 | 64378-1 | 1276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT POLE 37820073A00089, POLE TOP BURNED OFF ON POLE 37820073A00527.........POWER RESTORED @ 17:45.......M.ROBINETTE RELEASED BY CREW 074H14//VER/CRB IDC XXXX
8139 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-10-07 23:40 | 2014-10-08 10:18 | 2 | 638 | 4570911 | 1276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK AM// A PHASE LINE FUSE IS OUT ON POLE 38831148000021. IT IS ACROSS CREEK. THIS NEEDS TO WAIT TILL DAYLIGHT. G.R. LINE FUSE IS OUT ON POLE 38831148000021. IT IS ACROSS CREEK. THIS NEEDS TO WAIT TILL .DAYLIGHT.&SHOULD BE SAME AS OUTAGE #45703361 G.R. NOW PATROLLING LINE.REPLACED BAD CUTOUT ON POLE #38831148000029.& POWER IS NOW RESTORED// COD 2// VER/ ADH
8140 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-03-09 11:13 | 2013-03-09 12:11 | 22 | 58 | 4893201 | 1276 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK COD-22 ISO TF 38830045D37225 VER/HFP L3/HFP IDC XXXX
8141 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-10-03 10:05 | 2016-10-03 11:30 | 15 | 85 | 4955821 | 1275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACING 10 CSP XFM WITH 25 KVA POWERQUILITY ISSUES HAD TO LINE FUSE ON PL474-38 DUE TO CRACK CUTOUT REPLACED LINE CUTOUT AN XFM OPEN AT 10:05 CLOSED AT 11:30 RELEASED BY CREW 075H03 VER/CRB L3/HFP HFPC CNT13
8142 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-03-18 08:55 | 2017-03-18 16:00 | 3 | 425 | 4566961 | 1275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP: 37.5 -7200,120-240 XFMER. TRK TO POLE. HAD OUT LAST NIGHT. RELEASED BY CREW 078S07,REPAIRS MADE ALL CUST RESTORED @1600 PLEASE CLOSE TICKET THANKS.BT/ ISO 38830043000065/ COD 3/ VER/BOW
8143 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2008-11-13 05:59 | 2008-11-13 13:04 | 3 | 425 | 64336-1 | 1275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202// RELEASED BY CREW 080S013200202// , ON SITE, BAD CUTOUT, CALLED FOR CUTOUT AND HELP, NOT TRUCK APPROACH IDC XXXX
8144 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2008-12-11 20:30 | 2008-12-12 03:35 | 3 | 425 | 57011-1 | 1275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE NCALLED FORCEEW TO BRING XFMR & MATERIAL HANDLER L3/IDC IDC XXXX
8145 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-11-17 03:50 | 2018-11-17 05:15 | 15 | 85 | 4446921 | 1275 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer, duplex, unknown if other apartment having same trouble//lights dimming and going back to normal//possible service drop issue//.spliced 1/0 sec,, chgd out 3 connections on xfmr, heating up..took xfmr 130 off at 3:50.back on at 5:15. L3/HFP
8146 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-12-29 14:48 | 2022-12-29 17:50 | 7 | 182 | 4375581 | 1274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 19.9 Cutout on Pole 33-C-1. Flaggers will be needed RESTORED at 17:50
8147 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-12-18 02:23 | 2016-12-18 13:00 | 2 | 637 | 4206941 | 1274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR F IS OUT,WILL RE-FUSE////////CUTOUT ACTUALLY BROKEN,REPLACED IT AND RESTORED,ALL OK AFTERWARDS/ ISO 38820986000105/ COD 2/ VER/BOW
8148 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2014-06-30 22:48 | 2014-07-01 01:50 | 7 | 182 | 4177001 | 1274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1/0 DROP..NEUTRAL PULLED OUT OF SLEEVE..HOT CONNECTIONS EXPOSED.OPEN UP XFMR 786-409 AT 00.50.BACK ON AT 1.50..
8149 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-05-03 08:03 | 2019-05-03 18:40 | 2 | 637 | 4206571 | 1274 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2/3 secondary down/safe now/feeds parking lot lts on lower end of lodge tr on 177 open meter533763459---bucket /2 men /1 hour work/deadend and 3 connections /no traffic or rw Released by crew 077S06
8150 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2009-01-10 19:53 | 2009-01-10 21:00 | 19 | 67 | 54092-1 | 1273 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2150105//ON SITE, LINE FUSE OUT//COD 19// VER/DBM L3/KEP IDC XXXX
8151 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-08-11 15:09 | 2016-08-11 16:55 | 12 | 106 | 4762661 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CUSTOMER PUTTING IN POOL DUG INTO U/G SERVICE // DISCONNECTED UNTIL CUSTOMER FINISHED INSTALLING POOL.38830785D40493 (40-4) IS BROKE AT GROUND LINE. OPENED FUSE 785-123 @ 14:58 TO ISOLATE. INSTALLED TEMPORARY GUYS TO HOLD POLE. RESTORED LINE FUSE @ 16:55. PLEASE SEND TO ENGINEERING TO REPLACE 785-493 & 785-494 (ROTTEN) ALSO RIGHT OF WAY WILL NEED TO BE CUT @ 785-494 BEFORE REPLACING POLE. THANKS, SH/ ISO 38830785D40123/ COD 12/ VER/BOW AJBC TOF1149 FIRST ALL OUT CALL NOT UNTIL 15:09
8152 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2015-02-19 06:03 | 2015-02-19 13:07 | 3 | 424 | 4041171 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 COPPER PRIMARY AND NEUTRAL // TAGGED TO VIRGIN GROUNDS PLACED AT FUSE/NEED TO COME IN GRAYSON ROADS BAD FROM GRAHNCRELEASED BY CREW 078S03--REPAIRED #4 P&N 1 SPAN---12T PL#251-143 ALL REST @ 1307 COD-3 VER/HFP L3/HFP
8153 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2020-10-24 13:44 | 2020-10-24 15:30 | 12 | 106 | 4580971 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 38830214000208 pole smoking approx 1/3 gone. needs lowered, new ridge pin and insulator and c/o with fiberglass t bracket.crew req-ds102420 // opened line fuse to make repairs @ 1344 closed @ 1530
8154 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-11-07 09:03 | 2013-11-07 12:35 | 6 | 212 | 4018161 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT IS BROKE. LINE CREW WILL BE HERE SOON WITH A BUCKET TRUCK TO HELP REPLACE IT. VER/CRB L3/HFP
8155 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-01-06 11:04 | 2014-01-06 16:22 | 4 | 318 | 4236711 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOW//// BAD 25KV 19.9, BUCKET ACCESSABLE, NEED FLAGGERS RELEASED BY CREW 077S08//COD 4// VER/DBM
8156 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-11-23 05:25 | 2011-11-23 08:57 | 6 | 212 | 4105131 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | HOT TAP BURNT OFF ///VER/CRB IDC XXXX
8157 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2010-08-18 20:01 | 2010-08-19 03:05 | 3 | 424 | 57955-1 | 1272 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BROKEN PRIMARY BUSHING------- POWER ON @ 03:05 //VER/GAH
8158 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-06-28 19:04 | 2009-06-28 21:25 | 9 | 141 | 66570-1 | 1269 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON SERVICE AT XFMR POLE. REPAIRED. SH
8159 | Hazard | 3302703 | HAZARD | HAZARD | 2014-01-24 12:18 | 2014-01-24 17:35 | 4 | 317 | 4308861 | 1268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSF === NEED LINE CREW AND TRANSF 50 KVA OR BIGER 7200 === RELEASED BY CREW 077S03..CHANGED OUT XFMER AND CHECKED VOLTAGE TO BE GOOD.P.HICKS COD-4 ISO TF 37830272D10958 VER/HFP L3/HFP
8160 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-12-16 21:23 | 2008-12-17 11:40 | 4 | 857 | 59288-1 | 1268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 2206403// BROKEN 40/4 XFORMER POLE, NEEDS NEW XFORMER AND MET. FOR POLE. NEEDS YARD DOG, DOWN OVER HILL. CUT LOOP ON POLE 214-199, ONE SPAN AWAY FROM BAD POLE. RELEASED BY CREW 078S01. WILL GET THIS FIRST THING IN DAYLIGHT, DIFFICULT LOCATION. RAYBURN//LAST CUST ON @ 1140 VER/KEP L3/KEP IDC XXXX
8161 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-04-05 20:22 | 2011-04-06 17:30 | 1 | 1268 | 50102-1 | 1268 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, BAD 25 KVA, 19.9 XFMR//VER/CRB IDC XXXX
8162 | Hazard | 3303901 | LESLIE | HYDEN | 2018-01-12 17:52 | 2018-01-12 20:23 | 25 | 151 | 4738051 | 1267 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 388-218. Fuse out on 338-315. Single phase out. closed line fuse at 18:29 opened other 2 xfmrs at 20:04 Released by crew 077H14 2023
8163 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2011-04-23 04:49 | 2011-04-23 08:20 | 6 | 211 | 62325-1 | 1266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | ////FUSE ON POLE 901-4541 OUT .. CANT FIND ANYTHING WRONG .. CUST SD LIGHTNING HIT AREA HARDFUSE ON POLE0901-5686 OUT .. CANT FIND ANYTHING WRONG .. CUST SD LIGHTNING HIT AREA HARD.. FUSE ON POLE 901-5686 WAS OUT LOAD SIDE RISER CAME OUT OF BOTTOM OF CUTOUT.. BACK IN AT 8:20 IDC DCMT XXXX
8164 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-08-15 13:29 | 2009-08-15 17:00 | 6 | 211 | 58907-1 | 1266 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WORK REQUEST # 31249072 //BAD 50 KVA X-FMR NEED 2 MEN AND A MATERIAL HANDLING BUCKETBAD 50 KVA X-FMR NEED 2 MEN AND A MATERIAL HANDLING BUCKET POWER RESTORED COD-6 ISO TF 37830412A00146 L3/HFP IDCC PN12 XXXX
8165 | Hazard | 3309302 | VICCO | JEFF | 2009-01-04 13:52 | 2009-01-04 16:30 | 10 | 158 | 51270-1 | 1265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309302// FOUND BAD CUTOUT ON POLE 346C-369 , LINE FUSE OUT ON POLE 346C-301// ISOALTED CUTOUT AND CLOSING IN FUSE @ 1445// RESTORED TRANS @ 1630 VER/TOM L3/TOM IDCC FP NULL XXXX
8166 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-04-17 08:20 | 2011-04-17 10:15 | 11 | 115 | 59651-1 | 1265 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN TRANSFORMER FUSE..REFUSED 50 KVA TRANSFORMER... COD-11 ISO TF 38830785D40156 VER/HFP L3/HFP IDC XXXX
8167 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2020-03-29 05:43 | 2020-03-29 09:44 | 11 | 241 | 4521081 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 385 open/cod 8/bad transformer on 1396Closed in the line fuse on pole 272-385 at 6:45, XFMR fuse on pole 37830272A41396 at 6:51 and it came back out, bad XFMR. Closed XFMR fuse on pole 272-1397 at 7:00. Need 25KVA, 2 men and big bucket. Truck access, 7200. Located at Turner AVE and Roy Gave st. Released by crew 077H20 closed xfmr back in on pole 272A-4-385 @ 9:44 Released by crew 075H04
8168 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-10-26 12:03 | 2008-10-26 22:35 | 2 | 632 | 59186-1 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW ON SITE // HAS BAD U/G BETWEEN TRANSFORMER & PEDISTAL. CALLING FOR ADDITIONAL HELP TO MAKE REPAIRS.GOING TO INSTALL TRANSFORMER AND PUT NEW UNDERGROUND ON DIFFERENT POLE TO MAK IT SHORTER** AT 2230 UPDATE BY CREW... OPENED TR AT POLE 1083-523 AT 2232 CLOSED AT 2235 TO RUN NEW SECONDARY ORDER 59307-1... ETR UPDATED TO 2330. VER/PDP IDC XXXX
8169 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-01-06 08:59 | 2011-01-06 11:37 | 8 | 158 | 59132-1 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38331325 // OPENED TR @ 0859 BAD 50 KVA TRUCK TO POLE NEED CUTOUT AND LA /// COD-8 ISO TF 38830020D37013 VER/HFP L3/HFP IDC XXXX
8170 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-05-22 14:27 | 2017-05-23 11:31 | 1 | 1264 | 4839721 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OCR OPEN ON OLE 37830306000211/ /POLE37830306A10261 HAS ANOTHER ARM PIN INSULATOR BAD , MAYBE ANOTHER STRING OF DEADEND INSULATORS I WOULD CHANGE THEM. WE WILL WORK TOMMOROWPOLE CUSTOMERS NOTIFIED AND AGREED TO OUTAGE.//OCR OPEN ON OLE 37830306000211/ RESTORED 1131
8171 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-05-12 08:19 | 2009-05-12 13:35 | 4 | 316 | 63464-1 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 KVA 7200 120/240 XFMR BAD CALLING FOR CREW//3307302//VER/CRB IDC XXXX
8172 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2021-02-23 18:56 | 2021-02-24 16:00 | 1 | 1264 | 4236351 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TR 213-80 open/needs new TR installed
8173 | Pikeville | 3311401 | REEDY STATION | DEANE | 2017-05-22 14:27 | 2017-05-23 11:31 | 1 | 1264 | 4839721 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OCR OPEN ON OLE 37830306000211/ /POLE37830306A10261 HAS ANOTHER ARM PIN INSULATOR BAD , MAYBE ANOTHER STRING OF DEADEND INSULATORS I WOULD CHANGE THEM. WE WILL WORK TOMMOROWPOLE CUSTOMERS NOTIFIED AND AGREED TO OUTAGE.//OCR OPEN ON OLE 37830306000211/ RESTORED 1131
8174 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2014-06-12 08:41 | 2014-06-12 10:00 | 16 | 79 | 4072501 | 1264 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTOR ON POLE 902-133, HAVE CUT IN THE CLEAR ALSO HAD TREE LIMB LAYING ACROSS IT, POWER RESTORED AT 1000 VER/HFP L3/HFP
8175 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2009-01-07 03:02 | 2009-01-07 10:03 | 3 | 421 | 52243-1 | 1263 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3200202//, ON SAME LINE FUSE AS TICKET #52244//, POLETOP BURNT OFF, LINE FUSE OUT ON POLE#1089-71, BOTH TICKETS ON SAME OUTAGE, CALLED R MARCUM, HE SAID TO WAIT UNTIL DAYLIGHT RELEASED BY CREW 080S1//MD FILED VER/CRB L3/KEP IDC XXXX
8176 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-03-23 23:28 | 2014-03-24 20:30 | 1 | 1262 | 4520611 | 1262 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOT TAPS LIFTED POLE 150-149 DUE TO POLE 150-127 BURNT OFF // REPAIRS WILL BE MADE ON 3-24-15 //CITY OF HAZARD REPORTS FEED WATER TANK AND BATTERY CHARGER AND WILL BE OKAY TO REPAIR ON 3-24-14 AND ALSO REPORTED CAN GET TRUCK TO POLE // MD FILED VER/KEP
8177 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2015-03-14 21:33 | 2015-03-15 00:33 | 7 | 180 | 4195081 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED TO MAKE REPAIRS ON 4195431 OPEN ____ VER/KEP AJB
8178 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-10-14 08:00 | 2010-10-14 11:30 | 6 | 210 | 59528-1 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37322845 // POLE 90-278 BURNT OFF LINE FUSE OUT 90-18 25T HOT OFF 90-162 ALSO CHGED BAD LA ON 90-162 SEND TO BILL FRALEY.------POWER ON @ 11:30 VER/HFP L3/HFP IDC XXXX
8179 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-09-02 22:18 | 2019-09-02 23:42 | 15 | 84 | 4973761 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp came off stirrup at line fuse pole 328-55, made repairs restored power at 23:42 // cod 15 L3/HFP
8180 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-07-26 01:50 | 2011-07-26 08:50 | 3 | 420 | 4622681 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3403201 // WILL HOLD TIL REGULAR WORKTIME AS PER GUIDELINES // LOOKS LIKE 1.6T FUSE BROKE REPLACED FUSE EVERYTHING OK IDC XXXX
8181 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-09-14 17:51 | 2010-09-14 18:21 | 42 | 30 | 66301-1 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WAS DOING ROUTINE WORK, AND FOUND 3 CUTOUTS THAT ARE CRACKED ON POLE 1073-3518, WELL NEED CREW TO MAKE REPAIRS, CAN USE TRUCK, MATERIAL NEEDS 3 NEW CUTOUTS, MAY NEED AWP, FOR TRAFFIC CONTROL RELEASED BY CREW 078S06/CREW REPAIRING BAD CUTOUTS/FETR1915/VEM/OPENED FUSE 1751/MADE REPAIRS AND RESTORED ALL CUST AT1821/PLEASE CLOSE TICKET/THANKS/VEM// COD 42// VER/DBM IDCC TOF1755 XXXX
8182 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2014-10-02 10:19 | 2014-10-02 14:31 | 5 | 252 | 4544261 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 TRANSFORMER CUTOUT. NO TRUCK ACCESS. CUSTOMER HAS DAMAGES TO HIS HOT TUB COVER FROM THE CUTOUT PIECES FALLING ON IT. RELEASED BY CREW 079S02 COD-5 ISO TF 38821112B00034 VER/HFP L3/HFP
8183 | Paintsville | 3401101 | FALCON | FALC-OILS | 2011-02-10 14:02 | 2011-02-10 16:22 | 9 | 140 | 55945-1 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ENROUTE. PATROLLING. PATROLLED LINE AND SAW NO PROBLEMS EXCEPT FOR A BLOWN PORCELIN ARRESTER ON 830-26. WILL CHANGE AND TRY LINE FUSE. RESTORED @ 16:22. SH//COD 9// VER/DBM IDC XXXX
8184 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-03-23 15:54 | 2018-03-23 19:58 | 9 | 244 | 4046091 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #2 al burned out of a hot line clamp on pole 38831125B00382 . Need two men to make repairs../ opened fuse 38831125B00204 @ 1948/ closed fuse @ 1958
8185 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-04-19 11:40 | 2013-04-19 14:40 | 7 | 180 | 4025841 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 162-125 , THIS TOOK OUT LINE FUSE ON POLE 162-66. COD-7 ISO LF 38830162B46066 VER/HFP L3/HFP IDC XXXX
8186 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-05-09 16:48 | 2011-05-09 21:00 | 5 | 252 | 4023701 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-5584 BAD 50 KVA ALSO CHGED CUTOUT AND LA TRUCK TO POLE RELEASED BY CREW 078S08//COD 5// VER/DBM IDC XXXX
8187 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-09-17 10:15 | 2018-09-17 10:29 | 90 | 14 | 4114161 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT//REPORTED BY BILL LYNCH//L/F IS NOT OPEN AT THIS TIME//WILL OPEN TO FIX CUTOUT//1015 CLOSED 1029BROKEN CUTOUT//REPORTED BY BILL LYNCH//replaced cutout open @ 1015 close @ 1029 please close ticket thanks.bt L3/HFP
8188 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-01-31 09:30 | 2014-01-31 12:30 | 7 | 180 | 4332491 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW REQUIRED #2 ALUM NEUTRAL DOWN NO TRUCKS /SEND TO MIKE PHELPS/NEEDS BRING #2 ALUM WITH/TOOK TRANSFORMER OFF AT 0930HRS/YELLOW CAUTION TAPE HANGING FROM TREE AT DRIVEWAY ACROSS FROM KNIPP BR. RELEASED BY CREW 078S03 REPAIRS COMP 1/31/14 MP//COD 7// VER/DBM
8189 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-05-04 22:20 | 2019-05-05 01:50 | 6 | 210 | 4220581 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse // cod 6
8190 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-07-19 01:07 | 2014-07-19 02:37 | 14 | 90 | 4261611 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | TRANS. LEAD GOING TO CUTOUT WAS OVER AGAINST POLE. LOOKS KIKE IT FLASHED OVER AND BLEW LINE FUSE ON 121-87. I RELOCATED LEAD. I AM GOING TO TRY LINE FUSE. I CLOSED LINE FUSE IN AT 02:37 AND IT STAYED. VER/SEF
8191 | Whitesburg | 3312902 | JENKINS | JENKINS | 2010-01-31 08:24 | 2010-01-31 10:30 | 10 | 126 | 61672-1 | 1260 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COD-10 (7 +3 MAPPED WRONG) VER/HFP L3/HFP IDC XXXX
8192 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2018-07-06 16:58 | 2018-07-07 13:57 | 1 | 1259 | 4742411 | 1259 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 cutout broken need big bucket to replace replairs made and power restored at 1357
8193 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-04-04 15:28 | 2014-04-04 16:05 | 34 | 37 | H4571461A | 1258 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE#448-C3-114 BURNT/ISOLATED 448-530 CLOSED CB AT 0602/FBR LOCKED OUT , BAD INSULATOR ON POLE 448-114, CUT LOOPS ON POLE 448-530 & PLACED TAGS FOR DDC.FBR LOCKED OUT , BAD INSULATOR ON POLE 448-114 POLE BURNT OFF, CUT LOOPS ON POLE 448-530 & PLACED TAGS FOR DDC. RELEASED BY CREW 077S11 SEE DDC LOG // //VER/GAH IDC XXXX
8194 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-12-11 05:31 | 2008-12-11 12:30 | 3 | 419 | 56519-1 | 1257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3307302// XFMR FUSE OUT, BAD XFMR, CALLING FOR HELP RELEASED BY CREW 077S02 COD 3 ISO/FLT POLE 37830201C10042 VER/TOM L3/TOM IDC XXXX
8195 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2019-10-31 19:19 | 2019-11-01 16:16 | 1 | 1257 | 4259001 | 1257 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT FAILED ON POLE 38821088B00046 NEED 7,200 CUTOUT/ NO TRUCK ..DJM Released by crew 074F04. repaired cutout door, time on 16:16, 11-1-19/ ISO 38821088B00046/ COD 1
8196 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2015-08-22 07:09 | 2015-08-22 12:23 | 4 | 314 | 4163031 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL WORK AT START TIME. PRIMARY BROKE BETWEEN POLE 449-254 AND POLE 255. WILL HAVE TO OPEN LINE FUSE AT POLE 449-37 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED L/F AT 1124, MADE REPAIRS CLOSED BACK IN AT 1223./DUPLICATE IN HOIS// VER/ ADH
8197 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-02-03 06:28 | 2014-02-03 09:05 | 8 | 157 | 4342301 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER AFTER HOURS TROUBLE CALLOUT GUIDE LINES WILL BE DISPATCHED AT REGULAR WORK TIME. CUTOUT HAS BROKEN DOWN AT POLE 168-151 AND BLEW LINE FUSE ON POLE 167-463. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT VER/SEF
8198 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-08-02 15:01 | 2017-08-02 20:01 | 6 | 300 | 4217541 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE 38830472000004 BACK IN @ 17:45 (4 CUST),,CREW REQUIRED BAD 25 KVA XFR @ 38830472000098 TRUCKS TO POLE RELEASED BY CREW 078S05/CREW ON SITE/FETR2030/VEM.REPAIRS MADE AND POWER RESTORED TO ALL CUST/ 38830472000098 2001 (2 CUST)/PLEASE CLOSE TICKET/THANKS/VEM/ VER/BOW SJGC PN 38830472000098
8199 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-01-07 07:52 | 2018-01-07 13:06 | 4 | 314 | 4715641 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse had melted out on 1105-C-14, also had to trim trees out of open wire crossing the road off this pole, got trees cut out and refused @1306./ ISO 38821105C00014/ COD 4
8200 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-01-13 08:30 | 2019-01-13 13:44 | 4 | 314 | 4665081 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer, no answerTREE FELL,PROBABLY BRUSHED THE LINE,OTHERWISE NO EVIDENT PROBLEM.WILL RE-FUSE THE LINETREE FELL,PROBABLY BRUSHED THE LINE,OTHERWISE NO EVIDENT PROBLEM.WILL RE-FUSE THE LINE///////FUSE BLEW,SAW FLASH ABT 2 POLES AWAY.THINK ITS A BAD PIN-TYPE INS THERE.WILL REPLACE IT.NEED 1MAN,INSULTR,PICKUP TRUCK TO X CREEK.ALSO BAD CUTOUT 961-76,REPLACED IT/////////////RESTORED POWER L3/HFP
8201 | Whitesburg | 3401301 | FLEMING | NEON | 2010-05-18 14:08 | 2010-05-18 16:45 | 8 | 157 | 64736-1 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35172946 // 10 KVA TRANSFORMER IS BAD WILL NEED 1 MAN AND BIG BUCKETT RELEASED BY CREW 074S07STS WR # 35172946 // 10 KVA TRANSFORMER IS BAD WILL NEED 1 MAN AND BIG BUCKETT REPLACED TRANSFORMER VER/HFP L3/HFP IDC XXXX
8202 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-01-24 08:18 | 2019-01-24 10:55 | 8 | 157 | 4715811 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | arrester on 1148-90320t lf open @ 1148-871, restored @ 10:55. ¦¦¦¦ NOTE XFMR ON THIS POLE IS ON LOAD SIDE OF THE FUSE = ENTERED MD -- ALSO ENTERED A MD FOR 1 MISS-MAPPED CUSTOMER AND ADDED IT TO THE TOTAL CUSTOMER COUNT -- HFP
8203 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-05-03 16:14 | 2022-05-04 02:42 | 2 | 628 | 4829511 | 1256 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva. 7200 120/240. trk to pole. old gravel drive between beige/green garage & old garden beside creek. Released by crew 078S07 crew on site FETR 3:00 LRM all pwr restored 02:42 please close ticket LRM
8204 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-05-07 08:05 | 2014-05-07 12:16 | 5 | 251 | 4669591 | 1255 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-3512 BAD 50 KVA TRUCK TO POLE NEED LINE CREW AND FLAGGERS DEAD MAN CURVE RELEASED BY CREW 078S08 D_JENT IS GOING TO REPLACE 50 KVA TRANSFORMER OLD #74TJ125024 NEW # COOPER 14A102342 TIME ON 12:16 VER/SEF
8205 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-06-01 14:43 | 2009-06-01 16:37 | 11 | 114 | 57380-1 | 1254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 30073942 //CREW ON SITE/FETR1715/XFMR CUTOUT CHANGED/ALL CUST RESTORED 1637/PLEASE CLOSE TICKET/THANKS/VEM L3/HFP IDC XXXX
8206 | Pikeville | 3407101 | TOPMOST | DEMA | 2009-12-26 14:13 | 2009-12-27 11:07 | 1 | 1254 | 50605-1 | 1254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR -WILL REPLACE 12-27-09 CPR-COMPLTED -12-27-09 11:07 -CPR
8207 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2012-07-02 05:32 | 2012-07-02 15:59 | 2 | 627 | 4207441 | 1254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT BROKEN ON POLE 326, NO TRUCK ACCESS, ISOLATED AT POLE 326 AND CLOSED LINE FUSE AT POLE 91 AT 15:35
8208 | Hazard | 3303901 | LESLIE | HYDEN | 2015-02-20 08:03 | 2015-02-20 18:30 | 2 | 627 | 4051811 | 1254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE 243-44 NEED 15 KVA CUTOUT AND BRACKET REPLACE 4/3 SERVICE WITH 2/3 TRUCK ACC NEED CHAINS STEEP ROAD 7.2 KV RELEASED BY CREW 077E02 VER/HFP L3/HFP
8209 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-04-12 06:07 | 2016-04-12 06:45 | 33 | 38 | 4083701 | 1254 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | OUTAGE NECESSARY TO ALLOW CREW TO BYPASS DEFECTIVE REGULATOR & REPLACE IT // NO DAVOX // ONLY OPENING C PHASE 53 CUST // TRACKING# KY030216-0314-8630// OFF FROM 0642 TO 0645 DUPLICATED DUE TO LOAD XFER AND LINE REBUILD - CUST COUNT APPROX SEE DUP ALSO 4083701 VER/HFP L3/HFP AJB
8210 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-06-01 15:41 | 2015-06-01 18:40 | 7 | 179 | 4494351 | 1253 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE37830178B00016 , FOUND BAD CUTOUT ON POLE 37830178B00018 . REPLACED CUTOUT . CLOSED LINE FUSE @ 18:40 VER/CRB. L3/DKG
8211 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-06-04 09:37 | 2009-06-04 14:50 | 4 | 313 | 57343-1 | 1252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR# 30136156 // LINE FUSE OUT ON POLE#69-8288 AND 8200 ENERGIZED 40T FUSE ON POLE 69-8288 AT 13;REPLACED 15T FUSE ON POLE69-82200 AT 14:50. BAD L. ARRESTER ON POLE 69-8278 IN ELKS PICNIC AREA NEEDS TO BE REPLACED. NEED TO CONTACT CARSON ELSWICK AT 922-2881 TO OPEN GATE.//MADE A MD/VER/CRB
8212 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-05-31 15:34 | 2011-06-01 02:00 | 2 | 626 | 4214891 | 1252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD 15 KVA SINGLE BUSHING TRANSFORMER, CREW REQUIRED, CAN USE TRUCKS RELEASED BY CREW 078S06//CREW ON SITE//REPLACED 15KVA TRANSFORMER POWER RESTORED AT 02:00 PRT/// VER/GAH IDC XXXX
8213 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-06-20 12:47 | 2022-06-20 18:00 | 4 | 313 | 4261921 | 1252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | per a sanders fuse has been out several times need transformer can truck 25 kva 7200v REPLACED TRANSFORMER 25KVA RESTORED AT 18:00.
8214 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2008-11-07 17:17 | 2008-11-07 22:30 | 4 | 313 | 63116-1 | 1252 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411901//BAD CUTOUT. REPLACED......DAH//COD 4// VER/DBM IDC XXXX
8215 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-09-12 14:53 | 2012-09-12 21:50 | 3 | 417 | 4042971 | 1251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 120/208 NETWORK TRANSFORMER. // MILLER & GOBLE XFMR CHANGED AND RESTORED @ 21:50. SH COD-3 ISO TF 38830785D20590 VER/HFP L3/HFP IDC XXXX
8216 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-11-11 09:09 | 2009-11-11 16:06 | 3 | 417 | 58523-1 | 1251 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP LINE FUSE OUT ON 202-36, PATROLLING LINE, TOP OF POLE BURNT OFF, CALLING FOR CREW RELEASED BY CREW 077S02 MADE REPAIRS AND RESTORED POWER AT 1606 CREW 077H01 //COD-3 ISO LF 37830202000036 L3/HFP IDC XXXX
8217 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-11-24 22:18 | 2008-11-25 14:20 | 3 | 962 | 51896-1 | 1250 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201// POLE FIRE AT 38830377000091, ISOLATED AT 377-84, LINE FUSE AT 402-64 RESTORED AT 00:42, NEED LINE CREW, 40-5 POLE, MAY HAVE ENOUGH CLEARANCE TO LOWER. 1 CUST OUT, WATCH XFMR RISER ON ISOLATING POLE WHEN SAGGING PRIMARY RELEASED BY CREW 078S05//VER/CRB IDC XXXX
8218 | Hazard | 3303901 | LESLIE | HYDEN | 2015-12-02 15:11 | 2015-12-03 12:00 | 1 | 1249 | 4504921 | 1249 | PARTIAL POWER | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON POLE 37830340000014 C PHASE ,PATROL LINE WHAT I COULD SEE , DID NOT SEE ANYTHING./ LINE CREW & FLAGGING CREW/ NEED 3 19.9 DEADEAND/ PER DUTY SUPERVISOR WILL WORK IN AM @ START OF REGULAR SHIFT VER/CRB
8219 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-08-14 21:35 | 2016-08-14 23:11 | 13 | 96 | 4776291 | 1248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CENTER PHASE ONLY IS OPEN//COD 13// STS BROKE ARRESTER ON POLE 37830056000036 CUT IT IN THE CLEAR//AED ENTERED// VER/DBM
8220 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-04-13 23:01 | 2015-04-14 00:45 | 12 | 104 | 4314171 | 1248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20 D1 6030, BAD 12 KV CO. CREW REQD.TRUCK OK RELEASED BY CREW 078S07/ ISO 38830020D16015/ COD 12//CREW ON SITE///CHANGED CUTOUT///REFUSED LF ON @ 20D1-6015 @ 12:45///TBL TKT COMP///RMV VER/SEF
8221 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-12-10 08:14 | 2008-12-10 15:10 | 3 | 416 | 56054-1 | 1248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411902//GIVE TO RICK RAY WHEN FRANK KICKS IT BACK 3411902// I HAVE ISOLATED THE CUTOUT AND HAVE EXTINGUISHED THE FIRE. A CREW IN ENROUTE FROM PIKEVILLE TO REPLACE THE POLE. RELEASED BY CREW 074S023411902//GIVE TO RICK RAY WHEN FRANK KICKS IT BACK3411902// I HAVE ISOLATED THE CUTOUT AND HAVE EXTINGUISHED THE FIRE. A CREW IN ENROUTE FROM PIKEVILLE TO REPLACE THE POLE. RELEASED BY CREW 074S02 CREW ON SITE WILL OPEN LINE FUSE ON PL. 120-81 R RAY3411902//GIVE TO RICK RAY WHEN FRANK KICKS IT BACK34//VER/CRB IDC
8222 | Hazard | 3309003 | JEFF | VIPER | 2020-04-26 07:21 | 2020-04-26 17:45 | 2 | 624 | 4751451 | 1248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad XFMR on pole 345C-319. Closed fuse in at 8:39, held just a few moments and opened back up. Need a 25KVA, 19.9KV and a linecrew. This is a manual pole behind a home. Released by crew 077H20 // repaired and restored at 1745
8223 | Whitesburg | 3312901 | JENKINS | KONA | 2014-01-31 13:27 | 2014-01-31 16:55 | 6 | 208 | 4333181 | 1248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANS. AT POLE 405-47, WILL BE CHANGING. CHANGED TRANS. CLOSED BACK IN AT 1655.//COD 6// VER/DBM
8224 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-12-23 23:34 | 2022-12-24 06:30 | 3 | 416 | 4336961 | 1248 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva xfmr. truck accessible.
8225 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2012-12-21 08:02 | 2012-12-21 18:25 | 2 | 623 | 4497861 | 1246 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | FOUND RISER OUT OF TRANSFORMER, I OPEN UP TRANSFORMER, NEED L/C TO MAKE REPAIRS, NO TRUCK TO POLE, BEWARE THIS IS THE CUST THAT SAID WE CAUGHT HIS HOUSE ON FIRE, DO NOT TAKE TRUCKS IN YARD RELEASED BY CREW 078S06 FETR 19:30 JEH/ REPAIRS COMP. POWER RESTORED @ 18:25 JEH ////VER/CRB L/3 CRB
8226 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-30 16:25 | 2009-01-31 13:11 | 1 | 1246 | 52775-1 | 1246 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE WIRE BURNT DOWN NEED SERVICE MAN AND FLAGMAN TO REPAIR. MAY HAVE TO OPEN XFMER ON POLE TO WORK. RELEASED BY CREW 077E02
8227 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-08-07 17:17 | 2017-08-07 18:40 | 15 | 83 | 4236041 | 1245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-7160 BAD CUTOUT AND LA CHGED BOTH/ ISO 38830045D37160/ COD 15/ VER/BOW
8228 | Hazard | 3303902 | LESLIE | WOOTON | 2014-01-27 05:27 | 2014-01-27 12:22 | 3 | 415 | 4315751 | 1245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK AT REGULAR WORK TIME *** @ 0723 - JIM MULLINS WILL HAVE LINEMAN WORK THIS OUTAGE BE ABOUT A HOUR.WILL CHECK AT REGULAR WORK TIME .TRANSFORMER FUSE BLOWN.BAD 50 KVA 19.9..120/240 V.TIM SMITH TO BRING ONE TO CREW.P.HICKS//COD 3 IDC XXXX
8229 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2010-05-02 14:59 | 2010-05-02 21:54 | 3 | 415 | 54096-1 | 1245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#34926197 BAD 25KVA SEND TO LLOYD MC. RELEASED BY CREW 078S08 //VER/GAH IDC XXXX
8230 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-12-22 10:11 | 2008-12-22 14:20 | 5 | 249 | 62428-1 | 1245 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001401//,,,,,BLOWN 15 KVA TRANSFORMER OIL HAS LEAKED OUT,,NEEDS TO BE UPGRADED TO HANDLE AT LEAST 10 HOMES TRANSFORMER IS TRUCK ACCESSIBLE RELEASED BY CREW 078S02/VER/CRB L3/JAW IDC XXXX
8231 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-11-08 14:31 | 2018-11-09 11:15 | 1 | 1244 | 4380441 | 1244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required truck ok just out of reach feeds barn and light Released by crew 078S03 // customer said it was ok to hold until normal hours.arrived RM xfm in @11:15 please close tic RM Released by crew 078H20 L3/HFP
8232 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-07-20 04:59 | 2020-07-20 15:21 | 2 | 622 | 4185801 | 1244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout GuidelinesXFRF IS OUT,WILL RE-USEXFRF IS OUT,WILL RE-FUSE////////XFR IS BAD,NEED A 25KVA,NO ACCESS WITH TRUCK.WINCH JOB.WILL ALSO NEED TO OPEN LINE TO CHANGE,PROBABLY.XFRF IS OUT,WILL RE-FUSE////////XFR IS BAD,NEED A 25KVA,NO ACCESS WITH TRUCK.WINCH JOB.WILL ALSO NEED TO OPEN LINE TO CHANGE,PROBABLY. Released by crew 074S06
8233 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-07-07 03:18 | 2017-07-07 13:40 | 2 | 622 | 4086021 | 1244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV C/O. CREW REQD. STATION CREW RELEASED BY CREW 078S07 REPAIRS MADE, XFMR CLOSED AT 13:40. TICKET COMPLETE VER/CRB
8234 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2018-04-06 10:49 | 2018-04-06 16:00 | 4 | 311 | 4195451 | 1244 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALL CUST BACK @ 1130////bad 25 kva 7200 37820145000008..will need big bucket to make repairs///repairs made.restored/ 37820145000008 transformer out originally (4cc)
8235 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2009-06-25 13:44 | 2009-06-25 15:37 | 11 | 113 | 59212-1 | 1243 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP #4 TRIPLEX BURNT DOWN. REPLACED WITH#2 TRIPLEX. JOB DONE. L3/HFP
8236 | Pikeville | 3409502 | BURDINE | LEVISA | 2017-10-28 23:15 | 2017-10-28 23:42 | 46 | 27 | 4506291 | 1242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENING SWS ON 359-54 FOR APPRX 45 MINUTES TO TIE IN PHASE FLOATING AT 334-78/NO OUTAGE TILL 2315///NEUTRAL DOWN FROM POLE 334-8 TO 334-78.PHASE FLOATING ON POLE 334-78..WILL OPEN @ POLE 359-54 SO CONDUCTOR CAN BE TIED BACK IN.WILL CUT NEUTRAL IN CLEAR/////OPENED @ 23:15 AND CLOSED BACK @ 23:42////PLEASE SEND COPY TO MIKE HATFEILD SO JOB CA/// VER/DKM L3/HFP XXXHFP ACB
8237 | Hazard | 3303902 | LESLIE | WOOTON | 2017-09-25 09:18 | 2017-09-25 12:45 | 6 | 207 | 4387031 | 1242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR FAILED PRIMARY DOWN RELEASED BY CREW 077S01 VER/AWD ACB
8238 | Paintsville | 3401802 | INDEX | HOSPITAL | 2011-04-16 13:54 | 2011-04-17 00:15 | 2 | 621 | 58673-1 | 1242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMR. NEED CUTOUT, 25KVA XFMR, BIG BUCKET, FLAGGING CREW AND THREE MEN (MIGHT HAVE TO HAVE A MAN ON POLE ALSO - LONG REACH). <<CREW REQUIRED>> RELEASED BY CREW 076S02 PUDDIN 03672 AND AWP CREW HEADING TO ASSIST VER/KEP IDC XXXX
8239 | Hazard | 3309301 | VICCO | REDFOX | 2008-12-31 04:54 | 2008-12-31 11:48 | 3 | 414 | 65327-1 | 1242 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 27857110 // BAD 50 KVA 7200 TRANSF == LINE CREW GET TO POLE WITH TRUCK == RELEASED BY CREW 077S03//3309301/VER/CRB L3/KEP IDC XXXX
8240 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-05-09 13:09 | 2016-05-10 09:50 | 1 | 1241 | 4189911 | 1241 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CUSTOMER IS OK WITH LEAVING THIS OUT TODAY RELEASED BY CREW 077S12//ISO POLE 37830427B00279//COD 1 REPLACED CUTOUT LEFT OPEN MRTER HAS BEEN DNP VER/CRB
8241 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-09-30 12:08 | 2019-09-30 19:00 | 10 | 412 | 4075031 | 1240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva csp tran--and--broke 7200 c/o--crew req-ds093019 Released by crew 078S01//arrived on site RM opening 334-48 20 t fuse to change xfm opened@17:28 closed @19:00 please close tic RM
8242 | Paintsville | 3401102 | FALCON | SALYERSVI | 2010-02-13 07:49 | 2010-02-13 10:24 | 8 | 155 | 57384-1 | 1240 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONN BURNED 2/3 SEC DOWN//VER/CRB IDC XXXX
8243 | Hazard | 3309301 | VICCO | REDFOX | 2015-10-09 01:35 | 2015-10-09 08:28 | 3 | 413 | 4329831 | 1239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON POLE 300-55, PATROLLING LINE. FOUND BAD LIGHTNING ARRESTOR ON CSP XFMR ON POLE 300-158/ ISO 37830300B00055/ COD 3/ K. NAPIER SAID HE WAS GOING TO TALK TO TECH TO TRY AND GET THIS TRANSFORMER AND ARRESTER REPLACED / IN THE ABNORMAL/ VER/BOW L3/HFP XXXHFP
8244 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-11-06 13:19 | 2014-11-06 20:04 | 4 | 405 | 4705421 | 1239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT CRACKED, 45 CL 4 POLE BURNT OFF AT CUTOUT, NEED TO REPLACE POLE, NEED DEAD END UNIT, GUY, CUTOUT AND ARR.=== TRANSFORMER OK, TRUCK ACCESS. 7.2 KV // COD-4 ISO LF 37830175000247 VER/HFP L3/HFP
8245 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-12-19 13:43 | 2008-12-19 16:40 | 7 | 177 | 60427-1 | 1239 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3310501// FOUND BAD INSULATOR @ 29-38// GOING TO OPEN OTHER FUSE OUTAGE 1 ADDITIONAL CUSTOMER TO MAKE REPAIRS// STS BAD INSULATOR ON POLE 29-38, GOING TO CHANGE IT OUT VER/KEP L3/KEP IDC XXXX
8246 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-10-31 14:38 | 2019-11-01 11:15 | 1 | 1237 | 4239521 | 1237 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks side of hill Released by crew 078S03,repairs made all cust restored @ 1115 please close ticket thanks.bt
8247 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-11-12 12:37 | 2021-11-12 14:20 | 12 | 103 | 4085331 | 1236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cleared bad lightning arrester on 458-143. Power restored@ 14:20
8248 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-09-28 19:28 | 2015-09-28 19:40 | 103 | 12 | H4280801 | 1236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF MAIN LINE POLE BURNT OFF, POLE 184-200, CAN OPEN SWITCHES ON POLE 207-177, MADE RECLOSER BACK HOT AT 07:40, CUT LOOPS ON 207-239 AND MADE HOT AT 08:33/ UPDATE ALL CUSTOMERS RESTORED THAT CAN BE, REMAINDER OUTAGED UNTIL REPAIRS COMPLETE/ TO MAKE HOT TAP UP @ 1935 ON 207-239 OPENED SWITCH 207-54 @1928 CLOSED @1940/ VER TIMES PER VOICE RECORDER --- VER/HFP L3/HFP AJB
8249 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2010-08-02 04:43 | 2010-08-02 11:35 | 3 | 412 | 60290-1 | 1236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAD 75KVA DEAD FRONT UG TRANSFORMER--NEED CREW--RIGHT BESIDE ROAD--NEWER INSTALLITION EVERYTHING SHOULD WORK BACK//COD 3// OPEN LINE FUSE ON POLE 1123-8033 (SEE 60409-1) AT 11:05 CLOSED IN AT 11:35 REPLACED PAD MOUNT// VER/DBM IDC XXXX
8250 | Hazard | 3310502 | HADDIX | CANOE | 2009-02-23 10:23 | 2009-02-23 17:15 | 3 | 412 | 50810-1 | 1236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3310502// HAD TO OPEN TO COMPLETE REPARIS ASSOCIATED WITH 50617-1 (GOT TAKEN OVER HAD TO RE-CREATE THE OUTAGE IN HOIS)// OPEN FUSE @ 1623 AND CLOSED @ 1715// 19 ON TAP (INCLUDING MISMAPPED TRANSFOMER SHOULD BE ON LOAD SIDE OF FUSE NOT LINE SIDE) 3 ON COD// - TAP OUTAGE ON DUPLICATE// THIS ONLY COVERS TRANSFORMER // VER/TOM L3/TOM IDC XXXX
8251 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-10-14 13:40 | 2010-10-14 15:23 | 12 | 103 | 59675-1 | 1236 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE ON 199-80 AT 13:40 , BACK ON AT 15:23 COD-12 VER/HFP L3/HFP IDC XXXX
8252 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-09-13 07:43 | 2019-09-13 09:18 | 13 | 95 | 4012391 | 1235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | hot line clamp coming from top of cutout came out hanging in clear, made repairs and back on at 09:18 ¦¦¦ QUESTION = WAS THIS A NEWLY INSTALLED CUTOUT? L3/HFP
8253 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2018-01-05 22:38 | 2018-01-06 02:45 | 5 | 247 | 4710901 | 1235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUST//NEIGHBOR IS ALSO EXP. PROBLEMS// bad 25 kva 7200 xfmr.made repairs restored power at 02:45..
8254 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-12-05 07:53 | 2017-12-05 12:00 | 5 | 247 | 4621491 | 1235 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o. no trks Released by crew 078S07,replaced bad cutout all cust restored @ 1200 please close ticket thanks.bt
8255 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2014-01-28 09:08 | 2014-01-28 11:25 | 9 | 137 | 4319071 | 1233 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ON SITE RM HAVE BAD 25 KVA ON POLE 69-4135 TRUCK TO POLE ,ALLY VERY SLICK RELEASED BY CREW 078H20,,CREW ON SITE,,UPGRADED TO 37.5 KVA, ALL POWER RESTORED//COD 9
8256 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2020-11-01 14:39 | 2020-11-01 17:35 | 7 | 176 | 4617181 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Resagged open wire, repaired and restored @ 17:35
8257 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-07-09 17:00 | 2022-07-09 17:44 | 28 | 44 | 4444811 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Two outside phases on pole 123-35 is laying on the arm///will need crew///Will open switches on pole 122-61 ///opened switches @ 17:00 to makes repairs///Repairs made closed switches in @ 17:44 and restored service
8258 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-07-23 09:15 | 2009-07-23 12:11 | 7 | 176 | H64687-1 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP THIS RECORD FOR LINE FUSE OUTAGE //OPENED LINE FUSE ON POLE 39831147A00172 AT 09:15--BAD CUTOUT BURNT POLE OFF-NEED CREW--V MULLINS TO WORK /// 8 CUSTOM OFF @ 0838 & 7 MORE @ 0915/CREW LOADING MATERIAL/FOREMAN ON SITE/FETR1315/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1211/PLEASE CLOSE TICKET/THANKS/VEM L3/HFP IDC XXXX
8259 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-01-31 14:15 | 2020-01-31 14:43 | 44 | 28 | 4351661 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER 37830447000121 TO REPLACE INSULATER ON POLE 37830447000061//OFF @ 1415 ON @ 1443
8260 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2017-03-02 16:08 | 2017-03-02 18:42 | 8 | 154 | 4504571 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | LINE FUSE 67-190 OUT ,, LINE FUSE CUTOUT BROKE WAITING ON HELP POWER ON AT 1842
8261 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-10-27 17:59 | 2011-10-27 20:55 | 7 | 176 | 4027981 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS FUSE OUT ON POLE # 247-825..ALSO BELIVE I MIGHT HAVE A PHASE OUT ALSO ,NOW PATROLING..FOUND BLOWN FUSE ON POLE 247C-144, CAUSING ONE PHASE OUT TO SCHOOL, SCHOOL BOARD, AND NURSING HOME,.REFUSED LINE FUSE @ 20:05 HRS,..FOUND BAD 7.2KV CUT OUT ON 247-825, REPLACING NOW,..ALL POWER RESTORED @ 20:55HRS..P.HICKS//COD 11// VER/DBM IDCC CNT11 PER COMMENTS ONLY ONE FUSE OUT XXXX
8262 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-08-11 10:48 | 2022-08-11 15:56 | 4 | 308 | 4726951 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | hd a bad arrester on pole 211-C-348 cut in clear and got resored at a time of 15:55 on pole 211-C-209
8263 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-05-09 19:01 | 2015-05-09 20:53 | 11 | 112 | 4406951 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE BROKE REPAIRED BAD CONN. ON TRANS RISER L3/DKGXXX
8264 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-08-09 21:19 | 2010-08-10 00:15 | 7 | 176 | 51788-1 | 1232 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE LEAD ON TRANSFORMER BAD CHANGED TRANSFORMER VER/ARN IDC XXXX
8265 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-03-19 13:36 | 2008-03-19 15:55 | 14 | 139 | 58609-1 | 1231 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3008702// POLE 117-383 BAD 19.9 INS. POLE 117-6148 40T ON 14;50 11CUST ON HOT TAP OFF POLE 117-381 RELEASED BY CREW 078S08//REPLACED 19.9 INSULATOR AND RE-ENERGIZED AT 15:55 P R TOLLIVER///// VER/TOM IDC XXXX
8266 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-05-20 11:40 | 2008-05-20 15:05 | 6 | 205 | 66392-1 | 1230 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008002//RE-PLACED 10-T FUSE FUSE LINK WAS BROKEN//COD 6// VER/DBM IDC XXXX
8267 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-05-18 09:29 | 2014-05-18 13:35 | 5 | 246 | 4720571 | 1230 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPAN OF 1/0 SECONDARY AT SPLICE HAS SHORTED OUT IN MIDSPAN AT A SPLICE. I DISC. SERVICE DROP. I AM GOING TO RUN INTO PIKEVILLE AND GET SOME 1/0 WIRE TO REPLACE SPAN. TERRY AND I CHANGED OUT SPAN OF 1/O SECONDARY. I OPENED TRANSFORMER ON POLE 37830167D00289 AT 13:15 AND CLOSED IT AT 13:35.//COD 1 + 4
8268 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2009-01-10 12:08 | 2009-01-10 17:15 | 4 | 307 | 53954-1 | 1228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3412901//300AMPCUTOUTBROKEDDOWNFIXED011009 TOM MCCOWN// SOLID BLADE BROKE DOWN, FIXED BUT OTHER TWO PHASES WERE OPEN AND NO ABNORMAL TO EXPLAIN WHY... ADDED AED AND ALSO LATERAL WAS MOVED FROM LOAD SIDE TO SOURCE SIDE OF SOLID BLADES ON THIS POLE... MD FILED... //COD 4// VER/DBM L3/KEP IDC XXXX
8269 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-08-12 18:35 | 2013-08-13 15:03 | 1 | 1228 | 4656331 | 1228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NEED 4 WHEEL DRIVE PICKUP OR 6 WHEELER TO ACCESS TOWER / GXJ RELEASED BY CREW 074S03 FUSE HAS BROKE REFUSING CLOSED IN AT 15:03//COD 1// VER/DBM
8270 | Paintsville | 3409302 | KENWOOD | AUXIER | 2020-07-30 10:15 | 2020-07-30 11:12 | 22 | 57 | 4254011 | 1228 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 38830858B00153 ¦¦ OPENED FUSE ON POLE 38830858B00155 @ (13 CUST) ¦¦ OPENED FUSE ON POLE 38830858B00156 @ (9 CUST) ¦¦ LIFTED TAP AT POLE 38830858B00270 (NO CUST PER PO) ALL CUST RESTORED @ 1112
8271 | Hazard | 3310502 | HADDIX | CANOE | 2015-07-20 17:31 | 2015-07-21 00:20 | 3 | 409 | 4919301 | 1227 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | J COMBS, P HICKS & B COMBS VER/KEP
8272 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2014-01-30 21:35 | 2014-01-31 01:40 | 5 | 245 | 4332031 | 1225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE WAS BLOWN, BUT I COULD NOT FIND ANY REASON OTHER THAN SOME TREES GROWED UP IN THE OPEN WIRE SECONDARY. PLEASE SEND TO RYAN ROWE TO HAVE CUT. TRANSFORMER HELD FOR FIFTEEN MINUTES AND THEN BLOWED THE FUSE, ONE MAN AND MATERIAL HANDLER IS ON THE WAY TO REPLACE THE TRANSFORMER. TRANSFORMER REPLACED AND POWER IS BACK ON. VER/HFP L3/HFP
8273 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-06-18 09:24 | 2015-06-18 12:07 | 15 | 163 | 4593931 | 1225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE FUSE OUT ON POLE 38830092B00187 //COD 15//CLOSED FUSE @ 1005//POLE 92-144 1-SPAN OF NUMBER 4 COPPER TRUCK TO POLE POLE 92-187 80T LINE FUSE 10:05 AMPOLE 92-144 CREWPOLE 92-144 1-SPAN OF NUMBER 4 COPPER TRUCK TO POLE POLE 92-187 80T///STEPDOWN LOW SIDE @11:40---BACK IN @ 12:07///1 SPAN #4CU B PH. DOWN///REPAIRED/// RELEASED BY CREW 078H16//MADE SEPARATE OUTAGE TIX VER/CRB L3/DKG SEE 4594761 FOR OPENING STEPDOWN AND OUTAGING THE 85 CUSTOMERS THAT WAS ON
8274 | Hazard | 3303903 | LESLIE | HALSFORK | 2015-09-30 14:35 | 2015-09-30 15:00 | 49 | 25 | 4295941 | 1225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WIRE OFF INSULATOR ON POLE 37830362000323..OPENED LINE CUTOUT ON POLE 53 AT 14:35 CLOSED BACK IN AT 15:00 VER/CRB L3/DKG
8275 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2017-11-28 13:15 | 2017-11-28 13:40 | 49 | 25 | 4607191 | 1225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Crews lifted clamp on 37830421A20121 after opening recloser on 37830421A20395 to drop load. Approx 1 hr outage toinstall an insulator and ridge pin to hold up a loop at 37830421A20070. 1315-1340
8276 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2008-07-30 15:07 | 2008-07-30 19:12 | 5 | 245 | 62274-1 | 1225 | DISTRIBUTION SOURCE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309102//BAD XFMR CHANGED OUT//VER/CRB IDC XXXX
8277 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-12-15 10:20 | 2010-12-15 14:25 | 5 | 245 | 50568-1 | 1225 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38118659 // BAD 50 KVA--7200 TRANSFORMER---OIL SPILL, TRUCK ACCESSIBLE, CUST SAID OK TO TAKE DOWN FENCE IF NEEDED.BAD 50 KVA--7200 TRANSFORMER---OIL SPILL, TRUCK ACCESSIBLE, CUST SAID OK TO TAKE DOWN FENCE IF NEEDED. RELEASED BY CREW VER/HFP L3/HFP IDC XXXX
8278 | South Williamson | 3200301 | BELFRY | BELFRY | 2008-12-11 15:10 | 2008-12-11 16:18 | 18 | 68 | 56784-1 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3200301//, BAD CUTOUT, POLE#1014-192, REPLACING IT COD-18 L3/HFP IDC XXXX
8279 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-02-19 13:23 | 2013-02-19 14:35 | 17 | 72 | 4830441 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONDUCTOR ON ARM BURNING OPENED UP C/O TO MAKE REPAIRSCOMPL. ORDER IDCC TOF0355, OPENED WHILE MAKING REPAIRS TO 4828621 XXXX
8280 | Hazard | 3309302 | VICCO | JEFF | 2011-02-05 12:42 | 2011-02-05 15:15 | 8 | 153 | 54231-1 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RED/RED FROZE OUT//COD 8// VER/DBM IDC XXXX
8281 | Hazard | 3307301 | BULAN | ARY-HEINE | 2014-09-17 13:39 | 2014-09-17 15:55 | 9 | 136 | 4506351 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE 153-D-39 VER/CRB
8282 | South Williamson | 3411401 | DEWEY | INEZ | 2015-07-09 15:15 | 2015-07-10 11:39 | 1 | 1224 | 4759201 | 1224 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | HOT LEG HAD CORRODED INTO AT SPLICE IN CUSTOMERS SERVICE DROP///I REPAIRED CONDUCTORS//RESTORED AT 11:39//COMPLETE//EM VER/SEF
8283 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-09-07 15:38 | 2009-09-07 18:02 | 10 | 144 | H52565-1 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | 3402802// PHASE C OPEN ONLY //COD 57 //PATROLLED LINE AND COULDNT SEE ANY CAUSE FOR OUTAGE.//OPENED TWO TAPS (NOT ALREADY OUTAGED) @ 1538 DUE TO UNRELATED TROUBLE (FAILED ARRESTOR AND CUTOUT)// CLOSED RECLOSER AT 15:40.// CHANGED CUTOUT. CLOSED FUSE ON TAP 737-220 AT 17:35. REPLACED ARRESTER AND RESTORED TAP ON POLE 737-56 AT 18:02. PLEASE SEND TO J. BRADSHAW TO HAVE VINES SPRAYED ON POLE 737-56. SH IDCC DUP TO OPEN FUSES ON TWO TAPS XXXX
8284 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-01-07 05:58 | 2010-01-07 11:04 | 4 | 306 | 64644-1 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33341889 //116-594 BAD 25 KVA 19.9 TRANS NEED 37.5 CUTOUT AND LA RELEASED BY CREW 078S08 RELEASED BY CREW 078H02 VER/HFP L3/HFP IDC XXXX
8285 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-03-12 13:57 | 2014-03-12 16:30 | 8 | 153 | 4476391 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE FAILED CUTOUT - CENTER PHASE OUT PHASE OPENED, HAD TO OPEN OTHER 2 PHASES @ 1540 CLOSED @ 1627 // OLYC CUSTOMERS ON B PHASE -
8286 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-11-14 23:08 | 2008-11-15 00:20 | 17 | 72 | 64984-1 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 45-2514 25T SEND RAYBURN NOTE BAD LA NEEDS CHGED NO TRUCK 45-2173 VER/PDP IDC XXXX
8287 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-08-30 22:38 | 2011-08-31 00:20 | 12 | 102 | 4777021 | 1224 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 SEC. RISER APPEARS TO HAVE BURNED IN TWO // WILL REPAIR//REPAIRED RISER VER/KEP IDC XXXX
8288 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2015-04-08 14:15 | 2015-04-08 15:23 | 18 | 68 | 4289471 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE CUTOUT ON POLE 38820965C00182, ILL REPLACE IT. CLOSED 25 T FUSE IN ON POLE 38820965C00017, POWER IS BACK ON. VER/SEF
8289 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-04-21 08:39 | 2011-04-21 15:27 | 3 | 408 | 61606-1 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER BAD, NEED TO CUT RIGHT OF WAY ON OPEN SEC POLE IS COVER RELEASED BY CREW 077S05 // COD-3 ISO TF 38831083C20514 VER/HFP L3/HFP IDC XXXX
8290 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2018-06-26 17:25 | 2018-06-27 13:49 | 1 | 1224 | 4673181 | 1224 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Will check on wednesday Bad 10 KVA transformer in three phase bank. Only one customer affected. LCS advised crew will replace when finished with current trouble. // QUESTION ABOUT FAULT POLE = POR DOES NOT SHOW BANK ON POLE 38830954B40093 - HFP
8291 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2012-07-14 13:24 | 2012-07-14 23:35 | 2 | 611 | 4723401 | 1222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S03NEED A 25 KVA TX CUT BRACKET TO REPLACE CP TX ONE BAD LEG INTERNAL TX RELEASED BY CREW 079H01//COD 2 VER/ARN IDC XXXX
8292 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-06-26 03:50 | 2009-06-26 05:24 | 13 | 94 | 61406-1 | 1222 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BAD ON POLE 927-23 LINE FUSE -FUSE THAT FEEDS LIMEVILLE HOLLOW BAD CALLED CREW TO HELP WAITING LIGHTNING TO DIE DOWN WORK COMP, LINE BACK HOT VER/KEP L3/KEP
8293 | Whitesburg | 3401301 | FLEMING | NEON | 2011-08-15 15:56 | 2011-08-15 17:30 | 13 | 94 | 4714101 | 1222 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | REFUSED XFMRS. PLEASE SEND THIS TICKET TO DOUG CHRISTIAN HE NEEDS TO PUT A JOB OUT TO REWORK THE HIGHSISE BUS ON THIS BANK THE GROUNDS NEED TO BE FLOATED (POWERON DOES NOT SHOW 3 PHASE CUSTOMERS AND THIS WAS 2 XFMRS OUT OF A 3 PHASE BANK OUT) COD-13 ISO TF 37830355D40011 VER/HFP L3/HFP IDC XXXX
8294 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2019-11-08 23:28 | 2019-11-09 09:39 | 2 | 611 | 4013791 | 1222 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection bad , replaced transformer leads and connections
8295 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-10-15 14:08 | 2018-10-15 20:55 | 3 | 407 | 4255241 | 1221 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva 7.2kv 120/240. can use truck. Released by crew 074S07 L3/HFP
8296 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-02-27 06:10 | 2015-02-27 11:15 | 4 | 305 | 4084971 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD TRANSFORMER/POLE 38830219000018/TRUCKS OK BRING 25KVA/SEND TO YOUNGMAN RELEASED BY CREW 078S03.. CREW ON SITE .. FETR 12:45.. CAY XFMR CHANGED AND BACK IN AT 11:15 VER/CRB
8297 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2021-02-24 11:56 | 2021-02-24 16:00 | 5 | 244 | 4240911 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Resagged open wire, restored @ 16:00. Please send copy to tech. Pole 45-a3-1008 rotten, Needs new pole, and can change out open wire at later date. Tagged pole rotten do not climb. windstream pole
8298 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2011-10-15 15:19 | 2011-10-15 16:20 | 20 | 61 | 4985681 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHGED OLD CUTOUT ON POLE 116-78 30T LINE FUSE//COD 20// VER/DBM IDC XXXX
8299 | Hazard | 3303902 | LESLIE | WOOTON | 2012-07-08 23:45 | 2012-07-09 09:55 | 2 | 610 | 4630211 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A
8300 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-01-05 10:50 | 2012-01-05 14:54 | 5 | 244 | 4234991 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED NEED TO CHG 25KVA TRUCKS OK BEEN LEAKING AND SECONDARY BUSHNINGS R BROKEN TRANSFOMER IS AT 3900 ADDRESS RELEASED BY CREW 078S03 ///VER/CRB IDC DIM LIGHT CALL CHANGED TIME OFF FROM 1028 ESTIMATED TIME OFF XXXX
8301 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-01-14 14:14 | 2010-01-14 15:15 | 20 | 61 | 54199-1 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR ON LOW SIDE OF STEP DOWN TRANS CAP NUT WAS OFF OF DOOR. REFUSED EVERYTHING OK. VER/HFP L3/HFP IDC XXXX
8302 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2015-03-07 11:55 | 2015-03-07 17:00 | 4 | 305 | 4157991 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REFUSED XFMR, FUSE HAD ROTTED INTO/ COD 4// VER/ ADH
8303 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2014-07-29 01:10 | 2014-07-29 11:20 | 2 | 610 | 4304481 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE SERVICER CHECK DURING DAYLIGHT HOURS// CUTOUT FELL APART NEED LINE CREW NO TRUCK RELEASED BY CREW 078S08,,CREW ON SITE,REPLACED CUTOUT. ALL POWER RESTORED VER/CRB
8304 | Hazard | 3303902 | LESLIE | WOOTON | 2010-08-07 12:38 | 2010-08-07 14:40 | 10 | 122 | 51050-1 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLED LINE,,FOUND BAD ARRESTOR ON POLE 438-49 ON CSP XFMR,,NO CUSTS SERVED OFF THIS,,REMOVED RISER...(ISOLATING POLE # IS ACTUALLY 438-144),,,,,POWER RESTORED @ 14:40...RGP....//COD 10// VER/DBM
8305 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-10-31 16:15 | 2017-10-31 18:17 | 10 | 122 | 4520381 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER NO ANSWER GOT SPAN OF PRIMARY ON POLE 38831135000003 WIRE IS ROTTEN //COD 10 //
8306 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-11-03 18:04 | 2009-11-03 23:09 | 4 | 305 | 59006-1 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN///// BAD 25KVA 7200 XFMR BAD. MANUAL. BIG MATERIAL MIGHT REACH? RELEASED BY CREW 077S08 REPLACED XFMR AND CHECKED VOLTAGE JKC// VER/TOM L3/TOM IDC XXXX
8307 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2018-03-24 18:25 | 2018-03-25 14:45 | 1 | 1220 | 4054301 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Crew required. #4 service burned in two. This is behind the house down over the hill across a fence on Card Mtn. Released by crew 074S07/ replaced squeeze on xfmr,, all power restored //can close mwl
8308 | Paintsville | 3409302 | KENWOOD | AUXIER | 2015-04-26 15:09 | 2015-04-26 20:14 | 4 | 305 | 4367791 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP XFMR. CAN TRUCK - NEED 25 KVA XFMR, CUTOUT AND FIBERGLASS BRACKET. CREW ENROUTE TO REPLACE./ ISO 38830882D00086/ COD 4/ SIDE TAPS 1930 TO 2007/ ORIGINAL TRANSFORMER 2014 SEE H4367791 FOR OUTAGE ON SIDE TAPS TO REPLACE XFMR VER/HFP L3/HFP
8309 | Pikeville | 3421001 | BREAKS | CITY | 2013-10-18 08:25 | 2013-10-18 12:45 | 12 | 260 | 4945641 | 1220 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED BURNED OFF TOP OF POLE 219-172 RELEASED BY CREW 074S02 FUSE OPEN ON POLE 37820243C00056 CREW ONSITE MAKING REPAIRS POWER RESTORED @ 12:45 RELEASED BY CREW 074H18//COD 12// VER/DBM L3/HFP IDC XXXX
8310 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-04-07 14:42 | 2018-04-07 17:36 | 7 | 174 | 4199451 | 1218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUST//NO RDG ON MTR// Transformer fuse broke, back in at 17:36
8311 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2014-01-06 17:59 | 2014-01-07 00:45 | 3 | 406 | 4239961 | 1218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830249D00071 3PHASE POLE BURNT OFF ABOVE XFMR, HANGING IN AIR. 40/5 POLE,25KV XFMR 12KV,1- ARM AND BRACES, 2- ARM PINS AND INSULATORS, POLE TOP PIN AND INSULATOR, PRIMARY TAP OFF POLE DEADEND, 1-GUY, 2 CUTOUTS AND ARRESTORS.COMBS, HICKS, MELTON & SEXTON SWITCHES @249D-205 IN AT 00:45 VER/SEF IDC MADE DUP ASSUMING ONLY ONE OUT TILL WE OPENED RECLOSER CHANGED COUNT FROM 295 XXXX
8312 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-09-10 01:09 | 2015-09-10 01:38 | 42 | 29 | H4219711 | 1218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE 4219711.... B PHASE ONLY 18 CUSTOMERS/ BAD CUTOUT 38821082000187/ TO SAFELY CHANGE CUTOUT OPENED A &C PHASES 42 CUSTOMERS @0109/ ALL POWER RESTORED @ 0138/ ISO 38821082B20293/ COD 60/ B PHASE ONLY 18 CUSTOMERS/ VER/BOW L3/HFP XXXHFP AJB TOF 9/9
8313 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2022-12-24 03:14 | 2022-12-24 10:00 | 3 | 406 | 4338281 | 1218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Needs to be looked at first thing/crossing/has generator going right now. Repaired riser//RECONDUCTORING GOING ON COD 3 AT THIS TIME//CALLED CSX TO INFORM THEM POWER WAS RESTORED AT 1000
8314 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-04 09:19 | 2008-08-05 05:37 | 1 | 1218 | 64896-1 | 1218 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 3308603 OFF DUE TO STATION TRANSFORMER FAILURE/WILL HAVE TO REMAIN OPEN UNTIL MOBILE IS INSTALLED AT 2359 MONDAY NIGHT VER/KEP IDC XXXX
8315 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-01-16 07:29 | 2013-01-16 14:15 | 3 | 406 | 4610071 | 1218 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CREW ENROUTE.. ///VER/CRB /L/3 CRB IDC XXXX
8316 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-03-04 14:28 | 2016-03-05 10:45 | 1 | 1217 | 4817071 | 1217 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1- BAD 25KVA 7200 240/480 2 BUSHING CAN. CREW REQD. TRUCK OK. POLE 70-3683 RELEASED BY CREW 078S07/ ISO 38830070B33683/ COD 1/ VER/BOW
8317 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-07-17 10:30 | 2018-07-17 15:34 | 4 | 304 | 4786811 | 1216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout door burnt up, need new cutout and arrestor. No trucks, crew required. Released by crew 078H04. Repairs made ticket complete. L3/HFP
8318 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-05-04 08:37 | 2016-05-04 13:41 | 4 | 304 | 4172481 | 1216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED REPLACE BAD 25 KVA TRANSFORMER TRUCK TO POLE RELEASED BY CREW 078S02/CREW ON SITE/FETR 1415/VEM/REPAIRS MADE AND ALL CUST RESTORED 1341/PLEASE CLOSE TICKET/THANKS/VEMVER/AWD
8319 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-05-28 18:53 | 2021-05-29 15:09 | 1 | 1216 | 4640011 | 1216 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | middle phase has burnt down at recloser pole, primary is in the clear. will need line crew, manuel r-o-w crew, flagging crew. cust agreed to wait untill morning Released by crew 077S02.. restored power at 15:09
8320 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2020-10-11 07:31 | 2020-10-11 12:35 | 4 | 304 | 4543811 | 1216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed andburned the top off of pole 473/101. this pole does have a xfmr on it. will need fiberglass pole top extention and new 7200 cutout. not by truck should bring the utv. isoltaed groundedandtagged to B.tackett at pole 38830497000098 Released by,repairs made all cust restored @ 1235please close ticket thanks.bt
8321 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-12-21 15:23 | 2011-12-21 16:39 | 16 | 76 | 4193561 | 1216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | <<ONLY PHASE B FUSE BLOWN>> PATROLLING. CUTOUT BROKE DOWN AND BURNED POLE 737-240 OFF. ISOLATED ON POLE 38830737000209 AND WILL RESTORE ALL BUT THIS ONE XFMR.CLOSED FUSE IN AT 16:39 ALL BACK ON BUT ONE AND CUSTOMER WANTS THAT METER REMOVED SH// WILL MAKE REPAIRS AND LEAVE CUSTOMER DISCONNECTED//COD 40// VER/DBM IDCC CNT40, PH A XXXX
8322 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2013-08-11 17:21 | 2013-08-11 17:53 | 38 | 32 | 4650461 | 1216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING CUTOUTBAD CUTOUT ON POLE 353-127 ,OPENED STEPDOWN ON POLE 353-328 AT 17:21 TO ISOLATEBAD CUTOUT ON POLE 353-127 ,OPENED STEPDOWN ON POLE 353-328 AT 17:21 TO ISOLATE . MADE REPAIRS RESTORED POWER AT 17:53 VER/CRB L/3 CRB
8323 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-07-19 12:02 | 2022-07-19 13:18 | 16 | 76 | 4523171 | 1216 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | primary off pin @ 184-153..repairs made ,,line fuse 184-246 in @ 13:18 ,,complete
8324 | Hazard | 3311101 | STINNETT | REDBIRD | 2012-10-08 14:30 | 2012-10-08 15:15 | 27 | 45 | 4123861 | 1215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE FUSE TO REPLACE DEFECTIVE CUTOUT ON POLE 37830554000048 /// COD-27 ISO LF 37830554000045 RELATED TO ORDER 4123571 AND COMMENTS FROM THAT ORDER " 7.2KV CUTOUT BAD NO POWER OFF AT THIS TIME CREW IN ROUTE POWER OFF @ 1430 AND POWER RESTORED @ 1515 " VER/HFP L3/HFP IDC XXXX
8325 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-11-27 13:02 | 2019-11-27 17:05 | 5 | 243 | 4081081 | 1215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | crew on site broken neut in service drop . FETR 16:50 pwr on @ 17:05//cod 5
8326 | Paintsville | 3401103 | FALCON | BURNINGFK | 2020-12-25 14:15 | 2020-12-26 10:30 | 1 | 1215 | 4817301 | 1215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed in service. Repaired and restored @ 10:30. sh
8327 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-12-20 23:45 | 2012-12-21 00:30 | 27 | 45 | 4491621 | 1215 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO 38830116C00048//COD 27//FUSE DOOR ON 12KV SIDE OF STEPDOWN BAD NEED TO OPEN 12KV SIDE REPLACE DOOR.DOOR WAS WELDED CLOSE .OPEN LINE FUSE 116-48 AT 23:45 ON AT 00:30 CHANGED 12KV CUTOUT ON 116-775 STEPDOWN.POWER RESTORED// VER/DBM
8328 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2016-04-22 00:49 | 2016-04-22 10:56 | 2 | 607 | 4113371 | 1214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT CREW ENROUTE RELEASED BY CREW 074S02..CUTOUT CHANGED ALL WORK COMPLETE VER/CRB
8329 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-07-25 14:57 | 2017-07-26 11:11 | 1 | 1214 | 4178621 | 1214 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQ BAD 50KVA, SINGLE BUSHING 7200 120/240 CAN USE TRUCK CAN WAIT TILL TOMMORROW PER DALE CHATTERTON//, JUST FEEDS BILL BOARD SIGN, MAY WANT TO GO BACK WITH A 25KVA RELEASED BY CREW 078S06///REPLCED XFMER ////CUST RESTORED @ 11:11///COMPLETE BR/ ISO 39831048000147/ COD 1/ VER/BOW
8330 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-04-24 23:23 | 2011-04-25 09:30 | 2 | 607 | 63924-1 | 1214 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOLD TICKET TILL DAY BREAKER, BOTH CUSTOMERS SAID THIS WILL BE OK RELEASED BY CREW 074S05HOLD TICKET TILL DAY BREAKER, BOTH CUSTOMERS SAID THIS WILL BE OK . REPAIR LOOSE CONNECTION. CUSTOMER AT 377 HAD EQUIPMENT DAMAGE. THEY WILL CALL IN. VER/KEP IDC XXXX
8331 | South Williamson | 3411401 | DEWEY | INEZ | 2016-07-20 15:17 | 2016-07-21 11:30 | 1 | 1213 | 4661481 | 1213 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100 KVA 19.9 XFMR ON POLE BANK POLE 768-221///THIS FEEDS SCHOOL///TALKED TO CUSTOMER AND THEYRE OK WITH US CHANGING IT IN THE MORNING///TALKED TO TIM MILLER,PAINTSVILLE CREW WILL BE HERE IN THE MORNING TO REPLACE XFMR// RELEASED BY CREW 079S01// REPAIRS COMPLETE, SERVICE RESTORED, RDM VER/CRB
8332 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-07-18 17:19 | 2008-07-18 19:00 | 12 | 101 | 54024-1 | 1212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001//REPLACED BAD CUTOUT......DAH//COD 12// VER/DBM IDC XXXX
8333 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-11-15 03:24 | 2021-11-15 13:30 | 2 | 606 | 4093011 | 1212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout linecrew required Released by crew 078S11/ crew making repairs/ power restored @ 1330/ please close ticket/MLH
8334 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-07-05 23:29 | 2011-07-06 09:35 | 2 | 606 | 4472311 | 1212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER LAST CHECK SHOWS TRANSFORMER TO BE SHORTED, MANUAL 19.9 - 50 KVA, CUSTOMER SAID OK TO WAIT UNTIL MORNING TO REPLACE. NEED LINE CREW AND RIGHT OF WAY CREW. RELEASED BY CREW 077S04 VER/KEP IDCC PN267 XXXX
8335 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2018-11-22 03:02 | 2018-11-22 06:24 | 6 | 202 | 4468461 | 1212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 424-13, restored power at 06:24//// one trouble call at 02:54 not downstream from clearing device. Also comments indicate fault pole should be on 37830424000013 due to bad cutout, however that fault pole is upstream from the clearing device, and not customers not accounted for in this outage. Wondering if there should be more customers out on this outage? ACB ////// CALLED RICK MAGGARD ABOUT THIS THE FAULT POLE WAS ACTUALLY POLE 37830424000015 (TYPO ON FAULT POLE #) & LINE FUSE OUT ON POLE 37830424000163
8336 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-07-19 22:24 | 2008-07-20 00:05 | 12 | 101 | 54275-1 | 1212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008702// CREW OPENED FUSE BANK TO SAFELY REPLACE FAILED STEP-DOWN TRANSFORMER ON POLE 164-233 RELATED TO ORDER 54223 COD-12. VER/KEP IDC XXXX
8337 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-05-07 09:52 | 2008-05-07 14:55 | 4 | 303 | 57663-1 | 1212 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409301// COD-4 // SECONDARY BUSHING BAD - TRANSFORMER NEEDS REPLACED // RELEASED BY CREW 076H063// ARRIVED ON JOB GOING TO CHANGE XFMER// VER/DBM IDC XXXX
8338 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-02-26 04:38 | 2008-02-26 08:40 | 5 | 242 | 50396-1 | 1210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000903// FOUND A BAD TRANSFORMER CUTOUT ON POLE 1098-694, NEED CREW TO CHANGE THIS, CAN NOT USE TRUCK, BEHIND HOUSE, HAVE TALKED TO MR. FRALEY, WELL TAKE CARE OF THIS, WHEN HIS CREW GETS IN THE SHOP AT 7:30 RELEASED BY CREW 078S06-------TAP OFF AT 08:20 BACK ON AT 08:40 VER/HFP IDC XXXX
8339 | Pikeville | 3421001 | BREAKS | CITY | 2010-05-27 17:48 | 2010-05-27 21:50 | 5 | 242 | 51732-1 | 1210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON SIDE-TAP ON POLE 243-38 IS BROKEN,IS FRAMED HIGH ALMOST BETWEEN PHASES,NEED BIG BUCKET AND 1 MAN//VER/CRB IDCC CDC92 XXXX
8340 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2014-06-05 17:30 | 2014-06-05 19:20 | 11 | 110 | 4987791 | 1210 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 600 AMP HOT TAP BURNT IN CLEAR B PH OPEN REC, TO CLEAR UP FAULT 1909 POWER RESTORED AT 1920 CHECK CUST WHO CALLED IN OUTAGE THIS ORDER IS FOR THE 3 PHASE CUST WHO HAD PART POWER. NEED TO DUP IN HOIS FOR 17 CUST OUT FROM 1909 - 1920 THAT WERE OUTAGED WHEN RECL OPENED //// ISO OCR 38830190000146 VER/HFP L3/HFP
8341 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-11-29 10:58 | 2016-11-29 15:00 | 5 | 242 | 4142931 | 1210 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | ***SEE H4142931**** 25 KVA PADMOUNT TRANSFORMER BAD/ CREW ENROUTE TO REPLACE/ CREW ON SITE REPLACING PAD MOUNT/ PULLED ELBOW AT 811-183 (ADD 7 CUST) @ 1336 TO CHANGE BAD 50 KVA 38830811B10185 (ORIGINAL 5 CUT) ABOUT 12 CUSTOMERS OUTAGED TOTAL WHILE CHANGING PAD COUNTING THE 5 SERVIED OFF OF 811-185/ ALL POWER BACK ON AT 15:00/ NO CUSTOMERS SHOWN ON UNDERGROUND RISE FUSE 38830811B00062 AND NEED TO KNOW HOW MANY CUSTOMERS ON EACH UNDERGROUND XFMR/ ISO 38830811B10183/ COD 12/ VER/BOW
8342 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-01-12 19:08 | 2011-01-12 20:41 | 13 | 93 | 60965-1 | 1209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 384213388 //BROKEN HOT TAP LEAD-- SEND TO V MULLINS RELEASED BY CREW 078S07 // COD-13 ISO PO 38830044C35095 VER/HFP L3/HFP IDC XXXX
8343 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2014-04-07 22:52 | 2014-04-08 00:25 | 13 | 93 | 4584121 | 1209 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BROKEN TIE WIRE ON 225-25 PATROLING REST OF LINE/LINE FUSE OPEN ON 225-62/NO CREW REQUIRED 25T LINE FUSE VER/CRB IDC XXXX
8344 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-04-28 13:26 | 2008-04-28 17:55 | 10 | 269 | 55054-1 | 1208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701//OPENED FUSE POLE#188-68 COD 10//TO ISOLATE POLE#188-493//RELEASED BY CREW 078S01-----ALL POWER ON AT 17:55 VER/HFP IDC XXXX DEB OK
8345 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2010-06-01 10:58 | 2010-06-01 16:00 | 4 | 302 | 54827-1 | 1208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNT-OFF AT HOT-LINE-CLAMP CONNECTION ON 1 PHASE. DUTY SUPERVISOR NOTIFIED - ATTEMPTING TEMPORARY REPAIR UNTIL CREW CAN MAKE PERMANENT REPAIRS. RESTORED @ 16:00. WILL TURN IN JOB FOR CREW TO MAKE PERMANENT REPAIRS. SH//COD 4// VER/DBM IDC XXXX
8346 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-01-24 09:48 | 2014-01-24 14:50 | 4 | 302 | 4307911 | 1208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR, NEED A CREW AND A XFMR 19.9 RELEASED BY CREW 077S12 POWER RESTORED@14:50 REPLACED WITH 25 KVA COD-4 ISO TF 37830306000127 VER/HFP L3/HFP
8347 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-08-17 20:37 | 2017-08-18 01:39 | 4 | 302 | 4273371 | 1208 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ETA: 2115. CONNECTION BURNT OFF 1 LEG 1/0 SEC. 4 HOUSES PART POWERING. POLE 45-D4-7605 RELEASED BY CREW 078S07--CREW ON SITE--WILL OPEN LOAD BUST OPEN XFMR 7603--TO MAKE REPAIRS--ALL REPAIRS MADE--BUILT 2 NEW 1/0 LOOPS AND RE-SQUEEZED 2 SERVICES---VOLT CK GOOD--OPENED XFMR AT 00:55 (SEE H4273371)--BACK ON AT 01:39---TBL TKT COMP---RMV//COD 4 (+9)// VER/DBM
8348 | Paintsville | 3401101 | FALCON | FALC-OILS | 2010-04-25 09:02 | 2010-04-25 19:06 | 2 | 604 | 50635-1 | 1208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34818631 // BAD 15 KVA XFMR. DUTY SUPERVISOR SAID WE WILL CHANGE AS SOON AS WE CAN GET TO IT. CREW ENROUTE. REPLACED XFMR AND RESTORED TO SERVICE @ 19:06. SH COD-2 VER/HFP L3/HFP IDC XXXX
8349 | Paintsville | 3410602 | E.PRESTON | LANCER | 2020-11-15 16:06 | 2020-11-15 18:37 | 8 | 151 | 4689381 | 1208 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 6a primary netural down between pole # 38830979D00030 & 38830979D00036will require crew Released by crew 074S04
8350 | Cannonsburg | 3000103 | ASHLAND | 25-14STREET | 2017-08-20 20:38 | 2017-08-20 21:45 | 18 | 67 | 4281001 | 1206 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMER OFF @ 21:30,ON@ 21:45// VER/ ADH
8351 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-03-28 07:38 | 2012-03-28 14:20 | 3 | 402 | 4623661 | 1206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNED OFF. I REPLACED THE HOT TAP. ///VER/CRB IDC TRAINING MEETING XXXX
8352 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2016-07-08 19:29 | 2016-07-09 15:35 | 1 | 1206 | 4585681 | 1206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT,CREW REQ.,TRUCK APPROACH. ADDRESS IS 55636 RT 194 PATRICIA JACKSON IS CUST. JUST BEFORE HURLEY STORE RELEASED BY CREW 079M01REPLACED CUTOUT RESTORED POWER AT 15:35/ ISO 37820011A00501/ COD 1/ VER/BOW
8353 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-06-19 09:18 | 2022-06-19 19:21 | 2 | 603 | 4252611 | 1206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfm open on 1149-28// checking// fuse melted// refused restored
8354 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-02-20 08:09 | 2014-02-20 11:30 | 6 | 201 | 4404261 | 1206 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--BAD CUTOUT ON POLE 38830019D00194 NEEDS REPLACED NO TRUCKS--IST DRIVEWAY ON HE RIGHT UP DONAHUE RD RELEASED BY CREW 078S07 RELEASED BY CREW 078H03CREW REQUIRED--BAD CUTOUT ON POLE 38830019D00194 NEEDS REPLACED NO TRUCKS--IST DRIVEWAY ON HE RIGHT UP DONAHUE RD RELEASED BY CREW 078S07 ..TAGGED AT FUSE, GROUNDS AT SITE, CREW ON SITECREW REQUIRED--BAD CUTOUT ON POLE 38830019D00194 NEEDS REPLACED NO TRUCKS--IST DRIVEWAY ON HE RIGHT UP DONAHUE RD VER/SEF IDC XXXX
8355 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2017-06-13 11:34 | 2017-06-13 15:35 | 5 | 241 | 4957331 | 1205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 118-89 BAD 15KVA NEED 25KVA TRUCK TO POLE NEED A CUTOUT BROKE REMOVED RELEASED BY CREW 078S08 CREW ON SITE FETR 15:40 ALL PWR RESTORED @ 15:35 PLEASE CLOSE TICKET VER/CRB
8356 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2022-01-01 17:25 | 2022-01-02 13:30 | 1 | 1205 | 4251901 | 1205 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew req bad truckable 25KVA 120/240 7200 XFMR Released by crew 074H07crew req bad truckable 25KVA 120/240 7200 XFMR //power restored at 13:30
8357 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-04-08 10:38 | 2010-04-08 11:21 | 28 | 43 | 60773-1 | 1204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP BURNT BASKET INTO-B FRALEY TO ASSIST WR#34583507 VER/HFP L3/HFP IDC XXXX
8358 | Hazard | 3310502 | HADDIX | CANOE | 2010-08-07 16:22 | 2010-08-07 17:48 | 14 | 86 | 51107-1 | 1204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREWS WORKING 50739-1, HAD TO OPEN RECLOSER IN ORDER TO MAKE SAFE REPAIRS//COD 14// VER/DBM
8359 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2013-02-27 16:11 | 2013-02-27 21:12 | 4 | 301 | 4861051 | 1204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE 4861341 FOR OUTAGE TO ISOLATE CUTOUT //POLE 271-4005 OFF AT 1721 HRS TO REMOVE BROKEN CUTOUT ON 271-140POLE 271-4005 OFF AT 1721 HRS TO REMOVE BROKEN CUTOUT ON 271-140/BACK AT 271-4005 IN AT 1755 HRS CALLED FOR ONE MAN TO ASSIST IN CUTOUT CHG COD-4 ISO PO @ 38830271000140 VER/HFP L3/HFP IDC XXXX
8360 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-03-01 09:32 | 2014-03-01 14:33 | 4 | 301 | 4441931 | 1204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 817-30//NEED BIG BUCKET AND FLAGGERS// REED & JUSTICE & THOMAS & AWP CREW/REPAIRS MADE//RESTORED AT 14:33//COMPLETE//EM COD-4 ISO LF 38820817D00030 VER/HFP L3/HFP
8361 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-03-14 12:22 | 2021-03-14 13:47 | 16 | 85 | 4334921 | 1204 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B phase line fuses blown// Opened C phase @ 13:40 will check line/// A phase L/F cutout had burnt up and flash also damaged B phase cutout causing outage. I replaced all three cutouts and restored @ 14:47
8362 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2014-10-04 08:13 | 2014-10-04 18:14 | 2 | 601 | 4551441 | 1202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE BAD 7200 CUTOUT ON THIS POLE, WELL NEED CREW TO CHANGE OUT, MAY BE ABLE TO USE BIG BUCKET WELL BE CREW REQ. RELEASED BY CREW 078S06 VER/CRB
8363 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-09-25 08:26 | 2015-09-25 17:20 | 3 | 534 | 4267991 | 1202 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | @ 0937 CHECKING XFMRS FOR POSSIBLE PROBLEMS //TRIED LINE FUSE ON 24B-73 AND CAME BACK THIS FEEDS TWO PAD MOUNT XFMS D.SAMMONS IS COMING TO HELP. FIRST SPAN AND XFMR HOT AT 11:50 CHECKING OTHER SPAN, LAST SPAN BAD IN PROCESS OF REPLACING. LAST XFMR ON AT 17:20 D SAMMNONS. RELEASED BY CREW 074H02// VER/ ADH
8364 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-03-12 19:26 | 2014-03-13 15:27 | 1 | 1201 | 4486601 | 1201 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***1000 - CREW HAS PLACED RECL 194-33 NR ** CUTOUT FAILED POLE 98-B-623 //LINE FUSE FEEDING SINGLE TAP OFF 98-B-623 STILL OUT. POLE IS 60 CL 2 WILL NEED REPLACED. TRACK MACHINE NEEDED. CREW ON SITE // CREATED 4488941 - FOR WHEN CREW OPENED RECL & SWS//CUTOUT FAILED POLE 98-B-623 //LINE FUSE FEEDING SINGLE TAP OFF 98-B-623 STILL OUT. POLE IS 60 CL 2 WILL NEED REPLACED. TRACK MACHINE NEEDED. CREW ON SITE//POLE REPLACED AND POWER RESTORED. ALL ON @ 1527 03/13/14 COD-1 VER/HFP L3/HFP IDC XXXX
8365 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-01-25 09:30 | 2010-01-25 14:30 | 4 | 300 | 59210-1 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33572697 // RESQUEEZED NEUTRALS ON POLE. I BELIEVE THE XFMR HAS A BAD CONNECTION INTERNALLY RELEASED BY CREW 074S02 REDONE SOME SEC LEADS AND SER. VOLT GOOD//VER/CRB IDC CHANGED START TIME FROM 0658 XXXX
8366 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-04-23 18:42 | 2008-04-23 19:30 | 25 | 48 | 53652-1 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3010602//OPENED LINE FUSE ON POLE 1148-565// AT 18:42;// E-MAIL TO MARTIN AN RAYBURN-POLE 1148-33 IS BURNT OUT AT THE TOP AN NEEDS REPLACED/// LINE FUSE CUTOUT ON POLE 1148-565 NEEDS REPLACED AN RELOCATED OFF CROSSARM// VER/DBM IDCC PN33 XXXX
8367 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-03-12 17:42 | 2022-03-12 18:30 | 25 | 48 | 4615971 | 1200 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | lead had burned open at xfmr /// repairs made // on @ 18:30
8368 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-04 09:15 | 2008-08-05 05:15 | 1 | 1200 | 64894-1 | 1200 | TRANSMISSION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 3308603 OFF DUE TO STATION TRANSFORMER FAILURE/WILL HAVE TO REMAIN OPEN UNTIL MOBILE IS INSTALLED AT 2359 MONDAY NIGHT VER/KEP IDC XXXX
8369 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2011-08-17 16:23 | 2011-08-17 19:43 | 6 | 200 | 4721591 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 37830253000038 LINE FUSE BLOWN, CHECKING LINE//// POLE 37830253000071 LOOKS LIKE WE HAVE A BAD DEADEND INSULATOR. NEED BIG BUCKET, CALLED JEFF HE SAID HE WOULD COME TO ME AS WHEN HE GOT DONE WERE HE,S AT/// INSULATOR CHANGED, POWER RESTORED..//VER/CRB IDC XXXX
8370 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-11-10 10:23 | 2014-11-10 15:23 | 4 | 300 | 4717551 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT ON 204-67, PATROLLING LINE, FOUND BAD DEADEND INSULATOR, CUTOUT AND ARRESTER ON POLE 204-187, CALLED FOR HELP//COD 4 L/F FEEDS 3 TAPS //MADE MDC// VER/CRB // SEE 4717621 WHICH IS RELATED TO THIS & 4716381 WHICH THIS ORDER REPLACED (CLOSED ACCIDENTALLY) L3/HFP HFPC FP204-187 TON1530
8371 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-03-05 14:45 | 2022-03-05 18:45 | 5 | 240 | 4569411 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKEN,WILL REPLACE IT//TRANSFORMER IS ON THE LOAD SIDE OF L/F//COD 5//
8372 | Hazard | 3302704 | HAZARD | KENMONT | 2014-02-17 10:21 | 2014-02-17 14:21 | 5 | 240 | 4393911 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT. RELEASED BY CREW 077S04BAD CUTOUT. REPLACED CUTOUT, POWER RESTORED.//COD 5// VER/DBM
8373 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2011-12-12 09:10 | 2011-12-12 14:10 | 4 | 300 | 4170271 | 1200 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 37.5 BRING 50KVA 4/0 RISERS NO TRUCK BRING YARD DOG ALSO NEED TREE CREW PULLED METERS ON HOUSES 09;10 AM RELEASED BY CREW 078S08// COD 4// IDCC TOF0805 ESTIMATED PER COMMENTS XXXX
8374 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2021-08-16 01:06 | 2021-08-16 11:05 | 2 | 599 | 4075031 | 1198 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DISAPATCHED IN ACCORDANCE TO KENTUCKY POWER LATE NIGHT CALLOUT GUIDELINES// broke 7200 cutout of the cross arm. repairs made. power restored at 1105
8375 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2016-08-18 14:47 | 2016-08-19 10:45 | 1 | 1198 | 4811601 | 1198 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, UG | WORK 08/19/16 /WE HAVE BAD SECONDARY LEG ON UNDERGROUND SERVICE BETWEEN PEDISTAL AT 1012-C-210 AND METER BASE COULD NOT CONTACT CUSTOMER TALKED TO TIM HALL ADVISED TO WAIT UNTLL TOMORROW AND HAVE CREW COME OUT AND MAKE REPAIRS/ REPAIRS MADE ON AT 10:45 D SAMMONS/ ISO 38821012C00210/ COD 1/ VER/BOW
8376 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2019-11-15 13:15 | 2019-11-15 19:22 | 171 | 10 | 4037811 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | DOL 971262/ Load Transfer/ 12kV Bus regulators at Breaks have failed//voltage is floating high, need to add load from other sources to bring voltage down//cod 171
8377 | Hazard | 3302704 | HAZARD | KENMONT | 2012-12-21 01:11 | 2012-12-21 01:45 | 222 | 34 | 4495091 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER ON POLE 37830320C00325 AT 01:11 TO CLEAR FAULT ON POLE 37830321A00369, CLOSED REC. AT 01:16, REPLACED CUTOUT ON POLE 37830321A00369, ALL POWER RESTORED AT 01:45 RELEASED BY CREW 077S04// VER/DBM
8378 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-11-30 19:32 | 2010-11-30 21:45 | 9 | 133 | 61352-1 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37933178 //C\O GATE BURNED UP ON MIDDLE PHASE, LOW SIDE STEPDOWN//// INSTALLED NEW GATE AND FUSE POWER RESTORED. VER/HFP L3/HFP IDCC CNT11 XXXX
8379 | Pikeville | 3408103 | SALISBURY | MARTIN | 2022-06-24 12:17 | 2022-06-24 15:08 | 7 | 171 | 4308361 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lat fuse open @ 1099-31.//Replaced 7200 cutout on 38831099000113.//Restored @ 15:08
8380 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-04-29 21:47 | 2014-04-30 00:38 | 7 | 171 | 4649621 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BROKEN POLE TOP INSULATOR ON POLE 37830273A00213 ---- POWER RESTORED, VER/ARN
8381 | Paintsville | 3401102 | FALCON | SALYERSVI | 2021-06-09 15:07 | 2021-06-09 16:10 | 19 | 63 | 4697681 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | resage condutors due to low clearnce..//off@1507 on@1610
8382 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-04-11 16:11 | 2014-04-11 22:50 | 3 | 399 | 4596211 | 1197 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | C PHASE FUSE OUT (3 CUST) ON POLE 38830251000034 BAD INSULATOR @ POLE 251-10,NEED LINE CREW TO REPLACEBAD INSULATOR @ POLE 251-10, // REYNOLDS & PHELPS & GRIFFITHBAD INSULATOR @ POLE 251-10,NEED LINE CREW TO REPLACE RELEASED BY CREW 078S05//REPLACED INSULATER AND TRIED FUSE AND IT CAME BACK OUT//RE- PATROLLING//FOUND BAD LA ON POLE 251-4 CHANGING IT OUT VER/CRB
8383 | Hazard | 3311103 | STINNETT | WENDOVER | 2018-09-17 14:08 | 2018-09-17 15:00 | 23 | 52 | 4119481 | 1196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PRIMARY LOOP LAYING AGAINST POLE MADE REPAIRS REFUSED LINE @ 1500 L3/HFP
8384 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2020-06-16 14:24 | 2020-06-17 10:20 | 1 | 1196 | 4028191 | 1196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | trans fuse out on 1112B30 due to vines.removed vines,when i closed cutout it broke.diffulcult location,serving a barn that is overgrown with vines and debris,customer hs built barn roof around pole.will need big bucket to make repairs.customer ok with making repairs tomorrow Released by crew 079S03//changed C/O and removed vines, power restored at 10:20
8385 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2008-09-28 13:13 | 2008-09-28 14:45 | 13 | 92 | 51660-1 | 1196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT == REPLACED CUTOUT ON POLE 272B4- 4 == 1 OF 3 == COD-13 (12 + 1 FROM MISS MAPPED CALL - ENTERED MD FOR THAT CUSTOMER HFP) IDC XXXX
8386 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2017-07-22 23:19 | 2017-07-23 19:15 | 1 | 1196 | 4158231 | 1196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, BROKEN C/O ON POLE 1072-88, CAN NOT USE TRUCK RELEASED BY CREW 078S06 RELEASED BY CREW 078H14. L3/HFP XXXHFP
8387 | South Williamson | 3200302 | BELFRY | TOLER | 2010-01-04 04:41 | 2010-01-04 09:40 | 4 | 299 | 59493-1 | 1196 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHANGE OUT TRANSFORMER AT DAYLIGHT // CSP TRANSFORMER HAS BEEN OUT 3 TIMES IN 24HRS //. VER/KEP L3/KEP IDC XXXX
8388 | Hazard | 3308002 | JACKSON | PANBOWL | 2017-06-11 17:55 | 2017-06-11 21:54 | 5 | 239 | 4931571 | 1195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 20MIN ETA GOT BAD 50 KVA 7200 TRANSFORMER NEED BUCKET , TRANFORMER, CUTOUT AND ARRESTOR RELEASED BY CREW 077S05/// VER/DKM
8389 | Hazard | 3303902 | LESLIE | WOOTON | 2008-12-19 05:11 | 2008-12-19 09:10 | 5 | 239 | 60051-1 | 1195 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP BAD ARRESTER L3/HFP IDC XXXX
8390 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-08-11 08:42 | 2013-08-11 15:20 | 3 | 398 | 4649141 | 1194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WE ARE CHANGING CUTOUT AND ARRESTORS ON POLE426-470 VER/CRB L/3 CRB
8391 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-10-21 18:21 | 2016-10-21 21:40 | 6 | 199 | 4041811 | 1194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-5040 BAD CUTOUT VER/CRB AJB
8392 | Pikeville | 3421001 | BREAKS | CITY | 2017-07-24 16:24 | 2017-07-24 19:43 | 6 | 199 | 4174421 | 1194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA CSP 7200/120/240/ WILL NEED TO INSTALL A CUTOUT. CAN USE TRUCK RELEASED BY CREW 074S02..MAKING REPAIRS.. VER/ARN SJG
8393 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2011-05-27 12:33 | 2011-05-27 15:52 | 6 | 199 | 4192471 | 1194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 40148589 // BAD 15KVA BRING 25KVA TRUCK TO POLE RELEASED BY CREW 078S08 COD-6 ISO TF 39831147A00402 VER/HFP L3/HFP IDC XXXX
8394 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-07-13 09:52 | 2011-07-13 16:30 | 3 | 398 | 4540151 | 1194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO REPLACE CSP 25 KVA 7200 TRANSFORMER, UP SPEARS BR 1ST LEFT TRAILER AT END OF ROAD RELEASED BY CREW 074S05 COD-3 ISO TF 37830046000040 VER/HFP L3/HFP IDC THIS COULD HAVE BEEN OUT FROM 11TH BUT NOT SURE XXXX
8395 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2010-11-22 16:45 | 2010-11-22 20:04 | 6 | 199 | 58598-1 | 1194 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WR#37848311--ROTTEN POLE--SEND TO PAT THOVSON RELEASED BY CREW 078S07....TREE TRIMMERS ON SITE CLEARING R/W...CREW IN ROUTE..ORDER WILL BE WORKED BY DONNIE G. AND CREW (DHE)..NEED TO REPLACE PRIMARY DE TRANSFORMER POLE.//COD 6//ISO 38830045B33126 // VER/DBM IDC XXXX
8396 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-04-15 15:24 | 2020-04-16 11:17 | 1 | 1193 | 4700481 | 1193 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | EVERYTHING ENERGIZED TO XFMR FUSE AT 37820097000237; NO VISABLE DAMAGE TO FUSE; NO POWER TO METER; REPLACE XFMR FUSE TO SEE IF RESOLVES ISSUE.T.MITCHELL Released by crew 036E43
8397 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-09-25 08:28 | 2020-09-25 14:15 | 10 | 347 | 4494231 | 1193 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Leg bad on UG cable have crew enroute to locate. Will be opening xfmr fuse when crew arrives to locate and make repairs/// Opened xfmr @ 12:41. Installed temporary overhead serice and restored power @ 14:15. Tech is writing job for permanent repairs to be done at later date
8398 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-01-29 09:42 | 2014-01-29 14:40 | 4 | 298 | 4323191 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR.TRUCK ACCESIBLE..CALLE TIM MILLER. RELEASED BY CREW 076S01/ CREW ON SITE NOW TCM// INSTALLED 50 KVA , TCM// COD-4 ISO TF 38830875A00150 VER/HFP L3/HFP
8399 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-01-06 11:22 | 2009-01-06 13:48 | 20 | 146 | 51889-1 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408303//, CUT LOOP AT POLE# 1136-2, TWO CUST WILL BE OFF UNTIL REPAIRS ARE MADE, POLE TOP BURNT OFF, CREW ON WAY, 20T FUSE NOT SWITCH, ON AT 1212 /MD FILED/RESTORED LAST 2 AT 1348 VER/KEP L3/KEP IDC XXXX
8400 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-11-15 00:47 | 2011-11-15 05:45 | 4 | 298 | 4077121 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED CHGS CUTOUT//COD 4// VER/DBM
8401 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-03-04 19:12 | 2019-03-05 00:10 | 4 | 298 | 4951691 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout calling for help//cod 4 L3/HFP
8402 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-11-22 01:59 | 2015-11-22 06:15 | 7 | 256 | 4477651 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ON POLE 39831121B02013, CREW ON SITE,,, ISOLATED AT 1121-2011,,CLOSED FUSE AT 04:15,,INSTALLED POLE EXTENSION,, ALL POWER RESTORED/ CLOSED LOOP AT 06:15 RELEASED BY CREW 078H03 VER/KEP
8403 | Hazard | 3307301 | BULAN | ARY-HEINE | 2022-08-09 15:10 | 2022-08-09 15:18 | 149 | 8 | 4709431 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | Per Byron Combs Need Crew To Bypass Regukator Released by crew 077H02 LR- It does not show the device open until 15:10 and there were no outage calls so I went with the 1st time that showed it open.
8404 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2019-03-14 21:08 | 2019-03-15 17:00 | 1 | 1192 | 4985401 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o in back yard, crew req, can reach with big bucket from sismooch lane/
8405 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-01-26 06:36 | 2011-01-26 09:05 | 8 | 149 | 64341-1 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38577749 // ONLY CENTER PHASE OUT B PHASE 8 CUSTOMERS. OPEN RECLOSER ON POLE 48-24 AT 07:42 CLOSER IN AT 08:20 (251 CUSTOMERS ))RELEASED BY CREW 074S05//REPLACED C/O AND REPAIRED GUY AND CLOSED IN ALL 3 C/OS AT 9:05 SEE H64341-1 FOR RECL OUTAGE VER/HFP L3/HFP IDC XXXX
8406 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-12-23 12:38 | 2017-12-23 17:36 | 4 | 298 | 4667941 | 1192 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse open on pole 450-37. did not find anything wrong. gave line fuse a try and it blew. Released by crew 077H17line fuse open on pole 450-37. did not find anything wrong. gave line fuse a try and it blew. Bad cut-out on pole 450-274. Power restored at 17:36
8407 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-11-26 11:01 | 2010-11-26 13:00 | 10 | 119 | 59845-1 | 1190 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HAD A CONNECTION BURN OFF SECONDARY AT POLE 834-442 MADE REPAIRS GOT ALL BACK ON AT 13:00 RN//VER/CRB IDC XXXX
8408 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-09-11 15:48 | 2011-09-11 17:47 | 10 | 119 | 4857511 | 1190 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | LINE FUSE OPEN ON POLE 472-56, PRIMARY DOWN AT 472-210 SLEEVE PULLED OUT OF PRIMARY LINE FUSE OPEN ON POLE 472-56, PRIMARY DOWN AT 472-210 SLEEVE PULLED OUT OF PRIMARY.. MADE REPAIRS RESTORED POWER AT 17:47 COD-10 ISO LF 37830472000056 VER/HFP L3/HFP IDC XXXX
8409 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-11-18 07:18 | 2014-11-18 07:30 | 99 | 12 | 4740151 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TO ISSUE A HOLD ORDER TO SAFELY MAKE UP LOOPS// VER/SEF L3/DKGXXXC TOF 0552 THIS ORDER IS RELATED TO 4739901 AND 4738681.......LISTENED TO VOICE RECORDER AND USED OUTAGE REPORT AJB
8410 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-05-14 05:49 | 2015-05-14 12:25 | 3 | 396 | 4428321 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL LOOK AT ON REG. SHIFT PER LATE NIGHT CALLOUT GUIDELINES.. BAD 7200-25KVA CREW REQD. TRK OK. RELEASED BY CREW 078S07. CHANGED 25KVA AND RESTORED POWER 1225 WDR COD-3 ISO TF 38830118D16084 VER/HFP L3/HFP
8411 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-06-03 19:24 | 2008-06-04 02:00 | 3 | 396 | 55386-1 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT BAD NO TRUCK 140-602 2200 MIDLAND CT 2-CUST OFF 40T OUT ON 140-7 BACK ON 20;10 RELEASED BY CREW 078S08 IDCC CNT1, PN4 XXXX
8412 | Hazard | 3303902 | LESLIE | WOOTON | 2017-01-16 21:21 | 2017-01-16 23:00 | 12 | 99 | 4303901 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OPEN ON 37830510000074. OPENED RECLOSER ON 37830510000086 WITH OUTAGE 4303961 TO PICKUP ALL CUSTOMERS. FUSE BROKE ON 510-74(30T). SENT EMAIL TO D CHRISTIAN TO REMOVE LINE FUSE. VER/AWD L3/HFP HFPC LCD37830510000086 CDC86 CCU FEC57
8413 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-07-12 04:16 | 2011-07-12 14:10 | 2 | 594 | 4523561 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LIGHTNING HIT POLE BURN UP CUTOUT AND 50KVA XFMR IDC XXXX
8414 | Hazard | 3310502 | HADDIX | CANOE | 2014-12-23 00:46 | 2014-12-23 02:58 | 9 | 132 | 4875651 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 5-29 , FOUND BAD CUTOUT ON POLE 74-78 . REPLACED CUTOUT , CLOSED LINE FUSE @ 2:58. VER/SEF
8415 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-08-20 08:56 | 2015-08-20 11:08 | 9 | 132 | 4156811 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | BROKEN CUTOUT ON POLE 37830024D21588 COD-9 VER/HFP L3/HFP
8416 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-04-16 04:45 | 2018-04-16 11:21 | 3 | 396 | 4236381 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | top of pole 111-174 burned off. single phase dead-end, no truck access, need pole top extension, cutout, arrester, bracket, NO GROUNDS OR TAGS PLACED Released by crew 074S03. Repair crew on site.Made repairs and restored power @ 11:21..Per Tim Hall send copy to Cliff Freeman to right job for pole to be replace @ later date // ent to cliff freeman JEM
8417 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-10-17 19:01 | 2015-10-17 19:55 | 22 | 54 | HB4357231 | 1188 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 HEDRIX BURNED APART AT SPACER, TRUCK ACCESS//COD 42 FROM START A PHASE //OPENED SOLID BLADES ON POLE 38831074D00062 @ 1901 //OPENED RECLOSER38831074D00032 @ 1859//CLOSED IN SOLID BLADES @ 1955 PICKING UP 22 COD//CLOSED RECLOSER PICKING UP REMAINING CUSTS @ 2000//1/0 HEDRIX BURNED APART AT SPACER, TRUCK ACCESS. ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 VER/CRB AJBC LCD38831074D00032
8418 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-04-05 06:48 | 2019-04-05 14:15 | 7 | 447 | 4058961 | 1185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required isolated 223-186 /223-40 back in at 0851 hrs/send to b reynolds Released by crew 078S03,,,replaced cut out L3/HFP sjg
8419 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-11-12 11:40 | 2015-11-12 18:15 | 3 | 395 | 4432951 | 1185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 7200-25 KVA. LINE CREW .TRK TO POLE. OIL SPILL BAG RELEASED BY CREW 078S07 REPLACED TRANSFORMER, REMOVED 2/3 SERVICE FROM BARN./ ISO 38830090000226/ COD 3/ VER/BOW
8420 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-12-27 09:45 | 2015-12-27 16:20 | 3 | 395 | 4563521 | 1185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY DOWN @ POLE 374-10 TO 374-11,OPEN LINE FUSE @ 374A1-82 @ 0945 ISO & TAG TO DDC NEED LINE CREW TO MAKE REPAIRS NO TRUCK RELEASED BY CREW 078S05//1136 GAVE C YOUNGMAN PERMISSION TO REPLACE DDC TAG WITH HIS OWN//PRIMARY DOWN @ POLE 374-10 TO 374-11,OPEN LINE FUSE @ 374A1-82 @ 0945 ISO & TAG TO DDC NEED LINE CREW TO MAKE REPAIRS NO TRUCK RELEASED BY CREW 078S05.. CREW ON SITE ETR 13:45 AJB
8421 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-03-08 15:45 | 2021-03-09 11:30 | 1 | 1185 | 4316451 | 1185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | delivery truck caught communication cable shaking pole.. closd in came back out.. checked transformer and its bad.. need 25 kva 19.9 transformer.. customer said its ok to wait til morning.. Released by crew 077S11 // WRONG XFMR ON TICKET ONLY THING OUT WAS 37830398D00397 //REPLACED TRANSFORMER POWER RESTORED @1130
8422 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2019-12-20 12:18 | 2019-12-20 18:53 | 3 | 395 | 4172741 | 1185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 230-339 bad 50 kva xfr ,no truck ,,need 6 wheeler Released by crew 078S05//arived RM power on @ 18:53 please close tic RM
8423 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2014-07-22 15:51 | 2014-07-23 11:36 | 1 | 1185 | 4273571 | 1185 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THIS IS A CLOSED DELTA BANK, CHECKED VOLTAGE IN METERBASE AND GOT 175 VOLTS ON THE HIGH LEG. BAD 15 KVA 7200 2 BUSHING TRANSFORMER. POSSIBLY NO TRUCK APPROACH. I LEFT THE TRANSFORMER BANK OFF LINE. RELEASED BY CREW 079S02//COD 1// VER/DBM
8424 | Hazard | 3302703 | HAZARD | HAZARD | 2017-01-21 17:47 | 2017-01-21 20:15 | 8 | 148 | 4317751 | 1184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100 KVA//BAD 100KV TRANSFORMER 72KV, VER/CRB L3/HFP XXXHFP
8425 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2018-04-25 05:09 | 2018-04-25 10:05 | 4 | 296 | 4276021 | 1184 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines.///called cust-got recording saying call could not be complted as dialed/// Bad cutout on 501-399, also fuse is not on maps please do a MD fuse size is 25t, thanks. Apr at 1005 close ticket COD-4 ISO LF 38830501000331 ENTERED MD
8426 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-06-05 12:23 | 2022-06-05 15:12 | 7 | 169 | 4020961 | 1183 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken transformer fuse. changing15
8427 | Hazard | 3303902 | LESLIE | WOOTON | 2021-01-10 11:36 | 2021-01-10 15:00 | 8 | 204 | 4859681 | 1182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LIFTED A CLAMP ON POLE 37830366B00006 AND CLOSED L/F IN @ 1330//Released by crew 077S06. bad epoxilator insulator on pole #366-b-187, lifted clamp on pole #366-6 to isolate, and closed fuse on 365-d-72 for partial restore @13:30 hrs p.hicks
8428 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2008-02-05 13:08 | 2008-02-05 16:25 | 6 | 197 | 66544-1 | 1182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3403002//SECONDARY IS OPEN SERVING APT. BUILDING. I AM LOOKING FOR TROUBLE NOW. //3403002 TRANSFORMER ON POLE# 24-150 WAS BAD. WE CHANGED TRANSFORMER.//COD 6// VER/DBM IDC XXXX
8429 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-09-11 20:37 | 2013-09-12 16:19 | 1 | 1182 | 4840211 | 1182 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW//REPLACING CUTOUTCUTOUT BURNED UP ON POLE 24A4-1337..ABOUT 200 FT. BACK ON MOUNTAIN BEHIND LIGHTYEAR BLDG. WILL TAKE 3 MAN CREW IN THE MORNING..CUSTOMER SAID THEY COULD WAIT TILL MORNING..I TOLD THEM WE WOULD HAVE SOMEONE THER AROUND 8 AM.. RELEASED BY CREW 074H08 COD-1 ISO TF 37830024A41337 VER/HFP L3/HFP IDC XXXX
8430 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-04-24 16:48 | 2009-04-25 12:30 | 1 | 1182 | 58505-1 | 1182 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 29518428 //BAD TRANS 100 277 480 CALLING D SAMONDS//BAD TRANS 100 277 480 CALLING D SAMONDS RELEASED BY CREW 074H11 XFMR CHANGED ON AT 12:30 D SAMMONS// VER/DBM IDC XXXX
8431 | Hazard | 3309302 | VICCO | JEFF | 2018-09-18 07:26 | 2018-09-18 13:30 | 4 | 364 | 4123871 | 1181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 275-194 is burnt off, bad cutout, will need to replace pole, can take clamp off pole 118 and get fuse back in, fuse back in at 08:55 Released by crew 077S02
8432 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-07-06 22:37 | 2018-07-07 18:18 | 1 | 1181 | 4745881 | 1181 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | per customer ok to clean up 7-7-18 replaced cutout and arr
8433 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-10-07 19:17 | 2014-10-07 23:13 | 5 | 236 | 4568461 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 67-289 BAD CUTOUT NO TRUCK WILL NEED TO OPEN LINE BACK UP 67-280 TO FIX ASAP /// ROB PLEASE TAKE CARE OF THIS FIRST OPENED FUSE AT 2220 COSED IN AT 2313 (SEE 4569651) RELEASED BY CREW 078Q08 VER/KEP L3/HFP
8434 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-11-14 18:41 | 2017-11-14 22:37 | 5 | 236 | 4556891 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | bad splice in sec burnt sec down//cod 5//had to open xfmr to make repairs//opened @ 2147 // closed @ 2237//interrupted 1 addtl customer //iso 37830171000104
8435 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-09-17 23:40 | 2014-09-18 09:30 | 2 | 590 | 4507671 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PER AFTER HOURS GUIDE LINES THIS WILL BE CHECKED 09/18 DURRING REGULAR HOURS ARRESTER BLEW AND CAUSED POLE GROUND TO CONTACT XFMR RISER. CLEARED AND RESTORED @ 9:30. SH VER/CRB
8436 | Whitesburg | 3314401 | MAYKING | ERMINE | 2008-12-19 16:34 | 2008-12-20 12:14 | 1 | 1180 | 60784-1 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP COD-1 3314401// POLE 426-503 IS BROKE AND WILL CHG POLE OUT LATER TODAY RELEASED BY CREW 074S07 // LARRY LAWSON WILL BE COMING OUT THIS MORNING TO WORK THIS JOB// L3/HFP IDC XXXX
8437 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-11-18 09:07 | 2019-11-18 11:05 | 10 | 118 | 4043441 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT IN CLEAR ON C PHASE RECLOSER 38831052A00339//COD 12 FROM THE BEGIINING OF OUTAGE//PICKED CUSTS BACK UP @ 1105/ C PHASE RECLOSER 38831052A00339//COD 12 FROM THE BEGIINING OF OUTAGE//. hot tap & sturrip have been replaced reclosure is back to normal Released by crew 074S04
8438 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2021-11-26 15:54 | 2021-11-26 19:50 | 5 | 236 | 4127021 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 lash coming off of pole 1064B-29 has a broke neutral.non truck..opened transformer on pole 29 at 19:00 and got it back in at 19:50
8439 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2022-09-03 12:43 | 2022-09-03 16:15 | 13 | 212 | 4833361 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | b phase only (5 customers) out originally due to B phase hot tap broke off the line fuse cutout/ // opened a & c phase (8 customers) at 1600/ closed all 3 phases at 1615
8440 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-12-22 17:36 | 2022-12-23 13:16 | 1 | 1180 | 4287721 | 1180 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad manual 25 kva 19.9 on 37830204000007. Will need line crew and manual ROW crew to make repairs. Will hold till 12-23-22 per Glen Combs. Released by crew 077S06 ///restored at 1316
8441 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2008-06-23 00:12 | 2008-06-23 06:45 | 3 | 393 | 52575-1 | 1179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3300601// SERVICER WILL CHECK FIRST THING IN MORNING.- OK VIA DUTY SUPV // FUSE ROTTED INTO/COD-3 VER/KEP IDC XXXX
8442 | Hazard | 3301401 | COMBS | COMBS | 2015-02-10 09:32 | 2015-02-10 11:43 | 9 | 131 | H4004231 | 1179 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION AT TRANSFORMER GOING BAD, NEED LINE CREW AND 4/0 TRANSFORMER LEADS AND 5 FT OF 336 SECONDARY CONDUCTOR. RELEASED BY CREW 077S04CONNECTION AT TRANSFORMER GOING BAD, NEED LINE CREW AND 4/0 TRANSFORMER LEADS AND 5 FT OF 336 SECONDARY CONDUCTOR. OPENED TRANSFORMER AT 09:32/CONNECTION AT TRANSFORMER GOING BAD, NEED LINE CREW AND 4/0 TRANSFORMER LEADS AND 5 FT OF 336 SECONDARY CONDUCTOR./10 CUSTOMERS PART POWER FROM 737/FIX IT IN HOIS/COD 10+9// VER/ ADH L3/HFP AJB
8443 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-03-13 15:57 | 2014-03-13 16:35 | 31 | 38 | 4490121 | 1178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE TO REPLACE FAILED CUTOUT OPEN LINE AT 1557 CLOSED AT 1635 VER/SEF IDC XXXX
8444 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2017-11-18 16:12 | 2017-11-19 11:50 | 1 | 1178 | 4568611 | 1178 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required big bucket ok for yard Released by crew 078S03 Released by crew 078Q04crew required big bucket ok for yard Released by crew 078S03. broken cutout @ 250-c1-306. transformer reenergized @ 1150/ ISO 38830250C10306/ COD 1
8445 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-05-28 10:53 | 2008-05-28 12:40 | 11 | 107 | 52124-1 | 1177 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BROKE INTO ON POLE 311-65. I AM GOING TO REPLACE CUTOUT. IT BLEW THE LINE FUSE ON POLE 311-32. I CHANGED CUTOUT AND CLOSED LINE FUSE IN AT 12:40 AND IT STAYED.//3409502//VER/CRB IDC XXXX
8446 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-07-04 17:34 | 2016-07-05 13:10 | 1 | 1176 | 4524991 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED VER/HFP L3/HFP
8447 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-05-31 09:50 | 2017-05-31 13:06 | 6 | 196 | 4885201 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POE 283-101. BAD CUT-OUT ON POLE 283-172, CHANGED CUT-OUT AND RESTORED POWER AT 12:55. COD-6 ISO LF 37830283000101
8448 | Hazard | 3303902 | LESLIE | WOOTON | 2021-05-27 12:39 | 2021-05-27 15:55 | 6 | 196 | 4632001 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broken cut-out on 37830462000222. Power restored @ 15:55
8449 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2019-01-22 09:16 | 2019-01-22 10:40 | 14 | 84 | 4702971 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout failed. Replaced and Restored @ 10:40. sh
8450 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-01-20 04:21 | 2022-01-20 08:30 | 19 | 249 | 4389251 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout at 221-25. need 19.9 cutout and big bucket//found cracked cutout on LF at 221-25 and opened it at 0818 to change that cutout as well (15 COD)//line fuse also broke had open from 08:18 to 08:30 Released by crew 077S10
8451 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2019-04-25 16:54 | 2019-04-25 17:50 | 21 | 56 | 4158991 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv door, replaced door restored 30t L3/HFP
8452 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2015-06-20 15:45 | 2015-06-20 17:23 | 12 | 98 | 4619571 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN AT POLE 353-58, WILL BE PATROLLING, FOUND A BAD CUT OUT AT POLE 329-165, WILL BE CHANGING. CHANGED C/O AND CLOSED L/F AT 1723.// VER/ ADH
8453 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-10-28 11:11 | 2015-10-28 12:35 | 14 | 84 | 4387391 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN AT POLE 421-8, PATROLLED LINE BAD CUT-OUT ON POLE 421-8, CHANGED CUT-OUT AND CLOSED L/F BACK IN AT 1235.// VER/ ADH L3/HFP XXXHFP
8454 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-02-09 13:40 | 2010-02-09 16:56 | 6 | 196 | 54426-1 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAVE 2 BAD CUTOUTS ONE ON FAULT POLE 38831125B00355 THE OTHER IS ON A LINE FUSE POLE 38831125B00204 THIS HAS A 40 T ON IT WILL HAVE OFF TILL WE GET POWER RESTORED. TIM MCCOY//COD 6I RELEASED BY CREW 074H10//VER/CRB IDCC PN355 XXXX
8455 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-05-05 11:29 | 2016-05-05 14:45 | 6 | 196 | 4177401 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW ON SITE--CHANGING CUTOUTS ON TAP--OPENED PRIMARY AT 11:43 AT POLE 39831147C14013--XFMR ON THIS POLE STILL ON--CLOSED PRIMARY LOOP(HOTTAP) AT 14:45---ALL CUST RESTORED ISO 39831147C14013 COD 6 VER/AWD
8456 | Hazard | 3308002 | JACKSON | PANBOWL | 2018-09-03 10:26 | 2018-09-03 13:14 | 7 | 168 | 4037361 | 1176 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 1083-804 rotted off at ground will need replaced before arrester can be replaced L3/HFP
8457 | Pikeville | 3402003 | KEYSER | MULLINS | 2013-06-29 18:39 | 2013-06-29 22:34 | 5 | 235 | 4428471 | 1175 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE COTOUT . VER/TOM L3/TOM IDC XXXX
8458 | Cannonsburg | 3000101 | ASHLAND | 25-25STREET | 2012-10-28 01:51 | 2012-10-28 03:00 | 17 | 69 | 4177461 | 1173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-7307 BAD CUTOUT 10T FUSE. CC 17 VER /SDB IDC XXXX
8459 | Hazard | 3310502 | HADDIX | CANOE | 2014-09-14 05:10 | 2014-09-14 05:27 | 69 | 17 | 4497531 | 1173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | JIM MULLINS OPENING RECLOSER TO MAKE UP LOOP OPENED AT 0510 CLOSED AT 0527 VER/SEF /// RELATED TO 4497481 L3/HFP HFPC FP AJB
8460 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-08-18 02:19 | 2015-08-18 08:50 | 3 | 391 | 4145521 | 1173 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK IN THE AM. BAD CURRENT LIMITING FUSE// VER/ ADH
8461 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-10-27 07:49 | 2010-10-27 17:35 | 2 | 586 | 65463-1 | 1172 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BOTTOM BRACKET ON XFRM HAS PULLED LOOSE FROM POLE XFRM IS DENTED NEED 50 KVA XFRM 19.9 KV AND CREW POLE NEEDS TO BE STRAIGHTENED XFM FUSE TUBE BROKE RELEASED BY CREW 077E07//COD 2// VER/DBM IDC XXXX
8462 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-11-18 21:41 | 2017-11-19 17:12 | 1 | 1171 | 4571741 | 1171 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfm. cutout broken on pole 237-245/////will make repairs.l/f off 1630-1712 37830237C00014
8463 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-02-22 06:22 | 2015-02-22 07:40 | 15 | 78 | 4069621 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE ASSOCIATED WITH 4065181// OPENED STEPDOWN TO ISOALTE FAULT AND MAKE REPAIRS//. VER/SEF
8464 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-08-13 14:06 | 2018-08-13 16:16 | 9 | 130 | 4947911 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | primary broke at deadend on pole #38831052A00048 will make repairs.closed in @ 16:16 L3/HFP
8465 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-12-28 10:13 | 2014-12-28 14:07 | 5 | 234 | 4887951 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37830134B00009 , BAD CUT OUT ON POLE 37830134B00180 . NEED 1 MAN & 19.9 CUT OUT .//L/F FEEDS BOTH TAPS MADE MD//COD 5// VER/CRB
8466 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-05-29 10:35 | 2012-05-29 17:05 | 3 | 390 | 4840031 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFORMER, NEED TO GO BACK WITH 25KVA . NEED LINE CREW , TRUCK TO POLE. HOLD FOR EVEN. CREW. RELEASED BY CREW 078S01/FETR 17:30/ JEH/ REPAIRS COMP. POWER REST @ 17:05 078H05 COD-3 ISO TF 38830210000109 VER/HFP L3/HFP IDC XXXX
8467 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2020-04-03 09:24 | 2020-04-03 11:34 | 9 | 130 | 4557011 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50KVA XFMR on pole 296A-657. Released by crew 077H20,crew on site , all power restored @ 11:34 hrs.p.hicks
8468 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-05-17 07:50 | 2014-05-17 14:20 | 3 | 390 | 4718121 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OUT POLE 68-A-240// OPEN LINE FUSE AT POLE 68-A-58 AT 0849// B.FRALEY, C. YOUNGMAN, K.GRIFFITH & W. BARKER //NEED TECH AND 3 MAN PRC CREWNEED TECH AND 3 MAN PRC CREW--OPENED LINE FUSE ON POLE 38830068A00058 AT 08:48--INSTALLD TAG FOR DDC--INSTALLED GROUND AT POLE 38830068A00058NEED TECH AND 3 MAN PRC CREW--OPENED LINE FUSE ON POLE 38830068A00058 AT 08:48(SEE 4718281)--INSTALLD TAG FOR DDC--INSTALLED GROUND AT POLE 38830068A0005//COD 3// VER/DBM IDC XXXX
8469 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-09-12 21:15 | 2015-09-12 22:00 | 26 | 45 | 4233071 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DANNY OPENING LINE FUSE TO PUT OUT POLE FIRE VER/SEF L3/DKG VERIFIED TIMES WITH VOICE RECORDER AJB
8470 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-04-27 16:45 | 2013-04-27 18:15 | 13 | 90 | 4051881 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | REPLASING PEDESTAL , OPENED XFMR ON POLE 1083-779 @ 16:45 CLOSED BACK IN @ 18:15 ///VER/CRB L/3 CRB IDC XXXX
8471 | Cannonsburg | 3001401 | LOUISA | CITY | 2010-12-15 21:10 | 2010-12-15 22:40 | 13 | 90 | 50838-1 | 1170 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PART POWER ON POLE 38830454A30119 //BAD POLE TO WORK FOR ONE MAN// BILL F IN ROUTE // OPENED TRANSFORMER AT 2110 // POWER RESTORED AT 2240// CLOSE TICKET//COD 13 // VER/DBM IDC XXXX
8472 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2014-06-16 23:03 | 2014-06-17 01:50 | 7 | 167 | 4099471 | 1169 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL REPLACE BAD CUTOUT WILL NEED A LINEMAN & COVERUP
8473 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2022-05-22 19:40 | 2022-05-22 20:53 | 16 | 73 | 4929701 | 1168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout Released by crew 078S02
8474 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-01-25 14:03 | 2016-01-25 14:19 | 73 | 16 | 4649361 | 1168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED UP STEPDOWN TO SAFELY REPLACE CUTOUT. OPENED STEPDOWN ON PN 502- 179 AT 14:03 CLOSED AT 14:19 ALL POWER RESTORED PLEASE CLOSETICKET THANKS DWW/ VER/AWD AJB
8475 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2017-01-05 16:48 | 2017-01-05 19:14 | 8 | 146 | 4271971 | 1168 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILING ON 46-142 CATHING POLE ON FIRE POLE BURNT ABOUT 1/8AY THRU REMOVED HOT TAP TO DE-ENERGIZE CUTOUT NEED BIG BUCKET TO MAKE REPAIRS CUTOUT IS IN PRIMARY ZONE REMOVED HOT TAP AT 16:48 RELEASED BY CREW 079H03//PUT FIRE OUT AND REPLACED BAD CUTOUT RESTORED POWER AT 19:14 TIM MCCOY/ ISO 37830046000142/ COD 8/ VER/BOW L3/HFP XXXHFP
8476 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-12-15 19:25 | 2009-12-15 20:18 | 22 | 53 | 63676-1 | 1166 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED BAD HOT TAP ON LINE FUSE//COD 22// VER/DBM
8477 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-02-05 16:40 | 2011-02-05 20:33 | 5 | 233 | 54551-1 | 1165 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 SPAN OF PRI. DOWN ON POLE 1150-73 WILL NEED TO OPEN TO REPAIR ON POLE 1150-63 WHEN CREW ARRIVES---OPENED AT 19:58 CLOSED IN AT 20:33 VER/KEP IDC XXXX
8478 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-06-17 23:03 | 2015-06-18 03:54 | 4 | 291 | 4591841 | 1164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT, PATROLLING LINE. FOUND BAD INSULATOR ON POLE 205-293, VINES ALL OVER POLE AS WELL, POWER RESTORED VER/ARN
8479 | Hazard | 3302703 | HAZARD | HAZARD | 2018-06-18 19:41 | 2018-06-18 22:55 | 6 | 194 | 4618381 | 1164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANS//50 KVA LEAKING WILL NEED REPLACED 7200 Released by crew 077S01
8480 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-12-30 16:11 | 2018-12-30 19:25 | 6 | 194 | 4614351 | 1164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on crossarm at pole 138-17, crew required Released by crew 078H04 crew on site FETR 20:00all pwr restored @ 19:25 please close ticket LRM
8481 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2014-03-03 09:12 | 2014-03-03 12:26 | 6 | 194 | 4446731 | 1164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY BURNT INTO IN MIDSPAN WILL HAVE TO OPEN XFMR TO REPAIR. CONNECTOR FROZE OUT OPENED XFMR AT 12: CLOSED AT 12:26 VER/SEF
8482 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-09-17 15:36 | 2013-09-18 11:00 | 1 | 1164 | 4861721 | 1164 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THIS IS SINGLE CUSTOMER OUT. NEED AWP, AND A BUCKET RIGHT OF WAY CREW TO CUT TREES FROM SECODARY POLE. ALSO TWO MEN AND BUCKET TRUCK TO REPLACE SECONDARY EXT CONDUCTOR THAT CROSSES THE MAIN ROAD. THE CONDUCTOR IS BLOWED APART OVER THE HOUSE. THIS IS AT SAMS TOWING ON THE RIGHT JUST BEFORE BARRENSHEE. TIM HALL WILL SEND A CREW FIRST THING IN THE MORNING. RELEASED BY CREW 079S02//112FT OF 2/3  POWER RESTORED @ 11:00 VER/SEF IDC XXXX
8483 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-08-17 13:35 | 2016-08-17 14:02 | 43 | 27 | 4801741 | 1161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NUMBER 6A WIRE UN RAVELING OPEN LINE LONG ENOUGH TO MAKE REPAIRS OPENED LINE AT 1335 MADE REPAIRS AND RESTORED POWER AT 1402 RELEASED BY CREW 077H01 38831060A40375 43 VER/AWD L3/HFP XXXHFP AJB
8484 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2011-05-22 20:39 | 2011-05-23 16:00 | 1 | 1161 | 4131441 | 1161 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER/SECONDARY POLE BROKE/12:47CREW ENROUTE WITH 35`5POLE AND 15KVA XFMER-PRB COD-1 ISO TF 38830738A00322 VER/HFP L3/HFP IDCC FP NULL XXXX
8485 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-07-18 15:49 | 2014-07-18 17:45 | 10 | 116 | 4260171 | 1160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-117 19.9 CUTOUT FELL APART SEND TO BRENT RELEASED BY CREW 078S08,,CREW ON SITE, REPAIRS MADE, ALL POWER RESTORED//COD 10// VER/DBM
8486 | Hazard | 3303902 | LESLIE | WOOTON | 2009-04-25 10:32 | 2009-04-25 20:12 | 2 | 580 | 61361-1 | 1160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3303902//STS WR# 29523349 BAD TRANSFORMER CAL,LED FOR ONE RESTORED POWER JKC VER/LDA IDC XXXX
8487 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-05-04 10:59 | 2019-05-04 13:24 | 8 | 145 | 4217041 | 1160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT/////////REPLACED BROKEN CUTOUT ON POLE 170-37,RESTORED POWER L3/HFP
8488 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-11-05 12:18 | 2013-11-05 16:10 | 5 | 232 | 4011711 | 1160 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CREW REQUIRED RELEASED BY CREW 074S02//COD 5// VER/DBM
8489 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-02-05 23:38 | 2017-02-06 09:17 | 2 | 579 | 4360211 | 1158 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200-120/240 25 KVA XFMER. CHANGE C/O & ARRESTOR. TRK TO POLE. CREW REQD. RELEASED BY CREW 078S07--CREW ON SITE---CHANGED OUT 25KVA. CUTOUT AND BRACKET VER/CRB L3/HFP XXXHFP
8490 | Whitesburg | 3401301 | FLEMING | NEON | 2013-09-18 10:37 | 2013-09-18 10:50 | 89 | 13 | 4863541 | 1157 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | ROGER AMBURGEY OPENING "A" PHASE TO BY PASS REGULATER HE IS GETTING READY TO CHANGE OUT COD 89 VER/SEF L3/HFP IDC XXXX
8491 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-03-27 11:45 | 2010-03-27 12:53 | 17 | 68 | 54924-1 | 1156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR# 34421948 // RELATED TO ORDER 54914-1 " POLE BURNT OFF DUE TO CUTOUT FAILURE. OPENED LINE FUSE ON 737-32 @ 11:45 TO ISOLATE TROUBLE. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE." VER/HFP L3/HFP IDC XXXX
8492 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-12-20 11:57 | 2008-12-20 21:35 | 2 | 578 | 61211-1 | 1156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR FUSE IS OUT,WILL RE-FUSECUTOUT IS BURNED UP,WILL REPLACE IT SOON AS A BUCKET CAN GET TO ME,MEANWHILE AM GOING TO JACKSON TO HELP PUT UP SOME WIRE// COD-2 // VER/LDA L3/KEP IDC XXXX
8493 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2022-08-16 09:52 | 2022-08-16 19:30 | 2 | 578 | 4749371 | 1156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer pole is bad shape crew is going to need to route secondary from diff direction there is a primary tap..pole 31-C-516 that is close by they will need a 25 kva transformer 7200 no truck access..roll of 2/3 secondary wire one hand dig anchor for new transformer pole and one screw anchor for secondary pole 81-506 . will also need tree crew with big bucket to trim out pine trees out to re energize primary tap Released by crew 079S02 CREW ON SITE. RESTORED AT 19:30
8494 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-07-08 15:11 | 2008-07-08 20:00 | 4 | 289 | 64580-1 | 1156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TREE LIMBS BLOWING FUSE TO 1 TR----BAD 50 KVA 19.9--NEED MATERIAL BUCKET 2 MEN RELEASED BY CREW 077S06//3310501//VER/CRB IDC XXXX
8495 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2008-02-18 10:14 | 2008-02-18 15:03 | 4 | 289 | 64707-1 | 1156 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 3409002//PRIMARY POLE ROTTED OFF AT GROUNDLINE. OPENED FUSE AND LIFTED HOT LINE CLAMP ON POLE 38830783000039. CREW ENROUTE. RELEASED BY CREW 076S02 //REPLACED POLE--CLOSED FUSE AT 15:03//VER/CRB IDCC PN49, CNT1 XXXX
8496 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-08-10 17:15 | 2009-08-10 20:00 | 7 | 165 | 58701-1 | 1155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WORK REQUEST # 31162184 // POLE 1123-253 BAD CUT OUT DOOR 10T FUSE VER/KEP L3/KEP IDC XXXX
8497 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-11-04 10:30 | 2013-11-04 10:45 | 77 | 15 | 4007031 | 1155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 188-B-113. CALLED TIM HALL CREW ON THE WAY WHEN THY GET HERE AND SET UP. WE WILL HAVE TO OPEN SOLID BLADE SWITCH ON POLE 188-65 C PHASE ONLY. FOR ABOUT 30 MINUTES TO MAKE REPAIRS. OPENED C PHASE SWITCH ON POLE 188-65 AT 10:30 CLOSED BACK IN AT 10:45 EVERYTHING OK//COD 77//ISO 37830188A00065// VER/DBM L3/HFP IDCC PN100 XXXX
8498 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-02-02 20:20 | 2014-02-03 02:45 | 3 | 385 | 4338831 | 1155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNT OFF. BROKEN CUTOUT. /// T SMITH & V HURT // TOP OF POLE BURNT OFF. BROKEN CUTOUT. OPENED LINE CUTOUT ON POLE 182-131 AT 1:30... CLOSED BACK IN AT 2:45.. COD-42 ISO LF 37830182C00131 DUP IN HOIS VER/HFP L3/HFP IDC XXXX
8499 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-07 09:05 | 2008-07-07 12:56 | 5 | 231 | 63532-1 | 1155 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401//PULLED LINE FUSE AT 09:05, POLE BURNT OFF, BAD CUTOUT//COD 5/. MIKE CHAFFIN WITH ELLIOT DAVIS CONTRACTORS TO REPLACE POLE // VER/DBM IDC XXXX
8500 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-06-28 09:14 | 2019-06-28 15:39 | 3 | 385 | 4611131 | 1155 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | found connection burnt up on xfm. pole @ sec. connections..repairs made.restored..
8501 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2013-07-12 03:27 | 2013-07-12 08:15 | 4 | 288 | 4511221 | 1152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | HELD TO AM PER GUIDLINES REPLACED TRANSFORMER FUSE THAT BROKE. COD-4 ISO 38821038D00298 VER/HFP L3/HFP IDC XXXX
8502 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2014-02-04 16:28 | 2014-02-04 18:36 | 9 | 128 | 4348521 | 1152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PATROLLING LINE.//COD 9 MADE MDC//FUSE FEEDS BOTH WAYS//PATROLLING LINE. FUSE APPEARS TO HAVE MELTED OUT. CUTOUT DOOR IS OLD TYPE AND IS STOPPED UP. CHANGING CUTOUT.PATROLLING LINE. FUSE APPEARS TO HAVE MELTED OUT. CUTOUT DOOR IS OLD TYPE AND IS STOPPED UP. CHANGING CUTOUT. REPAIRS COMPLETE - RESTORED @ 18:36. SH VER/CRB
8503 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-01-12 02:27 | 2019-01-12 07:15 | 4 | 288 | 4661011 | 1152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Loop on pole 38830624000005 is broken. Linecrew required Released by crew 078S11Loop on pole 38830624000005 is broken. Linecrew required ////Instaled a SB cutout on 624-5 to replace loop. apr at 0715 please send copy to be added to maps L3/HFP
8504 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-03-28 10:27 | 2008-03-28 12:35 | 9 | 128 | 61544-1 | 1152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008001// WIRE DOWN 69-6022 SAVE FOR JOHN HALL RELEASED BY CREW 078S08WORK COMP. POWER BACK ON 1235 PM RELEASED BY CREW 078H03 // VER/TOM IDC XXXX
8505 | Hazard | 3303902 | LESLIE | WOOTON | 2015-11-29 01:17 | 2015-11-29 10:53 | 2 | 576 | 4490591 | 1152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH AT START OF REGULAR SHIFT//TOM BAD CUTOUT ON POLE389-158. VER/CRB
8506 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2015-12-07 12:17 | 2015-12-07 17:05 | 4 | 288 | 4515911 | 1152 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DEADEND INSULATOR ON POLE 37830096D00122 IS BAD AND CAUSING TRACKING DOWN POLE.TALKED TO TIM HALL AND HE HAS HELP ON WAY.//LIFTED HOT TAP ON POLE 96-D-271 @ 1605 CLOSED @ 1655 TO ISOLATE TROUBLE//DEADEND INSULATOR ON POLE 96D-122 IS BAD AND CAUSING TRACKING DOWN POLE.TALKED TO TIM HALL AND HE HAS HELP ON WAY. RELEASED BY CREW 074H21 VER/CRB
8507 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-04-06 16:50 | 2018-04-07 12:01 | 1 | 1151 | 4197061 | 1151 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xform cutout broken feeds cust garage talk with cust said it would be ok to make repairs monday unless trouble crew can get to it earlier 197-231 Released by crew 078S04---made repairs--pwr restored @ 12:01---tbl tkt comp--rmv
8508 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-02-21 10:10 | 2018-02-21 15:20 | 43 | 310 | 4867681 | 1150 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout is broke on manuel pole, will need help. will need to drop line to replace cutout, it is same height as primary Released by crew 077S02/ 1500-1520/ ISO 37830256000017 COD 42/ ISO 37830280000021 COD 1
8509 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2016-10-09 08:27 | 2016-10-09 14:50 | 3 | 383 | 4977271 | 1149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT . BAD XFMR ON 275-32 . NEED 2 MEN & BUCKET , 15KVA XFMR 7200 . POLE MARKED WITH FLAG . RELEASED BY CREW 075H04 CHANGED XFMR AND RESTORED POWER AT 1450 CREW 077H01 VER/CRB L3/HFP XXXHFP
8510 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-03-05 15:37 | 2011-03-05 22:00 | 3 | 383 | 50114-1 | 1149 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39051575 //BAD 15KVA 72000, DOLLY AND BLOCKS, MANUAL. 4MEN CREW RELEASED BY CREW 077S08 IDCC FP20 XXXX
8511 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-11-30 05:02 | 2020-11-30 11:25 | 3 | 383 | 4729651 | 1149 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830307000057pole top rotted off--12t lat open pole38830307000050-crew req-no tag or ground-ds113020 Released by crew 078S01 crew on site FETR 11:45 LRM all pwr restored 11:25 please close ticket LRM
8512 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-12-06 15:47 | 2022-12-06 17:09 | 14 | 82 | 4235051 | 1148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 379-D-113. had brnt the pole. put fire out on pole and replaced cutout. power restored
8513 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-05-08 02:41 | 2012-05-08 12:15 | 2 | 574 | 4757941 | 1148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT NEED BIGGER BUCKET TRUCK AND OBSERVER TO FIX RELEASED BY CREW 078S09 REPLACED CUTOUT AND ARRESTOR POWER RESTORED AT 12:15//COD 2// VER/DBM IDC XXXX
8514 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-09-22 17:46 | 2017-09-22 22:33 | 4 | 287 | 4383151 | 1148 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE FAILED (BROKEN FUSE LINK) ON 101-96 RE-FUSED CUTOUT RESTORED POWER AT 22:33 VER/KEP VER/ALB
8515 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-07-19 17:38 | 2015-07-20 12:45 | 1 | 1147 | 4912301 | 1147 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PART POWER BAD LEG ON UNDERGROUND FIXED WIRE LOOSE ON BOTH ENDS FEADY FOR TEMP. RELEASED BY CREW 078S08/ VER/CRB
8516 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2016-12-15 03:27 | 2016-12-15 13:00 | 2 | 573 | 4194941 | 1146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LOOKS LIKE UNDERGROUND BAD 2-CUST SEND CREW AT WORK TIME// VER/ ADH
8517 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-04-19 12:28 | 2010-04-19 15:39 | 6 | 191 | 65066-1 | 1146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34730655 //--BAD 25 KVA TRANSFORMER-NEED TO REPLACE WITH 37.5--POLE BESIDE RD-CALLING CREW RELEASED BY CREW 078S07 COMP. 4/19/10 M.PHELPS RELEASED BY CREW 078H12 COD-6 VER/HFP L3/HFP IDC XXXX
8518 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2018-02-11 17:51 | 2018-02-11 20:27 | 23 | 156 | 4831341 | 1146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 208-126 37830208000126 (cod: 1) , will need to open line at 37830184D20448, line fuses (addl 22 cod)cutout broke on pole 208-126, will need to open line at 37830184D20448, line fuses. all power restored. opened at 19:42, closed in at 20:27
8519 | Hazard | 3303902 | LESLIE | WOOTON | 2008-06-09 11:53 | 2008-06-09 18:15 | 3 | 382 | 60502-1 | 1146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSF CSP ==//3303902//VER/CRB IDC XXXX
8520 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-12-24 20:41 | 2022-12-24 23:52 | 6 | 191 | 4352281 | 1146 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 trans. @24-B3-545, will be changing. Got trans. changed out and power restored @2352.
8521 | Hazard | 3309302 | VICCO | JEFF | 2012-12-18 10:06 | 2012-12-18 13:55 | 5 | 229 | 4479131 | 1145 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTOR ON SECONDARY BURNED OFF === REPAIRED == POWER OK ///VER/CRB L/3 CRB
8522 | Hazard | 3303901 | LESLIE | HYDEN | 2011-12-08 08:59 | 2011-12-08 13:45 | 4 | 286 | 4158681 | 1144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 120/240 TRUCK ACCESS WILL NEED FLAGGERS RELEASED BY CREW 077S01//FLAGGERS SETTING OUT SIGNS,,STARTING TO SET UP COD-4 ISO TF 37830412C00255 VER/HFP L3/HFP IDC XXXX
8523 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-06-30 08:24 | 2017-06-30 10:47 | 8 | 143 | 4060611 | 1144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | COMPLETE ORDER
8524 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-05-17 14:01 | 2010-05-17 19:13 | 9 | 312 | 63956-1 | 1144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35151757 // LINE FUSE 90-67 20T, HOT TAP POLE 90-142, BURNT XFMR POLE 90-323 RESTORED @19:13 RELEASED BY CREW 078H12 VER/KEP L3/KEP IDC XXXX
8525 | Pikeville | 3402002 | KEYSER | STONECOAL | 2020-10-28 18:56 | 2020-10-28 20:24 | 13 | 88 | 4593341 | 1144 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | B phase URD riser open @1152-B2-353, fuse had pulled into, refused @2024.
8526 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2010-11-10 12:57 | 2010-11-10 13:49 | 22 | 52 | 54591-1 | 1144 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SW ORDER CREATED TO SHOW FEEDER OUTAGE AND LOAD TRANSFER ON THE 47TH/49TH ST AND ASHLAND/29TH ST 12KV CKTS. SEE ORDER 54504-1 VER/PDP IDC XXXX
8527 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-07-21 18:48 | 2010-07-21 20:55 | 9 | 127 | 55307-1 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WR#36091694 POLE 70-3107 10T FUSE BROKE//VER/CRB IDC XXXX
8528 | Hazard | 3302703 | HAZARD | HAZARD | 2009-06-02 17:08 | 2009-06-02 19:15 | 9 | 127 | 60683-1 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 077S08 HENDRIX CABLE BURNED INTO AT SPACER , HAD BEEN SPLICED AT THIS SAME SPOT BEFORE , REPAIRED AND RESTORED POWER TO 8 CUSTOMERS AT 1915 JEFF COMBS VER/KEP L3/KEP IDC XXXX
8529 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2011-05-12 20:44 | 2011-05-13 15:47 | 1 | 1143 | 4079301 | 1143 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | XFMR HAS NO COPPER RISER IN HOT SECONDARY BUSHINGS....ALUMN SERVICE DROP UNDER LUGS.....ONE HOT LEAD BURNT IN TWO...THE OTHER ALMOST....SEND TO CREW....CALLED JOEY REED...HE S EXPECTING TCKET...THANX....JRV RELEASED BY CREW 080S01 IDC XXXX
8530 | Hazard | 3303902 | LESLIE | WOOTON | 2022-01-27 06:19 | 2022-01-27 12:40 | 3 | 381 | 4407981 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr fuse, bad 25 kva 19.9 truckacess Released by crew 077S07xfmr fuse, bad 25 kva 7200 truck acess Released by crew 077S07 power restored at 12:40
8531 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-07-26 19:39 | 2016-07-27 02:00 | 3 | 381 | 4684671 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CUTOUT DOOR BURNT UP ON 990-446 WILL TRY TO REPLACE DOOR REPLACED CUTOUT DOOR RESTOREDPOWER AT 02:00
8532 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-05-26 17:09 | 2022-05-26 23:30 | 3 | 381 | 4954441 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 357-A-15. will need 2 men and big bucket. 50 kva transformer 7200
8533 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2008-02-06 16:24 | 2008-02-06 22:45 | 3 | 381 | 51717-1 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3010602//ORDER CONFIRMED TO PREVENT IT FROM ROLLING UP NEEDS CHECKED/// PRIMARY RISER BURNT OFF TRANSFORMER/ MADE REPAIRS//COD 3// VER/DBM IDC XXXX
8534 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-12-24 20:57 | 2009-12-25 16:00 | 1 | 1143 | 61291-1 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TO STRAIGHTEN POLE @REPLACE BROKEN CUTOUT RELEASED BY CREW 075H01NEED TO STRAIGHTEN POLE @REPLACE BROKEN CUTOUT COMPT POWER RESTORED
8535 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2015-06-20 14:33 | 2015-06-20 16:40 | 9 | 127 | 4618171 | 1143 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 92-620 30T LINE FUSE POLE 92-621 BAD LA POLE 92-936 INSTALLED 12T LINE FUSE SEND NOTE TO TREE PEOPLE LINES NEED CUT/ROW EMAILED/MD MADE/AED MADE/ADH// VER/ ADH
8536 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-10-05 08:29 | 2018-10-05 15:04 | 13 | 395 | 4200061 | 1142 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke line fuse cutout on hillside,need line crew and may want a r/w crew to cut path through brush Released by crew 077S04 opened recloser at 14:32 closedback at15:04 all power restored Released by crew 077H02 L3/HFP
8537 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-07-17 17:26 | 2014-07-17 20:09 | 7 | 163 | 4257611 | 1141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANS AT 1726//CREW CALLED SEC DOWN//SEC. BURNT DOWN 1099- 3104 3079-3080-3082 NEED 70 FT. 1/0 ROLL OF 4/2SEC. BURNT DOWN 1099- 3104 3079-3080-3082 NEED 70 FT. 1/0 ROLL OF 4/2 RELEASED BY CREW 078S08/LAST CUST RESTORED 2009/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14//NO OUTAGE TIL TRANS WAS OPENED VER/CRB
8538 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-10-25 20:02 | 2011-10-25 22:45 | 7 | 163 | 4020791 | 1141 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE SEC. WIRES APPEARS TO BE BURNED OPEN AT XFMR // CHECKING XFMR//BAD 50 KVA CSP//REPLACED XFMR//POWER IS RESTORED//COD 7// VER/DBM IDC XXXX
8539 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2020-05-20 11:22 | 2020-05-20 16:07 | 4 | 285 | 4867631 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | broke aep pole 118-4121. 30-6, xfmer open on 118-4122 @ 12:30, sec. down between 4122 & 4572. trks to pole. tree crew. line crew Released by crew 078S07 Closed xfmr on 118-4122 at 16:07 ticket complete.
8540 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-05-24 06:52 | 2020-05-24 08:27 | 12 | 95 | 4894781 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | riser burnt up out of top of cutout causing top of cutout to be burnt up. repairs made. pls close. tre
8541 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2018-10-07 10:30 | 2018-10-07 11:46 | 15 | 76 | 4205291 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required repair basket// B phase only COD 15 L3/HFP
8542 | Hazard | 3308001 | JACKSON | S.JACKSON | 2022-07-07 10:50 | 2022-07-07 15:35 | 4 | 285 | 4418581 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral broke, replaced service. Replaced meter.
8543 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2017-01-24 11:25 | 2017-01-24 16:10 | 4 | 285 | 4326391 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEED LINE CREW AND R/W CREW TO CUT PATH (MANUAL0 RELEASED BY CREW 077S01 37830487000036 VER/AWD L3/HFP XXXHFP
8544 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2008-11-16 13:50 | 2008-11-16 17:00 | 6 | 190 | 65702-1 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3411902// TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. 50 KVA ON POLE 97-254. I WILL CALL DUTY SUPER. WE CHANGED TRANSFORMER.LOST FUSE VER/KEP IDC XXXX
8545 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-07 19:10 | 2008-06-07 20:45 | 12 | 95 | 59938-1 | 1140 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | 3008702// 1/0 RISER BURNT OFF NEEDS 4/0 RISER INSTALLED VER/HFP IDC XXXX
8546 | Hazard | 3308002 | JACKSON | PANBOWL | 2014-11-12 08:36 | 2014-11-12 14:56 | 3 | 380 | 4721621 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CROSSARM BURNT OFF ON POLE 3084-336. NO OUTAGE YET. GETTING PLAN TOGETHER TO MAKE REPAIRS// WILL INSTALL 300AMP SB @ 1084-335 TO ISOLATE FAULT AND MAKE REPAIRS//MAP DISC ENTERED//TOM RELEASED BY CREW 077H18// VER/BOW
8547 | Whitesburg | 3401301 | FLEMING | NEON | 2022-12-31 10:30 | 2022-12-31 15:15 | 4 | 285 | 4381131 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva on pole 332-B-67. had this out last week as well. tried closing transformr today and the fuse blew. will need 50 kva 7.2 and line crew to change transformer Released by crew 077S11,,restored @ 15:15
8548 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2017-03-27 11:55 | 2017-03-27 12:55 | 19 | 60 | 4588081 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARMS38820967B00111 ARE SO ROTTEN UNSAFE TO DO HOT WILL HAVE TO OPEN LINE FUSE ON POLE 38820967A00389 WILL KEEP TRACK OF MY TIMES. /// PULLED OFF AT 11:55 BACK ON 1255 AT TIM MCCOY VER/CRB
8549 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-12-20 20:20 | 2012-12-21 05:50 | 2 | 570 | 4492301 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | GUY BROKEN, ANCHOR PULLED OUT AT POLE 37830247B00545, REPAIRED GUY AND ANCHOR AND RESAGED WIRE. POWER RESTORED. VER/PDP
8550 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2017-04-20 09:23 | 2017-04-20 14:08 | 4 | 285 | 4659681 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE820-101//POLE TOP BURNED OFF ON POLE 820-319///TRUCK ACCESSIBLE///CAN FRAME DOWN ON IT//CREW ENROUTE//REPAIRS MADE//RESTORED AT 14:08//COMPLETE//EM VER/CRB L3/HFP HFPC FP38820820D00319
8551 | Pikeville | 3401001 | ELWOOD | DORTON | 2022-10-17 04:48 | 2022-10-17 11:08 | 3 | 380 | 4034371 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout GuidelinesBad Dead end Bell at pole 239-67,Myles is on the way to Help make repairs.Bad Dead end Bell at pole 239-67,Myles is on the way to Help make repairs.Restored at 11:08..Replaced Line fuse cutout at 239-307 and Trans cutout at 239-67..
8552 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2019-05-21 10:18 | 2019-05-21 11:15 | 20 | 57 | 4310451 | 1140 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse melted out. all power restored @ 11:15. pls close. tre
8553 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2016-07-27 15:22 | 2016-07-28 00:21 | 4 | 539 | 4690971 | 1139 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER BAD ON 54-114 NTA CAN USE UTV TO ACCESS POLE NEED 15 KVA 7200 TRANS CUTOUT AND STANDOFF BRACKET RESTORED MAIN LINE AT 18:42 RELEASED BY CREW 079H03 VER/CRB
8554 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-05-01 10:12 | 2018-05-01 14:55 | 10 | 283 | 4293471 | 1136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 cu neutral and one of the #4 cu secondary wires down. Need flaggers, bucket and line crew to repair. Crew enroute. Released by crew 076S02. fuse open 1414.
8555 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-12-26 19:34 | 2010-12-27 14:30 | 1 | 1136 | 55910-1 | 1136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR# 38199575 // BAD UNDERGROUND SEND TO RAYBURN FOR TOMORROW RELEASED BY CREW 078S08 AT 2049- BOBBY REYNOLDS REPORTS HE WILL HAVE CREW WORK THIS IN THE AM. CUSTOMER APPROVED . VER/HFP L3/HFP IDC XXXX
8556 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-01-24 14:15 | 2017-01-24 15:26 | 16 | 71 | 4326131 | 1136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HIGH SIDE CUTOUT BROKEN. OPENED 1415-1525. 37830184A00270 VER/AWD L3/HFP XXXHFP
8557 | Hazard | 3303902 | LESLIE | WOOTON | 2011-10-19 16:19 | 2011-10-19 18:41 | 8 | 142 | 4999921 | 1136 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSES BLOWN, BAD EPOXILATOR D.E. INSULATOR ON 438-29, WILL TRY TO CHANGE INSULATORS.P.HICKS.ALL POWER RESTORED @ 18:41 HRS P.HICKS //COD 8// VER/DBM IDC XXXX
8558 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-02-15 11:40 | 2016-02-15 15:27 | 5 | 227 | 4697221 | 1135 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9 CUTOUT BROKEN,MAY BE ABLE TO REACH IT,WILL TRY.////////COULD REACH BUT CUTOUT WILL REQUIRE 2 MEN TO CONTROL IT,RICK RAY ENROUTE////NOTE NEW FETR//MADE MDC TO SHOW MIS-MAPPED CUST// VER/CRB L/3 CRB
8559 | Whitesburg | 3409503 | BURDINE | JENKINS | 2022-09-08 13:42 | 2022-09-09 08:36 | 1 | 1134 | 4856321 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | bad transformer that is fed from pole 358-B-89. this 3 phase padmount doesnt show on map. talkedto G. Combs getting everything in order to replace padmount and underground primary that feeds it. send copy of ticket to G. Combs and R. NOTHING ON MAPS
8560 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-10-10 12:28 | 2017-10-10 18:46 | 3 | 378 | 4442241 | 1134 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED ,TRUCKS TO POLE ,A PHASE,, BAD 100 KVA XFR ON XFR BANK 120/240 ON NAME PLATE,7200,,OPENED B&C PHASE RELEASED BY CREW 078S05/ON SITE RM OPENING 3 LINE FUSE ON POLE 206-103 TO SAFELY CHANG XFM OPEN @17;45 CLOSED IN @18;46 VOLATGE GOOD PLEASE CLOSE TIC RM VER/AWD L3/HFP HFPC MCCDL TOF1745
8561 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2010-04-23 10:24 | 2010-04-23 12:30 | 9 | 126 | 66609-1 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T LINE FUSE OUT DUE TO BAD CUTOUT ON POLE 1149-67. CHANGED CUTOUT FUSED UP EVERYTHING OK. COD-9 VER/HFP L3/HFP IDC XXXX
8562 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-07-20 10:35 | 2008-07-20 13:17 | 7 | 162 | 54320-1 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000901// BAD 50KVA TRANSFORMER-TRUCK OK NEED FLAGMAN-OPENED TRANSFORMER AT 10:35-VOLTAGE COMPLAINTS-VOLTAGE WAS 198 TO GROUND ON BOTH LEGS AN 386 PHASE TO PHASE-CALLING CREW-DAMAGE COMPLAINTS E MAIL TO P WYSONG-SEND TO LLOYD RELEASED BY CREW 078S07//BACK ON @ 13:17 RESAGGING 1 DROP // VER/TOM IDC XXXX
8563 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-12-10 15:00 | 2011-12-10 18:09 | 6 | 189 | 4167431 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B-PHASE LINE FUSE OPEN ON POLE 401D-20. PATROLLING LINE. FOUND BUSTED POLE TOP INSULATOR ON POLE 402B-161. WILL NEED ONE MAN TO HELP CHANGE OUT INSULATOR AND ARM. B PHASE AT 18:09, RESTORING ALL POWER. 12/10/2011 J.S.B. ///VER/CRB IDC LOOKS LIKE PH A NOT B XXXX
8564 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-08-28 09:36 | 2010-08-28 12:45 | 6 | 189 | 61448-1 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE RISER PULLED OUT OF HOTLINE CLAMP ON POLE 38831109000001//// REPLACED HOTLINE CLAMP, POWER RESTORED VER/KEP L3/KEP IDC XXXX
8565 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-07-14 21:26 | 2014-07-15 16:20 | 1 | 1134 | 4245771 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ENCLOSED CUTOUT NEEDS TO BE CHANGED. NEED LINE CREW AND R/W CREW RELEASED BY CREW 077S01//COD 1// VER/DBM
8566 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-06-08 10:03 | 2014-06-08 12:45 | 7 | 162 | 4994331 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRANSFORMER FUSE OPEN// ARRRESSTOR BLOWN CHANGED ARRESSTOR AND REFUSED CUTOUT POWER RESTORED // COMPLETE TT//COD 7// VER/DBM
8567 | Pikeville | 3407101 | TOPMOST | DEMA | 2016-09-18 20:30 | 2016-09-18 23:12 | 7 | 162 | 4905351 | 1134 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANS CUTOUT//OPENED L/F 37830186000033. OPENED LINE CUTOUT AT 20:30 . REPLACED CUTOUT AND ARRESTER POLE 37830186000072, ALL WORK COMPLETE /GXJ/// VER/DKM L3/HFP HFPC TOF1922
8568 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-02-12 00:04 | 2018-02-12 09:30 | 2 | 566 | 4832441 | 1132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | spoke with customer, this is for a business (repair garage), and they dont start work until 0900// they are ok if we look at it at 1st light //no crew required inactive transformer COD-2 IOS LF 38830292B00074
8569 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-02-21 06:42 | 2018-02-21 12:34 | 7 | 352 | 4866801 | 1132 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | line fuse out on pole 38830805000211 csp transformer on pole 38830805000025 goin to give line fuse a shot to see if it stays // bad 25kva csp transformer need cutout an arresstor // line fuse on pole 38830805000211 is closed 1028 3 cust lifted hot tap on pole 38830805000025 to isolate the transformer// RE-opened @ pole 38830805000211 @ 12:00 closed @ 12:34
8570 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2016-09-18 01:43 | 2016-09-18 08:00 | 3 | 377 | 4902171 | 1131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 076S02..BAD 25 KVA XFMR. RELEASED BY CREW 076S01RELEASED BY CREW 076S02..BAD 25 KVA XFMR. MAY NEED TO CHG BAD CROSS ARM.WILL LET RYAN ACCESS ON ARRIVAL..XFMR CHANGED BACK ON AT 8 AM. VER/KEP
8571 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-08-26 19:03 | 2014-08-27 01:20 | 3 | 377 | 4426491 | 1131 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 245D-41 . NEED 1 MAN , BUCKET TRUCK & FLAGERS . 50KVA XFMR 7200 . CLOSED XFMR @ 01:20
8572 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2021-06-28 16:40 | 2021-06-29 11:30 | 1 | 1130 | 4817031 | 1130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | no one living here, can change in the morning, oil all over xfmr , customer ok with holding til morning Released by crew 077S12// opening hotline clamp on pole 37830278A00044
8573 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2019-03-01 09:34 | 2019-03-01 13:20 | 5 | 226 | 4941541 | 1130 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | cust checked breakers, 496-86 top pole burnt off,,made all repairs,,and customer restored @ 13:20 complete L3/HFP
8574 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-08-15 19:28 | 2016-08-16 14:18 | 1 | 1130 | 4788161 | 1130 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BAD ON TRANSF === REPAIRED ==== POWER OK VER/HFP L3/HFP
8575 | Hazard | 3309003 | JEFF | VIPER | 2020-05-11 10:30 | 2020-05-11 13:38 | 6 | 188 | 4823591 | 1128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Service neutral pulled out of a splice.
8576 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-09-08 13:16 | 2014-09-08 14:50 | 12 | 94 | 4480091 | 1128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | FOUND INSULATOR THAT HAD BEEN FLASHING OVER ON POLE 110-62, REPLACED IT, RE-FUSED LINE AND IT STAYED VER/CRB
8577 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-08-12 15:40 | 2017-08-12 21:56 | 3 | 376 | 4253961 | 1128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LINEF 984-20 IS OUT,WILL PTRL///////NOTHING EVIDENT,WILL RE-FUSE/////RE-FUSED,FUSE BLEW.NEED CREW W 4WHEELER TO PTRL HD OF HOLLOW////POLE BROKE 961-65,CUT DEADEND@961-58,8T OPEN CUTOUT THERE.RE-ENERGIZED TO 961-58@21:56/////PLACED GRND @ 961-58//NOTE PLACED ON MAP FOR TAGS,GROUNDS AND NEW FUSE//MD FILED//COD 3// VER/DBM
8578 | Pikeville | 3421001 | BREAKS | CITY | 2012-12-19 16:21 | 2012-12-19 17:55 | 12 | 94 | 4483691 | 1128 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOT TAP LEAD HAS BURNT OFF ON C/PHASE ON POLE 244-15 NEED TO OPEN 3 SOLID BLADES ON POLE 244-15 TO MAKE REPAIRS . REPLACED BAD CUT - OUT AND HOT TAP LEAD ON POLE 244-15 OPENED 3 SOLID BLADES UP @17:25 ON POLE 244-15 AND CLOSED BACK IN @ 17:55 RESTORED SERVICE//COD 12 (+ 1, SEE H4483691)// VER/DBM
8579 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2021-12-21 02:34 | 2021-12-21 05:15 | 7 | 161 | 4215491 | 1127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Power Restored
8580 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2020-10-11 13:39 | 2020-10-11 16:20 | 7 | 161 | 4545341 | 1127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN DOWN,POLE BURNING//////////REPLACED CUTOUT&EXTINGUISHED FIRE(I THINK).RESTORED ALL POWER AFTERWARDS.SEND THIS TO A TECH.MIGHT WANT TO REPLACE THE POLE,ITS BURNED HALFWAY INTO AT CUTOUT LOCATION ON POLE
8581 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-06-22 07:04 | 2013-06-22 09:45 | 7 | 161 | 4384921 | 1127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE1148-186 BAD CUTOUT 8T TRANS FUSE VER/TOM L3/TOM
8582 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2009-01-18 12:09 | 2009-01-18 14:50 | 7 | 161 | 58049-1 | 1127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-7 WR # 28107494 // @ 1316 CALLING FOR CREW TO REPLACE TRANSFORMER L3/HFP
8583 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2014-04-29 17:05 | 2014-04-30 11:52 | 1 | 1127 | 4648771 | 1127 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L INE FUSE BLOWN ON POLE#1052-71 . TRIED LINE FUSE ON POLE 1052-71 CAME BACK OUT WILL TRY TO PATROL LINE. PRIMARY DOWN ON POLE #1051-28 NEED 1 MAN. TOP OF POLE#1051-29 IS BURNT OFF TALKED TO TIM HALL SAID WE WOULD WORK IN THE A.M. CAN LOWER NO TRUCK NEED 4 MEN RELEASED BY CREW 074H17//CUST OKD THIS.SERVICE RESTORED AT 11:52..D LEWIS//COD 1// VER/DBM
8584 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2022-01-24 22:20 | 2022-01-25 04:35 | 3 | 375 | 4401991 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830197000060 20t lat bad c/o--ds012522 Released by crew 078S01//arrived RM replaced 2 cutouts XFM open @ 04:13 closed @04:31 LF in @04:35 please close tic RM
8585 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-12-28 11:25 | 2009-12-28 17:40 | 3 | 375 | 60764-1 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED,BAD 19.9 15 KVA XFR,SHOULD GO BACK W A 25 KVA.NO VEHICLE ACCESS.PROBABLY WILL NEED TO SET UP IN ROAD UNLESS WE USE ROPE BLOCKS RELEASED BY CREW 074S06
8586 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-12-01 07:20 | 2022-12-01 11:05 | 5 | 225 | 4215991 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew reqd/bad 19.9 xfmer 25kva/truck ok Released by crew 078S04//arrived RM xfm replaced power on @ 11:05 please close tic RM
8587 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-05-14 17:14 | 2018-05-14 20:34 | 27 | 200 | 4348791 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | got hlc and struripp burned off on pole 172-164 (12 CUST) going to made it solid and will to open fuse to repair call 438-9708 and dale vires let u in to pole opened fuse @ 2005 closed @ 2034 (15 cust)
8588 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-08-28 10:15 | 2008-08-28 16:30 | 3 | 375 | 56853-1 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701// RELEASED BY CREW 078S07//SERVICERS TRUCK IS STUCK, CALLING GARAGE// BAD 19.9 CUTOUT DOOR 30T LINE FUSE//COD 3//ISO 38830164A00088// VER/DBM IDC XXXX
8589 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2013-05-14 11:55 | 2013-05-14 18:10 | 3 | 375 | 4112691 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BOBBY REYNOLDS REPLACING PADMOUNT//COD 3 ///VER/CRB L/3 CRB IDC XXXX
8590 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2021-09-01 17:03 | 2021-09-01 23:18 | 3 | 375 | 4198421 | 1125 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25 behind house yard dog side by side no trucks Released by crew 078S03 crew on site FETR 22:30 LRM all pwr restored 23:18
8591 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-07-15 00:48 | 2020-07-15 10:10 | 2 | 562 | 4165681 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout GuidelinesDispatched in accordance with KYPCo Late Night Callout Guidelines/xfmr fuse blown//found nothing//closed in and cutout broke//replaced cutout/restored at 10:10//complete//em
8592 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-04-03 16:11 | 2012-04-04 10:55 | 1 | 1124 | 4644091 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 SINGLE--CREW WITH BIG BUCKET RELEASED BY CREW 077S10 COM CHANGED XFMR RESTORED POWER AT1055 CREW 077H01//COD 1// VER/DBM IDC NEEDED YARD DOG XXXX
8593 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-07-14 16:56 | 2017-07-14 18:14 | 24 | 78 | 4122911 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTNING ARRESTOR ON 38830117A00280.POLE 117-280 BAD LA TRANS FUSE OUT POLE 117-282 40T LINE FUSE BACK IN 17:40POLE 117-280 BAD LA TRANS FUSE OUT POLE 117-282 40T LINE FUSE BACK IN 17:40 RELEASED BY CREW 078S08--CREW ON SITE--REPLACED L/A--PWR CK 123-123-246--TBL TKT COMP--RMV RELEASED BY CREW 078H16 38830117A00282 VER/AWD MLR
8594 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-04-06 08:09 | 2009-04-06 12:50 | 4 | 281 | 66239-1 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 42C455. 65T LINE FUSE OUT ON POLE 42C66. REPLACED CUTOUT EVERYTHING OK. VER/KEP L3/KEP IDC XXXX
8595 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-11-12 13:21 | 2022-11-12 18:02 | 4 | 281 | 4135881 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 50 kva manuel, need replaced 19.9 Released by crew 077S07..alll power restored @ 18:52 p.hicks
8596 | South Williamson | 3411401 | DEWEY | INEZ | 2020-03-03 14:54 | 2020-03-03 19:35 | 4 | 281 | 4448311 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 768-24//cutout broke behind home on 768-213///only feeds light//i isolated with long stick//customer ok with us coming back in coupl days in daylight to climb pole and replace cutout//restored at 19:35//complete//em
8597 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2009-12-24 17:32 | 2009-12-25 12:16 | 1 | 1124 | 60129-1 | 1124 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSFORMER.... NEEDS NEW 25 KVA TANSFORMER, 7200V MWL// REPLACED XFMR AND RESTORED COMPLETE AT 12:15 122509 SC RELEASED BY CREW 077S04
8598 | Whitesburg | 3409503 | BURDINE | JENKINS | 2022-03-14 07:44 | 2022-03-14 12:25 | 4 | 281 | 4621951 | 1124 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | connection burnt out. replaced connections, power restored. pole number should be 358-435. take off pole that feeds this tap is 358-485.. mdr complete
8599 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-03-10 13:21 | 2020-03-10 15:03 | 11 | 102 | 4465741 | 1122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | bad recloser on pole 400-331, took stepdown fuse out on 400-330, isolated recloser closed by pass in , closed stepdown fuse in at 15:03 restoring power. control handle open & tagged ,source & load risers removed & placed tag for DDC..
8600 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2020-10-29 00:13 | 2020-10-29 10:45 | 36 | 632 | 4593571 | 1122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Guidelines got a 19.9 cutout bad need crew to change Released by crew 077S05 line fuse opened @ 1022 closed @ 1036 xfer closed @ 1045
8601 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2013-10-07 11:53 | 2013-10-07 15:00 | 6 | 187 | 4918321 | 1122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED POLE BURNT OFF POLE 273-177 TRUCKS OK CAN LOWER RELEASED BY CREW 078S03,,,CREW ON SITE, LOWERED FACILITIES, ALL POWER RESTORED VER/CRB L/3 CRB IDC XXXX
8602 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-01-17 09:08 | 2009-01-17 10:50 | 11 | 102 | 57210-1 | 1122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28105484 // COD-11 3411802// RELEASED BY CREW 074S01 L3/HFP
8603 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-08-30 12:26 | 2022-08-30 13:17 | 22 | 51 | 4815491 | 1122 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | The line fuse on pole 466-37 is open with a broken cutout on pole 466-113. I isolated this cutout and closed the line fuse on 466-37 at 13:17. The XFMR on 466-113 was closed at 14:43. LR- 1st All Out call came in at 12:26 and don't show any devices opened before that point
8604 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-04-14 13:32 | 2014-04-14 13:51 | 59 | 19 | 4603051 | 1121 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 140-473 HOT TAP BURNT OFF REPAIRED VER/CRB IDC XXXX
8605 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2009-06-26 16:10 | 2009-06-26 18:50 | 7 | 160 | 63358-1 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE DOOR BURN UP. REPLACED DOOR AND FUSE//COD 7// VER/DBM IDCC FEC49 XXXX
8606 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2015-12-02 13:25 | 2015-12-02 14:35 | 16 | 70 | H4503671 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 21-85 PHASE DOWN TRUCKS TO POLES OPEN LOOP ON HENDRICKS CABLE CREW ENROUTE/OPENED BREAKER TO GIVE HOLD ORDER FOR CREW TO MAKE REPAIRS/ VER/KEP
8607 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2022-05-25 14:24 | 2022-05-25 18:08 | 5 | 224 | 4948011 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 25KVA xfrm manual on hillside. Need 4 man linecrew and manual row crew. Released by crew 077H15.. restored @ 18:08
8608 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-06-29 08:50 | 2008-06-29 18:10 | 2 | 560 | 59162-1 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15 KVA XFORMER NO TRUCKS RELEASED BY CREW 078S11 REPAIRS MADE BACK ON AT 18:10 COMPLETTED AJBC LOC #38830230000242 CNT7, PER TROUBLE MAN ONLY AN XFR WAS OUT. CUST MAY BE MIS MAPPED. VER/KEP
8609 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-03-31 17:02 | 2015-03-31 21:42 | 4 | 280 | 4251081 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON 1035-154,WILL REPLACE//////////REPLACED CUTOUT AND RESTORED,ALL OK AFTERWARDS COD-4 ISO TF 38821035000154 VER/HFP L3/HFP
8610 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2018-09-03 17:24 | 2018-09-03 20:04 | 7 | 160 | 4038941 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse blown on pole 37820058B00102. Cleared up bad transformer cutout on pole 37820058B00514. Power restored at 20:04. L3/HFP
8611 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2009-07-26 11:30 | 2009-07-26 12:50 | 14 | 80 | H58675-1 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOOP IS BURNED INTO ON POLE 189-102. WE ARE GOING TO HAVE TO OPEN LINE FUSE ON POLE 189-51 LONG ENOUGH TO MAKE UP LOOP. WE HAVE TO WAIT UNTIL STORM MOVES ON. RELEASED BY CREW 074S01//COMPLETED @ 1250 PER TIM HALL// IDC XXXX
8612 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2011-09-06 21:00 | 2011-09-06 21:40 | 28 | 40 | 4839841 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | I OPENED LINE FUSE ON POLE 67-C-38 25T FUSE AT 21:00 AND CLOSED FUSE IN AT 21:40. CONDUCTOR LAYING ON ARM BURNING. LOOKS LIKE TIE WIRE WAS BROKEN. PROBLEY DUE TO TROUBLE THIS MORNING THIS WAS JUST ABOVE THE SLIDE AND TREE THAT TORE WIRE DOWN. //VER/CRB IDC XXXX
8613 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-11-16 08:36 | 2011-11-16 12:20 | 5 | 224 | 4080981 | 1120 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | BAD CONNECTION IN PEDESTAL // COD-5 ISO TF 37830205A00273 VER/HFP L3/HFP IDCC FP224 XXXX
8614 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-06-26 05:22 | 2014-06-26 11:35 | 3 | 373 | 4157401 | 1119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK AT START OF SHIFT 6-26-14 BAD 50 KVA XFMR. CREW ENROUTE TO REPLACE. CREW ONSITE. RELEASED BY CREW 076S02 // REPLACING NOW. RDM // REPAIRS COMPLETE VER/CRB
8615 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-05-26 21:27 | 2019-05-27 16:06 | 1 | 1119 | 4343881 | 1119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout Released by crew 077E10//RESTORED 1606
8616 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-10-14 07:32 | 2010-10-14 13:45 | 3 | 373 | 59502-1 | 1119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37322513 //OPENED FUSE AT 0732 /// COD-3POLE TOP BURNT OFF ON POLE 234-104 , 40/5 NEED TO REPLACE IT WITH 45/5.TRUCKS TO POLE. OPENED A PHASE LINE FUSE ON POLE 234-143 AT 07:30.POLE TOP BURNT OFF ON POLE /234-104 , 40/5 NEED TO REPLACE IT WITH 45// POWER RESTORED @ 13:45 J. HEMLEPP & CREW RELEASED BY CREW 078H05 VER/HFP L3/HFP IDC DCMT XXXX
8617 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2011-06-30 15:27 | 2011-06-30 21:40 | 3 | 373 | 4442951 | 1119 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE AND LINE IS ON HILL. HAVE TO PATROL ON FOOT. POLE 473-39 IS SPLIT OUT AND PRIMARY IS SAGGING VERY LOW. NEED TO DE-ENERGIZE TAP ON POLE 473-37 TO MAKE SAFE. OPENED CUT-OUT ON 473-37 AT 16:41. POWER RESTORED AT 21:40. J.S.B. RELEASED BY CREW 075H01 VER/KEP IDC XXXX
8618 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-10-20 22:52 | 2018-10-21 17:30 | 1 | 1118 | 4284061 | 1118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | repaired hot tap @ 45-5040, bank off @ 17:15 on @ 17:30 Customer lost power from failed hot clamp// opened Xfer to make repairs L3/HFP
8619 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-07-30 20:46 | 2011-07-30 21:12 | 43 | 26 | 4644841 | 1118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830247D00919 BURNT OFF AT CUTOUT ,OPENED LINE FUSE ON POLE 37830247D00449 AT 20:45 DUTY SUPERVISOR CONTACTED. ----- POWER RESTORED TO ALL CUSTOMERS AT 12;55 IDCC TOF1946 XXXX
8620 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-08-22 18:55 | 2015-08-23 13:33 | 1 | 1118 | 4164191 | 1118 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 7200 CUTOUT WILL WORK IN THE DAYLIGHT RELEASED BY CREW 077S01ARRIVED AT JOB SIGHT WAITING ON RIGHT OF WAY CREW OPENED SWITCH ON POLE 130 /135 AT 1200 REPAIRS MADE AND CLOSED BACK RESTORING POWER AT 1333 RELEASED BY CREW 077H03// VER/ ADH
8621 | Pikeville | 3421001 | BREAKS | CITY | 2022-08-10 23:12 | 2022-08-11 17:50 | 1 | 1118 | 4723511 | 1118 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Hot leg has burnt open between secondary and service. This is no truck access and crew is onsite making repairs/// Entire service was bad had to replace complete drop. OFF@17:15 ON@17:50
8622 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-01-07 03:48 | 2014-01-07 04:50 | 18 | 62 | H4244251 | 1116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ENERGIZED PRIMARY LAYING ON GROUND// OPENING RECLOSER TO ISOLATE//OPENED AT 03:48// INSTALLED PRIMARY DEADEND AT 881-79// 2 SPANS OF 6A COPPER DOWN // NEED LINE CREW AND BUCKET TREE CREW, 6A WIRE AND 1 PRIMARY DEADEND ASSEMBLY // CLOSED RECLOSER ON 882-564 AT 04:50 ENERGIZING UP TO 881-79 RELEASED BY CREW 076H02//???? IDCC DUP TO OPEN RECLOSER XXXX
8623 | Whitesburg | 3314401 | MAYKING | ERMINE | 2015-07-08 20:04 | 2015-07-09 14:40 | 1 | 1116 | 4747981 | 1116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK IN DAYLIGHT/ BAD 25 KVA 7200 XFMR ON POLE 497-121, WILL HOLD TILL TOMORROW DUE TO LOCATION. RELEASED BY CREW 077S11 VER/CRB
8624 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2008-02-23 17:04 | 2008-02-23 17:40 | 31 | 36 | 66574-1 | 1116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3410502- POLE FIRE AT POLE 47-461// SEVR OPENED FUSE AT POLE 47-31 POLE# 47-461 IS BURNED OFF AT TOP. I OPENED LINE FUSE AT 17:15 AND CLOSED IT BACK IN AT 17:40. I MADE TEMP. REPAIRS TO POLE. I WILL GIVE NOTE TO DENNIS TO HAVE CREW COME MONDAY MORNING AND REPAIR POLE.//VER/CRB IDC LOOKS LIKE OUTAGE A LITTLE EARLIER PER CUSTOMER TICKETS, CHANGED START TIME XXXX
8625 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-02-22 13:52 | 2022-02-22 20:04 | 3 | 372 | 4529321 | 1116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | line fuse blown on pole 375-B-164.line is together @ pole 375-B-165 to pole 375-B-186.. conductor is bad out of sag. line will need to be resagged to get clearance between primary and neutral. line crew required Released by crew 077S11restored @ 20:04
8626 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-07-06 07:33 | 2012-07-06 16:51 | 2 | 558 | 4530221 | 1116 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO SEND TO DWAYNE TO REDO THE METER TO SINGLE PHASE AND NOT 3 PHASE
8627 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2013-04-02 09:01 | 2013-04-02 12:44 | 5 | 223 | 4973761 | 1115 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD CUT OUT AND LA/DIFFICULT LOCATION/FETR1315/VEM ///VER/CRB L/3 CRB //WAS OFF DURING THE RECLOSER OUTAGE AND A LITTLE AFTER IDC XXXX
8628 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-12-23 23:47 | 2009-12-24 00:40 | 21 | 53 | 50056-1 | 1113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T TRANS FUSE MELTED OUT ON 50KVA INSTALLED 10T
8629 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-08-04 21:56 | 2012-08-05 00:35 | 7 | 159 | 4897641 | 1113 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1147-5002 BAD 15KVA NEED 25 OR 37.5 SEND TO JIM. RELEASED BY CREW 078S08 (ALL POWER RESTORED AT 00:35) VER/KEP IDC XXXX
8630 | Whitesburg | 3409503 | BURDINE | JENKINS | 2021-03-05 06:52 | 2021-03-05 11:30 | 4 | 278 | 4305161 | 1112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I changed cutout and arrestor
8631 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2020-01-09 15:21 | 2020-01-09 17:40 | 8 | 139 | 4228751 | 1112 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | open can on 45-2098 @ 17:15, restored 17:40, replaced 8 burnt up connections//ALL CUSTOMERS HAD PART POWER FROM BEGINNING OF OUTAGE //
8632 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-11-03 20:12 | 2016-11-03 22:31 | 8 | 139 | 4073821 | 1112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTER ON POLE 37830344000084 WENT BAD CUT IN THE CLEAR WILL REPLACE LATER REFUSED POWER OK/ ISO 37830344000017/ COD 8/ VER/BOW
8633 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2019-12-14 17:43 | 2019-12-14 21:15 | 6 | 212 | 4154721 | 1112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | arrived found 1097-345 top to be burned off, open l/f on 1097-80 about 1815, crew req, no grds or tg placed may be able to lower equip down, is a 454 pole deadend pri pole transformer installation, may not be able to get truck to pole // cod 1 (+5) L3/HFP
8634 | South Williamson | 3411401 | DEWEY | INEZ | 2021-09-22 14:37 | 2021-09-22 19:15 | 4 | 278 | 4276251 | 1112 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr cutout broke//big bucket enroute//repairs made//restored at 1915//complete//em
8635 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-07-19 16:14 | 2008-07-19 17:55 | 11 | 101 | 54189-1 | 1111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000901//LOW VOLTAGE RUNNING SEC FROM OTHER POLE // VER/TOM IDC XXXX
8636 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-07-28 14:59 | 2017-07-28 16:40 | 11 | 101 | 4195651 | 1111 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE RECLOSURE OPEN @ 833-438 COD 11 ,CUTOUTS BROKE @833-211 GOING TO ISULATE CUTOUTS. GOING TO OPEN OTHER RECLOSURES TO MAKE SAFE REPAIRES.@ 1620 CLOSED @ CLOSED 1640 . OPENED RECOLSURES @ 14:20 CLOSED @ 14:40 38830833C00438 VER/AWD SJGC CNT86, CREATED H4195651
8637 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-10-05 12:06 | 2009-10-05 13:47 | 11 | 101 | 52349-1 | 1111 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3008003// BAD CONN. ON POLE REPAIRED VER/JHM IDCC MCCNI XXXX
8638 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2008-06-03 11:36 | 2008-06-03 12:50 | 15 | 74 | 54894-1 | 1110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3117601// PATROLING LINE/BAD ARRESTOR NEEDS REPLACED-E-MAIL TO RAYBURN-NO TRUCK VER/HFP
8639 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-09-10 17:15 | 2016-09-11 02:30 | 2 | 555 | 4883181 | 1110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LINE FUSE OPEN @351-82.////1 SPAN.#4 COPPER PRIMARY DOWN 351-82 TO 351-83///351-84 SPAN GUY POLE BROKE.NEED CUTOUT LIGHTING ARRESTOR AND ROLL OF GUY WIRE//COD 2// RELEASED BY CREW 078H19// VER/DBM
8640 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2021-07-28 15:18 | 2021-07-28 15:33 | 74 | 15 | 4972481 | 1110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | Recloser went out related to order 4972411 B phase out (74 COD)
8641 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-06-17 00:32 | 2012-06-17 00:47 | 74 | 15 | 4922091 | 1110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | HAD TO OPEN RECLOSER TO SAFELY CLOSE GOAB - WILL THEN CLOSE RECLOSER BACK - OUTAGE APPROX 45 MINUTES FROM BEGINNING TO END// MADE AED AND PLACED NOTE ON POWERON MAP // OPENED AT 0032 CLOSED AT 0047 IDCC TOF22, TON50 XXXX
8642 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-01-20 11:30 | 2019-01-20 16:00 | 5 | 270 | 4694541 | 1110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kv 19.9 xfm..will need flagging crew and big bucket to make repairs..restored/ bad xfmr on pole 37820146000019 also blew line fuse on that same pole/ restored line fuse 37820146000019 at 1500 (4cc)/ restored xfmr 37820146000019 at 1600 (1cc) L3/HFP
8643 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-01-24 06:10 | 2014-01-24 09:52 | 5 | 222 | 4306881 | 1110 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | STEP DOWN FAILED ON POLE 37830029000196 TRANSFORMER FUSE PULL INTO/// THIS IS ALSO OUT DUE TO THE STEPDOWN TR FAILING ON ORDER 4306051 AND WILL NEED THE TIME ON FOR THAT ORDER VER/HFP L3/HFP IDC XXXX
8644 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-05-19 17:40 | 2009-05-19 22:17 | 4 | 277 | 50322-1 | 1108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830295B00069 CUTOUT BROKEN, LINE C/OLINE CUTOUT BROKEN POLE 295-69 , REPLACE BAD C/O POWER RESTORED//ISO//COD 4// VER/DBM IDC XXXX
8645 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-11-12 06:07 | 2019-11-12 11:18 | 11 | 311 | 4022731 | 1108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 Kva transformer bad on 925-3. Crew enroute to replace. Released by crew 076S02 line fuse 1024-1118
8646 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-09-03 09:43 | 2008-09-03 14:20 | 4 | 277 | 58841-1 | 1108 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3202201// UNDERGROUND BAD. CALLED JOEY REED 10:51 RELEASED BY CREW 079S01.SEND COPY TO RON RYE TO REPLACE UNDERGROUND.//COD 4// VER/DBM IDC XXXX
8647 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-04-08 13:36 | 2015-04-08 19:45 | 3 | 369 | 4288861 | 1107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-325 BAD CUTOUT 100T LINE FUSE RELEASED BY CREW 078S08POLE 68-325 BAD CUTOUT 100T LINE FUSE CHGED 3-CUTOUT 3-100T FUSES VER/TOM L3/TOM
8648 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-03-12 17:10 | 2019-03-12 23:19 | 3 | 369 | 4975361 | 1107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dave Lewis ... bad trans on 53-205.trk app 25 KVA 7200.bad trans on 53-205.trk app 25 KVA 7200.replaced tranns.restored power at 23:19
8649 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2020-05-03 18:47 | 2020-05-03 20:50 | 9 | 123 | 4791411 | 1107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required took 199-32 off line no meter on it
8650 | South Williamson | 3411401 | DEWEY | INEZ | 2009-09-04 12:24 | 2009-09-04 14:27 | 9 | 123 | 65202-1 | 1107 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JRV ON SITE @ 13:35...CHECKED CSTS VOLTAGE.....REPLACED BAD CUTOUT....CLOSED BACK WITH SOLID DOOR....JRV...09/04/09 VER/TOM L3/TOM IDC XXXX
8651 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-02-20 19:20 | 2015-02-21 13:45 | 1 | 1105 | 4059071 | 1105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WAITING ON PICKUP TRUCK TO COME AND TAKE ME TO TROUBLE SITE. ROADS ARE VERY SLICK. NEUTRAL IN #2 SERVICE BURNED INTO AT SPLICE OUT IN MID SPAN. I REPLACED SERVICE DROP. SEND TO PEGGY. CUSTOMER HAS DAMAGES. ONE TV AT LEAST HE SAID WAS BURNED UP. ALSO HE SPELLED SOMETHING LIKE WIRES BURNING WHEN HE TURNED HIS BREAKERS ON. I ADVISED HIM TO TURN EVERTHING OFF AND CALL AN ELECTRICIAN. HE WILL BE CALLING IN A DAMAGE COMPLAINT.//EMAILED TO P WYSONG// VER/DBM
8652 | Pikeville | 3403001 | PIKEVILLE | CITY | 2022-05-06 14:05 | 2022-05-06 15:30 | 13 | 85 | 4846251 | 1105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 37830024B21503 / repaired and restored line fuse @ 1530
8653 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-02-06 12:19 | 2010-02-06 16:00 | 5 | 221 | 50105-1 | 1105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS FAILED CREW CALLEDPOLE 92- 552 BAD 37.5 NEED 50KVA AND CUTOUT AND T BRACKETPOLE 92- 552 BAD 37.5 NEED 50KVA AND CUTOUT AND T BRACKET RELEASED BY CREW 078S08 RELEASED BY CREW 078H01 IDC XXXX
8654 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2011-07-23 18:15 | 2011-07-23 19:40 | 13 | 85 | 4602691 | 1105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE MELTED OUT. RE-FUSED @ RELEASED BY CREW 076S02 VER/ARN
8655 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2019-10-07 16:45 | 2019-10-07 18:10 | 13 | 85 | 4113261 | 1105 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced line fuse cutout,,,225-62 all customers restored complete
8656 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-01-18 20:09 | 2010-01-19 00:45 | 4 | 276 | 56247-1 | 1104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33487107 BAD 15KVA NEED 25 KVA AND CUTOUT 3-CUST OUT TRUCK TO POLE NEED FLAGMAN TIED RED RIBBON ON POLE RELEASED BY CREW 078S08CREW ON SITE VER/LDA IDC XXXX
8657 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-05-22 08:52 | 2018-05-22 15:00 | 3 | 368 | 4391911 | 1104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830165A00035 --19,9 c/o broke--crew req-- bytrk--ds052218 Released by crew 078S01
8658 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2011-12-30 14:44 | 2011-12-30 16:16 | 12 | 92 | 4216281 | 1104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | PHASE A LINE FUSE BLOWN ON 809-687. PATROLLED LINE AND FOUND NO PROBLEMS. FUSE LINK BROKE. RE-FUSED @ 16:16. SH ////VER/CRB IDCC CNT2 XXXX
8659 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-06-25 00:45 | 2010-06-25 01:33 | 23 | 48 | H57180-1 | 1104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASING.....TRUCK BROKE DOWN RELEASED BY CREW 079H08 CUTOUT IS BAD, WILL HAVE TO OPEN LINE TO CHANGE. OPENED FUSE ON POLE 9-C-190./VER/CRB IDCC DUP TO OPEN LINE FUSE XXXX
8660 | South Williamson | 3411401 | DEWEY | INEZ | 2018-08-19 11:14 | 2018-08-19 15:50 | 4 | 276 | 4973161 | 1104 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva xfmr on 673-18. Replaced xfmr & Restored @ 15:50. sh L3/HFP
8661 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2015-12-25 14:44 | 2015-12-25 23:55 | 2 | 551 | 4559701 | 1102 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD CONNECTION AT TRANSFORMER, POWER RESTORED.
8662 | Pikeville | 3410602 | E.PRESTON | LANCER | 2010-04-23 17:43 | 2010-04-23 18:12 | 38 | 29 | 50043-1 | 1102 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSERS @ 174?XFMR CUTOUT BROKE AND SET POLE AND CROSSARM ON FIRE. OPENED ALL THREE RECLOSERS ON 979-255 @ 17:43, PUT OUT FIRE, CHANGED CUTOUT, MADE TEMPORARY REPAIRS TO CROSSARM AND CLOSED RECLOSERS @ 18:12 RESTORING ALL CUSTOMERS. I WILL SEND A JOB TO ENGINEERING TO CHANGE ARM - IS OK FOR NOW. SH VER/HFP L3/HFP IDC XXXX
8663 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-06-18 08:03 | 2008-06-18 14:10 | 3 | 367 | 50212-1 | 1101 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA TRUCKS IFFY/SEND TO JOE HEMLEPP RELEASED BY CREW 078S03//3103101/CREW HAS LOADED MATERIAL . IN ROUTE/ CREW ON SITE/ DIFFICULT POLE LOCATION//VER/CRB IDCC CNT1 XXXX
8664 | South Williamson | 2153502 | MIDDLE BURNING CRK | NAUGATUCK | 2009-06-06 05:15 | 2009-06-06 08:55 | 5 | 220 | 50203-1 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO ORIGINAL OUTAGE....OPENED REC ON P820C3-309 @ 0515 TAKING 96 CUST OUT TO ISOLATE POLE FIRE.//CALLED FOR 2 MEN AND BIG BUCKET TO HELP REPLACE BAD C/O---TICKET 50382 FOR TRANSF OUTAGE IN WV WITH 5 CUSTS. VER/DKG ONLY 5 KY CUST AFFECTED WHEN OPENED REC ON POLE 309 ALSO CORRECTED TIME OFF IDC XXXX
8665 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2010-12-15 08:15 | 2010-12-15 10:05 | 10 | 110 | 50481-1 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | APPEARS CONNECTION FAILED AND DAMAGED 1/0 SECONDARY @ XFMR POLE. WORKING TO REPLACE DAMAGED WIRE. RE-WORKED XFMR LEADS TO SPLIT LOAD BETWEEN CONNECTIONS AND RE-FUSED XFMR @ 10:05. SH COD-10 ISO TF 38830785D20259 VER/HFP L3/HFP IDC XXXX
8666 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-01-07 16:00 | 2010-01-08 10:20 | 1 | 1100 | 65707-1 | 1100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK TOMORROW 01/08/10 REPLACED CONNECTION ON POLE VER/KEP L3/KEP IDCC MCCDL XXXX
8667 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2021-03-08 20:18 | 2021-03-08 23:58 | 5 | 220 | 4317211 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 25KVA tansformer on pole 225-A-254, truck access. Shouldnt need any flaggers here, theres a wide spot next to highway 476 that this can be worked from. This is the XFMR just before the Willow Fern Church about 1/2 mile above the Bulan Substation. I closed the XFMR fuse in at 21:55 but it did not restore power, the fuse did not blow but I opened it back up. Released by crew 077S04..all power restored @ 23:58 hrs ..p.hicks/ ISO 37830225A00254/ COD 5
8668 | Pikeville | 3421002 | BREAKS | GRASSY | 2011-04-12 18:25 | 2011-04-12 18:50 | 44 | 25 | H1150600-1 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | STS WR # 39541783 // RECLOSER ON POLE 197-98 IS OPENED. WITH BACK TO STATION THE LEFT HAND RECLOSER IS OUT. THE OTHER 2 IS IN. INSULATOR ON POLE 197-17 LOOKS LIKE IT HAS BROKEN DOWN AND POLE AND CROSSARM IS SMOKING AT TIMES. DENNIS IS BRINGING HELP TO CHANGE INSULATORS. WE WILL HAVE TO OPEN RECLOSERS AT POLE 197-98 WHEN CREW ARRIVES FOR ABOUT 45 MINUTES. I OPENED THE OTHER 2 RECLOSERS AT 18:25 SO WORK COULD BE DONE. WE FIXED PROBLEM AND CLOSED ALL 3 RECLOSERS IN AT 1850 FROM 55937-1 VER/HFP L3/HFP
8669 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-31 15:12 | 2009-02-01 09:32 | 1 | 1100 | 53549-1 | 1100 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WORK WITH OUTAGE 51899 OFF SAME POLE RELEASED BY CREW 077S04WORK WITH OUTAGE 51899 OFF SAME POLE //4/3 SERVICE DROP BURNED INTO DUE TO OVERLOAD ON ADJACENT SERVICE DROP
8670 | Hazard | 3302703 | HAZARD | HAZARD | 2021-10-06 15:50 | 2021-10-06 19:30 | 5 | 220 | 4324331 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | wire off insulator at pole 272-d2-740. help on the way. restored 19:30
8671 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2016-04-15 11:00 | 2016-04-15 12:40 | 11 | 100 | 4093561 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP @ 11:00, STAND OFF BKT. 12 KV C/O & ARRESTOR RELEASED BY CREW 078S07/ON SITE RM REPAIRS MADE BACK ON @12:40 PLEASE CLOSE TIC RM/ ISO 39831099B33044/ COD 11/ VER/BOW
8672 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-10 22:02 | 2016-01-10 22:22 | 55 | 20 | H4598731C | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38831027D00064/ CUTOUT FAILED AND BURNT POLE OFF. AJB OUTAGE TO RESTORE 38831052A00339 TO NORMAL.
8673 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-04-17 02:00 | 2010-04-17 02:50 | 22 | 50 | 64230-1 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENED LINE FUSE IN ORDER TO CUT TREE AND REPLACE TWO BLOWN SURGE ARRESTORS / SEE ORDER #64221-1 / OFF AT 0200 ON AT 0250 VER/LDA IDCC CCSCO XXXX
8674 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2016-02-21 14:47 | 2016-02-21 15:31 | 25 | 44 | H4743701 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 190-59 PER TOM CANTRELL // ONE CUSTOMER OUT AT THIS TIME, OFF TIME 1335 RELEASED BY CREW 078S11/CREW ON SITE/WILL NEED TO OPEN FUSE 190-19 FOR REPAIRS/APROX ONE HOUR OUTAGE/VEM/OPEN LINE FUSE AT 1447/REPAIRS MADE AND ALL CUST RESTORED 1531/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB AJB
8675 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2019-02-12 17:55 | 2019-02-12 22:30 | 4 | 275 | 4782621 | 1100 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 810-96//repairs made/restored at 22:30//complete//em
8676 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2015-01-09 14:02 | 2015-01-09 16:39 | 7 | 157 | 4924051 | 1099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BASKET BURNT OFF REC. POLE 137C3248 LINE CREW 4/0CON. RELEASED BY CREW 078H12///OCR OFF LINE @ 16:04---RESTORED OCR @ 16:39---TBL TKT COMP/ ISO 38830137C30248/ COD 7/ VER/BOW L3/DKGXXXX
8677 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-02-03 20:44 | 2020-02-03 23:21 | 7 | 157 | 4359061 | 1099 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse 206-2475,,cutout broke ,manual work over hill ,called for assistance,fetr 23:30,,,all repairs made customers restored @ 23:21,,,complete/ ISO 38830206A42475/ COD 7
8678 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-07-31 15:32 | 2018-07-31 18:35 | 6 | 183 | 4881071 | 1098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE XFR CUTOUT@1080-15 TOOK LINEF 1080-14 OUT.REPLACED XFR CUTOUT&RE-FUSED@1080-14/////////ALL BACK ON
8679 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2009-12-12 06:24 | 2009-12-12 12:30 | 3 | 366 | 60310-1 | 1098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1/0 SECONDARY CONDUCTOR GOT HOT AT A SPLICE IN MID SPAN AND SHORTED OUT AND THEN BURNED INTO IN 3 PLACES. I CALLED DALE AND HE IS SENDING CREW TO REPLACE SEC. COND. WE JUST HAVE 3 CUSTOMERS OUT RIGHT NOW. WHEN CREW GETS HERE WE WILL HAVE TO OPEN TRANS. AND THIS WILL HAVE 2 MORE CUSTOMERS OUT. I HAVE INFORMED THEM THEY WOULD BE OUT FOR ABOUT AN HOUR AND A HALF. I CAUGHT WIRE WITH BOOM OF MY TRUCK AND JERKED PHONE AND TV CABLE OFF CUSTOMERS HOUSE. IT TORE CORNER MOLDING O VER/KEP L3/KEP
8680 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2009-08-16 20:14 | 2009-08-17 02:20 | 3 | 366 | 59745-1 | 1098 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | CAME TO THIS LOC, FOUND NOT ONLY THIS CUST HAVING PROBLEM, BUT THE WHOLE STREET, THOUGHT I HAD BURNTED OFF RISER, BUT NOTHING WAS BURNTED OFF, SUSPECT, I HAVE A BAD 50 KVA SINGLE BUSHING 7200 120/240, CAN NOT GET TRUCK TO POLE, THERE IS A FIELD BEHIND THIS POLE, BUT NO WAY TO GET TO IT, WILL NEED CREW, NONE TRUCKS ACCESIBLE, WILL NEED TO BRING YARD DOG, TO CHANGE THIS IT IS IN BEHIND HOUSE, 4 MEN RELEASED BY CREW 078S06 //VER/GAH IDC XXXX
8681 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-05-16 19:47 | 2013-05-16 20:48 | 18 | 61 | 4124271 | 1098 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLED FOUND NOTHING WRONG ON THE LINE, FIND CUTOUT DOOR TO BE ALMOST BURNTED INTO, I REPLACED AND AND POWER IS RESTORED AT THIS LOC AT 2048//COD 18// VER/DBM IDCC FEC49 XXXX
8682 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2008-01-09 03:03 | 2008-01-09 05:20 | 8 | 137 | 54941-1 | 1096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BROKE COD-8 VER/KEP IDC XXXX
8683 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-08-08 23:57 | 2013-08-09 09:05 | 2 | 548 | 4637851 | 1096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCHED AT REG WORK TIME. XFMR CUTOUT BROKE. REPLACED AND RESTORED @ 9:05. SH VER/CRB L/3 CRB
8684 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2009-10-11 06:58 | 2009-10-11 11:32 | 4 | 274 | 56510-1 | 1096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT GATE == REPLACED GATE == POWER OK /./ VER/TOM IDC XXXX
8685 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-06-26 09:51 | 2009-06-26 14:25 | 4 | 274 | 62110-1 | 1096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANSF == NEED TWO MEN == CHANGED CUTOUT == POWER OK VER/KEP L3/KEP IDC XXXX
8686 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2011-08-21 11:32 | 2011-08-21 20:40 | 2 | 548 | 4735341 | 1096 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 45-6159 BAD 25KVA TRANS. TRUCK TO POLE SEND TO CREWS RELEASED BY CREW 078S08 COMP. M.P. IDC XXXX
8687 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-08-20 14:21 | 2010-08-20 15:34 | 15 | 73 | 58744-1 | 1095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE OPEN AT 38830183D00020, PATROLED LINES AND FOUND NO HAZARDS, CUSTOMER REPORTED FLASH IN BACK YARD, CHANGED LIGHTNING ARRESTER,//VER/CRB IDC XXXX
8688 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2019-10-18 13:26 | 2019-10-18 17:05 | 5 | 219 | 4166191 | 1095 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 37820079000175 .c phase hot line stirrup burned open. 30 ft 4/0 riser,3 -556 stirrups& 3-200amp hot taps. crew in route restored @ 1705
8689 | Hazard | 3307301 | BULAN | ARY-HEINE | 2011-03-05 15:37 | 2011-03-05 21:42 | 3 | 365 | 50222-1 | 1095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CLOSED IN AT 2142 IDCC FP20, TON2213 XXXX
8690 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-02-29 10:12 | 2020-02-29 16:17 | 3 | 365 | 4440941 | 1095 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva xfm on pole 38821110A00079 Released by crew 074S11//MADE MD TO SHOW A MIS MAPPED CUSTOMER //COD 3//bad 25 kva xfm on pole 38821110B00079 Released by crew 074S11/// REPAIRS MADE// POWER RESTORED @ 16:17
8691 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-08-14 10:51 | 2016-08-14 11:30 | 28 | 39 | 4773211 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 70-2128 HOT TAP BURNT OFF REPAIRED ISO 38830070B12128 COD 28 VER/AWD L3/HFP XXXHFP AJB
8692 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2021-05-24 19:59 | 2021-05-24 23:01 | 6 | 182 | 4617561 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required ,bad 25 kva ,,trucks to pole Released by crew 078S05 crew on site FETR 23:59 LRM all pwr rstored23:01 please close ticket LRM//cod 6
8693 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-03-20 13:06 | 2015-03-20 13:48 | 26 | 42 | 4213281 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT PULLED OFF OF POLE AND SWINGING LOOSE//CREWS OPENED RECLOSER TO MAKE REPAIRS//COD 60 OPENED RECL @ 1306 CLOSED @ 1308 CUTOUT PULLED OFF OF POLE AND SWINGING LOOSE//OPENED RECL AGAIN AT 13:45 CLOSED BACK AT 13:48 ON POLE 180:20 DUP IN HOIS ******** VER/HFP L3/HFP AJB
8694 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-12-25 20:59 | 2010-12-25 22:30 | 12 | 91 | 55717-1 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION ON OPEN WIRE VER/PDP IDC XXXX
8695 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-06-22 14:56 | 2016-06-22 21:00 | 3 | 364 | 4409141 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP,,WILL NEED 19.9 KV C/O,,ARR.,HLC & 18 FIB. BRACKET..CREW WITH BIG BUCKET.RGP. RELEASED BY CREW 077E09 VER/AWD
8696 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-12-10 05:33 | 2008-12-10 08:35 | 6 | 182 | 55982-1 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3312202//FUSE IS OPEN ON 126-1//COD-6 STS BAD INSULATOR ON POLE 127-50, TOOK CLAMP OFF AND READY TO REFUSE, TAP DIDNT SERV ANY CUST//MADE A MAP DISC ////VER/CRB L3/IDC IDC XXXX
8697 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-06-24 00:45 | 2010-06-24 03:47 | 6 | 182 | 56237-1 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA TRUCKS OK VOLTAGE 150 TO GROUND 1 LEG RELEASED BY CREW 078S03 //VER/GAH IDCC TOF2355 ESTIMATED TIME OFF XXXX
8698 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2015-02-20 08:24 | 2015-02-20 14:28 | 3 | 364 | 4052581 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA TRANSFORMER BURNED UP. 7200/120/240. THIS SERVES 3 CUSTOMERS, WE MAY NEED TO UPGRADE THE XFMR SIZE. CREW REQUIRED. CAN USE TRUCK. RELEASED BY CREW 074S02 CREW ON SITE RESTORED AT 14:28P VER/HFP L3/HFP
8699 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2020-06-20 15:33 | 2020-06-20 16:25 | 21 | 52 | 4051481 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | at pole 45-23 tie wire broke, wire came off isoater. repairs made power restored at 1625
8700 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2018-06-16 14:16 | 2018-06-16 17:18 | 6 | 182 | 4608281 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | line fuse blown 211-C-24 patrolling...Pole 211-C-74 has rotted off at ground and fell no customers are served from this pole so we will make deadend on pole 211-C-73 and remove this span of wire and hardware.Send copy to Cliff Freeman to have guy and crossarm added on pole 73 @ later date..restored power @ 17:18
8701 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2013-01-09 18:44 | 2013-01-09 20:08 | 13 | 84 | 4582301 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER SERVING LIGHT CKT BLEW LID OFF THE CAN AND BUSHING LAID OVER PRIMARY, BLOWING FUSE// CREW TO REPAIR THE TRANSFORMER TOMORROW//COD 13//CREW WILL NEED TO BRING: 15KVA XFMR, CUTOUT AND ARRESTER, FIBERGLASS BRKT AND A TRANSFORMER BAG // TOOK BOTH TAPS OFF AT 9:28 PUT BACK ON AT 9:44 VER/KEP IDC XXXX
8702 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-08-13 18:54 | 2011-08-13 19:15 | 52 | 21 | H4703451 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CONDUCTOR FELL OFF INSULATOR. OPEN OTHER 2 PHASES AT 19:00//COD 96// IDCC DUP TO OPEN OTHER RECLOSERS, NOT SURE OF TIME ESTIMATED FROM SCADA DATA XXXX
8703 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2019-04-19 21:18 | 2019-04-20 01:51 | 4 | 273 | 4136351 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON POLE BREAKING DOWN. DIFFICULT ACCESS TO POLE. WILL TRY TO GET TO IT.///////////WILL NEED HELP ON THIS/OPENED 1011-144@21:18/////////MADE REPAIRS&RESTORED/ ISO 38821011D00144/ COD 4/ MD DONE (CUTOUT ON POLE 1035-8) L3/HFP
8704 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-01-08 07:48 | 2014-01-08 10:50 | 6 | 182 | 4257971 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SEC. RISER BURNED IN TWO// WILL MAKE REPAIRS// POWER IS RESTORED // OPENED AT 9:55 CLOSED 10:50// //VER/GAH IDC XXXX
8705 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2008-01-12 07:12 | 2008-01-12 08:30 | 14 | 78 | 56208-1 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409001///FUSE LINK BROKE ON XFMR FUSE. . RE-FUSED XFMR. SH VER/ARN IDC XXXX
8706 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2012-01-20 11:42 | 2012-01-20 14:18 | 7 | 156 | 4277921 | 1092 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER POLE 18-89. LINE CREW ON THE WAY RELEASED BY CREW 074S11// REMOVED BAD TRANSFORMER AND MADE A OPEN WYE OPEN DELTA BANK CHECKED THE VOLTAGE AND RESTORED POWER. TIM MCCOY/// VER/CRB IDC XXXX
8707 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-10-04 00:39 | 2014-10-04 18:50 | 1 | 1091 | 4550521 | 1091 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUSTOMER TO MAKE METER BASE REPAIRS, NEED NEW 7200-25 KVA,MAN.TREE CREW, AND LINE CREW, WORK IN DAYLIGHT NO TRUCK TO POLE RELEASED BY CREW 078H12//TAKE 2/3 SERVICE DROP---REPLACED XFMR,CUTOUT, & INSTALLED NEW SERVICE DROP---CHECKED VOLT. CKD GOOD---CUST STILL MAKING REPAIRS TO SERV ENT.---COMPLETE VER/CRB
8708 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-06-11 22:04 | 2011-06-12 16:15 | 1 | 1091 | 4299161 | 1091 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONDUCTOR LOOSE ON POLE 1014-C1-325 & DANGEROUS. OPENED STA BREAKER AT 1918, CUT CONDUCTOR IN CLEAR & CLOSED STA BREAKER AT 1932, 1 CUSTOMERS REMAINING OUT. SDB / 1615 / RESTORED. VER/SDB IDC XXXX
8709 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-08-08 07:06 | 2019-08-08 08:55 | 10 | 109 | 4857201 | 1090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer back in at 08:55, broken fuse door
8710 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-07-24 04:44 | 2020-07-24 08:22 | 5 | 218 | 4223721 | 1090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad lightning arrestor on pole 302-184, cut in clear, power restored
8711 | South Williamson | 3202201 | LOVELY | LOVELY | 2013-11-18 15:26 | 2013-11-19 09:36 | 1 | 1090 | 4054411 | 1090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 19.9 KV / 240-480 TRANSFORMER BAD, TRUCK ACCESS19.9 KV / 240- 480 2 BUSHING 50 KVA TRANSFORMER BAD . TRUCK ACCESS RELEASED BY CREW 074S03 VER/CRB IDC XXXX
8712 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-09-28 07:37 | 2021-09-28 11:15 | 5 | 218 | 4297281 | 1090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830357000048 broke c/o--replaced-- 15t lat in at 11:15--allgood-ds092821
8713 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-06-08 16:34 | 2015-06-08 20:12 | 5 | 218 | 4530621 | 1090 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 19.9KV TRANSFORMER. RELEASED BY CREW 074S02/ ON SITE WORKING ON CHANGING TRANSFORMER TIM MCCOY RELEASED BY CREW 074H10 VER/CRB
8714 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-07-18 12:27 | 2012-07-18 14:28 | 9 | 121 | 4755761 | 1089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 170-228 ONE CUSTOMER OUTAGED.
8715 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-02-03 09:44 | 2016-02-03 15:47 | 3 | 363 | 4671221 | 1089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 37830029000211 HAD LINE FUSE OUT ON POLE 29-347 VER/CRB
8716 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2013-04-19 17:42 | 2013-04-19 19:43 | 9 | 121 | 4029501 | 1089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 523-83 ON FIRE. PLEASE SEND COPY TO STEVE M TO HAVE JOB WRITTEN TO TAKEOUT OPENWIRE. APR CLOSE TICKET ///VER/CRB L/3 CRB IDCC CDC48 XXXX
8717 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-06-29 12:26 | 2009-06-29 14:27 | 9 | 121 | 51252-1 | 1089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3002107// BASKET BURNT OFF ON POLE 45-109//ISO 38830045A10109//COD 9// VER/DBM
8718 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-05-11 08:22 | 2009-05-11 14:25 | 3 | 363 | 58921-1 | 1089 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NEEDS TO CHANGE POLE OUT TOP PART OF POLE SPLIT OUT NEEDS REPLACED WITH NEW POLE. CUSTOMERS HAVE POWER. WAS TEMPORAILLY FIXED. WILL BE GOING BACK TODAY (MAY/11/2009) TO COMPLETE. WILL NEED TO TURN CUSTOMERS POWER OFF FOR AN HOUR - HOUR AND HALF TO WORK//POLE HAS BEEN CHANGE OUT//VER/CRB
8719 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-05-22 20:31 | 2019-05-23 14:40 | 1 | 1089 | 4317291 | 1089 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | voltage checked good in pedistal. voltage checked low at meterbase, seem to have a phase out between meterbase and pedistal//customer does not need this fixed tonight//customer has turned off main breaker// on scene, set pole and temp ug service till techs make job to replace entire ug. restored @ 14:40 hrs p.hicks
8720 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-01-31 11:09 | 2014-01-31 13:25 | 8 | 136 | 4332811 | 1088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 079S02 TRANSFORMER FUSE HAD BROKE, REPLACED THE FUSE AND POWER IS BACK ON.//COD 8// VER/DBM IDC XXXX
8721 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2013-11-09 06:08 | 2013-11-09 10:40 | 4 | 272 | 4023471 | 1088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK IN THR AM 11-9-13// XFMR FUSE BLOWN// WILL REFUSE// FUSE LINK APPEARED TO HAVE BROKE// POWER IS RESTORED//COD 13// VER/DBM VER/HFP HFPC PN34 CNT13
8722 | Pikeville | 3408101 | SALISBURY | PRINTER | 2017-02-13 13:04 | 2017-02-13 14:12 | 16 | 68 | 4393821 | 1088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE AT PL #1146-23 TO MAKE REPAIRS TO BROKEN ARRESTOR AND CUTOUT, DIFFICULT LOCATION/1304// BACK ON AT 14:12 R RAY 38831146D00023 VER/AWD L3/HFP HFPC CCO FEC57
8723 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-12-27 18:09 | 2016-12-27 20:25 | 8 | 136 | 4243911 | 1088 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALLED CUSTOMER: (1818) SAID LIGHTS ARE FLICKERING AND CAUSING APPLIANCES TO BURN. CUSTOMER SERVICE BROKEN IN SPLICE NEXT TO HOUSE. REPAIRED CONNECTION VER/AWD
8724 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-11-11 13:57 | 2014-11-11 16:58 | 6 | 181 | 4720131 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE BLOWN // WILL REFUSE// BAD CUTOUT // WILL REPAIR// POWER RESTORED 16:58 VER/CRB L3/HFP AJB
8725 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-07-03 19:44 | 2014-07-04 01:46 | 3 | 362 | 4191261 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR BAD ON POLE 1109-115 CLOSED LINE FUSE ON POLE 1109-28 @ 01:46 POWER BACK ON . VER/KEP
8726 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-01-09 08:26 | 2016-01-09 14:28 | 3 | 362 | 4596641 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA DOUBLE BUSHING N O TRUCKS TO WET NEED YARD DOG AND 4 MEN/BEST PLACE TO COME IN 550 KRESTVIEW BEHIND RAIDER MART RELEASED BY CREW 078S03---CREW ON SITE---RECL. 38830206D02051 NRO AND TAGD TO CREW BACK TO NORMAL @ 1439//---REPLACED BAD 50 KVA---CKD ALL 3 UG SERV.124-124-248V---CKD GOOD---3 CUST FEED OFF OF XFMR SEND NOTE TO MAPPING----TBL TKT COMP.//MADE MIS-MAPPED CUST MDC//COD 3 VER/CRB
8727 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2019-05-12 05:58 | 2019-05-12 08:59 | 6 | 181 | 4255711 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF cutout broke on pole 235-18///changing///repairs made///closed LF in at 08:59///complete BR L3/HFP
8728 | Hazard | 3310502 | HADDIX | CANOE | 2009-03-04 07:47 | 2009-03-04 13:49 | 3 | 362 | 54819-1 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3310502// STS GOT ONE SPAN OF # 4 AL PRIMARY DOWN ON POLE # 169-128, WIRE ROTTEN NO TREE ON IT. CALL GLEN AND HE IS GETTING CREW TOGETHER .WIRE IS DOWN RIGHT AT TO D.E. SHOE ON TAKE OFF POLE RELEASED BY CREW 077S05 RELEASED BY CREW 077H04//COD 3//OPENED RECLOSER ON POLE 27 TO MAKE REPAIRS... SEE ORDER 54984-1// VER/DBM IDCC CNT1 XXXX
8729 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2017-04-07 04:38 | 2017-04-07 10:36 | 5 | 358 | 4626141 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED XFMR @ 0550/ CUTOUT BROKE DOWN AND BURNT THE TOP OF POLE 267-59 OFF @ CUTOUT.WILL NEED LINE CREW TO MAKE REPAIRS.MIGHT BE ABLE TO FRAME DOWN ON POLE.WILL NEED 7200 CUTOUT AND DEADEND INSULATOR, GUY ATT. AND INSULATOR../ ISO 37820267000052/ COD 5/ XFMR 37820267000052 ON @ 0740 4 CUST/ FUSE 37820267000052 ON @ 1036 1 CUST/ VER/BOW // SHOULD BE DUPLICATE FOR FUSE OUTAGE, WHEN WAS IT OPENED? = HFP
8730 | Hazard | 3309904 | SLEMP | ROYAL DIAMOND | 2020-08-31 18:13 | 2020-09-01 03:16 | 2 | 543 | 4409511 | 1086 | TRANSMISSION LINE | EQUIPMENT FAILURE | TRANSFORMER, STATION SERVICE | DOL 1050048 // T-Line outage // Station source is out // investigating load xfers // t-line completed work and closed CB @ 0316
8731 | Hazard | 3311103 | STINNETT | WENDOVER | 2016-08-01 18:13 | 2016-08-01 21:14 | 6 | 181 | 4720161 | 1086 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 459C-59 . BAD CUTOUT ON POLE 459A-59 , CLOSED FUSE ON POLE 459C-58 @ 21:14 . VER/AWD L3/HFP XXXHFP
8732 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-08-27 06:25 | 2008-08-27 09:00 | 7 | 155 | 55691-1 | 1085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3001002//LIGHTNING ARRESTER FELL APART AND PRIMARY SIDE WAS RESTING AGAINST METAL BRACKET//COD 7// VER/DBM
8733 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-01-17 12:03 | 2010-01-17 15:40 | 5 | 217 | 55418-1 | 1085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078S07 FOUND BAD CUTOUT ON TRANSFORMER POLE, BEHIND THIS HOUSE, RIGHT ACROSS FROM WHERE OLD STORE WAS, WHITE HIOUSE WITH A RED ROOF, NEED CREW TO CHANGE, HAVE CONTACTED MR. LYNCH, WELL NEED NEW CUTOUT, NO TRUACKS RELEASED BY CREW 078S06---CREW ON SITE VER/TOM IDC XXXX
8734 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2011-10-08 17:55 | 2011-10-09 12:00 | 1 | 1085 | 4958491 | 1085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CREW RELEASED BY CREW 078S07//WILL BE WORKED IN THE AM ** ONLY ONE CUSTOMER OUT.//VER/CRB IDC XXXX
8735 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-07-25 19:30 | 2011-07-26 13:35 | 1 | 1085 | 4621401 | 1085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND, WILL WORK ON THIS IN THE MORNING 7/26/11, PER BRUCE LINDON. CREW REQUIRED RELEASED BY CREW 077S08 REPAIRED UNDERGROUND AND RESTORED POWER AT 13..35 VER/KEP IDC DIM LIGHTS CALL CHANGED TIME OFF FROM 1804, ESTIMATED XXXX
8736 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-03-02 18:03 | 2009-03-02 18:38 | 31 | 35 | 54261-1 | 1085 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP CREW HAD TO OPEN RECLOSER ( 31 CUSTOMERS) TO ALLOW THEM TO SAFELY INSTALL GUY ON POLE THAT IS LEANING & ROTTED OFF AT THE GROUND. SENT EMAIL TO RON RYE & TIMM HALL TO HAVE POLE REPLACED. L3/HFP IDC XXXX
8737 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-07-10 15:39 | 2017-07-10 20:10 | 4 | 271 | 4102661 | 1084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA XFMR. CREW ENROUTE TO REPLACE. REPLACED AND RESTORED @ 20:10. SH/ ISO 38830881000131/ COD 4/ VER/BOW
8738 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-11-04 08:29 | 2019-11-04 10:55 | 9 | 146 | 4288771 | 1084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse broken on 852-137 B PHASE//will have to open the other line fuse on this pole to change.i have called steve hall to assist.open cutout at 10:21 back on at 10 50.2nd cutout back in 10:55 Released by crew 076S01
8739 | Pikeville | 3409502 | BURDINE | LEVISA | 2012-03-20 17:56 | 2012-03-20 22:27 | 4 | 271 | 4600151 | 1084 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER, CREW ENROUTE.//COD 4// VER/DBM IDC XXXX
8740 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2013-10-25 23:29 | 2013-10-26 05:30 | 3 | 361 | 4963781 | 1083 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2 SPANS OF PRIMARY DOWN..NEED 2 MAN CREW.6AA DOWN BETWEEN 679-38-39-40..LINE FUSE OUT ON 679-1 VER/TOM L3/TOM
8741 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-06-04 18:49 | 2016-06-05 00:50 | 3 | 361 | 4300531 | 1083 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT . WILL NEED 1 A LINEMAN & CUTOUT RELEASED BY CREW 074S04BAD 19.9 CUTOUT . WILL NEED 1 A LINEMAN & CUTOUT . REPLACED CUTOUT VER/KEP
8742 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-03-05 18:58 | 2013-03-06 13:00 | 1 | 1082 | 4873501 | 1082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S08--BROKE CUTOUT NEED BIG BUCKET AND FLAGERS NEED 7200 CUTOUT AND ARRESTER VER/KEP IDC XXXX
8743 | South Williamson | 3202201 | LOVELY | LOVELY | 2018-08-19 12:54 | 2018-08-19 17:03 | 18 | 249 | 4973411 | 1082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad primary tap cutout on pole 38820673C00071. No truck access. Top of cutout is close to grounding out on the primary neutral. I will need to open switch at pole 38820673C00233 when help arrives.//COD 1 FROM BEGINNING OF OUTAGE//OPENED SW ON POLE 38820673C00233 @ 1614 L3/HFP
8744 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-08-04 14:20 | 2022-08-04 14:52 | 43 | 32 | 4635521 | 1082 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | fuse open and wire down///neutral broken from pole 37830229000077-37830229000078. Will need manual tree & line crews. OPENED OCR 37830205D00448 TO MAKE REPAIR @ 1425 CLOSED 1445fuse open and wire down///neutral broken from pole 37830229000077-37830229000078. Will need manual tree & line crews. Released by crew 034M29
8745 | Hazard | 3302704 | HAZARD | KENMONT | 2011-09-13 16:26 | 2011-09-14 10:28 | 1 | 1082 | 4866111 | 1082 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WORK IN MORNING, BIG PRESS TOOL, 350 TO 2/0 CONNECTOR, SMALL PIECE OF 2/0 3FT LONG. BILL HAS KEY TO GATE. GO THRU CUMMINS LOT AT BACK TO GATE FAR RIGHT. ROAD HAS BEEN FRESHLY DOZED. BUCKET ACCESSABLE. CONNECTOR BURNED UP. SEND TO BRUCE, JIM,GLEN RELEASED BY CREW 077S08 VER/HFP L3/HFP IDC XXXX
8746 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2016-08-22 20:54 | 2016-08-22 21:30 | 30 | 36 | 4826921 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 69-5637 CONN BURNT OPEN CHGED CUTOUT AND REPAIRED WIRE VER/AWD L3/HFP HFPC FP AJB
8747 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-11-01 16:33 | 2012-11-01 18:03 | 12 | 90 | 4324371 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | NO CREW REQUIRED FUSE BLOWN ON 222-112 WITH BAD ARRESTOR CUT IN CLEAR LINE FUSE ON 222-76 ALSO BLOWN // SENT EMAIL TO L RAYBURN TO HAVE ARRESTOR CHANGED COD-12 ISO LF 38830222D00076 VER/HFP L3/HFP IDC XXXX
8748 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2020-07-12 22:12 | 2020-07-13 00:12 | 9 | 120 | 4156411 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester on pole 149-134. restored power at 12:12
8749 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-11-20 20:05 | 2011-11-20 20:35 | 36 | 30 | 4095121 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PRC CREW REQUIRED--LINE FUSE CUTOUT THAT FEEDS MEDOWLARK RD IS CRACKED AND NEEDS REPLACED ON POLE 39831148A00131--TRUCK TO POLE BAD TRAFFIC LOCATION RELEASED BY CREW 078S07 VER/ARN IDCC TOF1611 XXXX
8750 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-05-07 17:57 | 2011-05-07 19:57 | 9 | 120 | 4017481 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE ON 786-143. NO TRUCK ACCESS TO POLE. REPLACED CUTOUT AND RE-FUSED @ 19:57. SH COD-9 ISO LF 38830786B00007 VER/HFP L3/HFP IDC XXXX
8751 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-01-03 15:33 | 2014-01-03 15:45 | 90 | 12 | 4225411 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED RECLOSER ON POLE 529-143 TO MAKE REPAIRS ON TIX 4219861 VER/CRB IDCC CCSCO XXXX
8752 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-06-11 13:20 | 2013-06-11 14:05 | 24 | 45 | 4258831 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED OCRS POLE 1121-13 AT 13:20 . REPAIRS TO WIRE COMPLETE, CLOSED AT 14:05, ALL WORK COMPLETE / GXJ//COD 24// VER/DBM IDC XXXX
8753 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2016-09-02 00:06 | 2016-09-02 06:06 | 3 | 360 | 4862481 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WI WORK AT START OF REGULAR SHIFT. LINE FUSE OPEN @ 992-C-124, PATROLLING. FOUND NO TROUBLE ON LINE, FUSE HAD PULLED INTO, CLOSED L/F BACK @0606. VER/TOM L3/TOM L3/HFP XXXHFP
8754 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-02-16 16:20 | 2011-02-16 19:20 | 6 | 180 | 58300-1 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LATERAL FUSE BLOWN ON 1014-C1-370....JUST RUNS ONE SPAN TO POLE 1014-C1-195.....LINE IS CLEAR....WILL RE-FUSE...//...RE-FUSED LATERAL....XFMR FUSE WAS ALSO BLOWN....RE-FUSED XFMR...BAD XFMR....CALLED J REED CREW...THEW WILL CHANGE XFMR....I WILL ASSIST THEM....//......REPLACED BAD XFMR.....POWER ON.....JRV....02/16/11//COD 6// VER/DBM IDC XXXX
8755 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-06-07 22:12 | 2015-06-08 01:48 | 5 | 216 | 4522041 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV CUTOUT, ARRESTOR..TRAILER PARK END OF GAIL DR. 5TH TRAILER ON LEFT. RELEASED BY CREW 078S07//COD 5// VER/DBM
8756 | Pikeville | 3421001 | BREAKS | CITY | 2009-10-28 06:00 | 2009-10-28 15:00 | 2 | 540 | 60182-1 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP 3400901// ARRESTER ON CSP FAILED. L3/HFP IDC XXXX
8757 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2018-09-23 14:35 | 2018-09-23 19:05 | 4 | 270 | 4145131 | 1080 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | line fuse out on pole 468-3, guywire burnt into on pole 468-89 , removed guywire .restored power at 19:05.crew needs to replace guywire later date.//SENT TO TECH L3/HFP
8758 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-15 22:46 | 2010-05-16 16:45 | 1 | 1079 | 62993-1 | 1079 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON POLE 1038-115 REFUSED BUT FUSE BLEW INSTANTLY BELIEVE XFME IS BAD WILL NEED 10 KVA 19.9 XFMR STEEP ROAD TO SITE CAN GET PICKUP TO POLE BUT NOT SURE ABOUT LINE TRUCK RELEASED BY CREW 077E02//COD 1// VER/DBM IDC XXXX
8759 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-06-06 07:37 | 2019-06-06 09:00 | 13 | 83 | 4436061 | 1079 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke on pole 69-c2-4568, Linefuse back in at 09:00
8760 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-07-03 19:21 | 2019-07-03 20:10 | 22 | 49 | 4650141 | 1078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 Bad cutout on A phase tap and single phase tap on pole 24-B3-748, had to open all 3 phases to make repairs, opened all 3 @1921, got cutouts changed and closed all 3 back in @2010. L3/HFP
8761 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2018-12-30 11:16 | 2018-12-30 13:50 | 7 | 154 | 4613861 | 1078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 188-B-96, will be changing. Got c/o changed and restored @1350.
8762 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-08-26 01:11 | 2013-08-26 10:10 | 2 | 539 | 4706201 | 1078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CREW REQUIRED--#4 CU OPENWIRE DOWN--TRUCK TO POLE RELEASED BY CREW 078S07///REMOVED #4CU OPENWIRE SECONDARY///NOT FEEDING ANYTHING//HOUSE VACATED AND MTR WAS PULLED///TALKED TO CUST NO INTENT ON METERING HOUSE///ALSO REPAIRED BROKEN #4CU PRIM NEUT, RESAGED ACROSS ROADWAY///CHANGED CUTOUT//ALSO BROKEN GROUND WIRE ON POLE REPLACED DRIVEN GROUND ROD AND POLE GROUND VER/CRB L/3 CRB IDC XXXX
8763 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-09-18 11:12 | 2017-09-18 12:29 | 14 | 77 | 4370561 | 1078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | DOL 772292 // SCADA INDICATES FEEDER L/O @ 1112 // SWITCHES BURNT UP ON POLE 38830046B11075 //600A DISC. SWITCHES BAD @ 46-B1-1075 RELEASED BY CREW 078S07//COD 1939 // CLOSED ASHL-29TH CB AND RESTORED 516 CC @ 1214 // CLOSED 47TH-49TH CB @ 1229 AND RESTORED 1336 // VER/DBM L3/HFP XXXHFP ACBC CCAF
8764 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-04-15 11:58 | 2008-04-15 12:20 | 49 | 22 | 51257-1 | 1078 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LIGHTNING ARRESTOR BLEW ON POLE 1101-40 & TOOK OCR ON POLE 1101-533 OUT. CLEARED ARRESTOR&CLOSED IN RECLOSER. THANKS G.R.//A PHASE COD 10//VER/CRB IDC LOOKS LIKE THIS SHOULD BE PH B CHANGED COUNT FROM 10 XXXX
8765 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-03-29 10:41 | 2009-03-29 15:50 | 13 | 309 | 62633-1 | 1077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29128132 // COD-13 POLE 38830209000168 BURNT AT CUTOUT, ISOLATED AT 38830209000046,POLE 38830209000168 BURNT AT CUTOUT, ISOLATED AT 38830209000046, CLOSED FUSE AT 11:45, 1 CUSTOMER OUT, BIL---CREW ON SITEL LYNCH HAS BEEN NOTIFIED, 45-4 POLE.POLE 3883020 L3/HFP IDC XXXX
8766 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-09-01 02:40 | 2022-09-01 08:39 | 3 | 359 | 4824421 | 1077 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Jeff states TR 37830127B10501 is TR that is openlightning arester blow on xmfr at pole 127-501.made repairs and got xmfr restored to power @08:39.
8767 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-12-10 09:31 | 2009-12-10 14:00 | 4 | 269 | 65161-1 | 1076 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRE NEED TO REPLACE BAD CUTOUT, POLE 1103-292, LOCATION IN TRAILER PARK ON LEFT AT THE FORKS OF COWPEN. NEED A BIG BUCKET SAME AS 57591 RELEASED BY CREW 074S05 COMPLETE POWER BACK ON PLAYNE 10-10-09
8768 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-02-25 11:21 | 2022-02-25 14:56 | 5 | 215 | 4545361 | 1075 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout went bad and burned top of pole 246-30 off wire is 3 foot high crossing the road, need 40 foot pole flying corner clamp 1 de unit and 2 de insularors 2 clevis and spools 7200 cutout and tee brkt, pole is manual but might can set new pole off old one took clamp off 246-25 got recloser in at 1048 Released by crew 077S05, changed pole out, all power restored @ 14;56 P.HICKS
8769 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-12-31 17:02 | 2022-12-31 23:00 | 3 | 358 | 4382891 | 1074 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad XFMR, the left had secondary bushing has burnt out of the side and this customer has part power, will need to replace this 25KVA 7200 XFMR. The pole number on the maps shows 250-A-5 but it is 250-4 in the field. Truck access, crew required. Released by crew 077S04.. restored @ 23:00
8770 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-03-31 12:01 | 2014-03-31 15:00 | 6 | 179 | 4547861 | 1074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PHASE A OPEN//COD 28//OPENED B & C @ 1313 (SEE H4547861)//COD +11//BAD CUTOUT BURNED ALLEY ARM BRACE OFF AND IT WENT BETWEEN PHASE B AND C. I OPENED PHASE A & C RECLOSER ON POLE 38820939C00020 AT 13:13, PHASE B WAS ALREADY OPENED. JOEY IS ENROUTE TO REPLACE THE ARM AND CUTOUT. RELEASED BY CREW 079S02.MADE REPAIRS.REPLACED ARM AND CUTOUT.//TOTAL COD 39// VER/DBM IDC XXXX
8771 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-10-14 11:00 | 2010-10-14 16:58 | 3 | 358 | 59578-1 | 1074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37324167 LIFTED HOT TAP ON POLE 226-63 AT 11:00,, POLE FIRE AT 226-97, CREW REQUIRED, 45 POLE, TRUCK OK, DONNIE GENT IN ROUTE. RELEASED BY CREW 078S05 COD-3 VER/HFP L3/HFP IDCC TOF1115, PN97 XXXX
8772 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-12-31 01:18 | 2017-12-31 10:15 | 2 | 537 | 4689651 | 1074 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer, no response //crew required green pole behind house Released by crew 078S03//broke cutout//spoke with customer and they have gas heat, have agreed to wait until daylight for crew to make repairs//ARCOS PRC crew at daylight /crew on site//Prim lead laying on steel CO bkt--will need to open OCR on 38830199000205 to safely clear broken CO--opened ocr @ 09:49-cleared broke CO--closed OCR 119-205 @ 09:53--changed cutout on 200-110, pwr restored at 10:15--rmv38830199000205 cod 2 on t
8773 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-06-17 16:49 | 2009-06-18 10:42 | 1 | 1073 | 64167-1 | 1073 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD C/O. COMP. CCW COD-1 ISO 37830104B00111 L3/HFP IDC XXXX
8774 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2021-08-09 15:53 | 2021-08-10 09:46 | 1 | 1073 | 4023341 | 1073 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm fuse blown will refuse///Refused xfm and top of cutout broke in the clear///This is a difficult location will need help on this replacing cutout///Hold till in the morning so i can get help on thisper Dennis Massey///Send copy to Paul Keese Released by crew 074S02// email sentXfm fuse blown will refuse///Refused xfm and top of cutout broke in the clear///This is a difficult location will need help on this replacing cutout///Hold till in the morning so i can get help on thisper Dennis Massey
8775 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-06-30 00:26 | 2017-06-30 02:40 | 8 | 134 | 4060191 | 1072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ALL 3 CAPACITORS OIL SWITCHES OPEN @24-B4-353, I PLACED TAGS ON ALL 3 FOR DDC AND PUT IN ABNORMAL, ALSO TRANS. FUSE OPEN @24-B4-251, CHECKING. //TAGGED TRANS.CUT-OUT TO DDC @24-B4-251// LOOKS LIKE RISER ON TOPSIDE OF CUT-OUT GOT AGAINST OTHER PHASE OF THE SPACER CABLE AND BURNDT THE EYE OUT OF THE HOT LINE CLAMP, ALSO BURNDT THE RISER INTO, BURNDT ITSELF INTO THE OTHER PHASE AND MAY HAVE TO SPLICE THIS 556, THIS WILL TAKE A LINE CREW AND MAYBE AN OUTAGE TO REPAIR.
8776 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2012-02-10 00:16 | 2012-02-10 02:30 | 8 | 134 | 4331491 | 1072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD TO RESET CSP TRANSFORMER, SERVICE DROP MELTED CAUSING TRANSFORMER TO DROP OUT VER/ARN IDC XXXX
8777 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-12-26 15:58 | 2009-12-27 09:50 | 1 | 1072 | 51382-1 | 1072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF BAD JUMPERED TO ANOTHER TRANSF. POWER ON
8778 | Pikeville | 3402002 | KEYSER | STONECOAL | 2021-09-11 08:53 | 2021-09-11 13:21 | 4 | 268 | 4231591 | 1072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #2ACSR SEC WIRE DOWN.NEED CREW,200FT WIRE.IS ACCESSABLE,BESIDE RD JUST BEFORE CUSHAW BR OF STONECOAL RD///////MADE NECESSARY REPAIRS&RESTORED,ALL OK AFTERWARDS
8779 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-07-16 11:37 | 2020-07-16 13:51 | 8 | 134 | 4170561 | 1072 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burnt up in sec replaced connections. pls close. tre
8780 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2008-11-23 12:10 | 2008-11-23 14:24 | 8 | 134 | 51339-1 | 1072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP 3200201//, ON SITE, CHECKING TROUBLE, CONNECTOR FROM XFORMER LESD TO AERIAL CABLE BURNT UP COD - 8 IDC XXXX
8781 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-01-05 07:12 | 2011-01-05 09:26 | 8 | 134 | 58797-1 | 1072 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SECTIONALIZER | C- PHASE ONLY OUT. I REMOVED 3 100 AMP CES ON POLE 117-41 AND INSTALLED 3- 30T FUSES. SEND COPY TO ENG. ALSO SEND COPY TO ROW PIKEVILLE TREES ARE GETTING UP BETWEEN PHASES NEEDS CUT FROM FUSE POLE ALL THE WAY UP FILED MD TO HAVE SECT REMOVED AND 30T INSTALLED MADE SEPERATE OUTAGE FOR THE OTHER PHASE VER/KEP L3/KEP IDC XXXX
8782 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2010-11-16 19:09 | 2010-11-16 19:30 | 51 | 21 | 56617-1 | 1071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEVICER ON SITE - FAULT POLE IS1148-2019 , P TOLLIVER EN ROUTE TO ASIST--OPENED RECLOSER AT 19:09P TOLLIVER EN ROUTE TO ASIST--OPENED RECLOSER AT 19:09--LEFT TRANSFORMER ON POLE 39831148B42019 OFF--SEASONAL USE--E MAIL TO RAYBURN TOLLIVER MARTIN OUTAGE ON RECLOSER ONLY FROM 1909-1930. VER/PDP IDCC PN502 XXXX
8783 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2022-06-07 19:40 | 2022-06-07 21:39 | 9 | 119 | 4034731 | 1071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | open lf @ 925-75 @ 19:40. fault @ 901-380. no trks Released by crew 078S07 crew on site FETR 21:45 LRM pwr restored 21:39 pleaseclose ticket LRM
8784 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-06-07 15:46 | 2010-06-08 09:37 | 1 | 1071 | 58461-1 | 1071 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE OPEN ON BANK OF XFMER.BAD 50 KVA 480 VOLT XFMER BANK NEED A 19.9 50KVA 277 VOLT XFMER // PER DUTY SUPERVISOR WILL CHANGE TRANSFORMER IN THE MORNING 06/08//COD 1// VER/DBM IDC XXXX
8785 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2019-02-11 21:38 | 2019-02-11 23:25 | 10 | 107 | 4779431 | 1070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 376-78, replaced cutout restored power at 11:25..
8786 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2018-07-21 16:25 | 2018-07-22 10:15 | 1 | 1070 | 4828981 | 1070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replace xfrm 25 kva---7.2 voltage reads n1-136 v2 136 v12-272 --disconnected meter in meter base info customer to turn breaker off---customer will have boat moved to get truck to pole will be a tight fit--crew needed Released by crew 074M02 all repairs made and power restored e. mckinney
8787 | Hazard | 3309302 | VICCO | JEFF | 2014-02-08 14:59 | 2014-02-08 18:33 | 5 | 214 | 4368131 | 1070 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 077S08 BAD CUTOUT REPLACED AND RESTORED POWER AT 1833 VER/SEF
8788 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2022-12-04 07:55 | 2022-12-04 15:35 | 4 | 460 | 4226371 | 1069 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | crew reqd. no voltage at home/checked at sec going dup hill/4/0 hot leg & #2 stranded neut/send to L.Mccoy Released by crew 078S04//(COD ! ) FROM BEGINNING OF OUTAGE//OPENING XFMER TO OUT 3 MORE CUSTS//crew reqd. no voltage at home/checked at sec going dup hill/4/0 hot leg & #2 stranded neut/send to L.Mccoy Released by crew 078S04. opened xfmr at 12:12 back in at 14:30. customer with bad underground restored at 15:35
8789 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-08-23 08:48 | 2021-08-23 13:15 | 4 | 267 | 4137841 | 1068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | on pole 38830142A00127 bad 25kva 7200 by truck Released by crew 078S12 crewon site ETR 14:00 all pwr restored13:15 pleasecloseticket LRM
8790 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-01-18 16:12 | 2011-01-18 19:10 | 6 | 178 | 62360-1 | 1068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//// 19.9 50KVA XFMR BAD RELEASED BY CREW 077S08//VER/CRB. IDC XXXX
8791 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-04-19 16:25 | 2008-04-19 19:23 | 6 | 178 | 52402-1 | 1068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE IS ON FIRE,WILL TRY TO LIFT XFR HOT-TAP FRM GROUND,IF CANT WILL LIFT HOT-TAP ON THIS TAP AT TAKE-OFF POLEPOLE NEARLY BURNED INTO,WILL HAVE TO SLICE REPAIR IT.CREW NOTIFIED AND ENROUTE SHORTLY.NOTE FETR CHANGE//3411802//VER/CRB IDCC PN170, CNT7 XXXX
8792 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-10-25 11:09 | 2009-10-25 12:38 | 12 | 89 | 52901-1 | 1068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP LINE FUSE OUT ON POLE 38830019C00043--BROKEN FUSE LINK COD-12 ISO LF 38830019C00043 L3/HFP IDCC CCO XXXX
8793 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2010-12-13 06:19 | 2010-12-13 10:46 | 4 | 267 | 65765-1 | 1068 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | CREW ON SITE PATROLLING LINE,CONDUCTOR FLOATING ON POLE 53-155//VER/CRB IDC XXXX
8794 | Hazard | 3310502 | HADDIX | CANOE | 2017-09-01 14:30 | 2017-09-01 14:56 | 41 | 26 | 4317211 | 1066 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEE 4316701/ OPENING RECLOSERS TO REPLACE SWITCH CUTOUT ON POLE 37840216000001/ ISO 37830169C00338/ COD 41/ 1430-1456/ VER/BOW SJG (RELATED TO 4316701)
8795 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2010-05-02 11:54 | 2010-05-02 13:05 | 15 | 71 | 53802-1 | 1065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#34925868//BAD CUTOUT DOOR//VER/CRB IDC XXXX
8796 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-01-19 18:55 | 2016-01-20 00:50 | 3 | 355 | 4633751 | 1065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25 KVA 19.9 / 120/240, 4 MAN LINE CREW, NO TRUCK ACCESS, CAN GET PICKUP WITHIN 100 FT OF POLE FROM CEMETARY RD ( CEMETARY RD HAS UNLOCKED CABLE ACROSS RD - GRAVEL RD ON RIGHT ) RELEASED BY CREW 074S03//COD 3// VER/DBM
8797 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-03-01 10:32 | 2013-03-01 14:05 | 5 | 213 | 4864521 | 1065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEW CUTOUT FAILED GOT GREG SHOUSE CREW COMMING TO HELP IN ABOUT HOUR/ MD FILED ON FUSE`S ONLY 1 HERE VER/KEP IDC XXXX
8798 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-07-19 17:15 | 2012-07-20 11:00 | 1 | 1065 | 4774371 | 1065 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ON SITE BAD TRANSFORMER 15 KVA 19.9. 2 MEN AND MATERIAL HANDLER..HWY 476 TO RUSSEL BR. TOP OF MOUNTAIN TURN RT THOUGH COAL PLANT TURN RIGHT UNDER CONVE BELT. RELEASED BY CREW 077H07 COD-1 ISO TF 37830031D10092 VER/HFP L3/HFP IDC XXXX
8799 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-02-02 05:59 | 2009-02-02 10:25 | 4 | 266 | 54397-1 | 1064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH SERVICER AT REG TIME. RELEASED BY CREW 077S10 // ADDD 1 FROM 54935 IDC XXXX
8800 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-04-13 19:04 | 2015-04-13 20:00 | 19 | 56 | 4313961 | 1064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 40T RESTORED @ 116B183 @ 20:00, 19.9 ARRESSTER @ 116-648 IN CLEAR.. CHANGE W/ BIG BKT/ ISO 38830116B00183/ COD 19
8801 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-06-16 14:51 | 2015-06-16 19:17 | 4 | 266 | 4580481 | 1064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HAVE A BAD 25 KVA XFMR WILL NEED 35.5 OR 50 KVA ,FOREMAN 1 A LINEMAN& 2 C LINEMAN. MATERIAL HANDLER BUT IT IS NOT TRUCK ACCESSABLE. REPLACED XFMR & POOWER RESTORED @19:17// VER/ ADH
8802 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2016-05-09 09:00 | 2016-05-09 09:38 | 28 | 38 | 4188341 | 1064 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON SECONDARY SIDE OF TRANSF GOING BAD WILL REWORK 5-9-16 NO POWER OFF RELEASED BY CREW 077S03//NO OUTAGE TILL TRANS OPENED//CONNECTION ON SECONDARY SIDE OF TRANSF GOING BAD WILL REWORK 5-9-16 NO POWER OFF === REPAIRED CONNECTION ON TRANSF === OPEN TRANSF AT 9:00 TO 9:38 === VER/CRB AJB
8803 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2008-10-16 16:24 | 2008-10-16 21:59 | 14 | 335 | 56267-1 | 1063 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 26820751 ///, ISOLATED @ POLE 39831000A00276 CLOSED FUSE @ FOUND POLE 1000-277, TO BE BURNTED OFF, IT IS A 404 POLE, NEED CUTOUT AND ARRESTOR, EVERYTHING ELSE WILL WORK BACK, I HAVE LOOP CUT ON POLE 1000-276, AND LINE IS GROUNDED, THERE ALSO, HAVE ALL CUSTOMER BACK ON AT 17:20, WITH THE EXPECTION OF MAYNARD ACE HARDWARE THIS IS WHERE THE POLE IS BURNTED, CAN USE TRUCKS ON THIS, SEND CREW TO REPAIRSTS WR # 26820751 /// FAULT POLE 39831000A00277, ISOLATED @ PO IDC XXXX
8804 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-10-20 21:03 | 2016-10-20 23:01 | 9 | 118 | 4034231 | 1062 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE IS OPEN ON 600-28 PATROLLING LINE///FOUND AND REPLACED BAD CUTOUT ON 600-96, APR AT 2301 CLOSE TICKET. D WEST VER/CRB L3/HFP XXXHFP
8805 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-10-04 19:13 | 2012-10-04 22:10 | 6 | 177 | 4115471 | 1062 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HEMLEPP & PHELPS & MCCANN//// FETR 22:15//JEH/REPAIRS COMPLETE ALL POWER REST.@ 22:10 JEH COD-6 ISO SO 38830044C45596 VER/HFP L3/HFP IDC XXXX
8806 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-03-25 03:46 | 2016-03-25 09:40 | 3 | 354 | 4880691 | 1062 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, WILL GO IN AND GET ONE, POWER RESTORED/ ISO 37830230B00102/ COD 3/ VER/BOW
8807 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-02-15 18:18 | 2010-02-16 12:00 | 1 | 1062 | 58175-1 | 1062 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SEND TO RAYBURN UNDERGROUND GOING BAD AGAIN COULDN`T GET TO DUE TO BAD ROAD CALLED CUSTOMER THEY HAD LEFT ALREADY AND AGREED THAT IT WOULD BE BETTER TO WAIT TILL NEXT DAY//BAD CONNECTION ON SEC POLE..BLR// VER/DBM IDC XXXX
8808 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-11-22 01:44 | 2008-11-22 10:35 | 2 | 531 | 50866-1 | 1062 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3201001// CREW WILL GET FIRST THING IN MORNING / WILL HAVE TO REPLACE TRANSFORMER THAT IS ON A HILL// RELEASED BY CREW 080S01 SHOULD BE SERVED ON POLE 38821110B00087 2 CUSTOMERS IDC XXXX
8809 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-01-21 08:35 | 2012-01-21 13:00 | 4 | 265 | 4279791 | 1060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED 3 MEN 25 KVA 120/240 - 7200 1 BUSHING MATERIAL HANDLER & POLY PADS TO BACK TRUCK ON. RELEASED BY CREW 074S04 XFMR CHANGED ON AT 13:00 D SAMMONS ///VER/CRB IDC XXXX
8810 | South Williamson | 3200302 | BELFRY | TOLER | 2012-12-09 15:58 | 2012-12-09 19:30 | 5 | 212 | 4454691 | 1060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SIDE-TAP FUSE OUT,NO EVIDENT REASON,WILL RE-FUSE//ISO 38821063A00009//MD FILED//COD 5//BAD DE INSULATOR ON POLE 94,NEED 1 MAN,BUCKET,DE INSULTR// // VER/TOM L3/TOM IDC XXXX
8811 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-07-26 07:25 | 2009-07-26 16:15 | 2 | 530 | 63953-1 | 1060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008701// WR 30911825 POLE 115-423 BAD 75 KVA 7200 TRUCK TO POLE ALSO NEED CUTOUT 1- COMM. CUST POLE 115-422 25T ON 10:45 RELEASED BY CREW 078S08 VER/KEP L3/KEP IDC XXXX
8812 | Pikeville | 3407101 | TOPMOST | DEMA | 2013-12-29 13:30 | 2013-12-29 15:16 | 10 | 106 | H4209891 | 1060 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TAP AT POLE 35 AT 13:17 (3 CUST), OPENED AT POLE 37830113000099 AT 13:30 (10 CUST)OPENED TAP AT POLE 35 AT 13:17, OPENED AT POLE 37830113000099 AT 13:30 . EXTINGUISHED FIRE AND REPLACED CUTOUT AT POLE 35, RESTORED ALL CUSTOMERS AT POLE 99 AT 15:16 , ALL WORK COMPLETE / GXJ DUP OF 4209891 VER/HFP L3/HFP
8813 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-10-03 05:04 | 2009-10-03 10:57 | 3 | 353 | 66063-1 | 1059 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR#32030586 / SECONDARY DOWN BETWEEN 162B-105 & 162B-6 / COD-3 / NEED CREW /WR#32030586 / #4 SOLID COPPER SEC. DOWN FROM POLE 162-105 TO 162- 6, NO TRUCKS TO POLE. NEED LINE CREW TO PUT BACK UP.WR#32030586 / #4 SOLID COPPER SEC. DOWN FROM POLE 162-105 TO 162- 6, NO TRUCKS TO POLE. NEED LINE CREW TO PUT BACK UP. RELEASED BY CREW 078S01/CREW ON SITE/FETR1200/VEM/REPAIRS MADE AND ALL CUST RESTORED 1057/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
8814 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-08-12 00:52 | 2010-08-12 06:45 | 3 | 353 | 53258-1 | 1059 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT STS BROKE CUTOUT RELEASED BY CREW 077S05 VER/KEP L3/KEP
8815 | Hazard | 3302704 | HAZARD | KENMONT | 2012-04-22 15:37 | 2012-04-22 21:30 | 3 | 353 | 4694371 | 1059 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT WENT BAD AND BURN TOP OF POLE OFF == NEED 4 MEN == ALSO LINE FUSE OUT ON POLE 37830321A00369 == REPLACED POLE === REFUSED LINE POWER OK VER/TOM L/3 TOM IDC XXXX
8816 | Hazard | 3308002 | JACKSON | PANBOWL | 2018-02-11 18:07 | 2018-02-12 11:45 | 1 | 1058 | 4831391 | 1058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WORK 02/12 HIGH WATER HAZARDS IN AREA part out// HAD ELECTRICIAN OUT. PROBLEM AT POLE:Directions-LAST HOUSE ON RIGHT ON LAKESIDE/1070 lakeside dr/ hold vtil tomorrow need bucket/possible bad ug customer agreeed Released by crew 077S06. bad connection on xfmr/ ISO 38831059D00122/ COD 1
8817 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-02-01 12:02 | 2009-02-01 20:51 | 2 | 529 | 54021-1 | 1058 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | //VER/CRB
8818 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2020-01-09 14:34 | 2020-01-09 17:05 | 7 | 151 | 4228621 | 1057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Have one span of wre down, Will need a couple of men to help get it pulled back up to me,Looks lke it came out of sleeve will make repairs.Restored service to the customers at pole 191-401 at a tme of 17:05
8819 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2011-05-12 19:19 | 2011-05-12 21:50 | 7 | 151 | 4078661 | 1057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS. 50KVA VER/HFP L3/HFP
8820 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2021-02-14 18:18 | 2021-02-15 11:55 | 1 | 1057 | 4056241 | 1057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Hold till tomorrow pre. G.Combs Released by crew 077S03 bad cutout on pole 37830321D00458, restored power at 11:55..
8821 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2015-08-03 21:56 | 2015-08-04 00:27 | 7 | 151 | 4972111 | 1057 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | P 38830223000109 BAD LA SERVICER TO CHANGE// 25T IN @ 00:27 PLEASE CLOSE TICKET LRM VER/CRB L3/HFP XXXHFP
8822 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2017-02-02 03:37 | 2017-02-02 03:48 | 96 | 11 | 4353561 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BROKE RISER FELL ACROSS BYPASS/SAME POLE DIFFERENT TAPS THIS IS TAP TOWARDS REG 228 "B" PHASE/ CUSTOMERS ARE ON TILL RECL OPENED (@0337) TO MAKE REPAIRS/ THIS WAS DISCOVERED WHILE SERVICER WAS CHECKING RECL FOR OUTGAGE UP COOKEY FORK 4353431 NO CONNECTION BETWEEN OUTAGES/RESTORED 0348 VER/KEP L3/HFP XXXHFP AJB
8823 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-05-30 10:04 | 2015-05-30 11:40 | 11 | 96 | 4484671 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OPEN AT POLE 426-106, WILL BE PATROLLING. PATROLLED LINE, EVERYTHING OK, I THINK FUSE PULLED INTO. /CLOSED L/F BACK IN AT 1140./COD11// VER/ ADH
8824 | Hazard | 3420001 | SOFT SHELL | VEST | 2022-11-18 09:19 | 2022-11-18 15:35 | 6 | 376 | 4158021 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Secondary line down at pole 37830156000256. 12T LF Open at 37830156000015 and TR Open at 37830156B20325. LF Close at -1135 ///// TR - Close at - XXXX. (LF COD 5) (TR COD 1)line fuse on pole 156-15 restored at 11:35, bad 25 KVA bucket truck access 19.9 pole 156-325 Released by crew 077H05
8825 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-09-29 08:08 | 2009-09-29 10:20 | 8 | 132 | 53562-1 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ROTTEN WIRE//VER/CRB
8826 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2011-05-14 07:08 | 2011-05-14 11:32 | 4 | 264 | 4089381 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE IS OPEN ON POLE 478-108 PATROLLING LINE; PATROLLED LINE NOTHING FOUND FUSE APPEARED LIKE IT HAD PULLED LOOSE APR AT 1132 CLOSE TICKET
8827 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-03-04 00:54 | 2016-03-04 02:00 | 16 | 66 | 4813141 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RELATED TO ORDER 4809451 - CREW HAD TO OPEN RECL @ 0103 TO MAKE REPAIRS IN THAT ORDER // SPLICE FAILED // COD-16 ISO OCR 38820865A00020
8828 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2020-07-04 23:12 | 2020-07-05 08:00 | 2 | 528 | 4111061 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Need to go to plant 4040 Winchester Ave for key/bad transformer 333 2 secondary bushnings 7200 277/480 Released by crew 078S03
8829 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-07-13 01:03 | 2010-07-13 06:49 | 6 | 346 | 65785-1 | 1056 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW NEEDED BROKE CUTOUT ON POLE 572-70 L, CREW WILL NEED 7200V ARRESTER CUTOUT AND FIBERGLASS BRACKET. NO TRUCK ACCESS. RELEASED BY CREW 078S02/WR#35958910/ COD-4 VER/HFP L3/HFP IDCC CDC92, CNT3, STP MISSING, PN83 XXXX
8830 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-07-12 04:55 | 2011-07-12 22:30 | 1 | 1055 | 4523891 | 1055 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRANSFORMER FUSE BLOWN ON 19.9 KV TRANSFORMER. NEED A SERVICEMAN TO REFUSE THE CUTOUT ON POLE M38831126B00575. I DONT THINK A SERVICEMANS BUCKET WILL REACH THE TRANSFORMER. RELEASED BY CREW 074E09.// POWER RESTORED @ 2230 PER MIKE COLEMAN // COD 1 //AED CREATED// VER/DBM
8831 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2015-08-14 14:37 | 2015-08-14 15:39 | 17 | 62 | 4135161 | 1054 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | OPENED RISER POLE 37830047B00155 TO SAFELEY CHANGE OUT PADMOUNT 37830047B00203//SEE PO 4129861 VER/CRB L3/HFP HFPC CCO FP37830047B00155
8832 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2020-12-08 04:56 | 2020-12-08 09:55 | 26 | 299 | 4752981 | 1054 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | //. stinger had come out of step down on pole 376-C-18. repairs made. opened step downs @ 09:36 closed @ 09:55.. power restored
8833 | Pikeville | 3421001 | BREAKS | CITY | 2016-02-27 11:33 | 2016-02-27 13:30 | 9 | 117 | 4782201 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LEFT HAND PHASE CUTOUT DOOR IS BURNED UP ON POLE 37820243D00230. I OPENED THE MIDDLE AND RIGHT HAND PHASE AT 13:18, AND CLOSED ALL THREE AT 13:30./9 CUSTOMERS TOTAL/BELIEVE A PHASE, SO 5 CUSTOMER PART POWER ORIGNALLY AND 4 ALL OUT.,// VER/ ADH
8834 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-04-28 16:11 | 2014-04-28 17:32 | 13 | 81 | 4642651 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 520-2, BAD CUTOUT ON POLE 520-44, REPLACED CUTOUT RESTORED POWER AT 17:32 /// COD-13 ISO LF 37830520000002 VER/HFP L3/HFP IDC XXXX
8835 | Hazard | 3302703 | HAZARD | HAZARD | 2014-02-11 10:38 | 2014-02-11 12:35 | 9 | 117 | 4373061 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER LEADS BURNT UP,...REPLACED LEADS AND REMADE ALL CONNECTIONS. VER/TOM L3/TOM
8836 | Pikeville | 3401001 | ELWOOD | DORTON | 2016-02-15 12:03 | 2016-02-15 14:00 | 9 | 117 | 4697261 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE FUSE BLOWN/////WILL PATROL...//COD 9 FROM THE BEGINNING OF OUTAGE//MADE MDC TO SHOW CORRECT PHASING ON TRANS 287-38B PHASE FUSE BLOWN/////WILL PATROL...FOUND BAD 7200 CUTOUT BAD ON POLE 287-36 THAT FEEDS A DD LIGHT WHICH CAUSED LINE FUSE TO BLOW... LIFTED HOT TAP TO GET CUSTOMERS BACK ON.PLEASE SEND COPY TO TIM HALL AND STEVE RAY..CLOSED FUSE BACK IN @ 14:00.//SENT TO LINE CREW DEPT VER/CRB L/3 CRB
8837 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-04-05 20:29 | 2021-04-06 14:02 | 1 | 1053 | 4421561 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | per customer, they dont want us to come until tomorrow mornign after 0730 // no one there now // --38830358000049 cntr phase c/o riser off broke need big bucket crew req Released by crew 078S01 crew on site fetr 14:30
8838 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2018-03-19 21:30 | 2018-03-20 03:21 | 3 | 351 | 4028511 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | all customers partial power originally opened xfmr @ 2233/ Bad 25 kva. 7200, only reading 60v on one leg and 120 on the other. crew required/crew on site/FETR 0345/vem/repairs made and all cust restored 0321/please close ticket/thanks/vem
8839 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-11-12 14:14 | 2013-11-12 20:05 | 3 | 351 | 4032551 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | UP STREAM DEVICE OUT PATROLING , FOUND BAD 25 KVA 7200 SINGLE BUSHING NEED CREW REQ, PERFORMED THREE DIFFERENT VOLTAGE CHECKS KWB THEY ARE GOING TO LEAVE GATE UNLOCK TONIGHT RELEASED BY CREW 078S09 VER/CRB L3/HFP HFPC CDC81
8840 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2018-01-09 04:56 | 2018-01-09 10:47 | 3 | 351 | 4723151 | 1053 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c/o broke -crew req-ds010918 //,replaced cutout all cust restored @ 1047 please close ticket thanks.bt // ENTERED MD COD-3 ISO LF 38830262000111
8841 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2013-05-05 19:06 | 2013-05-05 23:29 | 4 | 263 | 4074261 | 1052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 425-240 ISOLATED ON POLE 425-139, MADE REPAIRS RESTORED POWER AT 23:29 VER/TOM L3/TOM IDC FIRST CALL WAS FULL POWER BUT DO NOT KNOW WHEN IT WENT OUT XXXX
8842 | Hazard | 3310502 | HADDIX | CANOE | 2011-04-01 07:59 | 2011-04-01 16:45 | 2 | 526 | 61022-1 | 1052 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER// WR#39398409BAD TRANSFORMER--//MAIN LINE OFF FROM 1530 TILL 1645 // VER/KEP IDC XXXX
8843 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2009-02-06 17:29 | 2009-02-07 11:00 | 1 | 1051 | 56304-1 | 1051 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | MAY HAVE A BAD INSULATOR ON POLE 38830399000049, SEND TO BOB REYNOLDS RELEASED BY CREW 078S05//NOT ABLE TO GET TO THIS TONIGHT, BAD ROAD, NEED SIX WHEELER//BOB REYNOLDS CALLED CUSTOMER AND CUSTOMER SAID HE HAS HEAT SO HE WAS FINE IF WE GOT A CREW ON THIS....... REMOVED TREE FROM 399-51/REPLACED 15T FUSE ON 399-48 BLR// VER/TOM L3/TOM IDC XXXX
8844 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2011-05-11 17:49 | 2011-05-12 11:20 | 1 | 1051 | 4065411 | 1051 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONECTION ON POLE, ONE CUST. HAD PART POWER IDC CHANGED COUNT FROM 15 XXXX
8845 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2009-03-20 04:16 | 2009-03-20 10:06 | 3 | 350 | 60238-1 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3403302 -THINK XFMER FUSE IS OUT GOING TO TRY . LEAD BURNT OUT OF THE TOP OF CUTOUT GOING TO NEED SOME HELP TO CLOSE TO PRIMARY WILL HAVE TO HAVE AN OUTAGE. OPENED AT POLE 954-908 AT 9:20 CLOSED AT 10:06//(CREATED OTHER ORDER TO SHOW OUTAGED CUSTOMERS//COD 3// VER/DBM IDC XXXX
8846 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-01-10 21:30 | 2016-01-10 23:15 | 10 | 105 | 4604491 | 1050 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | COD 5 FROM BEGINNING OF OUTAGE//LEG ON XFMR BURNT OPEN,, ALL REPAIRS MADE POWER BACK ON///OPENED XFMR AT 22:55 CLOSED IN AT 23:15
8847 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2010-02-02 09:50 | 2010-02-02 12:20 | 7 | 150 | 62277-1 | 1050 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | NEUT RISER BROKE IN ONE OF THE XFMRS WILL CALL FOR WIRE -----REPLACED RISER//VER/CRB IDC XXXX
8848 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2014-07-17 11:45 | 2014-07-17 12:35 | 21 | 50 | H4256051 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 114-184 BAD CONN. ON SEC. POLE ON HILL SIDE NEED CREW.CUST HAS MAIN BRK OFF.TALK TO CUST WHEN CREW HAS COMPLTED THEIR WORKPOLE 114-184 BAD CONN. ON SEC. POLE ON HILL SIDE-- NEED CREW RELEASED BY CREW 078S08---OPENED 114-149@ 11:45 - CLOSED @ 12:35 REPLACED CUTOUT ON POLE 114-10 RELEASED BY CREW 078H01 VER/CRB AJB
8849 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2020-03-26 10:32 | 2020-03-26 10:42 | 105 | 10 | 4511971 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | SHORT OUTAGE TO ISOLATE DEFECTIVE REGULATOR ON POLE 37830021000119 ¦¦ COD-105 OFF@1032 ON@1042
8850 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-07-24 21:59 | 2016-07-25 00:29 | 7 | 150 | 4675081 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07--CREW ON SITE--BAD XFMR ON 69-5533--LF OPEN ON 69-5529--GOING TO LEAVE LF OPEN DUE TO TIGHT SPACING ON XFMR POLE--15T LF IN ON 69-5529 AT 00:29---CHANGED 15KVA TO 25KVA--VOLT CK GOOD---TBL TKT COMP--RMV VER/ARN
8851 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-10-25 18:20 | 2015-10-25 21:50 | 5 | 210 | 4375541 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT POLE 24-737 OPENED LOOPS AT 24-709 TO ISOLATE PUT OUT FIRE MADE REPAIRS AND RESTORED AT 2150 VER/KEP L3/HFP XXXHFP
8852 | Hazard | 3309302 | VICCO | JEFF | 2011-05-20 04:16 | 2011-05-20 10:06 | 3 | 350 | 4115661 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL DISPATCH SERVICER AT REG WORK TIME AFTER DAYLIGHT. BAD 25 KVA 19.9 == U CAN GET TRUCK TO IT BUT U HAVE TO SET UP IN ROAD == NEED FLAGERS == RELEASED BY CREW 077S03 REPLACED XFMR RESTORED POWER AT 1006 077H01//COD 3// VER/DBM IDC XXXX
8853 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-06-24 22:03 | 2010-06-25 01:33 | 5 | 210 | 57180-1 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASING.....TRUCK BROKE DOWN RELEASED BY CREW 079H08 CUTOUT IS BAD, WILL HAVE TO OPEN LINE TO CHANGE. OPENED FUSE ON POLE 9-C-190./VER/CRB IDCC TRANSF ONLY INITIALLY CNT28 XXXX
8854 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-10-28 04:20 | 2014-10-28 04:34 | 75 | 14 | H4666021 | 1050 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 37830235000175 HOT LINE CLAMP BURNED OPEN ON A PHASE, OPENED 3 PHASE SECTIONALIZER AT POLE 175 AT 04:20 INTERRUPTING B & C PHASES TO REPAIR . ALL REPAIRS COMPLETE / ALL CUSTOMERS ON AT 04:34 // GXJ // DUP OF 4666021 FOR B & C PHASE OUTAGE - 75 CUST // VER/HFP L3/HFP AJB
8855 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2012-07-15 19:43 | 2012-07-16 04:27 | 2 | 524 | 4734321 | 1048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PREVIOUS OUTAGE WAS `CAUSE UNKNOWN`//CALLED CUSTOMER AND THIS WAS RESTORED BUT IS OUT AGAIN//PREVIOUS OUTAGE WAS CAUSE UNKNOWN//CALLED CUSTOMER AND THIS WAS RESTORED BUT IS OUT AGAIN//,BAD XFMER CREW REQ TRUCK OKPREVIOUS OUTAGE WAS CAUSE UNKNOWN//CALLED CUSTOMER AND THIS WAS RESTORED BUT IS OUT AGAIN//,BAD XFMER CREW REQ TRUCK OK WATCH FOR DOWN GUY CROSSING ROAD AT POLE RELEASED BY CREW 078H04PREVIOUS OUTAGE WAS CAUSE UNKNOWN//CALLED CUSTOMER AND THIS WAS RESTORED BUT IS OUT AGAIN//PREVIOUS OUT VER/ARN
8856 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-05-16 19:33 | 2017-05-16 23:55 | 4 | 262 | 4806161 | 1048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 NO TRUCKS YARD DOG IF FIXED RELEASED BY CREW 078S03..CREW ON SITE,,REPLACED XFMR,, ALL POWER RESTORED VER/ARN
8857 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-02-02 17:23 | 2013-02-03 10:51 | 1 | 1048 | 4787011 | 1048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 25KVA XFORMER, TRUCKS TO POLE. RELEASED BY CREW 078S01//WILL BE WORKED IN DAYLIGHT PER CUSTOMER/CREW ON SITE/FETR 1130/VEM/REPAIRS MADE AND POWER RESTORED AT 1051/PLEASE CLOSE TICKET/THANKS/VEM //VER/GAH IDC XXXX
8858 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-08-22 20:58 | 2014-08-23 01:20 | 4 | 262 | 4408241 | 1048 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 94-6628 BAD CUTOUT 10T FUSE POLE 94-6662 20T LINE FUSE
8859 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-09-08 18:13 | 2012-09-09 11:40 | 1 | 1047 | 4032221 | 1047 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED /POLE BURNT OFF/ISOLATED ON 195-21 HOTTAP/CAN DO A CUTOFF AND LOWER TRANSFORMER BRING SMALL BUCKET A SERVICE 4X4 DRIVE TO POLE PROPERTY OWNER OK /2 MAN MANUAL TREE CREW ALSO RELEASED BY CREW 078S03 //J. LINKOUS, D. RUGGLES, M. PHELPS, B. REYNOLDS // TECH - B. PARSONS (POWER RESTORED AT 11:40) //VER/GAH IDC XXXX
8860 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-07-25 23:50 | 2008-07-26 05:39 | 3 | 349 | 60368-1 | 1047 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008701 BAD 50 NEED 75KVA//3008701//19.9//STS#25443577 RELEASED BY CREW 078S08/CREW ON SITE /FETR0630/DIFFICULT LOCATION/VEM/REPAIRS MADE ALL CUST RESTORED 0539/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
8861 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-12-18 08:57 | 2016-12-18 17:40 | 2 | 523 | 4213281 | 1046 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE 4217381*** LINE FUSE CUTOUT BROKEN ON POLE 236-15... WILL NEED 12KV CUTOUT AND LINE CREW TO MAKE REPAIRS.WILL HAVE TO OPEN STEP-DOWN ON POLE 236-02 TO MAKE REPAIRS THIS IS NON-TRUCK APPROACH../ NO TAGS AND GROUNDS..REPAIRS COMPLETE..ISO 37830236000015/ COD 2/ 1740/ VER/BOW
8862 | Hazard | 3303902 | LESLIE | WOOTON | 2015-03-10 13:58 | 2015-03-10 15:33 | 11 | 95 | 4177841 | 1045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGE CUTOUT ON 486--160 OPENED ON POLE 486 58 AT 13:58 CLOSED BACK AT 15:33/ ISO 37830486000058/ COD 11/ VER/BOW
8863 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2012-07-25 17:58 | 2012-07-25 21:27 | 5 | 209 | 4828521 | 1045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WIRE HAS BROKEN AT POLE 48-291. WIRE BURNED INTO UNDER A SQUEEZE -ON. I AM GOING TO CALL FOR HELP. WE WILL HAVE TO OPEN RECLOSERS ON POLE 48-1165 WHEN HELP GETS HERE FOR APROX. 45 MIN. THERE IS NOTHING OPEN OR BLOWN AT THIS TIME. WIRE IS HANGING IN THE CLEAR.//PHASE A ONLY FROM POLE 37830048C10291//COD 5. WE OPENED RECLOSERS AT 20:55 AND CLOSED 21:27. VER/ARN
8864 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2012-09-25 15:10 | 2012-09-25 16:05 | 19 | 55 | 4086361 | 1045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED UP LINE FUSE TO PUT OUT POLE FIRE  CUTOUT HAS BROKEN DOWN ON POLE 38821017A20371 AND CAUGHT POLE ON FIRE  GOING TO OPEN LINE FUSE ON POLE 38821017A20255 TO MAKE REPAIRS  OPENED LINE FUSE @ 15:10  REPAIRS COMPLETE & POWER RESTORED @ 16:05 ///VER/CRB L/3 CRB IDC XXXX
8865 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-01-24 11:21 | 2019-01-24 14:50 | 5 | 209 | 4717251 | 1045 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | oh splice bad in midspan, going to have transformer open to repair it so got virgil coming to help were it wont b off so long
8866 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-05-27 00:06 | 2015-05-27 03:35 | 5 | 209 | 4469621 | 1045 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT NEED AWP FLAGGERS AND LINE CREW CHANGED BAD 7200 CUTOUT COD-5 ISO LF 39831122A00030 VER/HFP L3/HFP
8867 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2012-03-15 16:08 | 2012-03-15 17:35 | 12 | 87 | 4584751 | 1044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLING LINE REMOVED CLAMP ON POLE 222B-305 GOING TO POLE 222B-381 NO CUSTOMERS ON THIS SECTION OF LINE//COD 12// VER/DBM IDC XXXX
8868 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-10-24 13:27 | 2016-10-24 17:48 | 4 | 261 | 4049141 | 1044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ONE LEG OUT ONCSP TRANS ON 1013-C-113 NEED 25 KCA 7200 STANDOFF BRACKET AND CUTOUT ONE MAN AND MATERIAL HANDLER TRK RELEASED BY CREW 079H03/// CHANGING X-FMR VER/AWD
8869 | Hazard | 3302703 | HAZARD | HAZARD | 2012-07-17 14:39 | 2012-07-17 16:35 | 9 | 116 | 4749421 | 1044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 077S04 COD-9 ISO PO 37830296A30710 VER/HFP L3/HFP
8870 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-09-10 19:07 | 2022-09-10 23:58 | 16 | 291 | 4863331 | 1044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 674-B-9002///no truck access//top of cutout hanging down only inches from bracket//will have to open line fuse on pole 674-B-97 before climbing to change out//need line crew //opened fuse 38820674B00097 at 2325 // closed at 2357 // cod 2 + 14
8871 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-07-19 08:11 | 2012-07-19 11:05 | 6 | 174 | 4765731 | 1044 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN. REPLACED BAD CUTOUT AND ARRESTOR, POWER RESTORED AT 11:05 VER/KEP
8872 | South Williamson | 3200302 | BELFRY | TOLER | 2016-04-22 18:49 | 2016-04-22 21:18 | 7 | 149 | 4117521 | 1043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE ON 38820990D20415. LIFTING TAP ON 38820990D20467 TO ISOLATE.CUTOUT FAILED ON 990D 415 BURNING OFF TOP OF POLE I CAN MAKE REPAIRSCUTOUT FAILED ON 990D 415 BURNING OFF TOP OF POLE I CAN MAKE REPAIRS OPENED LINE FUSE ON 990D467 AT 20:00 AND RESTORED POWER AT 21:18 COD 5 VER/AWD
8873 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-06-19 20:03 | 2011-06-20 13:26 | 1 | 1043 | 4346241 | 1043 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | ONE LEG OF UNDERGROUND SERVICE BAD///GOOD VOLTAGE AT XFMR//ONLY ONE LEG AT METER// NEED TO REPAIR UG CONDUCTOR//CREW REQUIRED//CUSTOMER SAID OK TO WAIT TIL FIRST THING IN MORNING// SDB / JOEY REED TO MAKE REPAIRS ON 6-20-11. INSTALLED TEMPORARY OVERHEAD SERVICE. POSSIBLY UNDER CONCRETE SIDEWALK.//VER/CRB
8874 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2009-08-05 07:10 | 2009-08-05 09:39 | 7 | 149 | 61129-1 | 1043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | PRIM WIRE DOWN BETW 51-143 & 51-141,CUT LOOP AT POLE 51-143 TO CLEAR.WILL GO RE-FUSE LINE AND GET EVERYBODY ONWIRE DOWN AT 51-143,CUT LOOP THERE,RE-FUSED AND RESTORED VER/KEP L3/KEP IDC XXXX
8875 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-10-22 06:26 | 2016-10-22 08:55 | 7 | 149 | 4043571 | 1043 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT START TIME 10-22 POLE 91-309 BAD 19.9 CUTOUT 25T LINE FUSE/ ISO 38830091D00309/ COD 7 VER/TOM L3/TOM
8876 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-02-23 16:44 | 2017-02-24 10:05 | 1 | 1041 | 4417301 | 1041 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ***SEE 4418031*** WIRE BROKE IN CONNECTION ===TALKED CUST HE SAIDED BE OK TO WORK IN DAY LIGHT HOURS BARN IS ONLY THING OFF RELEASED BY CREW 077S03WIRE BROKE IN CONNECTION ===TALKED CUST HE SAIDED BE OK TO WORK IN DAY LIGHT HOURS BARN IS ONLY THING OFF === REPAIRED LINE OPEN LINE FUSE AT 8:15 CLOSED 10:05 POWER OK/ ISO 37830173B00200/ COD 1/ L3/HFP XXXHFP
8877 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-09-05 18:20 | 2022-09-06 11:41 | 1 | 1041 | 4841861 | 1041 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CUSTOMER//NO ONE LIVES HERE, CAN WAIT TILL THE MORNING//restored @ 1141
8878 | Whitesburg | 3401301 | FLEMING | NEON | 2012-12-05 03:43 | 2012-12-05 04:03 | 52 | 20 | H4443151 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED POLE 331-D-63 // OPENED RECL POLE 331-D-229 @ 0343 //REPLACED CUTOUT & CLOSED RECL POLE 331-D-229 @ 0403 // //VER/GAH IDC XXXX
8879 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-05-26 02:53 | 2008-05-26 03:58 | 16 | 65 | H51249-1 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3008702 - AT 0253 OPENED RECLOSER ON POLE 188-180 TO MAKE REPAIRS INTERRUPTING 16 ADDITIONAL CUSTOMERS// AT 0358 CLOSED RECLOSER188-180// PRI AND NEUTRAL DOWN ON POLE ON POLE 188-201 WILL HAVE TO OPEN UP REC 188-180 WHEN CREW ARRIVES LINE DID NOT OPEN BECACSE PRI HAS INSLATED WIRE STILL HOT WHEN ARRIVED3008702 -PRI AND NEUTRAL DOWN ON POLE ON POLE 188-201 WILL HAVE TO OPEN UP REC 188-180 WHEN CREW ARRIVES LINE DID NOT OPEN BECACSE PRI HAS INSLATED WIR SEE ALSO 51249-1 VER/LDA IDC XXXX
8880 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2015-01-18 12:22 | 2015-01-18 13:02 | 26 | 40 | 4942571 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNT ONE CROSSARM OF DOUBLE ARMS INTO CUTOUT HANGING IN AIR 38830070B43594----- WILL OPEN FUSES ON POLE 38830070B43590@ 12:30 TO MAKE REPAIRS VER/CRB L3/HFP XXX AJB
8881 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-06-18 22:53 | 2009-06-19 02:21 | 5 | 208 | 50783-1 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CALLED CREW TO HELP LOCATE FAULTY CABLE WILL MAKE TEMP REPAIRS TO RESTORE PUT IN ABNORMAL DATA BASE UNTILL CREW MAKE REPAIRS ON LATER DATE CABLE BAD FROM 1073-2624 TO 1073-3618 TO NORMAL OPEN POINT NO BACK UP FEEDIF FUSE GOES OUT ON LOOP ARRESTOR ALSO NEED REPLACED ON BOTH FEEDS.//VER/CRB IDCC CDC83 XXXX
8882 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-04-23 07:50 | 2009-04-23 11:18 | 5 | 208 | 52580-1 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409301/// CUTOUT FAILED CAUSING POLE TO CATCH ON FIRE. LIFTED HOT-LINE CLAMP ON POLE 38830858C00029 AT 7:50 TO ISOLATE TROUBLE. POLE BURNT 2/3. CAN FRAME DOWN ON IT - CREW ENROUTE TO ASSIST. RELEASED BY CREW 076S02///// REPAIRS COMPLETE AT 11:18 ///VER/CRB IDCC PN535, CNT2 XXXX
8883 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-10-28 10:00 | 2014-10-28 12:10 | 8 | 130 | 4666771 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER. 7.2 KV,// COD 8 VER/HFP L3/HFP
8884 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-02-04 08:39 | 2009-02-04 12:59 | 4 | 260 | 55403-1 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3116702// NEED 50 KVA 50FT. 2/3 SERVICE RELEASED BY CREW 078S08//VER/CRB
8885 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2016-05-24 09:45 | 2016-05-24 11:55 | 8 | 130 | 4254351 | 1040 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | *** SEE 4253431***OPENED SWITCH 38831151D00536 TO ISOLATE TROUBLE ON POLE 38831151D00102/ OPENED @ 0945/ CLOSED 1155/ ISO 38831151D00536/ COD 8/ VER/BOW
8886 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2012-09-01 19:46 | 2012-09-02 13:05 | 1 | 1039 | 4992951 | 1039 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 19.9 XFMR. MANUAL ON HILLSIDE. GOING TO NEED R/W CREW AND 4 MAN LINE CREW.1ST DRIVEWAY ON LEFT GOING UP HILL ABOVE BEHIVE BR. NARROW DRIVEWAY BEST TO BACK UP NO PLACE TO TURN. HOLD TILL DAYLIGHT, ROUGH TERRAIN. RELEASED BY CREW 077S08 REPLACED TRANSFORMER RESTORED POWER AT 13 05 COD-1 TF 37830490000018 VER/HFP L3/HFP IDC XXXX
8887 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2012-11-16 05:59 | 2012-11-16 11:45 | 3 | 346 | 4401711 | 1038 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL DISPATCH AFTER 0730 START TIME. BAD 15 KVA, NO TRUCK. TALKED TO TIM HALL HE IS GETTING A CREW TOGETHER. GOING TO REPLACE WITH A 25 KVA RELEASED BY CREW 079H06//COD 3// VER/DBM IDCC PN58, CCOL XXXX
8888 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-01-10 08:09 | 2016-01-10 13:55 | 3 | 346 | 4598711 | 1038 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | MATERIAL REQUIRED: 25 KVA 120/240 7.2KV , ONE MAN WITH MATERIAL HANDLER RELEASED BY CREW 074S03MATERIAL REQUIRED: 25 KVA 120/240 7.2KV , ONE MAN WITH MATERIAL HANDLER . REPLACED 25 KVA TRANSFORMER WITH SAME , ALL WORK COMPLETE / GXJ VER/CRB
8889 | Paintsville | 3404002 | SPRINGFORK | 1PHASEDIS | 2012-12-06 17:13 | 2012-12-07 10:30 | 1 | 1037 | 4448071 | 1037 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | WILL HAVE SERVICER CHECK 12/07/12..GUY WIRE RUSTED INTO..RE SAGGED GUY .MARKED GUYS ON POLE WITH RIBBONS.//COD 1// VER/DBM IDC XXXX
8890 | Hazard | 3310502 | HADDIX | CANOE | 2015-02-17 18:26 | 2015-02-18 11:42 | 1 | 1036 | 4037331 | 1036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 37830169B00040 GOING TO HOLD UNTIL TOMORROW , NEED 15KVA 7200 XFMR . SMALLER TRUCK WOULD BE BETER TO GET ACROSS BRIDGE TO HANG XFMR ( 177 ) . RELEASED BY CREW 075H04//HELD PER BRUCE LINDON VER/HFP L3/HFP
8891 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2010-01-21 21:07 | 2010-01-22 05:45 | 2 | 518 | 57503-1 | 1036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33549460 // IDC XXXX
8892 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2014-01-07 10:56 | 2014-01-07 15:15 | 4 | 259 | 4250071 | 1036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED 15 KVA XFMR IS BAD ON 738-207. CUSTOMER GAVE PERMISSION TO GET TRUCK IN YARD BUT IM UNSURE IF IT WILL BE POSSIBLE SO IT MAY BE MANUAL. RELEASED BY CREW 076S02 //VER/GAH
8893 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2013-08-29 05:42 | 2013-08-29 10:01 | 4 | 259 | 4717631 | 1036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR HIGH SIDE RISER BROKEN (HOT LINE CLAMP) PL# 45C3-383///REPAIRED W/ NEW HOT LINE CLAMP///BACK ON 09:57///PWR CK OK///WRONG CUST COUNT AND POLE# ON TKT.. RELEASED BY CREW 078H16 COD 4 ISO TF 45C-383 ***CHANGE ISO POLE*** VER/SEF IDC XXXX
8894 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-06-17 17:56 | 2017-06-17 22:15 | 4 | 259 | 4988851 | 1036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV TRANSFORMER 19,9 KV,2 MAM LINE CREW AND BIG BUCKET RELEASED BY CREW 077H07//COD 4//
8895 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2013-09-03 14:33 | 2013-09-03 15:10 | 28 | 37 | 4816971 | 1036 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 284-85. I OPENED LINE FUSE AT 284-3 AT 14:33 TO CHANGE INSULATOR. WE CHANGED INSULATOR AND CLOSED LINE FUSE IN AT 15:10//COD 28// VER/DBM L3/HFP HFPC TOF1431 IDCC XXXX
8896 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2011-09-06 11:16 | 2011-09-06 17:01 | 3 | 345 | 4833291 | 1035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200, CAN UPGRADE TO AN 25 KVA NEED NEW CUT-OUT AND TRANSFORMER,CREW REQ, RELEASED BY CREW 078S09 //VER/CRB IDC XXXX
8897 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-11-23 08:34 | 2021-11-23 09:43 | 15 | 69 | 4117961 | 1035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Released by crew 079S01//line fuse open on 771-b-395//primary had pulled out of sleeve at ole 771-430//repairs made//restored @ 9:43//complete//em
8898 | Hazard | 3309302 | VICCO | JEFF | 2016-01-01 12:15 | 2016-01-01 18:00 | 3 | 345 | 4579931 | 1035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 SIDE OF CSP XFMR HAS NO VOLTAGE CALLING FOR CREW TO HELP CHANGE XFMR BAD MANUEL/ WAS PART POWER WHEN GOT THERE OPENED TRANSFORMER TO CHANGE IT/ OPENED TAP AT 16+57 CLOSED ALL BACK AT 1800/ ISO 37830322C00059/ COD 3/ VER/BOW
8899 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-03-19 19:00 | 2008-03-19 19:45 | 23 | 45 | 58860-1 | 1035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3311101// CREW OPENING UP RECLOSER TO REPLACE BROKEN INSULATOR AND RETIE PHASE WIRE/// RELATED TO ORDER 58814-1// VER/KEP IDC CCSCO, CNT124 1 CUSTOMER OUT AT 1748, CHANGED RECLOSER FROM TIME OFF 18:00 I BELIEVE WRONG TIME REPORTED BY FIELD, AND INCORRECT ISOLATING POLE, CHANGED ISOLATING FROM 37830459C00235 CREATED DUPLICATE FOR SINGLE CUSTOMER OUTAGE, PN235 XXXX
8900 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-06-29 14:36 | 2018-06-29 15:45 | 15 | 69 | 4689501 | 1035 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | burnt off riser on can, reapired both. restored
8901 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-03-04 13:41 | 2012-03-04 15:15 | 11 | 94 | 4544311 | 1034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE OUT //COD 12//LINE FUSE OUT,LINE FUSE OUT, WIRES ARE OUT OF SAG, PLEASE SEND JOB TO GLEN COMBS TO HAVE WIRES RE-SAGGED. THIS WILL EFFECT EMMALENA GRADE SCHOOL//COD 11// VER/DBM
8902 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-12-30 12:06 | 2011-12-30 13:40 | 11 | 94 | 4215651 | 1034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | REPLACING CROSSARMS ////VER/CRB IDC XXXX
8903 | Hazard | 3301401 | COMBS | COMBS | 2010-04-02 07:46 | 2010-04-02 09:20 | 11 | 94 | 57281-1 | 1034 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER BURNED OFF 7200VOLT XFMR CUTOUT// REPLACED CLAMP AND RISER // VER/KEP IDC XXXX
8904 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-07-18 07:12 | 2019-07-18 14:50 | 3 | 458 | 4726251 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutoout on pole 3831061A00165 cannot reach cutout call jim mullins and he is sending tim smith crew to change cutout, took clamp off going to put in line fuse in at 1159 Released by crew 077S05 Released by crew 077H02
8905 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2022-07-18 14:30 | 2022-07-18 18:48 | 4 | 258 | 4514451 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout. manual. need 19.9 cutout, arrester and bracket Released by crew 077S10
8906 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-10-14 22:38 | 2010-10-15 15:50 | 1 | 1032 | 59874-1 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CHECKED VOLTAGE AT XFORMER 125 PHASE TO GROUND, 250 PHASE TO GROUND. RELEASED BY CREW 078S01 /// VER/CRB IDC XXXX
8907 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2020-10-22 16:03 | 2020-10-22 18:55 | 6 | 172 | 4577001 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke xfm cutout. manual. crew on the way. restored 18:55
8908 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-07-21 11:54 | 2008-07-21 20:30 | 2 | 516 | 55764-1 | 1032 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 LEG OF 2 DIFF SERVICES PULLED OUT, 2 CUST ON XFMR HAVE POWER 2 HAVE PART POWER/ NEED SERVICER TO RE TAP, TRUCK ACCESSIBLE ON ST RELEASED BY CREW 075E01. VER/KEP IDCC CNT11 XXXX
8909 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-07-09 12:23 | 2009-07-09 15:15 | 6 | 172 | 65688-1 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE LINK BROKE.//COD 6// VER/DBM IDC XXXX
8910 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-06-29 10:27 | 2018-06-29 11:10 | 24 | 43 | 4688551 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACING BAD INSULATER ON POLE 37830238000098//OPENED L/F 37830238000264//opened @ 1027 closed @ 1110
8911 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2016-06-01 12:09 | 2016-06-01 13:35 | 12 | 86 | 4279491 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-7287 50T BAD CUTOUT DOOR REPLACED/ ISO 38830045D37287/ COD 12/ C PHASE ONLY/ VER/BOW
8912 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-01-05 07:27 | 2010-01-05 11:45 | 4 | 258 | 60738-1 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT WILL TRY IT TO SEE WHAT HAPPENS.//// FUSE CAME BACK OUT BAD 15 KVA TRANSFORMER WILL NEED TO GO BACK WITH A 37.5 4 200 AMP SERVICES ON THIS TRANSFORMER. ALSO NEED TO REPLACE OLD CUTOUT WITH A NEW ONE AND BRACKET FIBERGLASS TIM MCCOY RELEASED BY CREW 074H10 VER/KEP L3/KEP IDC XXXX
8913 | Hazard | 3310502 | HADDIX | CANOE | 2011-06-19 12:44 | 2011-06-19 17:02 | 4 | 258 | 4344361 | 1032 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER, GOT JOHN LAWSON COMMING WITH TRANSFORMER COD-4 ISO TF 37830052000004 VER/HFP L3/HFP IDC XXXX
8914 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-05-21 23:30 | 2015-05-22 08:05 | 2 | 515 | 4455231 | 1030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE WORKED AT THE START OF NORMAL SHIFT ON 5/21/2015. TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. CUTOUT IS BAD. I AM GOING TO CHANGE CUTOUT. I CHANGED CUTOUT VER/CRB
8915 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2020-08-04 12:17 | 2020-08-04 14:00 | 10 | 103 | 4285311 | 1030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced 2-4 triplex drop 100 ft.
8916 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-12-31 21:34 | 2019-01-01 01:00 | 5 | 206 | 4617351 | 1030 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | the primary came off of the insulator
8917 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2013-09-28 12:47 | 2013-09-28 18:30 | 3 | 343 | 4894681 | 1029 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/0 HENDRIX BURNED DOWN AT INSULATOR..1 PHASE DOWN.CREW CALLED..785-264 HANGING DOWN ON BOTH SIDES.2 FEET OFF GROUND. @ 1652 OPENED SWS AT POLE 785-D-331 ** SWS AT POLE 785-B-1571 OPENED ON MAP BY MISTAKE. .WIRE UP CLOSED SWICHES AT 18.30 /// **SHOULD BE CCEQF** SEE H4894681 VER/HFP L3/HFP IDCC CCO XXXX
8918 | Whitesburg | 3401301 | FLEMING | NEON | 2008-08-15 07:23 | 2008-08-15 09:50 | 7 | 147 | 52165-1 | 1029 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | 3401301// CLIMBED 2 POLES AND REPLACED ALL CONNECTIONS AND CUT CUDZU VINES // VER/TOM IDC XXXX
8919 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2008-02-26 06:58 | 2008-02-26 11:15 | 4 | 257 | 50413-1 | 1028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE AND HANGING FROM RISER. CREW ENROUTE TO ASSIST. REPAIRS COMPLETE. SH VER/HFP IDCC PN13 XXXX
8920 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-07-21 09:06 | 2015-07-21 13:23 | 4 | 257 | 4924431 | 1028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT BAD CUTOUT ON POLE 30-64, GOT HELP COMMING TO HELP CHANGE OUT VER/CRB
8921 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2010-08-14 21:07 | 2010-08-15 14:15 | 1 | 1028 | 54892-1 | 1028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07...POLE #38830020C45506 HAS AN OPEN DELTA 3 PHASE BANK ON IT...THE C/O FEEDING THE LIGHTING CAN IS OPEN...C/O ON POWER CAN IS STILL IN...SEE NO VISIBLE ISSUES WITH BANK OR SVC. DROP...NEED TO REFUSE LIGHTING CAN AND CHECK VOLTAGE...HAD CUSTOMER TURN MAIN BREAKERS OFF UNTIL WE RESTORE POWER....P.THOVSON RADIO 3342...CELL 831-2307 RELEASED BY CREW 078E06 COD-1 VER/HFP L3/HFP
8922 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2011-12-27 05:13 | 2011-12-27 09:30 | 4 | 257 | 4203831 | 1028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL DISPATCH AT REG WK TIME.--BROKEN FUSE ////VER/CRB IDC XXXX
8923 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-10-03 02:57 | 2015-10-03 11:31 | 2 | 514 | 4306921 | 1028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED APART ON POLE 375-351, REFUSED AT 1131.// VER/ ADH L3/HFP XXXHFP
8924 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2012-11-08 09:53 | 2012-11-08 14:10 | 4 | 257 | 4373601 | 1028 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10T FUSE OUT DUE TO BAD 50KVA TRASFORMER. I HAVE CALLED STEVE RAY HE WILL HEAD CREW THIS WAY TO CHANGE TRANSFORMER OUT RELEASED BY CREW 074S11 COD-4 ISO TF 37830042D00057 VER/HFP L3/HFP IDC XXXX
8925 | Hazard | 3302703 | HAZARD | HAZARD | 2011-07-31 18:53 | 2011-07-31 20:12 | 13 | 79 | 4648881 | 1027 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTIONS BAD--- OPENED TRANSFORMER AT 19:50 CLOSED AT 20:12, POWER RESTORED. VER/KEP IDC CHANGED TIME OFF FROM 1950, PART POWER PRIOR TO OPENING TRANSFORMER XXXX
8926 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2020-06-11 10:18 | 2020-06-11 16:00 | 3 | 342 | 4003441 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broken on pole 379-181, replaced & restored power at 1600
8927 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-01-15 22:22 | 2020-01-16 03:25 | 8 | 303 | 4309931 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | riser to bottom of cutout broke loose, no truck, crew reqd. has 2 taps on 3 phase pole that will need opened to make repairs. Released by crew 078H17
8928 | Pikeville | 3410602 | E.PRESTON | LANCER | 2011-06-06 13:36 | 2011-06-06 15:30 | 9 | 114 | 4241521 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE 10T FUSE BROKE. FUSED UP EVERYTHING OK. SEND COPY OF THIS TO ENG PIKEVILLE 50KAV HAS 9 CUST ON IT CHECK LOAD.//COD 9// VER/DBM IDC XXXX
8929 | Hazard | 3309003 | JEFF | VIPER | 2019-07-31 11:58 | 2019-07-31 17:40 | 3 | 342 | 4817041 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GAS WELLS OUT DUE TO WIRE OUT // restored @ 1740
8930 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-06-17 06:54 | 2016-06-17 12:36 | 3 | 342 | 4374281 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TANSFORMER NTA.. R/W BEING CUT NOW..REPLACED TRANSFORMER. INSTALLED CUTOUT AND STANDOFF BRACKET/ CANT SEE SEC POLE,NEEDS CUT SO PROBLEM CAN BE DETERMINED.WE HAVE A BAD 15 KVA CSP ON POLE 37830069000063 THIS WILL BE A HAND JOB . CAN POSSIBALLY SET 40 FT SEC POLE &SERV FROM POLE 295. ISO 37830069000063/ COD 3/ VER/BOW
8931 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2018-02-05 07:13 | 2018-02-05 12:18 | 6 | 305 | 4805491 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr pole 810-339 burnt off due to cutout failure. Crew enroute to make repairs. Lifted hot line clamp on 810-256 to isolate. Closed fuse on 810-5 @ 8:57 restoring up to & including 810-256. Crew working to repair. Restored remaining customers @ 12:18. sh Released by crew 076S02
8932 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-03-19 22:08 | 2008-03-19 23:05 | 18 | 57 | 59131-1 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3116701// BROKEN INSULATOR VER/KEP IDC XXXX
8933 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-12-02 02:47 | 2018-12-02 11:20 | 2 | 513 | 4499381 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad 25kva 7200 xfmer. trk to pole. Released by crew 078S07 L3/HFP
8934 | Hazard | 3308001 | JACKSON | S.JACKSON | 2022-05-16 07:31 | 2022-05-16 09:25 | 9 | 114 | 4895001 | 1026 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 1083-C4-210 and had to open to change it TR 1083-C4-495 was never out///had line fuse cutout on pole 1083-c4-210 open line fuse at 0915 and closed at 0925
8935 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2016-01-26 11:09 | 2016-01-26 14:34 | 5 | 205 | 4651101 | 1025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830372000144 == NEED LINE CREW TO CHANGE MANUAL === RELEASED BY CREW 077S03 VER/CRB
8936 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-05-15 17:00 | 2013-05-15 20:25 | 5 | 205 | 4118471 | 1025 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER--NEED OIL CONTAINMENT BAG FOR TRANSFORMER--NEED TO CHECK LOAD ON TRANSFORMER--TRANSFORMER OVERLOADED--NEED 3 MAN PRC CREW AND SMALL MATERIAL HANDLER--NEED AT LST A 25KVA RELEASED BY CREW 078S07/ CREW ON SITE /FETR 21:00 JEH/ REPAIRS COMP. POWER REST. @ 20:25 //JEH//COD 5// VER/DBM
8937 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-05-10 00:26 | 2020-05-10 08:58 | 2 | 512 | 4818731 | 1024 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout GuidelinesDispatched in accordance with KYPCo Late Night Callout Guidelines. bad cutout on pole 350-215.. cutout replaced.. power restored @ 08:58
8938 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-05-16 18:27 | 2009-05-16 20:00 | 11 | 93 | 59100-1 | 1023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT COD-11 ISO POLE 37830102A40293 L3/HFP
8939 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-06-13 16:56 | 2022-06-14 09:59 | 1 | 1023 | 4067471 | 1023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | tran c/o broke-crew req-ds061322 Released by crew 078S01
8940 | Pikeville | 3410602 | E.PRESTON | LANCER | 2013-07-02 02:46 | 2013-07-02 08:27 | 3 | 341 | 4442971 | 1023 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK IN THE AM ON 7-2-13. RUSE LINK WAS BROKE ,NOT BLOWN VER/CRB L/3 CRB IDC XXXX
8941 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-01-22 00:27 | 2014-01-22 08:58 | 2 | 511 | 4300171 | 1022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER UNABLE TO RESPOND TO THIS CALL AT THIS TIME DUE TO TERRIBLE ROAD CONDITIONS//THIS WILL BE LOOKED AT WHEN CONDITIONS IMPROVE//*** DAVE SAMMONS LIVES AT HEAD OF THIS HOLLOW , HE WAS DISPATCHED TO CK ** REPORTS POLE BURNED OFF WILL NEED TO OPEN LINE FUSE . AT 0552 (30 CUST) // 2 CUST ON TR @ 38831150000315 // COD-32 ISO LF 38831150000028 DUP IN HOIS VER/HFP L3/HFP IDC XXXX
8942 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-09-26 16:14 | 2009-09-26 18:40 | 7 | 146 | 64225-1 | 1022 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | THE NEUTRAL IN SPAN OF SEC. COND. HAD PULLED OUT OF SLEEVE. CUSTOMER SAID A CAR HIT SEC. POLE PRETTY HARD BEFORE THIS HAPPENED. I FIXED COND. VER/ARN IDC XXXX
8943 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-02-09 02:24 | 2013-02-09 04:50 | 7 | 146 | 4804021 | 1022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. REPLACED FUSE AND CLOSED XFMR @ 4:50. SH //VER/GAH IDC XXXX
8944 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-04-16 21:22 | 2018-04-16 22:35 | 14 | 73 | 4242721 | 1022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Copper on bottom side of cutout broke in clear at pole 38830069C35084. Repairs made, power restored at 22:35/ ISO 38830069C35084/ COD 14 L3/HFP
8945 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-11-27 12:42 | 2022-11-27 21:13 | 2 | 511 | 4185951 | 1022 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke XCO on 1125-C2-40// made repairs and restored at 21:13
8946 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-07-26 19:28 | 2008-07-26 20:28 | 17 | 60 | 60615-1 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001/ RISER WIRE CUTOUT LOOSE//COD 17//TRANSFORMER OFF AT 20:15//TOOK OFF TRANSFORMER ON THE SAME POLE AS THE FUSE TO WORK SAFELY//INTERRUPTED 1 EXTRA CUSTOMER// VER/DBM IDC XXXX
8947 | Hazard | 3309302 | VICCO | JEFF | 2019-06-16 04:20 | 2019-06-16 07:10 | 6 | 170 | 4511991 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Left Hand Phase Out Only (C)Pole # 299C/254 stirrup brunt into on C phase recloser power on 07:10//cod 6
8948 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-07-21 19:56 | 2018-07-22 12:56 | 1 | 1020 | 4830631 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 205-42, 35/5 pole rotted off at ground ,cust agreed to wait till tomorrow , will need 3 men truck acess 1/0 sec and 2/3 service on pole no damage to any wire just transfer , cut hot legs on xfmr pole..all power restored @ 12:56 hrs..p.hicks
8949 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2014-04-30 12:06 | 2014-04-30 15:30 | 5 | 204 | 4651221 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 655-342..BLEW LINE FUSE ON 655-107.NO TRUCK.CHGING CUTOUT.BACK ON AT 15.30//COD 5// VER/DBM
8950 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2020-05-29 10:01 | 2020-05-29 11:43 | 10 | 102 | 4927161 | 1020 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Customer said they seen a flash,Have a bad splice in secondary that burned neutral into,That let the service hang low going to fix splice to METER 190-221-479 had to pull METER to make repairs. Got Cust restored at 11:43.
8951 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-11-29 07:50 | 2015-11-29 16:20 | 2 | 510 | 4491011 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGGED & GROUNDED// POLE 287-49 CAN BE REPAIRED BY TRUCK WITH WOODEN POLETOP, BIG BUCKET MUST BE BACKED DOWN ROAD IN ORDER TO STAY IN OLD DRIVEWAY CUSTOMER SAID I287ROUND&TAGGED TO DDC AT 287B-12, CREW REQUIRED RELEASED BY CREW 078S11.. CREW ON SITE TO MAKE REPAIRS ETR 17:00.. REPAIRS MADE AND LINE FUSE BACK IN AT 16:20 AND TICKET COMPLETE CAY VER/CRB
8952 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2012-03-14 15:10 | 2012-03-14 15:30 | 51 | 20 | H4578681 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PART OF 4578681//OPENED RECLOSER ON POLE 517-85 AT 15:10 TO TAKE LOAD OFF //COD +51// CLOSED BACK ON RECLOSER @ IN AT 15:30// RESTORED 51// VER/DBM IDC XXXX
8953 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2018-11-28 09:55 | 2018-11-28 11:37 | 10 | 102 | 4486831 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke on the low side of the phase A stepdown. Power restored at 11:37.//// A phase only showing out
8954 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-04-11 17:59 | 2012-04-11 18:09 | 102 | 10 | 4667251 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENED C PHASE RECLOSER (111 CUSTOMERS ) TO ALLOW CREW TO REPLACE DEFECTIVE SWITCH.. VER/HFP L3/HFP IDC REMOVED 3 MIN STEP FOR 9 CUSTOMERS XXXX
8955 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2018-04-19 03:31 | 2018-04-19 05:13 | 10 | 102 | 4253731 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B phase line fuse is blown at pole 38820917D20056. Replaced bad transformer cutout at pole 38820917D00137. Power restored at 05:13.
8956 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2016-04-10 21:48 | 2016-04-10 22:22 | 30 | 34 | 4078411 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED TO SAFELY REPLACE FAILED CUTOUT, SEE PO 4078351 VER/KEP AJB
8957 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-07-02 16:55 | 2015-07-02 22:15 | 8 | 320 | 4711441 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD ON POLE 1148-198 AND IT TOOK OUT LINE FUSE ON POLE 1148-24. I OPENED BANK OF TRANSFORMERS ON POLE 198 AND CLOSED LINE FUSE ON 24 BACK IN AT 18:35 . WE CHANGED TRANS AND CLOSED BANK OF TRANS. IN AT 22:15 RELEASED BY CREW 074S01 VER/KEP
8958 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2016-01-23 22:11 | 2016-01-24 03:51 | 3 | 340 | 4646311 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074S04
8959 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2016-02-24 15:18 | 2016-02-24 22:14 | 3 | 416 | 4760881 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S02 REPAIRS MADE AT POLE 311 HOT TAP ON AT POLE 241 AT 22:14 D SAMMONS RELEASED BY CREW 074H02 VER/ARN
8960 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-11-30 14:29 | 2014-11-30 15:20 | 20 | 51 | 4819261 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED POLE 292-96 BROKEN FUSE LINK/ ISO 38830292B00096/ COD 20/ VER/BOW AJB
8961 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-07-03 09:45 | 2022-07-03 14:00 | 4 | 255 | 4369401 | 1020 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout, changing
8962 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2013-04-12 12:26 | 2013-04-12 20:55 | 2 | 509 | 4004471 | 1018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF == NEED LINE CREW AND 45 POLE AND 15 KVA 7200 ==CUTOUT AND T BRACKET === REPLACED POLE POWER OK COD-2 ISO LF 37830344000103 VER/HFP L3/HFP IDC XXXX
8963 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-05-28 00:50 | 2017-05-28 17:48 | 1 | 1018 | 4874521 | 1018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 174C-428 . NEED LINE CREW WITH MATTS TO GET TO POLE . RELEASED BY CREW 075H04 VER/CRB
8964 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2021-06-13 20:17 | 2021-06-14 13:15 | 1 | 1018 | 4735921 | 1018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE//////////XFR IS BAD,NEED MATERIAL BUCKET,IF IT CAN GET OFF ROAD ENOUGH,LITTLE BIT TIGHT HERE.IF NOT,WILL NEED FLAGGERS.SHOWS A 7.2 10KVA HERE.CHANGE PORCELIN CUTOUT ALSO./////////going to work this in the am per steve ray Released by crew 074S06. Closed at 13:15
8965 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2013-09-21 19:16 | 2013-09-22 03:45 | 2 | 509 | 4875771 | 1018 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED TRUCKS OK POLE 171-23 CAN DO A CUTOFF AND LOWER EVERYTHING NO TELEPHNE OR CABLE /BEHIND HOUSE FIRE OUT/20T LINE FUSE OUT AND HANGING ON BASS OF POLE NOT FUSED/2 PEOPLE OUT RELEASED BY CREW 078S03//20T LINE FUSE ON 171-22 BACK ON @ 03:45 VER/ARN IDC XXXX
8966 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-07-25 09:06 | 2016-07-25 14:45 | 3 | 339 | 4675871 | 1017 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT ON XFMR BANK POLE 1083C-562 . BAD XFMR . NEED BIG BUCKET & 50 KVA XFMR 7200./ ISO 38831083C30562/ COD 3/ VER/BOW
8967 | Pikeville | 3407103 | TOPMOST | KITE | 2013-01-31 02:00 | 2013-01-31 18:57 | 1 | 1017 | 4766521 | 1017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED : NEED TO REPLACE TWO POLES 210-73 (ROTTEN AT GROUND LEVEL ) AND POLE 210-72 ( EARTH REMOVED AND LEANING ) . NEED 1 40 FT POLE AND 1 45 FT POLE, MATERIAL FOR ( 7.2 KV ) 1 SINGLE PHASE ANGLE AND 1 SINGLE PHASE STRAIGHT LINE POLE , #2AA, 3/8 GUY WIRE, GUY INSULATOR, 2/3 TRIPLEX, CUTOUT AND ARRESTER . NEED 1 MANUAL ROW CREW AND 1 BUCKET ROW CREW . BOTH POLES TRUCK ACCESS / ISOLATED AT POLE 210-97 RELEASED BY CREW 074S03//COD 1//ISO 37830210000097//// VER/DBM IDCC TOF2352 ESTIMATED TIME OFF XXXX
8968 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-09-05 09:21 | 2013-09-05 15:00 | 3 | 339 | 4821631 | 1017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | ONLY THREE CUSTOMERS AFFECTED BAD UG XFMR. CREW ENROUTE TO REPLACE. RELEASED BY CREW 076S02//MADE MDC// REPLACED XFRM, RE-ENERGIZED AT 15:00 VER/CRB L/3 CRB IDC XXXX
8969 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-03-22 17:03 | 2009-03-23 10:00 | 1 | 1017 | 60718-1 | 1017 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-1 WR # 29025020 // POLE 17-21, 10 KVA CSP TRANSFORMER BAD, WILL NEED TO REPLACE WITH 15 KVA , CUSTOMER SAYS OK TO COMPLETE MONDAY 03-23-09 A.M. / GXJ RELEASED BY CREW 074S03//COD 1// COMPLTED R RAY L3/HFP IDC XXXX
8970 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-11-05 11:41 | 2020-11-05 15:55 | 4 | 254 | 4645491 | 1016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | broke pole 117-354. need 40-5, 12kv 37.5 kva 120/240 xfmer. xfmer bag oil spill clean up, 3 pc 3 conduit Released by crew 078S07//arrived RM grounding & tagging at 117-204 to RM fuse in @ 15:55 please close tic RM //WO to BE WROTE
8971 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-05-06 08:16 | 2011-05-06 12:30 | 4 | 254 | 4013401 | 1016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 39857242 // REPLACED TRANSFORMER COD-4 ISO TF 37830245A00246 VER/HFP L3/HFP IDC XXXX
8972 | South Williamson | 3411401 | DEWEY | INEZ | 2012-05-22 07:11 | 2012-05-22 11:25 | 4 | 254 | 4816461 | 1016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE HAS BLOWN FOUR TIMES IN LAST WEEK//I HAVE BEEN REFUSING AND IT STAYS TIL THE NEXT DAY// I TRIED FUSE THEN AND CAME BACK OUT//THIS IS ALL U/G PRIMARY//CREW ENROUTE//FOUND ARRESTOR TRCKING ON POLE 861-141// CLEARED UP AND ALL RESTORED //COMPLETE//EM ///VER/CRB L/3 CRB IDCC CDC83 XXXX
8973 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-12-24 02:21 | 2015-12-24 08:10 | 4 | 349 | 4554281 | 1016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20T LF OPEN @ 115-94, BAD C/O @ 115-97 20T RESTORED @ 05:00.. NO TRUCK, 19.9 C/O RELEASED BY CREW 078S07//COD 4//,,CREW ON SITE,,CUTOUT REPLACED,,ALL POWER RESTORED VER/CRB
8974 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2009-03-10 08:51 | 2009-03-10 13:05 | 4 | 254 | 56811-1 | 1016 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-4 BAD 50 KVA XFORMER 7200. TRUCKS TO POLE. RELEASED BY CREW 078S01 L3/HFP IDC XXXX
8975 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2010-12-15 07:47 | 2010-12-15 11:10 | 5 | 203 | 50458-1 | 1015 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | TRANS. RISER BURNED INTO CREW ON THEIR WAY---REPLACED XFMR RISER COD-5 ISO TF 37830047C00221 VER/HFP L3/HFP IDC XXXX
8976 | Pikeville | 3413401 | GARRETT | GARRETT | 2010-12-17 13:00 | 2010-12-17 15:25 | 7 | 145 | 53190-1 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DEFECTIVE CUTOUT HAS BURNED ARM, NO CUSTOMER OUT AT THIS TIME, CREW ENROUTE ... OPENED AT 13:00 ... CLOSED AT 15:25 .../ ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03//VER/CRB IDCC CNT5 XXXX
8977 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2020-05-24 17:21 | 2020-05-25 10:16 | 1 | 1015 | 4897841 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole 257B/113 bad cutout need line crew cutout and t/bracket 7200V Released by crew 077S03.. restored power at 10:16..
8978 | South Williamson | 3411401 | DEWEY | INEZ | 2009-06-11 08:35 | 2009-06-11 11:00 | 7 | 145 | 57500-1 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 30243987 // FOUND CUTOUT BROKEN ON POLE 814-95 REPLACING NOW TCM// IDCC PN20, CNT7 XXXX
8979 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2015-03-04 12:55 | 2015-03-04 14:40 | 15 | 105 | 4099181 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED ISOLATED HOT TAP ON 38830248000073/1 CUSTOMER STILL OFF ON 38830248000177 LINE FUSE BACK IN AT 1400 HRS ON POLE 38830248000071/248-77 BACK IN AT 1440 HRS RELEASED BY CREW 078S03 VER/CRB
8980 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-09-16 12:10 | 2010-09-16 14:35 | 7 | 145 | 50468-1 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36913475 // POLE 45-527 BAD CUTOUT AND LA SEND TO JOE H. LINE FUSE OUT 30T ON POLE 45-525 CALLED TREE CREW RELEASED BY CREW 078S08/ GRND. LINE MAKING REPAIRS/RESTORED @ 14:35 J. HEMLEPP COD-7 VER/HFP L3/HFP IDC XXXX
8981 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2013-05-16 15:02 | 2013-05-16 15:37 | 29 | 35 | H4121931 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | "B" PHASE CAME LOOSE AT POLE 649-63HOT TAP CAME OFF AT POLE 649-63///CABLE COMPANY PULLING IN CABLE IN AREA,MAY HAVE SHOOK POLES TO CAUSE IT TO COME OFF//GOING TO OPEN RIGHT HAND RECLOSER ON 649-202 TO PUT HOT TAP BACK ONHOT TAP CAME OFF AT POLE 649-63/////OPENED RECLOSER AT 15:02,CLOSED BACK RESTORING ALL CUST. AT 15:37//COMPLETE VER/KEP
8982 | South Williamson | 3411401 | DEWEY | INEZ | 2013-05-16 15:02 | 2013-05-16 15:37 | 29 | 35 | 4122391 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED "B" PHASE TO SAFELY CLEAR UP TROUBLE ON ORDER 4121931 COD-202 VER/KEP IDCC CNT202, CDC88, XXXX
8983 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-09-06 10:05 | 2018-09-06 12:30 | 7 | 145 | 4048481 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | blown arrester on b phase
8984 | Paintsville | 3401102 | FALCON | SALYERSVI | 2020-07-18 22:38 | 2020-07-19 01:03 | 7 | 145 | 4181281 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva xfmr on p-38830851B00013 has been pumping oil, need changed xfmr bank off at 12.10 a.m .back on at 1:03 send a copy to ryan newsome.
8985 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2020-02-06 06:03 | 2020-02-06 09:26 | 5 | 203 | 4367571 | 1015 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3309101/gaj/0606/report of pole down disp 3144 R Maggard. bad cutout on pole 449-49 will take big bucket, also tree fell tearing phone & tv cables off pole .restored power at 09:26..
8986 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-03-15 14:01 | 2009-03-15 16:50 | 6 | 169 | 58820-1 | 1014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401302// HAD TO OPEN LINE FUSE ON POLE 379-343 @ 1401// TO DE-ENERGIZE LINE DUE TO A POLE FIRE...3401302// BAD CUTOUT BURNT POLE OFF GOING TO LOWER EQUIPEMENT ON POLE MANUAL JOB // VER/TOM L3/TOM IDC XXXX
8987 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2021-11-21 22:21 | 2021-11-22 01:10 | 6 | 169 | 4113761 | 1014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 19.9 Xfrm cutout on pole 398-B-8. Need big bucket. Power restored at 1:10.
8988 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-07-09 07:48 | 2012-07-09 16:15 | 2 | 507 | 4633541 | 1014 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON POLE#117B-232, LINE CUTOUT BROKEN, CAN USE TRUCK, WILL NEED FLAGGERS, NEEDS LINE CREW RELEASED BY CREW 078E09/CREW ON SITE MAKING REPAIRSFETR1700 RM/ALL REPAIRS COMPLET AT 16:15 PLEASE CLOSE TICKET RM VER/HFP L3/HFP IDC XXXX
8989 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-02-06 06:27 | 2008-02-06 23:20 | 1 | 1013 | 50557-1 | 1013 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE WORK TRUCK TO POLE NEUT. BROKEN AT POLE 502-114 CUSTOMER HAS MAIN BRK. OFF AT THIS TIME....CPS RELEASED BY CREW 078E04//DHE CREW REPAIRED NEUT. AND RESTORED SERV.//COD 1// VER/DBM IDCC CDC92 XXXX
8990 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2013-02-08 21:34 | 2013-02-09 01:47 | 4 | 253 | 4803591 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200, POLE IN BACK YARD, WILL HAVE TO DRIVE ALL THE WAY AROUND HOUSE TO GET TO IT, RELEASED BY CREW 078S05 /// FRALEY & MCCOY & YOUNGMAN & VIRGIN///REPLACED BAD 25KVA XFMR///BACK ON AT 01:47///VOLT CK GOOD //VER/GAH IDC XXXX
8991 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-06-04 12:47 | 2008-06-04 14:19 | 11 | 92 | 56129-1 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3007904//UNKNOWN CAUSE//LOOKED LIKE IT MELTED OUT//COD 11// VER/DBM
8992 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-02-21 13:08 | 2010-02-21 14:40 | 11 | 92 | 59514-1 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE REPLACED FUSE AND RESTORED POWER. TIM MCCOY//COD 11// VER/DBM IDC XXXX
8993 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-04-20 20:35 | 2017-04-20 22:07 | 11 | 92 | 4662951 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT WENT BAD AND CAUGHT POLE ON FIRE. HAD TO OPEN UP LINE FUSE ON POLE 353-58 AT 20:35 TO MAKE SAFE. WILL NEED ONE MAN. RESTORED POWER AT 22:07/ ISO 37830353C00058/ COD 11/ VER/BOW L3/HFP XXXHFP
8994 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-12-15 11:25 | 2010-12-15 15:38 | 4 | 253 | 50615-1 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38119615 // CREW ON SITE STARTING REPAIRS TCM// COD-4 ISO TF 38830852000206 VER/HFP L3/HFP IDC XXXX
8995 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-05-20 20:53 | 2012-05-20 22:25 | 11 | 92 | 4811851 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAD TO OPEN TRANSFORMER TO SAFELY CUT TREE AROUND TRANSFORMER POLE// BAD CONNECTOR AT TRANSFORMER POLE POWER RESTORED OFF AT 2210 ON AT 2225 IDCC TON2236 CHANGED CAUSE FROM TREE IN XXXX
8996 | Pikeville | 3421001 | BREAKS | CITY | 2014-02-24 09:42 | 2014-02-24 10:04 | 46 | 22 | 4429991 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED FUSE TO ALLOW SERVICER TO SAFELY MAKE REPAIRS TO BUSTED HOT TAP// THIS OUTAGED 46 CUSTOMERS// ASSOCIATED WIT OUTAGE 4429841//FLT 220-D1-341 // OPENED @ 0942 CLOSED @ 1004 // VER/TOMN L3/TOM
8997 | Cannonsburg | 3001401 | LOUISA | CITY | 2014-03-02 14:47 | 2014-03-02 19:00 | 4 | 253 | 4444181 | 1012 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA(7200) CSP CAN NEED CREW TRUCK TO POLE UPDATED FETR TO 19:30 RELEASED BY CREW 078H06,,CREW ON SITE,,REPACED XFMR AND CUTOUT,,,ALL POWER RESTORED//COD 4// VER/DBM
8998 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-03-05 05:23 | 2013-03-05 11:00 | 3 | 337 | 4870831 | 1011 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED AT REG WORK TIME. XFORM CUTOUT DOOR BURN UP ,REFUSE NEW DOOR MADE HOT 11:00AM ENTERED MD CCC COD-3 ISO TF 38830141B00103 VER/HFP L3/HFP IDC XXXX
8999 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2022-11-13 16:39 | 2022-11-13 22:16 | 3 | 337 | 4138921 | 1011 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout gate burnt up. Dont have gate to go back in cutout its old style cutout. Needs to be changed out. Need 7200 cutout, arrester and tbracket. Also there is a service hanging down off pole that needs to be cleared up. Need linecrew and manual row crew. Released by crew 077H15. all power restored @ 22:16 p.hicks
9000 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-12-29 10:10 | 2013-12-29 15:00 | 9 | 290 | 4209471 | 1010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A BAD CUTOUT HAS BURNED THE TOP OF A POLE OFF, I HAVE ISOLATED ON POLE426-461 . & 426-75 I NEED A THREE MAN CREW TO MAKE REPAIRS. // R AMBURGEY & J BAKER & V HURT COD-9 ISO LF 37830426C00005 FUSE IN @ 1140 (8 CUST) A BAD CUTOUT HAS BURNED THE TOP OF A POLE OFF, I HAVE ISOLATED ON POLE426-461 . I NEED A THREE MAN CREW TO MAKE REPAIRS. I CLOSED FUSE IN AT 11:40 /// LAST CUST ON @ 1500 VER/HFP L3/HFP
9001 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-03-08 10:35 | 2020-03-08 12:16 | 10 | 101 | 4460651 | 1010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12kv c/o.pole 20d14563. feeds pri. ug. trk to pole. beside road. 119 new hampshire. bellefonte. fieldview incorrect Released by crew 078S07///replacing cutout//complete 12:16 BR
9002 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-02-24 03:35 | 2012-02-24 12:00 | 2 | 505 | 4490671 | 1010 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFORM 25KVA SINGLE BUSHING 7200 LINE CREW LEVEL GROUND BUT REAL MUDDY TR.MAYBE , MATERIAL HANDLER AND PICKUP HOUSE NO. 1549 1ST HS ON LEFT PAST OLD STORE ON RT RELEASED BY CREW 078S04/REPAIRS COMP. POWER REST.@12:00/// 078H05 J. HEMLEPP // COD-2 ISO TF 38830574000135 VER/HFP L3/HFP IDC XXXX
9003 | Hazard | 3308401 | BECKHAM | HINDMAN | 2010-11-04 13:06 | 2010-11-04 19:15 | 11 | 369 | 51786-1 | 1009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37629136 // POLE # 155-109 HAS BURNT OFF AT CUTOUT, POLE IS ROTTON, WILL NEED TO REPLACE. ALL CREWS ARE TIED UP ON OUTAGE RIGHT NOW IN PERRY CO. // COD-54STS WR # 37629136 // POLE # 155-109 HAS BURNT OFF AT CUTOUT, POLE IS ROTTON, WILL NEED TO REPLACE. ALL CREWS ARE TIED UP ON OUTAGE RIGHT NOW IN PERRY CO. ALL POWER EXCEPT CUST ON POLE 109 IS BACK ON AT 14:10 LAST CUSTOMER ON AT 19;15// VER/DBM IDC DCMT XXXX
9004 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-05-20 19:50 | 2018-05-21 12:39 | 1 | 1009 | 4383591 | 1009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | got bad transformer 10 kva 19.9 up on side of hill fuse stay in but only getting 70 volts phase to ground and 140 phase to phase i got cust breaker off under meter cust has big gen running Released by crew 077S05
9005 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-08-28 14:33 | 2022-08-28 18:00 | 19 | 207 | 4804941 | 1009 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke 7200 cutout on pole 273-B-52, manual. I have spoken with Phillip Hicks and he is sending someone to make repairs. The line fuse on this pole will need to be opened to make repairs. Released by crew 077S04 // open LF @1725 restored all @1800
9006 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-11-10 14:28 | 2012-11-10 18:40 | 4 | 252 | 4380221 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE BROKE FUSED UP EVERYTHING OK ///VER/CRB L/3 CRB IDC XXXX
9007 | Pikeville | 2974101 | BIG ROCK STATION | CONAWAY | 2014-11-26 18:21 | 2014-11-26 21:09 | 6 | 168 | 4804461 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 CUST OUT SINCE 1659//L/F ON POLE 37820175000005 OPENED @ 1821//COD 6//CUTOUT BROKE ON POLE # 151-203 NO TRUCK/// OPENED LINE FUSE ON POLE# 175-5 @ 18:21 TO ISOLATE TROUBLE/// NEED 1 MAN// REPAIRS MADE AND CLOSED IN LINE FUSE ON POLE # 175-5 @ 21:09 AND RESTORED SERVICE///// SEND TICKET TO CLIFF FREEMAN ABOUT POLE # 151-203 BEING BURNT VER/CRB
9008 | Hazard | 3303902 | LESLIE | WOOTON | 2016-06-21 08:11 | 2016-06-21 09:35 | 12 | 84 | 4393941 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/CRB
9009 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-01-09 09:37 | 2008-01-09 12:25 | 6 | 168 | 55137-1 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3116703//BAD 25 KVA// TRUCK ACCESSIBLE//REPLACED TRANSFORMER AND REPAIRED 2 SERV. DROPS AND RELOCATED ONE SERV. FOR CLEARENCE///SEE EARLIER OUTAGE//)//VER/CRB IDC XXXX
9010 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2012-10-28 09:44 | 2012-10-28 16:50 | 3 | 426 | 4178161 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNED OFF AT POLE 38821013A00264, AND I HAVE ISOLATED AT POLE 38820989B00296, I CAN GET THE TWO OTHER CUSTOMERS BACK ON. NEED THREE MAN CREW. AT 14:35 CLOSED FUSE IN ON POLE 1013-A-247. RELEASED BY CREW 079H06//COD 3// VER/DBM IDC XXXX
9011 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-10-03 15:08 | 2008-10-03 19:20 | 4 | 252 | 53232-1 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA NEEDS 37.5 END OF IRENE ST ENGLAND HILL RELEASED BY CREW 078S08//COD 4//POWER RESTORED 1920//ISO 38830142C00130// VER/DBM IDC XXXX
9012 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2016-01-28 02:36 | 2016-01-28 11:00 | 2 | 504 | 4655351 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP TRANSFORMER IN DIFFICULT LOCATION WILL REQUIRE POLARIS ATV OR POSSIBLY A 4X4 PICKUP WITH CHAINS. WILL REPLACE FIRST THING IN THE MORNING. RELEASED BY CREW 076S02// WORK COMPLTED, RESTORED AT 11:00 VER/KEP
9013 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-07-27 09:03 | 2010-07-27 11:51 | 6 | 168 | 57747-1 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR FUSE IS OUT,ALSO LINE FUSE AT MO IS OUT.WILL FUSE XFR UP FIRST,THEN LINE FUSECUTOUT ON 1059-287 WAS BROKEN,TOOK LINE FUSE OUT,REPLACED CUTOUT,RE-FUSED LINE AND RESTORED TO ALL CONCERNED // COD-19 VER/HFP L3/HFP IDC LOOKS LIKE THIS SHOULD BE PHC ONLY, CHANGED COUNT FROM 19 XXXX
9014 | South Williamson | 3411401 | DEWEY | INEZ | 2013-11-20 11:24 | 2013-11-20 17:00 | 3 | 336 | 4059191 | 1008 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3411401// ALL WORK COMPLETE / GXJ 3 CUSTOMERS HAD PART POWER. VER/SEF
9015 | Pikeville | 3401001 | ELWOOD | DORTON | 2018-08-04 12:24 | 2018-08-04 14:30 | 8 | 126 | 4907781 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrester on p-214-243..line fuse blown on 214-50//MADE AED
9016 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-05-01 15:47 | 2011-05-01 19:35 | 61 | 228 | 53255-1 | 1008 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BURNT OFF POLE ISOLATED ON 254-186 CAN CUT OFF AND LOWER/254-175 BACK ON AT 1600 HRS/TRUCK OK RELEASED BY CREW 078S03//COD 61// VER/DBM IDCC TOF1457 PER TICKETS XXXX
9017 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2019-12-14 02:34 | 2019-12-14 10:57 | 2 | 503 | 4152241 | 1006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. On pole 38821137C0048 we have a broke cutout,Will have to climb pole to make repairs.Got cut out changed and Restored service at 10:57..
9018 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2015-04-03 15:16 | 2015-04-03 23:39 | 2 | 503 | 4265401 | 1006 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT//COD 2// VER/DBM
9019 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2017-04-11 22:04 | 2017-04-12 01:25 | 5 | 201 | 4638921 | 1005 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BLANK METER 37820073B00009 COD 1//////BAD 25KVA 19.9 XFM.ON POLE 73-09 NEED CLASS B LINEMAN AND BIG BUCKET TO MAKE REPAIRS.REPAIRS MADE../// VER/DKM L3/HFP XXXHFP
9020 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2011-04-24 06:31 | 2011-04-24 07:38 | 15 | 67 | 63382-1 | 1005 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 453-275 GOT A BAD HIGH SIDE CUTOUT; CHANGED CUTOUT AND PATROLLED LINE; APR AT 0738 CLOSE TICKET VER/KEP IDC XXXX
9021 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-08-07 04:12 | 2017-08-07 09:47 | 3 | 335 | 4232231 | 1005 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | BAD 25 KVA, 7200-120/240.TRK TO POLE. OK TO HOLD TO START TIME RELEASED BY CREW 078S07 VER/ARN
9022 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-12-27 17:39 | 2020-12-27 22:39 | 6 | 300 | 4828641 | 1005 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F cutout has failed and broke on 655-A4-372. Will be opening xfmr on that pole also to safely make repairs. No truck access///opened TR on pole 655-A4-372 at 2204 to make repairs and restored at 2239 (3 COD)
9023 | Hazard | 3301401 | COMBS | COMBS | 2019-05-21 14:39 | 2019-05-21 18:50 | 4 | 251 | 4309811 | 1004 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CONTACTED CUSTOMER TO LET HER KNOW THAT WE WILL BE REPLACING POLE TODAY//NO OUTAGE TILL CLAMP LIFTED ON POLE 37830271C00147//OFF @ 1439 ON @ 1850
9024 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2016-07-29 20:52 | 2016-07-30 01:03 | 4 | 251 | 4710861 | 1004 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 50KVA TRANS 4/0 RISER BEING PADS AND YOU MIT GET TO POLE TRANS. VERY HOT RELEASED BY CREW 078S08/FOREMAN ON SITE/CREW ENROUTE/FETR 0200/VEM/REPAIRS MADE AND ALL CUST RESTORED 0103/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
9025 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-08-07 20:50 | 2012-08-07 21:07 | 59 | 17 | 4909501 | 1003 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED RECLOSER TO SAFELY WORK ON TIX 4909241 ///VER/CRB L/3 CRB IDCC CCSCO XXXX
9026 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-06-19 21:12 | 2011-06-20 13:55 | 1 | 1003 | 4346851 | 1003 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PATROLLING. TALKED WITH CUST, OKAY TO CHECK IN THE A.M., WILL HAVE TO BE WALKED OUT, FEEDS TOWER & SHOP. RECLOSER OPEN AT POLE 306-211. I PUT RECLOSER IN AT 11:45 IT STAYED ABOUT FIVE MINUTES AND CAME BACK OUT I FOUND TWO INSOLATORS BLOWN OFF POLE NO.306-247 , I WILL ISOLATE THAT PHASE AT POLE NO.306-169 ALSO I CUT LOOPS ON ALL THREE PHASES AT POLE NO.306-270 AND CLOSED RECLOSER IN AT 17:55, COAL CO. STILL OUT OF POWER, CREW NEEDED RELEASED BY CREW 077S12OPENED RECLOSER//VER/CRB
9027 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2021-03-09 11:33 | 2021-03-09 19:54 | 2 | 501 | 4318731 | 1002 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad connection at weatherhead. Replaced and restored @ 19:54. sh/ opened @ 1933
9028 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2015-06-02 09:55 | 2015-06-02 10:01 | 167 | 6 | 4499951 | 1002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | OUTAGE NECESSARY TO ALLOW CREW TO REPLACE DEFECTIVE REGULATOR /// OFF @ ON @ (C PHASE ONLY 157 CUST) // 9:55 TO 10:01/ ISO 38830207A00259/ COD 157/ VER/BOW L3/HFP HFPC CNT157 AJB
9029 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-06-19 11:09 | 2015-06-19 16:43 | 3 | 334 | 4610201 | 1002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1081-236 TOP BURNED OFF.WILL ISOLATE AT POLE 1081-72 WITH HOTTAP///////CREW NEEDED////BELIEVE THIS CAN BE LOWERED,CAN USE TRUCK///////IF POSSIBLE,PUT A HOTTAP ON LOOP AT POLE 1081-73 AS 72 IS IN A DIFFICULT LOCATION RELEASED BY CREW 074S06/ MD DONE/ ISO 38821081000072/ COD 3/ VER/BOW
9030 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-04-02 00:32 | 2011-04-02 08:53 | 2 | 501 | 61256-1 | 1002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN-----FUSE APPEARED TO HAVE BROKEN //VER/GAH IDC XXXX
9031 | Hazard | 3303902 | LESLIE | WOOTON | 2018-11-29 14:09 | 2018-11-29 22:30 | 2 | 501 | 4491211 | 1002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cut out manuel pole might reach with bucket Released by crew 077H14 repairs made and power restored at 2230
9032 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-02-16 18:40 | 2010-02-17 03:01 | 2 | 501 | 58477-1 | 1002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT POLE 38830472000109, ISOLATED AT 38830472000010, 45-5 POLE, TRUCK OK, ROAD CROSSING, 1 XFMR OUT WAS HOT TILL 1840 WHEN OPENED FUSEPOLE FIRE AT POLE 38830472000109, ISOLATED AT 38830472000010, 45-5 POLE, TRUCK OK, ROAD CROSSING, 1 XFMR OUT RELEASED BY CREW 078S05/ WR#33894466 / VER/LDA IDCC TOF1641 XXXX
9033 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-07-12 10:36 | 2012-07-12 13:23 | 6 | 167 | 4695571 | 1002 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IDC XXXX
9034 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-07-05 16:37 | 2016-07-05 19:00 | 7 | 143 | 4541521 | 1001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T FUSE OUT DUE TO BAD CUTOUT. REPLACED CUTOUT FUSED UP EVERYTHING OK./ ISO 37830018D00003/ COD 7/ VER/BOW
9035 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2009-07-10 05:55 | 2009-07-10 06:08 | 77 | 13 | 52961-1 | 1001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | THIS SW ORDER ASSOCIATED WITH SW ORDER 52787-1 TO SHOW 77 CUST. OUTAGE TO CHANGE ANOTHER SET OF BELL D.E. INSULATORS. VER/ARN MLRC CDC 90
9036 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2013-03-18 10:13 | 2013-03-18 11:30 | 13 | 77 | 4915041 | 1001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 359 - 9 INACTIVE XFERMER, LINE FUSE OPENED ON POLE 357-7 3. ISOLATED BAD CUTOUT ON INACTIVE XFORMER ON POLE 357-9, LINE CREW CAN MAKE REPAIRS LATER. NO TRUCKS TO POLE.//COD 13//EMAILED TO RAYBURN// VER/DBM IDCC CDC92 XXXX
9037 | South Williamson | 3411401 | DEWEY | INEZ | 2020-05-05 07:41 | 2020-05-05 08:58 | 13 | 77 | 4799721 | 1001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 744-32//cutout broke on pole 744-286//making repairs//repairs made//restored at 8:58//complete//em
9038 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-12 22:35 | 2012-02-13 00:06 | 11 | 91 | 4343731 | 1001 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | MADE REPAIRS TO SECONDARY CONDUCTOR VER/ARN IDC XXXX
9039 | South Williamson | 3411401 | DEWEY | INEZ | 2021-05-20 19:17 | 2021-05-20 21:40 | 7 | 143 | 4605451 | 1001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink failed in service burning neutral and one hot conductor open. Made repairs and restored @ 21:40. sh
9040 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2015-07-19 10:31 | 2015-07-20 03:12 | 1 | 1001 | 4910501 | 1001 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE TOP OF 404 POLE BURNTED OFF POLE #901-534, LINE FUSE IS OPEN ON POLE 901-8026, NO GRDS OR TAG, CREW REQ, THIS IS ACROSS FROM GRANT BRIDGE, FIREWORKS BUSINESS ON HILL, CAN USE TRUCKS RELEASED BY CREW 078S06 ****CHANGE ISO POLE ***** VER/SEF
9041 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-01-06 11:15 | 2009-01-06 13:20 | 8 | 125 | 51884-1 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3010601//LINE FUSE BLOWN ON POLE 20-1036 FAILED CUT-OUT ON POLE 20-1071 WILL NEED CREW CALLED LLOYD RAYBURN IS TRYING TO FIND A CREW TO ASSIGNED TICKET TO CAN NOT ISOLATE HOT TAP WELDED TO BASKET ALREADY TRIED TO CLEAR UP VER/KEP L3/KEP IDC XXXX
9042 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-09-01 18:45 | 2014-09-02 11:25 | 1 | 1000 | 4445941 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 141-6032 BAD TRANS NO TRUCK 25KVA TRANS. RELEASED BY CREW 078S08// COD 1/// ISO 38830141B26032// VER/BOW
9043 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-11-07 13:20 | 2009-11-07 17:30 | 4 | 250 | 50000-1 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP BAD XFMR. DUTY SUPERVISOR NOTIFIED - CREW ENROUTE. XFMR CHANGED AND SERVICE RESTORED @ 17:30. SH COD-4 ISO TF 38830852000165 L3/HFP IDC XXXX
9044 | Pikeville | 3402003 | KEYSER | MULLINS | 2022-02-23 08:15 | 2022-02-23 12:25 | 4 | 250 | 4534681 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Riser coming out of the center trans. on bank pole 1127-B-481 burndt out, will have to open other 2 trans. to make repairs, will keep track of times. Opened other 2 trans. @1212, closed all 3 @1225.
9045 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-03-07 10:00 | 2013-03-07 10:25 | 40 | 25 | 4886881 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREW OPENED CENTER "B" PHASE RECLOSER TO SAFELY MAKE REPAIRS ON 4885911 VER/KEP IDC XXXX
9046 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-03-26 10:40 | 2017-03-26 11:30 | 20 | 50 | 4585431 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 1123-7094 BAD LA POLE 1123-7022 20T LINE FUSE/ ISO 39831123D37022/ COD 20/ VER/BOW
9047 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-12-12 07:54 | 2016-12-12 11:14 | 5 | 200 | 4186281 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 206:5 / LINE FUSE OUT ON POLE 206:12 VER/AWD L3/HFP XXXHFP
9048 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-03-29 08:43 | 2018-03-29 12:03 | 5 | 200 | 4145721 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | change two cutouts on pole 38831084D00070 and had a phase line fuse blown. 40 t line fuse A phase closed @ 1203
9049 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-09-02 14:15 | 2014-09-02 14:40 | 40 | 25 | 4448431 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PRI HAS COMEOFF PTP, NEED CREW WITH SMALL BUCKET TO RETIE PRI ON PTP, RON VIRGIN BUCKET, WILL MAKE IT ACROSS BRIDGE I DID NOT DRIVE ACROSS BRIDGE, CREW REQ TURN IN MAILBOX IS 547 ON BOX RELEASED BY CREW 078S06 14:15 OPENED FUSE ON 39831047000003 CLOSED AT 14:40 VER/HFP L3/HFP AJB
9050 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-04-12 14:30 | 2019-04-12 16:35 | 8 | 125 | 4086601 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE LINE FUSE CUTOUT ON 37830165000022 found B PHASE broken line cutout on pole 165-22..made repairs..restored.. Released by crew 074S01//MADE MD TO SHOW TRANSFORMER 37830141000062 ON B PHASE//CORRECT COD 8// L3/HFP
9051 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2016-12-11 15:55 | 2016-12-11 20:05 | 4 | 250 | 4184601 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | .LINE FUSE BLOWN ON 727-30,-..LINE DOWN 727-34..GRD TAGGED FOR MYSELF ON POLE 727-30 VER/CRB L3/HFP XXXHFP
9052 | Hazard | 3420001 | SOFT SHELL | VEST | 2017-05-03 00:02 | 2017-05-03 08:22 | 2 | 500 | 4738271 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE/ ISO 37830110000116/ COD 2/ RESTORED 0822
9053 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-03-13 16:20 | 2011-03-13 20:30 | 4 | 250 | 54054-1 | 1000 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER...CALLED ROGER MAYNARD TO SEND TRANSFORMER..TRANSFORMER CHANGED OUT....POWER ON...20.30.BB//VER/CRB IDC PROBABLY MORE TRAVEL TIME THAN SHOWING XXXX
9054 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2010-09-12 05:48 | 2010-09-12 11:21 | 3 | 333 | 65709-1 | 999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE BURNT OFF CREW REQUIRED 40/4 DEADEND WITH UNDERGROUND 1 CUSTOMER OFF ISOLATED ON 248-159/SEND TO MULLINS RELEASED BY CREW 078S03 STS WORK ORDER 36839983/CREW ON SITE AROUND 0830/FETR1200/VEM COD-3 ISO PO 38830248000159 VER/HFP L3/HFP IDC XXXX PAF
9055 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2008-05-12 18:56 | 2008-05-12 19:05 | 111 | 9 | 63229-1 | 999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308503// HAD TO OPEN RECLOSER ON POLE 246B-75 TO MAKE UP LOOPS // ASSOCIATED WITH OUTAGE# 62671-4// // VER/TOM IDC XXXX
9056 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-11-13 23:22 | 2018-11-14 04:55 | 3 | 333 | 4396641 | 999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA transformer - can truck. Crew enroute to replace. Replaced and restored @ 4:55. sh//cod 3 L3/HFP
9057 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2014-05-07 17:59 | 2014-05-07 19:50 | 9 | 111 | 4672271 | 999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ 296-28,REPLACE CUTOUT ALL CUST RESTORED @ 1950 PLEASE CLOSE TICKET THANKS.BT//COD 9// VER/DBM
9058 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2012-08-16 17:51 | 2012-08-16 19:42 | 9 | 111 | 4944931 | 999 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANSFORMER ON POLE 38830045B12098 AT18:52 TO MAKE REPAIRS//COD9 IDC XXXX
9059 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-10-16 08:20 | 2019-10-16 10:11 | 9 | 111 | 4144741 | 999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout going bad, line fuse melted out. changed cutout. pls close. tre L3/HFP
9060 | Hazard | 3303902 | LESLIE | WOOTON | 2012-11-22 18:09 | 2012-11-22 20:00 | 9 | 111 | 4415111 | 999 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING, FOUND BAD LIGHTNING ARRESTOR ON POLE 365C-145...ALL POWER RESTORED @ 20:00 HRS .P.HICKS COD 9//AED CREATED // VER/SDB IDC XXXX
9061 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2008-12-19 16:30 | 2008-12-19 23:10 | 27 | 400 | 60534-1 | 998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3004301/ NO OUTAGE TILL TONY CUT LOOPS AT POLE 903-74 AT 1630 POLE FIRE POLE 903-98, WHICH IS A 405, BURNTED OFF, NEED CREW TO REPLACE, WELL NEED CUTOUT AND ARRESTOR, EVERYTHING ELSE, SHOULD WORK BACK, HAVE ONE CUST OFF AT THIS TIME, CREW REQUIRED FIRE DEPT // VER/TOM L3/TOM IDCC PN54 XXXX
9062 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2020-12-11 00:42 | 2020-12-11 09:01 | 2 | 499 | 4760261 | 998 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Held until daylight per KPCO late night callout guidelines.---fuse link broken--repaired--power restored 09:01---tbl tkt comp.rom
9063 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-05-03 11:22 | 2009-05-03 19:40 | 2 | 498 | 64060-1 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP `WR # 29637159 /// COD-2 ISO POLE 38830524000161 HIT HARD ROCK REPLACED POLE AND HARDWARE ALL POWER RESTORED AT 19:40 L3/HFP IDC XXXX
9064 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2012-03-16 11:11 | 2012-03-16 15:20 | 4 | 249 | 4587811 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT // COD-4 ISO TF 37830190B00115 VER/HFP L3/HFP IDC XXXX
9065 | Pikeville | 3407102 | TOPMOST | CANEY | 2008-04-12 14:07 | 2008-04-12 19:39 | 3 | 332 | 50505-1 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 1 OF 3 FUSES OUT AT 137-35.FOUND COND FLOATING AND BLOWING INTO ANOTHER PHASE.CREW COMING TO RE-TIE COND IN ORDER TO KEEP FROM DROPPING OTHER PHASES OUT AND TAKING MORE CUSTS OUT WHEN NOT NECESSARYMADE NECESSARY REPAIRS,RE-FUSED,ALL OK AFTERWARDS VER/HFP
9066 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2013-01-14 18:54 | 2013-01-15 00:26 | 3 | 332 | 4604391 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINKOUS & RUGGLES & TACKETTAPTS 283 - 284- 285APTS( INSTALLED POWER TEMP ;TECH TO WRITE W.O. TO REPLACE U.G. THIS HAS BEEN SPLICE SEVERAL TIMES) /////WORK COMPLETED NEED TO CLOSE TICKET//IT FORCE CLOSED IDCC CNT18 XXXX
9067 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2009-05-20 07:12 | 2009-05-20 15:30 | 2 | 498 | 51060-1 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER CREW ENROUTE RELEASED BY CREW 074S02 COD-2 ISO 37820266000093 IDC XXXX
9068 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-04-20 06:49 | 2011-04-20 09:35 | 6 | 166 | 60971-1 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN XFMR CUTOUT....CAN REPLACE....//....REPLACED CUTOUT....RE-FUSED....POWER ON.....JRV.....04/20/11 /// COD-6 ISO TF 38820990A00059 VER/HFP L3/HFP IDC XXXX
9069 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2019-05-01 13:45 | 2019-05-01 15:08 | 12 | 83 | 4192591 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke braces on pole 1147A571, & on pole 1147A691 arm burnt into & pri riser cutout hanging from saddle. will need new 8ft arm, braces, cutout, arrestor, & arm bracket. No outage at this time, will keep power on until crew arrives. should be able to get service bucket to both poles. Released by crew 078H17,open line fuses @ 1345 repairs made all cust restored @ 1508 please close ticket thanks.bt ///// L3/HFP
9070 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-04-26 15:30 | 2022-04-26 18:16 | 6 | 166 | 4803521 | 996 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad transformer cutout on pole 32A00010 got it changed out and restored at 18:16
9071 | Hazard | 3309302 | VICCO | JEFF | 2014-02-23 07:49 | 2014-02-23 11:08 | 5 | 199 | 4427731 | 995 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DAYSHIFT SERVICER WILL BE DISPATCHED AT START OF SHIFT @ 1000.//COD 5// VER/DBM
9072 | Whitesburg | 3312902 | JENKINS | JENKINS | 2022-12-15 04:00 | 2022-12-15 12:17 | 2 | 497 | 4261251 | 994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout is broke on pole 381-B1-1021. cutout changed, power restored
9073 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-07-30 13:16 | 2019-07-30 17:00 | 12 | 224 | 4807471 | 994 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | Bad URD pedestal @ Lot #B-2, will need line crew to change out, Joey Reed coming to change out. Released by crew 074S05//OPENED UP PADMOUNT TRANSFORMER 38831127B00359 @ 1520 THIS OUTED 11 MORE CUSTS//Bad URD pedestal @ Lot #B-2, will need line crew to change out, Joey Reed coming to change out. Released by crew 074S05;;;replaced pedestal all power restored, opened pad mt xfmr at 15:20, back in at 16:30,,origal cust restored at17:00 Released by crew 074H07 L3/HFP
9074 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-01-05 04:41 | 2011-01-05 10:12 | 3 | 331 | 58772-1 | 993 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38322178 // XFMR FUSE OUT.....WILL RE-FUSE.....LOOKS LIKE CUTOUT DOOR HAS DETERIORATED....NOT SURE....WILL TAKE CLOSER LOOK.....TREE IN THE WAY OF ACCESS....//...TRIED FUSE....BAD XFMR.....CALLED CREW....THEY WILL BVRING TREE CREW ALSO...PLEASE SEND TO JOEY REED....THANKS....JRV....01/05/11 RELEASED BY CREW 080S01.SEND COPY TO CORY FARMER. VER/KEP L3/KEP IDC XXXX
9075 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-07-12 05:44 | 2021-07-12 14:00 | 2 | 496 | 4896051 | 992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | looks like a sleeve pulled out. 1 span primery 6a down, by truck. no grounds or tags placed by service Released by crew 078H03
9076 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-03-15 10:59 | 2021-03-15 19:15 | 2 | 496 | 4336691 | 992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Replaced one span of sec and new service drop. Also repaired dn guy. Bad 25 kva 12 kv. Crew required , would be best to bring small material handler. Meter laying on porch please check voltage inside meterbase. Released by crew 078S11 crew on site FETR 19:45 LRM all pwr restored 19:15 please close ticket LRM
9077 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2016-04-28 17:01 | 2016-04-28 21:09 | 4 | 248 | 4139271 | 992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED TRUCKS OK NEED 25KVA RELEASED BY CREW 078S03--CREW ON SITE--CHANGED OUT XFMR UPGRADE TO 25KVA---CUTOUT AND LA---TBL TKT COMP---RMV/ ISO 38830249000103/ COD 4/ VER/BOW
9078 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2017-04-06 10:19 | 2017-04-06 10:51 | 31 | 32 | 4621141 | 992 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT CRACKED ON STEPDOWN POLE 37820025D30446. OPENED UP TO REPLACE. // OPENED @ 1019 CLOSED @ 1051//TOM L3/HFP HFPC TOF1010 TON1112 AJB
9079 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-04-23 18:19 | 2020-04-24 10:50 | 1 | 991 | 4742481 | 991 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 transformer @ 93-259. No trucks to pole, No six wheeler. Hold till daylight per vernon mullins Released by crew 078S02 //crew on site FETR ? fetr 12:30 ¦¦ outage extended due to customer - POLICE WERE CALLED ON 04/23 FOR SERVICER TO GAIN ACCESS TO PROPERTY
9080 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-09-02 20:02 | 2012-09-02 23:20 | 5 | 198 | 4996951 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TOLLIVER & MCCANN & MULLINSBAD LIGHTING ARRESTOR ON POLE 354-117 IT BLEW INTO CLEAR AFTER REMOVING VINES FROM POLE -POWER RESTORED AT 23:20 COD-5 ISO LF 38830356000008 VER/HFP L3/HFP IDC XXXX
9081 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-09-03 07:00 | 2012-09-03 12:30 | 3 | 330 | 4998491 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1147-571 BAD 10KVA NEED 25KVA TRUCK TO POLE NEED CREW RELEASED BY CREW 078S08//COMPLETE PRTOLLIVER AT 12:30 CLOSE TKT/// ///VER/CRB L/3 CRB IDC XXXX
9082 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-04-06 10:50 | 2011-04-06 12:20 | 11 | 90 | 50449-1 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREWS OPENED SWITCH IN ORDER TO REPLACE BAD CROSSARMS ON POLE 648-5//COD 11// VER/DBM IDC XXXX
9083 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-09-07 15:18 | 2009-09-07 18:36 | 5 | 198 | 52772-1 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR FUSE IS OUT,WILL RE-FUSE,MAY HAVE TO TRIM SOME LIMBS,ALSO A XFR CUTOUT TO REPLACEREPLACED CUTOUT,CUT LIMBS AWAY,RE-FUSED AND RESTORED.ALL OK AFTERWARDS//COD 5// VER/DBM IDC XXXX
9084 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-03-10 11:51 | 2008-03-10 17:21 | 3 | 330 | 55879-1 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409502// DOUG HALL 3838 REPORTED FUSE BLOWN// LOOKS LIKE FUSE LINK HAS BROKEN ON CUTOUT. I AM GOING TO REFUSE CUTOUT. I REFUSED CUTOUT AND IT STAYED IN.//VER/CRB IDC XXXX
9085 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2012-07-13 13:30 | 2012-07-13 15:00 | 11 | 90 | 4712521 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNED TOP OF POLE BAD WILL NEED CREW TO MAKE REPAIRS, I HAVE TALKED TO CECIL AND HE IS ON HIS WAY OPENED AT 1330 MD FILED COD-11 RESTORED 1500 IDC XXXX
9086 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-01-25 07:37 | 2015-01-25 10:55 | 5 | 198 | 4962121 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER IS HERMAN WEST AT 110 TIGHT ELKINS ROAD, ALL OUT/ OPEN WIRE SEC DOWN TOWARDS POLE 1-8, NEED 1 A-MAN AND MATERIAL HANDLER/COD5/,,WIRE BURNT DOWN UNDER CONNECTION, ALL REPAIRS MADE POWER BACK ON// VER/ ADH
9087 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-05-13 22:42 | 2009-05-14 02:00 | 5 | 198 | 54340-1 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSF BAD RELEASED BY CREW 079S01// JOEY THE WR# 29819933 // //VER/GAH IDC XXXX
9088 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2016-01-13 10:25 | 2016-01-13 10:55 | 33 | 30 | 4616601 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO REPAIRS FOR ORDER 4615511//OPENED SIDE TAP UP TO REPAIR FAILED LOOP ON POLE 43-13//COD 33// VER/DBM AJB
9089 | Hazard | 3302703 | HAZARD | HAZARD | 2008-08-06 18:29 | 2008-08-06 22:50 | 6 | 261 | 66171-1 | 990 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3302703// A & C LINE FUSES BLOWN ON POLE #272D2-437..BAD CUTOUT ON POLE #272D3262 ..CLOSED LINE FUSES IN AT 20;26 RESTORING POWER TO ALL THREE PHASE RESTORED POWER TO LAST CUSTOMER AT 22;50 /? COD 6 IDCC STP MISSING XXXX
9090 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2020-03-17 15:30 | 2020-03-17 15:53 | 43 | 23 | 4485731 | 989 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | Tie wire broke on pole 126-38 laying agianst pole top pin/// will need to open line fuse on pole 126-25 when help arrives to minimize outage due to difficult location// Opened line fuse @ 15:30 /// Repairs made closed line fuse in @ 15:53 and restored service
9091 | Hazard | 3303901 | LESLIE | HYDEN | 2015-02-28 03:28 | 2015-02-28 07:35 | 4 | 247 | 4086891 | 988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 387-C-318 WE HAVE A C/O BROKEN LINE C/O. NEED ONE A LINEMAN AND BIG BUCKET///// REPLACED LINE C/O, POWER RESTORED L3/DKGXXXX VERIFIED WITH VOICE RECORDER
9092 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2019-03-08 15:31 | 2019-03-08 16:47 | 13 | 76 | 4962731 | 988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt up neut & hot leg. all repairs made. pls close. tre
9093 | South Williamson | 3200302 | BELFRY | TOLER | 2021-11-30 17:47 | 2021-12-01 10:15 | 1 | 988 | 4135971 | 988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | cust has a bad transformer.only cust on that transformer..25kva 7200.hold till morning.paul layne seen the job..he knows what material to bring.if he dont get the job .who ever gets it make contact with paul.he know what to bring Released by crew 079S03
9094 | Hazard | 3310502 | HADDIX | CANOE | 2009-02-23 16:23 | 2009-02-23 17:15 | 19 | 52 | H50810-1 | 988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3310502// HAD TO OPEN TO COMPLETE REPARIS ASSOCIATED WITH 50617-1 (GOT TAKEN OVER HAD TO RE-CREATE THE OUTAGE IN HOIS)// OPEN FUSE @ 1623 AND CLOSED @ 1715// 19 ON TAP (INCLUDING MISMAPPED TRANSFOMER SHOULD BE ON LOAD SIDE OF FUSE NOT LINE SIDE) 3 ON COD// - TAP OUTAGE ON DUPLICATE// THIS ONLY COVERS TRANSFORMER // VER/TOM L3/TOM IDC XXXX
9095 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-02-07 14:45 | 2016-02-07 18:52 | 4 | 247 | 4681781 | 988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE FAILED, BYPASSED CLF ( NONE ON TRUCK ) AND REFUSED TRANSFORMER, ALL WORK COMPLETE / GXJ// VER/ ADH
9096 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-09-28 13:13 | 2019-09-28 14:05 | 19 | 52 | 4067851 | 988 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Step down on pole 38830117B00033 open, patrolling Step down on pole 117-33 open, patrolling, broken fuse, back in at 14:05
9097 | Paintsville | 3401102 | FALCON | SALYERSVI | 2009-05-31 08:27 | 2009-05-31 10:48 | 7 | 141 | 53135-1 | 987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN HANGING DOWN, HAS BURNED TRU CROSSARM..CHG CUTOUT REFUSED FUSE...BB//COD 7// VER/DBM
9098 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-05-03 08:58 | 2008-05-03 14:27 | 3 | 329 | 56546-1 | 987 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008701//140-513 BAD 50 KV 19.9 2-19.9 CUTOUTS RELEASED BY CREW 078S08/CREW ON SITE/VEM/REPAIRS MADE POWER RESTORED TO ALL CUST 1427/PLEASE CLOSE TICKET /THANKS /VEM// COD 3// VER/DBM IDCC PN513 XXXX DEB OK
9099 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-05-13 02:32 | 2016-05-13 10:45 | 2 | 493 | 4210881 | 986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED CURRENT LIMITING FUSE/ON @ 1045// VER/ ADH
9100 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-05-14 04:56 | 2009-05-14 05:54 | 17 | 58 | 54566-1 | 986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3010601 - -REPLACED BAD ARRESTOR ON POLE 39831148B40345/ VER/KEP L3/KEP
9101 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-12-11 22:57 | 2010-12-11 23:55 | 17 | 58 | 65436-1 | 986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR 38077123// POLE 70-3092 BAD CUTOUT POLE 70-3085 30T OUT B PHASE // 16 B PHASE CUST - 1 3 PHASE CUST // VER/TOM IDC XXXX
9102 | South Williamson | 3200301 | BELFRY | BELFRY | 2013-07-18 19:17 | 2013-07-18 20:15 | 17 | 58 | 4551811 | 986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BURNED UP CUTOUT DOOR THAT PROTECTS SIDE TAP.//COD 17// VER/DBM IDC XXXX
9103 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-06-05 07:08 | 2014-06-05 15:21 | 2 | 493 | 4982591 | 986 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING BAD CUTOUT ON 38830404000066 APR AT 1521 CLOSE TICKET. PLEASE SEND LOYD R A COPY OF THIS TICKET POLE 404-147 HAS BOTH BRACEES BROKE NEEDS REPLACED VER/CRB
9104 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-08-19 18:13 | 2021-08-19 21:30 | 5 | 197 | 4123051 | 985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | opening line fuse to isolate pole fireBELIEVE DE INSULATOR BREAKING DOWN@1082-102/////OPENED@1082-98BELIEVE DE INSULATOR BREAKING DOWN@1082-102/////OPENED@1082-98///////MADE REPAIRS&RESTORED@21:30
9105 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-01-30 08:46 | 2008-01-30 12:03 | 5 | 197 | 61979-1 | 985 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3000102//BAD HOT-TAP VER/ARN IDC XXXX
9106 | Pikeville | 3401001 | ELWOOD | DORTON | 2010-06-07 14:50 | 2010-06-07 18:07 | 5 | 197 | 58444-1 | 985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35453430 // CUTOUT BROKE DOWN AND BURNED TOP OF POLE 310-52 OFF. CREW IS ON THE WAY TO PUT EXT. ON POLE. IT BLEW LINE FUSE ON POLE 310-49.//ISO 37830310000049//COD 5//MD FILED//CUTOUT BROKE DOWN AND BURNED TOP OF POLE 310-52 OFF. CREW IS ON THE WAY TO PUT EXT. ON POLE. IT BLEW LINE FUSE ON POLE 310-49. RELEASED BY CREW 074S01 COD-5 VER/HFP L3/HFP IDCC FP NULL, PN167 XXXX
9107 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2010-04-08 10:31 | 2010-04-08 13:48 | 5 | 197 | 60765-1 | 985 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CONFIRMED LINE FUSE OUT PATROLLING LINE//19.9 ARRESTOR BAD ON XFMR AT POLE 37830174B00475 COD-5 VER/HFP L3/HFP IDC XXXX
9108 | South Williamson | 3411401 | DEWEY | INEZ | 2015-05-27 15:44 | 2015-05-27 19:50 | 4 | 246 | 4473431 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKE ON POLE38830766B00067// RELEASED BY CREW 079S01//COD 4//MADE MDC TO SHOW TRANS ON LOAD SIDE OF L/F//LINE CUTOUT BROKE ON POLE38830766B00067// DUPLICATE/SAME AS 4473501/ ISO 38830766B00067/ COD 4/ VER/BOW
9109 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2021-11-14 12:32 | 2021-11-14 18:00 | 3 | 328 | 4090721 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 1139A-92.myles robinettes crew came and changed the transformer and we got the fuse on pole 1139A-92 back in at 18:00
9110 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-03-26 07:34 | 2010-03-26 11:40 | 4 | 246 | 54576-1 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34409641 //BAD 15KVA XFMR ON POLE 876-183. ONLY ONE CUSTOMER AFFECTED. CREW ENROUTE. RELEASED BY CREW 076S02.CHANGING NOW//VER/CRB IDC XXXX
9111 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-10-06 11:49 | 2014-10-06 17:17 | 3 | 328 | 4557471 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 67D278 BAD 7200-25KVA, CUT OUT YARD DOG. 305 GREENHILL RD // SEE ORDER 4559301 FOR OUTAGE TO REPLACE TR //LINE FUSE OPEN ON POLE 67-272 @ 16:25 CLOSED @ 17:17// COD 3/// ISO 38830067D00272// VER/BOW VER/DKG L3/DKGXXXX THIS IS FOR TRANSFORMER COUTAGE
9112 | Paintsville | 3401102 | FALCON | SALYERSVI | 2017-04-04 02:00 | 2017-04-04 03:22 | 12 | 82 | 4610751 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | RELATED TO 4610701//OPENED FUSE 875-A-167 IN ORDER TO MAKE REPAIRS TO FAILED INSULATOR ON 875-A-53//COD 12// VER/DBM // TIME PER VOICE REC = L3/HFP XXXHFP
9113 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-03-05 21:58 | 2013-03-06 06:10 | 2 | 492 | 4874971 | 984 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | NEED 3 MAN PRC CREW--HOT TAP BURNT OFF ON POLE 38830045B12056--SAME PHASE FUSE OUT ON RANSFORMER BANK POLE 38830045B12275 TRUCKS TO ALL POLES RELEASED BY CREW 078S07 REPAIRED IDCC CNT11 XXXX
9114 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-08-15 10:27 | 2010-08-15 15:55 | 3 | 328 | 55747-1 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE CREW REQD TO REPLACE BAD 50 KVA REFUSED C/O CAME BACK OUT POLE 38830184A00331 TRUCK TO POLE O.K.....STAMPER RELEASED BY CREW 078E04
9115 | Hazard | 3303903 | LESLIE | HALSFORK | 2013-02-19 17:45 | 2013-02-19 19:48 | 8 | 123 | 4830051 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 384-102 HAS ROTTED OFF AND LEANING WILL NEED TO REPLACE WITH 40 CL4 PTP AND CLEVIS AND SPOOL IN A BOTTOM MAYBE TRUCK ACCESSIBLE RELEASED BY CREW 077S01 REPLACED POLE AND RESTORED CUSTOMERS OPENED LINE (LIFTED CLAMP AT POLE 37840384000030) AT 1745 AND RESTORED AT 1948//COD 8//ISO// VER/DBM IDC XXXX
9116 | Pikeville | 3401001 | ELWOOD | DORTON | 2019-04-08 09:25 | 2019-04-08 12:09 | 6 | 164 | 4068521 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 287-09..will patrol////xfm. cutout broken on pole 263-116..will need flagging to safely make repairs..talked to PR.flagging crew enroute..restored
9117 | Hazard | 3307301 | BULAN | ARY-HEINE | 2020-11-14 05:24 | 2020-11-14 13:36 | 2 | 492 | 4674631 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr got one on the way .comp
9118 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-06-16 21:50 | 2018-06-17 03:18 | 3 | 328 | 4609171 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | attempted to call customer, no response///crew required bad 25kva material handler yes Released by crew 078S03/arrived RM power on at 03:18 please close tic RM//cod 3
9119 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-07-04 06:32 | 2012-07-04 12:00 | 3 | 328 | 4305151 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 078H08RELEASED BY CREW COMPLETE
9120 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2018-02-17 05:16 | 2018-02-17 08:00 | 6 | 164 | 4853801 | 984 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with late night callout guidelines/ New 40T line fuse on 38830785C40544 broke. Restored @ 8:00. Please add 40T line fuse protecting both latterals and xfmr on 785-544. sh/ ISO 38830785C40544/ COD 6
9121 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2009-12-27 20:22 | 2009-12-28 12:45 | 1 | 983 | 58724-1 | 983 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BROKE
9122 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-03-12 20:17 | 2022-03-13 12:40 | 1 | 983 | 4617371 | 983 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 5KVA 7200 on pole 225-D-219, manual. Phillip Hicks said a crew would replace this with a 10KVA in the morning. Released by crew 077S04.comp.. CCW
9123 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-05-19 02:53 | 2018-05-19 19:15 | 1 | 982 | 4374801 | 982 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole rotted off at ground fell over , manuel pole in bottom no yard dog acess, 30/6 clevis spool 5 men hand set, told cust would help mount meter base back to house ,no damage to base just pulled loose Released by crew 077H14 replaced pole and repairs made , power restored at 1915 jkc
9124 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-07-11 23:53 | 2012-07-12 16:15 | 1 | 982 | 4692631 | 982 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED RIGHT OF WAY CREW, WILL RETURN IN THE AM TO RESTORE THIS CUSTOMER. CUTOUT FAILED. TOP OF POLE 169-65 BURNED OFF. MIKE COLEMAN IS REPLACING THE POLE. RELEASED BY CREW 074S02 IDC XXXX
9125 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-01-02 18:09 | 2014-01-03 10:30 | 1 | 981 | 4219831 | 981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG BURNDT INTO ON TRANS. POLE 379-244, THIS IS MANUAL AND WILL NEED 1 MAN TO HELP MAKE REPAIRS. 1 CUST. OUT. RELEASED BY CREW 075H01. CHANGED CONNECTOR AND REFUSED XFMR VER/CRB IDC XXXX
9126 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-11-14 08:46 | 2015-11-14 10:35 | 9 | 109 | 4447211 | 981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE// VER/ ADH
9127 | Paintsville | 3401802 | INDEX | HOSPITAL | 2009-02-18 12:41 | 2009-02-18 14:30 | 9 | 109 | 64214-1 | 981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ALL FUSES ARE IN NOW BUT THE CENTER PHASE...THESE PEOPLE HAVE POWER NOW...BB IDC SEE 64239-1 ALSO XXXX
9128 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-10-27 18:54 | 2008-10-28 11:15 | 1 | 981 | 59711-1 | 981 | DISTRIBUTION LINE | EQUIPMENT FAILURE | PEDESTAL | 3409301//BREAKER BAD IN SERVICE PEDESTAL. LOOKING FOR PARTS TO MAKE TEMPORARY REPAIRS WITH. DUTY SUPERVISOR NOTIFIED. TRIED TO MAKE TEMP REPAIRS WITH NO SUCCESS. WILL REPAIR IN THE MORNING. RELEASED BY CREW 076S02//REPAIRS MADE TO PEDSTALL BUILT CUSTOMER STILL NEEDS TO DO SOME WORK TO GET BACK IN SERVICE , TALKED WITH CUSTOMER GETTING ELECTRICAN.TCM//VER/CRB IDC XXXX
9129 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2020-06-01 08:55 | 2020-06-01 13:00 | 4 | 245 | 4938311 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830044A00143 bad 12 kv c/o . line fuse. arm burnt almost thru. Released by crew 078S07 back in at 1300
9130 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2008-08-01 07:56 | 2008-08-01 09:34 | 10 | 98 | 63278-1 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | A PHASE SWITCH HAS LEAD BURNT OFF COD-20 CUSTOMERS OUT// CREW CALLED TO REPLACE SWITCH/ B FRALY TO REPLACE RELEASED BY CREW 078S07---REPLACED BOLTS ON LOOP PAD VER/HFP IDC XXXX
9131 | Hazard | 3303901 | LESLIE | HYDEN | 2010-05-09 15:25 | 2010-05-09 19:30 | 4 | 245 | 58705-1 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 120/240//VER/CRB IDC XXXX
9132 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-08-29 08:05 | 2013-08-29 09:45 | 12 | 100 | 4717871 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | "C" PHASE LINE FUSE OUT, ISOLATED XMER BANK AT POLE 785-1087 (BAD C/O) COD 12CUTOUT BROKE ON POLE 785-1087//LINE FUSE BLOWN ON 785-967///GOING TO ISOLATE XFMR BANK AND GET LINE BACK HOT//CREW GOING TO CHANGE ALL 3 CUTOUTS//CLOSED FUSE AT POLE 967 AT 9:25//CREW ON SITE TO CHANGE CUTOUTS/RESTORED TRAN AT 0945 VER/KEP IDC XXXX
9133 | Cannonsburg | 3110901 | WURTLAND | WURTLAND | 2021-10-07 11:42 | 2021-10-07 12:31 | 20 | 49 | 4327241 | 980 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 69/12kV TR 1 tripped from service due to failed bushing at station At 1231 Closed DA SWS at 1098-B3-3165 restoring via transfer to Highland/Wurtland restoring 20 CC
9134 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2009-03-16 10:15 | 2009-03-16 12:35 | 7 | 140 | 59049-1 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3409402// FAILED CUTOUT.//COD 7// VER/DBM IDC XXXX
9135 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2013-06-18 04:15 | 2013-06-18 08:20 | 4 | 245 | 4361491 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL CHECK IN THE AM ON 6-18-13 POLE 45-4014 15T TRANS FUSE BROKE SEND NOTE TO RAYBURN PLATFORM BOARDS FALLING IN ALLEY NEEDS TO BE REPAIRED CUTOUTS NEEDS CHGED TO VER/HFP L3/HFP IDC XXXX
9136 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-01-31 05:25 | 2012-01-31 09:30 | 4 | 245 | 4307201 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE BLOWN.---- BAD CUTOUT, NEED CUTOUT, ARRESTOR, TEE BRACKET AND BUCKET TRUCK.---- REPLACED CUTOUT, POWER RESTORED. VER/TOM L3/TOM IDC XXXX
9137 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2019-03-19 06:08 | 2019-03-19 14:18 | 2 | 490 | 4998911 | 980 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | APPEARS TO BE A SHORTED-OUT SERV DROP,WILL REPAIR////WRONG ABT SERV,NO PROBLEM THERE,ONLY LOOKED THAT WAY///////XFRF WAS OUT,DOOR DIDNT DROP.RE-FUSED&RESTORED POWER,ALL OK AFTERWARDS.FUSE ROTTED INTO
9138 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2008-01-04 07:51 | 2008-01-04 09:20 | 11 | 89 | 53576-1 | 979 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 2206403// ASSOCIATED W/OUTAGE 53451-1// OPENED RECLOSER TO MAKE REPAIRS ON BROKE NEUTRAL OPENED @ 0751 CLOSED RECLOSED @ 0924 WILL NEED TO ADJUST IN HOIS//// VER/TOM IDCC CNT75 XXXX
9139 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-07-12 05:04 | 2010-07-12 10:30 | 3 | 326 | 65176-1 | 978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35939364 // 25 KVA 7200 120/240 BAD CALLING FOR LINE CREW RELEASED BY CREW 077S04 COD-3 VER/HFP L3/HFP IDC XXXX
9140 | Paintsville | 3401102 | FALCON | SALYERSVI | 2009-08-02 04:37 | 2009-08-02 07:20 | 6 | 163 | 58658-1 | 978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 207 ISOLATED IT DOSENT FEED ANYTHING//// GIVING FUSE A SHOT/// COMPLETE TT VER/LDA IDC XXXX
9141 | Hazard | 3307301 | BULAN | ARY-HEINE | 2008-11-08 08:01 | 2008-11-08 16:10 | 2 | 489 | H63217-1 | 978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW WILL WORK THIS ORDER NEXT . C/L TR IN HAZARD AT THIS TIME. POLE BURNED OFF BAD LINE CUTOUT POLE 153-66 // LOAD BUSTED SECTIONALIZERS ON POLE 177-287 @ 1317 (INTERRUPTING 494 CUSTOMERS) TO DE-ENERGIZE AND OPEN 3-600 AMP SWICHES @ POLE 153-84// OPENED SWITCHES @ 1326 AND CLOSED SWITCHES @ 1610 // CLOSED SECTIONALIZERS ON POLE 177-287 @ 1328 RESTORING 43 CUSTOMER// LEAVING 451 CUSTOMERS OUT OF SERVICE FOR DURATION OF JOB//// IDCC DUP FOR ORIGINAL 2 CUSTOMERS, CCF XXXX
9142 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-12-15 11:46 | 2013-12-15 17:12 | 3 | 326 | 4163211 | 978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA, NEED TO REPLACE WITH 25 KVA 7200. MANUAL. NEED 3 MEN AND YARD DOG. RELEASED BY CREW 077S04 REPLACED TRANSFORMER AND RESTORED POWER AT 1712 SEE 4163681 VER/CRB L3/HFP
9143 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2009-07-20 20:37 | 2009-07-20 23:20 | 6 | 163 | 51080-1 | 978 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE CREW IN RT. TO CHANGE BAD CUTOUT ON POLE # 1027-604 REPLACED CUTOUT VER/TOM L3/TOM IDCC CNT21 PH C CUTOUT XXXX
9144 | Hazard | 3303902 | LESLIE | WOOTON | 2012-07-25 22:55 | 2012-07-26 15:12 | 1 | 977 | 4829581 | 977 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER CALLED CUSTOMER AND REPORTS ALRIGHT TO WAIT TILL DAYLIGHT.FOUND BAD SEC BUSHING WILL NEED 25KVA 19.9 CREW WILL CALL FOR TICKET RELEASED BY CREW 077S01//COD 1// VER/DBM
9145 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-11-29 15:14 | 2015-11-29 16:15 | 16 | 61 | 4492511 | 976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED AND BURNT TOP OF POLE 806-155 OFF. ISOLATED FAULT WITH HOT-LINE CLAMP ON 806-154. CLOSED LINE FUSE @ 16:15 RESTORING ALL OUTAGED CUST EXCEPT XFMR ON 806-154. RESTORED FINAL OUTAGED CUSTOMER ON 806-154 @ 17:15. LEFT UNUSED LATTERAL OPEN - FIRE IS OUT AND PRIMARY IS CAUGHT OFF. SH RELEASED BY CREW 076S02//MADE AED//NO ONE ON TRANS 806-154 VER/CRB
9146 | South Williamson | 3411401 | DEWEY | INEZ | 2008-11-19 16:07 | 2008-11-19 20:11 | 4 | 244 | 50055-1 | 976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411401//LATERAL FUSE OUT ON 648-A-41.....PATROLLING LATERAL....RELEASING BOTH TICKETS BACK, SO YOU CAN ROLL THIS OUTAGE UP...JRV ....//...ALL 5 SPANS OF THIS LATERAL LOOK OK.....FUSE MAY HAVE MELTED OUT OR BROKE....WILLL NGIVE IT A TRY WHEN I GET BACK TO IT.....WILL BE AWAY FROM TRUCK... ISSUED MAP DISC// VER/TOM IDCC PN70 XXXX
9147 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2008-06-22 12:48 | 2008-06-22 14:50 | 8 | 122 | 51792-1 | 976 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3008001//E MAIL TO RAYBURN-BAD ARRESTOR NEEDS REPLACED-CAN REACH WITH LINE BUCKET // MAP NEEDS FIELD CHECKED// // VER/TOM
9148 | Hazard | 3311103 | STINNETT | WENDOVER | 2012-06-07 09:00 | 2012-06-07 10:15 | 13 | 75 | 4890161 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ALMOST EVERY L/A IN THE HOLLOW IS BLOWN VER/KEP IDC XXXX
9149 | Hazard | 3309003 | JEFF | VIPER | 2019-01-02 09:44 | 2019-01-02 12:59 | 5 | 195 | 4622081 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Power on refused trasformer on 368D/53 bad took line fuse out on 368D/15..changed out bad xfmr.all restored p.hicks
9150 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2018-08-29 09:20 | 2018-08-29 14:45 | 3 | 325 | 4010551 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required
9151 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2020-07-23 13:12 | 2020-07-23 16:27 | 5 | 195 | 4216541 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | complete. tre.
9152 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-01-09 06:40 | 2014-01-09 09:55 | 5 | 195 | 4263611 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BROKEN CUTOUT. BAD 25 KVA TRANSFORMER, REPLACED CUTOUT AND TRANSFORMER WITH 50 KVA. VER/CRB L3/HFP
9153 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2008-07-09 19:35 | 2008-07-09 20:00 | 39 | 25 | 66663-1 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001202// 69-1599 40T BROKE - TOT COD 50// MAP WRONG - SENT MAP DISC/// ISO 38830069A41599 IDCC PN4741 XXXX
9154 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2021-01-01 12:43 | 2021-01-01 18:08 | 3 | 325 | 4841021 | 975 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kVa/need 1 man/material handler/10KVA LEAKING OIL.NEEDS REPLACED.SEND 25KVA,MATERIAL BUCKET,1 MAN10KVA LEAKING OIL.NEEDS REPLACED.SEND 25KVA,MATERIAL BUCKET,1 MAN.replacing porcelin cutout with polymer also////////////REPLACED XFR&RESTORED POWER
9155 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-07-21 17:41 | 2018-07-22 09:55 | 1 | 974 | 4829501 | 974 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Neutral Broke in Ser Drop at pole 166-206. Need to replace service, apx 50. Pole is in back yard. XFMR is pole 117. Beware of dog signs & dog barking close to pole-no one home at 117. BJ Released by crew 074E04/// Replaced service drop/// Tension splice pulled into no obvios reason/// Everything ok now/// Send copy to Peggy Wysong//SENT TO CLAIMS
9156 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2019-01-30 04:43 | 2019-01-30 12:50 | 2 | 487 | 4733121 | 974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 trans. @ 38831124D00014, will need a line crew, no truck access, will also need a large trans. bag, blowed top bushing off of trans. Released by crew 074S05//RESTORED 1250 L3/HFP
9157 | Pikeville | 3120102 | STANVILLE | TRAM | 2019-11-12 11:19 | 2019-11-12 14:40 | 6 | 201 | 4024911 | 974 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 7200 xfmr.This is no truck approach I have contacted PR and he is getting line crew to come and replace it. Will be best to bring 25kva to replace it with. Released by crew 076S03 off 1350 - on 1440
9158 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-10-18 22:31 | 2008-10-19 00:50 | 7 | 139 | 56935-1 | 973 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 1SPAN WIRE DOWN AT FUSE POLE == SPLICE FAULTED == REPAIRED VER/ARN IDC XXXX
9159 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-03-24 18:09 | 2018-03-25 10:22 | 1 | 973 | 4053671 | 973 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew req, broke c/o on pole 381-181, maybe able to get trucks to this Released by crew 078S06 1022
9160 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-06-03 12:43 | 2008-06-03 15:25 | 6 | 162 | 54931-1 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3401102 / ETA 1330 /..50 T FUSE BLOWN ON 851-372..TOOK HOT TAP OFF ON POLE 851-2...REFUSED 851-372...TOP OF POLE BURNED OFF..851-393..ALL BACK ON EXCEPT 6 CUSTOMERS..BB RELEASED BY CREW 076S01// ON SITE MAKING REPAIRS TC MILLER
9161 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-02-23 15:51 | 2011-02-23 16:45 | 18 | 54 | H60527-1 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | C PHASE WAS OPENED COD 12//OPEDED A&B AT 1551 //1 PHASE DOWN,WILL REPAIR///////MADE REPAIRS AND RESTORED//VER/CRB IDCC DUP TO OPEN OTHER PHASES XXXX
9162 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-05-31 11:17 | 2008-05-31 15:20 | 4 | 243 | 53216-1 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3403201// ARRESTER HAS BROKEN INTO. I AM GOING TO CLEAR IT UP AND REFUSE TRANS. I CLEARED ARRESTER AND REFUSED TRANS.//COD 4//NO WIRE DOWN// VER/DBM IDC XXXX
9163 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2018-03-01 18:30 | 2018-03-01 22:33 | 4 | 243 | 4895191 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke xfr cutout complete//cod 4
9164 | Pikeville | 3407103 | TOPMOST | KITE | 2011-08-22 07:26 | 2011-08-22 12:50 | 3 | 324 | 4740941 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S03 PRIMARY OPEN DUE TO BAD CUTOUT. I HAVE CUST AT POLE 210-67 SWITCHED OVER TO A PHASE. WE HAVE CUTOUT CHANGED ON POLE 210-47. CLOSED IN EVERYTHING OK. I SWITCHED CUST ON POLE 210-67 BACK OVER ON B PHAASE.//VER/CRB IDC XXXX
9165 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2014-05-01 04:02 | 2014-05-01 05:23 | 12 | 81 | 4653611 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 2300// POLE FIRE ON POLE 142-178 35/5 TRUCKS TO POLE,NEED TO LOWER XFORMER INST. TRUCKS TO POLE. RELEASED BY CREW 078S01//NO OUTAGE TIL 2300//REPLACE POLE TOP AND CUTOUT/ARRESTOR//OPENED LF ON PL#142-259 @ 04:02//TAGGED TO CREW(VIRGIN)//CLOSED LF @ 05;23///PWR CK OK///TBL TKT COMPLETE 12 CUSTOMERS VER/ARN L3/HFP HFPC PN 38830142C00178 FP38830142000178 CDC92 XXXX
9166 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-09-26 16:18 | 2010-09-26 19:00 | 6 | 162 | 53740-1 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT ON THIS POLE I OPENED THE TRANSFORMER UP AT 1618 CREW ENROUTE REPLACED FAILED CUTOUT. VER/KEP L3/KEP IDC XXXX
9167 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2021-10-01 04:46 | 2021-10-01 10:10 | 3 | 324 | 4307001 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva, 120/240 7200 . trk ok-TR needs to have 2 primary bushings//Released by crew 078S07. changed bad transformer time restored 1010
9168 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2016-03-10 11:15 | 2016-03-10 11:27 | 81 | 12 | 4833771 | 972 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | OPENING RECLOSER BECAUSE THE BYPASS SWITCH WAS BROKE/ REPLACING BYPASS SWITCH THEN PUTTING RECLOSER BACK ON/ OPENED @ 1115/ CLOSED @ 1127// ISO 37830380C00053/ COD 81/ VER/BOW AJB
9169 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2011-02-12 16:12 | 2011-02-12 17:49 | 10 | 97 | 56444-1 | 970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE--BAD ARRESTOR POLE 38830162C00040--TRUCK WHEN DRY VER/PDP IDC XXXX
9170 | Pikeville | 3421001 | BREAKS | CITY | 2014-02-13 03:25 | 2014-02-13 19:35 | 1 | 970 | 4377901 | 970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER WILL CHECK ONCE THE ROAD CONDITIONS IMPROVE// BAD 25 KVA TRANSFORMER HERE CREW REQUIRED. CANNOT USE TRUCK. NEED 4 LINESMEN AND A MANUAL TREE CREW TO DO THIS. 7200/120/240. RELEASED BY CREW 074S02 VER/KEP
9171 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-07-06 22:35 | 2016-07-07 14:45 | 1 | 970 | 4552251 | 970 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NEED LINE CREW TO REPLACE NO TRUCK RELEASED BY CREW 078S05,,CREW ON SITE,,XFMR REPLACED,,ALL POWER RESTORED// VER/ ADH
9172 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2010-06-20 15:37 | 2010-06-20 21:00 | 3 | 323 | 51826-1 | 969 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400601// STS WR# 35644300 //10 KVA TRANSFORMER IS BURNED UP ON POLE 235-9. DALE IS SENDING HELP.. WE CHANGED TRANSFORMER. THERE WAS ACTUALLY ONLY 1 CUSTOMER OUT.IDCC PN6 XXXX
9173 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-09-15 17:00 | 2021-09-15 21:02 | 4 | 242 | 4245321 | 968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830262000106 c/o on x-arm broke crew req-ds091521 Released by crew 078S01//arrived RM opening LF 262-142 to safely climb pole
9174 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2020-02-02 09:26 | 2020-02-02 13:28 | 4 | 242 | 4354461 | 968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on manual pole.repaced cutout restored power at 13:28..
9175 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-01-22 19:01 | 2012-01-23 11:09 | 1 | 968 | 4283021 | 968 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 25KVA 19.9 , CUT-OUT AND TEE- BRKT., 4 MEN , & LINE TRK. MANUAL JOB. CUST. AGREED TO WAIT UNTIL FIRST THING MONDAY. RELEASED BY CREW 077H13 // CHANGED TRANSFORMER ,RESTORED POWER AT 1109 JKC //COD 1 IDC XXXX
9176 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-09-04 19:23 | 2011-09-05 11:30 | 1 | 967 | 4810911 | 967 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DUTY SUPERVISOR SAID WAIT UNTIL DAYLIGHT TO START ON THIS, CANT SEE ANYTHING ROW IS SO BAD. RELEASED BY CREW 077S04 COD-1 ISO LF 37830225D00273 VER/HFP L3/HFP IDCC PN529 XXXX
9177 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-12-17 09:57 | 2013-12-17 12:15 | 7 | 138 | 4167261 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | OPEN AT 957 TO REPAIR // CLSED AT 1215//COD 7 VER/HFP L3/HFP
9178 | South Williamson | 3411401 | DEWEY | INEZ | 2017-12-05 10:51 | 2017-12-05 12:00 | 14 | 69 | 4622201 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 744-208 and744-27(not on map)//broke cutout on pole 744-217//repairs made//restored at 12:00//complete//em /// SENT EMAIL TO ENGINEERING TO VERIFY & CORRECT POR MAP
9179 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2020-10-01 20:04 | 2020-10-02 01:26 | 3 | 322 | 4519051 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830453000100 c/o has cracks and on metal t bracket--need tree crew and crew --nbt--ds100120 Released by crew 078S01arrived RM tree crew to cut trees around pole replaced cutout &arrester power on @01:26 please close tic RM
9180 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-11-27 15:23 | 2019-11-27 20:45 | 3 | 322 | 4090001 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Need to replace 7.2 cut, bracket, and arrester. Truck accessible. restored power at 20:45/ ISO 38831059D00203/ COD 3
9181 | Whitesburg | 3401301 | FLEMING | NEON | 2011-01-28 17:31 | 2011-01-28 18:13 | 23 | 42 | 51474-1 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE IS AT 331-116BAD CUTOUT BURNED TOP OF POLE TOOK POWER OFF AND PUT POLE EXTENION ON POLEBAD CUTOUT BURNED TOP OF POLE TOOK POWER OFF AND PUT POLE EXTENION ON POLE I TOOK POWER OFF AT17:31//VER/CRB IDC DCMT XXXX
9182 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-09-28 12:27 | 2009-09-28 14:45 | 7 | 138 | 50380-1 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 078S04 HOT TAP BURNT OFF ON POLE 69-563//VER/CRB IDC XXXX
9183 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-02-02 16:12 | 2009-02-02 18:30 | 7 | 138 | 54817-1 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP TRANSFORMER CUTOUT FAILED. L3/HFP
9184 | Cannonsburg | 3002106 | 10TH STREET | FRONT STREET | 2013-10-25 10:31 | 2013-10-25 13:33 | 99 | 182 | 4962051 | 966 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1031 OPENED CB TO ALLOW SERVICERS TO ISOLATE TROUBLE COD-99 // WILL HAVE ALL BUT 1 CUSTOMER ON BY 1100 // CLOSED CB @ 1039 RESTORING 98 CUST// RELEASED BY CREW 078S07/CRE ON SITE/FETR1330/VEM/POWER RESTORED TO ONE CUST @1333/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 COD-99 VER/HFP L3/HFP IDCC TOF0940, PN57 XXXX
9185 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-07-08 20:41 | 2016-07-08 23:54 | 5 | 193 | 4587451 | 965 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I CHANGED BAD CUTOUT VER/AWD
9186 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-08-19 16:29 | 2015-08-19 20:30 | 4 | 241 | 4154161 | 964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER CUTOUT BROKE ON POLE 784-40///REPLACED BAD CUTOUT///CLOSED XFMER ON POLE 784-40 @ 20:30///COMPLETE BR/ ISO 38830784C00040/ COD 4/ VER/BOW
9187 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2019-06-17 17:56 | 2019-06-18 10:00 | 1 | 964 | 4528381 | 964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr cut out on 226-106/ making repairs/ bad 25kVA/ truck ok/ line crew required/ replaced TL
9188 | Paintsville | 3401103 | FALCON | BURNINGFK | 2014-05-27 21:13 | 2014-05-28 05:15 | 2 | 482 | 4940701 | 964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY LEAD BURNED OUT OF HOT TAP.TREES BURNING IN PRIMARY.NEED 1 MAN. RELEASED BY CREW 076S01PRIMARY LEAD BURNED OUT OF HOT TAP.TREES BURNING IN PRIMARY.NEED 1 MAN.AND BUCKET TREE CREW..PRIMARY LEAD BURNED OUT OF HOT TAP.TREES BURNING IN PRIMARY.NEED 1 MAN.AND BUCKET TREE CREW..OPENED LINE FUSE AND XFMR ON POLE 852-84 AT 4.45 BACK ON AT 515..CUST WOULD NOT LET US TRIM TREES.SEND TO COREY FARMER, NEEDS SPAN CUT OUT.. VER/ARN
9189 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-02-22 18:34 | 2008-02-23 10:38 | 1 | 964 | 66383-1 | 964 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3310501//STS TRANSFORMER FUSE HANGING DOWN, BROKE LINE CUTOUT ON POLE 5-3 RELEASED BY CREW 077S05// SAM SPOKE W/CUSTOMER DUE TO SAFETY WE ARE GOING TO WAIT UNTIL MORNING TO MAKE REPAIRS// WILL HOLD TROUBLE ORDER UNTIL THEN////VER/CRB IDC XXXX
9190 | Hazard | 3309301 | VICCO | REDFOX | 2011-10-25 10:43 | 2011-10-25 12:30 | 9 | 107 | 4018841 | 963 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PATROLLING LINE, FOUND LAST SPAN IN HOLLOW DOWN, CUT IN CLEAR ///VER/CRB IDC XXXX
9191 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-09-28 04:09 | 2022-09-28 09:30 | 3 | 321 | 4931521 | 963 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO broke on 22-B1-263, Ty Brock is coming with big bucket to change it out
9192 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-02-11 10:39 | 2018-02-11 11:05 | 37 | 26 | 4828481 | 962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | High side stepdown fuse open on 38830117A00504. Patrolling. b phase only (cod: 37)/opened recl on 159 and refused stepdown/ closed recl at 1105 38830117A00159 picking up all customers. L3/HFP
9193 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2008-07-30 14:56 | 2008-07-30 17:15 | 8 | 139 | 62262-1 | 962 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3309104// ISOLATION POLE IS 426-273// CUT OPEN POINT TO PICK UP TRANSFORMER OUTSIDE THE FUSE// WILL NEED HELP TO REPLACE INSULATORRE REPLACED INSULATOR//COD 8// VER/DBM IDCC PN272 ADDED A STEP XXXX
9194 | Whitesburg | 3312901 | JENKINS | KONA | 2008-03-19 16:55 | 2008-03-19 17:26 | 31 | 31 | 58778-1 | 961 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312901//CREW OPENED CUTOUT TO REPLACE CUTOUT ON POLE 37830403A00190 //RELATED TO ORDER 58607-1 VER/HFP IDC XXXX
9195 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-05-25 15:30 | 2010-05-25 15:50 | 48 | 20 | 50754-1 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED FUSE`S TO SAFELY REPLACE CUTOUT VER/KEP L3/KEP IDC XXXX
9196 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2012-11-03 13:35 | 2012-11-03 17:35 | 4 | 240 | 4349091 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENED FUSE ON POLE 1134-30 @ 1335 TO ISOLATE TROUBLE XARM BURNED INTO,NEED BUCKET,3 MAN, 45` 5 POLE & 2 8FT XARM,BRACES,3 PINS AND INSULATORS,OPENED AT 1134-30 TO ISOLATEXARM BURNED INTO,NEED BUCKET,1 MAN,8FT COD-4 ISO LF 38821134000030 VER/HFP L3/HFP IDC CHANGED FROM UNKNOWN XXXX
9197 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-02-27 12:55 | 2018-02-27 13:55 | 16 | 60 | 4887701 | 960 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | bad connection @ pole, repaired, restored
9198 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-04-09 09:10 | 2019-04-09 11:50 | 6 | 160 | 4073071 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | crew changing pedstal off @ 0910 on @ 1150
9199 | Paintsville | 3401802 | INDEX | HOSPITAL | 2014-06-15 11:55 | 2014-06-15 17:15 | 3 | 320 | 4093401 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA XFMR.DONNIE SMITH P-655-30.NEED 1 MAN AND MATERIAL HANDLER..TRUCK ACCESSIBLE..BACK ON AT 1715.. VER/KEP
9200 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-04-29 16:19 | 2017-04-29 16:27 | 120 | 8 | H4695191 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | DKM/OPENED UPPER ROCKHOUSE 34KV CB K AT 1528 THEN ROGER AMBURGEY OPENED 34KV LINE SWS AT POLE 37830352A00297 AT 1528 THEN CLOSED BREAKER AT 1533 SO HE COULD REPLACE CROSSARM AT POLE 37830352A00085---SEE DOL 737958///RECORD FOR OPENING BREAKER FOR RESTORAL/// VER/DKM /// TIMES PER SCADA - L3/HFP XXXHFP AJB
9201 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2011-03-21 13:25 | 2011-03-21 13:35 | 96 | 10 | 56276-1 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | BAD REGULATOR CONTROL - NEED TO HAVE SERVICER DROP RECLOSER TO BYPASS REGULATOR AT POLE 403-228, WILL OUTAGE 96 CUSTOMERS// REGULATOR SITTING AT 7 RAISE AT 129.0V // OPENED REC AT 13:25 BACK ON AT 13 :35 VER/KEP IDC XXXX
9202 | Hazard | 3308502 | BONNYMAN | HAZARD | 2022-10-12 21:42 | 2022-10-13 13:42 | 1 | 960 | 4021351 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Attempted to contact customer/no answer. This customer said that this power was out all day and that a crew doing debris removal cut a tree on the line. At least 2 spans of 6A neutral down here manual. This customer had 230V on one leg so I left this XFMR off. This will be crew required in the morning. Released by crew 077S04 replaced 2 spans of netural power restored at 13 :42
9203 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2012-03-17 11:10 | 2012-03-17 15:30 | 15 | 260 | 4590011 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PHIL CALL DANNY // POLE 69-648 BADPOLE 69-648 BAD 25-KVA NEED 37.5 OR 50KVA NEED RISER WIRE CHGED TRUCK TO POLE//PRT ON SITE//REPLACED WITH 37.5 KVA INSTALLED NEW RISER ALL POWER RESTORED @ 15:30 CLOSE TKT PRT/// COD-15 ISO LF 38830069A20593 VER/HFP L3/HFP IDC XXXX
9204 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2010-05-19 09:00 | 2010-05-19 11:00 | 8 | 120 | 64969-1 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CONTRACTORS OPENING RECLOSER AT APPROX 0900 TO MAKE REPAIRS ON CROSSARM ON POLE 916-20/OFF POSSIBLY UNTIL 1200//VER/CRB IDC XXXX
9205 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2022-04-13 23:49 | 2022-04-14 01:25 | 10 | 96 | 4760451 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Restored @ 01:25
9206 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-11-28 06:48 | 2019-11-28 08:08 | 12 | 80 | 4098451 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced bad hot line clamp all customers restored @ 08:08 complete // cod 12
9207 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-09-09 10:00 | 2010-09-09 12:00 | 8 | 120 | 64791-1 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | I HAVE BIG BUCKET IN ROUTE TO MAKE REPAIRS ON TRANSFORMER TRANSFORMER IS BAD WILL NEED A 50 KVA REPLACED TRANSFORMER AND CUTOUT VER/KEP L3/KEP IDC CHANGED TIME OFF FROM 7:35 PER DIM LIGHT CALLS, ESTIMATED TIME OFF XXXX
9208 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-12-12 12:33 | 2016-12-12 17:53 | 3 | 320 | 4188411 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | KYDDC TAGS @ 350-16. POLE NEEDS TO BE REPLACED 40 CLASS 4/ NEED TECHNICIAN.CREW REQUIRED WITH A TECH 40/4 POLE BURNT OFF 351-263 ISOLATED ON 350-16 NO GROUNDS TRANSFORMER ISOLATED ALSO 2 CUSTOMERS OFF TAGGED POLE TO DDC/ 3 CUSTOMERS NOT 2--TAGD TO CREW--CREW ON SITE--FETR 19:23--RESTORED AT 17:53/ ISO 38830350000016/ COD 3 VER/HFP L3/HFP
9209 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2019-12-14 13:22 | 2019-12-14 17:22 | 4 | 240 | 4153951 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @125-3, checking. Cutout went bad on pole 125-129 and burndt the top of the pole off, I have enough room to lower the conductors, will be making repairs. Got pole lowered and all repairs made, closed L/F back in @1722.
9210 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2012-07-25 10:00 | 2012-07-25 18:00 | 2 | 480 | 4823371 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRUCK OK PER B TACKETT//COD 2// VER/DBM
9211 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2022-02-01 09:29 | 2022-02-01 10:49 | 12 | 80 | 4420821 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STEP DOWN FUSE OPEN ON POLE 38830620B10332//COD 12//Replacing broken cutout. All repaires made& apr at 1049 close ticket
9212 | Hazard | 3302703 | HAZARD | HAZARD | 2009-03-25 18:00 | 2009-03-25 19:20 | 12 | 80 | 61458-1 | 960 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 XFMR CUTOUT FAILED AT POLE 37830296B30266 CALLING FOR CREW TO ASSIST//VER/CRB IDC NO OUTAGE UNTIL OPENED, APPROXIMATELY 1800 XXXX
9213 | Hazard | 3303901 | LESLIE | HYDEN | 2019-06-24 19:47 | 2019-06-25 11:46 | 1 | 959 | 4584281 | 959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ/// BROKE CUTOUT 37830290000060 COD 1BROKE CUTOUT ON 290-60 Released by crew 077S01
9214 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-12-31 14:34 | 2015-12-31 16:51 | 7 | 137 | 4578871 | 959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE LINE FUSE OPEN AT POLE 470-28, B PHASE CUTOUT BROKE ON POLE 470-91, WILL HAVE TO OPEN OTHER 2 PHASES ON POLE 28 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES.//ALL CUSTS ARE 3 PHASE//B PHASE LINE FUSE OPEN AT POLE 470-28, B PHASE CUTOUT BROKE ON POLE 470-91, WILL HAVE TO OPEN OTHER 2 PHASES ON POLE 28 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED OTHER 2 LINE FUSES AT 1600, CLOSED BACK IN AT 1651, ALL POWER RESTORED. VER/CRB
9215 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-07-13 11:53 | 2011-07-13 14:10 | 7 | 137 | 4541171 | 959 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD 19.9 KV CUTOUT COD-7 ISO LF 37840648000011 VER/HFP L3/HFP IDC XXXX
9216 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2019-06-17 18:18 | 2019-06-18 10:15 | 1 | 957 | 4528741 | 957 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Blown ug primary fuse on 139-A-308. This is underground primary metering. Would need to open other 2 phases to make repairs, need to replace all 3 old porcelain cutouts. Spoke with customer, can hold until tomorrow.
9217 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-12-22 20:47 | 2020-12-22 22:05 | 13 | 78 | 4796031 | 956 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | riser bad on 70-3078, opened xfmers @ 21:45, restored @ 22:05
9218 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-05-06 17:32 | 2013-05-06 21:31 | 4 | 239 | 4078631 | 956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10T /LINE FUSE LINK BROKE, REFUSE POWER RESTORED ///VER/CRB L/3 CRB IDCC CCWU XXXX
9219 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-10-28 01:31 | 2014-10-28 05:30 | 4 | 239 | 4666011 | 956 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CENTER XFMR BAD IN 120/208 BANK.TAPPED ON CENTER AND RIGHT HAND BUSHING. NEED TWO MEN AND MATERIAL HANDLER TO CHANGE. REPLACED XFMR AND RESTORED @ 5:30. SH VER/ARN
9220 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-10-03 16:36 | 2009-10-03 19:15 | 6 | 159 | 50124-1 | 954 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE CONNECTION AT POLE 37830040C30047, 6 CUSTOMERS HAD 120V ONLY, REPAIRED ... ALL WORK COMPLETE / GXJ/VER/CRB IDC XXXX
9221 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2011-01-29 13:37 | 2011-01-29 18:55 | 3 | 318 | 51983-1 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAD UG XFMR (785-843) NOT IN USE. ISOLATED AND RESTORED XFMR 785-841 @ 18:55 RESTORING ALL OUTAGE CUSTOMERS. SH//VER/CRB IDCC CDC83 XXXX
9222 | Hazard | 3420001 | SOFT SHELL | VEST | 2009-01-16 06:21 | 2009-01-16 09:00 | 6 | 159 | 55524-1 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP 3420001// BAD XFMR, POWER RESTORED AT 09:00 HRS COD-6 L3/HFP
9223 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-04-06 10:21 | 2009-04-06 13:00 | 6 | 159 | 66361-1 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT REPLACED CUTOUT VER/KEP L3/KEP IDC XXXX
9224 | Paintsville | 3410602 | E.PRESTON | LANCER | 2018-10-13 02:12 | 2018-10-13 03:05 | 18 | 53 | 4245191 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need 25 kva 7200--120/240 3 linemen & foreman pulled off at 02:12 BACK ON @03:05 Released by crew 074S04 L3/HFP
9225 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-03-15 07:12 | 2012-03-15 12:30 | 3 | 318 | 4580521 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANS NO TRUCKS RELEASED BY CREW 078S08//PRT ON SITE//TRANSFORMER REPLACED POWER RESTORED AT 12:30 PLEASE CLOSE TKT PRT//COD 3/// VER/DBM IDC XXXX
9226 | Hazard | 3309302 | VICCO | JEFF | 2018-10-08 05:59 | 2018-10-08 11:17 | 3 | 318 | 4207061 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines xfmr fuse out. bad 25 kva , 19.9 kv, can replace with bucket Released by crew 077S02..crew on site..changed bad xfmr, all power restored @ 11:17 p.hicks L3/HFP
9227 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-03-14 19:06 | 2018-03-15 11:00 | 1 | 954 | 4015241 | 954 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WORK 03/15 customer neighor built a 10ft fence to secondary pole, making it unsafe to climb talk to duty can wait till morning,customer ok with it,may have to set another pole. Unable to make OPS order for this. repairs made/ ISO 37830223B00012/ COD 1
9228 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-07-02 13:22 | 2012-07-02 18:40 | 3 | 318 | 4220841 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUSTOMER DID NOT COME BACK ON - BAD CUTOUT MWL --CAN CLOSE TICKET MWL
9229 | Hazard | 3309301 | VICCO | REDFOX | 2009-03-19 08:07 | 2009-03-19 09:53 | 9 | 106 | 59988-1 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3309301// STS LIGHTING ARRESTOR BAD ON POLE301-72, CUT IN THE CLEAR AND GOING TO REFUSE LINE FUSE // VER/TOM L3/TOM IDC XXXX
9230 | South Williamson | 3200302 | BELFRY | TOLER | 2017-05-13 10:50 | 2017-05-13 10:59 | 106 | 9 | 4794581 | 954 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | SEE DOL CASE 741489///BELFRY - BELFRY ISOALTION FOR BUS DISCS REPLACEMENT///ORIGINAL RECORD FOR BELFRY-TOLER 12KV CB B THAT WAS PARTIALLY RESTORED AND BEING CARRIED VIA THE TRANSFER BUS DISCS BY THE BELFRY - BELFRY 12KV CB A/// VER/DKM AJB
9231 | Hazard | 3303901 | LESLIE | HYDEN | 2022-02-16 18:37 | 2022-02-17 10:30 | 1 | 953 | 4489521 | 953 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | looks like splice in service drop failed, and burnt neutral into, need about 50 feet 2/3 service wire truck acess, need to work from behind home, cust said we can not move anything, big bucket Released by crew 077S07. crew on site, ran new service, all power restored @ 10:30 p.hicks
9232 | South Williamson | 3411401 | DEWEY | INEZ | 2020-03-29 10:36 | 2020-03-29 12:35 | 8 | 119 | 4522811 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38830744C00142 ¦¦ both fuses were blown
9233 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-02-02 12:40 | 2009-02-02 13:48 | 14 | 68 | 54649-1 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 543-1 VER/KEP L3/KEP
9234 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-04-21 19:35 | 2013-04-22 11:27 | 1 | 952 | 4034791 | 952 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CUSTOMER DID NOT THINK WE WOULD COME TONIGHT //COULD NOT FIND ANYTHING WILL NEED HELP TO CLIMB POLE AND CK CONNECTIONS TAKE TWO PEOPLE ..CK IN MORNING ..TOLD CUSTOMER WILL BE HERE AROUND 10 THEY WANT TO GO TO BED..SAID OK TO CK MONDAY RELEASED BY CREW 077H07 STS BAD CONNECTION ON TRANSFORMER POLE ///VER/CRB L/3 CRB IDC XXXX
9235 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-07-09 20:29 | 2017-07-10 04:25 | 2 | 476 | 4100171 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 22-55, BAD 25KVA 7200, CREW REQUIRED, TRUCKS TO POLE. RELEASED BY CREW 078H04,REPAIRS MADE ALL CUST RESTORED @ 0425 PLEASE CLOSE TICKET THANKS.BT//VER/ADH
9236 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2011-07-12 17:03 | 2011-07-12 19:02 | 8 | 119 | 4535481 | 952 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | CONNECTION BAD ON 1 LEG OF TRANS RISER CLOSED AT 1902 CAN CLOSE TICKET MWL//COD 8// VER/DBM
9237 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2016-11-19 15:29 | 2016-11-19 19:27 | 4 | 238 | 4115091 | 952 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | NEEDS RISERS REPLACED//TRUCK ASSESSIBLE THROUGH ALLEY//CREW ON SITE/WILL NEED TO OPEN XFMR FOR REPAIRS APROX 30 MINUTE OUTAGE/VEM/OPEN XFMR 1919/TO REPAIR RISERS/FETR 1945/VEM/REPAIRS MADE AND FULL POWER RESTORED TO ALL CUST 1927/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
9238 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2011-07-24 16:47 | 2011-07-24 20:45 | 4 | 238 | 4610451 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. BAD 25 KVA 7200 120/240 CSP. TRUCK OK, NEED CUTOUT AND BRACKET. RELEASED BY CREW 078S05/CREW ON SITE/FETR 2130/VEM/XFMR CHANGED AND POWER RESTORED TO ALL CUST 2045/PLEASE CLOSE TICKET/THANKS/VEM// COD 4/// VER/DBM IDC XXXX
9239 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2017-02-26 19:35 | 2017-02-26 23:33 | 4 | 238 | 4424561 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 XFMR, MADE REPAIRS RESTORED POWER AT 23:33..//COD 4// VER/DBM L3/HFP XXXHFP
9240 | Pikeville | 3403001 | PIKEVILLE | CITY | 2016-12-08 18:29 | 2016-12-08 22:27 | 4 | 238 | 4179531 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR FAILED ON 24-D1-1304 REPLACED CUTOUT DOOR RESTORED POWER AT 22:27/// VER/DKM L3/HFP XXXHFP
9241 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-07-03 06:57 | 2018-07-03 07:25 | 34 | 28 | 4715171 | 952 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out door burnt up all pwr restored please close ticket LRM COD-34 ISO LF 38830091D00285
9242 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-08-05 07:08 | 2016-08-05 12:25 | 3 | 317 | 4737221 | 951 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TAGGED TO KYDDC AND GROUNDED @ 38830118D16103/ BAD 37.5 KVA TRANS NEED CUTOUT AND LA CHGED T- BRACKETTRUCK TO POLE. REPLACED BAD 37.5 AND CUTOUT RELEASED BY CREW 078H25 VER/CRB
9243 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-07-09 02:57 | 2014-07-09 06:07 | 5 | 190 | 4216141 | 950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PATROLLING LINE/VEM/LOOP BURNT OPEN 162-66/WILL NEED TO OPEN FUSE ON 162-28 FOR REPAIRS/APPROX 30 MINUTE OUTAGE/VEMOPEN FUSE @0553/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0607/NOT TO MAPPING CUST OFF OF FUSE 162-C-28 ARE ON A PHASE/PLEASE CLOSE TICKET/THANKS/VEM *****DUPLICATE TICKET FOR OTHER 8 CUSTOMERS FROM 0553 TILL 0607***** VER/SEF
9244 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2015-07-22 09:45 | 2015-07-22 10:35 | 19 | 50 | 4930471 | 950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LINE FUSE TO CHANGE CUTOUT AND LA/ 901-C2-4625/ 945 1035/ ISO 39830901C24575/ COD 19/ VER/BOW
9245 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-10-29 18:40 | 2021-10-29 21:50 | 5 | 190 | 4039711 | 950 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had to lift hot tap on pole 1076-51 to make safe, lifted at 18:40, cutout on pole 1076-164 broke and about burnt top of pole off, crew required Released by crew 074S09
9246 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2020-08-25 19:41 | 2020-08-26 11:30 | 1 | 949 | 4376001 | 949 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad csp transformer on pole 492-34. talked to customer and told them someone would be back in the morning to replace it. will let duty supervisor know about it in the morning Released by crew 077S11
9247 | Paintsville | 3401101 | FALCON | FALC-OILS | 2021-02-23 04:26 | 2021-02-23 12:20 | 2 | 474 | 4227121 | 948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Xfm riser broke and service nuetral broke @ 38830828000183. Made repairs and restored @ 12:20
9248 | Pikeville | 3414901 | FISHTRAP | DISTRIBUTION | 2020-08-22 13:59 | 2020-08-22 19:15 | 3 | 316 | 4357431 | 948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | at pole 78-121 c phase is on the ground will need a line crew and manual ROW crew.. switches on 77-34 opened at 1359 closed at 1915
9249 | Hazard | 3310502 | HADDIX | CANOE | 2017-01-07 19:56 | 2017-01-07 21:15 | 12 | 79 | 4276251 | 948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OPEN ON POLE37830028000006/ COD-12 MD FILED FOR TAP TOWARDS POLE 122/LINE FUSE OPEN ON POLE37830028000006,BROKE FUSE/ RESTORED 2115 VER/KEP L3/HFP XXXHFP
9250 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-06-29 12:31 | 2008-06-29 20:25 | 2 | 474 | 59348-1 | 948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 500-157 , TOP OF POLE BURNT OFF ON POLE 500-148, THINK CAN LOWER ALL METARLS DOWN. TRUCKS TO PLOE , FIRST RIGHT OFF 32 ON TO DEER LICK TOP OF HILL. GROUNDS ON POLE 500-148.40/4 RELEASED BY CREW 078S01 NEED A 45-2 POLE 25KVA 19.9KV PRIMARY D.E. RELEASED BY CREW 078E04 COD-2 VER/KEP IDC XXXX
9251 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2017-03-02 11:36 | 2017-03-02 19:30 | 2 | 474 | 4499781 | 948 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830024B40682, CHANGED OUT AND REFUSED @1930. VER/AWD
9252 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-06-03 19:19 | 2010-06-04 11:05 | 1 | 946 | 56118-1 | 946 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | AS PER D/S SERVICER WILL CHECK IAT DAYLIGHT. BAD CONNECTION ON TRANSF POLE REPAIRED COD-1 VER/HFP L3/HFP IDC XXXX
9253 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2022-02-17 18:35 | 2022-02-18 10:20 | 1 | 945 | 4495651 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 37830110B40005 manual need 19.9 cutout and t bracket. need line crew Released by crew 077H05
9254 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2011-04-28 11:35 | 2011-04-28 13:50 | 7 | 135 | 51362-1 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGED XFORMER//VER/CRB IDC XXXX
9255 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-11-22 23:35 | 2015-11-23 01:20 | 9 | 105 | 4479001 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POLE 1123-6580 OPEN WIRE RAPPED UP 1/0 SERVICE BURNT DOWN REPAIRED VER/KEP
9256 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-06-04 00:10 | 2014-06-04 00:45 | 27 | 35 | 4969501 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | DEFECTIVE RECLOSER ON POLE 38830147000078 - AED ENTERED // COD-27 ISO OCR 38830147000078 AJB PH A.
9257 | South Williamson | 3200302 | BELFRY | TOLER | 2012-03-15 09:25 | 2012-03-15 14:40 | 3 | 315 | 4580771 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD PRIMARY BUSHING ON TRANSFORMER WILL NEED CREW TO CHANGE TRANSFORMER 15 KVA.RST *** UPDATE AT 1205--- CONTRACTOR BUCKET HAS BROKE DOWN ... WILL EXTEND RESTORATION TO 1500 HR//COD 3// VER/DBM IDCC TOF0800, ESTIMATED TIME OFF XXXX
9258 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-12-19 11:06 | 2022-12-19 14:15 | 5 | 189 | 4275991 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Have a Bad Trans at 167-D-289,Spoke with Steve Ray and is getting help to make repairs..7200 50 KVA.Restored at 14:15.
9259 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-03-18 13:51 | 2013-03-18 15:36 | 9 | 105 | 4916201 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED, LNE FUSE OUT AS WELL//COD 9// VER/DBM IDC XXXX
9260 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-05-16 07:44 | 2015-05-16 10:53 | 5 | 189 | 4434481 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT ON POLE 481-54/ ISO 37830481000054/ COD 5/ VER/BOW
9261 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-10-28 20:42 | 2016-10-29 01:57 | 3 | 315 | 4061151 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV TRANSFORMER AND CUTOUT 7.2KV,NEED R/W CREW TO FLAG ROAD AND LINE CREW WITH BIG BUCKET ,TRUCK ACCESSIBLE RELEASED BY CREW 077H07 VER/TOM L3/TOM
9262 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2020-09-03 17:12 | 2020-09-03 20:21 | 5 | 189 | 4427631 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse out @ 37830211B00002 will be patrolling. Bad xfm cutout @ 37830235000066. Will be replacing. Restored @ 20:21
9263 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-07-14 17:50 | 2012-07-14 19:35 | 9 | 105 | 4726281 | 945 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE IS BLOWN ON POLE 1126-112. WE PATROLLED LINE AND SEEN NOTHING WE ARE GOING TO REFUSE LINE. WE FOUND INSULATOR BAD ON POLE 1126-280 AND ISOLATED IT. WE CLOSED LINE FUSE IN AT 1126-112 AT 19:35 AND IT STAYED//COD 9
9264 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-06-14 15:22 | 2017-06-14 16:21 | 16 | 59 | 4968211 | 944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND AND REPLACED BROKEN CUTOUT ON 500-221, APR AT 1621 CLOSE TICKET/ ISO 38830500000188/ COD 16/ VER/BOW
9265 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2014-04-01 20:23 | 2014-04-02 04:15 | 2 | 472 | 4554131 | 944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT REPLACED 7200 VER/ARN IDC XXXX
9266 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-09-01 00:20 | 2018-09-01 08:12 | 2 | 472 | 4026621 | 944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad insulator
9267 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2009-05-02 08:23 | 2009-05-02 16:15 | 2 | 472 | 63014-1 | 944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 29634782 // POLE FIRE DUE TO BROKE DOWN CUTOUT , SINGLE PHASE DEAD END POLE WITH 19.9 25KVA VER/HFP TRANSFORMER #2 ALUM PRIMARY AND NEUTRAL,, POLE IS TRUCK ACCESSIBLE POLE NEEDED WILL BE A 45 CLASS 5.,,,,I OPEN FUSE ON POLE 524-177 LOCATED AT TOP OF HILL ACCROSS HWY32 RELEASED BY CREW 078S02 REPLACED POLE ALL POWER RESTORED AT 16:15 L3/HFP IDC XXXX
9268 | Hazard | 3303901 | LESLIE | HYDEN | 2015-07-17 16:17 | 2015-07-17 18:15 | 8 | 118 | 4902981 | 944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POWER RESTORED AT 18:15 // CAN CLOSE MWL
9269 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2019-10-16 09:16 | 2019-10-16 13:12 | 4 | 236 | 4145551 | 944 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout Released by crew 078H25 crew on site FETR 13:45 All pwr restored@ 13:12 please close ticket LRM L3/HFP
9270 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-09-09 20:48 | 2022-09-09 23:25 | 6 | 157 | 4861191 | 942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required fuse on 244-48 blown tie wire on 244-52//cod 6
9271 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-10-02 19:24 | 2012-10-03 11:06 | 1 | 942 | 4109631 | 942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON MANUEL POLE BEHIND HOUSE POLE LEANING REAL BAD WILL NEED TO STRAIGHTEN BEFORE WE CAN CLIMB TALKED TO CUST SAID WAS OK TO WORK TOMORROW TALKED TO BRUCE SAID OK RELEASED BY CREW 077H14 REPLACED CUTOUT , ARR & BRKT , REMOVED VINES OFF OF POLE ... RESTORED POWER AT 1106 ///VER/CRB L/3 CRB IDCC PN14 XXXX
9272 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-06-20 18:01 | 2008-06-20 23:15 | 3 | 314 | 51272-1 | 942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 3000303// CALLED CREW POSSIBLE BAD 25KVA TRANSFORMER //COD 3 IDC XXXX
9273 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2018-03-24 20:53 | 2018-03-24 23:30 | 6 | 157 | 4060751 | 942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse open on 249-86 crew required 40/4 pole burnt off dead transformer install trucks ok/need tech also/tagged line fuse to ddc /BTackett remove ddc tags 2119.line fuse open on 249-86 crew required 40/4 pole burnt off dead transformer install trucks ok/need tech also/tagged line fuse to ddc Released by crew 078S03line fuse open on 249-86 crew required 40/4 pole burnt off dead transformer install trucks ok/need tech also/tagged line fuse to ddc Released by crew 078S03,repairs made all cust
9274 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-01-23 18:25 | 2017-01-23 23:39 | 3 | 314 | 4324151 | 942 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA 19.9 XFM..NEED BUCKET AND ONE MAN TO CHANGE OUT.RESTORED @ 23:39/ ISO 37830214A00467/ COD 3/ VER/BOW L3/HFP XXXHFP
9275 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-01-22 18:04 | 2016-01-23 09:45 | 1 | 941 | 4642321 | 941 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON HOT LEAD AT XFMR POLE ON AT 09:45 D SAMMONS/ ONLY EFFECTED 1 CUSTOMER FIXED LEAD ON TRANSFORMER/ ISO 37830047B00144/ COD 1/ VER/BOW
9276 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-06-27 14:42 | 2015-06-27 17:50 | 5 | 188 | 4679451 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLACED CUTOUT === ALSO LINE OPEN === REFUSED LINE FUSED === POWEROK/ ISO 37830511000045/ COD 5/ VER/BOW
9277 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-04-11 14:30 | 2009-04-11 18:25 | 4 | 235 | 51490-1 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT APPEARS TO HAVE BROKEN DOWN,CAUGHT POLE ON FIRE.WILLIE TRYING TO GET ME ONE MAN AND A BIG BUCKETTIM MCCOY ENROUTE W BIG BUCKET RELEASED BY CREW 074S06 WE SPLICED POLE ND CLOSED LINE FUSE IN AT POLE 27-120 AT 18:25//VER/CRB IDCC CDC90 CNT5, TOF1308 XXXX
9278 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-09-04 08:30 | 2022-09-04 12:25 | 4 | 235 | 4834781 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | clamp burnt off at pole 421-9 Released by crew 077H03
9279 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2017-05-21 14:47 | 2017-05-21 17:55 | 5 | 188 | 4835211 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRIED CALLING CUSTOMER NO ANSWER. 6T FUSE BROKE FUSED UP EVERYTHING OK/ ISO 37830236A00064/ COD 5/ VER/BOW
9280 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2022-07-06 15:00 | 2022-07-06 18:08 | 5 | 188 | 4399871 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 511-119
9281 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-01-19 22:45 | 2009-01-20 02:40 | 4 | 235 | 58441-1 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER VER/ARN L3/KEP
9282 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-02-19 07:25 | 2013-02-19 11:20 | 4 | 235 | 4829011 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED--BAD 25 KVA TRANSFORMER--TRUCK TO POLE--NEED NEW CUTOUT RELEASED BY CREW 078S07 ///VER/CRB L/3 CRB IDC XXXX
9283 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-08-19 10:36 | 2009-08-19 12:10 | 10 | 94 | 50160-1 | 940 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT IS BAD ON POLE # 202-184, REPLACED CUTOUT, POWER RESTORED COD-10 ISO LF 37830202000014 L3/HFP IDC XXXX
9284 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-01-01 17:35 | 2009-01-01 22:48 | 3 | 313 | 50665-1 | 939 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308401//XFMR FUSE BLOWN. XFMER IS BAD. UPDATE TO 2 CUSTOMERS OUT 25 KVA, 7200, 120/240V. NEED.XFMR FUSE BLOWN. XFMER IS BAD. UPDATE TO 2 CUSTOMERS OUT 25 KVA, 7200, 120/240V. ... PWER RESTORED. P.HICKS VER/ARN L3/KEP IDC XXXX
9285 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-06-29 20:36 | 2013-06-30 12:15 | 1 | 939 | 4428761 | 939 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVE BURNED UP WILL NEED TO GO BACK WITH A 15 KVA 120/240-7200. WILL BE A HAND JOB . RELEASED BY CREW 074S04 //S.RAY, J.GARRETT, J.HAWKINS, & J. SMITH // OPENED TAP POLE 1125-184 AT 10:00 VER/CRB L/3 CRB
9286 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-11-29 22:37 | 2015-11-30 03:50 | 3 | 313 | 4493201 | 939 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER REPORTS THEY HAVE WIRE DOWN IN THEIR DRIVEWAY//TOM # 2 AL OPENWIRE DOWN FROM 43-65 TO190 TO 66. HOT LEGS CUT @ XFMERCUSTOMER REPORTS THEY HAVE WIRE DOWN IN THEIR DRIVEWAY//TOM # 2 AL OPENWIRE DOWN FROM 43-65 TO190 TO 66. RELEASED BY CREW 078S07.. CREW ON SITE TO MAKE REPAIRS OPENED XFMR ON 43-65 AT 02:35 ETR 03:15.. NEW ETR 04:00.. REPAIRS MADE AND XFMR BACK IN AT 03:40.. TICKET COMPLETE RELEASED BY CREW 078H22// WILL NEED DUP FOR 2 CUSTOMERS//TOM
9287 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2010-02-22 10:06 | 2010-02-22 17:55 | 2 | 469 | 59768-1 | 938 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33962067 // BAD CUTOUT == SET POLE ON FIRE == NEED LINE CREW AND YARD DOG AND POLE == CALLED GLEN COMBS GOT LINE CREW & ROW CREW == RELEASED BY CREW 077S03//MADE A MD// POWER RESTORED VER/KEP L3/KEP IDC XXXX
9288 | Hazard | 3309301 | VICCO | REDFOX | 2022-07-18 21:47 | 2022-07-19 13:24 | 1 | 937 | 4519411 | 937 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER//OK TO WAIT TILL THE AM JUST FEEDS A BARN// tranformer needs changed out 15kva 19.9.. Bucket access Released by crew 077H05
9289 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2010-05-12 01:03 | 2010-05-12 03:00 | 8 | 117 | 59763-1 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3003703 REPLACED BAD LINE FUSE CUTOUT. IDC XXXX
9290 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-05-30 14:43 | 2011-05-30 16:40 | 8 | 117 | 4210261 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR 40161740POLE 188-399 BAD LA SEND NOTE TO RAYBURN NO TRUCK SEND NOTE TO TREE PEOPLE PRI. UNDERGROUND POLE 188-238 COVERED IN VINES FROM TOP TO BOTTOM NEED CUT POLE 188-344 40T LINE FUSE//VER/CRB IDC XXXX
9291 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-02-10 14:34 | 2008-02-10 17:10 | 6 | 156 | 55160-1 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3008002//BROKEN HOT TAP LEAD// VER/DBM IDC XXXX
9292 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2022-07-21 07:51 | 2022-07-21 11:45 | 4 | 234 | 4539441 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout on 24-a1-177 //cod 4
9293 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2012-11-29 08:28 | 2012-11-29 10:12 | 9 | 104 | 4430071 | 936 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | R. AKEMON WORKED ON THIS 11-28-12, REMADE ALL CONNECTIONS. == WILL REPLACE TRANSFORMER NOW. == DID NOT REPLACE TRANSFORMER, FOUND BAD CONNECTION AT TRANSFORMER BUSHING., POWER RESTORED. VER/KEP IDC XXXX
9294 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-02-20 09:42 | 2015-02-20 12:18 | 6 | 156 | 4054031 | 936 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | SPLICE PULL OUT ON NETURAL ON 1 / 0 LASH POLE HAS JUST BEEN CHANGE OUT HAD MANUEL SLEEVE THAT PULL OUT OF NETURAL AND HAS BURNED UP MICROWAVE AND BREATHING MACHINE, TOLD THEM TO CALL CLAIM IN AND NEED TO SEND COPY TO PEGGY WYSONG VER/HFP L3/HFP
9295 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-12-16 22:39 | 2016-12-16 22:51 | 78 | 12 | 4202011 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SORRY FOR THE INCONVENIENCE/ AFTER REPLACING LEAKING TRANSFORMER AND RESTORING POWER THERE WAS A HOT LINE CLAMP THAT IS HEATING UP AND COULD BURN INTO TAKING THE POWER OUT AGAIN THAT NEEDED TO BE REPLACED/ OPENED LINE FUSE ON POLE 38830117A00106 TO REPLACE CLAMP/ COD 78/ 2239-2251/ VER/BOW AJB
9296 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2020-01-06 15:14 | 2020-01-06 15:23 | 104 | 9 | 4218251 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Conductors sagged below neutral @38831151D00077, will have to open all 3 rec. @1151-D-95 to make repairs. Open @1514, closed back @1523.
9297 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-11-29 10:51 | 2015-11-29 14:45 | 4 | 234 | 4491641 | 936 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING CUTOUT.OPENED XFMR BANK AT..14..25 VER/CRB
9298 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-07-07 05:54 | 2022-07-07 08:30 | 6 | 156 | 4415911 | 936 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout door burnt up. repairs made
9299 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2013-08-14 20:10 | 2013-08-14 21:05 | 17 | 55 | 4666501 | 935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VENTURINO OPENING FUSE TO PUT OUT POLE FIRE VER/SEF
9300 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2018-09-07 21:32 | 2018-09-08 13:07 | 1 | 935 | 4056131 | 935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva truck ok. send to v mullins. Released by crew 078H17/crew on site/FETR 1345/vem/repairs made and all cust restored 1307/please close ticket/thanks/vem
9301 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2018-12-27 22:05 | 2018-12-27 23:00 | 17 | 55 | 4603421 | 935 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Gatlin replaced broken cutout on pole 38830066000036 then restored fuse at 2300 L3/HFP
9302 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-07-21 19:16 | 2014-07-22 01:05 | 6 | 349 | 4270531 | 934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CUTOUT//POLE 19 D 9 25T LINE FUSE RESTORED @ 20:15 POLE 19D195 BAD 25 KVA TRUCK ACC. RELEASED BY CREW 078H12,,CREW ON SITE, REPLACED XFMR, ALL POWER RESTORED VER/DKG L3/DKG
9303 | Hazard | 3309302 | VICCO | JEFF | 2015-04-28 11:28 | 2015-04-28 19:15 | 2 | 467 | 4372671 | 934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD MANUAL TRANSFORMER. E PRATT COMING TO CHANGE. RELEASED BY CREW 077S04BAD MANUAL TRANSFORMER. E PRATT COMING TO CHANGE. ..POWER RESTORED. VER/KEP
9304 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-01-21 03:05 | 2012-01-21 10:52 | 2 | 467 | 4279141 | 934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WATER IS OVER HWY, CANT GET TO JONES BR RELEASED BY CREW 077S05WATER IS OVER HWY, CANT GET TO JONES BR STS CUTOUT BROKE GOING TO CHANGE IT OUT //VER/GAH IDC XXXX
9305 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-05-15 03:58 | 2014-05-15 11:45 | 2 | 467 | 4705481 | 934 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES //BAD 25 KVA XFMR.TRUCK ACCESSIBLE..CALLED TIM MILLER. CHG OUT XFMR.BACK ON 11.45.. VER/SEF
9306 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-08-18 20:07 | 2019-08-19 11:40 | 1 | 933 | 4903291 | 933 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 181D-45, manual on cliffside at the bottom of the hill at the Hindman intersection. Released by crew 077H20
9307 | Hazard | 3308002 | JACKSON | PANBOWL | 2022-09-27 13:19 | 2022-09-27 18:30 | 3 | 311 | 4930111 | 933 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Released by crew 077H20, ug in trl park is bad, hooked up auto xfmr for customer tonight. will work on more permanite fix tommarow. p.hicks
9308 | Pikeville | 3421001 | BREAKS | CITY | 2022-01-02 11:57 | 2022-01-02 14:10 | 7 | 133 | 4260851 | 931 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 CUTOUTS BROKE ON POLE 220-C-67 WILL HAVE TO OPEN 3rd CUTOUT TO MAKE REPAIRS, WILL TAKE ABOUT AN HOUR. CHANGED 3-CUTOUTS RESTORED AT 14:10
9309 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2022-11-28 08:22 | 2022-11-28 10:35 | 7 | 133 | 4195201 | 931 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | riser wire that feeds pad mount burned into on pole 942B4-1445.replace riser and got cust restored at 10:35
9310 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-10-07 19:33 | 2011-10-07 19:52 | 49 | 19 | 4956831 | 931 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | MIDDLE PHASE LOOP BURNT OPEN ON POLE48-291//SEE ORDER 4956541//OPENED ALL 3 PHASES @ 1933 AND CLOSED BACK AFTER REPAIR @ 1952//COD 49// VER/DBM IDC XXXX
9311 | Pikeville | 3413401 | GARRETT | GARRETT | 2010-10-02 08:39 | 2010-10-02 16:24 | 2 | 465 | 56201-1 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY IS DOWN FROM POLE #37830041B00115NEED CREW & SMALL PIECE #4 COPPER. APPEARS TO HAVE PULLED OUT OF SLEVE //ISO // COD 2// VER/DBM IDC XXXX
9312 | Hazard | 3301101 | CHAVIES | CHAVIES | 2011-04-21 10:15 | 2011-04-21 10:45 | 31 | 30 | H61589-1 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 39658426 / LOOP BURNED INTO ON POLE 147-40 AT 10:15 OPENED RECLOSER AT POLE 147-54--ALL BACK ON AT 10:45 VER/KEP IDC XXXX
9313 | Hazard | 3303901 | LESLIE | HYDEN | 2016-07-04 05:54 | 2016-07-04 11:04 | 3 | 310 | 4520251 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT ON 412-88-NEW CUTOUT ON FIBER BRACKET???---1 -A LINEMAN AND CUTOUT-BIG BUCKET-WE WILL BLOCK ROAD TO REPAIR--THEY CAN GO AROUND--FETR 1 HOUR AFTER HELPER ARRIVES
9314 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2014-01-07 18:32 | 2014-01-07 23:42 | 3 | 310 | 4255111 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA XFMR ON 978-223. NEED FLAGGERS TO BLOCK ONE LANE OF S. LAKE DR IN S CURVE, 3 MEN AND A 50 KVA XFMR. THIS HAS (2) 320 AMP AND (1) 200 AMP SVCS AND FEEDS BRICKHOUSE RESTURAUNT. /// MAYNARD & NEWSOME & GOBLE// CHANGING NOW// COMPLTED AND SERVICE RESTORED AT 23:42 VER/SEF
9315 | Hazard | 3309302 | VICCO | JEFF | 2022-08-21 19:30 | 2022-08-22 11:00 | 1 | 930 | 4774851 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7.2 15kva Transformer/// Need new 7.2 Cutout//// Need linecrew big bucket Released by crew 077H12.all power restored @ 11:00 p.hicks
9316 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-08-17 12:15 | 2021-08-17 15:21 | 5 | 186 | 4086451 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broken on 852-17.line fuse.bad location .high wall back on the hill.
9317 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-12-27 11:04 | 2009-12-27 14:10 | 5 | 186 | 55207-1 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | REPLACED LIGHTING ARRESTER & REFUSED RESTORED POWER THIS TICKET IS SAME OUTAGE AS 54839 POWER RESTORED 12-27-09 AT 14:10 RELEASED BY CREW 074M02
9318 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2017-09-18 09:50 | 2017-09-18 15:00 | 3 | 310 | 4370251 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | POWER IS OFF TO TWO POST TOP LIGHTS AND A POWER BOX FOR SOME RECEPTACLES, PLEASE SEND TO ROGER AMBURGY RELEASED BY CREW 077S12WORK IN PROGRESS. REPAIRS MADE AND POWER RESTORED. 1500 VER/HFP L3/HFP
9319 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-04-22 05:52 | 2015-04-22 07:25 | 10 | 93 | 4351031 | 930 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUTBAD CUTOUT ON 875-106.OPENING UP OTHER 2 PHASES TO CHG..OPENED OTHER 2 PHASES AT 7.00 BACK ON AT 7.25. VER/KEP
9320 | Pikeville | 3402002 | KEYSER | STONECOAL | 2021-07-16 22:11 | 2021-07-17 13:40 | 1 | 929 | 4922871 | 929 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Contacted 911/customer reported outage at transformer. Holding for daylight hours per KPCO late night guidelines/// bad 25kva 7.2 XFM
9321 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2016-08-21 19:58 | 2016-08-22 11:26 | 1 | 928 | 4823041 | 928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | THE LINE IS OUT THATS FEEDS TRANSFORMER IS OUT AND ITS GOES CROSS THE RIVER AND I DONT KNOW HOW TO GET TO IT, CUST SAID TO WAIT TILL MONDAY TO REPAIR RELEASED BY CREW 077S05 FOUND BAD INSULATOR ONPOLE 245-103 CHANGED INSULATOR AND RESTORED POWER AT 1126 RELEASED BY CREW 077H01 VER/CRB
9322 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-03-21 16:10 | 2022-03-21 17:08 | 16 | 58 | 4655081 | 928 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | OPEN LF TOMMY MORRIS FOUND POLE BURNING BROKE JUMPER 37830228000021 // LF OFF@ 1610 ON@ 1708
9323 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2013-01-22 04:21 | 2013-01-22 09:30 | 3 | 309 | 4726041 | 927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR APPEARS TO BE OPEN//CSP WILL NOT RESET// NEED 25 KVA// CUTOUT// LA// FIBER. BKT.// 7,200// CAN USE TRUCK RELEASED BY CREW 074S05 CREW ONSITE @ 08:50 REPAIRS COMPLETE AND POWER RESTORED @ 09:30 COD-3 ISO TF 37830024B40164 VER/HFP L3/HFP IDC XXXX
9324 | South Williamson | 3411401 | DEWEY | INEZ | 2014-08-03 19:21 | 2014-08-04 00:30 | 3 | 309 | 4328371 | 927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR OUT ON POLE 672-128///TRIED AND CAME BACK OUT///NEED 1 MAN AND BIG BUCKET AND 25KVA 19.9 XFMR///. VER/KEP
9325 | Whitesburg | 3401301 | FLEMING | NEON | 2016-03-27 16:31 | 2016-03-27 21:40 | 3 | 309 | 4885361 | 927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR , NEED TWO MEN,BIG BUCKET, AND 25KVA XFMR//COD 3
9326 | Whitesburg | 3312901 | JENKINS | KONA | 2014-12-13 09:51 | 2014-12-13 15:00 | 3 | 309 | 4858401 | 927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM FUSE MELTED OUT ON POLE 404-159, WILL REFUSE.REFUSED AND STAYED ABOUT 5 MINUTES AND BLEW AGAIN. BAD XFM NEED ONE MAN BIG BUCKET , 25KVA 7200V XFM.REPLACED XFM RESTORED POWER AT 1500.// COD 3//VER/ ADH
9327 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-07-14 23:39 | 2014-07-15 15:06 | 1 | 927 | 4246221 | 927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CELL TOWER CUSTOMER REPORTS TRANSFORMER FUSE OUT. WILL NEED 6 WHEELER TO CHECK. ROAD IN BAD SHAPE.. BAD 15 KVA, 19.9 TRANSFORMER, JIM MULLINS GETTING CREW. RELEASED BY CREW 077S04//COD 1// VER/DBM
9328 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2008-09-01 18:24 | 2008-09-02 09:51 | 1 | 927 | 58344-1 | 927 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUSTOMER IS GETTING ONLY 120 VOLTS COMING IN ON UNDERGROUND SERVICE. DENNIS IS GETTING SOME HELP TO FIND PROBLEM.CUSTOM REQUESTED FOR US TO WAIT TILL 9-2-08 TO FINISH//3410501//THIS IS GOING TO BE WORKED ON AN OUTAGE TICKET ON 9-2-08//OUTAGE TICKET 58456-1//VER/CRB IDC CHANGED FROM NO INTERRUPTION PQ PER COMMENTS ABOUT 120V ONLY XXXX MLR FEC 57
9329 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-05-21 23:34 | 2011-05-22 15:00 | 1 | 926 | 4121151 | 926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WE HAVE AN UNDERGROUND FEEDING PUMPHOUSE ONLY BAD. CUSTOMER SAID WE COULD WAIT UNTIL SUNDAY MORNING TO CHECK IT OUT. RELEASED BY CREW 074S01 ALL REPAIRS MADE POWER BACK ON..TOOK XFMR OFF AT 13:10 BACK ON AT 15:00//COD 4// VER/DBM IDCC CNT4, TOF XXXX
9330 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-05-31 19:54 | 2018-06-01 11:20 | 1 | 926 | 4535091 | 926 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19,9 KV CUTOUT DUTY SUPV SAID LEAVE TO MORNING Released by crew 077S01
9331 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-06-04 23:23 | 2008-06-05 14:48 | 1 | 925 | 57714-1 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3110902//XFMER FUSE OUT NEED TO REFUSE ON POLE 39831121A00139 XFMER MAY BE BAD RELEASED BY CREW 078E04//DOESN`T HAVE MDC/GAB XFMR BAD/ IKE REPLACING.DH//COD 1// VER/DBM IDC XXXX
9332 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2018-07-25 08:10 | 2018-07-25 11:15 | 5 | 185 | 4853041 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broken, changing/ ISO 38830785D20196/ COD 5 L3/HFP
9333 | Hazard | 3310502 | HADDIX | CANOE | 2019-01-12 22:50 | 2019-01-13 14:15 | 1 | 925 | 4662581 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | on pole 37830075000107got broke 19.9 cutout broke on new tee brkt , this is up on side of hill , bring two to change on transformer pole, cust said work in the morning, cust has two dogs but said wont bite Released by crew 077S05,. changed broken line cutout and cracked xfmr cutout..complted AS BUILTo.all power restored @ 14:15 P.HICKS L3/HFP
9334 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-06-14 23:20 | 2011-06-14 23:45 | 37 | 25 | 4318501 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | THERE IS A PHASE WIRE OFF THE ARM AND IS FLOATING ABOUT 12 FT. OFF GROUND @ 1-12//T. HALL IS CALLING FOR CREW//WILL OPEN UP AT POLE 1-9WHEN THEY ARIVE FT. OFF GROUND @ 1-12//T. HALL IS CALLING FOR CREW//WILL OPEN UP AT POLE 1-9*WHEN THEY ARIVETHERE IS A PHASE WIRE OFF THE ARM AND IS FLOATING ABOUT 12 FT. OFF GROUND @ 1-12//T. HALL IS CALLING FOR CREW//WILL OPEN UP AT POLE 1-8 WHEN THEY ARIVE CLOSED SWITCHES AT 23:45 VER/ARN IDCC CDC98, TOF2013, ESTIMATED TIME OFF DCMT XXXX
9335 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-02-01 18:00 | 2011-02-01 21:05 | 5 | 185 | H52861-1 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | B & C PHASE OUT 8 CUSTOMERS OPENED OTHER RECLOSER @ 1800 29 CUSTOMERS /// CROSSARM ON POLE 166-20 BROKE AND LET PHASE WIRE FALL. IT OPENED ONE OF THE RECLOSERS ON POLE 166-230. I OPENED THE OTHER RECLOSERS AT 18:00. CREW IS ON SITE TO CHANGE ARM COD-37 ISO RECL 37830166000230 DUP FROM 52861-1 VER/HFP L3/HFP IDC CHANGED COUNT FROM 29 APPEARS A AND C OUT INITIALLY XXXX
9336 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-04-11 10:40 | 2009-04-11 13:45 | 5 | 185 | 51443-1 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE,OPEN TAP ON POLE 1127-214 AT 12:14 THAT TOOK 6 OTHER CUSTOMER OUT OF SERVICE//CALLED 911 TO PUT THE FIRE OUT PER THE SERVICER @1252//3402001POLE FIRE,OPEN TAP ON POLE 1127-214 AT 12:14 THAT TOOK 6 OTHER CUSTOMER OUT OF SERVICE. LEFT TAP OFF THAT SERVICE POLE 1127-514/VER/CRB IDC XXXX
9337 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-09-27 10:30 | 2010-09-27 10:55 | 37 | 25 | 54075-1 | 925 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER OPENED FUSE AT POLE1146-26 AT _________TO MAKE REPAIRS.HAD TO OPEN UP LINE FUSE ON POLE 1146-26, OPENED IT AT 10:30, CLOSED IT BACK IN AT 10:55, ALSO HAD BAD CUTOUT ON POLE 1146-111, HAVE IT CHANGED AND EVERYONE SHOULD BE BACK ON AT THIS LOC//COD 37// VER/DBM IDC XXXX
9338 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2022-10-02 00:47 | 2022-10-02 08:29 | 2 | 462 | 4964081 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfm fuse blown.//Restored @ 8:29
9339 | Hazard | 3301101 | CHAVIES | CHAVIES | 2019-12-09 05:56 | 2019-12-09 11:04 | 3 | 308 | 4136301 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | need 2 7.2 cutouts truck access parking lot old church building beside chavies medical center Released by crew 077H14
9340 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-07-20 16:28 | 2008-07-20 18:40 | 7 | 132 | 54416-1 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3407101// WILL REPLACE CUTOUT AND LIGHTNING ARRESTER....... ALL WORK COMPLETE / GXJ IDCC CNT1 XXXX
9341 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-03-11 11:07 | 2014-03-11 16:15 | 3 | 308 | 4467751 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED NO TRUCKS CLOSE SPACING NEED CUTOUT AND BASKET INSTALLED ON COPPER PRIMARY RELEASED BY CREW 078S03,,CREW ON SITE,,REPAIRS MADE, ALL POWER RESTORED VER/SEF
9342 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-12-09 09:25 | 2010-12-09 09:37 | 77 | 12 | H64618-1 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PART OF 64618-1. OPENED B PHASE AT 09:25 TO MAKE REPAIRS//REPAIRS COMPLETE 0937 // COD 77 // VER/DBM IDC XXXX
9343 | Hazard | 3303901 | LESLIE | HYDEN | 2012-07-08 17:25 | 2012-07-08 18:42 | 12 | 77 | 4613561 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREWS OPENED FUSE IN ORDER TO WORK SAFELY ON TRANSFORMER//COD 10//SEE ORDER 4597341//
9344 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-12-18 15:00 | 2012-12-18 16:06 | 14 | 66 | 4480481 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3200202 OPENED RECLOSERS ON POLE 1090C158 AT 15:00. MAKING REPAIRS . LOOP BURNED OPEN AT POLE 1091-66. VER/CRB L/3 CRB IDC XXXX
9345 | Pikeville | 3413401 | GARRETT | GARRETT | 2013-02-01 05:22 | 2013-02-01 10:30 | 3 | 308 | 4779641 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WILL WORK IN THE AM DUE TO HAZARDOUS ROAD CONDITIONS. 6T FUSE OUT DUE TO BROKEN SEC POLE. I HAVE TALKED TO TIM HALL I AM GOING TO TRY TO PUT DROP BACK UP WITHOUT SEC POLE AND HE WILL GET A JOB TO REPLACE POLE I HAVE SERVICE DROP AND SEC DROP SPLICED OUT. FUSED UP EVERYTHING OK. SEC POLE 65-361 ON GROUND VER/PDP IDC XXXX
9346 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-04-29 17:59 | 2020-04-29 23:07 | 3 | 308 | 4773351 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 39830902D00335/ Crew required, no trucks to pole. Fuse on pole 39830902D00655 open. Solid blade switch is actually on pole 902-335. Released by crew 078S02
9347 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2012-07-16 09:12 | 2012-07-16 14:20 | 3 | 308 | 4736431 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38820842A00004 COD-3 REPLACED CUTOUT AND RESTORED @ 14:20. SH VER/HFP L3/HFP
9348 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-08-09 18:51 | 2012-08-10 10:15 | 1 | 924 | 4919321 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA CSP. NEED 15 KVA AND CUTOUT BRACKET, CAN USE TRUCK..CUSTOMER SAID WE COULD CHANGE OUT TOMARROW. RELEASED BY CREW 079H06 COD-1 ISO TF 37820035A00005 VER/HFP L3/HFP IDC XXXX
9349 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2011-06-05 21:52 | 2011-06-06 00:26 | 6 | 154 | 4238601 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION FAILED ON XFMR POLE. <<ONLY AFFECTS SIX CUSTOMERS>> WILL HAVE TO OPEN XFMR ON 785-452 FOR 15 MINUTES TO MAKE REPAIRS. OPENED XFMR @ 23:52. RE-WORKED CONNECTIONS AND CLOSED XFMR @ 00:26. SH VER/TOM L3/TOM IDCC TOF2352 XXXX
9350 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-05-11 16:28 | 2015-05-12 00:10 | 2 | 462 | 4412301 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED VER/CRB
9351 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-05-16 10:50 | 2011-05-16 13:24 | 6 | 154 | 4100121 | 924 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OFF TIME 13:12. LOOSE CONNECTION ON POLE//COD 6// VER/DBM
9352 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-06-15 20:04 | 2015-06-15 21:15 | 13 | 71 | 4576381 | 923 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | POLE 45-6579 4/0 RISER MELTED OF SECOND TIME TEP. BACK TOGETHER SEND NOTE TO RAYBURN NEEDS REPAIRED TUESDAY NEEDS LARGER RISERS/ ISO 38830045D26579/ COD 13/ VER/BOW
9353 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-05-30 14:31 | 2018-05-30 22:12 | 2 | 461 | 4520911 | 922 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 19.9kv The customer is ok with backing a truck in the yard. need 2 men and byucket truck Released by crew 074S07..made repairs
9354 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-12-29 19:28 | 2012-12-30 00:35 | 3 | 307 | 4553601 | 921 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CREW REQUIRED--BAD UG ALL ELECTRIC HOME--IST A FRAME ON RIGHT ON MEADEWOOD HTS RELEASED BY CREW 078S07 .INSTALLED POWER TEMP.WILL MAKE REPAIRS NEXT WEEK.BLR VER/ARN
9355 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-02-20 21:49 | 2014-02-21 13:10 | 1 | 921 | 4407641 | 921 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK WHEN PERSONNEL AVAILABLE,BAD CUTOUT @ 254C-450 REPAIRS MADE ALL CUST RESTORED @ 1310 PLEASE CLOSE TICKET THANKS.BT//COD 1//ISO 38830254C00450// VER/DBM
9356 | Pikeville | 3421001 | BREAKS | CITY | 2019-08-02 17:14 | 2019-08-02 23:20 | 4 | 366 | 4834291 | 921 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva. 7200 on pole 220-632.will need one man with bucket to make repairs. l/f cod 4 37820220B00220/tfo 37820220B00632 cod 1 l/f 2010-2315/tfo back on 2320
9357 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-04-26 16:17 | 2016-04-26 17:49 | 10 | 92 | 4128231 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 BAD CUTOUTS ON POLE 444-13 , LINE CUTOUT & XFMR CUTOUT BAD, REPLACED CUTOUTS RESTORED POWER AT 17:49. VER/AWD
9358 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2017-09-14 14:07 | 2017-09-14 15:39 | 10 | 92 | 4362931 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACE DOOR COD-10 ISO LF @ 38830272000073 VER/HFP L3/HFP
9359 | Paintsville | 3401101 | FALCON | FALC-OILS | 2008-06-03 15:25 | 2008-06-03 19:15 | 4 | 230 | 55078-1 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401101////VER/CRB IDC XXXX
9360 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2011-12-24 11:53 | 2011-12-24 15:43 | 4 | 230 | 4200131 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT DOOR BURNED INTO. REAL OLD CUTOUT WILL HAVE TO BE REPLACED. COD-4 ISO PO 37820148000017 VER/HFP L3/HFP IDC XXXX
9361 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-12-23 16:48 | 2014-12-23 18:20 | 10 | 92 | 4877611 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE ON POLE 496-33 IS OPEN PATROLLING LINE. PRIMARY CONDUCTOR HAS COME OFF OF POLE TOP PIN ON POLE 496-50. POLE IS LOCATED ON SIDE OF MOUNTAIN. GOING TO CLIMB POLE AND MAKE REPAIRS. POWER RESTORED AT 18:20. 12/23/2014// COD 10// VER/ ADH
9362 | Hazard | 3310502 | HADDIX | CANOE | 2018-07-11 15:42 | 2018-07-11 16:05 | 40 | 23 | 4762971 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened recl to safely change a broken cutout on pole 37830121000003 opened @ 1542 closed @ 1605
9363 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2013-01-29 12:25 | 2013-01-29 14:20 | 8 | 115 | 4750681 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | GREG SHOUSE OPENED L. FUSE AND P/T FOR HIMSELF. AT POLE 248-324 , TO MAKE REPAIRS AT POLE 248-771 . POLE TOP IS BROKEN OFF. ///VER/CRB L/3 CRB IDC XXXX
9364 | Hazard | 3310502 | HADDIX | CANOE | 2013-11-25 16:13 | 2013-11-25 20:03 | 4 | 230 | 4073481 | 920 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT, BAD 25, 7200 TRANSFORMER, NEED BUCKET AND TRANSFORMER RELEASED BY CREW 077S05 REPLACED TRANSFORMER AND RESTORED POWER AT 2003 VER/SEF IDC XXXX
9365 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-10-06 16:26 | 2014-10-06 17:17 | 18 | 51 | 4559301 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED LINE FUSE @ 38830067D00272 TO CHANGE TRANSFORMER IN ORDER # 4557471/// 16:26 TO 17:17/// ISO 38830067D00272/// COD 21// VER/BOW VER/DKG L3/DKGXXXC CNT21 - SHOULD HAVE DEDUCTED THE 3 CUST OUT ON THE ORIGGINAL TRANSFORMER OUTAGE
9366 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-07-22 21:44 | 2010-07-23 02:50 | 3 | 306 | 55785-1 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHGED BURNT UP 4/3 SERVICE TO 2/3 ALSO CHGED BAD CUTOUT AND LA CHGED BAD 15KVA TRANS. 25KVA VER/ARN IDC XXXX
9367 | Pikeville | 3421302 | RACCOON | FROZEN CREEK | 2022-09-19 07:42 | 2022-09-19 10:15 | 6 | 153 | 4894381 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | span of primary conductor broke // restored @ 1015 // cod 6
9368 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2022-11-22 11:48 | 2022-11-22 13:30 | 9 | 102 | 4172921 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse failed. Power restored at 13:30
9369 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2013-04-16 19:36 | 2013-04-17 00:42 | 3 | 306 | 4014911 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 217-82 BURNED OFF ABOUT 3 FT. FROM TOP..THINK WE CAN LOWER EVERYTHING..NEED 19900 CUTOUT, ARRESTOR, AND BRACKET.POLE TOP PIN AND INSULATOR, AND POLE TOP EXTENSION, # 2 SERVICE DROP. REMOVED HOT TAP AND PLACED TAG ON 217-80.AND GROUND PLACED AT POLE 82 IN MIDSPAN.. RELEASED BY CREW 074H08 CREW ON SITE REPAIRS COMPLETE RESTORED AT 00:42AM ///VER/CRB L/3 CRB IDC XXXX
9370 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2019-01-16 08:06 | 2019-01-16 10:39 | 6 | 153 | 4677401 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 271-140/no crew required L3/HFP
9371 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-01-05 08:17 | 2020-01-05 10:50 | 6 | 153 | 4214611 | 918 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | secondary riser burned into at connection will need aprox 6 ft. 4/0 copper riser & 1 man.replaced secondary riser.pulled xfmr. off @ 10:45 back on at 10:50//APPROX COD 6//CUSTOMERS ARE MIS MAPPED//WILL SEND SOMETHING TO TECHS L3/HFP
9372 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2012-10-05 10:15 | 2012-10-05 10:24 | 102 | 9 | 4116841 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REPLACING CRACKED CUTOUT//COD 102 (C PHASE)//OPENED NEW RECLOSERS ON POLE 38830140A20478//ISO// VER/DBM IDC XXXX
9373 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-01-08 18:20 | 2016-01-08 20:53 | 6 | 153 | 4596271 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 1147-5564 BAD 7200- 25 KVA, TRK OK RELEASED BY CREW 078S07---CHANGED 25KVA AND CUTOUT---VOLT CK GOOD---TBL TKT COMP// VER/ ADH
9374 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2010-06-16 10:06 | 2010-06-16 17:45 | 2 | 459 | 66140-1 | 918 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HACE A CUTOUT BROKE ON POLE 76-233 I TALKED TO T. HALL AND HES SENDING A BIG BUCKET TO HELP CHANGE THIS//COD 2// VER/DBM
9375 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-06-01 19:01 | 2012-06-01 21:12 | 7 | 131 | 4869521 | 917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEE ORDER 4864631//CREW OPENED SWITCHES IN ORDER TO MAKE REPAIRS TO DOWNED PRIMARY//COD 7// VER/HFP L3/HFP IDC XXXX
9376 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2017-12-08 10:40 | 2017-12-08 12:51 | 7 | 131 | 4630271 | 917 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | repairs made on at 12:51 d sammons 1040-1251
9377 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-05-28 09:26 | 2013-05-28 13:15 | 4 | 229 | 4189891 | 916 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ON SITE WORKING REPLACED ALL WIRE SECONDARY AND SERVICE // BAD PLACE IN NEUTRAL COD-4 ISO TF 37830199B00027 VER/HFP L3/HFP IDC XXXX
9378 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2020-11-30 19:16 | 2020-11-30 23:05 | 4 | 229 | 4732911 | 916 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 conductor 1/0 open wire down from xfmer 69-5695 to sec pole 69-5700. crew reqd. no trucks Released by crew 078S07 crew on site FETR 23:00
9379 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2021-06-12 02:22 | 2021-06-12 10:00 | 2 | 458 | 4721311 | 916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched according to late night call out guide lines. xfm fuse pulled into. restored 10:00
9380 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2008-12-22 11:20 | 2008-12-22 15:09 | 4 | 229 | 62504-1 | 916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS TRANSFORMER FUSE HANGING DOWN//3312202STS TRANSFORMER FUSE HANGING DOWN, BAD TRANSFORMER GOT JEFF COMBS CREW COMMING TO HELP/VER/CRB L3/KEP IDC XXXX
9381 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-11-21 20:08 | 2009-11-22 11:24 | 1 | 916 | 61007-1 | 916 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS FUSE OUT UP ON HILL SIDE RELEASED BY CREW 077S10 WILL WORK IN THE MORNING, PAUL HICKMAN NOTIFIED CHANGED TRANSFORMER AND CUTOUT , POLE MANUEL ON HILLSIDE JKC//COD 1// VER/DBM IDC XXXX
9382 | Hazard | 3310502 | HADDIX | CANOE | 2014-08-18 06:25 | 2014-08-18 09:28 | 5 | 183 | 4377381 | 915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON TRANSFORMER VER/CRB
9383 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2017-07-30 06:13 | 2017-07-30 11:18 | 3 | 305 | 4206171 | 915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830126D30271 . CHANGED CUTOUT , CLOSED XFMR BACK @ 11:18 VER/CRB
9384 | Hazard | 3309301 | VICCO | REDFOX | 2008-01-31 10:30 | 2008-01-31 15:35 | 3 | 305 | 62706-1 | 915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN NEUTRAL//3309301OPEN NEUTRAL BAD TERMINAL BLOCKS ON XFMR POLE HAD A COUPLE CUTOUT GATES BURNT UP ON POLE# 324-150//VER/CRB IDCC PN68 XXXX
9385 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2020-08-18 05:32 | 2020-08-18 10:37 | 3 | 305 | 4341361 | 915 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 7200 on pole 21-b4-3608, trucks to pole. Released by crew 078S02//all repairs made///complete BR
9386 | Hazard | 3310501 | HADDIX | QUICKSAND | 2021-10-11 19:40 | 2021-10-12 10:54 | 1 | 914 | 4341501 | 914 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | per duty supervisor, unsafe to cross river at this time // will work in the a.m. // cust has been advised to turn off main breaker until we can arrive in the morning // change leads on transformer
9387 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-02-21 10:40 | 2015-02-21 12:03 | 11 | 83 | 4061421 | 913 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 94-242 WILL HAVE TO PULL STEP DOWN OFF TO GET FIRE OUT.WILL NEED 7200 & 19.9 CUT OUTS & 2 FIBERGLASS T BRACKETSBAD CUTOUT ON 94-242 NEED MATERIAL HANDLER 7200 & 19.9 CUTOUTS & ARRRESTORS 2 FIBERGLASS T BRACKETS WILL HAVE TO PULL OFF AT POLE 10 TO ISOLATE.PULLED OFF AT 10:40//COD 11//
9388 | Hazard | 3301401 | COMBS | COMBS | 2010-03-31 11:33 | 2010-03-31 12:56 | 11 | 83 | 56465-1 | 913 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP BURNED OFF XFMR RISER AT POLE COD-11 VER/HFP L3/HFP AJB
9389 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-07-21 21:42 | 2010-07-22 12:55 | 1 | 913 | 55337-1 | 913 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | WR#36094311 POLE 44-7128 BAD UNDERGROUND NEED TO WORK 07-22-10 TRANS. POLE 44-7127 TURN UP CHIPPEWA ST. FIRST HOUSE ON LEFT RELEASED BY CREW 078S08// VER/DBM IDCC PN7160 XXXX
9390 | Hazard | 3303902 | LESLIE | WOOTON | 2017-08-26 07:38 | 2017-08-26 11:26 | 4 | 228 | 4300381 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE 37830389A00249 VER/AWD
9391 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2011-05-26 19:48 | 2011-05-26 20:45 | 16 | 57 | 4177471 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 44-9094 BAD LA NO TRUCKS SEND NOTE TO RAYBURN SEND NOTE TO TEC. POLE NEEDS CHGED FALLING OVER SEND NOTE TO TREE PEOPLE POLE COVERED IN TREES AND VINES POLE 44-4063 40T VER/KEP
9392 | Hazard | 3301401 | COMBS | COMBS | 2010-12-12 15:33 | 2010-12-12 19:21 | 4 | 228 | 65644-1 | 912 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 38077903 // SPLICE ON TRANSF POLE BAD == REPAIRED == POWER OK VER/HFP L3/HFP IDC XXXX
9393 | Pikeville | 3413402 | GARRETT | LACKEY | 2010-04-24 10:14 | 2010-04-24 11:30 | 12 | 76 | 50129-1 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20T LINE FUSE BROKE. AND BAD CUTOUT DOOR. REPLACED DOOR FUSED UP EVERYTHING OK. VER/HFP L3/HFP IDC XXXX
9394 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-06-19 19:11 | 2016-06-19 22:59 | 4 | 228 | 4389111 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BLEW REFUSING// CORRECTION FUSE BROKE REFUSED TRANSFORMER POWER RESTORED// COMPLERE TT//COD 4// VER/DBM
9395 | Hazard | 3303902 | LESLIE | WOOTON | 2016-02-21 18:47 | 2016-02-21 22:35 | 4 | 228 | 4745051 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , NEED 1 MAN TO HELP . POLE IS MANUEL
9396 | Hazard | 3420001 | SOFT SHELL | VEST | 2021-04-10 17:43 | 2021-04-10 20:15 | 6 | 152 | 4438771 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout power restored
9397 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2021-02-09 17:41 | 2021-02-09 22:45 | 3 | 304 | 4952931 | 912 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | all customers that feed off of this XFM are getting part power// will have to open XFM on pole 868-D-117 will keep up with times// bad 25KVA 7200 XFM will need line crew to change it out// XFM on pole 868-D-117 off @ 19:40 on@ 22:45/ ISO 38820868D00117/ COD 3
9398 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-11-28 17:39 | 2011-11-29 01:15 | 2 | 456 | 4121231 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED PRC CREW--TOP OF POLE 38830140B00342 BURNT OFF--NO TRUCKS RELEASED BY CREW 078S07.POWER ON AT 01:15 BLR RELEASED BY CREW 078H07. CC = 2. ISOL POLE 139-D-92. VER/SDB IDC NEEDED GO TRACK XXXX
9399 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-07-22 08:16 | 2010-07-22 09:13 | 16 | 57 | 55431-1 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT ON POLE 400-54//COD 16// VER/DBM IDC XXXX
9400 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-05-20 09:51 | 2016-05-20 13:39 | 4 | 228 | 4238521 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARRESTER IS BLOWN & CUTOUT LOOKS TO BE CRACKED, NO TRUCKS LINECREW REQUIRED, ALSO SEND COPY TO TECH TO HAVE REMAPPED. RELEASED BY CREW 078S11 RELEASED BY CREW 078H14ARRESTER IS BLOWN & CUTOUT LOOKS TO BE CRACKED, NO TRUCKS LINECREW REQUIRED, ALSO SEND COPY TO TECH TO HAVE REMAPPED. RELEASED BY CREW 078H14. CREW ON SIGHT REPLACING CUTOUT, APR AT 1339 CLOSE TICKET VER/AWD
9401 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-05-14 21:34 | 2010-05-15 05:10 | 2 | 456 | 62428-1 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35133029 // CLOSED FUSE IN ON TRANSFORMER POLE 044-561 AND FUSE CAME BACK OUT .. BAD 25 KVA XFMR TRIMMED TREES OUT CLOSE TO XFMR.. CUST SAID HEARD LIGHTNING CLOSE TO HOUSE RELEASED BY CREW 078H22//CREW ON SITE P R T//COMPLETE AT 05:10 P R TOLLIVER/// IDC XXXX
9402 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-01-27 06:56 | 2014-01-27 12:00 | 3 | 304 | 4315921 | 912 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND TO B TACKET--BROKEN HOT TAP JUMPER--CUTOUT NEEDS REPLACED --IN ARBYS PARKING LOT RELEASED BY CREW 078S07, CREW ON SITE, REPAIRS MADE, ALL POWER RESTORED COD-3 ISO
9403 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-01-21 22:47 | 2011-01-22 02:35 | 4 | 228 | 63507-1 | 912 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOKS LIKE CONNECTIONS AT WEATHER HEAD IS BAD. WILL BE MAKING REPAIRS. I HAVE REPAIRS MADE EVERYTHING OK. SEND COPY OF THIS TO ENG PIKEVILLE. POLE 54-86 IS LEANING AND COVERED UP WITH TREES AND HAS AN 3 WIRE DROP THAT GOES TO A HOUSE THAT HAS JUST ABOUT FELL IN. 4-3 DROP THAT SERVES CUST NEEDS TO BE CHANGED TO 2-3 DROP POLE NEEDS TO BE RELOCATED TO UPPER END OF CHURCH LOT. POLE 54-137 LOCATED CROSS ROAD FROM CHURCH DONT HAVE ENYTHING ON IT BUT POLE TAG NEEDS REMOVED. VER/PDP IDC XXXX
9404 | Hazard | 3311103 | STINNETT | WENDOVER | 2010-09-21 14:09 | 2010-09-21 15:40 | 10 | 91 | 51919-1 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ROTTON #4 WIRE BROKE//COD 10// VER/DBM IDC XXXX
9405 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-11-29 01:41 | 2009-11-29 03:12 | 10 | 91 | 50540-1 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3401302// REPLACED 4/0 CONNECTION ON TRANSFORMER POLE IDC XXXX
9406 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2021-09-10 17:23 | 2021-09-10 18:33 | 13 | 70 | 4230111 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | rottn 35/6 in the back yard of 1115 walnut ave being held up by ropes since ice storm. sevices are low enough to touch. will need yard dog. Released by crew 078S12 1732-1833rottn 35/6 in the back yard of 1115 walnut ave being held up by ropes since ice storm. sevices are low enough to touch. will need yard dog. Released by crew 078S12//RM opened xfm @ 17:32 closed @ 18:33 please close tic RM
9407 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2014-08-02 09:50 | 2014-08-02 12:00 | 7 | 130 | 4318791 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK IN THE AM 8-2-14 BAD 25KVA OPENED TRANS, 09:50 TRUCK TO POLE CHGED OLD CUTOUT RELEASED BY CREW 078S08 VER/CRB
9408 | Whitesburg | 3314401 | MAYKING | ERMINE | 2009-08-28 07:26 | 2009-08-28 07:39 | 70 | 13 | 54689-1 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP CREW OPENED RECLOSER ON POLE 37830449D30188 TO ALLOW THEM TO SAFELY REPLACE CUTOUTS @ POLE 449-95 OPENED @ 0726 CLOSED @ 0739 COD-70 L3/HFP IDC XXXX
9409 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2018-07-27 17:12 | 2018-07-27 20:14 | 5 | 182 | 4864501 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad trans cutout on 8-B-156.NTA, replaced trans cutout restored power at 20;14 L3/HFP
9410 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2008-01-09 06:17 | 2008-01-09 07:22 | 14 | 65 | 55014-1 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SWITCH, OH | 3000102 SAME AS 55039LOOP BURNT RELEASED BY CREW 078S08 VER/JHM DEBBIE/ONLY 14 CUST AFFECTED BECAUSE AT TIME OF OUTAGE THE NC SWITCH AT POLE 45-5014 WAS OPEN DUE TO A PREVIOUS SWITCHING JOB...CIRCUIT IS BACK TO NORMAL NOW 010908//FAULTED SWITCH ON POLE 38830045C45962 IDC XXXX
9411 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2010-01-11 07:25 | 2010-01-11 15:00 | 2 | 455 | 52275-1 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33383352 // BAD 15 KVA XFORMER TRUCK OK MAY WANT UP SIZE TO 25 KVA RELEASED BY CREW 078S11 COD-2 VER/HFP L3/HFP IDC XXXX
9412 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-10-22 08:30 | 2014-10-22 10:40 | 7 | 130 | 4654041 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15KVA NEEDS CHGED TO 37.5 POLE 68-9001 7 CUST ON POT. NEED TREE CREW TO. RELEASED BY CREW 078S08// PER DUTY SUPERVISOR WILL HOLD UINTIL START OF REGULAT SHIFR 10/23 - TOM RELEASED BY CREW 078Q08/ 8:30-10:40/ ISO 38830068B09001/ COD 7// VER/BOW DKG/SENT EMAIL TO DISPATCHER...DISP SENT EMAIL TO TECH SPV TO HAVE TECH CHECK POLE FOR XMER SIZE AND CUST METERS AFFECTED VER/DKG L3/DKGXXXX
9413 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-12-10 06:20 | 2022-12-10 08:30 | 7 | 130 | 4247801 | 910 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse open 98-B-99,Will be trying to get it back in.Trans fuse open 98-B-615,Will be looking it over..Trans fuse open 98-B-615,Will be looking it over..Restored at 08:30.
9414 | Paintsville | 3401101 | FALCON | FALC-OILS | 2016-05-15 06:12 | 2016-05-15 11:15 | 3 | 303 | 4219141 | 909 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE FAULTED IN MID SPAN BETWEEN 805-10-805-267..2 ALL ELECTRIC CUST. OFF 2-3 TRIPLEX, 479 OF SECONDARY FEEDING 3 CUST..MOSTLY 2-3..UPGRADING 1 SPAN TO 1/0.. VER/CRB
9415 | Hazard | 3303902 | LESLIE | WOOTON | 2020-12-20 01:11 | 2020-12-20 06:14 | 3 | 303 | 4787791 | 909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Called customer/full power/no arcing/ broke cutout 19.9 cutout arr, t bracket, truck acess, cust said he would move truck so we could back bucket next to trl, Released by crew 077S07 On @ 1614
9416 | Pikeville | 3411801 | JOHNSCREEK | META | 2018-12-14 09:57 | 2018-12-14 15:00 | 3 | 303 | 4564171 | 909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFER, GETTING CREW TO REPLACEXFR TO RE-FUSE////////BAD 10KVA XFR(19.9),NEED A 25 KVA.TRUCK APPROACH DOUBTFUL/////CREW ENROUTE SHORTLY/////////REPLACED XFR&RESTORED POWER,ALL OK AFTERWARDS ¦¦¦¦¦ L3/HFP
9417 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-12-05 14:42 | 2015-12-05 19:45 | 3 | 303 | 4512531 | 909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR..RAN SPAN OF SECONDARY FROM POLE 874-41. TO 874-124 PICKING UP ALL CUSTOMERS..WILL CHANGE XFMR NEXT WEEK..PER TIM MILLER..ALL CUSTOMERS OFF 874-97 ARE BACK ON AT 19.45// VER/ ADH
9418 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-04-12 20:55 | 2015-04-13 01:58 | 3 | 303 | 4310301 | 909 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED TRANSFORMER 37830250A00131 AT 20:55, LARGE OIL SPILL, NEED 4 MAN CREW AND 5 BARRELS, 25 KVA, CUTOUT AND TEE BRACKET, 7200 KV, TRUCK ACCESS.//ERIC PRATT (DHE0 AND CREW ENROUTE//..OPENED LINE FUSE ON 37830250A00065 @ 00:35, ALL POWER RESTORED @ 01:58 VER/KEP
9419 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-08-27 20:36 | 2014-08-28 11:45 | 1 | 909 | 4430221 | 909 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND ONE LEG HAS 20 VOLTS OTHER LEG HAS 123AT METER///// CHECKED AT TRANSFORMER GOOD VOLTAGE 124/124/248 //// TALKED TO DAVE SAMMONS WILL GET FIRST THING IN THE MORNING 4/0 UNDERGROUND ABOUT 75 TO 80 FT. RELEASED BY CREW 074H17 REPAIRS MADE ON AT 11:45 D SAMMONS38830214B40313
9420 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-06-24 10:03 | 2009-06-24 13:50 | 4 | 227 | 54809-1 | 908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 30442222 // XFR TO RE-FUSE25 KVA XFR IS BAD,CREW WILL REPLACE.WILL BE ENROUTE SHORTLY.NOTE FETR.CREW REQUIRED RELEASED BY CREW 074S06 COD-4 ISO 38821132000029 L3/HFP IDC XXXX
9421 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2011-02-28 09:48 | 2011-02-28 21:20 | 4 | 692 | 64197-1 | 908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38967435 ///I HAVE A BAD CUTOUT ON POLE NO. 357-170. I NEED HELP TO CHANGE MANUAL CUTOUT . I ISOLATED BAD CUTOUT AND RESTORED ALL BUT 1 CUSTOMER AT 11:00 M.D.I.I HAVE A BAD CUTOUT ON POLE NO. 357-170. I NEED HELP TO CHANGE MANUAL CUTOUT . I ISOLATED BAD CUTOUT AND RESTORED ALL BUT 1 CUSTOMER AT 11:00 M.D.I. RELEASED BY CREW 077S12POWER ON AT 2120//VER/CRB IDC DCMT XXXX
9422 | Pikeville | 3413402 | GARRETT | LACKEY | 2011-07-07 17:07 | 2011-07-07 20:54 | 4 | 227 | 4483041 | 908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED TO REPLACE BAD TRANSFORMER 25KVA 7200//VER/CRB IDC XXXX
9423 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2014-06-21 06:26 | 2014-06-21 14:00 | 2 | 454 | 4133001 | 908 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SINGLE ALL OUT, BAD 25 KVA TRANSFORMER WILL NEED NEW CUT-OUT TRUCK S OK NEAR SIDE RD, CREW REQ, RELEASED BY CREW 078S09 VER/CRB
9424 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2016-06-14 23:03 | 2016-06-15 14:10 | 1 | 907 | 4348161 | 907 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSFORMER. CAN USE TRUCK WILL NEED TO BLOCK ONE LANE ROAD. WILL REQUIRE 2 MEN AND A MATERIAL HANDLER. SHOULD PROBABLY UPGRADE TO A 25 KVA. THIS IS 7.2 KV. RELEASED BY CREW 074S02/// POWER RESTORED @ 14:10 VER/HFP L3/HFP
9425 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2017-11-05 13:20 | 2017-11-05 15:51 | 6 | 151 | 4531851 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | opening transformer to replace a connection/ ISO 38830045D47569/ COD 6/ opened @1320 closed @ 1551/ pole 45-7569 bad 25kva bushind burnt off bring 37.5 TRUCK TO POLE/ xfmr replaced all cust restored @ 1551 please close ticket thanks.bt
9426 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-06-29 09:33 | 2008-06-29 14:35 | 3 | 302 | 59205-1 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 155..55 CREW IN ROUTE VER/ARN IDCC PN18 CNT2 XXXX
9427 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2018-07-04 18:28 | 2018-07-04 23:30 | 3 | 302 | 4723691 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Fuse blown on transformer also neutral broke in1/0 triplex//BAD 25KVA
9428 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-10-21 19:54 | 2021-10-22 11:00 | 1 | 906 | 4001481 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout is broke , need big bucket and 19,9 cutout and flagers Released by crew 077S05 // hold until daylight per crew lead //cod 1//will require flaggers //
9429 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2015-10-10 03:00 | 2015-10-10 10:33 | 2 | 453 | 4335781 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL LOOK AT ON REGULAR SHIFT PER LATE NIGHT CALLOUT.BAD 25 KVA XFMR WILL NEED 1 A LINEMAN ,MATERIAL HANDLER,CUTOUT,ARRESTOR,XFMR & T BRACKET/ ISO 38831152000127/ COD 2/ VER/BOW L3/HFP XXXHFP
9430 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-09-13 10:15 | 2010-09-13 15:17 | 3 | 302 | 65884-1 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | APT 285 70/124 VOLTS BAD UNDERGROUND SECONDARY. D/S REPORTS WILL WAIT UNITL REG. WORK TIME ON 9/13/10 TO MAKE REPAIRS. CC 3 NOT 17 AS PER SERVICER. DANNY TRAUGOTT WILL NOTIFY L.RAYBURN IN THE A.M. /CREW ON SITE LOCATING FAULT/FETR1300/VEMAPT 285 70/124 VOLTS BAD UNDERGROUND SECONDARY//VER/CRB PAF CHANGED TIME OFF 22:56(FULL POWER CALL) DATE CHANGED FROM 09/12 TO 09/13. IDC XXXX
9431 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-11-07 11:51 | 2009-11-07 14:22 | 6 | 151 | 66600-1 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP HIGH SIDE FUSE OUT-BAD ARRESTOR ON STEPDOWN--CALLED CREW NEED HELP WITH TRAFFIC // COD-6 ISO 38830116B00120 L3/HFP IDC XXXX
9432 | Hazard | 3302703 | HAZARD | HAZARD | 2011-07-02 14:19 | 2011-07-02 16:50 | 6 | 151 | 4448901 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE ON POLE.//COD 6// VER/DBM IDC XXXX
9433 | Hazard | 3309002 | JEFF | JEFF | 2020-01-23 07:27 | 2020-01-23 09:58 | 6 | 151 | 4330861 | 906 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Bad transformer connections on pole 345C-144. Going to have to open up this transformer to make repairs. Power restored at 9:58
9434 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2017-12-30 08:38 | 2017-12-30 13:40 | 3 | 302 | 4688581 | 906 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA CSP transformer. Will need to block rd (Dicey Fk) to replace. Line crew & flaggers enroute. Replaced xfmr and restored @ 13:40. sh
9435 | Hazard | 3420001 | SOFT SHELL | VEST | 2019-06-05 09:15 | 2019-06-05 16:47 | 2 | 452 | 4429331 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole completly covered in vines, bad r/w, 7.2 kv cutout burnt up, requires r/w crew and 2 linemen, new cutout, arr, brkt, manual pole Released by crew 077H09pole completly covered in vines, bad r/w, 7.2 kv cutout burnt up, requires r/w crew and 2 linemen, new cutout, arr, brkt, manual pole .AS BUILT COMPLETED.p.hicks
9436 | South Williamson | 3200302 | BELFRY | TOLER | 2018-11-27 19:56 | 2018-11-28 11:00 | 1 | 904 | 4485601 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required. bad 25 KVA trans .trk app . talked to customer and we can wait and replace trans in the morning.can reach trans with bucket trk,also replace cutout and arrestor on the arm. Released by crew 079H03// only one cust per servicer//cod 1//al repairs made power restored at11:00
9437 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2019-11-19 10:34 | 2019-11-19 14:20 | 4 | 226 | 4047021 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 30 t line fuse back in at 14:20 L3/HFP
9438 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2020-11-23 07:19 | 2020-11-23 09:12 | 8 | 113 | 4717051 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | xfmr fuse out on pole 785-217//cutout door had deteriorated and door dropped open//i replaced with new cutout door//restored at 9:12//complete//em
9439 | Hazard | 3309003 | JEFF | VIPER | 2022-05-13 09:29 | 2022-05-13 13:15 | 4 | 226 | 4885431 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout on pole 393-C-19, calling for a big bucket.
9440 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-07 15:47 | 2018-02-07 17:40 | 8 | 113 | 4813941 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 766-36 and also on pole 766-17///cutout broke on pole 766-79//no truck//this doesnt feed anything can isolate with long stick//restored at 17:40//complete//em/ ISO 38830766C00017/ COD 8
9441 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2011-09-18 17:37 | 2011-09-18 19:30 | 8 | 113 | 4882081 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | NO CREW REQUIRED HARDWARE LOOSENED UP LET LOOP HIT POLE 268-142 //VER/CRB IDC XXXX
9442 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-10-31 13:49 | 2009-10-31 17:35 | 4 | 226 | 53643-1 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 37830004D00097 WE HAVE C/O ON XFMR BROKEN AND WILL HAVE TO BE CHANGED OUT, LOCATED ON KVAR POLE. RELEASED BY CREW 077S08 MD FILED REPLACED CUTOUT AND RESTORED POWER AT 1735 077H01 COD-4 2 MISMAPPED CUSTOMERS VER/KEP L3/KEP IDCC PN96 XXXX
9443 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2011-06-06 08:34 | 2011-06-06 12:20 | 4 | 226 | 4239431 | 904 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SER DROP BURNT UP , CALL CREW FOR ASSISTANCE RELEASED BY CREW 078S09---- POWER ON @ 12:20//COD 4// VER/DBM IDC XXXX
9444 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-01-06 09:53 | 2018-01-06 14:54 | 3 | 301 | 4712391 | 903 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer/ customer stated neighbors out of power as well Bad 25 KVA transformer on 852-18. Can truck. Crew enroute. Released by crew 076S02called customer/ customer stated neighbors out of power as well Bad 25 KVA transformer on 852-18. Can truck. Crew enroute. Replaced xfmr & restored @ 14:54. sh/ ISO 38830852000018/ COD 3
9445 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-05-11 14:20 | 2022-05-11 16:29 | 7 | 129 | 4878261 | 903 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a broke Trans cutout at 214-C-126 causing Line fuse to Blow,Will be making repairs..also had a broke cutout at 214-C-32 Restored Line fuse at 16:29..
9446 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2017-03-17 19:59 | 2017-03-17 22:08 | 7 | 129 | 4565891 | 903 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | NO CREW REQUIRED 8T FUSE VER/KEP
9447 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-11-11 03:14 | 2018-11-11 10:45 | 2 | 451 | 4388321 | 902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | /ooTWO CUSTOMERS AFFECTEDoo Secondary connection burnt in two on 851-81. Made repairs and restored @ 10:45. sh L3/HFP
9448 | Pikeville | 3409502 | BURDINE | LEVISA | 2022-08-28 03:49 | 2022-08-28 11:20 | 2 | 451 | 4803961 | 902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA 7200//// will need line crew and flaggers///Opened line fuse on 265-148 @ 05:00 xfm was on fire upon arrival// No truck will have to set up in road to winch xfm Released by crew 074S02///Replaced xfmr and cutout POWER ON @11:20
9449 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2013-01-17 18:13 | 2013-01-17 19:35 | 11 | 82 | 4635721 | 902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HEATED UP AND BURNT NEUTRAL AND BOTH HOT WIRES IN TWO ON SERVICE. REPAIRED AND CLOSED XFMR @ 19:35. PLEASE SEND TICKET TO PEGGY WYSONG IN DAMAGE CLAIMS DEPT. THANKS, SH COD-11 ISO TF 38830785D10409 VER/HFP L3/HFP IDC XXXX
9450 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-02-01 18:58 | 2021-02-01 20:20 | 11 | 82 | 4927121 | 902 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Changing cutout that door has burned up onbad cutout on pole 449-B3-398. will have to replace cutoutbad cutout on pole 449-B3-398. will have to replace cutout. cutout replaced.. power restored @ 20:20
9451 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2018-03-01 18:34 | 2018-03-02 09:35 | 1 | 901 | 4895491 | 901 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | equipment failure cutout/will replace/Broken cutoutBroken cutout, power restored at 09:35
9452 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-06-12 15:45 | 2017-06-12 16:45 | 15 | 60 | 4954041 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED TRANS 69-266 15:45 TILL 16:45 4/3 SERVICE BURNT DOWN VER/CRB
9453 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-01-21 22:51 | 2009-01-22 00:31 | 9 | 100 | 58968-1 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3408303//, ON SITE, XFORMER FUSE BLOWN, REFUSING IT, CONNECTOR IN SERVICE DROP FAILED, MELTING INSULATION, SHORTING OUT SERVICE// VER/ARN L3/KEP
9454 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2014-02-20 21:00 | 2014-02-20 22:15 | 12 | 75 | 4406661 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HAVE BAD SECONDARY CONNECTION AT XFMR POLE. HAVE CALLED FOR MATERIAL HANDLER ,4/0 COPPER 4/0 AUL. & 2 POLY PADS // OFF @ 2100 VER/TOM L3/TOM
9455 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2015-07-15 22:00 | 2015-07-16 13:00 | 1 | 900 | 4888351 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFOMER CUTOUT, REPLACED CUTOUT, POWER RESTORED; CAN CLOSE MWL
9456 | Pikeville | 3120103 | STANVILLE | HAROLD | 2021-04-16 13:00 | 2021-04-16 13:50 | 18 | 50 | 4456541 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO OUTAGE TILL L/F OPEN ON POLE 38831102000070//COD 18//poefire on pole 38831102000145,,opened line fuse on pole 1102-70 at 13:00 tomake repairspoefire on pole 38831102000145,,opened line fuse on pole 1102-70 at 13:00 tomake repairs//power resored at 13:50
9457 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-07-18 13:22 | 2012-07-18 18:22 | 3 | 300 | 4756571 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT BROKEN,,WILL NEED BIG BUCKET,,CUTOUT & FIB. BRKT(12 ),,2 MEN & FLAGGING CREW.RGP.
9458 | Hazard | 3309302 | VICCO | JEFF | 2019-12-08 06:03 | 2019-12-08 08:33 | 6 | 150 | 4134481 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole 323D/417 cutout gate went bad replaced power ok cust.count 3
9459 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2021-12-12 09:57 | 2021-12-12 12:57 | 5 | 180 | 4187451 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50kva nt compl. at 1257 all cust, on,
9460 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2010-08-16 08:39 | 2010-08-16 12:24 | 4 | 225 | 56256-1 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFR FUSE IS BLOWN,WILL RE-FUSE/////////FUSE LINK HAD SIMPLY ROTTED INTO,REPLACED,RE-FUSED,AND RESTORED.ALL OK//COD 4// VER/DBM IDCC PN45 XXXX
9461 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-01-25 11:35 | 2009-01-25 14:05 | 6 | 150 | 59742-1 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411901// REPLACED TRANSFORMER.//COD 6// VER/DBM L3/KEP
9462 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-06-01 10:51 | 2016-06-01 11:01 | 90 | 10 | 4279121 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BAD CABLE ON REGULATOR WHEN CLOSEING IN TRIPPED THE STEP DOWN REPAIRING NOW/ ISO 38831007A00075/ COD 90/ RESTORED 1101/ VER/BOW AJB
9463 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-05-27 15:15 | 2018-05-27 20:15 | 3 | 300 | 4504681 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT
9464 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2022-11-15 10:19 | 2022-11-15 10:55 | 25 | 36 | 4144041 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced cutout door
9465 | Pikeville | 3411801 | JOHNSCREEK | META | 2010-02-01 13:15 | 2010-02-01 20:45 | 2 | 450 | 62003-1 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER 10 KVA 19.9 120/240 RELEASED BY CREW 074S08//VER/CRB IDC XXXX
9466 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-06-17 08:21 | 2018-06-17 09:11 | 18 | 50 | 4609801 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse melted. all restored @09:11. pls close.tre
9467 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-03-07 22:21 | 2017-03-08 02:06 | 4 | 225 | 4533251 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | LINEF OUT,WILL PTRL///////NOTHING EVIDENT ALTHO GUY ON SIDETAP IS BROKEN,LET SIDETAP GET PRETTY SLACK,NEED GUY RE-PULLED TO PULL SIDETAP BACK UP WHERE IT NEEDS TO BE/////////RE-FUSED&RESTORED.BELIEVE WIND MAY HAVE BLOWN SIDETAP CONDS TOGETHER/ ISO 38831056A00039/ COD 4/ VER/BOW
9468 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-03-25 13:36 | 2021-03-25 14:51 | 12 | 75 | 4373701 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout/repairs made. pls close. tre/ ISO 38830116A00035/ COD 12
9469 | Hazard | 3309302 | VICCO | JEFF | 2017-05-03 10:15 | 2017-05-03 11:00 | 20 | 45 | 4738891 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BROKEN CROSSARM 347-A-47/ OPENING STEPDOWN ON POLE 37830347A00315 TO REPLACE CROSSARM/ 1015-11/ ISO 37830347A00315/ COD 20/ VER/BOW
9470 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-12-07 11:00 | 2021-12-07 12:00 | 15 | 60 | 4158311 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout, p-900-27 bad. changing
9471 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-03-24 11:20 | 2013-03-24 15:05 | 4 | 225 | H4951341 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN STEP DOWN TRANSFORMER AT 11:20. DUE TO POLE 164-56 BEING ALMOST BURNT INTO AT BRACES. NEED 2 MAN CREW MATERIAL HANDLER BUCKET TRUCK 8 FOOT CROSS ARM CUTOUT AND ARRESTER SMALL BRACES. WE HAVE REPAIRS MADE EVERYTHING OK.//COD 6// VER/DBM IDCC DUP TO OPEN FUSE XXXX
9472 | Hazard | 3309302 | VICCO | JEFF | 2010-09-15 23:15 | 2010-09-15 23:27 | 75 | 12 | 50235-1 | 900 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | RELATED TO 50208-1//OPENED RECLOSER IN ORDER TO REPAIR FAILED LOOP// VER/DBM IDC XXXX
9473 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2018-04-16 04:38 | 2018-04-16 11:45 | 3 | 427 | 4236361 | 899 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 (2 CUST). Can use bucket truck. Also bring two 7200 cutouts with bracket.Crew required. Bad 25 kva 7200. Can use bucket truck. Also bring two 7200 cutouts with bracket. Only two customers that is off on this transformer, not five. OPENED FUSE ON 38821064B00104 @ 1100 (1 CUST) ALL CUST REST @ 1145
9474 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2011-06-11 17:47 | 2011-06-12 08:45 | 1 | 898 | 4296561 | 898 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | FUSE OUT ON CENTER XFMR.CENTER XFMR. BAD 25 KVA TRUCK APP.THIS IS AT KFC PIKEVILLE.CREW REQ. RELEASED BY CREW 074H04 XFMR CHANGED OUT POWER BACK ON//VER/CRB IDC XXXX
9475 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-03-28 02:26 | 2021-03-28 09:55 | 2 | 449 | 4388261 | 898 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO on pole 1149-72 broke, myles is coming with big bucket to change out// restored @0955
9476 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-10-06 11:10 | 2018-10-06 16:09 | 3 | 299 | 4203291 | 897 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened at 245-18 crew required 3 man trucks ok/ no grounds or tags/pole is 245-279//OPENED HT @ 1110 NO OUTAGE TILL THEN//opened at 245-18 crew required 3 man trucks ok/ no grounds or tags/pole is 245-279 Released by crew 078S03--crew on site--G&T to RMV--Take D.A.-fetr 16:16---solid rock-truck wont dig--had to install pole topper L3/HFP
9477 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2009-09-24 20:21 | 2009-09-25 11:18 | 1 | 897 | 61763-1 | 897 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 37830248D00541HAS ROTTED AND FELL I CUT SECONDARY AT POLE 37830248D00226 CUSTOMER AGREED TO WAIT TILL MORNING FOR RESTORE REQUIRES 3 MAN LINE CREW AND FLAGGERS 30 FT POLE RELEASED BY CREW 077S04//CALL BRUCE IN THE AM TO GET CREW ASSIGNED//STOP TIME IS 2109 CUST AGREED RESTORED 1118 VER/KEP L3/KEP IDC XXXX
9478 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2013-03-25 06:50 | 2013-03-25 10:34 | 4 | 224 | H4954031 | 896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD TAG PLACED FOR KY DDC//NEED 40` 5 POLE & CREW & AWP CREW// FRALEY TO REMOVE KY DDC TAGS & REPLACE WITH HIS //OPENED RECL ON 1048-279 @ 0650 HAVE A POLE BURNTED OFF, POLE NUM 1072-F-47, 405, WILL NEED POLE AND CUTOUT AND ARRESTOR, CREW REQ AND AWP REQ, I HAV RECLOSER ISOLATED AND GROUNDED AND TAGGED FOR DDC AT POLE 1049-D-279.OPENED RECL ON 1048-279 @ 0650 COD-60 ISO OCR 39831048D20279 VER/HFP L3/HFP IDCC DUP TO OPEN RECLOSER XXXX
9479 | Whitesburg | 3314401 | MAYKING | ERMINE | 2011-01-20 11:12 | 2011-01-20 11:40 | 32 | 28 | 62993-1 | 896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREWS OPENED FUSE IN ORDER TO MAKE REPAIRS RELATED TO 62930-1//COD 32// VER/DBM IDC XXXX
9480 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-01-23 09:50 | 2013-01-23 10:18 | 32 | 28 | H4731691 | 896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SEE ORDER 4731691// WE OPENED OTHER TWO RECLOSERS AT 09:50 (COD + 32)//COD 32 // VER/DBM IDC XXXX
9481 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-11-21 07:37 | 2016-11-21 09:45 | 7 | 128 | 4121091 | 896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION BURNT OPEN ON TRANSFORMER RISER. REPAIRED AND RESTORED @ 9:45. TREE GROWN UP INTO PRIMARY AT TRANSFORMER 978-224. PLEASE SEND A NOTE TO ROW TO HAVE TRIMMED ASAP. SH/EMAILED ROW/ADH// VER/ ADH
9482 | Whitesburg | 3314401 | MAYKING | ERMINE | 2020-03-10 20:11 | 2020-03-10 23:55 | 4 | 224 | 4467371 | 896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout.. replaced cutout restored power at 23:55..
9483 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-07-09 15:47 | 2010-07-09 17:55 | 7 | 128 | 64196-1 | 896 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUTS ON POLES 249-181 AND 249-19, D WHEELER ON SITE, FAULT WAS ON N/O POLE ALONG WITH TICKET 64167 COD-7 VER/HFP L3/HFP IDC XXXX
9484 | Cannonsburg | 3103103 | OLIVEHILL | W.CARTERS ELEM | 2016-06-27 19:45 | 2016-06-28 10:40 | 1 | 895 | 4489411 | 895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 12KV - 15KVA XFMR TRUCKS OK,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED VER/AWD
9485 | Paintsville | 3401102 | FALCON | SALYERSVI | 2022-07-11 07:46 | 2022-07-11 10:45 | 5 | 179 | 4458101 | 895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 850-163, cutout bad on 850-175.. changing cutout
9486 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-01-29 15:43 | 2012-01-29 18:42 | 5 | 179 | 4302881 | 895 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LEADS BURNED OFF TRANSFORMER, GOT CREW COMMING TO HELP RELEASED BY CREW 077S05//COD 3// VER/DBM IDCC PN294 XXXX
9487 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-08-11 15:15 | 2014-08-11 22:42 | 2 | 447 | 4354941 | 894 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | LOOKS LIKE BAD UNDERGROUND CONN. TWO HOMES NEED CREW RELEASED BY CREW 078S08//BAD SECONDARY HOT LEG///ATTEMPTING TO LOCATE, WAITING ON LOCATING EQUIP///LOCATING FAULTED CABLE//NO LUCK WITH LOCATING FAULTED SEC CABLE//IN ROUTE TO PICK UP 2 ADD-A-PHASES TO INSTALL ON HOUSES WITH FAULTED CABLE--ADD A PHS INSTALLED PWR RESTORED @ 10:42///PWR CK GOOD ON BOTH HOUSES//REYNOLDS TO FOLLOW UP ON REPAIRS TO UG// XFMR OUTAGE TIMES NOT PROVIDED BY REPAIR CREW // AJB
9488 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-07-03 15:43 | 2012-07-03 23:10 | 2 | 447 | 4278871 | 894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 CONDUCTOR REPAIR NEUT
9489 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2021-08-10 15:43 | 2021-08-10 20:41 | 3 | 298 | 4030501 | 894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva ,7200. trk to pole. line crew reqd. Released by crew 078S07//arrived RM
9490 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2019-04-09 20:51 | 2019-04-10 11:45 | 1 | 894 | 4076161 | 894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kv.7200 xfm.spoke to customer and said would be changed out in the a.m. this is truck accessible..please send copy to PR..chg out transformer restoration 11.45 tom mccown
9491 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-09-08 16:18 | 2018-09-08 23:45 | 2 | 447 | 4059191 | 894 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 19.9 on pole 68-148, will be changing out. Got trans. changed @2345, all ok.
9492 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-04-10 10:07 | 2015-04-11 01:01 | 1 | 894 | 4303251 | 894 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | CREW REQUIRE SPLICE PULLED LOOSE ON ONE LEG OF SERVICE DROP AT POLE 39831148D26536 NO TRUCK POLE IS BEHIND MCKINNY TIRE, RELEASED BY CREW 078H18 RELEASED BY CREW 078H06/CREW ON SITE/WILL NEED TO OPEN XFMR BANK@1148-6531 FOR REPAIRS/APPROX ONE HOUR OUTAGE/VEM/OPEN XFMR@0005/REPAIRS COMPLETE AND ALL CUST RESTORED 0101/PLEASE CLOSE TICKET/THANKS/VEM VER/KEP
9493 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2016-10-03 16:22 | 2016-10-03 20:05 | 4 | 223 | 4957031 | 892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 91-292 BAD 25KVA NEED 37.5 TRUCK TO POLE RELEASED BY CREW 078S08,,CREW ON SITE,,REPLACED XFMR,,ALL POWER RESTORED VER/AWD L3/HFP XXXHFP
9494 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-11-05 21:37 | 2012-11-06 01:20 | 4 | 223 | 4365161 | 892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, POSSIBLE BAD XFMR, CALLED FOR HELP.WILL NEED 7.2 KV CUTOUT AND 25 KVA XFMR. REPLACED CUTOUT //VER/GAH IDC XXXX
9495 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-11-04 06:25 | 2014-11-04 13:51 | 2 | 446 | 4697941 | 892 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN // WILL REFUSE // BAD 25 KVA TRANSFORMER // 19.9 // CREW REQ. RELEASED BY CREW 074S05// ON SITE, CHANGING NOW// WORK COMPLTED, RESTORED AT 13:51// ONLY 2 CUSTOMERS OFF TRANSFORMER 38831126C00678/ ISO 38831126C00678/ COD 2 CCC********// VER/BOW
9496 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2012-07-06 19:59 | 2012-07-07 10:50 | 1 | 891 | 4560241 | 891 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP XFMER///OUT OF TOWN CREWS OPENED YESTERDY WHILE WORKING ON LINE AND NEVER CLOSED BACK IN///CANT GET IT TO STAY IN///BACK ON HILLSIDE CUST SAID WE COULD SET SEC. POLE IN YARD AND COME FROM ACROSS OTHE SIDE OF ROAD IF WE WANTED///15 KVA ACROSS ROAD WILL NEED TO CHANGE TO 25KVA ALSO NEED 35 FOOT POLE AND ROLL OF 2/3 WIRE IF THEY RE-ROUTE IT///7200 VOLTAGE///CREW REQUIRED///BR RELEASED BY CREW 076H07 IDC XXXX
9497 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-08-04 20:11 | 2022-08-04 21:50 | 9 | 99 | 4676881 | 891 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored 21:50
9498 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2010-05-16 20:56 | 2010-05-17 11:47 | 1 | 891 | 63439-1 | 891 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35137242 // TREES IN ROW TOOK CURRENT LIMIT FUSE AT XFMR POLE 399-170.. WILL NEED TWO MEN & BIG BUCKET RELEASED BY CREW 077S11 CHANGED CURRENT LIMIT FUSE XFMR BAD , REPLACED BAD TRANS COD-6 VER/HFP L3/HFP IDCC PN38 CNT6 XXXX
9499 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-02-17 15:10 | 2008-02-17 22:35 | 2 | 445 | 64195-1 | 890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT == REPLACED == IDC XXXX
9500 | Whitesburg | 3314401 | MAYKING | ERMINE | 2014-01-08 08:01 | 2014-01-08 09:30 | 10 | 89 | 4258061 | 890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE VER/CRB L3/HFP IDC XXXX
9501 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2015-02-10 12:41 | 2015-02-10 14:10 | 10 | 89 | 4005701 | 890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// WILL REFUSEFUSE APPEARED TO HAVE BROKE// POWER RESTORED/COD 10// VER/ ADH L3/HFP
9502 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2009-01-21 09:22 | 2009-01-21 12:20 | 5 | 178 | 58779-1 | 890 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-5 WR # 28153060 // BAD CSP XFMR. CREW ENROUTE TO REPLACE. XFMR REPLACED. SH L3/HFP
9503 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-12-17 05:32 | 2009-12-17 08:30 | 5 | 178 | 51180-1 | 890 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 PHASE OF SECONDARY BURNED DOWN .I WILL BE ABLE TO REPAIR MYSELF . REPAIRED OPEN WIRE SECONDARY THAT BURNED DOWN COD-5 VER/HFP L3/HFP
9504 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2013-06-11 12:08 | 2013-06-11 14:15 | 7 | 127 | 4258331 | 889 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CLEARED UP BAD ARRESTER ON POLE 212-177.//CREATED AED ENTRY FOR BAD ARRESTER//COD 7// VER/DBM IDC XXXX
9505 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-03-25 12:00 | 2012-03-25 14:07 | 7 | 127 | H4615311 | 889 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP APPEARS TO HAVE BURNT OPEN ON DOUBLE DEADEND 955-35. ONLY FOUR CUSTOMERS AFFECTED. OPENED REC 955-508 @ 13:23. REPLACED INSULATOR AND LOOP. CLOSED BOTH RECLOSERS ON 955-508 @ 14:07 RESTORING ALL CUSTOMERS. SH //VER/CRB IDC DUP TO OPEN RECLOSER XXXX
9506 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2012-08-13 19:46 | 2012-08-14 10:35 | 1 | 889 | 4933901 | 889 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN ON POLE 37820149000132 10KVA 7200 XFMR IS BAD CAN USE TRUCK WILL WORK ON 8/14, COULD NOT REACH SUDDEN LINK CONTACT #, ONLY FEEDS BOOSTER, ALSO NEED TO ISOLATE 3 PHASE TAP W BROKEN CUTOUTS ON METERING RELEASED BY CREW 074H18 IDC XXXX
9507 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2018-07-01 12:06 | 2018-07-01 13:20 | 12 | 74 | 4694531 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer ETA approx 1240 broke cutout on pole 38830045D37123 back on at 13:20
9508 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-08-08 09:06 | 2011-08-08 16:30 | 2 | 444 | 4678031 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR.THIS IS A 50 KVA BUT SHOULD BE ABLE TO GO BACK WITH 25. IT ONLY FEEDS 2 - 200AMP SERVICES.THIS IS 1 POLE ABOVE TACKETT LANE. OR JUST BELOW CAM BR. RELEASED BY CREW 074S04//COD 2// VER/DBM IDC XXXX
9509 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2017-12-06 11:04 | 2017-12-06 11:10 | 148 | 6 | 4625791 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED ON POLE 37830379B00339 OPENED RECLOSER 37830379C00552//OPENED 1104 CLOSED 1110
9510 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-06-03 07:26 | 2013-06-03 14:50 | 2 | 444 | 4212401 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED--BAD 25KVA TRANSFORMER--NEED NEW CUTOUT--LOCATED AT DEADEND OF INDIA DR--CAN USE MATERIAL HANDLER--VINES ON POLE RELEASED BY CREW 078S07 ///VER/CRB L/3 CRB
9511 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-06 13:07 | 2009-06-06 16:49 | 4 | 222 | 50747-1 | 888 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP LOOSE CONNECTION ON POL COD-4 ISO 38831076000115 THIS IS FOR THE PART POWER DUPLICATING FOR THE TR OUTAGE TO MAKE REPAIRS L3/HFP IDC XXXX
9512 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-12-29 16:42 | 2010-12-29 21:38 | 3 | 296 | 56780-1 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CALLED CREW--OPENED TRANSFORMER AT 16:42 TO MAKE REPAIRS RELEASED BY CREW 078S07 RESQUEEZE NEUT. CONNECTIONS. MPHELPS RELEASED BY CREW 078H12 VER/TOM IDC XXXX
9513 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2016-02-20 13:49 | 2016-02-20 18:45 | 3 | 296 | 4740631 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 10 NEED 25 WITH NEW RISERS CUTOUT OK TRUCKS YES 280-79 RELEASED BY CREW 078S03/CREW ON SITE/FETR1830/VEM VER/CRB
9514 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2011-07-23 14:34 | 2011-07-23 19:30 | 3 | 296 | 4599771 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD19.9 CUTOUT REPLACED CUTOUT POWER RESTORED@19:30 VER/KEP
9515 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-04-03 15:16 | 2010-04-03 22:40 | 2 | 444 | 58131-1 | 888 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830206C02170 IS ROTTED AT GROUND AND LYING IN TREES, PULLED SERVICE OFF OF HOUSE, NEED CREW AND 45-4 POLE, THIS IS AN IN LINE XFMR POLE WITH SEVERAL SERVICES, IN BACK YARD BUT SOLID ENOUGH FOR TRUCKS./STREET LIGHT WIRE DOWN AT POLE 38830206C02369, ROAD CROSSING, ALSO TREE ON LINE GOING TO XFMR, NEED LINE AND TREE CREW VER/KEP AJB
9516 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-02-27 19:33 | 2011-02-28 10:20 | 1 | 887 | 63547-1 | 887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA PRIMARY BUSHING LOOKS BURNT ALSO COULD POSSIBLE SE BAD KMATE CUST AGREED TO WAIT TILL MORNING TO CHANGE CAN GET BIG BUCKET OFF ROAD RELEASED BY CREW 077S01 VER/KEP IDC XXXX
9517 | Hazard | 3311103 | STINNETT | WENDOVER | 2021-01-08 21:13 | 2021-01-09 12:00 | 1 | 887 | 4857701 | 887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 Kva 7200 on pole 37830411000020. Crew required. Truck accessible. Will hold till daylight per duty. //Arcos Phil Hicks and Dave Smith @ 0700 //, replaced xfmr, and secondary, all restored @ 12:00 hrs p.hicks
9518 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2019-09-13 08:20 | 2019-09-13 09:57 | 11 | 97 | 4012521 | 887 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse blown on 966-C1-102 due to bad arrester on 966-C1-113.closed line fuse on 102 in at 09:27,replaced arrester on 113 and closed trans on 113 in at 09:57 Released by crew 079H03 ¦¦¦ LOOKS LIKE THIS WENT THRU THE FUSE ON POLE 38820966C10104 TAKING OUT THE FUSE ON POLE 38820966C10102 - L3/HFP
9519 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2020-10-29 06:12 | 2020-10-29 13:35 | 2 | 443 | 4594321 | 886 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines CREW req, found bad c/o on 1000-40, house right across from Meadow Lane, will need big bucket can reach from drive way, my truck would not reach it, Released by crew 078S06
9520 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-01-20 14:35 | 2022-01-20 19:30 | 3 | 295 | 4391671 | 885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 1037B-83.going to be removing old can then illhave to run to the office to get a new one.made repairs and got transformer fuse on pole 1037B-83 back in at 19:30
9521 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2017-04-23 02:15 | 2017-04-23 17:00 | 1 | 885 | H4670131 | 885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 68-953 BURNT OFF POLE 68-88 40T ON 04:45 AM POLE 68-953 NO TRUCKS 1-CUST OFF 4134 PINE TERRACE CT. OFF PINE ST. IRONVILLE NEED DAY LIGHT RELEASED BY CREW 078S08 13 CUST RESTORED 0445/ LEAVING 2 CUST OFF ON 38830068A00953 ISOLATED BY TAP ON 38830068A00591 CLOSED AT 1700 VER/AWD OPENED TRANSFORMER ON THIS ORDER TO CLOSE IN. VER/AWD NEED TIME OFF COULD NOT FIND ON VOICE RECORDER = HFP
9522 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-08-15 07:04 | 2011-08-15 11:59 | 3 | 295 | 4711811 | 885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHANGE DEFECTIVE CUTOUT. REPLACED CUTOUT ./// COD-3 ISO TF 38830978C10118 VER/HFP L3/HFP IDC XXXX
9523 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-01-12 21:03 | 2012-01-13 01:58 | 3 | 295 | 4253891 | 885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ONE LEG OUT ON UNDERGR. SERVICE . SQUEEZEON BURN UP AND CAME APART ON XFORM. RISER LEG . NEED LINE CREW TO HELP NO TRUCKS, LINKOUS IS ON HIS WAY OPEN XFORM AT 1:20 AM ON AT 1:58 POWER RESTORED//COD 1 + 2 // IDC XXXX
9524 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-06-18 08:55 | 2013-06-18 13:50 | 3 | 295 | 4363181 | 885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1.6T FUSE OUT DUE TO BAD CUTOUT CHANGED CUTOUT FUSED UP EVERYTHING OK. COD-3 ISO TF 38831101D20188 VER/HFP L3/HFP
9525 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-03-17 23:15 | 2020-03-18 14:00 | 1 | 885 | 4486841 | 885 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva xfmr need flagging crew and material handler..Tommy Goble to change,,, Released by crew 076S01.Repairs made back to normal
9526 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-12-09 16:23 | 2008-12-09 17:31 | 13 | 68 | 55842-1 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP 3308002//STS WR 27613458// L3/IDC IDC XXXX
9527 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-04-01 15:19 | 2009-04-01 19:00 | 4 | 221 | 63819-1 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLING FOR CREW BAD 25KVA TRANSFORMER // 4 COD VER/TOM L3/TOM IDCC MCCDIS XXXX
9528 | South Williamson | 2970603 | HURLEY STATION | RACEFORK | 2015-12-05 21:48 | 2015-12-06 01:29 | 4 | 221 | 4512711 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 82-116 IS A POLE AND HAS ROTTED OFF AT THE GROUND LINE AND IS LAYED OVER BAD. THIS CAN BE ISOLATED AT POLE 37820082A10106 WHEN REPAIRS ARE MADE. POLE NEEDS REPLACED TONIGHT AND IS TRUCK APPROACH. REPLACED POLE AND ALL HARDWARE. OPENED LATERAL AT 21:48 - 68CC VER/TOM L3/TOM
9529 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2015-07-26 11:41 | 2015-07-26 15:43 | 5 | 242 | 4943521 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA CSP CREW REQ, TRUCK CAN BE USE, RESTORED L/F AT 1071-12 AT 1300, RELEASED BY CREW 078S06 /ON SITE RM ALL POWER RESTORED AT 15:43 PLEASE CLOSE TIC RM VER/CRB
9530 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-08-30 17:14 | 2018-08-30 22:48 | 5 | 334 | 4018161 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 kva xfmr bad manuel
9531 | Hazard | 3303901 | LESLIE | HYDEN | 2010-12-15 06:44 | 2010-12-15 14:06 | 2 | 442 | 50420-1 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38116558 // DON`T FORGET THE FETR // BAD 15KVA 19.9 AND OIL SPILL RELEASED BY CREW 077S01 COD-2STS WR # 38116558 // DONT FORGET THE FETR // BAD 15KVA 19.9 AND OIL SPILL RELEASED BY CREW 077S01 COD-2 REPLACED TRANSFORMER AND RESTORED POWER AT 1406 JKC /// COD-2 ISO TF 37830388B00060 VER/HFP L3/HFP IDC DCMT XXXX
9532 | Pikeville | 3421001 | BREAKS | CITY | 2018-02-12 06:58 | 2018-02-12 10:30 | 5 | 212 | 4833101 | 884 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | called customer no reading on meter and neighbors out as well/// Line fuse blown on pole#243-27// will patroll/// top of poleburnt off and let pole top pin float/// need crew to make repairs/// will lift hot tap on pole#243-87 to isolate trouble// Closed line fuse in @ 09:02 up to pole#243-87/// Repairs made put hot tap back on @ 10:30 and restored all customers Released by crew 074S02/ ISO 37820243D00027/ COD 5
9533 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-03-29 08:19 | 2010-03-29 13:13 | 3 | 294 | 55417-1 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JOURNEY OPERATING CALLED PAUL WIRE DOWN IN THIS AREA VER/KEP L3/KEP AJB
9534 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-05-31 19:09 | 2009-06-01 02:30 | 2 | 441 | 54941-1 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308402/ D/S WILL SEND SERVICER AS SOON AS ONE IS AVAILIABLE. CREWS ARE WORKING STORM TROUBLE FROM LAST NIGHT. ==BAD 10 KVA == WILL NEED A 25 KVA 7200 TRANSF == YOU CAN GET TRUCK TO POLE RELEASED BY CREW 077S03 REPLACED XFMR RESTORED POWER AT 0230 IDC XXXX
9535 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-03-20 14:22 | 2022-03-20 16:28 | 7 | 126 | 4650851 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on xfmr. Opened xfmr 882-145 @ 15:34, reworked all connections on xfmr pole and closed xfmr @ 16:28. sh
9536 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-01-10 08:13 | 2016-01-10 22:55 | 1 | 882 | 4598721 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, BAD C/O ON 1097-1280, NO TRUCKS, HOT TAP LIFTED ON POLE 1097-1278, GRD AND TAGGED TO DDC AT THIS POLE RELEASED BY CREW 078S06.. CREW ON SITE ETR 22:30. NEW ETR 23:00.. CUTOUT CHANGED AND CUST RESTORED AT 22:55 TICKET COMPLETE CY VER/CRB
9537 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2019-07-06 12:38 | 2019-07-06 15:05 | 6 | 147 | 4665731 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ONLY OUTAGE CUTOUT BROKE 20-5528, Cutout changed, line fuse re-energized at 15:05 L3/HFP
9538 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2016-05-29 10:02 | 2016-05-29 11:40 | 9 | 98 | 4270101 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED. REPLACED CUTOUT AND RESTORED @ 11:40. SH/ VER/BOW
9539 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-01-01 02:26 | 2015-01-01 03:15 | 18 | 49 | 4895861 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF @ POLE 184C-255, REPAIRS MADE ALL CUST RESTORED @ 0315 PLEASE CLOSE TICKET THANKS.BT VER/ARN VER/DKG L3/DKGXXXX
9540 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2016-11-22 08:53 | 2016-11-22 10:59 | 7 | 126 | 4123791 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 120-240 XFMER, TRK OK RELEASED BY CREW 078S07/CREW ON SITE/FETR 1115/VEM/POWER RESTORED TO ALL CUST 1059/PLEASE CLOSE TICKET/THANKS/VEM// VER/ ADH
9541 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-02-19 12:54 | 2019-02-19 15:00 | 7 | 126 | 4807481 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm fuse blown will refuse// Bad cutout on pole#267-28/// opened line fuse on pole 267-27 @ 14:20 to safely change cutout// Changed bad cutout and closed line fuse in @ 15:00 and restored service ¦¦¦ NOTE NO OTHER CUSTOMERS INTERRUPTED BY OPENING LINE FUSE = L3/HFP
9542 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2014-08-04 04:08 | 2014-08-04 09:02 | 3 | 294 | 4328581 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM 8-4-14, BAD CUTOUT ON POLE 496-158, MADE REPAIRS RESTORED POWER AT 09:02.//COD 3//ISO// VER/DKG L3/DKG
9543 | Hazard | 3311103 | STINNETT | WENDOVER | 2008-07-30 13:39 | 2008-07-30 15:45 | 7 | 126 | 62185-1 | 882 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3311103 -BAD L/A BLEW 15T LINE FUSE ON 459-58//SENT MAPPING REPORT//COD 7//ISO 37830459C00058// VER/DBM IDC XXXX
9544 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2017-01-06 18:05 | 2017-01-07 01:25 | 2 | 440 | 4274261 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 15 NEED 25 KV/ BESIDE HOUSE MAYBE TRUCKS BUT PROBABLY NOT/ NEED BAG TRASNFORMER LEAKING/ NEED 4 MAN CREW/ ISO 38830245A00241/ COD 2 VER/KEP L3/HFP XXXHFP
9545 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2022-04-08 02:32 | 2022-04-08 09:52 | 2 | 440 | 4739881 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Transformer cutout failed. Replaced and restored @ 9:52. sh
9546 | Pikeville | 3403001 | PIKEVILLE | CITY | 2017-06-13 14:10 | 2017-06-13 15:30 | 11 | 80 | 4956491 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAD 75 KVA PADMOUNT TRANS.37830024B31153, THIS WILL NEED A LINE CREW, CAN BACK A LINE TRUCK NEXT TO THIS CAN, TIM HALL IS GETTING A CREW TO MAKE REPAIRS. RELEASED BY CREW 074S05//SENT TO TECH TO GET MAPPING CORRECT AND COD//THIS TRANS SHOWS 0 CUSTS //SERVICER SAYS COD 12//OFF @ 14:10 //ON @ 15:30 VER/CRB SJGC STEP2 TON15:30 CNT11 (DELETED)
9547 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-08-03 17:02 | 2013-08-03 18:30 | 10 | 88 | 4619921 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-7034 PRI LOOP BOTTOM OF CUT OUT BURNT OFF INSTALLED ONE NEW CUTOUT REPLACED THE OTHER OPENED CUTOUT 18;00 TO 18;30 30T FUSES BOTH SIDES ORIGINAL 10 CUSTOMER OUT UNTIL 18:00 THEN ALL 28, ALL BACK ON AT 18:30 SEE DUPLICATE H4619921 VER/SEF
9548 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2018-06-26 17:10 | 2018-06-26 20:50 | 4 | 220 | 4673071 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 760-49.changing
9549 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-12-16 08:34 | 2008-12-16 12:25 | 40 | 231 | 58869-1 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27698375 //POLE FIRE AT 232-67, ISOLATED AT 38830232000067,POLE FIRE AT 232-67, ISOLATED AT 38830232000067, LINE FUSE RESTORED AT 08:45, 2 CUSTOMERS OUT, LINE CREW HAS BEEN NOTIFIEDPOLE FIRE AT 232-67, ISOLATED AT 38830232000067, LINE FUSE RESTORED AT 08:45, 2 CUSTOMERS OUT, LINE CREW HAS BEEN NOTIFIED RELEASED BY CREW 078S05 L3/HFP IDC CHANGED TIME OFF FROM 817 XXXX
9550 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-12-13 04:50 | 2021-12-13 08:30 | 4 | 220 | 4190021 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | holding per dennis massey //Trans fuse open at 120-C-118,Going to refuse and restore service.Trans fuse open at 120-C-118,The fuse had broke in Trans cutout,,.Restored at 08:30.
9551 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2019-01-04 14:14 | 2019-01-04 14:58 | 20 | 44 | 4628101 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DOL CASE #886657/ CROSS ARM BROKE AND CUTOUT ON POLE 37830449A20703. WILL NEED TO OPEN UP AT POLES 449-121 AND 449-A1-23 TO MAKE REPAIRS Released by crew 075H03
9552 | Pikeville | 3403001 | PIKEVILLE | CITY | 2011-06-13 09:56 | 2011-06-13 11:46 | 8 | 110 | 4309861 | 880 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD TO SLICE NEUTRAL TOGETHER
9553 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2013-03-13 12:55 | 2013-03-13 14:45 | 8 | 110 | 4903631 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | XFORMER POLE 308-48 ROTTEN AND FELL OVER INTO TREES, LIFTED PRIMARY JUMPER FROM POLE 308-46 TO 308-47.. MUST HAVE 4WHEEL DRIVE TRUCKS OR TRACK BUCKETT. THIS IS JUST HUNTTING CABIN, CAN WATE TILL DRY. RELEASED BY CREW 078S01 VER/KEP IDC XXXX
9554 | South Williamson | 3200301 | BELFRY | BELFRY | 2020-03-13 23:32 | 2020-03-14 03:12 | 4 | 220 | 4477381 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFRF IS OUT,WILL RE-FUSE////////XFR IS BAD,NEED 25KVA 7.2,MATERIAL HANDLER,1 MAN////////REPLACED XFR&RESTORED
9555 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-01-07 23:14 | 2022-01-08 00:34 | 11 | 80 | 4322821 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse is open @ 191-B-53,Going to refuse and restore..Trans fuse is open @ 191-B-53,Fuse had Broke, replaced fuse and Restored Trans @ 00:34.//cod 11
9556 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2022-01-27 15:19 | 2022-01-27 18:15 | 5 | 176 | 4410451 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad transformer on pole 1037B-79.i have a new transformer in route.ill be taking the old one down.made repairs and got fuse on pole 1037B-79 back in at 18:15
9557 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-06-24 13:36 | 2013-06-24 15:26 | 8 | 110 | 4392081 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 356-128, OPENED RECLOSER ON POLE 356-118 AT 15:03 TO ISOLATE.. REPLACED CUTOUT RESTORED POWER AT 15:26. IDCC CNT43 TON1533 XXXX
9558 | Paintsville | 3409302 | KENWOOD | AUXIER | 2014-08-09 11:10 | 2014-08-09 12:05 | 16 | 55 | 4347151 | 880 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOBBY BOWERSOCK OPENED FUSE ON POLE 882-C2-906 TO PERFORM WORK RELATED TO ORDER 434501//COD 16// VER/DBM AJB
9559 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-08-31 13:22 | 2013-08-31 18:15 | 3 | 293 | 4805471 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 38831059D00083, CHECKING/// ARRESTOR BROKEN ON POLE 38831059D00108 LYING ON ARM. WILL CUT IN CLEAR AND MAKE BACK HOT./// CUT ARRESTOR IN CLEAR, POWER RESTORED. VER/CRB L/3 CRB IDC XXXX
9560 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-01-18 16:12 | 2010-01-18 21:05 | 3 | 293 | 56175-1 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED 25 KVA NEEDS CHGD SECONDARY BUSHINGS BROKE NEED YARD DOG RELEASED BY CREW 078S03---CREW ON SITE2100 VER/HFP L3/HFP IDC XXXX
9561 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2017-03-05 20:38 | 2017-03-06 11:17 | 1 | 879 | 4524661 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PER CUSTOMER COMMENTS OK TO CHECK IN THE AM 3/6/17--/ BAD CUTOUT REPLACED POWER OK 37830292C10246 VER/AWD
9562 | Hazard | 3303903 | LESLIE | HALSFORK | 2012-11-13 09:37 | 2012-11-13 14:30 | 3 | 293 | 4392641 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE OPEN ON 361-95 POLE TOP BURNED OFF CREW ON WAY--HOT TAP LIFTED---POLE NEEDS CHANGED OUT DRY WEATHER SEND TO DOUG CHRISTIN VER/KEP IDC XXXX
9563 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-15 20:17 | 2010-05-16 10:56 | 1 | 879 | 62874-1 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | PART POWER,RED/RED OUT,VERY BAD POLE,LEANING,WILL NEED TO WAIT TIL DAY,STEEP METAL ROOF TO WORK-CANT REACH WITH LADDER--TOLD CUSTOMER--JIM RELEASED BY CREW 077S06//LEAD BURNT UP ON CUSTOMERS SERVICE// VER/DBM IDC XXXX
9564 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-03-04 15:53 | 2008-03-04 18:10 | 8 | 137 | 52774-1 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RESTORED MAIN LINE AT 1739 REPLACED BAD CUTOUT VER/HFP IDC XXXX
9565 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2021-12-12 19:06 | 2021-12-13 09:45 | 1 | 879 | 4189641 | 879 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 KVA xfm///Will need 15KVA 7200 ///Can use truck///This can be changed tomorrow DDC spoke with customer and said this feeds a meter where he is going to build a house Released by crew 074S02
9566 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-11-21 06:07 | 2008-11-21 13:50 | 6 | 463 | 50468-1 | 878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 27392729 /// POLE BURNT OFF, POLE # 134-134. CAN RESTORE ALL POWER EXCEPT THIS POLE, CALLING FOR CREW. ETR ON 1 CUST SET FOR 14:00 HRS RELEASED BY CREW 077H15 IDC XXXX
9567 | South Williamson | 3411401 | DEWEY | INEZ | 2017-05-06 01:51 | 2017-05-06 09:10 | 2 | 439 | 4759121 | 878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON TRANS 38830742D00079//REPLACING// COD 2 PER SERVICER VER/CRB
9568 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-05-20 18:16 | 2016-05-21 01:35 | 2 | 439 | 4240571 | 878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD DEAD END INSULATOR 19KV ON POLE38831108D00140,MANUAL MIGHT BE ABLE TO TO SOME TREES AND GET BIG BUCKET, NEED 3 MAN LINE CREW AND R/W CREW RELEASED BY CREW 077H07 MADE REPAIRS AND RESTORED POWER AT 0135//COD 2// VER/DBM
9569 | Hazard | 3303901 | LESLIE | HYDEN | 2012-12-21 10:26 | 2012-12-21 17:45 | 2 | 439 | 4499571 | 878 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON POLE REPLACED AND CHECKED VOLTAGE//COD 2// VER/DBM
9570 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-05-02 11:06 | 2008-05-02 14:56 | 5 | 230 | 56289-1 | 878 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000303// TRANS 20-3531//COD 5//ISOLATED BAD CSP AND RESTORED MAIN LINE @ 1240//BAD 50KVA NEED CUTOUT /LA CUT LOOP ON POLE 20-3510 GROUNDED LINE/WORK COMPLETE AND POWER RESTORED 1456/PLEASE CLOSE TICKET/THANKS /VEM// VER/DBM IDC XXXX
9571 | Pikeville | 3403001 | PIKEVILLE | CITY | 2019-03-11 10:34 | 2019-03-11 12:44 | 18 | 130 | 4970471 | 878 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Span of 1/0 open wire burndt down going from trans bank 24-D4-909 going to 24-D4-979, will have to open trans. bank on 909 up to make repairs, will let all customers know and will keep track of times. Opened trans. bank @1200 made repairs and put back in @1244.
9572 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2017-03-31 06:58 | 2017-03-31 09:24 | 6 | 146 | 4600651 | 876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNED UP/BROKEN CUTOUT TO REPLACE//////REPLACED CUTOUT&RESTORED,ALL OK AFTERWARDS COD-6 ISO TF 38821012C00020 VER/HFP L3/HFP
9573 | Hazard | 3301101 | CHAVIES | CHAVIES | 2010-10-25 07:00 | 2010-10-25 14:18 | 2 | 438 | 62665-1 | 876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT GOT FRANK HURLEY COMMING TO HELP ON CUTOUT SERVICER OPENED LF AT POLE 288-68 15 CC OFF 1402 ON 1418 MADE DUP ORDER VER/KEP L3/KEP APPOX 15 MIN. IDC XXXX
9574 | Hazard | 3309301 | VICCO | REDFOX | 2012-08-01 20:08 | 2012-08-02 10:44 | 1 | 876 | 4881361 | 876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT , MANUAL BEHIND HOUSE LIFTED CLAMP ON 301-259BAD 19.9 CUTOUT , MANUAL BEHIND HOUSE . RELEASED BY CREW 075H04. POWER RESTORED VER/KEP IDC XXXX
9575 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-07-04 14:30 | 2017-07-04 16:56 | 6 | 146 | 4071981 | 876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 185-141 LINE FUSE OPEN, 161-84 BROKE CUTOUT,CALLED FOR 1 MAN,BIG BUCKET,,,CUTOUT REPLACED..ALL CUST/ RESTORED COMPLETE VER/CRB
9576 | Hazard | 3302704 | HAZARD | KENMONT | 2015-02-17 07:51 | 2015-02-17 11:30 | 4 | 219 | 4035421 | 876 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD SPLICE IN 1/0 LASH ON POLE 37830296C20536/ ALSO FOUND BURNT OFF CROSSARM ON POLE 37830296C20537/ OUTAGE ON STEPDOWN 37830296C21296 TO REPAIR CROSSARM AND SPLICE/ ORIGINAL OUTAGE 4 C PHASE CUSTOMERS PART OUT ON POLE 37830296C20536 @ 0751/ 144 CUSTOMERS OUT ON POLE 37830296C21296 @ 0950/ ALL POWER RESTORED @ 1130// SEE DUP H4035421 FOR 143 CUST/ ISO 37830296C21296/ COD TOTAL 147/ VER/BOW
9577 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2018-06-29 16:53 | 2018-06-29 21:45 | 3 | 292 | 4689981 | 876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 1 man and material handler.
9578 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2011-10-16 07:32 | 2011-10-16 08:45 | 12 | 73 | 4987041 | 876 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE SPAN #2 AL DOWN FROM POLE 186-32 TO 186-234, TRUCKS TO POLE 186-32. PLACED GROUNDS ON POLE 186-32, ALSO THERE IS A 30 T LINE FUSE ON POLE 186- 32. LINE FUSE BACK IN ON POLE 186-33 AT 08:45. NEED LINE CREW. RELEASED BY CREW 078S01 VER/ARN IDC XXXX
9579 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2022-11-18 07:27 | 2022-11-18 09:20 | 13 | 113 | 4157601 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Jumper burned off at 38830930B00284 (7 COD) toward 38830930B00243-once crew gets on site will open LF 38830930B00275 (not on map-5 more COD)had a loopbrunt out at pole 930-B-284/// had to open 40T fuse at pole 930-B-275 to make repaires at a time of 9:06/// got repaires made at pole 930-B-284 and got lne fse at pole 930-B-275 restored t a time of 9:20 Released by crew 074S03//MD MADE
9580 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-04-17 20:15 | 2011-04-18 10:50 | 1 | 875 | 59995-1 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER-- NEED CREW MAY BE MANUEL BAD BRIDGE RELEASED BY CREW 077S10 FRANK REPORTS CUSTOMER AGREED TO WAIT UNTIL REG WORK TIME ON 4/18/11. //VER/GAH IDC XXXX
9581 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2022-05-06 10:15 | 2022-05-06 12:35 | 22 | 140 | 4843411 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lf out on pole 398B-244. Broke manual cutout on pole 37830398B00383. Got it in the clear. Will need crew to make repairs.//Lf closed back in at 10:50//Cutout replaced power restored at 12:35.
9582 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2012-10-19 14:50 | 2012-10-19 17:45 | 5 | 175 | 4157191 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT SECONDARY IN ROAD, OPEN WIRE SECONDARY HAS BURNT DOWN, HELP COMING. HAD TO OPEN XFMR ON POLE 181-57 RELEASED BY CREW 077S02 ///VER/CRB L/3 CRB IDC XXXX
9583 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-12-22 15:45 | 2018-12-22 16:10 | 35 | 25 | 4592711 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | OPENED GOAB SWITCH ON POLE 38830930B20861 @ 1545//COD 35//arm pin broke on pole 930-154 and phase is off arm laying on guy wire between guy breakers//crew enroute to put phase back up//will have to open GOAB on 930-b-861 when they get here to make repairs/opened at 15:45//CLOSED 1610 L3/HFP
9584 | Paintsville | 3401103 | FALCON | BURNINGFK | 2008-09-30 06:20 | 2008-09-30 09:15 | 5 | 175 | 52106-1 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTNING ARRESTOR...876-272..IA XFMR TOOK OFF LINE...REFUSED LINE FUSE...30 T FUSE..BB//3401103//VER/CRB IDC XXXX
9585 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-07-06 17:44 | 2011-07-06 20:39 | 5 | 175 | 4478301 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 142-6 BAD 25KVA NEED 37.5 0R 50KVA TRUCK TO POLE RELEASED BY CREW 078S08/CREW ON SITE/FETR2115/VEM/REPAIRS MADE AND POWER RESTORED 2039 /PLEASE CLOSE TICKET/THANKS/VEM.//VER/CRB IDC XXXX
9586 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2010-03-22 08:30 | 2010-03-22 11:25 | 5 | 175 | 52594-1 | 875 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | STS WR # 34337522 3000102// STS NEED TWO CUTOUTS AND LA.. SEND TO VERNON M.. RELEASED BY CREW 078S08/CREW ON SITE/WILL OPEN XFMR BANK/APPROX 1 HOUR OUTAGE/VEM/OPEN XFMR BANK 1041/RESTORED AT 1125/PLEASE CLOSE TICKET/THANKS/VEM COD- 5 - 3 PHASE CUSTOMERS VER/HFP L3/HFP IDC XXXX
9587 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-02-17 15:07 | 2018-02-17 21:00 | 3 | 353 | 4855251 | 875 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Both hot legs burndt into on #4 cu open wire secondery going from pole 1128-51 to pole 52, will need a line crew to help put back up, both poles manual and both poles have to be worked, only 1 customer was out until I opened trans. on 1128-51 @1639 2 add. cust. Made repairs and closed trans. back in @2100./ ISO 38831128000051/ COD 3
9588 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-07-20 20:38 | 2019-07-21 11:12 | 1 | 874 | 4739521 | 874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Spoke with Nelson Scott/OK to hold for am. Gate will be closed but unlocked.WILL CHECK FOR PROBLEMS,HAS PARTIAL POWERWILL CHECK FOR PROBLEMS,HAS PARTIAL POWER////////SERVE-IN CONNECTION PULLED APART AT THE MAST////////MADE NECESSARY REPAIRS,ALL OK AFTERWARDS
9589 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-07-15 14:19 | 2017-07-15 15:05 | 29 | 46 | 4128291 | 874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 69-505 65T OUT BACK ON 14:45 POLE 69:573 BAD LA CHGED CUTOUT AND LA BACK ON 15:05 38830069A20505 VER/AWD MLR
9590 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2011-03-15 11:38 | 2011-03-15 12:24 | 19 | 46 | 54477-1 | 874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RELATED TO 54446-1//CREWS OPENED SWICTHES IN ORDER TO ISOLATE DOWNED WIRE//ISO 38821065D20287 // COD 19// VER/DBM IDC XXXX
9591 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2021-12-26 07:28 | 2021-12-26 14:45 | 2 | 437 | 4227251 | 874 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on 37830357C00187.manual
9592 | Paintsville | 3401101 | FALCON | FALC-OILS | 2019-06-17 10:24 | 2019-06-17 15:15 | 3 | 291 | 4523271 | 873 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | c phase fuse onpen @ 80-251 and C pf\hase fuse door burnt up @ 805-41. Gong to need SidexSide to patrol.Going to open B phase to patrol safely..BA ck to normal
9593 | Whitesburg | 3308402 | BECKHAM | CARR CREEK | 2009-02-27 06:17 | 2009-02-27 13:54 | 3 | 457 | 51958-1 | 873 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT, PATROLLING LINE, FOUND BAD CUTOUT ON POLE # 303-67. TOOK CLAMP OFF AND RESTORED ALL BUT 1 CUSTOMER AT 0945 HRS RELEASED BY CREW 077S02LINE FUSE OUT, PATROLLING LINE, FOUND BAD CUTOUT ON POLE # 303-67. TOOK CLAMP OFF AND RESTORED ALL BUT 1 CUSTOMER AT 0945 HRS LAST CUST BACK ON AT 13:54 IDCC CNT3 STEP TIME XXXX
9594 | South Williamson | 3202201 | LOVELY | LOVELY | 2009-06-11 11:46 | 2009-06-11 13:23 | 9 | 97 | 59200-1 | 873 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON POLE 746-168 IDC XXXX
9595 | Whitesburg | 3401301 | FLEMING | NEON | 2009-11-06 09:11 | 2009-11-06 11:00 | 8 | 109 | 65006-1 | 872 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP ONE SIDE OF SECONDARY BURNED INTO AT XFMR WILL HAVE TO OPEN XFMR TO MAKE REPAIRS, RESTORED OPENEDTRANSFORMER AT 1043 POWER AT 11:00 L3/HFP IDCC TOF1043 XXXX
9596 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2012-07-26 17:23 | 2012-07-26 19:12 | 8 | 109 | 4835701 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | 8T FUSE OUT. LOOKS LIKE FUSE BROKE OR MELTED OUT. I PUT 10 T FUSE BACK IN THIS IS 50KVA FUSED UP EVERYTHING OK. SEND COPY TO ENG FOR LOAD CHECK ON THIS TRANSFORMER. DKG/072612/1959 HRS/SENT EMAIL TO ENGR TO CHECK
9597 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-09-23 16:44 | 2018-09-23 20:22 | 4 | 218 | 4146171 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 190-120.repairs made..restored.. L3/HFP
9598 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-09-19 07:59 | 2019-09-19 15:15 | 2 | 436 | 4035311 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | l/f c/o is broken, could not get it to close, need l/c with big bucket to change c/o, at this loc, will need traffic control also Released by crew 078S06///repairs made///back on at 15:15///complete BR
9599 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2010-12-02 21:04 | 2010-12-03 00:42 | 4 | 218 | 62604-1 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STS WR # 37974945 // ONE LEG OPEN IN SECONDARY. R MAYNARD ENROUTE TO HELP LOCATE UG JUNCTION BOX AND CABLE.ONE LEG OPEN IN SECONDARY. R MAYNARD ENROUTE TO HELP LOCATE UG JUNCTION BOX AND CABLE. SPLICE IN JUNCTION BOX IS PROB BAD. CUSTOMER HAD ONE LEG COMING IN TO METER. TEMP CORRECTED WITH AUTO XFMR UNTIL WE CAN HAVE CABLE AND UG JUNCTION BOX LOCATED. ALL OK FOR NOW. R MAYNARD WILL REPAIR AT A LATER DATE. SH IDC DCMT XXXX
9600 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-03-13 22:08 | 2009-03-13 23:57 | 8 | 109 | 58325-1 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JOHN BLANKENSHIP REPORTS WHOLE HOLLOW OFF - HE WILL PATROL WHAT HE CAN //JOHN BLANKENSHIP REPORTS THAT HE FOUND NOTHING EXCEPT THAT CUTOUT DOOR IS BURNED OUT.WILL RE-FUSE .RE-FUSED,ALL OK AFTERWARDS COD-8 VER/LDA IDC XXXX
9601 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2016-07-25 22:52 | 2016-07-26 02:30 | 4 | 218 | 4679891 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUT-OUT BROKE ON POLE 53-50, THIS IS UP ON THE MOUNTAIN, TALKED WITH JOEY R., HE IS COMING TO HELP. CHANGED OUT CUT- OUT AND CLOSED BACK IN AT 0230.
9602 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-10-27 00:17 | 2010-10-27 02:06 | 8 | 109 | 65332-1 | 872 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACE BAD CO COMP MP RELEASED BY CREW 078H12 VER/ARN IDCC PN638 XXXX
9603 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2020-12-31 13:37 | 2020-12-31 17:15 | 4 | 218 | 4838821 | 872 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BOTTOM SEC WIRE(6A)HAS BURNED INTO,NEED 1 MAN,6A WIRE,SLEEVES/////////MASSEY ENROUTE TO HELP//////////MADE NECESSARY REPAIRS&RESTORED,ALL OK AFTERWARDS
9604 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-03-24 20:19 | 2011-03-25 10:50 | 1 | 871 | 59088-1 | 871 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | CALL MTR ELECTRICIAN IN THE AM ABOUT THIS//DWAYNE THACKER THIS IS A TIME OF DAY MTR PER JOHNNY SHEPHERD // REPLACED METER VER/HFP L3/HFP IDC XXXX
9605 | Paintsville | 3401103 | FALCON | BURNINGFK | 2011-11-09 10:57 | 2011-11-09 13:22 | 6 | 145 | 4061511 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 PHASE PRIMARY BURNED DOWN UNDER A HOT TAP 875-536..CREW ON THE WAY.. MD FILED 2 SETS OF 30T FUSES GOING IN BOTH DIRECTIONS FROM POLE#437 VER/KEP IDC XXXX
9606 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-07-21 20:37 | 2009-07-21 21:35 | 15 | 58 | 57384-1 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 30 FT. 1/0 SEC. BURNT DOWN FROM POLE 118-6505 TO 6594. CUT IN THE CLEAR. V. MULLINS IS BRING A NEW PEICE. RESTORED TRANSFORMER AT 21:35 V VER/TOM L3/TOM IDC XXXX
9607 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2009-01-16 10:05 | 2009-01-16 14:55 | 3 | 290 | 55830-1 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28094288 //NOT ON MAPS I CALLED TIM HALL HE WILL BRING TRANSFORMER CREW IS GOING TO STOP BY AFTER DOING ANOTHER JOB. RELEASED BY CREW 074S11 /// REPLACED WITH 25 KVA TRANSFORMER ONLY THREE CUSTOMERS OUT ISO POLE 37830140B00390 ENTERED MD - HFP L3/HFP
9608 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-02-22 10:10 | 2014-02-22 12:35 | 6 | 145 | 4425791 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHECKING/// BAD XFMR 15KV 7200, CAN REACH WITH BUCKET WITH SKILLFUL DRIVING/// XFMR CHANGED, POWER RESTORED. VER/KEP
9609 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-12-15 14:41 | 2015-12-15 16:08 | 10 | 87 | 4535251 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONDUCTOR PULLED OUT OF SLEEVE @ POLE 447-5 VER/CRB
9610 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-03-10 16:15 | 2021-03-10 23:30 | 2 | 435 | 4323911 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 500kva step down--crew req-ds031021 Released by crew 078S01 B Reynolds enroute to replace//cod 2
9611 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-10-16 19:30 | 2012-10-17 10:00 | 1 | 870 | 4147381 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | LINE FUSE BLOWN ON UNDERGROUND/// UNDERGROUND CABLE FAULTED. ARCOS A CREW AT 6:00AM. AN N.E., A-LINEMAN AND 2-BOTTOM MEN. STOREROOM ATTENDENT. RELEASED BY CREW 077S08. CHANGED WIRE, RESTORED POWER 10 A.M. VER/KEP IDC XXXX
9612 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2019-08-07 12:04 | 2019-08-07 16:54 | 3 | 290 | 4853451 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Basket burned off at pole 38830118C14177, No trucks to pole. Isolated and tagged to luke mccoy at 38830118C10021 Released by crew 078H04 crew on site FETR 17:45 going to change cutouts while on site 16:54 all pwr restored
9613 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-12-24 18:30 | 2008-12-25 01:45 | 2 | 435 | 63641-1 | 870 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401703// TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. CUTOUT IS BROKEN. DENNIS IS GOING TO GET SOMEONE IN BIG BUCKET TO COME AND CHANGE IT. RELEASED BY CREW 074S01 VER/ARN L3/KEP IDC XXXX
9614 | Hazard | 3302704 | HAZARD | KENMONT | 2011-08-12 12:26 | 2011-08-12 13:45 | 11 | 79 | 4699901 | 869 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOOK CUTOUT OFF LINE WILL REPLACE LATER == REFUSED LINE POWER OK//COD 11// VER/DBM IDC XXXX
9615 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2014-06-06 17:36 | 2014-06-06 21:13 | 4 | 217 | 4991271 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | POLE 1099-3573 BAD 50KVA TRANS TRUCK TO POLE RELEASED BY CREW 078S08 MULLINS & MORGAN & EVANS & HOWARD/LOOP OPEN ON B PHASE/FETR 2145/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2113/ONLY B PHASE OUT/PLEASE CLOSE TICKET/THANKS/VEM COD-4 39831099B43504
9616 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2012-12-29 19:08 | 2012-12-29 21:12 | 7 | 124 | 4553411 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT LEG IN A SPAN OF 1/0 SECONDARY IS BURNED INTO FROM LOAD. I AM GOING TO OPEN TRANS. ON POLE 1127-54 LONG ENOUGH TO SPLICE WIRE. I OPENED TRANS. AT 21:05 AND CLOSED IT AT 21:12. SEND TO ENG. DEPT. WE NEED TO CHANGE SPAN OF SEC. CONDUCTOR TO 4/0 OR HANG TRANS. AND SPLIT LOAD. CUSTOMERS SAID THIS HAS HAPPENED BEFORE. VER/ARN
9617 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-05-18 14:48 | 2010-05-18 16:52 | 7 | 124 | 64765-1 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR FUSES OUT ON 2 SEPERATE POLES, FOUND BAD HOT CLAMP ON POLE # 279-42, WILL NEED TO OPEN RECLOSER ON POLE # 279-250 LONG ENOUGH TO ISOLATE TAP, CALLING FOR 1 MAN TO HELP SEE 64815-1 FOR RECLOSER OUTAGE TO CLEAR UP THIS TROUBLE COD-7 VER/HFP L3/HFP IDC XXXX
9618 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2013-11-18 19:47 | 2013-11-19 10:15 | 1 | 868 | 4055131 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 420-53 , WILL HOLD FOR CREW TOMORROW,WILL NEED FLAGGERS , 25 KVA XFMR 7200, CUTOUT & BRACKET ,POLE GROUND. RELEASED BY CREW 077S11POWER RESTORED AT 10:15 VER/CRB IDC XXXX
9619 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-10-10 18:07 | 2015-10-10 20:11 | 7 | 124 | 4337321 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | REPLACE 15KVA WITHA 25KVA/ ISO 39831099B10140/ COD 7---CHANGED XFMR- CUTOUT AND ARR.VOLT CK 122-122-244---TBL TKT COMP/ VER/BOW L3/HFP XXXHFP
9620 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-06-04 19:53 | 2008-06-04 23:30 | 4 | 217 | 57143-1 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 199-120/240. COD-4 VER/KEP
9621 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-06-03 10:42 | 2010-06-03 14:19 | 4 | 217 | 55850-1 | 868 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 35399089 // BROKEN XFRMER CUTOUT.....CAN REPLACE WITH LINE CREWS MATERIAL HANDLER BUCKET.....CALLED CREW (JOEY REED) THEY WILL REPLACE BAD CUTOUT.....PLEASE SEND TICKET TO JOEYS CREW.....THANKS...JRV....06/03/10 RELEASED BY CREW 079H08 VER/HFP L3/HFP IDC XXXX
9622 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-12-12 08:01 | 2022-12-12 12:50 | 3 | 289 | 4250971 | 867 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Old style Cut-out door burned up on transformer pole. Will need to replace cut-out once Virgil Hurt arrives. Power restored @ 12:50
9623 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-07-17 09:11 | 2011-07-17 14:00 | 3 | 289 | 4555161 | 867 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | WE HAVE 3 STEPDOWN TRANSFORMERS AT POLE 1126-958. LOW SIDE FUSE IS OUT ON RIGHT HAND PHASE WITH BACK TO STATION. THE OTHER 2 ARE STILL IN. I AM PATROLLING LINE NOW. I CLOSED LOW SIDE TRANS. FUSE IN AT 14:00 AND IT STAYED.//VER/CRB IDC FOUND BAD INSULATOR LATER CHANGED CAUSE FROM UNKNOWN XXXX
9624 | Paintsville | 3409302 | KENWOOD | AUXIER | 2019-05-29 19:24 | 2019-05-30 09:51 | 1 | 867 | 4379981 | 867 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | nuetral broke in service drop to house.. made repairs..complete rn
9625 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2018-01-11 17:57 | 2018-01-11 18:48 | 17 | 51 | 4731581 | 867 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open on 38830045C45715 (fuse size: 50t ) due to broken cutout on pole 38830045C45565.cutout broken at pole 38830045C45565 which blew 50T line fuse on pole 38830045C45715 1848
9626 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-11-30 04:56 | 2009-11-30 09:45 | 3 | 289 | 50847-1 | 867 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3408103// WELL DISPATCH IN THE AM N, FUSE LINK BROKEN ... NO FAULT / ALL WORK COMPLETE / GXJ // VER/TOM L3/TOM IDC XXXX
9627 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2021-09-07 11:07 | 2021-09-07 14:00 | 5 | 173 | 4217041 | 865 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced bad cutout. power restored at 1400
9628 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2015-04-10 13:17 | 2015-04-10 15:05 | 8 | 108 | 4304651 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIREDNEED FLAGGING CREWTRUCK OK COPPER WIRE IS BROKEN AT HOT TAP ON POLE 38830045A10089 NEED NEW CUT-OUT AND ARRESTER RELEASED BY CREW 078H18RESTORED 1505// VER/ ADH
9629 | Hazard | 3311103 | STINNETT | WENDOVER | 2022-07-06 21:36 | 2022-07-07 12:00 | 1 | 864 | 4413671 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Clamp fell off stirrup on csp transformer. Power restored @ 12:00
9630 | Pikeville | 3408401 | KIMPER | LONGFORK | 2008-10-16 23:51 | 2008-10-17 01:03 | 12 | 72 | 56385-1 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK COMPLAINT OUTREPLACED BROKEN CUTOUT,,BACK ON AT 01:03AM VER/ARN IDCC TOF2309, CNT1, CDC92 XXXX
9631 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2008-12-09 06:58 | 2008-12-09 14:10 | 2 | 432 | 55601-1 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409401// BAD TRANSFORMER CREW ENROUTE.//DAVE LEWIS`S (LID 3145)CREW TO CHANGE OUT//COD 2// VER/DBM L3/KEP IDC XXXX
9632 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2016-05-20 09:19 | 2016-05-20 11:43 | 6 | 144 | 4238381 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT VER/AWD
9633 | Hazard | 3303901 | LESLIE | HYDEN | 2020-11-17 10:26 | 2020-11-17 12:50 | 6 | 144 | 4699631 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse
9634 | Hazard | 3303903 | LESLIE | HALSFORK | 2009-04-01 06:19 | 2009-04-01 09:55 | 4 | 216 | 63670-1 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 29181186 //CUTOUT FAILURE NEED BIG BUCKET 37830387C00246 COD-4 L3/HFP IDC XXXX
9635 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2012-12-23 05:48 | 2012-12-23 06:20 | 27 | 32 | H1176580-1 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4510191 DUP FOR TO RESTORE LOOPS SERVICER FOUND LOOP OPEN AT POLE 345-406 NEED 1 MAN & BIG BUCKET. @ 0548 SERVICER OPENED FUSE AT POLE 45-C-45. VER/PDP
9636 | Pikeville | 3409502 | BURDINE | LEVISA | 2010-03-17 10:17 | 2010-03-17 15:05 | 3 | 288 | 51007-1 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVE-END ON TRANS. POLE FROOZE OUT ON A HOT LEG. I RESPLICED WIRE. VER/KEP L3/KEP IDC XXXX
9637 | Whitesburg | 3309901 | SLEMP | DEFEATED CREEK | 2013-03-23 08:37 | 2013-03-23 13:25 | 3 | 288 | 4949751 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BUSTED ON POLE 517-14, WILL NEED 1 MAN AND BIG BUCKET TO HELP CHANGE. WILL HAVE TO OPEN RECLOSER AND STEP DOWN AT POLE 517-85 TO ISOLATE C/O. WILL KEEP TRACK OF TIMES.OPENED AT 12:40 CLOSED AT 13:25. ALL POWER RESTORED.//COD 3 (+2 SEE H4949751)// VER/DBM IDCC PN85 XXXX
9638 | Pikeville | 3421001 | BREAKS | CITY | 2020-10-02 08:48 | 2020-10-02 12:24 | 4 | 216 | 4519671 | 864 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | The tail feeding pole 220-C-620 came out,The cutout feeds 2 ways,Pole 220-A-733 feeds a funeral home,When funeral breaks will open switch and make repairs.. // opened fuse to make repairs open@ 1219 closed in @1224
9639 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2018-09-05 20:30 | 2018-09-06 10:53 | 1 | 863 | 4047111 | 863 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Called customer no reading on meter----bad 25 kva 7200 nbt unless its a big one--will also need fiberglass t-bracket and c/o--crew req--note cust would like a phone call before coming out driveway .wants to get vehicle out before it gets blocked in.thanks ds090618 Released by crew 078S01/crew on site/FETR 1130/vem/ On @ 1053
9640 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-08-23 20:28 | 2011-08-24 10:50 | 1 | 862 | 4749451 | 862 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA CSP 7200 XFORMER ON POLE 188-54, IN BARN LOT. NEED YARD DOG TO CHANGE OUT. CUST WILL WATE UNTIL TOMORROW. NEED LINE CREW. RELEASED BY CREW 078S01//COD 1//ISO 38830188D00054//ONLY SERVES CUSTOMER`S BARN AND DD LIGHTS, WILL HOLD FOR CREW UNTIL THE MORNING // VER/KEP IDC XXXX
9641 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2011-10-17 06:22 | 2011-10-17 08:25 | 7 | 123 | 4989581 | 861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 45-135 12T FUSE LINK BROKE VER/KEP IDC XXXX
9642 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-09-13 14:37 | 2011-09-13 16:40 | 7 | 123 | 4864941 | 861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 350-76 LINE FUSE OPEN DOOR BURNT UP FUSE BLOWN MORELAND STANDING BY AT FUSE TACKETT PATROLING LINE/NO CREW REQUIRED 20T LINE FUSE //VER/CRB IDCC FEC49 XXXX
9643 | Hazard | 3303902 | LESLIE | WOOTON | 2016-10-31 18:48 | 2016-10-31 23:35 | 3 | 287 | 4066421 | 861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H04 . LINE FUSE OUT ON POLE 462-38 .BAD CUTOUT ON POLE 462-38 . DID NOT HAVE A CUTOUT , SO PUT TAPS ON LINE WITH CLAMP FOR TONIGHT . SERVECER WILL NEED TO CHANGE CUTOUT TOMORROW . CUTOUT HAS 10T FUSE .POWER BACK ON @ 23:35 RELEASED BY CREW 075H04/ ISO 37830462000038/ COD 3/ VER/BOW
9644 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-06-16 00:39 | 2010-06-16 15:00 | 1 | 861 | 65898-1 | 861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HELD TO AM PER MASSEY 123 VOLTS NEED SOMEONE TO CLIMB POLE & CHECK A CONNECTION AT XRFM POLE BEHIND HOUSE RELEASED BY CREW 074M02 NEED LARGE BUCKET DUE TO POISON IVY GROWN ALL OVER THE POLE. RELEASED BY CREW 074S02
9645 | Whitesburg | 3401301 | FLEMING | NEON | 2020-10-28 10:28 | 2020-10-28 15:15 | 3 | 287 | 4591821 | 861 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I beleive this needs new xfmr leads, I talked to George Whitakerabout it please send him this ticket Released by crew 077S12 redone all secondary leads one connector burnt out problem should be fix
9646 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-01-29 17:52 | 2010-01-29 19:55 | 7 | 123 | 61246-1 | 861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | COD-7 FUSE BROKE RESTORED 1955 VER/KEP L3/KEP IDC XXXX
9647 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2018-06-01 09:13 | 2018-06-01 14:00 | 3 | 287 | 4538251 | 861 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | no crew required replaced fuse door COD-3 ISO TF 38830268D30277
9648 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-06-25 08:03 | 2012-06-25 10:55 | 5 | 172 | 4958771 | 860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 92-117 BAD 50 KVA 19.9 TRANS NEED 75KVA 19.9 TRUCK TO POLE CAUTION LINE FUSE OVER TRANS SEND TO JIM LINKOUS RELEASED BY CREW 078S08
9649 | South Williamson | 3411401 | DEWEY | INEZ | 2015-02-21 20:25 | 2015-02-22 10:45 | 1 | 860 | 4067571 | 860 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPOKE W/CUSTOMER OK TO HOLD UNTIL 2/22 AM CONNECTION HEATED UP AND BURNT SERVICE NEUTRAL AND HOT CONDUCTOR IN TWO AT XFMR POLE. REPLACED SERVICE AND RESTORED @ 10:45. SH/ ISO 38820697A00005/ COD 1/ VER/BOW
9650 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2022-05-27 05:31 | 2022-05-27 09:15 | 4 | 224 | 4958761 | 860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | .B phase line fuse blown on 197-94 will patrolHs.A phase line fuse blown on 197-94 will patrol//insulator angle pin has pulledd out and laid over on crossarm @ pole 197-41 and has blowed A phase line fuse///Switched xfm 197-40 over to C phase@ 09:15 and xfm 197-36 over to Cphase@ 08:57 this restored all customers off of A phase///Send copy to Steve Ray so he can send crew back to make
9651 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2015-01-01 07:55 | 2015-01-01 11:30 | 4 | 215 | 4896071 | 860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 38830091D00190 BAD 25KVA 19.9 NEED CURRECT LIMING FUSE TRUCK TO POLE RELEASED BY CREW 078S08//--CHANGED BAD 19.9 XTMR AND C.L. FUSE---VOLT CK GOOD---124-124-248---TBL TKT COMP @ 11:30---ONLY 1 CUST FEED FROM XFRM VER/CRB VER/DKG L3/DKGXXXX POWERON SHOWS 4 CUSTS ON THIS TRANSFORMER...CHANGED CUST COUNT FROM 1
9652 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2020-07-07 22:00 | 2020-07-08 12:20 | 1 | 860 | 4126921 | 860 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQD////////XFRF IS OUT,WILL RE-FUSE////FUSE BLEW,XFR MUST BE BAD.IT IS A 50,BUT ONLY FEEDS 1 CUST.CAN GO BACK WITH A 25.CHANGE CUTOUT TO POLY ALSO.THIS IS A WINCH JOB ALSO Released by crew 074S06// restored 1220
9653 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-08-11 22:36 | 2013-08-12 12:55 | 1 | 859 | 4651851 | 859 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL BE DISPATCHED AT REG WORK TIME ON 8/12/13 * PLEASE HAVE CUSTOMER CALL BACK IF ALL OUT. COULD BE DEVICE OPERATIONS AND BETTER TO CHECK AFTER DAYLIGHT HRS.WILL BE DISPATCHED AT REG WORK TIME ON 8/12/13 PLEASE HAVE CUSTOMER CALL BACK IF ALL OUT. COULD BE DEVICE OPERATIONS AND BETTER TO CHECK AFTER DAYLIGHT HRS. TALKED TO MARK JACKSON AT 10:23 AND HE IS SENDING ME SOME FLAGGERS OUT OF PIKEVILLE.// VER/DBM
9654 | Pikeville | 3402002 | KEYSER | STONECOAL | 2018-12-09 19:17 | 2018-12-10 09:35 | 1 | 858 | 4536761 | 858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | assessed, splice failed causing service to burn down, servicer required, truck accessible, replace #2 triplex service Released by crew 074E11, spliced out service, made repairs @0935, only 1 customer was effected. RESTORED @ 0935 L3/HFP
9655 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-03-09 21:12 | 2011-03-10 11:30 | 1 | 858 | 52598-1 | 858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, CAN WORK WITH BIG BUCKET, CUSTOMER DOES NOT LIVE AT THIS ADDARESS ( CAN WAIT TILL MORNING) VER/KEP IDC XXXX
9656 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2019-06-08 09:50 | 2019-06-08 12:13 | 6 | 143 | 4455871 | 858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew on site---found bad 19.9 cutout---in process of replacing---replaced cutout---pwr restored @ 12:13---tbl tkt comp---rmv
9657 | Hazard | 3308401 | BECKHAM | HINDMAN | 2015-03-04 08:22 | 2015-03-04 10:45 | 6 | 143 | 4097051 | 858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PATROLLING LINE, FOUND BAD CUTOUT ON POLE 378302060000103//B PHASE L/F OUT //COD 6// VER/CRB L3/DKGXXXX
9658 | Pikeville | 3403801 | SECONDFORK | DISTRIBUTION | 2017-04-10 21:02 | 2017-04-11 11:20 | 1 | 858 | 4635981 | 858 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFM. 7200 IN BANK ON POLE 79-121..WILL HOLD TO WORK IN THE A.M. TALKED TO WAREHOUSE ATTENDANT AND SAID THIS WOULD BE OK.THIS FEEDS APEX ENERGY OFFICE.MATERIAL WILL HAVE TO BE MOVED IN ORDER TO GET BIG BUCKET IN TO POLE TO MAKE REPAIRS.PLEASE SEND COPY TO TIM HALL.. RELEASED BY CREW 074S01 VER/CRB L3/HFP XXXHFP
9659 | Pikeville | 3407103 | TOPMOST | KITE | 2016-02-01 10:45 | 2016-02-01 13:08 | 6 | 143 | 4663601 | 858 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED REC ON POLE 37830209000200 TO REPAIR BURNT OFF HOT TAP 0N POLE 209-100 AT10:45//CLOSED BACK IN AT 13:08//ALL WORK COMPLETE RELEASED BY CREW 074H07 VER/CRB
9660 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-06-16 22:15 | 2020-06-17 12:32 | 1 | 857 | 4030661 | 857 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 kva 19.9 transformer and one barrell to put little clean up in can get material hander bucket to it Released by crew 077S05
9661 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-07-01 03:11 | 2008-07-01 06:45 | 4 | 214 | 60678-1 | 856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE, NEED CREW, 45 CLASS 4 POLE, 7200 CUTOUT, ARRESTER, TRAVIS BURTON AND CREW IN ROUTE, MAY BE ABLE TO LOWER EQUIPEMENT ON POLE AND NOT CHANGE OUT.POLE FIRE, NEED CREW, 45 CLASS 4 POLE, 7200 CUTOUT, ARRESTER, MIKE PHELPS AND CREW ON SITE, MAY BE ABLE TO LOWER EQUIPEMENT ON POLE AND NOT CHANGE OUT.POLE FIRE, NEED CREW, 45 CLASS 4 POLE, 7200 CUTOUT, ARRESTER, MIKE PHELPS AND CREW ON SITE, MAY BE ABLE TO LOWER EQUIPEMENT ON POLE AND NOT CHANGE OUT. VER/HFP IDC XXXX
9662 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-12-08 21:29 | 2012-12-09 11:45 | 1 | 856 | 4452741 | 856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THIS XFMR FUSE BLOWS WHEN IT RAINS. I HAVE TURNED IT IN TWICE TO BE CHANGED. I WILL TRY TO RE-FUSE IT AGAIN. 15KVA CSP XFMR WONT RESET. CREW ENROUTE TO CHANGE. WILL WORK IN DAYLIGHT PER CUSTOMER. TT TM ARCOS AT 0700 // MILLER, NEWSOME & MAYNARD ARCOSED // CREW ON SITE MANUAL POT TCM//COD 1// VER/DBM IDC XXXX
9663 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-07-23 17:28 | 2019-07-23 19:15 | 8 | 107 | 4783531 | 856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OUT ON 37830248A00914 /// LF 37830248A00122 OPEN closed @ 1915//lowered equipment L3/HFP
9664 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2020-04-03 18:09 | 2020-04-03 19:56 | 8 | 107 | 4558721 | 856 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | L/F is blown on 835-D-98// Xfmr riser on CSP had gotten against pole and was burning on 836-1. I pulled riser in the clear and restored power @ 19:56
9665 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-03-31 19:10 | 2009-03-31 19:25 | 57 | 15 | 63582-1 | 855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | ASSOCIATED WITH 63572-1 // THIS OUTAGED CUSTOMERS ON A/C PHASES TO REPAIR RISER ON CENTER PHASE- 57 COD// 3401103//..RISER BURNED INTO COMING OUT OF RECLOSER. B PHASE RECLOSER......ALL 3 REC. OFF AT 19.10...BACK ON AT 19.25...BB IDCC FPNULL, PN50 XXXX
9666 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2012-11-05 14:15 | 2012-11-05 17:06 | 5 | 171 | 4363571 | 855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK ///VER/CRB L/3 CRB IDC XXXX
9667 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-05-12 11:15 | 2016-05-12 12:50 | 9 | 95 | 4205881 | 855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | TIM REYNOLDS REPLACING SECONDARY FROM 206-2560 TO 206-2568/ 1115-1250/ ISO 38830206A42552/ COD 9/ VER/BOW
9668 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-11-18 07:51 | 2010-11-18 08:48 | 15 | 57 | 57760-1 | 855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLING LINE-BAD ARESTOR ON POLE 38830070A20651 HAS BEEN CUT IN CLEAR-NEEDS REPLACED -TRUCK OK--DIDNT FIND CAUSE//AED ENTRY CREATED//COD 15// VER/DBM IDC XXXX
9669 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-11-26 21:35 | 2014-11-27 02:20 | 3 | 285 | 4809141 | 855 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ARCOSED CREW OUT//TRANSFORMER POLE 38821139B00174 IS BURNED OFF AT THE CUTOUT. EQUIPMENT CAN BE LOWERED TO GET THE POWER BACK ON. NO TRUCK ACCESS TO THIS, YOU CANNOT GET UNDER THE RAILROAD BRIDGE WITH BUCKET TRUCK. THREE CUSTOMERS ARE OFF. POWER IS BACK ON BUT THE POLE NEEDS REPLACED AND RELOCATED//ISO 38821139B00037//COD 3//EMAILED TO C FREEMAN//
9670 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2017-06-17 14:59 | 2017-06-17 16:00 | 14 | 61 | 4988261 | 854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 4/0 RISER MELTED OFF POLE REPAIRED SEND NOTE TO TEC. 14 CUST ON TRANS TO MANY// RISERS MELTING OFF POT.//SENT TO TECH VER/CRB
9671 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-06-26 16:08 | 2008-06-26 23:15 | 2 | 427 | 54931-1 | 854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND BAD CUTOUT, CAN NOT GET TRUCK TO THIS, BEHIND THE HOUSE, WILL NEED CREW TO CHANGE THIS, RELEASED BY CREW 078S06 VER/HFP IDC XXXX
9672 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-02-28 22:43 | 2010-02-28 23:44 | 14 | 61 | 61764-1 | 854 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3008003// STS 34056699 BROKEN FUSE LINK IDC XXXX
9673 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-07-06 21:02 | 2014-07-07 11:15 | 1 | 853 | 4197611 | 853 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOLD TO DAYLIGHT COULD NOT FIND POLE AT NIGHT 1/0 SEC. BAD FROM 139-285 SEND TO ROB. RELEASED BY CREW 078S08 REPLACED SECONDARY CHECKED VOLTAGE AND REINSTALLED METER POWER RESTORED AT 1115 VER/CRB
9674 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2016-05-17 18:16 | 2016-05-17 23:00 | 3 | 284 | 4227661 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2 LINE FUSES OUT ON POLE 230A-172 , BAD CUTOUT ON POLE 230A-175 . POWER BACK ON @ 23:00/ ROW NEEDS CUT/ ISO 37830230A00172/ COD 3/ VER/BOW
9675 | Pikeville | 3402002 | KEYSER | STONECOAL | 2010-04-02 22:15 | 2010-04-03 05:21 | 2 | 426 | 57763-1 | 852 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | LINE SWITCH ON 1129-382 IS BROKEN,HAVE TO REPLACE IT.WILL ALSO REPLACE ALL 3 WHILE ON POLELINE SWITCH ON 1129-413 IS BROKEN,HAVE TO REPLACE IT.WILL ALSO REPLACE ALL 3 WHILE ON POLE///OFF AT 04:39 ON AT 05:21 //VER/GAH IDC XXXX
9676 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2009-07-20 08:36 | 2009-07-20 12:09 | 4 | 213 | 62900-1 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP HOT LEAD FELL OUT COD-4 ISO TF 37820073A00228 L3/HFP IDC XXXX
9677 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-08-20 15:46 | 2012-08-20 20:30 | 3 | 284 | 4955971 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN////BAD XFMR 50KV, 19.9, MANUAL XFMR, NEED 3-MAN CREW/// XFMR CHANGED OUT AND POWER RESTORED.. VER/KEP IDC XXXX
9678 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2017-07-31 08:49 | 2017-07-31 13:33 | 3 | 284 | 4209471 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 44-4026 BAD 25KVA CSP TRUCK TO POLE WILL NEED LINE CREW AND FLAGGERS SEND NOTE TO TEC POLE ROTTEN AT TOP NEEDS CHGED RELEASED BY CREW 078S08/CREW ON SITE/FETR 1400/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1333/PLEASE CLOSE TICKET/THANKS/VEM VER/AWD
9679 | Hazard | 3307301 | BULAN | ARY-HEINE | 2018-06-17 06:31 | 2018-06-17 11:15 | 3 | 284 | 4609591 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr, will need 25 kva , 7.2 kv, and cutout, bucket accessible
9680 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-11-10 07:39 | 2015-11-10 14:45 | 2 | 426 | 4423561 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200/120/124 CAN USE TRUCK RELEASED BY CREW 074S02//I AM ON SITE WAITING FOR THE CREW. REPLACED BAD TRANSFORMER AND RESTORED POWER AT 14:45 TIM MCCOY /// COD-2 ISO TF 37820001000223 VER/HFP L3/HFP
9681 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-05-22 10:35 | 2022-05-22 14:08 | 4 | 213 | 4925901 | 852 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer opened on pole 448-243. Power restored at 14:08.
9682 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-07-06 21:34 | 2018-07-07 11:45 | 1 | 851 | 4745601 | 851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | old load break type cutout gate is burnt up.manual.very close to primary conductor. Released by crew 077H18
9683 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-08-12 18:49 | 2010-08-13 09:00 | 1 | 851 | 53951-1 | 851 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36424461 // NEED 19.9 CUTOUT-BUCKET JOB-RIGHT BESIDE RD-FEEDS 1 SMALLHOUSE---ROOM TO PASS- ON RD --2 MEN OK----JIM RELEASED BY CREW 077S06 COD-1 VER/HFP L3/HFP
9684 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-08-20 15:45 | 2011-08-20 16:10 | 34 | 25 | 4733861 | 850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW HAD TO OPEN RECLOSER TO MAKE EMERGENCY REPAIRS TO A CROSSARM THAT WAS BURNT AND ABOUT TO BREAK // RELATED TO 4732311 VER/HFP L3/HFP IDC XXXX
9685 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-09-24 13:38 | 2014-09-24 13:48 | 85 | 10 | 4525481 | 850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CONDUCTOR MID SPAN AT 38820966C20411 IS BREAKING AND HAS A COUPLE STRANDS HOLDING IT TOGETHER 1338 1348// VER/BOW AJB
9686 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-12-17 15:00 | 2015-12-17 15:25 | 34 | 25 | 4539811 | 850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INSULATOR BREAKING DOWN WILL HAVE TO HAVE AN OUTAGE FROM STEP DOWN POLE 37830603000070///BAD DEAD END INSULATOR, CHANGE OUT//OPEN AT 15:00 AND CLOSE AT 15:25 COD-34 ISO LF @ 37830603000070 VER/HFP L3/HFP AJB
9687 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-09-25 20:02 | 2020-09-25 22:52 | 5 | 170 | 4496881 | 850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva. crew reqd. truck ok. Released by crew 078S04//arrived RM xfm replaced and power on @22:52 please close tic RM
9688 | South Williamson | 3200302 | BELFRY | TOLER | 2009-05-31 21:15 | 2009-06-01 11:25 | 1 | 850 | 55442-1 | 850 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP ON SITE, CHECKING TROUBLKE, BAD CSP XFORMER, BACK ON HILL, NOT TRUCK APPROACH RELEASED BY CREW 080S01 CUSTOMER INFORMED CREW WILL BE BACK ON 6/1/09 AT REG WORK TIME TO CHANGE OUT. MUDDY COND. BOB WILL TALK TO RANDALL MARCUM. **** ORG. ORDER CLOSED BY MISTAKE. THIS NEW ORDER CREATED. NOTE : PLEASE CK WITH OFFICE TO MAKE SURE. L3/HFP IDC SEE 55187-1 XXXX
9689 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2021-01-07 14:46 | 2021-01-07 16:11 | 10 | 85 | 4854781 | 850 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | hot leg burnt up. repairs made. pls close. tre
9690 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-11-19 06:17 | 2013-11-19 11:00 | 3 | 283 | 4056131 | 849 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 116-6040 BAD CUTOUT REPAIRED VER/CRB
9691 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2016-07-28 03:16 | 2016-07-28 17:25 | 1 | 849 | 4695921 | 849 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK IN THE AM 7-28-16. BAD TRANSFORMER AT POLE 266-212, THIS IS A 25KVA 19.9. THIS TAKES A CREW, AND MAY NEED TO BRING SOME MUD BOARDS WITH THEM TO MAKE IT TRUCK ACCESSIBLE. RELEASED BY CREW 074S05ALL RESTORED VER/AWD
9692 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-04-01 14:08 | 2009-04-01 17:40 | 4 | 212 | 63795-1 | 848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR # 29188431 //WR/29188431 NEED 50KVA 19.9 TRANS 19.9 CUTOUT LA. STANOFF BRECKETWR/29188431 NEED 50KVA 19.9 TRANS 19.9 CUTOUT LA. STANOFF BRECKET RELEASED BY CREW 078S08 // 4 COD VER/TOM L3/TOM IDCC MCCDIS XXXX
9693 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-07-13 10:53 | 2012-07-13 14:25 | 4 | 212 | 4709841 | 848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1123-6510 6T TRANS FUSE BROKE//COD 4
9694 | Pikeville | 3403001 | PIKEVILLE | CITY | 2018-02-14 07:29 | 2018-02-14 09:15 | 8 | 106 | 4839121 | 848 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | will replace service drop & restore power.replaced service drop & restored power
9695 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2014-05-21 21:39 | 2014-05-22 11:45 | 1 | 846 | 4731721 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP BREAKER APPEARS KICKED/// WILL CHECK/// BAD CSP XFMR, ALSO PRI. NEUT BROKE AT THE XFMR // NEED 15KVA// CUTOUT // L/A// CUTOUT BRACKET// NO TRUCK// BACK ON HILL /// 5 MEN RELEASED BY CREW 074S05 REPAIRS COMPLETE @ 11:45//COD 1// VER/DBM
9696 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-10-27 08:33 | 2015-10-27 10:54 | 6 | 141 | 4379271 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOING TO CHANGE CUTOUT AND ARRESTOR, I HAVE HAD THIS OUT THREE TIMES/ ISO 38831061D00179/ COD 6/ VER/BOW L3/DKG VERIFIED WITH VOICE RECORDER/TIME ON WAS NOT MENTIONED
9697 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-03-02 20:34 | 2008-03-03 10:40 | 1 | 846 | 52005-1 | 846 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308402// PAGED SERVICER// PP @ 2107 - CONTACTED CUSTOMER THEY REPORT OK TO WAIT UNTIL REG START TIME 3/2/08// VER/DBM IDC XXXX
9698 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-06-29 10:03 | 2008-06-29 14:45 | 3 | 282 | 59237-1 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT. VER/KEP IDC XXXX
9699 | Hazard | 3311101 | STINNETT | REDBIRD | 2021-11-22 09:51 | 2021-11-22 14:33 | 3 | 282 | 4114871 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Fuse broke. Power restored @ 14:33
9700 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-08-13 21:29 | 2010-08-13 23:50 | 6 | 141 | 54510-1 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3409301// FUSE MELTED OUT..REFUSED TRANSFORMER..BB
9701 | Paintsville | 3401102 | FALCON | SALYERSVI | 2015-06-21 18:48 | 2015-06-21 23:30 | 3 | 282 | 4633271 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR.NEED XFMR AND MATERIAL HANDLER.BACK ON AT 23.30//COD 3// VER/DBM
9702 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-09-11 06:40 | 2010-09-11 11:22 | 3 | 282 | 65393-1 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36838157 //CUTOUT BROKE INTO ON TRANSFORMER ALSO LINE FUSE. TRANSFER TO DALE HAMILTON RELEASED BY CREW 074S05//DIFFICULT LOCATION, WILL HAVE TO CLIMB POLE.//REPLACED CUT-OUT AND BRKT. COD-3 VER/HFP L3/HFP IDC XXXX
9703 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2022-10-30 19:23 | 2022-10-31 00:05 | 3 | 282 | 4079331 | 846 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | line fuse blown on 833-521 15 t 10 kva csp bad on pole 833-421. no truck access.back on at 00:05.
9704 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-12-10 18:45 | 2012-12-11 08:50 | 1 | 845 | 4458641 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT BAD BRIDGE NEED HELP TOMORROW--WILL CALL IN THE MORNING CUSTOMER IS OK WITH IT. RELEASED BY CREW 077S10 COD-1 ISO TF 37830148000056 VER/HFP L3/HFP
9705 | Paintsville | 3401103 | FALCON | BURNINGFK | 2018-11-26 10:15 | 2018-11-26 11:20 | 13 | 65 | 4478051 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO OUTAGE UNTIL LINE FUSE OPENED - COD 13 ISO 38830901000062
9706 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2015-04-07 12:26 | 2015-04-07 15:15 | 5 | 169 | 4284251 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POE37830401B00122 RELEASED BY CREW 077S11//MADE MDC//CUST COUNT IS CORRECT// REPLACED CUTOUT POWER RESTORED AT 15:15 VER/CRB
9707 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2017-09-05 14:35 | 2017-09-05 17:24 | 5 | 169 | 4331661 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 501-343///MAKING REPAIRS///REPAIRS MADE///CLOSED BACK IN AT 17:24///COMPLETE BR VER/AWD
9708 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2010-11-06 16:57 | 2010-11-06 19:46 | 5 | 169 | 53558-1 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MADE A MDC ON PREV ACCT//COD IS 5//BAD CUTOUT ON 468-68BAD CUTOUT ON 468-68, CUTOUT SERVES THREE TAPS WITH 5 CUSTOMERSBAD CUTOUT ON 468-68, CUTOUT SERVES THREE TAPS WITH 5 CUSTOMERS... REPLACED CUTOUT RESTORED POWER AT 19:46//VER/CRB IDC DCMT XXXX
9709 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2011-10-19 12:00 | 2011-10-19 13:05 | 13 | 65 | 4998031 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SW ORDER CREATED TO MODEL SWITCHING TO TRANSFER CUST FROM GRAYSON/LANSDOWNE TO HITCHINGS/E.K. RD 12KV **C/O BAD INSLATORS AT POLE 206-B-2394 *** HOLD ORDER ISSUED TO BRENT TACKETT. SW ORDER CREATED TO MODEL SWITCHING TO TRANSFER CUST FROM GRAYSON/LANSDOWNE TO HITCHINGS/E.K. RD 12KV C/O BAD INSLATORS AT POLE 206-B-2394 HOLD ORDER ISSUED TO BRENT TACKETT. CUSTOMERS INTERRUPTED AT 12:00 IDC XXXX
9710 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2020-03-07 15:16 | 2020-03-07 18:05 | 5 | 169 | 4459781 | 845 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | replaced hot leg connectins at xfmer and sec. xfmer off at 17:50 on 18:05
9711 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-03-13 13:25 | 2009-03-13 14:30 | 13 | 65 | 58190-1 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3402801// CSP TRANSFORMER BLEW DECIDED IT DIDNT NEED ITS LID SO IT BLEW IT OFF IN THE DRIVEWAY// CREW COMING TO CHANGE // RELEASED BY CREW 076H04 // WR# 28922052// COMPLETE TT.....//COD 13// VER/DBM IDC XXXX
9712 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-10-19 21:50 | 2009-10-19 22:55 | 13 | 65 | 59201-1 | 845 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO MAKE REPAIRS ON BROKEN CUTOUT ON ORDER 58781 VER/KEP L3/KEP IDC XXXX
9713 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-04-10 00:14 | 2012-04-10 14:18 | 1 | 844 | 4659431 | 844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION ON POLE BURNT-INTO, MADE REPAIRS ///VER/CRB IDC SWITCHING AND TAGGING MEETING XXXX
9714 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-06-15 15:49 | 2020-06-15 19:20 | 4 | 211 | 4023461 | 844 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 38831109000074 bad 15 kva 7200 Released by crew 077S05 power restored at 19:20
9715 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2009-07-01 20:35 | 2009-07-02 10:38 | 1 | 843 | 60240-1 | 843 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG-TALKED TO CUSTOMER AN RAYBURN--CREWS WILL WORK IN THE MORNING RELEASED BY CREW 078S07// INSTALLED POWER TEMP SEND ORDER TO DAN HUFF SO IKE CAN MAKE REPAIRS FIRST OF WEEK VER/KEP L3/KEP IDC XXXX
9716 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-02-27 05:29 | 2021-02-27 10:10 | 3 | 281 | 4259851 | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout at 230-278. power restored 10:10
9717 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2020-07-09 20:28 | 2020-07-09 23:50 | 5 | 202 | 4137641 | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38820966A10612//COD 4//OPENED L/ F 38820966A19001 @ 2315 THIS OUTED 1 MORE CUSTOMER opened 2315-2350
9718 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2010-12-12 15:44 | 2010-12-12 20:25 | 3 | 281 | H65613-1A | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38077747 // POLE FIRE AT 38830182B43779, ISOLATED AT 38830182B43567 COD-26, SHOULD BE ABLE TO LOWER EQUIPMENT, CREW ENROUTE RELEASED BY CREW 078S05 DUPLICATE FOR 3 CUST ON POLE 38830182B43779 @ 1544 WHEN HOT TAP LIFTED... ISO LF 38830182B43779 COD-23 SEE 65613-1 VER/HFP L3/HFP IDC XXXX
9719 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-06-27 05:44 | 2015-06-27 10:25 | 3 | 281 | 4672371 | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BAD // REPLACING // POWER RESTORED @ 10:25 // TREE IS LAYING VERY HEAVY ON SPAN OF SEC. FROM POLE 38831126B10462 TO 38831126B10038 NEEDS CUT SOON BEFORE IT BREAKS SEC. // SEND TO C. FARMER/ ISO 38831126B10038/ COD 3/ VER/BOW
9720 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-06-12 20:44 | 2012-06-13 01:25 | 3 | 281 | 4908541 | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3 MAN CREW - GREG SHOUSE, TIM SMITH & JEFF COMBS // DONNA HURT FOR STORES // //VER/GAH IDC FEC57 XXXX
9721 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-06-18 22:07 | 2009-06-19 12:10 | 1 | 843 | 66640-1 | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP TREES ALL OVER POLE. NEED TO REFUSE TTRANSFORMER COVERED IN TREES. SEC POLES IN TREES. VIRGIL COMING BEHIND ME TO FIX.CREWS IN ROUTE. VIRGIL WILL PROVIDE. FETR. LAM RELEASED BY CREW 077E05 L3/HFP IDC XXXX
9722 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-09-29 23:19 | 2022-09-30 13:22 | 1 | 843 | 4939631 | 843 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout 37830508000037/ customer has generator and ok with waiting until morning. Replaced broken cutout and power restored @ 13:22
9723 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2016-02-04 02:53 | 2016-02-04 09:54 | 2 | 421 | 4674091 | 842 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK IN THE AM 2/4/16. HOT LINE CLAMP BURNED INTO, I REPLACED IT VER/TOM L3/TOM
9724 | Hazard | 3308401 | BECKHAM | HINDMAN | 2020-05-25 00:58 | 2020-05-25 15:00 | 1 | 842 | 4901551 | 842 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 10kva xfer/ narrow road and bridge no truck, all power restored @ 15:00 hrs p.hicks
9725 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-10-08 23:13 | 2017-10-09 13:15 | 1 | 842 | 4426101 | 842 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SCADA INDICATED THE JC-META OPERATED @ 2300 // DEAD END INSULATOR ON 1082-188 IS BAD,NEEDS REPLACED.NEED BUCKET,EPOXILATOR INSULATOR.TIM HALL SENDING CREW SHORTLY VER/HFP L3/HFP
9726 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-01-28 02:34 | 2016-01-28 09:35 | 2 | 421 | 4655331 | 842 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ATTEMPTED TO CONTACT CUSTOMER, NO RESPONSE, NO ANSWERING MACHINE// THE CURRENT LIMITING FUSE IS BURNED UP. I SPOKE WITH THE CUSTOMER WHO WILL MOVE A TRUCK SO THAT WE CAN GET A BIG BUCKET TO CHANGE THE CURRENT LIMITER. HE IS OK WITH WAITING UNTIL REGULAR STARTING TIME. RELEASED BY CREW 074S02 RELEASED BY CREW 074H21/// CHANGED BAD CURRENT LIMITER FUSE/// RESTORED SERVI CE @09:35/// ONY 1 CUSTOMER AFFECTED//SEND COPY TO MIKE HATFIELD POLE #239-199 IS BROKE UP AROUND XFM. VER/AWD
9727 | Pikeville | 3408103 | SALISBURY | MARTIN | 2016-06-28 00:39 | 2016-06-28 14:40 | 1 | 841 | 4491241 | 841 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 25T FUSE ON UNDERGROUND TO PAD MOUNT TRANSFORMER 1098-591 TRIED TO FUSE UP 1 TIME FUSE BLOWED. CREW REQUIRED RELEASED BY CREW 074S11/ DOING TESTS NOW TCM/ BAD 112.5 KVA BEING SHIPPED FROM ASHLAND/ METERING DEPT IN ROUTE VER/AWD
9728 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2009-12-10 03:25 | 2009-12-10 03:40 | 56 | 15 | 54844-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CAPACITOR | OPENED RECLOSER AT 0325 TO ISOLATE POLE FIRE CLOSED AT 0545 VER/KEP L3/KEP IDC XXXX
9729 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-10-06 04:13 | 2022-10-06 06:13 | 7 | 120 | 4981111 | 840 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Burnt up squeeze on at transformer. Made repairs.
9730 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-10-19 17:28 | 2018-10-19 19:48 | 6 | 140 | 4270991 | 840 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral and one hot leg burned into ,I repaired it
9731 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-03-15 23:05 | 2008-03-15 23:40 | 24 | 35 | 57577-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3308602// BAD INSULATORTOOK POWER OFF AT 2305 PUT IT BACK ON AT2340 VER/JHM IDCC TOF2122 XXXX
9732 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2016-03-02 15:03 | 2016-03-02 15:18 | 56 | 15 | 4803681 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | OPENED 500 KVA STEPDOWN IN ORDER TO CHANGE BAD CUTOUT AND BLOWN ARRESTER AT 15:03 RESTORED POWER AT 15:18 ALL POWER RESTORED PLEASE CLOSE TICKET THANKS DWW// VER/ ADH AJB
9733 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-04-08 14:23 | 2013-04-08 16:23 | 7 | 120 | 4988581 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | CUT TWO ARRESTERS IN THE CLEAR POLE 502-33 AND 502-130 PLEASE ADD TO ABNORMAL DATABASE. NO TRUCKS TO POLES. APR AT 1623 CLOSE TICKET DWEST//COD 7//AED ENTRY CREATED// VER/DBM IDC XXXX
9734 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-02-01 15:37 | 2013-02-01 18:25 | 5 | 168 | 4783111 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GOT BAD CUTOUT ON TRANSFORMER, GOT VIRGIL HURT COMMING TO HELP TO CHANGE OUT//COD 5// VER/DBM IDC XXXX
9735 | Paintsville | 3409302 | KENWOOD | AUXIER | 2017-03-15 02:45 | 2017-03-15 06:15 | 4 | 210 | 4557931 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #6A PRIMARY DOWN ON 905-62. OPENED REC 905-7 @ 4:03. 4CC OUT TO START 4 MORE AT 0403/#6A PRIMARY DOWN ON 905-62. OPENED REC 905-7 @ 4:03. MADE REPAIRS AND CLOSED REC @ 6:15. SH RELEASED BY CREW 076S02 VER/KEP
9736 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-07-25 10:15 | 2008-07-25 11:25 | 12 | 70 | 60095-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3402001//BLOWN ARRESTER, WILL CHANGE DEFECTIVE CUT-OUT & ARRESTER. ALSO WILL TRIM SOME TREES AROUND POLE. THEN WILL TRY TO REFUSE X-FMR.//COD 12// VER/DBM IDCC CDC92 XXXX
9737 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-02-15 06:45 | 2012-02-15 10:15 | 4 | 210 | 4349181 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT, BAD XFMR, WILL NEED CREW WITH BIG BUCKET, CAN WORK POLE WITH TRUCK, NO FLAGGERS NEEDED. 50 KVA, 19.9 VOLTAGE RELEASED BY CREW 077S02/// XFMR CHANGED, POWER RESTORED ///VER/CRB IDC XXXX
9738 | Hazard | 3309302 | VICCO | JEFF | 2022-11-07 16:05 | 2022-11-07 16:15 | 84 | 10 | 4108191 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | B PHASE OFF INSULATOR LAYING ON ARM ON POLE 37830323B00011 //// PHASES STILL HOT /// STEPDOWN STILL CLOSED ON POLE 323-D-542 /// NEED LINE CREW Released by crew 077H12//OPENED STEPDOWN @ 1605 OK@1615
9739 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-08-18 09:56 | 2009-08-18 11:20 | 10 | 84 | 63987-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE. R MAYNARD ENROUTE TO ASSIST. CUTOUT CHANGED. RESTORED AT 11:20. SH VER/KEP L3/KEP IDC XXXX
9740 | Hazard | 3309302 | VICCO | JEFF | 2017-02-23 12:27 | 2017-02-23 14:47 | 6 | 140 | 4416471 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REPLACING TRANSFORMER AND DOING WORK AT DIFFICULT LOCATION 37830346C00411/6 TFO ON 37830346C00470 1227-1447. VER/AWD L3/HFP XXXHFP
9741 | Cannonsburg | 3001401 | LOUISA | CITY | 2010-08-18 20:50 | 2010-08-19 03:50 | 2 | 420 | 57898-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT TRACKING ON GREEN POLE, BURNT 3/4 WAY THROUGH; POLE 454/3117--DEAD END SINGLE PHASE; ISOLATED AND GROUNDED AT POLE 454/1544; CREW REQUIRED; TRUCK ACCESSABLE; POLE IS 40 CLASS 6 BUT MIGHT BE ABLE TO EXTEND POLE; NEED CUTOUT AND BRACKET; RELEASE TO LINE CREW RELEASED BY CREW 078S12------POWER ON @ 03:50 //VER/GAH IDCC CNT13, TOF 2004 XXXX
9742 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2010-01-17 08:12 | 2010-01-17 11:00 | 5 | 168 | 55277-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | NO CREW REQUIRED/REPLACED BAD INSULATOR AND TIE WIRE/LINE FUSE 251-143 VER/TOM IDCC XXXX
9743 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2016-09-28 20:27 | 2016-09-28 23:15 | 5 | 168 | 4939431 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT HAD BROKE. COD-5 ISO TF 38820967A00110 VER/HFP L3/HFP
9744 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-07-13 08:42 | 2009-07-13 11:30 | 5 | 168 | 65500-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT VER/TOM L3/TOM IDC XXXX
9745 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2010-08-11 17:10 | 2010-08-11 17:30 | 42 | 20 | 52627-1 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | FOUND PRI LOOP ARCHING ON POLE 1072-7024, HAD TO OPEN UP LINE ON 1072-5523, HAVE REPAIRS MADED AND ALL CUST ARE BACK ON AT THIS LOC OPENED FUSE TO MAKE REPAIRS AT 1710 CLOSED AT 1730 VER/KEP L3/KEP IDC XXXX
9746 | Cannonsburg | 3001401 | LOUISA | CITY | 2017-04-19 10:50 | 2017-04-19 11:50 | 14 | 60 | 4656341 | 840 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | PLEASE DO MD THEY ARE A LINE FUSE ON 38830454A41655 PROTECTING TAP. CREW REQUIRED NEED TO BRING 4 12KV CUTOUTS.///MADE MDC//PLEASE DO MD THEY ARE A LINE FUSE ON 38830454A41655 PROTECTING TAP. CREW REQUIRED NEED TO BRING 4 12KV CUTOUTS. RELEASED BY CREW 078S11, MD LINE FUSE POLE454-655 15T OPENED XFMR BANK AND LINE FUSE AT 10:50 ,XFMR BANK RESTORED11:27 LINE FUSE AT 11:50 //ACCORDING TO DHE CREW NO OUTAGE TILL L/F OPENED L/F CUTOUT WAS TRKING VER/CRB L3/HFP XXXHFP
9747 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2012-11-19 01:56 | 2012-11-19 08:55 | 2 | 419 | 4407261 | 838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM// FOUND BAD CUTOUT CHANGING NOW TCM// REPLACE DOOR BACK ON 0855 TCM// CC 2 VER/SDB IDC XXXX
9748 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2009-06-12 21:47 | 2009-06-13 11:45 | 1 | 838 | 59280-1 | 838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 3301402//SERVICER TALKED TO CUST//WILL WORK TOMORROW//NEUTRAL OPEN IN UG SECONDARY TO PEDESTAL//INSTALLED TEMP. NEUTRAL SENDING IW TO TECH FOR A WORK ORDER TO REPLACE UG SERVICE VER/KEP L3/KEP
9749 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-07-15 07:39 | 2014-07-15 14:38 | 2 | 419 | 4247061 | 838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CREW ENROUTE RELEASED BY CREW 074S02.OPENED FUSE ON POLE 170-139 AT 14:14 AND CLOSED AT 14:38..SERVICE RESTORED.//COD 2 (+ 1 SEE H4247061)// VER/DBM
9750 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2008-05-28 07:36 | 2008-05-28 14:35 | 2 | 419 | 52038-1 | 838 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 140-4005 CUTOUT FELL APART NO TRUCK POLE COVERED IN VINES RELEASED BY CREW 078S08//3008701 CREW ON SITE J HEMLEPP//VER/CRB IDC XXXX
9751 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-04-23 10:32 | 2010-04-23 12:05 | 9 | 93 | 66618-1 | 837 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34806973 // --- LINE FUSE OUT ON POLE 293-30 -- PATROLING LINE NOW--- OUTAGE TIME FOR STEPDOWN 11:50 TILL 12:05 SEE 66641-1 VER/HFP L3/HFP IDC XXXX
9752 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-09-11 09:06 | 2014-09-11 13:45 | 3 | 279 | 4488321 | 837 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 7200 CUTOUT AND TEE BRKT . POLE BEHIND TAN DOUBLEWIDE ON SIDE ON HILL CALL JIM MULLINS AND HE IS GOING TO SEND CREW TO CHANE OUT RELEASED BY CREW 077S05// ISO 37830220000014/// COD 3// VER/BOW
9753 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2013-08-07 02:47 | 2013-08-07 09:45 | 2 | 418 | 4630631 | 836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | /////////RE-FUSED AND RESTORED//////HAD TO CUT IN CLEAR A SPAN OF 4/2 DD CABLE THAT HAD SHORTED OUT,INSULATION FAILURE.WILL CREATE A JOB AND REPLACE IT VER/SEF L3/HFP
9754 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-03-24 07:57 | 2011-03-24 14:55 | 2 | 418 | 58541-1 | 836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | TRANSFORMER FUSE BLOWN--BAD LIGHTENING ARRESTOR, NEED PADS AND BIG BUCKET, DUTY SUPERVISOR NOTIFIED. RELEASED BY CREW 077S04//COD 2// VER/DBM IDC CREW WAS ON REST XXXX
9755 | Whitesburg | 3409503 | BURDINE | JENKINS | 2008-01-30 13:27 | 2008-01-30 20:25 | 2 | 418 | 62333-1 | 836 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD CONNECTIONS ON TRANSFORMER POLE OPENED TRANSFORMER AT 2000/CLOSED @ 2025//ISO//COD 2// VER/DBM IDC XXXX
9756 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2012-08-14 21:55 | 2012-08-15 11:51 | 1 | 836 | 4937861 | 836 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA XFMR ON POLE 355-42 EXPLODED ON POLE LID HANGING AND RING ON GROUND.. CAUSE UNKNOWN.. CREW REQUIRED NO TRUCKS.. NEED YARD DOG OR TRACK BUCKET AND OIL SPILL BAG FOR XFMR.. OPENED LINE FUSE 356-27 23:27 BACK ON AT 23:45. CUST SAID OK TO LEAVE OFF UNTIL MORNING.. SEND TO RAYBURN RELEASED BY CREW 078H2215 KVA XFMR ON POLE 355-42 EXPLODED ON POLE LID HANGING AND RING ON GROUND.. CAUSE UNKNOWN.. CREW REQUIRED NO TRUCKS.. NEED YARD DOG OR TRACK BUCKET AND OIL SPILL BAG FOR XFMR.. OPENED LINE FU IDC XXXX
9757 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2010-01-04 12:33 | 2010-01-04 15:20 | 5 | 167 | 59983-1 | 835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD ON POLE 357-59 WILL NEED CREW AND A 50 KVA 7200 TRANSFORMER REPLACED TRANSFORMER//COD 5// VER/DBM IDC XXXX
9758 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2016-08-31 13:18 | 2016-08-31 16:05 | 5 | 167 | 4856141 | 835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE38830138D00139, BAD 7200-120/240 50KVA. TRK OK.. LYING LEES CAR SALES RELEASED BY CREW 078S07,REPLACED XFMR ALL CUST RESTORED @ 1605 PLEASE CLOSE TICKET THANKS.BT VER/CRB
9759 | Pikeville | 3409502 | BURDINE | LEVISA | 2013-06-12 09:10 | 2013-06-12 14:35 | 7 | 325 | 4262471 | 835 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WE HAVE A TRANS FUSE BLOWN ON POLE 359-35 AND A LINE FUSE OUT ON 359-7. I AM GOING TO CLOSE LINE FUSE IN FIRST AND THEN TRY TRANS. FUSE. I CLOSED LINE FUSE IN AT 10:35 AND IT STAYED. I AM GOING TO CLOSE TRANS. FUSE IN NOW. BAD TRANSFORMER. I HAVE CALLED FOR HELP. WE JUST HAVE 1 CUSTOMER OUT NOW. MD FILED. WE ARE CHANGING TRANS. NOW. WE CHANGED TRANS. AND CLOSED TRANS. FUSE AT 14:35 VER/KEP IDC XXXX
9760 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2012-05-21 11:38 | 2012-05-21 18:35 | 2 | 417 | 4813181 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 20-5638 BAD 50KVA TRUCK OK HOLD FOR BOB R. RELEASED BY CREW 078S08// EVENING SHIFT STARTS @ 1500//LMR..CHANGED OUT TRANSFORMER, ALSO CHANGED THE LINE FUSE CUTOUT TWO POLES AWAY..BLR IDCC PN5640 XXXX
9761 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-07-21 15:35 | 2010-07-21 17:54 | 6 | 139 | 55174-1 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE OUT, CUTOUT BROKE, TIME OFF 16:20//VER/CRB IDCC CDC83 CNT34, TOF1620 XXXX
9762 | Hazard | 3308401 | BECKHAM | HINDMAN | 2018-04-21 21:38 | 2018-04-21 23:57 | 6 | 139 | 4261831 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | //phase B only//cod 6//Looks like fuse broke// power ok//cod 6
9763 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2014-05-02 07:10 | 2014-05-02 14:07 | 2 | 417 | 4656691 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078S07 POLE 1124-3518 BAD 10KVA NEED 25KVA TRUCK TO POLE NEED FLAGGERS RELEASED BY CREW 078S08/CREW ON SITE/FETR1430/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1407/PLEASE CLOSE TICKET/THANKS/VEM // VER/TOM L3/TOM
9764 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-08-27 23:22 | 2008-08-28 04:00 | 3 | 278 | 56691-1 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3 HOMES ON A 25 KVA TRANSFORMER OUT, OIL ON THE BUSHING. RELEASED BY CREW 074S08 VER/LDA IDC XXXX
9765 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2008-06-28 22:06 | 2008-06-29 12:00 | 1 | 834 | 58651-1 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ,FIXING IT NOW /// REPLACED CUTOUT VER/KEP IDC XXXX
9766 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2014-06-21 09:48 | 2014-06-21 16:45 | 2 | 417 | 4133981 | 834 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S01 TRANSFORMER CUTOUT SERVING BANK OF TRANS. HAS FAILED. ERIC MCKINNEY IS BRINGING ME ONE TO CHANGE IT OUT. WE CHANGED CUTOUT. VER/CRB
9767 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2016-03-14 17:56 | 2016-03-14 20:15 | 6 | 139 | 4846251 | 834 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12KV C/O, CREW REQD. TRK OK RELEASED BY CREW 078S07.OPENED THE OTHER TWO FUSES ON POLE 38830044D37030 AT 19:30,, CHANGED ALLL THREE CUTOUTS, ALL POWER RESTORED AT 20:15.BLR/ ISO 38830044D37030/ COD 6/ VER/BOW
9768 | Hazard | 3303903 | LESLIE | HALSFORK | 2019-01-05 15:45 | 2019-01-05 16:34 | 17 | 49 | 4633771 | 833 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACING NEUTRAL WIRE AND CUTOUTS//replaced c/o and net//OPENED @ 1545 CLOSED @ 1634
9769 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-01-09 09:34 | 2011-01-09 16:30 | 2 | 416 | 60089-1 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER//VER/CRB IDC XXXX
9770 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2012-10-08 15:26 | 2012-10-08 17:10 | 8 | 104 | 4124051 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PER BRYANT LEWIS POLE 37830211B00038 HAS PRIMARY OFF THE PIN AT THE MOUTH OF THE RIGHT FORK OF FROZEN FORK ON JACKS CREEK 25T FUSE OUT DUE TO TIE WIRE BREAKING LETTING CONDUCTOR FALL DOWN ON CROSS ARM COD-8 ISO LF 37830211B00002 VER/HFP L3/HFP IDC XXXX
9771 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2010-06-25 06:17 | 2010-06-25 09:45 | 4 | 208 | 57232-1 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT CHANGED CUTOUT AND ARRESTER AND T BRACKET == REFUSED POWER OK VER/KEP L3/KEP IDC XXXX
9772 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2021-03-25 20:18 | 2021-03-25 23:46 | 4 | 208 | 4375611 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | L/F blown on 904-15 will patrol// Primary between 904-22 & 904-23 is sagged down below tv and telephone line. Possibly happened during ice storm. I have called for 1 man to help sag wire. No truc access/// Repaired conductor and restored @ 23:46
9773 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-05-15 11:47 | 2009-05-15 15:15 | 4 | 208 | 56780-1 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WE HAVE THE CENTER PHASE LOOP OPEN ON POLE#38831123B00004 . I HAVE CALLED FOR COVER UP & WILL REPAIR LOOP. G.R.//COD 4//WE HAVE THE CENTER PHASE LOOP OPEN ON POLE#38831123B00004 . I HAVE CALLED FOR COVER UP & WILL REPAIR LOOP. G.R. THIS ONLY HAS 4COUSTOMERS OUT/VER/CRB
9774 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-07-04 10:52 | 2016-07-04 11:44 | 16 | 52 | 4521771 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ***SEE 4519531***OPENED @ 1052 TO CHANGE BAD TRANSFORMER ON POLE 37830488000007/ CLOSED @ 1144/ VER/BOW
9775 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-02-02 19:37 | 2011-02-03 02:33 | 2 | 416 | 53656-1 | 832 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 38672732 // NEED 1 MAN , MATERIAL HANDLER AND 25 KVA 7200 XFMR. REPLACED XFMR. VER/ARN IDC XXXX
9776 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2017-06-19 11:20 | 2017-06-19 15:57 | 3 | 277 | 4998831 | 831 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ***SEE 4000921*** HAVE A BAD 25KV TRANSFORMER, CREW IN ROUTE./ ISO 38830737000007/ COD 3/. RESOTRED 1557/ VER/BOW
9777 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-01-27 05:17 | 2012-01-27 09:54 | 3 | 277 | 4297331 | 831 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL HAVE SERVICER CHECK AT REGULAR WORKTIME AS PER PRESET GUIDELINESXFR FUSE IS OUT,WILL RE-FUSE//CUTOUT IS BROKEN,WILL REPLACE//REPLACED CUTOUT AND RESTORED// COD 3// VER/DBM IDC XXXX
9778 | Hazard | 3308502 | BONNYMAN | HAZARD | 2014-08-12 09:28 | 2014-08-12 14:05 | 3 | 277 | 4359501 | 831 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN// WORKING ON GETTING1 MAN, TRANSFORMER, & MATERIAL// TRANSFORMER FUSE BLOWN,.. BAD 25 KVA 19.9 TRANSFORMER, CAN USE MATERIAL HANDLER.TRANSFORMER FUSE BLOWN,.. BAD 25 KVA 19.9 TRANSFORMER, CAN USE MATERIAL HANDLER. RELEASED BY CREW 077S04 /// COD-3 ISO TF 37830247C01151 VER/HFP L3/HFP
9779 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2018-04-23 14:01 | 2018-04-23 15:52 | 34 | 111 | 4266681 | 830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 125-42..will patrol.line fuse cutout broken on pole 125-42..will have to open rec. on pole 125-40 to make repairs...opened rec. @ 15:33 closed back in @ 15:52...
9780 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2021-08-21 11:27 | 2021-08-21 18:22 | 2 | 415 | 4132281 | 830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15 kva 7200 XFM, need a line crew to make repairs // restored @1822
9781 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-04-14 17:58 | 2012-04-14 19:21 | 10 | 83 | 4673361 | 830 | PARTIAL POWER | EQUIPMENT FAILURE | ARRESTER | XFR FUSE OUT AT 24-482,LOOKS LIKE LA HAS BLOWN AND TAKEN FUSE OUT,WILL RE-FUSE////////RE-FUSED AND RESTORED ///VER/CRB IDC XXXX
9782 | South Williamson | 3411401 | DEWEY | INEZ | 2021-07-09 07:29 | 2021-07-09 10:15 | 5 | 166 | 4876911 | 830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole744-13///cutout broke on 768-176//making repairs//cutout replaced//restored @ 10:15//complete//em
9783 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-04-01 02:05 | 2016-04-01 09:00 | 2 | 415 | 4013361 | 830 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 166-73.REPLACED AND CLOSED BACK IN @ 09:00.. VER/CRB
9784 | Hazard | 3308001 | JACKSON | S.JACKSON | 2010-10-30 08:27 | 2010-10-30 10:45 | 6 | 138 | 50173-1 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER LEAD BURNT ON POLE # 1108A-403---POWER RESTORED // COD7 VER/HFP L3/HFP IDCC PN401, CNT7 XXXX
9785 | Hazard | 3310502 | HADDIX | CANOE | 2015-04-30 12:04 | 2015-04-30 14:22 | 6 | 138 | 4378361 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKEN, REPLACED XFMR C/O, POWER RESTORED/ ISO 37830169C00066/ COD 6/ VER/BOW L3/HFP XXX
9786 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-02-05 21:42 | 2014-02-06 11:30 | 1 | 828 | 4360941 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HELD PER BRUCE LINDON TIL AM//PER ROAD CONDITIONS // 0840 SERVIER REPORTED BAD TRANSFORMER - CONTRACTOR BRINGING TRANSFORMER//BAD 25KVA 7.2 120/240 VER/TOM L3/TOM
9787 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-07-20 16:16 | 2012-07-20 17:25 | 12 | 69 | 4787281 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | A PHASE FUSE BLOWN ON POLE 37830023000310 DID NOT SEE ANYTHING WRONG CLOSED FUSE @ 17:25 & POWER RESTORED GOING TO RUN LEAD EQUIPMENT AND SNIFFER TO FIND EQUIPMENT THAT IS BLOWING FUSES PIN INSULATOR CRACKED ON POLE 37830047C00532 COD-12 ISO LF 37830023000310 VER/HFP L3/HFP
9788 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-07-19 11:04 | 2021-07-19 15:40 | 3 | 276 | 4934551 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | We need to replace a leaking 15KVA CSP XFMR at 1331 Couchtown RD. Need a line crew with flaggers, 15KVA and a 12KV cutout. The pole numbers are wrong and do not match up with our maps, but the closest pole number is 256-68. Very small oil spill at this location. Released by crew 077S04//COD 3//ON AT 1540
9789 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-07-08 14:17 | 2011-07-08 16:35 | 6 | 138 | 4487941 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND BAD TRANSFORMER 50KVA// P TOLLIVER ON SITE TO REPLACE XFMR CHANGED, ALL POWER RESTORED COD-7 ISO TF 38830206C02176 VER/HFP L3/HFP IDCC PN2176 XXXX
9790 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-01-03 18:12 | 2016-01-03 22:48 | 3 | 276 | 4582741 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONLY ONE CUSTOMER AFFECTED CUSTOMERS UG SERVICE (DIRECT BURIAL) HAS OPEN NEUTRAL. WE ARE RUNNING TEMPORARY NEUTRAL ABOVE GROUND FROM POLE TO METER BASE. TEMPORARY REPAIRS COMPLETE. RESTORED @ 22:48. I WILL SEND A JOB TO THE LINE CREW TO LOCATE AND REPAIR FAULT. SH//COD 1
9791 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2014-08-20 10:11 | 2014-08-20 17:05 | 2 | 414 | 4388851 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830419B00351 === NEED 1MAN AND FLAGS === CHANGED CUTOUT ==== POWER OK//// ISO 37830419B00351/// COD 2 CCC888888//// MAP DISCEPANCY MADE// VER/BOW
9792 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2014-04-13 17:09 | 2014-04-13 21:45 | 3 | 276 | 4600381 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRUCK TO POLE OUT BACK FROM ALLEY BESIDE BOB BEAM HOUSEBAD 25KVA TRUCK TO POLE OUT BACK FROM ALLEY BESIDE BOB BEAM HOUSE // B REYNOLDS & T CANTRELL & K GRIFFITH VER/ARN
9793 | Paintsville | 3401802 | INDEX | HOSPITAL | 2011-02-11 07:33 | 2011-02-11 11:00 | 4 | 207 | 56091-1 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA TRANSFORMER...BAD...MAY NEED TO UP GRADE..3 -200 AMP AND 1 -400 AMP ALL ELECTRIC../ CREW ON SITE STARTING CHANGE OUT TCM// VER/KEP IDC XXXX
9794 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2021-05-10 08:53 | 2021-05-10 12:20 | 4 | 207 | 4569091 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned into ,I replaced it
9795 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2009-08-09 19:13 | 2009-08-09 22:40 | 4 | 207 | 51100-1 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICER ETA 20:10 (4 CUSTOMERS WITHOUT POWER) NO INTERRUPTION ON OTHER 15. 1/0 TWIST SECONDARY BURNT DOWN. APPROX 130 FT OF WIRE DAMAGED - WILL HAVE TO REPLACE ENTIRE SPAN. GOING TO PAINTSVILLE OFFICE TO GET WIRE. OPENED XFMR ON 978-177 AT 22:10. RESTORED AT 22:40 PICKING UP ALL CUSTOMERS. HAD TO LEAVE SECONDARY SLACK DUE TO TREES IN PRIMARY AT 978-177. PLEASE SEND TO J. BRADSHAW. SH IDCC CNT19 XXXX
9796 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-01-17 10:06 | 2022-01-17 14:42 | 3 | 276 | 4369701 | 828 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 1062-44 broke. need 35-5 pole and 1/0 secondary to splice with Released by crew 077S10
9797 | Hazard | 3303902 | LESLIE | WOOTON | 2011-11-18 10:02 | 2011-11-18 12:00 | 7 | 118 | 4090011 | 826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOING TO CHANGE TO 50 KVA /// VER/CRB IDC XXXX
9798 | South Williamson | 3414301 | SIDNEY | BIG CREEK | 2022-12-23 18:36 | 2022-12-23 18:50 | 59 | 14 | 4331841 | 826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | line fuse burned out again on pole 963D-71.back in at 18:50..
9799 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-07-20 11:36 | 2009-07-20 12:35 | 14 | 59 | 64662-1 | 826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LA POWER RESTORED//COD 14// VER/DBM IDC XXXX
9800 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2015-08-22 11:24 | 2015-08-22 12:23 | 14 | 59 | H4163031 | 826 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WILL WORK AT START TIME. PRIMARY BROKE BETWEEN POLE 449-254 AND POLE 255. WILL HAVE TO OPEN LINE FUSE AT POLE 449-37 TO MAKE REPAIRS, WILL KEEP TRACK OF TIMES. OPENED L/F AT 1124, MADE REPAIRS CLOSED BACK IN AT 1223./DUPLICATE IN HOIS// VER/ ADH L3/DKG
9801 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-02-07 22:30 | 2021-02-08 01:15 | 5 | 165 | 4947781 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burned down at pole 22-264 had to open XFM on pole 22-27, opened at 22:30, will need help with repairs//cod 5
9802 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-04-09 14:15 | 2009-04-09 17:00 | 5 | 165 | 50802-1 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3312202///BROKE CUTOUT//BIG BUCKET REQUIRED//COD 5// VER/KEP L3/KEP IDC XXXX
9803 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-07-02 21:55 | 2011-07-03 02:30 | 3 | 275 | 4449811 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100 KVA TRANSFORMER // ISSUED MAP DISC // COD 3 IDC XXXX
9804 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2009-08-12 17:55 | 2009-08-12 20:40 | 5 | 165 | 50824-1 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT CUT OUT RESTORED POWER M.D.I. VER/KEP L3/KEP IDC XXXX
9805 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2017-10-28 13:05 | 2017-10-28 14:20 | 11 | 75 | 4505311 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STEPDOWN FUSE OPEN ON 37830329000214. BY-PASS CUTOUT HAS GONE BAD ON POLE 329-288. STEP DOWN FUSE IS OUT ON POLE 329-214 B PHASE. 37830329000288 VER/AWD L3/HFP HFPC CDC92
9806 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2017-09-24 18:25 | 2017-09-24 23:00 | 3 | 275 | 4386291 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER NO ANSWER 6T FUSE OUT DUE TO BAD TRANSFORMER NEED BIG BUCKET 1 MAN 15KVA TRANSFORMER 7200. WE HAVE TRANSFORMER CHANGED OUT EVERYTHING OK VER/KEP
9807 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-07-03 11:40 | 2017-07-03 12:35 | 15 | 55 | 4069051 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENING LF SO CREW COULD SAFELY REPLACE CUTOUT ON POLE 387-B-63/ PO 4068271//1140 TO 1235 VER/CRB
9808 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2008-12-22 09:25 | 2008-12-22 14:00 | 3 | 275 | 62385-1 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP == REPLACED GATE ==//3301701/VER/CRB L3/JAW IDC XXXX
9809 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-04-10 17:20 | 2021-04-10 20:05 | 5 | 165 | 4438641 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Bottom blown off arrester on 841-95 may have blown line fuse. Isolated arrester. Restored @ 20:05. sh
9810 | Whitesburg | 3401301 | FLEMING | NEON | 2016-12-29 11:00 | 2016-12-29 13:45 | 5 | 165 | 4248011 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | REMADE NEUTRAL CONNECTIONS ON XFMR POLE WE OPENED XFMR AT 11:00// VER/ ADH
9811 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2020-07-11 12:05 | 2020-07-11 14:50 | 13 | 165 | 4151821 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout at pole 47a326. no truck crew reqd. Released by crew 078S04 crew on site FETR 14:45 opened lf on p 1147-276 at 14:05 fetr 15:00 restored @ 1450
9812 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-07-11 19:40 | 2008-07-12 00:15 | 3 | 275 | 51396-1 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | 3001201// HAVE TO REPLACE A SPAN OF 1` // WILL NEED FLAGGERS// CALLED CREW //VER/CRB IDC XXXX
9813 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-06-06 10:55 | 2008-06-06 12:10 | 11 | 75 | 59041-1 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND REFUSED LINE HFP
9814 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2008-02-22 16:00 | 2008-02-22 18:45 | 5 | 165 | 66301-1 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000201// RELEASED BY CREW 078S02// BAD CUTOUT BURNT POLE - LOWERED EVERYTHING AND MADE BACK HOT @ 1845// VER/TOM IDC XXXX
9815 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2012-07-02 11:55 | 2012-07-02 16:30 | 3 | 275 | 4215881 | 825 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTIONS ON XFMR, POWER RESTORED CAN CLOSE TICKET MWL
9816 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-07-25 07:43 | 2022-07-25 14:35 | 2 | 412 | 4571181 | 824 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | hot leg burnt in the clear repairs made power restored
9817 | Hazard | 3308002 | JACKSON | PANBOWL | 2019-10-07 20:46 | 2019-10-08 10:30 | 1 | 824 | 4115661 | 824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | big screw on stirrup burning on line, opened line fuse before burnt down phase, opened fuse at 22:05 talked to cust said would be ok to leave till tomorrow, will need big bucket and flaggers,also might be safe to isolate before trying to remove stirrup Released by crew 077H14
9818 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2016-08-08 15:27 | 2016-08-08 17:10 | 8 | 103 | 4750421 | 824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKEN ON POLE 167B-132..WILL HAVE TO OPEN LINE FUSE ON POLE 167B-01 TO CHANGE CUTOUT SAFELY...OPENED @ 16:45 CLOSED BACK IN @ 17:10..RESTORED.. RELEASED BY CREW 074S01 VER/AWD L3/HFP XXXHFP
9819 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2010-05-16 12:24 | 2010-05-16 15:50 | 4 | 206 | 63225-1 | 824 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT CUT OUT AND RESTORED POWER M.D.I.//COD 4// VER/DBM IDC XXXX
9820 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-08-06 22:57 | 2015-08-07 12:40 | 1 | 823 | 4107331 | 823 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON MANUEL POLE, SUGGEST WAITING UNTILL MORNING, ONLY 1 CUST OUT, POLE # 184-38. WILL NEED CREW RELEASED BY CREW 077S02.REPLACED CUTOUT. ALL POWER RESTORED @ 12:40 HRS/ ISO 37830184A00037/ COD 1/ VER/BOW
9821 | Hazard | 3309301 | VICCO | REDFOX | 2011-07-07 08:14 | 2011-07-07 15:05 | 2 | 411 | 4479891 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 19.9 XFMR ON POLE 324-154 RELEASED BY CREW 077S11 VINES BURNED XFMR UP REPLACED XFMR WITH LIKE KIND RESTORED POWER AT 1505 CREW 077H01//COD 7// VER/DMB IDCC PN205, CNT7 XXXX
9822 | Hazard | 3309301 | VICCO | REDFOX | 2009-09-24 23:41 | 2009-09-25 01:58 | 6 | 137 | 61821-1 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | B-PHASE FUSE BLOWN ON POLE 323-430, PATROLLING LINE 3 SINGLE PH CUSTOMERS3 3PH CUSTOMERS VER/ARN IDC XXXX
9823 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-02-21 08:53 | 2015-02-21 15:44 | 2 | 411 | 4061501 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN // WILL REFUSE // BAD 25 KVA 19.9 // NEED 25 KVA// FLAGGING CREW// CAN USE TRUCK RELEASED BY CREW 074S05/// IN THE PROCESS OF MAKING REPAIRS.// CHANGED TRANSFORMER CHECKED VOLTAGE AND RESTORED POWER AT 15:44 TIM MCCOY RELEASED BY CREW 074H10//COD 2// VER/DBM
9824 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2015-08-10 16:49 | 2015-08-10 19:06 | 6 | 137 | 4118391 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 98/ LINE FUSE OUT ON POLE 38821060C00053// VER/ ADH L3/HFP HFPC PN38821060C00094
9825 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-09-09 09:54 | 2020-09-09 16:45 | 2 | 411 | 4444661 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 50 KVA 19.9 truck ok Released by crew 077S03.made repairs restored power at 16;45..
9826 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2017-11-19 00:33 | 2017-11-19 14:15 | 1 | 822 | 4577621 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | replaced bad serve end on pole
9827 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2009-01-20 04:16 | 2009-01-20 08:50 | 3 | 274 | 58455-1 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309104//OPEN SECONDARY IS DOWN FROM POLE 401-136 WILL NEED A CREW TO PUT WIRE BACK UP CECIL SEXTONS CREW WILL BE WORKING ON THIS PLEASE SEND TO HIS SPECTRUM RELEASED BY CREW 074S07 VER/TOM L3/TOM
9828 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2013-01-22 00:48 | 2013-01-22 03:05 | 6 | 137 | 4725741 | 822 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/KEP IDC XXXX
9829 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-03-19 19:19 | 2015-03-20 09:00 | 1 | 821 | 4211041 | 821 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | SEND NOTE TO RAYBURN FRIDAY NEED CREW 3-CURRENT LIMING FUSE FOR 19.9 TRANS BANK B PHASE FUSE BURNT UP ALL NEED CHGED RELEASED BY CREW 078S08/TAGGED TRANSFORMER 164-A-352 TO KYDDC/HAVE SOMEONE REPLACE FUSE IN THE MONRINIG 3/19/2015,,,CREW ON SITE,,CHANGED TAGS,,REPLACED FUSES,,ALL POWER RESTORED COD-1 ISO TF 38830164A00352 VER/HFP L3/HFP
9830 | Paintsville | 3401101 | FALCON | FALC-OILS | 2015-09-03 07:01 | 2015-09-03 09:45 | 5 | 164 | 4193411 | 820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKE ON 806-250. REPLACING. RESTORED @ 9:45. SH/ ISO 38830806A30250/ COD 5/ VER/BOW
9831 | Hazard | 3303902 | LESLIE | WOOTON | 2014-04-24 20:04 | 2014-04-24 23:29 | 4 | 205 | 4631111 | 820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HURT & RICE // NEED 25 KVA 19.9 TR AND MATERIAL BUCKET FOUND LINE FUSE OUT ON POLE 23 COD-4 ISO LF 37830365C00023 VER/HFP L3/HFP
9832 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2010-10-26 22:00 | 2010-10-27 01:25 | 4 | 205 | 65233-1 | 820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 242-105. NOT SERVING ANYTHING. I REMOVED THE HOT LINE CLAMP.//VER/CRB IDC XXXX
9833 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2014-11-24 17:06 | 2014-11-24 19:50 | 5 | 164 | 4775561 | 820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BAD HOTTAP RESTORED VER/CRB
9834 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-08-15 14:00 | 2014-08-15 14:41 | 20 | 41 | 4370291 | 820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ROTTEN POLE LAYED OVER// ONLY THING HOLDING IT IS PRIMARY & NEUTRAL//// LINE CREW WILL WORK TODAYWILL HAVE SERVICER CHECK DURING REGULAR WORK HOURS// POLE 552-31 IS ROTTEN AND WIRE HOLDING IT UP WILL NEED TO REPLACE 40/4 PTP AND CLEVIS RELEASED BY CREW 077S01 // COD-20 ISO LF 37840552000131 VER/HFP L3/HFP AJB
9835 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-05-19 12:05 | 2021-05-19 15:30 | 4 | 205 | 4599761 | 820 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | u/g bad in junction box//crew on site to assist//replaced junction box and connections//restpred at 15:30//complete//em
9836 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-04-06 15:33 | 2021-04-06 20:06 | 3 | 273 | 4424221 | 819 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | B phase cutout broke and riser went phase to phase burning lead off. This is on the DA line crew required. Please bring 3-19.9 cutouts. truck ok Released by crew 078S11,repairs made all cust restored @ 2006 please close ticket thanks.bt Released by crew 078H02 //sjg fuse not on map
9837 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-10-06 18:44 | 2014-10-06 19:47 | 13 | 63 | 4559971 | 819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELATED TO ORDER 4557681 -- CREW HAD TO OPEN LINE FUSE TO ALLOW CREW TO SAFELY REPLACE TRANSFORMER//OPEN STEP DOWN AT 1844.../MADE LINE HOT AT 19;47// VER/BOW L3/IDC XXXX AJB
9838 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2011-06-13 10:18 | 2011-06-13 14:51 | 3 | 273 | 4310131 | 819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | BAD XARM ON POLE 358-89, TRUCKS TO POLE OK. C PHASE LINE FUSE IS OPENED ON POLE 358-42, NEED TO OPEN A (3 CUST) . NEED LONE CREW, AND 8 FOOT X ARM AND BRACES. OPENED B & C (2 CUST)@ 1315 SEE H4310131 VER/HFP L3/HFP IDC XXXX
9839 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-12-23 09:47 | 2008-12-23 14:20 | 3 | 273 | 63006-1 | 819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409303//SECONDARY BURNT DOWN. WILL UPGRADE IT AND XFMR (25 TO 50KVA) (1/0 SEC TO 4/0). CREW GETTING MATERIAL AND WILL BE BACK.SECONDARY BURNT DOWN. WILL UPGRADE IT AND XFMR (25 TO 50KVA) (1/0 SEC TO 4/0). CREW GETTING MATERIAL AND WILL BE BACK. REPAIRS COMPLETE. SH COD-3 MD FILED VER/KEP L3/KEP IDC XXXX
9840 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-02-09 19:22 | 2010-02-10 09:01 | 1 | 819 | 54628-1 | 819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40/4 POLE ON FIRE AT POLE 37830151000279 THAT FEEDS A BARN WILL MANUAL ISOLATED AT POLE 151-18//CUST IS AWARE THAT BARN WILL REMAIN OUT UNTIL MORNING AND IS OK WITH IT//MD FILED ON INCORRECT TRANSFORMER LOCATION// RELEASED BY CREW 077S04 VER/ARN IDCC PN77, CNT3, MCCNI XXXX
9841 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2014-05-27 12:55 | 2014-05-27 13:04 | 91 | 9 | 4933621 | 819 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER LONG ENOUGH TO SAFELY REPAIR TIX 4933311//DONE AT 1304 VER/CRB MAF
9842 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-02-05 06:46 | 2021-02-05 12:15 | 4 | 329 | 4938841 | 818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Neutral connection has burnt up on xfmr in bank. Opened all 3 xfmrs @09:32 to check and make repairs. Have line crew on site to assist.Repaired/replaced neutral wire and connections. Restored customer to full voltage @12:15
9843 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-07-20 16:54 | 2010-07-20 23:43 | 2 | 409 | 54162-1 | 818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA YARD DOG OR PACKIN BEHIND HOUSE/BOTH METERS ARE PULLED RELEASED BY CREW 078S03/CREW GETTING TRACK BUCKET ON SITE/FETR 0130/ 7-21-10/VEM/REPAIRS MADE/POWER RESTORED 2343/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB IDC XXXX
9844 | Hazard | 3303901 | LESLIE | HYDEN | 2018-04-17 08:56 | 2018-04-17 15:45 | 2 | 409 | 4243901 | 818 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED 40FT POLE BURNT OFF 37830340000151/ pole replaced power restored at 15;45/ ISO 37830340000104/ COD 2
9845 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-03-31 15:19 | 2016-03-31 22:08 | 2 | 409 | 4010631 | 818 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF ON POLE 118-4653, B PHASEPOLE 118-4653 HOT TAP BROKE OFF NEED LINE CREW///NEED TO CHECK WITH DENZIL TO GET TIME AND CONFIRM BACK ON, BELIEVE TO BE ON/ APPEAR ON AS OF 1700//TOM
9846 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2018-03-16 21:08 | 2018-03-16 23:43 | 8 | 155 | 4021211 | 817 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempted to call cust/ 137-32 bad 12kv co. trk ok Released by crew 078S07/crew on site/will need to open line fuse for repairs/vem/opened fuse at 2329
9847 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2009-02-22 06:00 | 2009-02-22 06:48 | 17 | 48 | H50138-1 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801 - PREDICTED RECLOSER AT POLE 245-12 NOT OPEN. FOUND SOLID BLADE DISCONNECT FAULTED AT POLE 245-1 WHICH HAS 108 CUSTOMERS INTERRUPTED. 3000801 -CREW REQUIRED NO TRUCKS NEED TO OPEN RECLOSER AT POLE 245-12 TO REPAIR CUTOUT. THIS WILL INTERRUPT 17 ADDITIONAL CUSTOMERS RELEASED BY CREW 078S03/CREW ON SITE/FETR0730/VEM/ALL CUST RESTORED 0648/PLEASE CLOSE TICKET/THANKS/VEM IDC DUP TO OPEN RECLOSER XXXX
9848 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2013-12-02 14:44 | 2013-12-02 17:00 | 6 | 136 | 4093621 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE OUT AT POLE 501-343 TAP MADE UP ON LOAD SIDE OF FUSE, DID MD COD 6 ***CHANGE ISO POLE***//CUT BAD 19.9 ARRESTER IN THE CLEAR APR AT 1700 CLOSE TICKET. DEW IF GROUND IS FROZEN BIG BUCKET MAY REACH VER/SEF L3/HFP
9849 | Hazard | 3311101 | STINNETT | REDBIRD | 2013-03-11 13:17 | 2013-03-11 14:25 | 12 | 68 | 4897821 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT 19.9 ///VER/CRB L/3 CRB IDC XXXX
9850 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-03-30 16:14 | 2022-03-30 18:30 | 6 | 136 | 4692961 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830185000022 15 t lat blown --found bad c/o replaced--line fuse in at 18:30-allgood-ds033022
9851 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-09-25 16:27 | 2014-09-25 16:51 | 34 | 24 | H4528431 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNING ON POLE 38830251000096// NEED LINE CREW AND FLAGGING CREW// TRUCK OK// WILL HAVE TO OPEN SWITCHES ON POLE 251-207 OPENED B PHASE SWITCH @ 14:08// ISO 38830251000207// COD 95//CREW ON SITE/FETR1730/VEM/OPENED SWITCHES @1627/REPAIRS COMPLETE CLOSED SWITCHES@1651/ALLCUST RESTORED PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L3/IDC XXXX AJB
9852 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-12-01 11:58 | 2010-12-01 16:30 | 3 | 272 | 62013-1 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1 SPAN OF #4COPPER SEC DOWN ON POLE 37820010C00022//VER/CRB IDC XXXX
9853 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-06-26 09:12 | 2009-06-26 16:00 | 2 | 408 | 61988-1 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED BAD CUTOUT IDC XXXX
9854 | Hazard | 3309301 | VICCO | REDFOX | 2020-02-13 19:11 | 2020-02-13 19:35 | 34 | 24 | 4404001 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | primary conductor off insulator, will have to open recloser on pole #323-508, no outage now, but primary is below nuetral. need 2 men big bucket, 7.2 kv ptp insulator.,,open recl @19:11 hrs,.closed in @ 19:35 . all power restored p.hicks/ ISO 37830323C00508/ cod 34 L3/HFP
9855 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-01-12 07:05 | 2011-01-12 13:53 | 2 | 408 | 60806-1 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE TOP BURNT OFF 60/4 POLE. WIRE COMES ACROSS US23, NEED FLAGERS AND LINE CREW. RELEASED BY CREW 078S01//VER/CRB IDC CHANGED FROM CUTOUT, SERVICER HAD 60 FT POLE BURNT OFF - CREW SAID CO WAS FINE THINK IT WAS THE ARRESTER XXXX
9856 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2017-12-25 14:47 | 2017-12-25 15:55 | 12 | 68 | 4677481 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Opening transformer bank for approximately 1 hr to fix connections. 38830978A30107 cod 12Connection failed on 954-1148. Opened xfmr bank 978-107 to safely make repairs @ 14:47.Connection failed on 954-1148. Opened xfmr bank 978-107 to safely make repairs @ 14:47. Made repairs and closed xfmr bank @ 15:55. sh
9857 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2022-03-23 04:23 | 2022-03-23 08:55 | 3 | 272 | 4659821 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. fuse open @24-B4-1776, checking. Cutout was busted here, got it repalaced @0855.
9858 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2021-04-26 06:14 | 2021-04-26 08:30 | 6 | 136 | 4479321 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 25T Line fuse on 43-1 restored @ 08:30. Broken fuse Released by crew 078S02
9859 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-04-01 20:02 | 2010-04-02 09:38 | 1 | 816 | 57246-1 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 24 KVA 19.9 NEED MET HANDLER 2 MEN//PER JEFF COMBS, CREWS WILL WORK THIS TOMORROW MORNING//CUSTOMER HAS GENERATOR AND WILL BE FINE FOR TONIGHT// // VER/KEP IDC XXXX
9860 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2010-08-06 17:37 | 2010-08-06 18:45 | 12 | 68 | 50757-1 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 36338386 // POLE 45-3629 BAD LINE FUSE CUTOUT 30T
9861 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-10-03 14:58 | 2013-10-03 16:40 | 8 | 102 | 4908221 | 816 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT VER/CRB L/3 CRB IDC XXXX
9862 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-05-04 22:20 | 2018-05-05 01:03 | 5 | 163 | 4308781 | 815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | failed insulator replaced and restored
9863 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2013-06-16 19:02 | 2013-06-16 21:45 | 5 | 163 | 4350351 | 815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CHECKING NOW.TOP OF HOT TAP LEAD ON XFMER CUTOUT BURNT INTO.BACK TO NORMAL//COD 5// VER/DBM IDC XXXX
9864 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2013-11-13 09:47 | 2013-11-13 12:30 | 5 | 163 | 4034751 | 815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE ON 794-28//RESTORED AT 12:35//COMPLETE//EM COD-5 ISO LF 38820794D00028 VER/HFP L3/HFP
9865 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-12-23 11:56 | 2021-12-23 14:39 | 5 | 163 | 4222131 | 815 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Have a Broke Trans Cutout at 190-C-57,This is a Manual pole,Will be Making Repairs.Restored Trans at 14:39..
9866 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-03-22 02:17 | 2010-03-22 09:04 | 2 | 407 | 52444-1 | 814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, XFORMER FUSE BLOWN, REFUSING IT RELEASED BY CREW 080S01 RANDALL SAID HE WOULD WORK AT NORMAL START TIME VER/HFP L3/HFP IDC XXXX
9867 | Hazard | 3303901 | LESLIE | HYDEN | 2008-08-22 07:45 | 2008-08-22 07:56 | 74 | 11 | 54009-1 | 814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3303901// MANUALLY OPENED RECLOSER IN ORDER TO REPAIR OPEN LOOP IN LINE // WILL HAVE OFF FOR ABOUT 20 MINUTES // COD-74 // NEXT RECLOSER DOWNSTREAM WAS ALREADY OPEN DUE TO TREE IN LINE // VER/LDA REFER TO ORDER 53961-1 MLRC C SCO
9868 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2019-09-01 12:36 | 2019-09-01 14:30 | 36 | 114 | 4971131 | 814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 925-100 broke xfmer cutout/ opened solid blade on 925-96 @ 1410 to safely make repairs/ solid blade on 925-96 closed in @ 1430/ please close ticket/ MLH L3/HFP
9869 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-09-02 03:43 | 2010-09-02 10:30 | 2 | 407 | 62749-1 | 814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL HAVE TREE CREW RECLEAR AROUND XFMR AT 07:00 AND WILL CHECK XFMR BEFORE REFUSING DUE TO SEVERAL OUTAGES ON THIS XFMR RECENTLY RELEASED BY CREW 077S04 VER/KEP L3/KEP IDC XXXX
9870 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2016-05-11 04:56 | 2016-05-11 18:30 | 1 | 814 | 4196601 | 814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA NEED LINE CREW TO REPLACE TRUCK OK----CREW ON SITE---CHANGED BAD 25KVA---VOLT CK GOOD---TBL TKT COMP---RMV VER/AWD
9871 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-12-06 19:27 | 2010-12-07 02:14 | 2 | 407 | 63783-1 | 814 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN..BAD 25KVA 19.9 KV 120/240V XFMER..WILL BE MANUAL...REPLACE WITH 25KVA...W/R #38009548...CHANGED XFMER OUT..ALL POWER RESTORED @ 02:14 HRS P.HICKS //VER/GAH IDC XXXX
9872 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-08-15 22:15 | 2021-08-16 11:48 | 1 | 813 | 4074281 | 813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD TILL MORNING PER GLEN COMBS// broke cutout manual, have help on the way
9873 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-01-07 20:11 | 2022-01-08 00:42 | 3 | 271 | 4322321 | 813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 7200 by truck as long as you bring a big one and a digger to pull it out with. home owner said you can back in there to fix it but you may not get out Released by crew 078S12,repairs made all cust restored @ 0042 please close ticket thanks.bt//cod 3
9874 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2015-09-05 18:04 | 2015-09-05 22:35 | 3 | 271 | 4207901 | 813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER IN DIFFICULT LOCATION. REPLACED WITH 25 KVA AND RESTORED AT 22:35. SH VER/TOM L3/TOM
9875 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-08-27 20:44 | 2008-08-28 01:15 | 3 | 271 | 56637-1 | 813 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3008702//FUSE OUT ON POLE#165-35//MADE A MD//RELEASED BY CREW 078S01//WR#25992689 VER/LDA IDCC CNT10, PN263 XXXX
9876 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2012-01-17 22:09 | 2012-01-18 00:05 | 7 | 116 | 4271571 | 812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER //VER/GAH IDC XXXX
9877 | Pikeville | 3402003 | KEYSER | MULLINS | 2020-04-28 14:01 | 2020-04-28 18:14 | 19 | 253 | 4762521 | 812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Loop burndt open @1127-B-132, pole on hillside, will need a 3 man line crew, also will have to open L/F @1127-B-11 in order to make repairs.//COD 2 FROM BEGIINING OF OUTAGE//opened line fuse @ 1756 On @ 1814
9878 | South Williamson | 3417601 | NEW CAMP | S. SIDE | 2010-04-26 17:02 | 2010-04-26 18:00 | 14 | 58 | 51571-1 | 812 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//VER/CRB IDC XXXX
9879 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2012-05-08 07:15 | 2012-05-08 11:45 | 3 | 270 | 4758561 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PTP INSULATOR BAD ON POLE 473-140 NEXT TO LAST POLE IN HOLLOW. THIS IS A MANUAL POLE ON SIDE OF MTN. RELEASED BY CREW 077S12. REPLACED INSULATOR RESTORED POWER AT 11:45//COD 3// VER/DBM IDC XXXX
9880 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2014-04-13 00:15 | 2014-04-13 13:45 | 1 | 810 | 4599181 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UG NEED LINE CREW TO REPLACE RELEASED BY CREW 078S05,LOCATED FAULT, HAND DIGGING 30 DITCH, ALSO INSTALLNG NEW RISER, VER/HFP L3/HFP
9881 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-04-06 19:48 | 2016-04-06 22:30 | 5 | 162 | 4061071 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPAIRED SECONDARY POLE 98-301/ ISO 37820098C00301/ COD 5/ VER/BOW
9882 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-06-29 09:00 | 2009-06-29 15:45 | 2 | 405 | 50304-1 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN AND SET POLE ON FIRE, CALLING FOR HELP, ISOLATED TROUBLE AT 256-105 @ 0900, POLE ON FIRE IS 256-208//ISO 37830256000105//COD 2//CUTOUT BROKE DOWN AND SET POLE ON FIRE, CALLING FOR HELP, ISOLATED M ETROUBLE AT 256-105, POLE ON FIRE IS 256-208 RELEASED BY CREW 077S02 MADE REPAIRS AND RESTORED POWER AT 1545 077H01// IDCC CNT3, TOF0646, PN130 XXXX
9883 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2010-03-29 19:48 | 2010-03-30 02:33 | 2 | 405 | 55798-1 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE ON FIRE, WHEN I ARRIVED, LINE FUSE HAD ALREADY BLOWN ON POLE 1122-43, WELL NEED 405 POLE, CUTOUT AND ARRESTOR, AND THIS POLE HAS UNDERGROUND ON IT, 3IN PVC, WELL NEED CLAMPS, TO TRANSFER, CAN USE TRUCKS ON THIS, ALSO I HAVE LINE FUSE CLEARED UP, AND ALSO HAVE IT GROUNDED AT THIS POLE, 1122-43, RELEASED BY CREW 078S06//STS WR# 34443208 // CUSTOMER HAD FILLED AROUND POLE HAD HARD TIME FINDING UG SO WE COULD SET NEW POLE VER/PDP AJB
9884 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2010-05-24 10:30 | 2010-05-24 12:00 | 9 | 90 | 50170-1 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED TAP TOWARDS POLE#323 30T FUSE ON POLE# 258 MD FILED TO SAFELY REPLACE CUTOUT ON POLE# 258 VER/KEP L3/KEP IDC XXXX
9885 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-01-18 09:30 | 2008-01-18 10:51 | 10 | 81 | 57544-1 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000102 CREW OPENING SWITCH ON POLE 46B1-2148 TO REPLACE BURNT CROSSARM ON POLE 45D3-7130...SHOULD BE OFF APPROX UNTIL 1130 OR 1200 HRS. DKG IDCC FP NULL XXXX
9886 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2022-11-15 15:07 | 2022-11-15 17:22 | 6 | 135 | 4145401 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | 50T LF open on 1124-2047, Single phase on double arms, braces broken @ 1124-b1-2073, Primary off pin @ 1124-b1-2072. Crew required, no trucks. No tags or grounds Released by crew 078S02/ LF restored @ 1722/ please close ticket/ MLH
9887 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2009-06-08 18:40 | 2009-06-09 01:25 | 2 | 405 | 57925-1 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA SINGLE BUSHING, CAN USE TRUCK, HAVE TALKED TO BOB REYNOLDS, HE WILL TAKE CARE OF THIS RELEASED BY CREW 078S06 VER/PDP IDCC PN215 XXXX
9888 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2017-07-11 10:46 | 2017-07-11 12:07 | 10 | 81 | 4105271 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BURNT UP SECONDARY CONNECTIONS. CONNECTIONS BURNT UP ON POLE 38830045B22531 REPAIRED ON 7-11-17 VER/AWD
9889 | South Williamson | 3411401 | DEWEY | INEZ | 2014-11-23 21:35 | 2014-11-24 02:05 | 3 | 270 | 4757821 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NO VOLTAGE AT XFMR ON POLE 767-99///NEED 25KVA 19.9 XFMR///TRUCK ACCESS// RELEASED BY CREW 079S01NO VOLTAGE AT XFMR ON POLE 767-99///NEED 25KVA 19.9 XFMR///TRUCK ACCESS//REPAIRS MADE//RESTORED AT 2:05///OPENED LINE FUSE AT 1:10,CLOSED AT 2:05//COMPLETE//EM VER/KEP
9890 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2017-05-22 09:06 | 2017-05-22 11:48 | 5 | 162 | 4837791 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 0NE LINE FUSE OUT ON POLE 159-9, BROKEN CUTOUT ON XFMR ON POLE 159-10//COD 5 FROM THE BEGINNING OF OUTAGE//0NE LINE FUSE OUT ON POLE 159-9, BROKEN CUTOUT ON XFMR ON POLE 159-10, ALL POWER RESTORED//OPENED A&C @ 1120//DUPLICATE OUTAGE MADE VER/CRB
9891 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2019-10-13 15:37 | 2019-10-13 22:22 | 2 | 405 | 4136611 | 810 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR 7200 NEED LINE CREW MANUAL
9892 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-10-15 10:26 | 2012-10-15 16:01 | 7 | 335 | 4142201 | 809 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LINE FUSE OUT ON POLE 1097-89, PATROLLED FOUND POLE 1097-350 BURNTED OFF, I LIFFTED HOT TAP ON POLE 1097-265 AND GROUND AND TAGGED, NO ONE IS LIVING IN HOUSE AT THIS TIME IS UP FOR SELL, WELL BE CREW REQ, AT A LATER DATE LIKE TOMMORROW, ALSO ON POLE 1097-89 HAVE BAD CROSSARM BRACE, THAT NEED TO BE FIXED RELEASED BY CREW 078S06/TECH TO WRITE JOB/REPAIRS COMPLETE AND POWER RESTORED TO ONE CUST 1601/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14//MADE AED ///VER/CRB L/3 CRB IDC XXXX
9893 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-04-02 07:48 | 2021-04-02 11:10 | 4 | 202 | 4413451 | 808 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a Span of Open Wire that has came out of Sleeve from pole 97-11 up to 97-89,Will have to open both Trans on these poles to make repairs,Need to get me one Man to come and help make repairs,These R Both Manual poles..We have a Span of Open Wire that has came out of Sleeve from pole 97-11 up to 97-12,
9894 | South Williamson | 3200301 | BELFRY | BELFRY | 2015-09-26 16:24 | 2015-09-26 19:46 | 4 | 202 | 4275411 | 808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED TAP AT 38821014B10213 @ 1624 // PRIMARY DEAD END POLE IS BURNED 3/4 INTO. NO TRUCK ACCESS. NEED EIGHT FOOT ARM TO SPLINT POLE ALSO 7200 CUTOUT. SEND TO TECH TO SEE IF THIS POLE CAN BE REPLACED / RELOCATED /// COD-4 ISO LF 38821014B10213 VER/HFP L3/HFP
9895 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-07-25 06:13 | 2013-07-25 09:35 | 4 | 202 | 4590701 | 808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORK TIME AS PER SET GUIDELINES // CUTOUT IS BROKEN FEEDING TAP, IT WILL TAKE BIG BUCKET TO CHANGE, THE CREW IS COMMING RELEASED BY CREW 077S12 VER/CRB L/3 CRB IDC XXXX
9896 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2020-10-30 07:00 | 2020-10-30 10:22 | 4 | 202 | 4605221 | 808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cutout on 185-143, climbing pole to make repairs.Repairs made, closed 185-143 at 10:22 Ticket complete
9897 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2020-11-25 21:20 | 2020-11-26 00:42 | 4 | 202 | 4723751 | 808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Customer has Neutral broke in their service wire going to repair and restore service.Got wire spliced and restored at 00:42.
9898 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2021-07-11 19:36 | 2021-07-12 09:04 | 1 | 808 | 4894291 | 808 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQD/////BAD 25KVA 7.2XFR/////////NEED XFR,MAT BUCKET,1MAN/////GOING TO WORK TOMORROW PER STEVE RAY.1ST DW ON RIGHT@JUSTICE HOLLOW,BUILDING GARAGE ON THE END OF HOME.XFR STILL IN BUT LOW VOLTAGE@1 BUSHING Released by crew 074S06 Changed transformer and back on @ 9:04 Joshua Colley
9899 | South Williamson | 3200301 | BELFRY | BELFRY | 2016-03-19 12:13 | 2016-03-19 16:42 | 3 | 269 | 4863851 | 807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS,HAS VOLTAGE ON NEUTRAL AT MTR BASE///////NEED 1 MAN,ROLL 1/0 TRIPLEX,BUCKET TRUCK,INSULATION ON HOT LEGS FAILED,BURNED NEUTRAL INTO,WILL REPLACE WIRE////REPLACED WIRE,XFR OFF 15:30,ON AT 16:30/EMAILED PEGGY/ADH// VER/ ADH
9900 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2010-01-30 13:26 | 2010-01-30 17:55 | 3 | 269 | 61470-1 | 807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 519-35... REPLACED XFMR RESTORED POWER AT 17:55 VER/HFP L3/HFP IDC XXXX
9901 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-02-06 08:26 | 2010-02-06 12:55 | 3 | 269 | 66031-1 | 807 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL DISPATCH THIS ORDER TO THE SAT CREW . AT 10:00 A.M.// FUSE ROTTED IN TWO IDC XXXX
9902 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-09-26 07:04 | 2019-09-26 08:34 | 15 | 90 | 4059211 | 806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | opened line fuse 73-B-2 to safely replace blown arrestor//8 COD//off at 0812 on at 0834/////arrester blown on xfm. bank on pole 73-2.will make repairs..opened tap @ 08:12 closed back @ 08:34.restored.
9903 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2019-12-29 12:02 | 2019-12-29 13:45 | 22 | 103 | 4189521 | 806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 38830042000136 had to open the LF on pole 38830042000011 to change safely // line fuse off @ 1315 on @ 1345
9904 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2008-11-19 03:02 | 2008-11-19 09:45 | 2 | 403 | 66436-1 | 806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR 2735451 8BAD TRANSFORMER ON POLE 141-3.. 15KVA 19.9 TRANS ON POLE NOW NEED TO GO BACK WITH A 25KVA19.9 SINGLE BUSH TRANS. SERVES TWO CUST AT THIS TIME. SEND COPY OF THIS TO TIM HALL PIKEVILLE. CAN USE A MATERIAL HANDLER BUCKET. TIGHT GOING THROUGH GATES. RELEASED BY CREW 074S11 **** DISPATCHER TO FOLLOW UP WITH CALL TO TIM HALL REG. WORK TIME TODAY. VER/KEP IDCC CNT1 XXXX
9905 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2020-04-15 16:47 | 2020-04-15 23:30 | 2 | 403 | 4701161 | 806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 37.5--and c/o .7200 --leaning pole--per cust we can use squirtboom material handler--(and digger to pull em out save the grass)-ds041520 Released by crew 078S01/ xfmr back in @ 2330/ please close ticket/ MLH
9906 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-06-03 04:02 | 2013-06-03 10:45 | 2 | 403 | 4212001 | 806 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK AT BEGINNING OF REGULAR START TIME REPLACED BURNT UP DOOR IN CUTOUT. ///VER/CRB L/3 CRB
9907 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-02-17 12:45 | 2022-02-17 14:40 | 7 | 115 | 4491661 | 805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cut-out on 387A-333. Power restored 14:40
9908 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2012-02-03 00:25 | 2012-02-03 02:20 | 7 | 115 | 4317121 | 805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR ON XFMR POLE 1027-200 IS BURNT UP.WILL HAVE TO CHANGE CUTOUT.CHANGED CUTOUT AND REFUSED XFMR.VOLTAGE CHECKS GOOD. CC 7. VER/SDB IDC XXXX
9909 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-06-24 15:03 | 2013-06-24 15:26 | 35 | 23 | H4392081 | 805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 356-128, OPENED RECLOSER ON POLE 356-118 AT 15:03 TO ISOLATE.. REPLACED CUTOUT RESTORED POWER AT 15:26. IDCC DUP TO OPEN RECLOSER, TON1533 XXXX
9910 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-11-19 06:25 | 2014-11-19 08:20 | 7 | 115 | 4744491 | 805 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LEAD BURNED OFF, I REPLACED IT. VER/CRB L3/DKGXXXX
9911 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2009-06-17 08:34 | 2009-06-17 11:15 | 5 | 161 | 54901-1 | 805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT ON LINE FUSE GOING TO REPLACE CUTOUT L3/HFP
9912 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-10-07 12:40 | 2009-10-07 14:35 | 7 | 115 | 59507-1 | 805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, WILL ISOLATE ON POLE 472-79, WILL HAVE TO LOWER PRIMARY & REPLACE CUTOUT ON POLE 448-613 .. MADE REPAIRS RESTORED POWER AT 14:35//VER/CRB IDCC TOF1228 XXXX
9913 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-08-10 22:50 | 2009-08-10 23:25 | 23 | 35 | 63109-1 | 805 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW OPENED TO SAFELY REPLACE TRANSFORMER ON ORDER 60372 VER/KEP L3/KEP IDCC TOF1907 XXXX
9914 | Hazard | 3303902 | LESLIE | WOOTON | 2013-10-21 10:51 | 2013-10-21 17:33 | 2 | 402 | 4951291 | 804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 318-57 IS BURNT INTO AT THE CUTOUT LEVEL WILL NEED TO REPLACE POLE RELEASED BY CREW 077S01 REPLACED POLE AND RESTORED POWER AT 1733 COD-2 ISO LF 37830318B00341 VER/HFP L3/HFP
9915 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2014-04-28 19:47 | 2014-04-29 00:15 | 3 | 268 | 4644051 | 804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT ON POLE#217-53 WILL RE-FUSE. BAD 25 KVA 19.9 TRUCKABLE NEED 2 MEN TO HELP GET ON AND OFF ROAD RELEASED BY CREW 074H17CREW AT SITE RESTORED AT 00:15 04/29/14 VER/ARN
9916 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-01-28 08:49 | 2019-01-28 11:03 | 6 | 134 | 4727261 | 804 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | Splice in sec. has failed burning neutral in 2 between poles 1151-A-295 and 1151-357 will be opening xfmr to make repairs////opened xfmr @10:05 made repairs and closed back in @ 11:03
9917 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-01-14 12:38 | 2020-01-14 13:45 | 12 | 67 | 4304541 | 804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | xfmer restored, conection repaired
9918 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2011-11-18 13:10 | 2011-11-18 17:38 | 3 | 268 | 4090881 | 804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | `SEND TICKET TO WILLIE ROBINSON, NEED TO 10 KVA TO A 15KVA TRANSFORMER 7200 ON CEDAR FK OF ISLAND CR RELEASED BY CREW 074S05 COMPLTED J.HAWKINS /// VER/CRB IDC XXXX
9919 | Hazard | 3301401 | COMBS | COMBS | 2010-01-26 01:33 | 2010-01-26 08:15 | 2 | 402 | 59863-1 | 804 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER TALKED TO CUSTOMER AND HE REPORTED OKAY TO CHECK LATER THIS MORNING//SECONDARY RISER PULLED LOOSE FROM BUSHING ON XFMR // REPAIRS MADE , XFMR RESTORED COMPLETE COD-2 PER SERVICER VER/HFP L3/HFP IDC XXXX
9920 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-02-29 07:33 | 2016-02-29 14:15 | 2 | 402 | 4785961 | 804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--NO TRUCK CUT OUT ON POLE 206-2246 BROKE IN HALF AND FELL OFF POLE RELEASED BY CREW 078S02/ ISO38830206A42246 / COD 2/ VER/BOW
9921 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-02-19 18:22 | 2016-02-19 21:43 | 4 | 201 | 4739171 | 804 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT LINECREW REQUIRED RELEASED BY CREW 078S11MD MADE/ADH/CREW ON SITE/FETR2215/VEM/REPAIRS COMPLETE AND ALL CUST RESTORED 2143/PLEASE CLOSE TICKET/THANKS/VEM/MISMAPPED CUSTOMER ADDED TO 189-106 COD 4// VER/ ADH L3/HFP XXXHFP
9922 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2010-08-26 14:17 | 2010-08-26 15:30 | 11 | 73 | 60846-1 | 803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOTLINE CLAMP BURNT AT POLE 38830254B00316//COD 11// VER/DBM IDC XXXX
9923 | Pikeville | 3421001 | BREAKS | CITY | 2013-10-28 13:20 | 2013-10-28 14:33 | 11 | 73 | 4970301 | 803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE 243-351 VER/CRB L/3 CRB IDC XXXX
9924 | Hazard | 3308502 | BONNYMAN | HAZARD | 2012-10-21 03:24 | 2012-10-21 07:08 | 4 | 224 | 4160271 | 803 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SERVICER ON SITE * URD TROUBLE - CALLED OUT PAUL HICKMAN TO HELP. LIGHTHING ARRESTER BAD ON URD - CREW TO REPLACE - MATERIALS NEEDED FROM STORE ROOM. IDCC FP NULL XXXX
9925 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2011-12-09 10:55 | 2011-12-09 17:36 | 2 | 401 | 4164501 | 802 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | APPEARS TO BE A BAD CONNECTION AT XFR POLE,WILL REPAIR//GOING TO REPLACE CT MTRNG,IS IN BAD SHAPE,HELP MATERIALS ENROUTE,NOTE NEW FETR////////MADE NECESSARY REPAIRS AND RESTORED ///VER/CRB IDC XXXX
9926 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-01-04 20:16 | 2009-01-05 02:57 | 2 | 401 | 51332-1 | 802 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008702// 911 UPDATED THIS IS IN FRONT OF DENOTE ENTERPRISES - ACTUAL POLE IS 164-363// BAD CUTOUT ON Y DELTA BANK, NEED 25KVA 7200 XFORMER, TRUCKS TO POLE OK. NEED XFRMR REPLACED ASAP DUE TO COMMERCIAL /TRUCK IN GARAGE WITH LOAD THATS SCHEDULED TO BE VER/ARN L3/KEP IDCC PN224 XXXX
9927 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2012-08-04 09:45 | 2012-08-04 16:26 | 2 | 401 | H4893011 | 802 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | 2 PRIM UGS OUT,POLES 24-659&24-666,TRIED BOTH,FUSES BLEW,NEED HELP//TOLD THAT MORNING CREW WILL REPAIR RELEASED BY CREW 074S06 CREW ON SITECABLE F>24-659 >24-1097 GOOD REFUSE 30T AT 24-659 NEED TO HIPOT FROM 1097>1099//PAD 1097 IS HOT PARTIAL RESTORED AT 01:45 CABLE BAD AT PAD 1099 REPAIRS BEING MADEOPEN ON POLE 24-659 AT 9:45 CLOSED AT 18:26 RESTORING ALL CUSTOMER IDCC DUP TO OPEN DIP XXXX
9928 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-06-23 19:04 | 2015-06-24 01:45 | 2 | 401 | 4646931 | 802 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT HAS BURNED CROSS ARM OFF AND IS HANGING DOWN NEXT TO XFM ON POLE #97-131 CONDUCTOR IS STILL HOT WILL HAVE TO OPEN 3 SINGLE RECLOSERS ON POLE # 73-B-644 WHEN CREW GETS HERE ////NEED LINE CREW ,1 CROSSARM AND CUT OUT AND BRAKET/// NO TRUCK/// REPAIRS MADE CLOSED RECLOSER IN @ 1:45 AND RESTORED SERVICE RECL OUTAGE ONPO#4648651 VER/KEP
9929 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2014-03-29 23:52 | 2014-03-30 13:14 | 1 | 802 | 4537941 | 802 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | AS PER RYEN GIBSON MAINT DEPT OK TO WORK IN THE AM. FUSE IS OUT ON BANK OF XFMRS *** 1 FUSE IS OUT ON BANK OF XFMRS, BAD XFMR, NEED TO REPLACE 2 25 KVAS WITH 2 50 KVAS, 2 BUSHING XFMRS. ALSO NEED TO REPLACE 3 CUTOUTS AND ARRESTORS, WILL NEED CREW FOREMAN, 1 A LINEMAN, 1 ASSIST ONLY LINEMAN. 7.2 KV ALSO SOME 1/0 COPPER FOR LEAD VER/CRB
9930 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2017-07-04 12:38 | 2017-07-04 18:45 | 3 | 367 | 4071781 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | GROUND IS SOFT// LINE FUSE 38820771B10065 TOWARD 771-525 BLOWN (LF NOT ON MAPS) DUE TO XFMR CUTOUT FAILURE ON 771-525.//MADE MD TO SHOW L/F//GROUND IS SOFT// LINE FUSE 38820771B10065 TOWARD 771-525 BLOWN (LF NOT ON MAPS) DUE TO XFMR CUTOUT FAILURE ON 771-525. CLOSED 15T LINE FUSE ON 771-65 @ 16:15. THIS RESTORED ALL BUT XFMR ON 771-525. NEED 19.9 CUTOUT. RELEASED BY CREW 076S02GROUND IS SOFT// LINE FUSE 38820771B10065 TOWARD 771-525 BLOWN (LF NOT ON MAPS) VER/CRB
9931 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2008-03-14 15:39 | 2008-03-14 17:08 | 9 | 89 | 57212-1 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3001002// FUSE OUT ON POLE 38830350000078, PATROLED LINE AND FOUND NOTHING//VER/CRB IDC FOUND BAD INSULATOR LATER, CHANGED CAUSE FROM UNKNOWN XXXX
9932 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2020-03-16 08:33 | 2020-03-16 13:00 | 3 | 267 | 4481151 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANSFORMERbad 1kv 50 kva xfmer, old csp. will need c/o installed. alleyway trk to pole. Released by crew 078S07qasssssssssssssssssssssssssssssBAD 50KVA TRANSFORMERbad 1kv 50 kva xfmer, old csp. will need c/o installed. alleyway trk to pole. Released by crew 078S07,replaced xfmr & serv all cust restored @ 1300 please close ticket thanks.bt
9933 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-02-19 12:23 | 2014-02-19 16:50 | 3 | 267 | 4402661 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 378C-177 NEEDS REPLACED KENNY BROOME EN ROUTE TO REPLACE VER/SEF L3/GSL
9934 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-07-11 06:33 | 2010-07-11 11:00 | 3 | 267 | 64973-1 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9 CUTOUT NO TRUCKS RELEASED BY CREW 078S08 COMP 7/11/10 M.PHELPS RELEASED BY CREW 078H12//COD 3 AJB
9935 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2014-12-02 15:33 | 2014-12-02 20:00 | 3 | 267 | 4827001 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BAD CURRENT LIMING FUSE 19.9 ON POLE38830138C00089 NEED CREW BIG BUCKET RELEASED BY CREW 078S08,,CREW ON SITE MAKING REPAIRS,,ALL REPAIRS MADE,, ALL POWER RESTORED COD-3 ISO TF 38830138C00089 VER/HFP L3/HFP
9936 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2020-09-16 10:48 | 2020-09-16 15:15 | 3 | 267 | 4468501 | 801 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad UG neut. 1/0 ug. crew reqd. need ataphase put on to restore cust. Released by crew 078S04//MADE A DAE1000052132
9937 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-10-03 10:30 | 2010-10-03 17:10 | 2 | 400 | 56372-1 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BURNT OFF 40/5 SINGLE ARM 8 FOOT IN LINE WITH TRANSFORMER 2 SERVICES RELEASED BY CREW 078S03 ALL POWER RESTORED AT 17:10//COD 3// VER/DBM IDCC TOF0901 PER CONF CALL PN22 XXXX
9938 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2022-02-03 03:41 | 2022-02-03 09:58 | 4 | 377 | 4426081 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | -behind 2126 sr 1654 38830185000183 broke c/o on metal bracket --need 7200v c/o and fiberglass t-braket--crew req-(brown and white dog per cust nonbiter ???)-ds020322 Released by crew 078S01//arrived RM opening line fuse@185-19 to safely make repairs.open @09:35 closed at 09:58 please close tic RM Released by crew 078H20
9939 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-03-28 15:04 | 2012-03-28 17:25 | 9 | 141 | 4626061 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 115-352 WIRE OFF POLE NO TRUCK LINE FUSE 115-47 OUT RELEASED BY CREW 078S08...FIXED.POWER ON TO LAST 2 CUST @ 17:30 ////VER/CRB IDCC CNT11 ONLY ONE PHASE OUT XXXX
9940 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-09-02 04:08 | 2017-09-02 10:48 | 2 | 400 | 4322361 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200 25KV XFM. ON POLE 168-30//////WILL NEED ONE MAN AND BIG BUCKET TO MAKE REPAIRS...RESTORED/ ISO 37830168000030/ COD 2/ VER/BOW
9941 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2017-07-25 13:50 | 2017-07-25 20:30 | 2 | 400 | 4178371 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 38830286000182 BAD TRAN 15 OR 25 KVA AND CUT OUT --NBT??--125 PER FIELD VIEW STRING IN #2 OR 1/0??? TO 83-286/80 A TRAN W/1 CUST--BRING 25KVA W/CUT OUT AND 150 1/0 AND YOU FLIP COIN--DS072517 RELEASED BY CREW 078S01 VER/AWD
9942 | Hazard | 3303902 | LESLIE | WOOTON | 2016-08-18 08:10 | 2016-08-18 14:50 | 2 | 400 | 4809221 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV TRANSFORMER 19.9 ON POLE37830462000086,MAY BE ABLE TO USE TRUCK,BRING NEW CUTOUT OUT RELEASED BY CREW 077H07 REPLACED XFMR AND RESTORD POWER AT 1450 CREW 077H01 VER/AWD
9943 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-09-01 20:25 | 2012-09-01 23:05 | 5 | 160 | 4993041 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LATERAL FUSE OUT ON 1090-A-33.BAD XFMR CUTOUT ON 1090-A-283.WILL REPLACE.//.REPLACED BAD CUTOUT.RE-FUSED LINE AT 2305.JRV..09/01/12. CC 5. VER/SDB IDC XXXX
9944 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-05-21 08:40 | 2022-05-21 09:30 | 16 | 50 | 4920251 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cleared a blown arrester on 478-118, apr at 0930 close ticket, dwest//MADE DAE # 1000070646
9945 | Hazard | 3310502 | HADDIX | CANOE | 2009-04-01 14:00 | 2009-04-01 14:50 | 16 | 50 | 63783-1 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-16 RELATED TO ORDER 63657-1 CREW HAD TO OPEN LINE FUSE TO ALLOW THEM TO SAFELY REPLACE A TRANSFORMER THAT FAILED. L3/HFP IDC XXXX
9946 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-08-01 12:50 | 2009-08-01 15:30 | 5 | 160 | 56286-1 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUST. HAS A BROKEN CUTOUT-------REPLACED BROKEN CUTOUT VER/LDA IDC XXXX
9947 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2016-02-24 01:50 | 2016-02-24 04:30 | 5 | 160 | 4752791 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED ON 880-15. REPLACED CUTOUT AND RESTORED LINE FUSE @ 4:30. SH VER/ARN
9948 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-08-01 07:18 | 2013-08-01 10:38 | 4 | 200 | 4612171 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | /WIRE DOWN ON POLE328-54 TO POLE 328-56 NO TRUCK TO POLE RELEASED BY CREW 078S05///GROUNDED AND TAGGED TO CREW (RMV)///2 SPANS #4CU PRIMARY DOWN///REPAIRED PRIMARY///PWR BACK ON 10:38 VER/KEP IDC XXXX
9949 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-05-06 12:15 | 2013-05-06 14:55 | 5 | 160 | H4074131 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NO POWER OFF UNTIL 1215 -05/06 - 5 CUST & 1234 - 12 CUST // NEED TECH---POLE 39831147C24553 IS ROTTED OFF AN LEANING --TRUCK TO POLE--CLEARENCE PROBLEM--PHONE AT 13 FEET ACROSS RD--CITY TO BLOCK RD--JOHN SODA CONTACTED WINDSTREAM TO CHANGE POLE RELEASED BY CREW 078S07/ WINDSTREAM TO SET PL. FETR 16:00 JEH DUPLICATING FOR 5 CUST OFF @ 1215 FROM 4074131 -- VER/HFP L3/HFP IDCC SC, FP4553 XXXX
9950 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2014-03-09 13:34 | 2014-03-09 13:50 | 50 | 16 | 4462401-1 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | LOOKS LIKE POLE 188-60 ROTTED OFF AT GROUND LINE AND FELL OVER. CREW REQUIRED NEED 4 MEN 2 BUCKET TRUCKS LINE TRUCK 40-4 POLE 2 CROSS ARMS BRACESES 3 STEEL PINS INSULATORS CUTOUT ARRESTER 50KVA # 4 COPPER // OPENED LOOPS AT POLES 188-A-63 & 188-A-449, CLOSED RECL 187-15 AT 0825 (50 CC), CLOSE N.O. 188-B-83 AT 0915 (267 CC) FROM WEEKSBURY/DIST CKT // OPENED REC 187-C-15 AT 1334 TO CLOSE LOOPS //VER/GAH IDC XXXX
9951 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-03-01 13:31 | 2009-03-01 13:41 | 80 | 10 | H52635-1 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BOTH OUT SIDE PHASES ARE OPEN AC PHASE CC 303 PATROLLING LINE//POLE 37830153B00074 HAS BURNED INTO AT THE CROSSARM WILL REQUIRE A 4 MAN LINE CREW AND MANUEL POLE BOTH OUT SIDE PHASES ARE OPEN PATROLLING LINE// OPENED SWITCHES AT POLE 153-84 AT 00:50 AND CLOSED AT POLE 177-287AT 01:05 ALL CUST OUT FROM POLE 84 TO OPEN RECL ENTIRE OUTAG. * 6 PERSON CREW WILL BEGIN AT DAYLIGHT . 126 CC TRANS TO HADDIX/QUICKSAND SEE LOG.3307301 OUTAGE TO SHOW TIE BREAK VER/KEP L3/KEP IDCC TOF1331 2/28 XXXX
9952 | South Williamson | 3411401 | DEWEY | INEZ | 2011-07-12 12:30 | 2011-07-12 19:10 | 2 | 400 | 4532031 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 649-188//REPLACED//RESTORED AT 19:10//COMPLETE//EM//COD 2// VER/DBM IDC XXXX
9953 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2019-02-02 07:35 | 2019-02-02 10:15 | 5 | 160 | 4748211 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse broke on pole37830249A00006,,replace 72kv cutout // restored @ 1015 L3/HFP
9954 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2017-08-10 10:10 | 2017-08-10 11:30 | 10 | 80 | 4246211 | 800 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OUTAGE NECESSARY TO SAFELY REWORK SECONDARY AND REPLACE FAILING EQUIPMENT. 37830247D00331 REPLACED CUTOUT AND BKT. AND SERVICE WIRE ; OPENED AT 10:10 POWER RESTORED AT 11:30 VER/AWD
9955 | Pikeville | 3413402 | GARRETT | LACKEY | 2022-05-31 21:41 | 2022-06-01 11:00 | 1 | 799 | 4990721 | 799 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 7200 XFM on pole 135-130.// Customer said truck can be backed to pole. Released by crew 074S11// REPAIRS MADE ON AT 11:00
9956 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2020-07-26 16:06 | 2020-07-26 18:00 | 7 | 114 | 4234731 | 798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arresteron38830703000044, transformer did not serve anything lifted hot tap..re fused line fuse on 40 back on at 18.00
9957 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-05-14 15:39 | 2011-05-14 20:05 | 3 | 266 | 4091581 | 798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN 19.9KV CUTOUT....NEED ONE MAN AND CUTOUT, CANNOT GET BUCKET TO POLE..P.HICKS
9958 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2021-07-08 12:54 | 2021-07-08 19:33 | 2 | 399 | 4873421 | 798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva txmf 7200, no trucks but can get SXS to pole. crew required Released by crew 078S11///replaced XFMR///Complete BR 38830549D40162
9959 | South Williamson | 3411401 | DEWEY | INEZ | 2018-10-27 02:48 | 2018-10-27 09:27 | 2 | 399 | 4331531 | 798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Dispatched in accordance with KYPCo Late Night Callout Guidelines. I dont have a 19.9 arrester, so I cut it in the clear. Power restored.//MADE AED
9960 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2010-04-10 10:04 | 2010-04-10 14:30 | 3 | 266 | 61898-1 | 798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNED UP...CHG CUTOUT//VER/CRB IDC XXXX
9961 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-08-16 08:02 | 2009-08-16 10:15 | 6 | 133 | 59360-1 | 798 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 10:15 COD-6 ISO LF 37830445000022 L3/HFP IDC XXXX
9962 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2014-06-13 20:33 | 2014-06-14 09:50 | 1 | 797 | 4089251 | 797 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | LOOKS LIKE BAD UNDERGROUND NEED TEP INSTALLED SAT. TALKED TO CUST RELEASED BY CREW 078S08//CUST OKD THIS//ADD-A-PHASE INSTALLED///FORWARD COPY OF TICKET TO B REYNOLDS TO HAVE PERM. REPAIRS MADE///PWR CK GOOD VER/KEP
9963 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2015-04-09 00:43 | 2015-04-09 14:00 | 1 | 797 | 4293241 | 797 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ILL DISPATCH AT START OF REGULAR SHIFT BAD 19.9 25 KVA XMF NO TRUCKS YARD DOG REQUIRED, 6 WHEELER WOULD PROB BE BETTER ITS SOFT RELEASED BY CREW 078S11.. CREW ON SITE DIFFICULT LOCATION ETR 14:00.. TRANSFORMER REPLACED AND TICKET COMPLETE AT 14:00 AND TICKET COMPLETE.. VER/SEF
9964 | Pikeville | 3421001 | BREAKS | CITY | 2010-05-09 16:11 | 2010-05-09 19:30 | 4 | 199 | 58709-1 | 796 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CREATE AN OPS/IW TO REPLACE THE BAD TRANSFORMER RELEASED BY CREW 074S02//VER/CRB IDC XXXX
9965 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2010-06-15 22:07 | 2010-06-16 04:45 | 2 | 398 | 65857-1 | 796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BROKEN CUTOUT ON POLE 38830070B12286 //VER/CRB
9966 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-03-01 22:57 | 2015-03-02 05:35 | 2 | 398 | 4089491 | 796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 2017 BURNT OFF1147-1060 20T LINE FUSE MAYBE TRUCK TO POLE RELEASED BY CREW 078S08 VER/SEF L3/HFP XXX
9967 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-11-13 08:16 | 2013-11-13 11:35 | 4 | 199 | 4034281 | 796 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR , WE NEED A LINE CREW AND A 7200 - 50 KVA XFMR RELEASED BY CREW 077S12. POWER RESTORED AT 11:35. 11/13/2013. COD-4 VER/HFP L3/HFP
9968 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2019-11-12 06:14 | 2019-11-12 11:15 | 10 | 301 | 4022761 | 796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout, manuel pole, called for help ¦¦ OPENED LINE FUSE ON POLE 37830174C00295 TO REPLACE BROKEN CUTOUT ¦¦ (9 ADD CUST) OFF@ 1020 ON@ 1115
9969 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-11-02 14:41 | 2012-11-02 18:00 | 4 | 199 | 4339561 | 796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSE/////////19.9 25 KVA XFR IS BAD,T HALL GETTING CREW TOGETHER,NOTE NEW FETR,ALSO AN OIL SPILL HERE RELEASED BY CREW 074S06 COD-4 ISO TF 38821081000088 VER/HFP L3/HFP IDC XXXX
9970 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-07-22 06:51 | 2009-07-22 10:10 | 4 | 199 | 57881-1 | 796 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WORK REQ # 30854098 /// 2 BAD CUT-OUTS ON POLE 164-88,A AND C PH, 19.9 40 T REFUSE TRANS, BACK DID NOT CLOSE UNTILL LINE WAS MADE HOT TO TO CHECK VOLTAGE AFTER FIXING CUT-OUT, CREW REQ, RELEASED BY CREW 078S09 ---- COD-4 ISO LF 38830164A00088 L3/HFP IDC XXXX
9971 | Pikeville | 3409502 | BURDINE | LEVISA | 2015-02-20 07:52 | 2015-02-20 11:11 | 4 | 199 | 4051521 | 796 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | TRANSFORMER SECONDARY BUSHING BURNED UP I REPLACED THE CLAMP, AND HAVE THE POWER BACK ON HERE BUT THE TRANSFORMER SHOULD BE REPLACED WHEN WE HAVE THE OPPORTUNITY. VER/HFP L3/HFP
9972 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-09-14 18:05 | 2008-09-15 07:20 | 1 | 795 | 63132-1 | 795 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3002105//HOT TAP LEAD BROKE AT CUTOUT/REPAIRED HOTTAP LEAD VER/ARN IDC XXXX
9973 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-05-11 13:25 | 2008-05-11 17:50 | 3 | 265 | 61085-1 | 795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | BAD INSULATOR ON POLE 223-96. NEEDS CHANGED. ISOLATED LINE AT FUSE POLE 223-75 MADE HOT AT 5;50 //VER/CRB IDCC TON1800 XXXX
9974 | Hazard | 3302704 | HAZARD | KENMONT | 2017-11-21 16:46 | 2017-11-21 17:39 | 15 | 53 | 4593051 | 795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | .....pole 321-6 burnt off, bad cutout,..no power out until opened line fuse 321-2 @1646 to isolate and ground..all power restored @ 17:39 hrs..p.hicks/ ISO 37830321A00002/ COD 15
9975 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-02-22 00:42 | 2019-02-22 12:42 | 6 | 720 | 4841601 | 795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Dispatched in accordance with KYPCo Late Night Callout Guidelines./////bad 19.9 15kv xfm..will need line crew to make repairs..non truck approach. // Line fuse off @ 1215 on @ 1230 // Xfer restored @! 1242
9976 | Whitesburg | 3309102 | WHITESBURG | HOSPITAL | 2016-12-28 10:55 | 2016-12-28 11:10 | 53 | 15 | 4245711 | 795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | OPENING RECLOSER 449-137 TO REPAIR BUSTED INSULATOR AT POLE 425-77 /OPENED 1055 CLOSED 1110// VER/ ADH AJB
9977 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2016-03-25 19:36 | 2016-03-26 00:01 | 3 | 265 | 4882861 | 795 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 TRUCKS OKNO FLAGGER ON MCKENZIE LN RELEASED BY CREW 078S03---CREW ON SITE ---CHANGED 25KVA AND REPLACED CUTOUT---VOLT CK OK---TBL TKT COMP---RMV//COD 3
9978 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-06-03 07:28 | 2019-06-03 14:05 | 2 | 397 | 4418161 | 794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9kv overhead txmf. 50kva. truck ok. Linecrew required. Released by crew 078S11/ crew on site for repairs/
9979 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-12-07 01:49 | 2008-12-07 08:26 | 2 | 397 | 55061-1 | 794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308401/// BAD CSP XFMR *** 1 CC UNTIL ***** AT 0701 SEVICER OPENED LF AT POLE 227-52 TO SAFELY REPLACE TR. ALLL CUST RESTORED AT 08:26 FUSE OUTAGE SHOWN ON 55061-1A VER/KEP L3/KEP IDC XXXX
9980 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-06-16 21:01 | 2008-06-17 10:15 | 1 | 794 | 66192-1 | 794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE BLOWN,CUST HAS GATE OPEN,GENERATOR IN USE,,POLE 247/1600 RELEASED BY CREW 077E01. BAD 15 KVA 19.9 XFMR. CAN USE MATERIAL HANDLER RELEASED BY CREW 077S08 REPLACED TRANSFORMER JKC VER/HFP IDC XXXX
9981 | Pikeville | 3408101 | SALISBURY | PRINTER | 2010-04-03 12:38 | 2010-04-03 19:15 | 2 | 397 | 57913-1 | 794 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15KVA TRANSFORMER ON POLE 1146D47 IS BAD. CUTOUT IS ALSO BAD. NEED TO GO BACK WITH 25KVA. CALLED DALE HE WILL SEND CREW THIS WAY. RELEASED BY CREW 074S11 RELEASED BY CREW 074H03 REPLACED BAD TRANSFORMER , POWER BACK ON AT 19:15 RBW VER/KEP IDC XXXX
9982 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-09-20 00:09 | 2011-09-20 06:45 | 2 | 396 | 4886481 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 2 MEN, MATERIAL HANDLER, 3 - 7200 CUTOUTS AND FLAGGERS.---- POWER RESTORED.//COD 2//ISO// IDCC PN63 CNT1 XXXX
9983 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2018-03-04 07:52 | 2018-03-04 14:28 | 2 | 396 | 4958631 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 7200 c/o broke --crew req--big bucket (use low water crossing ..NOT BRIDGE..)-ds030418 Released by crew 078S01/arrived RM all power on @ 14:28 please close tic RM
9984 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2015-11-04 21:42 | 2015-11-04 23:21 | 8 | 99 | 4410511 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD HOT TAP REPLACED BAD HOT TAP POWER RESTORED KWB// VER/ ADH L3/HFP HFPC FP39830901C35008
9985 | Hazard | 3311103 | STINNETT | WENDOVER | 2012-09-07 16:17 | 2012-09-07 17:45 | 9 | 88 | 4027771 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD L/A ///VER/CRB L/3 CRB IDC XXXX
9986 | South Williamson | 3411401 | DEWEY | INEZ | 2009-10-02 17:25 | 2009-10-02 18:37 | 11 | 72 | 65562-1 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD//VER/CRB IDC XXXX
9987 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-12-09 10:00 | 2010-12-09 10:08 | 99 | 8 | 64754-1 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CONDUCTOR CAME OFF OF INSULATOR//CREWS OPENED "C" PHASE REC IN ORDER TO MAKE REPAIRS //COD 99// VER/DBM IDC XXXX
9988 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-07-29 10:51 | 2009-07-29 11:35 | 18 | 44 | 61026-1 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 404-138,, LOOKED OVER LINE SMALL TREE FELL ON PRIMARY I REMOVED WITH LONG STICK COD-18 38830404000138 VER/KEP L3/KEP IDC FOUND BAD CUTOUT LATER XXXX
9989 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-11-24 22:18 | 2008-11-25 00:30 | 6 | 132 | 51834-1 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308502//POLE 37830222A00282 BURNED INTO FROM POLE FIRE OPENED PRIMARY WITH CLAMP AT POLE 37830222A00255 AT 22:18//REPLACED 7200 CUTOUT AND ARRESTOR//COD 6//ISO 3783022A00255// VER/DBM IDC XXXX
9990 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2014-02-03 13:09 | 2014-02-03 13:27 | 44 | 18 | 4344581 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO FIX TIX 4343151 VER/CRB L3/HFP HFPC CCSCO FEC57 IDCC XXXX
9991 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-11-18 20:59 | 2008-11-18 21:32 | 24 | 33 | H66346-1 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3002105// FOUND SPAN OF HENDRIX DOWN AND WILL HAVE OPEN SWITCHES @ POLE 38830045C45784 @ 2059// THIS INTERRUPTED 24 ADDITIONAL CUSTOMERS// CLOSED SWITCHES BACK IN @ 2132 ALL POWER RESTORED// INITIAL OUTAGE WAS B PHASE TOTAL 86// RELEASED BY CREW 078S07 IDCC DUP TO OPEN SWITCHES XXXX
9992 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-05-18 08:50 | 2011-05-18 11:32 | 10 | 162 | 4108131 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 399-16, BAD CUTOUT ON 399-30 BURNT TOP OF POLE OFF, ISOLATED ON 399-29...CLOSED LINE FUSE AT 10:00, MADE REPAIRS TO POLE 399-30 RESTORED POWER AT 11:32 VER/KEP IDCC STP MISSING XXXX
9993 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2018-03-15 16:00 | 2018-03-15 16:33 | 24 | 33 | 4017721 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | tie wire broke/ had to open fuse/ 1600-1633/ ISO 37830394C00046/ COD 24
9994 | Pikeville | 3411801 | JOHNSCREEK | META | 2012-01-12 07:57 | 2012-01-12 12:21 | 3 | 264 | 4250091 | 792 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1031-46 ABT 2 FT BURNED OFF,OPEND AT 1031-6 AT 07:57.NEED CREW.BELIEVE IT CAN BE LOWERED.DOUBLE DEADEND POLE,COPPER 1 SIDE,ACSR THE OTHER.ALSO AN ANGLE GUY TO LOWER///////MADE NECESSARY REPAIRS AND RESTORED//COD 3// VER/DBM IDCC TOF0622 XXXX
9995 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-02-11 20:59 | 2014-02-11 22:52 | 7 | 113 | 4374701 | 791 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 SECONDARY IS BURNED INTO AT POLE 97-202 FROM LOAD. I AM GOING TO OPEN TRANS. ON POLE 97-202 LONG ENOUGH TO SPLICE CONDUCTORS. I OPENED TRANS. AT 22:35 AND CLOSED IT BACK IN AT 22:52. SEND TO ENG. DEPT. WE EITHER NEED TO CHANGE 1/0 SECONDARY BETWEEN POLES 97-202 AND 97-144 OR RUN A PRI. TAP UP HOLLOW AND HANG TRANSFORMER FOR LOAD PROBLEMS.//COD 2 + 5//EMAILED TO TECH
9996 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2015-09-12 05:34 | 2015-09-12 18:45 | 1 | 791 | 4230461 | 791 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL LOOK AT ON REG. SHIFT PER LATE NIGHT CALLOUT/// WE HAVE A CONNECTION ON XFMR THAT HAS COME APART OR WE HAVE A BAD XFMR. NEEDS MANUAL R/W CREW AND ONE LINEMAN B OR C// BAD XFMR 25KV 19.9. MANUAL RELEASED BY CREW 077S08// CHANGED XFMR 077H18// VER/ ADH
9997 | Pikeville | 3120102 | STANVILLE | TRAM | 2020-03-09 20:10 | 2020-03-09 22:03 | 7 | 113 | 4463641 | 791 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | line crew required.. pole broke at ground. need a 45-4 pole, single phase double dead end, 2-7200 dead end bells, 2 #2 shoes, pole top pin and insulator, 3 clevis, stirrup. cut out , 18 inch bracket. 2 htline .clamps. guy attachment.opened side tap on pole #38831052D00260 @ 20:10
9998 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-05-05 22:55 | 2020-05-06 05:30 | 2 | 395 | 4803951 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 38830404000245 bad 25kva 7200--100of grass level .by trk small material handler and digger so as not to spin--crew req-ds050620 Released by crew 078S01
9999 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2016-08-03 18:12 | 2016-08-04 00:47 | 2 | 395 | 4730141 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200 TRAN --CREW REQ 4X4 BUCKET SEE CUST --DS080316 RELEASED BY CREW 078S01/CREW ON SITE/FETR0130/VEM/WILL NEED TO OPEN LINE FUSE FOR REPAIRS/VEM/REPAIRS MADE AND ALL CUST RESTORED 0047/PLEASE CLOSE TICKET/THANKS/VEM VER/AWD
10000 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2017-08-07 01:35 | 2017-08-07 14:45 | 1 | 790 | 4232121 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DISPATCHED IN ACCORDANCE WITH KYPCO LATE NIGHT CALLOUT GUIDELINES. CREW REQUIRED. TIM HALL IS SENDING CREW. WE WILL BE REPLACING 3 CUTOUTS. RELEASED BY CREW 074S02- CHANGED 3-CUTOUTS AND ARR. REPAIRS HAVE BEEN MADE ON AT 14:45 R RAY/ ISO XFMR 37820241C00104/ COD 1 MD DONE VER/BOW
10001 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-12-02 11:58 | 2009-12-02 14:36 | 5 | 158 | 55940-1 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED HOT LINE CLAMP ON TRANSFORMER BANK IDC XXXX
10002 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2009-03-13 19:13 | 2009-03-13 20:32 | 10 | 79 | 58291-1 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308503//CREWS OPENED UP STEPDOWN TRANSFORMER IN ORDER TO PUT WIRE BACK UP SAFELTY//COD 10//SEE ORDER 58229-1// VER/DBM IDC XXXX
10003 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-07-19 10:32 | 2015-07-19 17:07 | 2 | 395 | 4910471 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ISO 38830122000023/ COD 2/CREW ON SITE/FETR1900/VEM/REPAIRS MADE AND ALL CUST RESTORED 1707/PLEASE CLOSE TICKET/THANKS/VEM/ VER/BOW
10004 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-02-06 15:29 | 2016-02-06 22:04 | 2 | 395 | 4681101 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED THE TRANSFORMER FUSE THAT HAD BROKE. VER/ARN
10005 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-04-12 07:11 | 2013-04-12 08:30 | 10 | 79 | 4002291 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT POLE 37830248B00137 == CHANGED CUTOUT == POWER OK//COD 15// VER/DBM IDCC CNT15, PN141 XXXX
10006 | Hazard | 3310501 | HADDIX | QUICKSAND | 2016-08-17 18:07 | 2016-08-17 20:45 | 5 | 158 | 4805971 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUT OUT ON POLE38830991000034,,,REPLACE CUTOUT VER/CRB
10007 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-01-29 07:48 | 2012-01-29 14:23 | 2 | 395 | 4301681 | 790 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CALL DRT TO HELP--CREW REQUIRED--BAD 350 UG FROM POLE TO PEDASTAL RELEASED BY CREW 078S07/WILL OPEN XFMR TO MAKE REPAIRS/WILL KEEP TRACK OF TIMES/FETR1500/VEM/XFMR OPEN AT 1319/REPAIRS MADE AND POWER RESTORED 1423/PLEASE CLOSE TICKET/THANKS/VEM//COD 2 IDC XXXX
10008 | Pikeville | 3421001 | BREAKS | CITY | 2021-12-06 12:47 | 2021-12-06 15:25 | 5 | 158 | 4154061 | 790 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 220-73///Will be making repairs///Changed bad cutout and restored service @ 15:25
10009 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-10-18 13:37 | 2009-10-18 18:00 | 3 | 263 | 55500-1 | 789 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 19.9KV C/O WILL REPLACE NOW.........C/O REPLACED, AND POWER RESTORED//COD 3//ISO 37830254B00016// VER/DBM IDC XXXX
10010 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2019-02-12 17:37 | 2019-02-12 22:00 | 3 | 263 | 4782571 | 789 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | crew reqd. bucket ok, hot tap broke off buck arm 39831147C14007 feeding 3phase tap, opening xfmer bank on pole 47c4173. xfmers open @ 19:27 Released by crew 078H17/arrived RM replaced bad hottap back on at 22:00 please close tic RM
10011 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2016-11-19 18:47 | 2016-11-19 23:10 | 3 | 263 | 4116131 | 789 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A XFMR CUTOUT WENT BAD AND BURNED A POLE INTO 425-383. NEED CREW AND BIG BUCKET TO MAKE REPAIRS VER/HFP L3/HFP
10012 | South Williamson | 3411401 | DEWEY | INEZ | 2010-03-26 06:47 | 2010-03-26 11:10 | 3 | 263 | 54567-1 | 789 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34409621 // CUTOUT BROKE RELEASED BY CREW 079S01 / CREW ON SITE STARTING REPAIRS TCM// COD-3 VER/HFP L3/HFP IDC XXXX
10013 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-05-08 05:26 | 2015-05-08 12:00 | 2 | 394 | 4402581 | 788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK AT START TIME , BAD XFMR. WILL NEED 15 KVA, 7.2 KV XFMR, CUTOUT AND BRACKET. BUCKET CAN WORK. LAST HSE ON ROAD RELEASED BY CREW 077S02/COD 2// VER/ ADH
10014 | South Williamson | 3411401 | DEWEY | INEZ | 2020-09-01 00:48 | 2020-09-01 07:22 | 2 | 394 | 4411041 | 788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke @ 769-129 making repairs now // repairs made and restored @ 0722
10015 | Hazard | 3310501 | HADDIX | QUICKSAND | 2011-01-01 05:55 | 2011-01-01 12:29 | 2 | 394 | 57492-1 | 788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38258400 // GOT BAD CUTOUT ON POLE # 55-213, GOT WOO MELTON COMMING TO HELP RELEASED BY CREW 077S05 COD-2 ISO LF 37830055000003 VER/HFP L3/HFP IDC XXXX
10016 | Paintsville | 3401103 | FALCON | BURNINGFK | 2021-02-27 05:41 | 2021-02-27 12:15 | 2 | 394 | 4259931 | 788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole #38830901000015have called for 1 man ,material handler & flaggers. complted@ 12:15
10017 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2018-03-30 09:41 | 2018-03-30 16:15 | 2 | 394 | 4154711 | 788 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required 7200 cutout failed on the crossarm possible trk app Released by crew 079H03 repairs made power restored/ ISO 38820989A00131/ COD 2
10018 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-04-27 21:38 | 2017-04-28 10:45 | 1 | 787 | 4689731 | 787 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | HELD TILL AM PER TIM HALL//BAD 15 KVA XFMR IN DIFFICULT LOCATION. ON LEFT ON HILL. CUSTOMER OK WITH REPLACING IN THE A.M. RELEASED BY CREW 076S02/ CREW ON SITE TCM/ ISO 38830833A20614/ COD 1/ VER/BOW L3/HFP XXXHFP
10019 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2013-10-24 08:46 | 2013-10-24 13:08 | 3 | 262 | 4959101 | 786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CREW ON SITE AND GOT THE BUCKET TO THE POLE. RELEASED BY CREW 079S02//COD 3// VER/DBM
10020 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2016-11-18 14:13 | 2016-11-18 18:35 | 3 | 262 | 4110711 | 786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O BROKE 6T LAT--REPLACED C/O--IN AT 18:35--ALLGOOD--DS111816 38830308000016 VER/AWD
10021 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2015-03-26 11:58 | 2015-03-26 14:09 | 6 | 131 | 4230111 | 786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 492-36, REPLACED CUTOUT RESTORED POWER AT 14:09 // COD-6 ISO LF 37830492000036 VER/HFP L3/HFP
10022 | Hazard | 3308001 | JACKSON | S.JACKSON | 2017-06-15 13:24 | 2017-06-15 17:46 | 3 | 262 | 4973341 | 786 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSF ==== NEED LINE CREW 50 KVA 7200 2 BUSHING 120V / 240 V RELEASED BY CREW 077S03. POWER RESTORED AT 17:46/ ISO 38831083C20358/ COD 3/ VER/BOW
10023 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2015-08-08 22:59 | 2015-08-09 12:05 | 1 | 786 | 4113331 | 786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 5KV @ 246-35.CREW REQUIRED//// TRUCKS OK///// NEED 25 KVA RELEASED BY CREW 078S05.. CREW ON SITE ETR 12:00.. NEW ETR 12:30 DIFFICULT LOCATION TO CHANGE/ ISO 38830246000035/ COD 1BAD 5KV @ 246-35.CREW REQUIRED//// TRUCKS OK///// NEED 25 KVA RELEASED BY CREW 078S05.. CREW ON SITE ETR 12:00.. NEW ETR 12:30 DIFFICULT LOCATION TO CHANGE.. TRANSFORMER CHANGED AND CUSTOMER RESTORED AT 12:05/ VER/BOW
10024 | Pikeville | 3403701 | RUSSELLFORK | LITTLE BEAVER | 2017-11-19 14:32 | 2017-11-19 18:54 | 3 | 262 | 4585201 | 786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SEE 4586571/ loop open on pole 197-28 center phase. Crew enroute. opened all thre phases on switch pole 197-27 (14 add cust) at 1821 closed at 1854./ C phase loop burnt open on 37820197000028 feeding both ways (mpa only shows 3 c phase customers)/
10025 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-03-01 21:24 | 2016-03-02 10:30 | 1 | 786 | 4797721 | 786 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | NO TAGS OR GROUNDS/ PRIMARY RISER BROKEN OUT OF TOP OF CUTOUT ON 818C6FEEDING TAP POLE 818C11 NTA CLIMBER NEED TWO MEN TO MAKE REPAIRS IN PRIMARY ZONE RELEASED BY CREW 079H03// VER/ ADH
10026 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2016-07-03 22:43 | 2016-07-04 11:48 | 1 | 785 | 4519531 | 785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSF ==== CUST SAID OK TO CHANGE AT DAY LIGHT MANUAL UP ON HILL ==== ALSO NEED ROW CREW AND 4 MAN LINE CREW RELEASED BY CREW 077S03 POWER RESTORED AT 11:48/ BACK ON/ ISO 37830488000007/ COD 1/ VER/BOW
10027 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2009-08-10 21:34 | 2009-08-11 10:39 | 1 | 785 | 62303-1 | 785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP BROKEN NEUTRAL ON SERVICE-NEED TO RELOCATE SERVICEE DROP--NEED HELP--TALKED TO CUSTOMER WILL WORK IN MPRNING CUSTOMER MB TURNED OFF. ONE CUSTOMER OUT UNTIL TOMORROW. OPENED TR @ 1034 TO CUT WIRE IN CLEAR--BACK ON AT 10:39--RELOCATED CUSTOMERS SERVICE FROM POLE 39831123D47577TO POLE 39831123D47539 RELEASED BY CREW 078S07 COD-5 ISO TF 39831123D47577 L3/HFP IDC XXXX
10028 | Whitesburg | 3312901 | JENKINS | KONA | 2013-04-22 06:03 | 2013-04-22 08:40 | 5 | 157 | 4035201 | 785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SDB / "WILL CHECK AT REGULAR TIME"SDB / WILL CHECK AT REGULAR TIME I HAVE A HOT LINE CLAMP BURNED OFF AT POLE 405-25SDB / WILL CHECK AT REGULAR TIME I HAVE A HOT LINE CLAMP BURNED OFF AT POLE 405-25 . REPLACED CLAMP ///VER/CRB L/3 CRB IDC XXXX
10029 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2013-02-20 11:59 | 2013-02-20 14:36 | 5 | 157 | 4834411 | 785 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN LINE C/O// TRUCK BREAK DOWN WAITING ON GARAGE////C/O CHANGED POWER RESTORED COD-5 ISO PO @ 37830256000041 VER/HFP L3/HFP IDC XXXX
10030 | Hazard | 3302703 | HAZARD | HAZARD | 2020-08-31 21:16 | 2020-09-01 00:32 | 4 | 196 | 4410491 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA XFMR on pole 296-A3-760, 12KV, truck access. Closed the XFMR fuse at 22:00 and it immediately opened back up. // made repairs restored power at 00:32 //cod 4
10031 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-06-05 15:39 | 2008-06-05 16:35 | 14 | 56 | 58395-1 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000902//VER/CRB
10032 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2011-05-03 22:43 | 2011-05-04 05:15 | 2 | 392 | 4005041 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED AND BURNED POLE HALF IN TWO. MADE REPAIRS BUT POLE NEEDS REPLACED. SEND COPY TO CLIFF FREEMAN.//EMAILED TO TECH//COD 2// VER/DBM IDC XXXX
10033 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-05-19 10:09 | 2015-05-19 13:25 | 4 | 196 | 4445071 | 784 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | WILL NEED TO CONTACT CUST BEFORE WE CAN DO ANYTHING TECH IS TRYING TO CONTACT CUST TO DECIDE TO GO OVERHEAD OR UNDERGROUND RELEASED BY CREW 077H14 /// WILL BE REPAIRED ON OPS ORDER 035166486 VER/HFP L3/HFP
10034 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-04-03 04:55 | 2015-04-03 06:33 | 8 | 98 | 4261821 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON POLE 400-33, BAD CUTOUT ON POLE 400-264 XFMR NOT SERVING ANYTHING REMOVED BAD CUTOUT , RESTORED POWER AT 06:33.//COD 8 L3/DKGXXX
10035 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2022-07-22 13:05 | 2022-07-22 14:01 | 14 | 56 | 4549061 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt up/replaced. tre
10036 | Pikeville | 3402003 | KEYSER | MULLINS | 2020-07-01 21:53 | 2020-07-02 01:09 | 4 | 196 | 4101861 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Report of xfmr fire/ fire is out now but xfmr is humming/ Crew required xfmr bad/Report of xfmr fire/ fire is out now but xfmr is humming. XFM fuse on pole 1151-A-325 out on arrival. bad XFM, need line crew, 50KVA XFM and cutout 7200Report of xfmr fire/ fire is out now but xfmr is humming. XFM fuse on pole 1151-A-325 out on arrival. bad XFM, need line crew, 50KVA XFM and cutout 7200.. repairs made and restored at 01:09
10037 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2022-02-26 15:14 | 2022-02-26 18:30 | 4 | 196 | 4548881 | 784 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 40tBroken cutout on pole 38830091A00012, should be able to reach with big bucket. crew requiredBroken cutout on pole 38830091A00012, should be able to reach with big bucket. crew required. Released by crew 078S02 crew on site FETR 18:45 LRM
10038 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-01-31 08:39 | 2016-01-31 13:00 | 3 | 261 | 4661071 | 783 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT AND ARRESTOR HAS FAILED, WILL NEED TWO MEN VER/CRB
10039 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2010-11-05 08:40 | 2010-11-05 09:07 | 29 | 27 | 53083-1 | 783 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 29//OPENED FUSE TO ISOLATE TRANS//OTHER 2 CUST WAS ON ANOTHER TIX//VER/CRB IDC XXXX
10040 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-02-19 22:32 | 2022-02-20 11:35 | 1 | 783 | 4519401 | 783 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout broke on tap up on side of hill , cust has gen runing and is fine for in the morning for crew to come first thing in morning, need a 2 19,9 cutout and change transformer cutout also Released by crew 077S05 // RESTORED @1135
10041 | Hazard | 3303902 | LESLIE | WOOTON | 2009-07-09 20:39 | 2009-07-10 01:00 | 3 | 261 | 52164-1 | 783 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O. NEED 19.9 KV C/O AND ONE MAN. VER/PDP IDC XXXX
10042 | Hazard | 3309302 | VICCO | JEFF | 2015-01-07 23:38 | 2015-01-08 01:05 | 9 | 87 | 4916911 | 783 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE ON SECONDARY SIDE OF TRANSF POLE === REPAIRED === POWER OK RELEASED BY CREW 077S03 VER/KEP L3/HFP XXX
10043 | Hazard | 3303901 | LESLIE | HYDEN | 2016-07-05 10:29 | 2016-07-05 17:00 | 2 | 391 | 4537361 | 782 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | POWER RESTORED/ ISO 37830267000130/ COD 2
10044 | South Williamson | 3411401 | DEWEY | INEZ | 2013-07-18 15:05 | 2013-07-18 19:25 | 3 | 260 | 4550081 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG CONNECTIONS BURNT INTO AT XFMR///RESTORED AT 1925//COMPLETE//EM//COD 3// VER/DBM
10045 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-05-08 22:10 | 2010-05-09 02:30 | 3 | 260 | 58530-1 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C/P SERVICER. 35032175 CUSTOMER COMPLAINING OF DAMAGED APPLIANCES. VER/PDP IDC CHANGED START TIME FROM 2139 XXXX
10046 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-12-22 08:10 | 2010-12-22 10:20 | 6 | 130 | 54982-1 | 780 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TOOK TRANSFORMER OFF 1T 954 AND PUT BACK ON AT 10.20 .6 ALL ELECTRIC ACCOUNTS ON THIS TRANSFORMER.BURNED SEC LEAD INTO.PARTIAL POWER..NEEDS TO HANG BIGGER TRANSFORMER.. VER/TOM IDCC TOF0954 PART POWER XXXX
10047 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2016-07-09 10:15 | 2016-07-09 13:30 | 4 | 195 | 4592351 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | CHANGING TRANSFORMER 39831148B30936/ / COD 4.TIME OFF 10:15, TIME ON 13:30, BADLY MISMAPED, CUST COUNT WRONG! TECHNICHAN NEEDED TO MAKE CORRECTIONS,BLR/ ISO 39831148B30328/ COD 4
10048 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2022-03-23 16:30 | 2022-03-23 20:50 | 3 | 260 | 4663431 | 780 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva xfmer pole 1072-5618, 2 primary bushing. trk ok. call sheriff before taking traffic lights out. Released by crew 078S07/ ISO 39831072C45618/ COD 3
10049 | Pikeville | 3408103 | SALISBURY | MARTIN | 2019-05-17 14:37 | 2019-05-17 17:52 | 4 | 195 | 4282491 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | One fuse blown on 2 pot xfmr bank. will check and refuse..Bad 50 KVA had to open remaining xfmr to isolate @ 14:37.Contacted crew and they are bring XFMR to replace///Changed xfmr power back on @ 17:52
10050 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2022-02-04 16:55 | 2022-02-04 19:05 | 6 | 130 | 4443431 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | restored @ 19:05, broken fuse
10051 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2012-12-21 14:13 | 2012-12-21 17:28 | 4 | 195 | 4501521 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CALLED TREE CREW POLE LEANING NEEDS ANCHOR REPLACED TRUCK TO POLE HOT TAP OFF 94-108 NEED LINE CREW RELEASED BY CREW 078S08 ////VER/CRB L/3 CRB
10052 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2017-06-13 21:20 | 2017-06-14 10:20 | 1 | 780 | 4964491 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === REPLAE CUTOUT AND ARRESTER & T BRACKET === POWER OK/ ISO 37830511000058/ COD 1
10053 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2009-01-01 18:50 | 2009-01-01 21:00 | 6 | 130 | 50682-1 | 780 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3308603// OPEN WIRE SECONDARY BURNED DOWN NEED ONE MAN TO HELP CONNECTION BAD CAUSING SEC TO BURN DOWN CUSTOMER HAS DAMAGES WILL BRING CREW BACK TOMORROW TODO MORE WORK VER/ARN L3/KEP IDC XXXX
10054 | South Williamson | 3411401 | DEWEY | INEZ | 2016-08-17 08:12 | 2016-08-17 08:42 | 26 | 30 | 4799481 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DKM/0754/PAUL MUNCY OPENING LINE FUSE AT 744-A2-44 TO REPAIR BROKEN INSULATOR ON POLE 744-A2-91 ETR 30 MINUTES/// VER/DKM // VER TIME PER VOICE RECORDER = L3/HFP XXXHFP AJB
10055 | Paintsville | 3401103 | FALCON | BURNINGFK | 2012-10-05 15:54 | 2012-10-05 18:30 | 5 | 156 | 4118221 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT ON 876-238. CHANGED CUTOUT AND RE-FUSED 30T ON 876-40. SH//COD 5// VER/DBM IDC XXXX
10056 | Hazard | 3311101 | STINNETT | REDBIRD | 2011-09-19 23:40 | 2011-09-20 12:40 | 1 | 780 | 4886401 | 780 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 1 OF THE HOT CONNECTION BURNED OFF == REPAIRED == POWER OK IDC XXXX
10057 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2018-09-13 11:29 | 2018-09-13 14:05 | 5 | 156 | 4091981 | 780 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | lead burnt off on xfmr secondary side Released by crew 077H14 replaced lead power restored at 14:05
10058 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2016-04-20 20:17 | 2016-04-20 21:35 | 10 | 78 | 4109391 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE LINK APPEARS TO HAVE BROKEN. RESTORED @ 21:35. SH VER/AWD
10059 | Hazard | 3302704 | HAZARD | KENMONT | 2008-01-23 16:18 | 2008-01-23 19:33 | 4 | 195 | 59253-1 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3302704// SERVICER WORKING WITH SWITCHING // XFMR FUSE OUT. REFUSED POWER RESTORED. FUSE BROKE// ISO/FLT - 37830296D10166 COD - 4//// VER/TOM IDC XXXX
10060 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2017-02-08 20:18 | 2017-02-08 21:36 | 10 | 78 | 4372621 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS CUTOUT FAILED ON 954D249 I REPLACED CUTOUT RESTORED POWER AT 21:36 38830954D20249 VER/AWD L3/HFP XXXHFP
10061 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-11-10 04:52 | 2010-11-10 09:12 | 3 | 260 | 54471-1 | 780 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LEAD BURNED OUT OF XFR,WILL REPLACE /////POSSIBLY A BAD CONNECTION AT SEC CONNECTIONS CAUSED PROBLEM,REPLACED LEAD & CONNCTIONS AND RESTORED,ALL OK AFTERWARDS //VER/CRB IDC XXXX
10062 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2008-03-24 20:27 | 2008-03-24 21:32 | 12 | 65 | 60426-1 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000102//OPENED TRANSFORMER ON POLE 46-2054 AT 21:09 TO MAKE REPAIRS// REPLACED BAD SPLITBOLT//COD 12// VER/DBM IDC XXXX
10063 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2016-05-14 10:57 | 2016-05-14 11:57 | 13 | 60 | 4216381 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT GOING BAD ON POLE 426C-87. REPLACED CUT-OUT AND RESTORED POWER AT 11:57. ALSO, FOUND ANOTHER CUT-OUT THAT IS CRACKED ON THIS SAME POLE BUT IT IS FEEDING ANOTHER TAP. WILL REPLACE THIS CUT-OUT ALSO. VER/CRB
10064 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2011-03-24 11:44 | 2011-03-24 14:20 | 5 | 156 | 58790-1 | 780 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND LOOP BURNTED OPEN ON 4/0 SECONDARY, HAVE REPAIRS MADE AND EVERYTHING IS OK AT THIS LOC //VER/GAH IDC XXXX
10065 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-11-05 14:58 | 2014-11-05 19:40 | 9 | 282 | 4702421 | 778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT OFF POLE @ 160-171 NEED LINE CREW NO TRUCK,ISO & GROUNDED & TAG TO BRENT TACKETT @ POLE 160-6 LINE FUSE IN @ 1600 RELEASED BY CREW 078S05,,CREW ON SITE,,ALL REPAIRS MADE,, ALL POWER RESTORED VER/HFP L3/HFP AJB
10066 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2013-07-08 08:56 | 2013-07-08 15:25 | 2 | 389 | 4485631 | 778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA XFMR . DUTY SUPERVISOR NOTIFIED AND CREW IS ENROUTE TO CHANGE IT. RELEASED BY CREW 076S02// CREW ON SITE TCM// CHECKING TO SEE WHICH CAN IS BAD NOW, TCM//CHANGED CAN OUT BACK ON 15:29 ALSO FOUND FUSE OPEN ON POLE 858-294 20 T CLOSED IT IN AT 15:25 LEFT PHASE WITH BACK TO STATION / TCM COD-2 ISO TF 38830858A00296 VER/HFP L3/HFP IDCC TON1529 XXXX
10067 | Pikeville | 3421001 | BREAKS | CITY | 2017-04-26 17:24 | 2017-04-26 23:53 | 2 | 389 | 4685611 | 778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 079H03 BAD TRANSFORMER CREW ENROUTE//COD 2 L3/HFP XXXHFP
10068 | Pikeville | 3408304 | COLEMAN | CALLOWAY | 2015-09-12 08:04 | 2015-09-12 14:33 | 2 | 389 | 4230721 | 778 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ALL OUT 129 BLACKBERRY FORK KIMPER, POLE 37820007A00008, REPLACED CUTOUT AND ARRESTER, ALL WORK COMPLETE / GXJ// VER/ ADH
10069 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-12-05 07:15 | 2016-12-05 09:06 | 7 | 111 | 4164991 | 777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LIFTED HOT TAP @0715 OUTAGEING7 E CUSTS//CUT OUT FAILED AND BURNT OFF TOP OF POLE 1150-280, WILL HAVE TO TAKE CLAMP OFF POLE 1150-26 TO ISOLATE, WILL KEEP TRACK OF TIMES.//NO OUTAGE TILL HOT CLAMP LIFTED PER SERVICER//. TOOK CLAMP OFF POLE 1150-26 @0715, PUT ALL BACK ON @0906. VER/CRB L3/HFP HFPC CDC92
10070 | Hazard | 3303901 | LESLIE | HYDEN | 2021-09-16 20:52 | 2021-09-17 01:11 | 3 | 259 | 4249871 | 777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva 19,9 Released by crew 077S05.. replaced xfmr & cutout restored power at 01:11..
10071 | Cannonsburg | 3000304 | BELLEFONT | ASHLAND TOWN CT | 2011-05-11 06:46 | 2011-05-11 19:43 | 1 | 777 | 4050561 | 777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | POLE 21-527 ARM 8 FT BURNT INTO BY A PHASE B PHASE BLEW REPLACED FUSE NEED ARM CHGD ASAP ALSO 4KV PRI METERING DESTROYED NEEDS JOB WROTE TO REPLACE BYPASSED RELEASED BY CREW 078M01 SEND TO TEC. RELEASED BY CREW 078S08 RELEASED BY CREW 078S09
10072 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2013-04-18 15:13 | 2013-04-18 19:32 | 3 | 259 | 4023001 | 777 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 1077-247.NEED ONE MAN TO HELP. RELEASED BY CREW 074H08CUTOUT BROKE ON POLE 1077-247.NEED ONE MAN TO HELP. REPAIRS MADE AND POWER RESTORED.THIS POLE IS BURNT AT TOP AND NEEDS CHANGED OUT.SEND TICKET TO TIM HALL. ///VER / CRB L/3 CRB IDC NOT SURE OF ACTUAL TIME OFF LEFT AS IS XXXX
10073 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-07-08 20:30 | 2009-07-08 23:44 | 4 | 194 | 63369-1 | 776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, BAD CUTOUT ON HILLSIDE, NEED HELP, CALLING R MARCUM FOR HELP VER/TOM L3/TOM IDC XXXX
10074 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2012-06-05 09:14 | 2012-06-05 15:42 | 2 | 388 | 4883251 | 776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER--ONE CUST--15 KVA--19.9 --- 2 MEN BUCKET--SEND TO JEFF COMBS RELEASED BY CREW 077S10 REPLACED TRANSFORMER AND CHECKED VOLTAGE RESTORED POWER AT 1542 JKC COD-2 ISO TF 37830174C24393 VER/HFP L3/HFP IDC XXXX
10075 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-07-30 10:50 | 2021-07-30 17:18 | 2 | 388 | 4982341 | 776 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15KVA XFMR 7200 Released by crew 078H22 all pwr restored 17:18 please closeticket LRM
10076 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-04-25 16:30 | 2011-04-25 19:05 | 5 | 155 | 64188-1 | 775 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | FOUND ROTTEN POLE, WELL NEED CREW AND TECH TO WRITE JOB TO REPLACE THIS POLE ALSO NEEDS TO BE TAKEN CARE OF TODAY, NEED A 405 POLE EVERYTHING ELSE SHOULD TRANSFER BACK TO NEW POLE, HAS UNDERGROUND ON IT// 40/5------ POWER ON @ 19:05 ADJUSTED TIME OFF TO TIME CREW ARRIVED VER/HFP L3/HFP IDC XXXX
10077 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2012-01-11 09:48 | 2012-01-11 16:15 | 2 | 387 | 4247031 | 774 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | POSSIBLE BAD URD, B REYNOLDS ON WAY TO ASSIST., GOING TI INSTALL POWER TEMP. RELEASED BY CREW 078S05 ///VER/CRB IDC CHANGED COUNT FROM 10 PER CONF CALL XXXX
10078 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-08-18 11:21 | 2010-08-18 13:30 | 6 | 129 | 57573-1 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | HI SIDE FUSE OUT AGAIN ON C PHASE STEPDOWN XFRMR ON POLE 38821136D20079.....PATROLLED LINE..ALL LOOKS OK...WILL RE-FUSE....//....FOUND ARRESTER BLOWN APART ON LOW SIDE OF STEPDOWN...CLEARED IT UP...WILL SEND NOTE TO ENGINEERING.....RE-FUSE STEPDOWN....POWER ON NOW....JRV...08/18/10/VER/CRB IDC XXXX
10079 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2009-10-28 07:48 | 2009-10-28 14:15 | 2 | 387 | 60521-1 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP WR # 32421199 //LINE FUSE OPEN ON POLE 37830259000003 ( 40T FUSE NOT ON MAP) RELEASED BY CREW 074S03 REWORKING POLE ,1600 SOUNDS GOOD R RAY BACK ON AT 14:15 ENTERED MD...HFP L3/HFP IDCC PN155 XXXX
10080 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2010-11-16 09:41 | 2010-11-16 13:59 | 3 | 258 | 56070-1 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP TRANSFORMER LOCK OUT, GOING TO TRY RESET TRANSFORMER STS BAD TRANSFORMER VER/ARN IDC XXXX
10081 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-10-27 10:44 | 2010-10-27 15:02 | 3 | 258 | 65633-1 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 X-FMR ALSO NEED 2 -7200 CUTOUTS-- TRUCK ACCESSIBLE--- AT LUMBER CO. ACROSS FROM WAL-MART.//COD 3// VER/DBM IDC XXXX
10082 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-12-24 19:44 | 2016-12-25 00:02 | 3 | 258 | 4235711 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE L/F OPEN @101-D3-33, PATROLLING. CUT- OUT FAILING AT POLE 101-D3-590, WILL BE CHANGING. ALSO A BAD LIGHTNING ARRESTOR AT POLE 101-D3-590, CUT IT IN CLEAR AND CLOSED L/F @0002. VER/TOM L3/TOM
10083 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2017-12-07 18:12 | 2017-12-07 22:30 | 3 | 258 | 4629281 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required trucks ok 50 kva Released by crew 078S03,repairs made all cust restored @ 2230 please close ticket thanks.bt/ ISO 38830247000060/ COD 3** per servicer only 3 map shows 4 cust
10084 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2010-10-26 22:06 | 2010-10-27 11:00 | 1 | 774 | 65238-1 | 774 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELEASED BY CREW 074S06SERV DROP TO REPAIR,APPEARS BROKEN FOR SOME REASONSERV DROP TO REPAIR,APPEARS BROKEN FOR SOME REASON///////SERVE-IN HEATED UP,BURNED SERV DOWN.REPLACED SERV,ALL OK AFTERWARDS// VER/DBM IDC DCMT XXXX
10085 | Hazard | 3309301 | VICCO | REDFOX | 2022-05-01 17:47 | 2022-05-01 21:00 | 4 | 193 | 4821511 | 772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Secondary Pole 351A-202 is broke. Need 30/6 pole clevis, spool and dd light. Need linecrew. Pole replaced and power restored at 21:00.
10086 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-06-20 13:46 | 2014-06-20 20:12 | 2 | 386 | 4122811 | 772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT TO XFRM BROKEN AND HANGING DOWN ON 174D-394--NEED CUTOUT-- 19.9-- BIG BUCKET MIGHT REACH--SERVICE GOES TO GARAGE AND CUST SAYS HE COULD WAIT A DAY OR TWO IF WE NEED TO DO LATER. RELEASED BY CREW 077M01//COD 2// VER/DBM
10087 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2011-03-09 15:00 | 2011-03-09 21:26 | 2 | 386 | 52285-1 | 772 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830369B00333 IS BURNED OFF AT THE CUTOUT, NEED 3 MAN CREW AND CAN LOWER EQUIPMENT ON THE POLE, THIS IS AT DOUG PENNINGTONS HOME, HE WILL SHOW THE CREW HOW TO DRIVE TO THE POLE. RELEASED BY CREW 077S04 CLOSED FUSE AT 21:26 VER/ARN IDC XXXX
10088 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2016-01-13 17:05 | 2016-01-13 21:22 | 3 | 257 | 4618201 | 771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TWO BUSHING 50 KVA TRANSFORMER IN 120/208 BANK. CENTER CAN WITH CENTER AND RIGHT HAND SECONDARY BUSHING IN USE. CAN TRUCK. REPLACED XFMR AND RESTORED @ 21:22. SH/ ISO 38830785D20590/ COD 3/ VER/BOW
10089 | South Williamson | 3202201 | LOVELY | LOVELY | 2008-06-27 16:57 | 2008-06-28 03:25 | 2 | 628 | 56529-1 | 771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | JRV ON SITE @ 18:53.....LATERAL FUSE OUT ON POLE 38820697C00029.... TOTAL OF 2 CUSTS....WIND/TREE CONTACT....WILL REFUSE....//.....LATERAL FUSE ON @ 19:20.....PICKED UP 1 CUST, SERVED FROM XFRMR ON THAT POLE.... HOWEVER ...XRFMER SERVING BIG ELK FREEWILL BPTS CHURCH IS BAD ON POLE 697C77.....SEND TICKET TO JOEY REED RELEASED BY CREW 079H08 // VER/TOM IDC XXXX
10090 | Hazard | 3309302 | VICCO | JEFF | 2020-01-18 17:37 | 2020-01-18 21:54 | 3 | 257 | 4319271 | 771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced cutout power on 3 custs.
10091 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-02-21 10:10 | 2011-02-21 14:27 | 3 | 257 | 59671-1 | 771 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BROKEN,WILL REPLACE IT AND POSSIBLY THE OTHER TWO ALSO.WILL TRY TO GET BIG BUCKET AND HELP,JOEY REED ENROUTEREPLACED CUTOUT AND ALSO A DAMAGED XFR,RESTORED AFTERWARDS.ALL OK//COD 3// VER/DBM IDC XXXX
10092 | Hazard | 3302703 | HAZARD | HAZARD | 2008-06-22 12:13 | 2008-06-22 16:30 | 3 | 257 | 51780-1 | 771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3302703//7200/120-240 50KVA XFMR BAD RELEASED BY CREW 077S04 REPLACED TRANSFORMER AND CUTOUT AND CLEARED AT 1645 SPACER ( HENDRIX ) CABLE BURNED DOWN ON LIBERTY ST TAKING POWER BACK OFF . JKC & WM // VER/TOM IDC XXXX
10093 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-03-01 11:55 | 2009-03-01 16:12 | 3 | 257 | 52748-1 | 771 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3117601//OPENED FUSE SO CREW COULD SAFELY MAKE REPAIRS VER/KEP L3/KEP IDC XXXX
10094 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2011-07-25 10:42 | 2011-07-25 11:37 | 14 | 55 | 4617561 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON POLE 37830224D00160 VER/KEP IDC XXXX
10095 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2015-02-15 11:40 | 2015-02-15 18:05 | 2 | 385 | 4027591 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 321-49/COD 2/WILL BE CROSING CSX/NOTIFIED AND HAVE PERMISSION TO CROSS ROW/ONSITE PERSONAL ENROUTE TO MEET SERVCIER TO BEGIN WORK/BAD CUTOUT ON POLE 321B-49 , THIS IS FOR RAILROAD . NEED 19.9 CUTOUT & TBRACKET . POLE IS MANUEL & ACROSS TRACKS .BAD CUTOUT ON POLE 321B-49 , THIS IS FOR RAILROAD . NEED 19.9 CUTOUT & TBRACKET . POLE IS MANUEL & ACROSS TRACKS .ONLY 1 CUST. ON XFMR . CLOSED XFMR @ 18:05/UPDATED LOG/COMPLETED R/R PROCEDURE SHEET// VER/ ADH L3/HFP XXX
10096 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2009-01-24 00:24 | 2009-01-24 01:34 | 11 | 70 | 59544-1 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3400302 -X FMR FUSE MELTED WILL REPLACE. //VER/GAH ADDED CUSTOMER FROM 59545 L3/KEP
10097 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-09-05 06:00 | 2011-09-05 07:50 | 7 | 110 | 4814271 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-2150 CUTOUT FELL APART 30T LINE FUSE REPAIRED IDC XXXX
10098 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2015-04-20 21:40 | 2015-04-20 22:50 | 11 | 70 | 4345081 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED ON 38830760D00341. OPENED LINE FUSE 38830760D00008 @ 21:40 TO REPLACE.//NO OUTAGE TIL L/F WAS OPENED//XFMR CUTOUT FAILED ON 38830760D00341. OPENED LINE FUSE 38830760D00008 @ 21:40 TO REPLACE. REPLACED CUTOUT AND CLOSED LINE FUSE 760-8 @ 22:50. SH RELEASED BY CREW 076S02 VER/CRB L3/HFPXXX
10099 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2018-05-14 06:56 | 2018-05-14 09:30 | 5 | 154 | 4345611 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout changed, all power restored at 09:30
10100 | Hazard | 3303902 | LESLIE | WOOTON | 2021-03-25 12:41 | 2021-03-25 15:15 | 5 | 154 | 4373361 | 770 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Opened transformer @ 14:15 to make repairs to connection. Closed @ 15:15
10101 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-02-22 06:58 | 2008-02-22 08:08 | 11 | 70 | 66135-1 | 770 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3000801///#4 COPPER OPEN WIRE CREW REQUIRED NO TRUCKS 1 SPAN RELEASED BY CREW 078S03//VER/CRB IDC XXXX
10102 | Hazard | 3309302 | VICCO | JEFF | 2012-12-05 03:45 | 2012-12-05 10:10 | 2 | 385 | 4443201 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK AT REGULAR WORKTIME AS PER SET GUIDELINES // BAD TRANSFORMER, CREW ENROUTE. === POWER RESTORED. //VER/CRB L/3 CRB IDC XXXX
10103 | Pikeville | 3411801 | JOHNSCREEK | META | 2011-07-12 22:13 | 2011-07-13 11:03 | 1 | 770 | 4538101 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN,WILL REPLACE,ALSO TREE CREW ENROUTE TO CUT PATH TO POLE,POSSIBLY 2 POLES TO CUT AROUND//////REPLACED CUTOUT AND RESTORED AFT ROW WAS CUT.//VER/CRB IDC XXXX
10104 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2015-06-20 11:06 | 2015-06-20 13:40 | 5 | 154 | 4616211 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE//MAKING REPAIRS//CUTOUT REPLACED//RESTORED AT 13:40//COMPLETE//EM// VER/ ADH
10105 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-05-01 09:50 | 2016-05-01 11:00 | 11 | 70 | 4149321 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/KEP
10106 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-02-09 16:58 | 2021-02-09 18:15 | 10 | 77 | 4952871 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | B PHASE FUSE OUT ON POLE 786-2 Line fuse cutout failed. Replacing. Replaced cutout and restored @ 18:15. sh
10107 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-12-22 19:02 | 2008-12-22 19:57 | 14 | 55 | 62804-1 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3308502// == ARRESTOR WENT BAD == CUT IN CLEAR ==//COD 14// VER/DBM L3/KEP IDC XXXX
10108 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2012-10-29 18:35 | 2012-10-30 01:00 | 2 | 385 | 4187181 | 770 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFORM ON 478-205 SMELLS OF BURN OIL NEED 7200 15 KVA ,CUTOUT AN ARR. RISER OK POLE RT. BESIDE RD . LINE CREW REQ.//1 MORE CUST ON TRANS //MADE MDC IDC XXXX
10109 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-07-10 20:18 | 2011-07-10 23:30 | 4 | 192 | 4501071 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO REPLACE 25 KVA CSP TRANSFORMER AT POLE 38831151D00102. CC= 4. IDC XXXX
10110 | Pikeville | 3401001 | ELWOOD | DORTON | 2015-04-22 16:44 | 2015-04-22 21:00 | 3 | 256 | 4355771 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE ON 37830238000019 IS OUT AS IS XFR F ON 238-142//////RE-FUSED 238-19 AT 18:24/////RE-FUSED 142,BAD 15 KVA XFR,NEED 25 19.9,MAT HANDLER,1 A LINEMAN/////////REPLACED XFR AND RESTORED,ALL OK AFTERWARDS//MDC MADE VER/CRB
10111 | Hazard | 3310502 | HADDIX | CANOE | 2010-01-01 20:12 | 2010-01-02 09:00 | 1 | 768 | 56278-1 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | ACROSS CREEK-LEAD BURNT INTO WILL NEED ANOTHER MAN-I WILL CALL ONE AND BE BACK 1ST THING TOMORROW-SMALL HOME-COAL HEAT --CUSTOMER OK--JIM COD-1 VER/HFP L3/HFP IDC XXXX
10112 | Hazard | 3307301 | BULAN | ARY-HEINE | 2019-08-13 08:45 | 2019-08-13 10:53 | 6 | 128 | 4877761 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | fuse broke
10113 | South Williamson | 3200302 | BELFRY | TOLER | 2010-06-12 09:29 | 2010-06-12 11:05 | 8 | 96 | 60617-1 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFRMER FUSE OUT AS PREDICTED....NO TREES NEAR.....SECONDARIES ALL LOOK GOOD TOO....WILL RE-FUSE...//....NO FAULT HERE....FUSE TAIL JUST BROKE FROM DETERIORATION....REPLACED CUTOUT DOOR & RE-FUSED....POWER ON....JRV...06/12/10//COD 8// VER/DBM
10114 | Paintsville | 3401102 | FALCON | SALYERSVI | 2014-04-21 17:44 | 2014-04-21 22:00 | 3 | 256 | 4623111 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XMFR GETTING 99 VOLTS PHASE TO GRD.ON ONE SEC. BUSHING..123 VOLTS ON THE OTHER..TALKED TO ALL 3 CUST OFF THIS XFMR, OK TO CHG TOMORROW..SNEND COPY TO TIM MILLER. TRUCK ACCESSIBLE 50 KVA XFMR NEED FLAGGERS.. //TRANSFORMER WILL BE REPLACED 04/21/14 ON OPS ORDER # 038456103 /// COD-3 ISO TF 38830875A00122 VER/HFP L3/HFP
10115 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-06-25 15:23 | 2009-06-25 15:29 | 128 | 6 | 59766-1 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | VER/HFP CREW OPENED RECLOSER TO ENERGIZE BYPASSED REGULATOR L3/HFP IDC XXXX
10116 | Pikeville | 3401001 | ELWOOD | DORTON | 2009-12-26 09:07 | 2009-12-26 11:15 | 6 | 128 | 64231-1 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUTOUT WAS BURNED UP ON POLE 287-16. I CHANGED CUTOUT.
10117 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-03-20 06:00 | 2011-03-20 09:12 | 4 | 192 | 56019-1 | 768 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 0600 ETA, WIRE BURNT DOWN ACROSS ROAD TO ADJACENT BUILDING, OPENED XFMR TO DE-ENERGIZE WIRE, GOT WIRE OUT OF ROAD AND CALLED FOR HELP0600 ETA, CLEARED WIRE OUT OF ROAD AND CALLED FOR HELP, OPENED XFMR UNTILL SECONDARY CAN BE PUT BACK//COD 4// VER/DBM IDC CHANGED POLE NUMBER FROM 38 XXXX
10118 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2010-08-16 16:10 | 2010-08-16 17:09 | 13 | 59 | 56587-1 | 767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED FUSE IN ORDER TO MAKE REPAIRS TO A POLE IN ORDER 56504-1 // COD 13// VER/DBM IDC XXXX
10119 | Hazard | 3303901 | LESLIE | HYDEN | 2013-10-28 22:33 | 2013-10-29 11:20 | 1 | 767 | 4971371 | 767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PER JAMES GILLEY THIS A BAD XFMR//PER DUTY SUPERVISOR TIM SMITH, WILL GET CREW ON THIS IN THE MORNING//RELOCATED SECONDARY AND SERVICE TO ANOTHER XFMR AND WILL RETIRE BAD XFMR IDC XXXX
10120 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2014-01-02 12:16 | 2014-01-02 13:15 | 13 | 59 | 4218741 | 767 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED ON 809-404 AND BLEW LINE FUSE 809-402. REPLACING. RESTORED @ 13:15. SH VER/SEF IDC XXXX
10121 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-01-21 09:07 | 2010-01-21 15:30 | 2 | 383 | 57116-1 | 766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMERREPLACED TRANSFORMER IDC XXXX
10122 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-10-12 23:37 | 2022-10-13 06:00 | 2 | 383 | 4021471 | 766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke Line fuse cutout at pole 216-11,Will be making repairs..Restored at 06:00..
10123 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-10-08 06:46 | 2019-10-08 12:35 | 4 | 349 | 4117381 | 766 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 38830223000096 ROTTED OFFKY DDC TAGS & GNDS DOL 960779 ¦¦/tagged to bob tackett/line fuse back in at 0905 hrs/will need side by side LAST CUST ON @ 1235 L3/HFP
10124 | Hazard | 3311102 | STINNETT | BEECH FORK | 2009-04-03 10:47 | 2009-04-03 13:20 | 5 | 153 | 64581-1 | 765 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | 3311102// SCADA INDICATES STATION OUTAGE HERE @ 10:47 // BUS REG BURNED UP ON PH 1 VER/KEP L3/KEP IDCC TOF1320 XXXX
10125 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-11-08 09:55 | 2011-11-08 11:20 | 9 | 85 | 4058781 | 765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I REPLACED BAD CUTOUT AND REFUSED XFMR AND LINE FUSE COD-9 ISO LF 37830378B00033 VER/HFP L3/HFP IDC XXXX
10126 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2010-11-01 13:05 | 2010-11-01 14:30 | 9 | 85 | 50670-1 | 765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CREW OPENED FUSE TO SAFELY MAKE REPAIRS ON ORDER 50540 OFF AT 13:05 BACK ON AT 14:30 VER/KEP L3/KEP IDC XXXX
10127 | Hazard | 3303903 | LESLIE | HALSFORK | 2017-07-13 15:20 | 2017-07-13 16:11 | 15 | 51 | 4113751 | 765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STRANDS BROKEN IN PRIMARY CALLING FOR HELP. NO OUTAGE AT THIS TIME/// GREG SHOUSE & CREW TO REPAIR LATER THIS AFTERNOON/ 1520-1611/ ISO 37830362000237/ COD 15/ VER/BOW
10128 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-05-04 18:12 | 2009-05-04 19:03 | 15 | 51 | 53464-1 | 765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3008701//MAKING REPAIRS ON ORDER 51360-1//COD 15//VER/CRB
10129 | Pikeville | 3308404 | BECKHAM | PIPPA PASSES | 2018-07-23 22:21 | 2018-07-23 22:36 | 51 | 15 | 4845131 | 765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Opened recloser on 37830231A20329 to safely replace cutout on order 4841441.//cod 501
10130 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-02-20 15:42 | 2015-02-20 18:15 | 5 | 153 | 4057661 | 765 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG BURNT INTO MAKING REPAIRS,REPAIRS MADE ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/HFP L3/HFP
10131 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-11-19 19:55 | 2022-11-20 00:10 | 3 | 255 | 4163111 | 765 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad XFM on pole 37830017000019.//10 KVA 7200. Released by crew 074S11Bad XFM on pole 37830017000019.//10 KVA 7200.//Restored @ 00:10
10132 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2020-02-04 11:00 | 2020-02-04 15:15 | 3 | 255 | 4360771 | 765 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Connection on pole 424-203 partial burnt in two. Re-squeezed connections on pole. Transformer on pole 424-203 opened from 14:47 to 15:15
10133 | Hazard | 3303902 | LESLIE | WOOTON | 2018-08-15 18:50 | 2018-08-16 01:12 | 2 | 382 | 4958111 | 764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 19.9 cutout on pole 366-9 need one man and big bucket. all restored @ 01:12 hrs. p. hicks//cod 2
10134 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-04-18 18:04 | 2020-04-18 21:15 | 4 | 191 | 4718491 | 764 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced burnt cutout gate power restored at 21:15
10135 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2014-09-04 08:50 | 2014-09-04 15:12 | 2 | 382 | 4462011 | 764 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND SERVICE IS SHORTED OUT. I CALLED TIM HALL AND HE SAID HE WOULD SEND A CREW. TRANS. POLE IS 37820097000223. RELEASED BY CREW 074S01// INSTALL ADD A PHASE AND RESTORED POWER AT 15:12. TIM MCCOY RELEASED BY CREW 074H10 VER/ARN
10136 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2018-05-10 20:52 | 2018-05-11 09:35 | 1 | 763 | 4334861 | 763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | broken neutral. in sd. meter pulled work in am Released by crew 078S07
10137 | Hazard | 3311101 | STINNETT | REDBIRD | 2019-12-29 22:12 | 2019-12-30 10:55 | 1 | 763 | 4191381 | 763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad deadend insulator on pole 555-7. manual pole need line crew//hold until daylight per Tim Smith //cod1//
10138 | Hazard | 3303902 | LESLIE | WOOTON | 2016-01-27 20:46 | 2016-01-27 22:35 | 7 | 109 | 4655201 | 763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED 7200 CUTOUT// VER/ ADH
10139 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2022-01-07 20:46 | 2022-01-07 22:35 | 7 | 109 | 4322471 | 763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replaced cutout and restored at 22:35. sh//cod 7
10140 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2012-02-16 21:17 | 2012-02-17 10:00 | 1 | 763 | 4354371 | 763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO ONE AT HOME OR LIVING IN HOUSE. CUSTOMER WOULD NOT ANSWER EITHE NUMBER ON TICKET. CALLED N.E. AND IT WAS DECIDED SINCE THIS WAS A MANUAL JOB IT WOULD BE HELD UNTIL TOMORROW. NEED 19.9 CUTOUT AND A COUPLE OF MEN OR CREW - NO TRUCK ACCESS//COD 1// VER/DBM IDC XXXX
10141 | Hazard | 3308502 | BONNYMAN | HAZARD | 2020-08-11 00:45 | 2020-08-11 13:28 | 1 | 763 | 4308611 | 763 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called csutomer neither numbers work. bad 25 kva 7200 xfm. truck acc. crew on the way Released by crew 077S10...comp.,xfmr replaced
10142 | Pikeville | 3410602 | E.PRESTON | LANCER | 2012-03-05 07:58 | 2012-03-05 12:12 | 3 | 254 | 4548591 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANS. CUTOUT IS BURNED UP AT POLE 955-226. WE ARE GOING TO CHANGE CUTOUT. WE CHANGED CUTOUT. //VER/CRB IDC XXXX
10143 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2016-05-11 08:41 | 2016-05-11 12:55 | 3 | 254 | 4198291 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT-AND ARRESTOR TRUCK OK CREW REQ. DUE TO SPACING AND APPROACH DISTANCE38830021B12056/CREW ON SITE/FETR1315/VEM/REPAIRS MADE AND ALL CUST RESTORED 1255/VEM/ ISO 38830021B12056/ COD 3/ VER/BOW
10144 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-07-15 06:21 | 2010-07-15 10:35 | 3 | 254 | 50418-1 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WRONG POLE #, CORRECT TRANSFORMER POLE IS 38830206C04057, BROKEN CUTOUT IN APPROACH DISTANCE, CREW REQUIRED, TRUCK OK RELEASED BY CREW 078S05//MADE A MD//VER/CRB IDCC PN4041 XXXX
10145 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2021-07-01 15:04 | 2021-07-01 19:18 | 3 | 254 | 4837761 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one hot lead of the open wire secondary burned its self in the clear on pole 965A-62.the hot side of it was being held by a hot lead off a flying tap..opened the transformer fuse on pole 965A-62 @ 18:17.to cut trees and make repairs..closed fuse on pole 965A-62 in @ 19:12
10146 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-12-08 12:24 | 2013-12-08 16:38 | 3 | 254 | 4116071 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | # 4 AL PULL INTO ROTTEN WIRE ON POLE 28-36 AND GOT PRIMARY DOWN RELEASED BY CREW 077S05 VER/SEF L3/HFP
10147 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2020-10-22 17:18 | 2020-10-22 19:25 | 6 | 127 | 4577141 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @22-31, checking. Found a bad cutout on a inactive trans. @22-251, got it removed, closed L/F back in @1925.
10148 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2022-01-04 20:50 | 2022-01-05 03:11 | 2 | 381 | 4303661 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | secondarys burnt up 350 riser needs high press to fix correctly// send to bryan ramey Released by crew 078S09///repairs complete///BR//cod 2
10149 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-05-07 10:11 | 2017-05-07 14:25 | 3 | 254 | 4764311 | 762 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANS//REPLACED 1425 VER/CRB
10150 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-02-22 11:39 | 2012-02-22 18:00 | 2 | 381 | 4478811 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | WE MADE REPAIRS ON SERVICE DROP EVERYTHING OK //VER/GAH
10151 | Pikeville | 3413401 | GARRETT | GARRETT | 2014-04-27 22:37 | 2014-04-28 11:19 | 1 | 762 | 4640001 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | CUSTOMER SAYS AFRAID OF POLE CATCHING ON FIRE.. OPENED TRANSFORMER AT 23:30 TO REMOVE SLACK FROM GUY WIRE . GUY WIRE CONTACTED TRANSFORMER RISER AND BLEW FUSE BUT DOOR DID NOT OPEN BURNING DOOR . GUY WIRE IS RUSTED APART UNDERGROUND AND IS TOO HIGH ON POLE TO REMOVE WITHOUT LINE OUTAGE . NEED NEW ANCHOR INSTALLED MONDAY AM . REMOVED ENOUGH SLACK FROM GUY WIRE TO REFUSE TRANSFORMER TEMPORARILY VER/HFP L3/HFP
10152 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-10-04 12:05 | 2011-10-04 14:12 | 6 | 127 | 4946281 | 762 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | DENSILS IS COMING TO USE BIG BUCKET TO REPLACE SOME CONNECTIONS/DENSIL WHEELER HERE ALSO///VER/CRB IDC XXXX
10153 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2015-07-02 06:50 | 2015-07-02 07:30 | 19 | 40 | 4707731 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 69-4743 BAD LA NO TRUCK TO POLE POLE 69-4741 20T LINE FUSE/ ISO 38830069C24741/ COD 19
10154 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2014-03-17 13:37 | 2014-03-17 13:57 | 38 | 20 | 4502421 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PAUL OPENING LINE TO REPLACE BAD HOT LINE CLAMP VER/SEF L3/HFP IDC XXXX
10155 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-08-04 12:45 | 2009-08-04 15:55 | 4 | 190 | 55551-1 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP REPLACED TRANSFORMER. COD-4 L3/HFP IDC XXXX
10156 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-03-26 08:19 | 2016-03-26 09:35 | 10 | 76 | 4883201 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED BAD CUTOUT DOOR/ ISO 38830182B22516/ COD 10/ VER/BOW
10157 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2022-07-01 22:10 | 2022-07-02 04:30 | 2 | 380 | 4359741 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | hold for daylight per duty supervisor //..broke cutout on pole 1111D-5..climbed and changed cutout on pole 5..got the transformer fuse on pole 1111D-5 back in at 04:30//cod 2
10158 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2013-08-08 17:28 | 2013-08-08 20:00 | 5 | 152 | 4637221 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | PATROLING LINE--PRIMARY OFF INSULATOR//COD 5// VER/DBM IDC XXXX
10159 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-01-17 11:59 | 2011-01-17 13:15 | 10 | 76 | 61868-1 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 842-5//ARRESTOR BROKE ON POLE 842-33 HITTING T-BRACKET//GOING TO CUT IN CLEAR//ALREADY HAS ARRESTOR ON XFMR//RESTORED AT 13:15//COMPLETE//EM COD-10 ISO LF 38820842A00005 VER/HFP L3/HFP IDC XXXX
10160 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2015-06-12 14:25 | 2015-06-12 16:57 | 5 | 152 | 4559851 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSF === NEED LINE CREW AND BIG BUCKET 50 KVA 19.9 TRANSF CUTOUT AND T BRACKET === RELEASED BY CREW 077S03BAD 50 KVA TRANSF === NEED LINE CREW AND BIG BUCKET 50 KVA 19.9 TRANSF CUTOUT AND T BRACKET === CHANGED TRANSF POWER OK// VER/ ADH
10161 | Paintsville | 3401802 | INDEX | HOSPITAL | 2020-10-11 07:48 | 2020-10-11 10:20 | 5 | 152 | 4543841 | 760 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 1 cutout has failed on 2 pot xfmr bank. I will replace///Replaced failed cutout and restored @10:20
10162 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2012-11-09 08:58 | 2012-11-09 10:07 | 11 | 69 | 4376241 | 759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | NEED CREW,#4 COP PRIM DN AT 1126-141 RIGHT OUT FRM MAIN 3-PHASE LINE,FUSE IS OUT,MIGHT OUGHT TO HAVE HELP TO WATCH TRAFFIC(EDGE OF ROAD) RELEASED BY CREW 074S06 ///VER/CRB L/3 CRB IDC XXXX
10163 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2022-03-07 21:32 | 2022-03-08 01:45 | 3 | 253 | 4586931 | 759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | line fuse out on pole 941C3-489.pole top burned off on pole 941C3-490..one span of primary down..i have some material on the way and i will be getting pole scabbed off so i can put primary back up. made all my repairs and got 12T line fuse on pole 941C3-489 back in at 01:45
10164 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2012-03-13 08:17 | 2012-03-13 12:30 | 3 | 253 | 4574171 | 759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR WILL NEED CREW. WE CHANGED XFMR COD-3 ISO TF 37830402C00102 VER/HFP L3/HFP IDC XXXX
10165 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-03-20 10:42 | 2018-03-20 10:53 | 69 | 11 | 4030431 | 759 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | related to 4029541//opened fuses in order to replace with solid blades//cod 69 //
10166 | Pikeville | 3408103 | SALISBURY | MARTIN | 2022-06-27 18:41 | 2022-06-28 01:00 | 2 | 379 | 4336731 | 758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfmr fuse blown due to vines.//Bad 25 KVA 7200 XFM.//No truck access.//Could use smaller XFMR //cod 2
10167 | Hazard | 3303902 | LESLIE | WOOTON | 2013-05-23 00:22 | 2013-05-23 13:00 | 1 | 758 | 4168001 | 758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT
10168 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-08-22 19:07 | 2014-08-23 07:45 | 1 | 758 | 4406801 | 758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQD. BAD 25 KVA TRUCK TO POLE 38830043B20719..CPS RELEASED BY CREW ..TRANSFORMER CHANGED NEW NUMBERS GE-PO47139-YNA...0LD NUMBERS..HI 3785792707 TIME ON 07:45 VER/CRB
10169 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-06-25 17:26 | 2022-06-25 23:45 | 2 | 379 | 4316441 | 758 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25kva truck ok material handler 268d10292 Released by crew 078S03/ xfmr was good/ power restored @ 2345/ please close ticket/ MLH
10170 | Hazard | 3301101 | CHAVIES | CHAVIES | 2017-08-28 08:42 | 2017-08-28 10:48 | 6 | 126 | 4303581 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | HAD BARE CONNECTION ON CSP TRANSFORMER GET AGAINST TANK OF TRANSFORMER AND LOCK HANDLE OUT/ FRICTION TAPE FAILED EXPOSING WIRE/ ISO 37830172A00269/ COD 6/ VER/BOW L3/HFP XXXHFP
10171 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-01-30 09:54 | 2014-01-30 10:30 | 21 | 36 | H4327111 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 37830563000018 === NEED LINE CREW AND CUTOUT FOR 34.5 === CHANGED CUTOT ==== OPEN LINE AT 9:54 CLOSED AT 10:30 === ALLPOWER ON 5 INITALLY OFF INTERRUPTED 21 @ 0954 ALL ON @ 1030 ENTERED MD DUP IN HOIS VER/HFP L3/HFP IDC XXXX
10172 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-06-21 07:14 | 2018-06-21 09:48 | 8 | 154 | 4632401 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | have isolated xfmr cutout on pole 45-135 will refuse @45182 7 WILL HAVE ALL BUT 1 COUSTOMER OUThave isolated xfmr cutout on pole 45-135 will refuse @45-16. all on but xfmr on 45-135 @08:40have isolated xfmr cutout on pole 45-135 will refuse @45-16. all on but xfmr on 45-135 @08:40. xfmr on pole#135 on @ 09:48 7 out until 0840 // one out until 948
10173 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-11-23 23:28 | 2014-11-24 10:17 | 2 | 649 | 4758621 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TAGGED TO KYDDC GROUNDS PLACED 91-649 15T LINE FUSE POLE 91C332 OPEN, LOOP CUT & GROUND PLACED @ 91C649 TAGGED TO KYDDC FAULT POLE 91C650.CREW REQD. TRK TO POLE.POLE TOP BURNT OFF WILL LOWER ALL ATTACHMENTS AND MAKE REPAIRS // COD-12 ISO LF 38830091C00332 VER/HFP L3/HFP
10174 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2008-07-10 23:28 | 2008-07-11 01:34 | 6 | 126 | 51041-1 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3001201// HAD OPEN WIRE SECONDARY BURNT DOWN// CREW COMING OUT TO HELP VER/PDP IDC XXXX
10175 | South Williamson | 3202201 | LOVELY | LOVELY | 2020-06-13 18:31 | 2020-06-13 21:40 | 4 | 189 | 4014431 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral burned into on service drop//opened xfmr to make repairs//replaced 4/3 drop with 2/3//opened xfmr at 19 :40//restored at 21:40//complete//em // cod 4
10176 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-08-10 22:32 | 2019-08-11 02:44 | 3 | 252 | 4870661 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25kva truck maybe Released by crew 078S03///making repairs///back on at 02:44///complete BR
10177 | Pikeville | 3421001 | BREAKS | CITY | 2010-05-10 11:56 | 2010-05-10 15:05 | 4 | 189 | 59004-1 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR# 35045322 -CUT TREE OFF SEC. CABLE CHANGED ARRESTERS CHANGEING OUT X-FMR NOW R RAY-JOB COMPLTED//COD 4// VER/DBM IDC XXXX
10178 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-01-15 16:21 | 2010-01-15 19:30 | 4 | 189 | 54823-1 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 080S01CUTOUT HAS BROKEN,WILL REPLACE ITCUTOUT HAS BROKEN,WILL REPLACE IT//////REPLACED BROKEN CUTOUT AND RESTORED,ALL OK AFTERWARDS//COD 4// VER/DBM IDC XXXX
10179 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2014-01-27 09:38 | 2014-01-27 13:50 | 3 | 252 | 4316381 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP FOR XFMR, CECIL IS COMMING TO CHANGE BAD CUTOUT RELEASED BY CREW 077S12//COD 3
10180 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2020-08-29 16:58 | 2020-08-29 21:10 | 3 | 252 | 4401141 | 756 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout broke on pole 37830212A00078. Replacedand restored @ 21:10
10181 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2016-04-12 18:00 | 2016-04-12 18:27 | 28 | 27 | 4086361 | 756 | DISTRIBUTION STATION | EQUIPMENT FAILURE | INSULATOR | WHILE SWITCHING SOS 3269 REV 26 AN INUSLATOR FAILED IN THE STATION//EMERGENCY OUTAGE REQUIRED TO REPLACE//SEE DOL CASES 649416 & 649458 // COD 28 AJB
10182 | Whitesburg | 3314401 | MAYKING | ERMINE | 2012-06-12 15:09 | 2012-06-12 16:12 | 12 | 63 | 4907151 | 756 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, GROUNDING | PART POWER ,GROUND BURNT INTO AT XFMR BUSHING *** OPENED AT 1542.TR TO MAKE REPAIRS.PART POWER ,GROUND BURNT INTO AT XFMR BUSHING.. OPENED BANK AT 16:00 MADE REPAIRS RESTORED POWER AT 16:12 IDC XXXX
10183 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2017-10-04 21:07 | 2017-10-05 09:42 | 1 | 755 | 4411061 | 755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUSTOMER IS MAPPED WRONG THEY ARE FEED OFF 501-33 THERE IS A BAD 25 KVA 7200 XFM HOLD TILL AM PER. BOBBY T. RELEASED BY CREW 078H01,REPAIRS MADE ALL CUST RESTORED @ 0942 PLEASE CLOSE TICKET THANKS.BT /// COD-1 ISO TF 38830501000033 VER/HFP L3/HFP
10184 | Hazard | 3301401 | COMBS | COMBS | 2011-09-30 19:44 | 2011-09-30 22:15 | 5 | 151 | 4935831 | 755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA//BRIAN CLEMONS ENROUTE//BAD 25KVA XFMR. NEED ONE MAN AND BIG BUCKET & 25 KVA XFMR 7200 VOLTS. //VER/CRB IDC XXXX
10185 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2010-04-12 13:02 | 2010-04-12 15:33 | 5 | 151 | 62326-1 | 755 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WIRE CONN, FAILED//COD 5// VER/DBM IDC XXXX
10186 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2021-08-06 11:29 | 2021-08-06 14:00 | 5 | 151 | 4011951 | 755 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken xfmr cutout,, changing
10187 | Hazard | 3308001 | JACKSON | S.JACKSON | 2014-10-06 11:42 | 2014-10-06 14:48 | 9 | 186 | 4557441 | 754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOOK CUTOUT OFF ON POLE38831083D30487 AND GOING TO PUT FUSE BACK IN AT 1253 RELEASED BY CREW 077S05//CREW ON SITE // COD-2 ISO LF 38831083D30073 VER/HFP L3/HFP AJB
10188 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2016-06-25 16:38 | 2016-06-25 22:55 | 2 | 377 | 4474421 | 754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 25KVA. TRK TO POLE. FLAGGERS RELEASED BY CREW 078S07.. CREW IN ROUTE.. WAITING ON MECHANIC TO CHANGE FLAT TIRE ON SERVICE TRUCK RELEASED BY CREW 078H22BAD 7200, 25KVA. TRK TO POLE. FLAGGERS RELEASED BY CREW 078S07.. CREW IN ROUTE.. WAITING ON MECHANIC TO CHANGE FLAT TIRE ON SERVICE TRUCK .. CREW ON SITE FETR 2315BAD 7200, 25KVA. TRK TO POLE. FLAGGERS RELEASED BY CREW 078S07.. CREW IN ROUTE.. WAITING ON MECHANIC TO CHANGE FLAT TIRE ON SERVICE TRUCK .. CREW ON SITE FETR 2315.. XFMR CHAN VER/ARN
10189 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2014-06-28 22:31 | 2014-06-29 11:05 | 1 | 754 | 4166521 | 754 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGOUND SERVICE , NEUTRAL BURNT INTO WILL HAVE TO DIG OUT & MAKE REPAIRS IN THE MORNING.WILL NEED 2 MEN. RELEASED BY CREW 077S11BAD UNDERGOUND SERVICE , NEUTRAL BURNT INTO WILL HAVE TO DIG OUT & MAKE REPAIRS IN THE MORNING.WILL NEED 2 MEN. REPAIRED NEUTRAL RESTORED POWER AT 11:05, ONLY CUSTOMER AFFECTED.//COD 1// VER/DBM
10190 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-10-25 19:58 | 2022-10-26 02:15 | 2 | 377 | 4065461 | 754 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm fuse blown///25 KVA 19.9 Xfm is bad///This is no truck///Will need Line crew//Changed bad xfm and replaced cutout and bracket and restored service @ 02:15
10191 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-07-06 23:57 | 2012-07-07 12:30 | 1 | 753 | 4566351 | 753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT ON POLE 38831077D00156  GOING TO TRY FUSE  CUTOUT DOOR BURNT UP, UNABLE TO FIND REPLACEMENT  GOING TO CHANGE CUTOUT  REPAIRS MADE & POWER RESTORED IDC XXXX
10192 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-11-06 08:10 | 2017-11-06 12:21 | 3 | 251 | 4533771 | 753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | b phase transforer cutout broke on pole37830184A00174//replace cutout
10193 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-11-22 12:49 | 2011-11-22 17:00 | 3 | 251 | 4100811 | 753 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ON POLE 400-131 ONLY TWO CUSTOMERS OUT, WILL NEED 25KVA 7200 XFMR & CUTOUT & BRACKET RELEASED BY CREW 077S11. CHANGED X-FMR AND CUT-OUT. RESTORED POWER AT 17:00. 11-22-2011. J.S.B. COD-3 ISO TF 37830400D00040 VER/HFP L3/HFP IDCC PN40 XXXX
10194 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2009-06-28 09:29 | 2009-06-28 15:45 | 2 | 376 | 65794-1 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE APPEARS BLOWN WILL HAVE TO CUT R/W TO REFUSE---- CUT OUT IS BURNED UP WILL NEED ONE MAN AND BIG BUCKET, VINES ALL AROUND POLE WILL CALL DUTY SUP.---CHANGED CUTOUT AND BAD ARRESTER IDC XXXX
10195 | Pikeville | 3408103 | SALISBURY | MARTIN | 2021-11-05 15:22 | 2021-11-05 18:30 | 4 | 188 | 4060971 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Trans. cutout busted here @ pole 1098-C-221, will be making repairs. Pole is very rotten please send to engineering it needs changed out ASAP. Got power restored @1830. pole is very rotten and needs changed out asap no truck access will need back yard machine.// email sent to bill johnson
10196 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-01-22 10:31 | 2020-01-22 13:39 | 4 | 188 | 4328611 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans. fuse open @220-27, checking.Trans. fuse open @22-27, checking. Bad 25kva 19.9 trans., will be changing out.Trans. fuse open @22-27, checking. Bad 25kva 19.9 trans., will be changing out. Got trans. changed out and power restored @1339. L3/HFP
10197 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-07-14 18:49 | 2017-07-15 01:05 | 2 | 376 | 4123911 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO 38831104000040/ COD 2/ VER/BOW
10198 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2015-04-10 01:53 | 2015-04-10 03:27 | 8 | 94 | H4299681 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2-PH OF SPACER CABLE DOWN WILL NEED CREW REQ MAP SHOWS 556 TO MAKE REPAIRS TRUCKS OK IN ALLEY PL.38830045C14435 FAULT RELEASED BY CREW 078S09/OPEN SWITCHES @ 45-C1-4022 TO SAFELY MAKE REPAIRS/APPROX 2 HOUR OUTAGE/VEM/SWITCHES OPEN @0153/VEM/JOB GOING WELL/NEW FETR0345/VEM/REPAIRS MADE AND ALL CUST RESTORED 0327/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP L3/DKGXXX
10199 | Hazard | 3303901 | LESLIE | HYDEN | 2018-10-06 17:00 | 2018-10-06 18:30 | 12 | 90 | 4204171 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | step-down opened @ 1700//cod 12//no outage till then//CLOSED STEP-DOWN IN @ 1749 UP TO TRANS 37830387C00002//COD 4bad cutout on pole 387-2 closed stepdowns at 17:49 closed xfmr bank in at 18:30 L3/HFP
10200 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-04-04 12:42 | 2014-04-04 15:50 | 4 | 188 | 4573751 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER 25 KVA CAN UPGRADE NEED RISER S TO RE-WORK POLE IN BAD SHAPE AT GROUND LINE MAY BE ROTTON CHECK BEFORE WORKING TRUCK TO POLE RELEASED BY CREW 078S09//COD 4// VER/DBM
10201 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2022-06-01 10:19 | 2022-06-01 13:27 | 4 | 188 | 4992301 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open @24-B4-164, checking. Line fuse cutout busted @24-B4-164, will be making repairs. Got cutout replaced and closed L/F back in @1327.
10202 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-10-30 19:47 | 2018-10-30 22:55 | 4 | 188 | 4344411 | 752 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 448-262, made repairs restored power at 22:55.. L3/HFP
10203 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2008-01-03 09:55 | 2008-01-03 12:25 | 5 | 150 | 53183-1 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED CREW TO REPLACE TRANSFORMER RELEASED BY CREW 074S07//3309103//VER/CRB IDC XXXX
10204 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-08-12 17:00 | 2012-08-12 19:30 | 5 | 150 | 4929951 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | R MAYNARD & T GOBLE // TOOK POWER OFF @ 1700REPLACED XFMR BANK. CLOSED @ 19:30. SH COD-5 ISO TF @ 38830785D20214 VER/HFP L3/HFP IDCC PN217 XXXX
10205 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2022-06-14 10:39 | 2022-06-14 11:29 | 15 | 50 | 4104291 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Lf cutout is broke on pole 520-2. Restored at 11:29.
10206 | Whitesburg | 3312901 | JENKINS | KONA | 2015-10-27 17:10 | 2015-10-27 17:40 | 25 | 30 | 4381361 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNED INTO ON POLE 404-52 , I OPENED THE CUTOUT UP AT 17:10 AND MADE REPAIRS AND CLOSED BACK AT 17: 40 TOTAL COD 25 FROM BEGINNING OF OUTAGE VER/CRB L3/DKG AJB
10207 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-02-03 11:15 | 2016-02-03 12:05 | 15 | 50 | 4671831 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LOOP BURNT INTO AT POLE 398-374, OPENED STEPDOWN AT 11:47 TO ISOLATE..//COD 15 FROM BEGINNING OF OUTAGE//LOOP BURNT INTO AT POLE 398-374, OPENED STEPDOWN AT 11:47 TO ISOLATE..REPAIRED LOOP RESTORED POWER AT 12:05.. VER/CRB
10208 | Cannonsburg | 3000601 | GRAHN | PLEASANTV | 2014-09-03 05:00 | 2014-09-03 06:15 | 10 | 75 | 4455641 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/DKG L3/DKG WILL CHECK IF THS IS A DUPLICATE OR OVERLAPPING ANOTHER OUTAGE
10209 | Hazard | 3303901 | LESLIE | HYDEN | 2012-07-08 12:27 | 2012-07-08 18:42 | 2 | 375 | 4597341 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR HAS BEEN OUT 3 TIMES IN ABOUT 3 WEEKS HAD TO OPEN LINE FUSE ON POLE 291-127 DUE TO CLOSE SPACING ON FAULT POLE OPENED AT 17:25 CLOSED AT 18:42//COD 2
10210 | Hazard | 3309301 | VICCO | REDFOX | 2011-07-03 18:51 | 2011-07-04 01:06 | 2 | 375 | 4451541 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER , MANUEL WILL HAVE TO GET MORE HELP REPLACED TRANSFORMER , RESTORED AND CHECKED POWER VER/TOM IDC XXXX
10211 | Hazard | 3303901 | LESLIE | HYDEN | 2014-01-02 10:10 | 2014-01-02 14:20 | 3 | 250 | 4218281 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 19.9 120/240 REPLACED XFMR VER/SEF
10212 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2019-12-19 14:05 | 2019-12-19 18:15 | 3 | 250 | 4170701 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | CREW REQUIRED 207-187 SECONDARY POLE broke ,truck to pole ,tech already called and windstream setting pole ,only 1 customer off Released by crew 078S05 crew on site FETR 18:30
10213 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-06-28 09:35 | 2019-06-28 22:05 | 1 | 750 | 4611271 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | vines growing around xfm. bank on pole 194-243.will cut in clear..bad 19.9 25kv xfm 2 bushing////will need one A man with big bucket to make repairs..due to vines growing up around pri. bushings on xfms on bank..burnt two 25 kva xfms up////please send copy to Cory Farmer to have vines sprayed..
10214 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-10-04 08:15 | 2019-10-04 12:25 | 3 | 250 | 4094131 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | transformer fuse blown will refuse..Bad 25 KVA 19.9 xfm/// Paul Layne is enroute to make repairs/// Replaced bad 25 kva xfm and restored service @ 12:25
10215 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2015-03-02 00:40 | 2015-03-02 01:05 | 30 | 25 | 4089411 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 140-2010 MAYBE BAD 19.9 CUTOUT CALLED CREW RELEASED BY CREW 078S08,,,,,BROKEN CUTOUT.OPENING LINE FUSES TO SAFELY MAKE REPAIR.BLR.. OPENED FUSES ON 140-2009 @ 00:40,CLOSED IN 140-2009 @ 01:05 VER/SEF L3/HFP XXX AJB
10216 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-06-05 08:32 | 2011-06-05 14:47 | 2 | 375 | 4235301 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 078H08 TRAN CUTOUT BROKEN CAUSING LINEFUSE TO BLOW ,CUTOUT CHANGED 15T LINEFUSE CLOSED IN 2 CUST RESTORED//VER/CRB IDC XXXX
10217 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2018-02-21 15:45 | 2018-02-21 22:00 | 2 | 375 | 4869581 | 750 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout broke on pole 524-303. Can use big bucket. line fuse back in at 17:33. Released by crew 078H17,,crew on site..replaced cutout,,all power restored
10218 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2015-04-05 23:01 | 2015-04-06 11:30 | 1 | 749 | 4278721 | 749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200, 25KVA XFMER. TRUCK TO POLE RELEASED BY CREW 078S07////CREW ON SITE////CHANGED BAD 25KVA XFMR/ CUTOUT AND ARRESTOR///VOLT CK GOOD///TBL TKT COMP
10219 | Paintsville | 3401802 | INDEX | HOSPITAL | 2015-01-20 17:08 | 2015-01-20 18:55 | 7 | 107 | H4946911 | 749 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | BAD CONNECTION ON U/G SEC.350.NEED WIRE /PRESS/.TOOK XFMR OFF AT 17.08..BACK ON AT 18.55..HAD TO REMOVE 1 SEC OF CONDUIT..CHG SPLICES INSIDE CONDUIT..2 SPLICES WERE BAD.REPLACED CONDUIT../ ISO 38830654B00408/ COD 12/// PER B BOWERSOCK CUST FROM PED 433 INITALLY HAD PART POWER (5 CUST) & 7 CUST INTERRUPTED WHEN TR OPENED // SEE 4946911 FOR 5 CUST PART OUT // VER/HFP L3/HFP
10220 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-12-16 10:13 | 2009-12-16 16:27 | 2 | 374 | 64711-1 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33099958 // CREW REQUIRED; BAD TRANSFORMER- 25KVA 19.9; NOT TRUCK ACCESSABLE UNLESS MAYBE A HIGHLINE BUCKET; NEED FLAGGERS; RELEASE TO LINE CREW RELEASED BY CREW 078S12/CREW ON SITE/FETR 1715/VEM COD-2 VER/HFP L3/HFP
10221 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-03-18 16:51 | 2016-03-18 19:58 | 4 | 187 | 4862691 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NO CREW REQUIRED REPAIRED SERVICE 38830182B30252 VER/AWD
10222 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2013-12-29 09:51 | 2013-12-29 16:05 | 2 | 374 | 4209391 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 3 MEN BUCKET - CALL HARVEY FOR DETAILS (MAY NEED XFMR AND OR POLE) // SAMMONS & LAYNE & GARRETT40T FUSE OUT DUE TO BAD CUTOUT. NEED 25KVA TRANSFORMER CUTOUT 3 MAN CREW ASPLUNDA CREW. WILL HAVE TO LOWER EVERYTHING ON POLE ALSO ABOUT 3 FOOT OF POLE BURNT OFF ENTERED MD COD-2 ISO LF 37830042D00396 VER/HFP L3/HFP IDC XXXX
10223 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2014-02-05 08:22 | 2014-02-05 14:36 | 2 | 374 | 4354971 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKEN ON POLE 38830525000145  REPLACED CUTOUT AND POWER RESTORED @ 14:36 //VER/GAH
10224 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2017-11-28 07:41 | 2017-11-28 13:55 | 2 | 374 | 4605951 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | need 10 kva xfmr..lightning arrester, cutout, bracket to hang both on. Released by crew 076S01.repairs made back to normal!!!
10225 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2015-02-25 17:52 | 2015-02-26 00:06 | 2 | 374 | 4081751 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 074H17CSP TRANSFORMER IS OPEN /// WILL TRY TO CLOSE BACK INCSP TRANSFORMER IS OPEN /// WILL TRY TO CLOSE BACK IN//// BAD CSP XFRM//// NEED 25KVA 7200 XFRM CUTOUT AND BRACKET/// CAN USE TRUCK NEED 1 MAN//// CHANGED BAD XFM AND RESTORED SERVICE @ 00:06
10226 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2013-11-05 14:43 | 2013-11-05 17:50 | 4 | 187 | 4012541 | 748 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | "C" PHASE FUSE ONLY//COD 4//ARRRIVED FOUND C PHASE LINE FUSE OUT, PATROLLED FOUND BAD L/A ON POLE 1098-3144, OPENED OTHER 2 PHASES 18 @ 1730 ON @ 1750 SEE H4012541 DUP IN HOIS FOR 18 // VER/HFP L3/HFP IDCC FP NULL XXXX
10227 | Pikeville | 3409502 | BURDINE | LEVISA | 2021-08-15 22:22 | 2021-08-16 10:50 | 1 | 748 | 4074321 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Vines grew up into TR & reports Broken bushing on CSP TR at 37830335B00037 25KVA , Cut out & bracket truck accessible Needs crew to make repairs; CREW ON SITE, CHANGED TRANSFORMER C/O AND ARRESTOR, BACK ON AT 10:50
10228 | Hazard | 3301401 | COMBS | COMBS | 2009-02-14 19:00 | 2009-02-14 20:08 | 11 | 68 | 60681-1 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | ASP-ROTTEN POLE NEEDS REPLACED USE 40/4 POLE -POLE TOP-TOP PIN %26 INSULATOR 4 CLEVIS %26 SPOOLS 3 SERVICE RAPS RELEASED BY CREW 074M02 PER DOUG HALL POLE # IS 271-117 COMPLTED CAN BE CLOSED. VER/LDA IDC DONT THINK OUT THE ENTIRE TIME CHANGED START TIME FROM 754 2/12 XXXX
10229 | Hazard | 3310502 | HADDIX | CANOE | 2019-11-08 07:17 | 2019-11-08 10:24 | 4 | 187 | 4010531 | 748 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned up
10230 | Hazard | 3309302 | VICCO | JEFF | 2012-07-16 14:06 | 2012-07-16 18:15 | 3 | 249 | 4739711 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE BURNED OFF == BAD CUTOUT === NEED LINE CREW BIG BUCKET AND A 15 KVA TRANSF AND 45 FT POLE 2 DEAD ENDS FOR 12KV AND CUTOUT == RELEASED BY CREW 077S03 SHOUSE ON SITE EST.TIME 19:30 // COD-3 ISO LF 37830298000004 VER/HFP L3/HFP
10231 | Hazard | 3303902 | LESLIE | WOOTON | 2011-03-23 23:45 | 2011-03-24 03:54 | 3 | 249 | 57864-1 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT POWER ON AS OF NOW ONLY 1 CUST WILL BE AFFECTED WHEN CUTOUT CHANGE WILL HAVE TO CHANGE POLE 40CL4 TALKED WITH CUST AND INFORMED HIM OF WHAT WAS GOING ON RELEASED BY CREW 077S01//LARRY LAWSON WORKING VER/KEP IDC XXXX
10232 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2016-01-02 09:52 | 2016-01-02 11:15 | 9 | 83 | 4581011 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BLOWN,,BROKE FUSE/ ISO 37830175000003/ COD 9/ VER/BOW
10233 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2009-05-25 15:47 | 2009-05-25 19:56 | 3 | 249 | 64146-1 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT//COD 3// VER/DBM IDC XXXX
10234 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2022-04-05 18:52 | 2022-04-05 20:15 | 9 | 83 | 4726131 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout @ 38830182B43686
10235 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-18 12:48 | 2019-06-18 19:50 | 6 | 422 | 4539241 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service drop burnt down here//secondary pole rotten at ground//unsafe to climb//LCS enroute //have new pole set//going to open xfmr on 720-74 to transfer sec.//opened at 18:45//restored at 19;50//complete//em
10236 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-01-12 14:21 | 2009-01-12 17:00 | 13 | 159 | 54492-1 | 747 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28029518 //C PHASE OUT 13 CUSTOMERSPOLE 20-7062 30T OUT BACK ON 15:OO//3000301//POLE 20-7062 30T OUT BACK ON 15:OO BAD TRANS 20-7096 RELEASED BY CREW 078S08/CREW ON SITE MAKING REPAIRS J. HEMLEPP/ XFMER REPLACED & TWO CUSTOMERS BACK IN SERVICE AT 17:00 HRS RELEASED BY CREW 078H05 L3/HFP IDC XXXX
10237 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2014-01-17 12:32 | 2014-01-17 18:45 | 2 | 373 | 4289471 | 746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 6T FUSE OUT DUE TO BAD 10KVA TRANSFORMER. CALLED TIM HALL WILL BE GETTING CREW TO HEAD THIS WAY WITH A 25KVA. CAN USE TRUCK RELEASED BY CREW 074S11 X-FMR.CHANGED OUT TO A 25 BACK ON AT 18:45R RAY VER/CRB L3/HFP IDC XXXX
10238 | Pikeville | 3413401 | GARRETT | GARRETT | 2018-10-22 18:07 | 2018-10-23 00:20 | 2 | 373 | 4311481 | 746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15 kva transformer 7.2kv 120/240 need flagging crew will have to close one lane. May reach it with out tallest bucket, but not sure.
10239 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-11-17 01:49 | 2016-11-17 08:02 | 2 | 373 | 4106191 | 746 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | JOHN HUNT WITH TELECOME REPORTS HIGH VOLTAGE ON RICHARDSON RADIO TOWER. READING VOLTAGE 203 TO LEG TO LEG//CELL PHONE FOR JOHN 304-928-1184/ COMBO LOCK 1399///----BAD 25 KVA 7200 TRAN NBT --CREW REQ RELEASED BY CREW 078S01--CHECK VOLT 139/139/279-ALSO CKD UPSTREAM XFR&REG--CKD OK--OP XFMR 622A2-67 AT 01:49--CANNOT GET TO POLE W/ 6WHEELER WILL NEED ASPLUNDH TO CUT OUT OLD RD BED TO ACCESS P--RMV --CHANGED XFMR--123/123/247V-ON AT 08:02--TBL TKT COMP--RMV/ ISO 38830622A20067/ COD 2/ VER/BOW AJB TOF11/16
10240 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2014-10-22 02:17 | 2014-10-22 14:42 | 1 | 745 | 4651101 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER 25KVA. TRANSFORMER CHANGED OUT BACK TO NORMAL R RAY COD-1 ISO TF 37820151000140// VER/BOW
10241 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-07-29 02:15 | 2016-07-29 04:44 | 5 | 149 | 4704681 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | NO OUTAGE TILL TRANS OPENED @ //SEC POLE 986-99,ROTTED INTO,FELL OVER/////NEED CREW,35C6POLE,SMALL LINE TRUCK IF AVAILABLE,CAN USE MY BUCKET TO WORK POLE//////POWER IS STILL ON AT THIS TIME//////DISCD WIRE TO 986-99 AS CUSTS WERE ALL OVER ITSEC POLE 986-99,ROTTED INTO,FELL OVER/////NEED CREW,35C6POLE,SMALL LINE TRUCK IF AVAILABLE,CAN USE MY BUCKET TO WORK POLE//////POWER IS STILL ON AT THIS TIME//////DISCD WIRE TO 986-99 AS CUSTS WERE ALL OVER IT///////811#1607290003SEC POLE 986-99,ROTTED INTO VER/KEP
10242 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2018-05-19 22:38 | 2018-05-20 11:03 | 1 | 745 | 4380291 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad UG neutral off pole 39831148B10720 behind residence. Need line crew, and power temp. Released by crew 078H04--crew on site---installed add a phase Pwr temp---volt ck good---tbl tkt comp---rmv---only 1 cust Released by crew 078H16
10243 | Hazard | 3309302 | VICCO | JEFF | 2018-03-24 01:10 | 2018-03-24 13:35 | 1 | 745 | 4047081 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. bad cutout on pole 275-246 need 1 man big bucket 7200 cutout Released by crew 077H14
10244 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2022-02-27 16:16 | 2022-02-27 18:45 | 5 | 149 | 4550281 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Lat fuse blown @ 38831121C00091.// Will be patrolling.// Bad arrester.//Replaced cutout also on pole 38831121C00355.//Restored @ 18:45
10245 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-10-21 13:43 | 2014-10-21 16:12 | 5 | 149 | 4649861 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA, 19.9, NEED TO REPLACE WITH 50 KVA PER MIKE LEWIS, NEED 1 MAN AND BUCKET TRUCK....POWER RESTORED. VER/CRB VER/DKG L3/DKGXXXX
10246 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-02-05 15:01 | 2009-02-05 17:30 | 5 | 149 | 55986-1 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401302 - CUST HAS A MINE EQUIP REPAIR SHOP AND WE NEED TO SEND MIKE LASSLO SOMETHING ON THIS WE NEED TO INSTALL LARGER TRANSFORMERS AND A 480/ VOLT SERVICE REPLACED TRANSFORMER//COD 5// VER/DBM
10247 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2017-07-17 19:38 | 2017-07-17 22:07 | 5 | 149 | 4135501 | 745 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER //NO ANSWER CREW REQ, BAD 25 KVA, SINGLE BUSHING, 7200 120/240, RIGHT BESIDE OF ROAD CAN USE TRUCK, RELEASED BY CREW 078S06---CREW ON SITE--CHANGED BAD 25KVA---CK VOLT GOOD---RESTORED PWR AT 22:07---TBL TKT COMP VER/CRB L3/HFP XXXHFP
10248 | Pikeville | 3400702 | DRAFFIN | YELLOWHIL | 2021-11-12 15:58 | 2021-11-12 19:04 | 4 | 186 | 4086271 | 744 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | We have a Trans Lead into at pole 147-A-112,Going to open Trans to make repairs,Will keep up with Time..Opened at 18:25 made repairs and restored at 19:04.
10249 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2008-11-05 12:38 | 2008-11-05 18:50 | 2 | 372 | 62405-1 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 27144936 ///BAD SECONDARY BUSHING ON 3 PHASE 120/240 WYE DELTA BANK--2 CUSTOMERS OUT -BOTH HAVE EQUIPMENT DAMAGE--FRALEYS CREW TO REPLACE TRANSFORMER RELEASED BY CREW 078S07 COD-1// VER/DBM IDC XXXX
10250 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-06-23 17:20 | 2014-06-23 21:28 | 3 | 248 | 4143651 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN//WILL REFUSE/// FUSE APPEARED TO HAVE BROKE//// POWER RESTORED @ 21:28/// COD 3/// VER/BOW
10251 | South Williamson | 3411401 | DEWEY | INEZ | 2009-10-07 02:54 | 2009-10-07 04:27 | 8 | 93 | 57222-1 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD VER/PDP IDC XXXX
10252 | Pikeville | 3413401 | GARRETT | GARRETT | 2016-02-25 17:22 | 2016-02-25 17:34 | 62 | 12 | H4766781 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HOLD ORDER REQUIRED/ENERGIZED FROM POLE 16D-280 TO 16C-53 AT 22:04 , GROUNDS PLACED AT POLE 3783-16C-38, 16C-45 ISOLATED AND TAGGED FOR KY DDC, 300A SWITCHES INSTALLED AT POLE 16C-296 ISOLATED AND TAGGED FOR KY DDC, CLOSED AT POLE 16-53 TO POLE 16-296 AT 02:35 RELEASED BY CREW 074S03 VER/KEP /// VER TIMES PER DOL L3/HFP XXXHFP AJBC TOF 2/24/2016
10253 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2020-10-19 19:08 | 2020-10-20 01:20 | 2 | 372 | 4568891 | 744 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | bad hot leg in underground service. pull in gravel just past drivway Released by crew 078H03,,,located fault in the underground service ,, splicing
10254 | Hazard | 3310502 | HADDIX | CANOE | 2014-01-22 20:40 | 2014-01-23 09:04 | 1 | 744 | 4302401 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CALL CUST AND SHE SAID THE ROADS WERE BAD AND SHE WANTED ME TO COME IN THE MORNING, SEND IT BACK TO ME RELEASED BY CREW 077S05CALL CUST AND SHE SAID THE ROADS WERE BAD AND SHE WANTED ME TO COME IN THE MORNING, SEND IT BACK TO ME STS BAD CONNECTION ON TRANSFORMER VER/HFP L3/HFP IDC XXXX
10255 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-07-25 19:47 | 2012-07-25 23:55 | 3 | 248 | 4829101 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | ONE OF THE HOT CONDUCTORS IN UG SERVICE IS OPEN. OPENED XFMR 833-281 @ 23:40, INSTALLED AUTO-XFMR AND CLOSED XFMR @ 23:55 RESTORING BOTH CUSTOMERS. PLEASE SEND E-MAIL TO TIM HALL TO HAVE UG FAULT LOCATED AND REPAIRED. SH VER/ARN
10256 | Hazard | 3309302 | VICCO | JEFF | 2008-01-03 19:15 | 2008-01-03 20:48 | 8 | 93 | 53351-1 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3309302// BAD CONNECTION//COD 8// VER/DBM IDC XXXX
10257 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2017-05-06 12:14 | 2017-05-06 13:47 | 8 | 93 | 4761541 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAULT POLE 37830139B00003//BAD CUTOUT CAUSED POLE FIRE//SENT TO TECH VER/CRB
10258 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2020-11-23 13:27 | 2020-11-23 15:00 | 8 | 93 | 4718421 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no crew required replaced bad connection
10259 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-04-22 03:13 | 2010-04-22 09:25 | 2 | 372 | 66193-1 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DUTY SUPERVISOR REPORTED WAIT TIL REGULAR WORKTIME TO CHECK FUSE BROKE REPLACED IT//VER/CRB IDC XXXX
10260 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-03-11 01:14 | 2009-03-11 04:20 | 4 | 186 | 57121-1 | 744 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3001202 - BAD 37.5KVA TR REPL.WITH NEW 37.5 //VER/GAH IDC XXXX
10261 | Whitesburg | 3309302 | VICCO | JEFF | 2014-04-16 14:43 | 2014-04-16 15:36 | 23 | 53 | 4612661 | 743 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | RELATED TO ORDER 4606171 - CREW OPENED RECLOSER TO ALLOW THEM TO MAKE UP DEADENDS /// FOUND CONDUCTOR THAT WAS FRAYED // COD-23 ISO OCR 37830396000089 VER/HFP L3/HFP IDCC TOF1443 4/15 XXXX
10262 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-06-24 16:59 | 2009-06-24 18:45 | 7 | 106 | 57157-1 | 742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER, AND LEAD ON THE TAKEOFF POLE HAD COME OUT OF THE HOTLINE CLAMP//COD 7// ISO 37830296C21122// VER/DBM IDC XXXX
10263 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2019-12-07 10:45 | 2019-12-07 12:31 | 7 | 106 | 4133221 | 742 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | opened xfmer on pole 38830045B22603 @ 11:53 to make repairs. repairs made,xfmer back in @ 12:31 pls close. tre//PART POWER FROM BEGINNING
10264 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-12-27 07:03 | 2022-12-27 13:14 | 2 | 371 | 4364871 | 742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25kva 19.9 transformer. Truck accessible Released by crew 077S06.comp ////Replaced TR and restored at 1314.
10265 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2017-12-29 04:49 | 2017-12-29 11:00 | 2 | 371 | 4686941 | 742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Xfm fuse blown will re-fuse/// Bad 25KVA Xfm 19.9 /// can use truck Released by crew 074S02
10266 | Hazard | 3420001 | SOFT SHELL | VEST | 2016-03-31 21:10 | 2016-04-01 09:32 | 1 | 742 | 4012581 | 742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT, REPLACED CUTOUT, POWER RESTORED VER/CRB
10267 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2017-05-04 16:27 | 2017-05-04 18:13 | 7 | 106 | 4746601 | 742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON 916B2 PARTOLLED LINE SAW NO HAZARDS REPLACED CUTOUT AND ARRESTOR ON 916B115 THAT LOOKED LIKE IT MIGHT BE TRACKING OVER RESTORED POWER AT 18:06 38820916B00002 38820916B00115 VER/AWD
10268 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-09-10 20:58 | 2010-09-11 09:20 | 1 | 742 | 65356-1 | 742 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE82-6--30 T---CANT SEE LAST SPAN--BAD 19.9 CUTOUT-482-10---CAN USE BIG BUCKET-1 MAN-LINE FUSE REFUSED,HUNG IN ---NOT CLOSED--55 FT POLE--ALSO CUT SOME TREES--HOLD TIL DAYLIGHT-JIM RELEASED BY CREW 077S06 * WILL DISPATCH CREW AT DAYLIGHT TO MAKE REPAIRS. VER/HFP L3/HFP AJBC CNT1 PER TROUBLE MAN. IDC XXXX
10269 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2020-03-03 15:05 | 2020-03-03 18:56 | 18 | 231 | 4448241 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Line fuse on 1123-1525 open at 15:05, closed @ 15:35. Line fuse open, grounded and tagged to rick morgan at 1123-1606. Pole 1123-1609 broke, laying across roadway. Released by crew 078S02//arrived RM 12 T in @ 18:56 please close tic RM /WOto be wrote
10270 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-02-25 09:03 | 2016-02-25 13:10 | 3 | 247 | 4771591 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37830343C00006 === NEED 2 MEN COUTOUT === MANUEL POLE RELEASED BY CREW 077S03LINE FUSE OUT ON POLE 37830343C00006 === NEED 2 MEN COUTOUT === MANUEL POLE == CHANGED CUTOUT === REFUSED LINE ==== VER/CRB
10271 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2018-01-27 13:54 | 2018-01-27 18:01 | 3 | 247 | 4777061 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | I talked to Tim Hall and he said that we probablyshould upgrade the transformer to a 50 kva today. Will need one LMA, 50 kva/7200, and some 2/0 secondary riser. Opened the transformer at 17:03, and closed in at 18:01./ ISO 38821062D00048/ COD 2/ MD DONE
10272 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-01-17 11:17 | 2020-01-17 15:24 | 3 | 247 | 4315751 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva single bushing 7200xfm..will need one man with big bucket and new xfm. to make repairs.repairs made and restored..
10273 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2015-06-25 20:02 | 2015-06-25 20:41 | 19 | 39 | 4657201 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED WHEN CUTOUT WAS CLOSED ON POLE 38820991D40138 VER/CRB
10274 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2021-04-08 09:33 | 2021-04-08 10:30 | 13 | 57 | 4429631 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required//BROKEN CUTOUT ON POLE 38830247000138
10275 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2014-04-07 08:56 | 2014-04-07 09:53 | 13 | 57 | 4580581 | 741 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE AT POLE 1114-27 FAILED CUTOUT. WILL HAVE TO LOWER EQUIPMENT. OPENED LINE FUSE FOR LEFT FORK AT POLE 1114-6.OPENED RECL @ 0856 //RESTORED AT 09:53 COD-13 ISO OCR 38821114A00006 VER/HFP L3/HFP IDC XXXX
10276 | Pikeville | 3411702 | CEDAR CREEK | IVY COURT | 2022-01-17 12:02 | 2022-01-17 14:30 | 5 | 148 | 4371601 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Line fuse open @37830022000043, checking. Rotten pole #23-214 fell over, only had 1 account that was disconnected on it, we was able to put the wire back up across it, Paul Reed is gonna get a W/O written up to change the pole in better weather, closed L/F @22-43 @1430.
10277 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-07-15 14:35 | 2016-07-15 17:03 | 5 | 148 | 4642951 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SERVICE NETURAL BROKE OUT IN MID SPAN GOT A MAN COMMING TO HELP RELEASED BY CREW 077S05 VER/CRB
10278 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2020-04-08 14:46 | 2020-04-08 16:26 | 32 | 100 | 4573531 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | xfmr fuse out bad cutout on xfer had to open line fuse to isolate opened fuse at 1608 closed @ 1626
10279 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-09-18 15:13 | 2018-09-18 18:18 | 4 | 185 | 4127361 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse cutout on pole 426-637 bad, opened other 2 fuses to isolate at 18:09 replaced cutout restored power at 18:18.
10280 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-07-13 03:26 | 2012-07-13 09:36 | 2 | 370 | 4703591 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR // COD 2
10281 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-06-26 23:49 | 2018-06-27 12:09 | 1 | 740 | 4675551 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | neutral is broke in 192 ft span of 1/0 secondary truck acc. if customer moves car pole 344-19..lc Released by crew 077E07.restored power at 12:09
10282 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-02-12 09:13 | 2015-02-12 15:23 | 2 | 370 | 4009791 | 740 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA UNDER SWUNG XFMR ONLY PUTTING OUT 120 VOLTS ON 1 PHASE & NOTHING ON OTHER. ALSO #4 COPPER NETURAL IS DOWN HERE. WILL NEED 15 KVA 200FT #4COPPER.THIS WILL BE HAND SET. RELEASED BY CREW 074S04 TRANSFORMER REPLACED ON AT 15:23 D SAMMONS VER/CRB L3/HFP XXX
10283 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-03-05 21:55 | 2012-03-06 10:15 | 1 | 740 | 4555031 | 740 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRED BROKEN NEUT MIDSPAN CHECKED VOLTAGE AT HOUSE 125.3 BOTH LEGS// VER/DBM IDC XXXX
10284 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-12-07 15:52 | 2020-12-07 17:55 | 6 | 123 | 4752251 | 738 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENING XFMR TO CLEAN BUSHINGS GETTING VOLTAGES OF 13v ON ONE LEG PUT 120 AT BUSHING OFF@1730 ON@1755 LR- The 1st call of Partial Power came in at 15:52.
10285 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-11-24 16:44 | 2013-11-24 20:50 | 3 | 246 | 4070911 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 67-69 BAD 15KVA NEED 25KVA TRUCK TO POLE SEND TO RAYBURN HOUSE EMPTY RELEASED BY CREW 078S08 VER/TOM L3/TOM IDC XXXX
10286 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-12-05 16:04 | 2013-12-05 20:10 | 3 | 246 | 4102321 | 738 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER// CREW COMING TO CHANGE OUT// VER/CRB L3/HFP
10287 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-09-11 18:52 | 2014-09-11 20:55 | 6 | 123 | 4491521 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE #1123-274 THAT BLEW LINE FUSE ON POLE #1123-4/// WILL CHANGE CUTOUT//// CHANGED BAD CUTOUT AND CLOSED LINE FUSE IN @ 20:55 AND RESTORED SERVICE// COD 6// VER/ ADH
10288 | Williamson | 3202201 | LOVELY | LOVELY | 2021-02-25 13:23 | 2021-02-25 14:45 | 9 | 82 | 4250141 | 738 | PARTIAL POWER | EQUIPMENT FAILURE | POLE | connection came out of serve in at xfmr pole//repairs made//restored @14:45//complete//em
10289 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2022-08-18 15:16 | 2022-08-18 19:15 | 7 | 239 | 4761131 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA 7200 manual. Need a line crew and manual ROW crew. Released by crew 077S04 / had to lift clamp on same pole to make repairs clamp off@1823 on@1915
10290 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-12-06 06:41 | 2017-12-06 10:47 | 3 | 246 | 4624881 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST//THEY SAY NEIGHBORS OUT AS WELL//CKD BREAKERS//,,line fuse 38830206D02053 open,,xfr pole38830206D06001 burnt off primary and neutral down,inactive xfr gonna clear up when crew arrives//REMOVED 1 span primary and neutral 206-2632 to 206-6001 and xfr pole 206-6001 ,,all customers restored @ 10:47 complete//MADE MDC//SENT TO TECH
10291 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2017-08-31 13:54 | 2017-08-31 20:03 | 2 | 369 | 4313521 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KV 7.2 BY TRUCK RESTORED AT 19:45/CONFIRMED TO BE ON BIG SANDY FALLSBURG-S. 38830381000172 VER/AWD
10292 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2012-12-25 17:09 | 2012-12-25 21:15 | 3 | 246 | 4516181 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED 1 MAN, MATERIAL HANDLER, 25 KVA 7.2 KV 120/240 TRANSFORMER, CUTOUT, ARRESTER, AND BRACKET. REPLACED TRANSFORMER, ALL WORK COMPLETE / GXJ
10293 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-07-18 11:09 | 2008-07-18 15:15 | 3 | 246 | 53908-1 | 738 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401// BAD CUTOUT GATE ...CHANGED GATE RESTORED POWER AT 15:15// COD 3 - TRANS OUT IDC XXXX
10294 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2013-12-07 00:58 | 2013-12-07 13:15 | 1 | 737 | 4111231 | 737 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | PAUL PRATT REQUESTED THIS TICKET BE CREATED - HE WILL COME BACK OUT SAT. WITH CREW TO MAKE REPAIRS. CHANGED TRANSF OUT POWER ON 13:15 === VER/SEF L3/HFP IDC XXXX
10295 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-12-07 16:03 | 2018-12-07 17:35 | 8 | 92 | 4516381 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Xfmr fuse link broke. Restored @ 17:35. sh L3/HFP
10296 | Hazard | 3311101 | STINNETT | REDBIRD | 2014-02-19 05:31 | 2014-02-19 11:39 | 2 | 368 | 4399691 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL BE DISPATCHED AT REG WK TIME. BAD 7200 XFMR CUTOUT RELEASED BY CREW 077S01..CREW ON SITE..P.HICKS..ALL POWER RESTOREED @ 11:39 HRS P.HICKS VER/SEF L3/GSL
10297 | Hazard | 3303903 | LESLIE | HALSFORK | 2018-04-13 00:14 | 2018-04-13 12:30 | 1 | 736 | 4218471 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | per wallace melton, had this out earlier, suspect bad xfmr//4 man line crew req // will need 25kva 19.9 xfmr// manual work, no trucks to pole,very manual //cod 1//called customer reporting arcing, they saw a flash after we left the first time but no arcing now, saw fuse blow// replaced transformer and restored power at 12:30
10298 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2009-09-01 08:26 | 2009-09-01 09:58 | 8 | 92 | 58545-1 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WORK REQUEST 31510578 // BAD CONN. ON POLE - IDC XXXX
10299 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-12-01 07:11 | 2022-12-01 10:15 | 4 | 184 | 4215951 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Insulink connection failed mid-span in service drop. Replaced connection and restored @ 10:15. sh
10300 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2017-05-23 15:42 | 2017-05-23 21:50 | 2 | 368 | 4843451 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 120/208 TRANSFORMER (TWO PRIMARY BUSHINGS) IN DIFFICULT LOCATION. CREW ENROUTE TO ASSIST. REPLACED XFMR AND RESTORED @ 21:50. SH 38830833A00268 VER/AWD
10301 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2017-04-06 14:31 | 2017-04-06 16:03 | 8 | 92 | 4622821 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED LINE FUSE ON POLE 38830376000058 TO SAFELY REPLACE WIRE ON POLE 38830353000007 (ORDER 4622021). VER/AWD L3/HFP XXXHFP
10302 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2013-03-15 17:39 | 2013-03-15 20:43 | 4 | 184 | 4908851 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA NO TRUCK RELEASED BY CREW 078S08/XFMR IN DIFFICULT LOCATION/CREW LOADING NEW CAN/FETR 2130/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2043/PLEASE CLOSE TICKET/THANKS/VEM//COD 4// VER/DBM IDC XXXX
10303 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2009-01-23 00:28 | 2009-01-23 02:00 | 8 | 92 | 59277-1 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3403201 - LOOKS LIKE SURGE ARRESTER BURNT INTO ON HIGHSIDE OF TRNASFORMER. I WILL BE OUT OF TRUCK CHECKING. I REMOVED WHAT WAS LEFT OF SURGE ARRESTER REPLACED WIRE BACK IN TOP OF TRANSFORMER EVERYTHING OK. //VER/GAH L3/KEP
10304 | Hazard | 3302703 | HAZARD | HAZARD | 2014-11-20 08:10 | 2014-11-20 09:42 | 8 | 92 | 4748201 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER IN BANK ON POLE 37830296A30710, OPERATED STATION BREAKER WHEN FUSE BLEW, J.COMBS AND CREW ENROUTE TO HELP POWER RESTORED @ 09:42 VER/CRB
10305 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2020-05-25 11:43 | 2020-05-25 17:51 | 2 | 368 | 4903461 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Tree growing into secondary // will need ROW crew. new xfmer was bad changed out back to normal...
10306 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-01-30 09:07 | 2008-01-30 15:15 | 2 | 368 | 62022-1 | 736 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3308603//SECONDARY LEADS BURNT UP ON THE TRANSFORMER//REWORKED SECONDARY CONNECTIONS//COD 2// VER/DBM IDC XXXX
10307 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-07-11 01:00 | 2022-07-11 13:15 | 1 | 735 | 4458461 | 735 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | neutral broke at secondary pole 21-56, will be making repairs
10308 | Paintsville | 3409302 | KENWOOD | AUXIER | 2008-10-21 01:41 | 2008-10-21 01:56 | 49 | 15 | H57486-1 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3409302// WIRE DOWN (PHASE B) AT RECLOSER POLE. DUTY SUPERVISOR NOTIFIED AND CREW ENROUTE. RESTORATION DEPENDS ON ARRIVAL TIME OF CSX RAILROAD FLAGGERS.(WIRE CROSSES RAILS)CSX ON SITE. WORK IN PROGRESS. REPAIRS COMPLETE. SH DROPPED (PHASE A) RECLOSER FROM 0141 TO 0156 INTERRUPTING 49 CUSTOMERS FOR SAFETY CLEARANCE. //VER/GAH IDC XXXX
10309 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-02-21 06:18 | 2011-02-21 08:45 | 5 | 147 | 59574-1 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM--- CUTOUT DOOR APPEARS BAD=CHANGED OUT BURNED UP CUTOUT DOOR//COD 5// VER/DBM IDC XXXX
10310 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2010-01-31 18:34 | 2010-01-31 22:39 | 3 | 245 | 61789-1 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33668706 //, BAD 15 KVA 7200 XFMR, POLE ABOUT 15 STEPS TO FENCE LINE, V MULLINS HAS BEEN CONTACTED, PLEASE SEND TICKET TO HIM RELEASED BY CREW 078S05/CREW ON SITE/REPAIRS MADE/POWER RESTORED 2239/PLEASE CLOSE TICKET/THANKS/VEM VER/LDA IDC XXXX
10311 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-05-23 11:15 | 2010-05-23 15:20 | 3 | 245 | 66480-1 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 35237350 //BAD 15 KVA TRANSFORMER--SEND TO FRALEY COD-3 VER/HFP L3/HFP IDCC TOF1020 CHANGED THE START TIME FROM 1020 XXXX
10312 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-07-24 20:55 | 2017-07-24 21:30 | 21 | 35 | 4175841 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | SAME AS 4174591. OPENED RECLOSER ON 38831109A40151 TO MAKE REPAIRS TO LOOP ON 38831110000004. COD 21 OPENED 2055-2130 VER/AWD SJG
10313 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-06-12 11:50 | 2011-06-12 12:25 | 21 | 35 | 4301401 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER OPENED LINE AT POLE 24-666 IN ORDER TO REPAIR BURNT OFF HOTTAP ON POLE 24-668 (SEE ORDER 4298971//COD 21//ISO// VER/DBM IDC XXXX
10314 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-06-21 13:05 | 2017-06-21 14:50 | 7 | 105 | 4011011 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 69-A4-1648 BAD 12KV C/O. TRK OK. L.CREW RELEASED BY CREW 078S07 VER/CRB
10315 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2019-05-29 07:03 | 2019-05-29 09:30 | 5 | 147 | 4358191 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfmr cutout has failed I can make repairs//Replaced broken cutout and restored power @ 09:30
10316 | Hazard | 3302703 | HAZARD | HAZARD | 2011-08-12 23:20 | 2011-08-12 23:55 | 21 | 35 | 4701521 | 735 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | OPENED TR @ 2320BAD CONNECTION AT TRANSFORMERBAD CONNECTION AT TRANSFORMER--- REPLACED SECONDARY LEAD, REMADE CONNECTIONS, POWER RESTORED. IDCC TOF2243, CDC91 XXXX
10317 | Pikeville | 3409502 | BURDINE | LEVISA | 2011-09-06 17:48 | 2011-09-06 23:55 | 2 | 367 | 4838551 | 734 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP TRANSFORMER CREW ENROUTE //VER/CRB IDC XXXX
10318 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2010-02-05 11:15 | 2010-02-05 17:21 | 2 | 366 | 63356-1 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED. TOP OF POLE 189-288 HAS BURNED OFF. CUTOUT BROKE DOWN. I LIFTED HOT TAP ON POLE 189-105 AT 11:15 AND ISOLATED THIS POLE. THIS HAS 2 CUSTOMERS OUT OF POWER UNTIL POLE IS FIXED. RELEASED BY CREW 074S01 CHANGING POLE OUT WR# 33757103 WO#DKY0063561 405 POLE//ISO//COD 2// VER/DBM IDC XXXX
10319 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2016-11-19 13:35 | 2016-11-19 16:38 | 4 | 183 | 4114041 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN ON P-38830785D11311.BURNING TOP OF POLE OFF..LINE FUSE BLOWN ON 785-100.GRD AND TAGGED ON 785-392.FRAMING DOWN VER/CRB L3/HFP XXXHFP
10320 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2013-07-21 12:20 | 2013-07-21 14:22 | 6 | 122 | 4568831 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANSFORMER FUSE BROKE. VER/CRB L/3 CRB IDCC PN264 XXXX
10321 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2018-09-14 00:14 | 2018-09-14 04:18 | 3 | 244 | 4094731 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Line fuse cutout broke. Replaced cutout and restored @ 4:18. sh
10322 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2017-05-05 09:12 | 2017-05-05 15:18 | 2 | 366 | 4754081 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | PADMOUNT TRANS. FUSE OUT @38831152B20218, CHECKING. BAD 50 KVA 7200 PADMOUNT. TIM HALL GETTING A CREW TO HELP CHANGE. HAD TO OPEN THE URD @ JUNCTION BOX 1152-214, OPENED @1407 PUT BACK ON @1518, ALL POWER RESTORED. RELEASED BY CREW 074S05//DUP MADE VER/CRB
10323 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-11-09 17:20 | 2011-11-09 21:24 | 3 | 244 | 4062891 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT BROKE ON POLE309-9.WILL NEED BIG BUCKET.WILL NEED 2 MEN BIG BUCKET 7200 C/O AND ARRESTER. RELEASED BY CREW 075H01 ///VER/CRB IDC XXXX
10324 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2018-06-27 16:11 | 2018-06-27 20:15 | 3 | 244 | 4680901 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced cutout
10325 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2015-02-13 17:18 | 2015-02-13 20:21 | 4 | 183 | 4014311 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 37830196D00045 CHECK LINE WILL REFUSE IF I DONT FIND A HAZARD/CLOSED FUSE IT BLOWED, TALKED TO CUSTOMER SAW FIRE ON POLE 37830220000102 CUT ARRESTOR IN CLEAR,GOING BACK TO REFUSE! POWER RESTORED/ ISO 37830196D00045/ COD 4/ VER/BOW L3/HFP XXX
10326 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2008-05-18 09:12 | 2008-05-18 12:15 | 4 | 183 | 65365-1 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116703// BROKE CUTOUT RELEASED BY CREW 078S08-----POWER ON @ 12:15 VER/HFP IDC XXXX
10327 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-03-05 07:57 | 2012-03-05 11:00 | 4 | 183 | 4548581 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP CREWS WILL WORK TODAY.CREW REPLACED XFMER //VER/CRB IDC XXXX
10328 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2018-01-02 08:31 | 2018-01-02 12:35 | 3 | 244 | 4696511 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 secondary burnt down (3 customers out originally)/ had to open the transformers on pole 38830045D37260/ opened xfmer @ 38830045D37260, @ 08:40 (affected 2 additional customers), 1/0 sec down across 29th st. @bill phillips auto sales crew on site fetr 12:45 replacing 1/0 with 4/0 sec. all pwr restored @ 12:35 plse close ticket lrm/ DUPLICATE IN DOVS
10329 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-10-15 12:47 | 2022-10-15 15:50 | 4 | 183 | 4030381 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed at bottom of line fuse cutout 805-255. Pole is in difficult location. Replaced line fuse and xfmr cutouts and brackets on 805-255. Restored @ 15:50. sh
10330 | Whitesburg | 3314401 | MAYKING | ERMINE | 2013-02-07 15:40 | 2013-02-07 16:41 | 12 | 61 | 4799121 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L/F OUT AT POLE 450-49. ARESSTOR BLOWED IN CLEAR AT POLE 450-52. CLOSED L/F BACK IN AT 16:41. COD=12 ISO LF 37830450A00049 VER/HFP L3/HFP IDC XXXX
10331 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-03-18 22:42 | 2008-03-19 01:45 | 4 | 183 | 58364-1 | 732 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3308402/ LEAD BURNT OUT OF BUSHING ON XFMR IDC XXXX
10332 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2014-06-04 00:07 | 2014-06-04 12:18 | 1 | 731 | 4969491 | 731 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA SINGLE BUSHING , TRUCK ACCESIBLE, CREW REQ RELEASED BY CREW 078S06 VER/CRB
10333 | Pikeville | 3411801 | JOHNSCREEK | META | 2009-12-29 06:25 | 2009-12-29 18:36 | 1 | 731 | 62818-1 | 731 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPLACED BAD 4/3 SERV DROP W 2/3 SERV DROP RELEASED BY CREW 074S06 VER/HFP L3/HFP IVDC XXXX
10334 | Hazard | 3420001 | SOFT SHELL | VEST | 2018-02-02 06:29 | 2018-02-02 12:34 | 2 | 365 | 4793391 | 730 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 133-11 willl return with help customer gone to work Released by crew 077H02..changed cutout, all power restored @ 12;34 hrs..p.hicks
10335 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2011-10-28 14:33 | 2011-10-28 15:00 | 27 | 27 | 4030621 | 729 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 38830182B43784, CUTOUT REPLACED, ALL POWER RESTORED ///VER/CRB IDC XXXX
10336 | Whitesburg | 3409503 | BURDINE | JENKINS | 2014-02-25 16:37 | 2014-02-25 17:58 | 9 | 81 | 4434201 | 729 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OPEN AT 37830358D00137 COD-9 VER/HFP L3/HFP
10337 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2020-01-13 09:12 | 2020-01-13 13:15 | 3 | 243 | 4296471 | 729 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20t lf open @ 140-203, burnt off pole @ 140-6512. line crew reqd. trk to pole. Released by crew 078S07 crew on site LRM fetr 13:45 all pwr restored @ 13:15 please close ticket LRM
10338 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2015-02-08 17:06 | 2015-02-08 21:09 | 3 | 243 | 4000791 | 729 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 38830045B33061 BAD 7200 25 KVA CAN. TRUCK OK//38830045B33061 BAD 7200 25 KVA CAN. TRUCK OK RELEASED BY CREW 078S07/CREW ON SITE RM/PART POWER/ONE LEG OUT/OPENED XFMR @2035/POWER RESTORED TO ALL CUST 2109/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN L3/HFP HFPC MCCDL
10339 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-02-25 06:42 | 2008-02-25 10:45 | 3 | 243 | 50059-1 | 729 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308401/// UPDATED FETR DUE TO UNFORSEEN ISSUES IN THE FIELD//3308401 BAD CUTOUT// VER/TOM IDC XXXX
10340 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2013-05-28 15:29 | 2013-05-28 17:00 | 8 | 91 | 4191511 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA XFMR. CREW ENROUTE TO CHANGE TO 50KVA. RAMEY, BRYANBAD 25KVA XFMR. CREW ENROUTE TO CHANGE TO 50KVA. CHANGED TO 50KVA. RESTORED @ 17:00. SH VER/HFP L3/HFP IDC XXXX
10341 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2017-09-08 09:44 | 2017-09-08 10:40 | 13 | 56 | 4340411 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 44-5536 BAD CUT OUT 20T LINE FUSE REPLACED CUTOUT COD-13 ISO & FAULT 38830044C45536 VER/HFP L3/HFP
10342 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2021-05-10 07:18 | 2021-05-10 10:20 | 4 | 182 | 4568501 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 261-16 made repairs and restored
10343 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-02-23 08:26 | 2012-02-23 14:30 | 2 | 364 | 4485201 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR FUSE IS OUT,WILL RE-FUSE//////XFR IS BAD,NEED CREW,25 KVA 7200,MIGHT ALSO NEED TREE CREW TO CLEAR BRUSH IF WINCHING SHOULD BECOME NECESSARY,ABT 150FT ON HILL///////NOTE NEW FETR-14:30////////REPLACED XFR AND RESTORED,ALL OK AFTERWARDS COD-2 ISO TF 37830071000023 VER/HFP L3/HFP IDC XXXX
10344 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2020-08-16 09:31 | 2020-08-16 15:35 | 2 | 364 | 4334701 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 by truck, Released by crew 078H03// crew on site FETR 15:00 all pwr restored 15:35 please close ticket LRM
10345 | Pikeville | 3402003 | KEYSER | MULLINS | 2019-12-24 23:19 | 2019-12-25 00:50 | 8 | 91 | 4180551 | 728 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | spoke with cust//multiple houses at this location experiencing part power & dim lights //connection @ xfm. was burnt into..restored..//cod 8
10346 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2011-03-15 14:29 | 2011-03-15 15:25 | 13 | 56 | 54520-1 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | WR# 39174816 // POLE 20-447 BAD LA NO TRUCK CSP TRANS. NEED CUTOUTS INSTALLED SEND NOTE TO RAYBURN SEND TO TREE PEOPLE 100 REQUEST LINE NEED CUT//COD 13//SENT TO FORESTRY AND LINE DEPT// VER/DBM IDC XXXX
10347 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2021-02-08 07:06 | 2021-02-08 13:10 | 2 | 364 | 4948061 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | broken guy wire // neutral burnt down making repairs restored@ 1310
10348 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-07-06 02:26 | 2013-07-06 08:30 | 2 | 364 | 4473351 | 728 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK AT REGULAR WORKTIME PER SET GUIDELINES // POLE 1099-6151 BAD CUTOUT DOOR 6T TRANS. FUSE 3- CUST. VER/PDP
10349 | Pikeville | 3421001 | BREAKS | CITY | 2022-04-22 21:28 | 2022-04-23 09:35 | 1 | 727 | 4791841 | 727 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans fuse open at 243-A-125..Bad 25KVA Trans Primary Voltage is 12KVA,This is Manual spoke with Paul Layne and is going to wait Until daylight to replace.. Released by crew 074S01//restored at 09:35
10350 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2013-03-28 16:43 | 2013-03-28 20:45 | 3 | 242 | 4965241 | 726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPAIRED SERVICE DROP AND REPLACED BROKEN CUTOUT. VER/KEP IDC XXXX
10351 | Cannonsburg | 3001401 | LOUISA | CITY | 2011-06-24 11:57 | 2011-06-24 18:00 | 2 | 363 | 4409611 | 726 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | DOOR BURNT UP ON C PHASE. CHANGED CUTOUT OPENED BANK AT 1751 ALL POWER RESTORED AT 1800 CLOSE TICKET//COD 2// VER/DBM IDC XXXX
10352 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2008-04-10 17:46 | 2008-04-10 18:52 | 11 | 66 | 65881-1 | 726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | SEND NOTE TO RAYBURN BAD LA POLE 68-764 NO TRUCK//3001101//I MADE A MAP DISCREP ON THIS//VER/CRB IDCC PN530 XXXX
10353 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-04-23 15:12 | 2011-04-23 19:14 | 3 | 242 | 62604-1 | 726 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | WILL HAVE TO WALK ON HILLSIDE TO REDO SERVICE CONNS IDC XXXX
10354 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2008-11-04 19:51 | 2008-11-04 20:24 | 22 | 33 | 62215-1 | 726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3002103// BROKEN FUSE//COD 22// VER/DBM IDC XXXX
10355 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2012-08-03 16:13 | 2012-08-03 20:15 | 3 | 242 | 4890441 | 726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 074S01 .REPLACED CUTOUT, ALL WORK COMPLETE / GXJ CCC COD-3 ISO TF 37830211D00030 VER/HFP L3/HFP IDC XXXX
10356 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2022-07-12 11:06 | 2022-07-12 15:08 | 3 | 242 | 4465251 | 726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | mismapped. bad xfmer pole 1071-118. crew reqd. no trk. carry in Released by crew 078S07///Opened LF 39831071000008 to replace TR
10357 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2011-06-16 00:03 | 2011-06-16 12:09 | 1 | 726 | 4325271 | 726 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND POLE 1122-135, ON FIRE, BAD CUTOUT, POLE IS BURNTED JUST ABOUT INTO, LIFTED HTSP ON POLE1122-191, SINGLE POLE TAP, HAVE FIRE BUT OUT, NEED 404 POLE CAN USE TRUCKS, TURN UP CHINNS BRANCH, PASSED KAYTEE LANE, TO WHITE DBL WIDE ON LEFT, FOR SALE SIDE IN FRONT YARD, CREW REQ, CAN BE DONE TOMMORROW, NO ONE IS LIVING IN TRAILER RELEASED BY CREW 078S06/ TECH WROTE JOB/REPAIRS MADE/PLEASE CLOSE TICKET/THANKS/VEM//ISO 39831122C00191//COD 1// VER/DBM IDC XXXX
10358 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2014-01-07 09:05 | 2014-01-07 11:30 | 5 | 145 | 4248131 | 725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSF === NEED BIG BUCKET AND 25 KVA TRANSF 7200 === LINE CREW AND SOME CLEAN UP TOO--- REPLACED TRANSF === POWER OK//COD 5// VER/DBM
10359 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2014-05-31 14:05 | 2014-05-31 16:30 | 5 | 145 | 4956951 | 725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMER FUSE BLOWN ON POLE 811-145///GOING TO REFUSE///BAD CUTOUT HAD TO CLIMB AND CHANGE///REFUED @ 16:30 RESTORING ALL CUST///COMPLETE BR VER/CRB
10360 | Hazard | 3308001 | JACKSON | S.JACKSON | 2011-07-12 07:43 | 2011-07-12 19:48 | 1 | 725 | 4525991 | 725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL NEED CUTOUT AND BRACKET 7.2 KV TRUCK ACC. 1 LANE ROAD. RELEASED BY CREW 077E07--NEED COVER UP RELEASED BY CREW 077S10//COD 1// VER/DBM
10361 | Pikeville | 3409502 | BURDINE | LEVISA | 2008-12-18 13:25 | 2008-12-18 15:50 | 5 | 145 | 59891-1 | 725 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3409502// LINE FUSE IS OUT ON POLE 334-9. I AM PATROLLING LINE NOW. PRI. CONDUCTOR IS OFF INSULATOR ON POLE 334-13. I HAVE LINE GROUNDED AND I AM GOING TO WALK BACK IN HILLS AND RETIE CONDUCTOR ON PIN. I CLOSED LINE FUSE IN AT 15:50.//COD 5// VER/DBM L3/KEP IDC XXXX
10362 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2011-10-01 17:28 | 2011-10-01 23:30 | 2 | 362 | 4938541 | 724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA XFORMER 7,200 NO TRUCKS TO POLE. NEED YARD DOG. RELEASED BY CREW 078S01 //VER/GAH IDC XXXX
10363 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2008-04-29 06:10 | 2008-04-29 12:12 | 2 | 362 | 55321-1H | 724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3408402///TOP OF POLE BURNED OFF,WILL CONTACT NEEDED CREWS ABT MATERIAL NEEDS RELEASED BY CREW 074S06 FRAMED DOWN ON POLE//VER/CRB IDCC DUP TO CUT LOOP XXXX
10364 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2011-09-05 14:24 | 2011-09-05 17:25 | 4 | 181 | 4819941 | 724 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DEFECTIVE CUT-OUT ON POLE 1057-67, HAS BLOWN LINE FUSE ON POLE 28-3. MANUAL JOB.DEFECTIVE CUT-OUT ON POLE 28-67, HAS BLOWN LINE FUSE ON POLE 28-3. MANUAL JOB. TWO CUSTOMERS RESTORED 17:25. CCC COD-4 ISO ISO LF 37820028000068 VER/HFP L3/HFP IDCC PN68 XXXX
10365 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-04-18 16:13 | 2014-04-18 22:15 | 2 | 362 | 4617301 | 724 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK FOR PROBLEMS///ONLY 105V ON ONE LEG,NEED 2 MEN,FOREMAN,NO APPROACH//25 KVA 19.9REPLACED DEFECTIVE XFR,ALL OK AFTERWARDS // VER/TOM L3/TOM
10366 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2017-11-19 00:42 | 2017-11-19 12:45 | 1 | 723 | 4577741 | 723 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout at pole 93-263 replaced and restored power at 12:45
10367 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2013-10-23 22:32 | 2013-10-24 10:35 | 1 | 723 | 4958371 | 723 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 19.9 PRI, TRANSFORMER OIL COMING OUT OF PRI, BUSHING WILL NEED CREW SPOKE TO CUST OK FOR IN MORNING RELEASED BY CREW 078S09//COD 1// VER/DBM L3/HFP IDC XXXX
10368 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-04-25 06:39 | 2016-04-25 10:40 | 3 | 241 | 4122091 | 723 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED 2 CUTOUTS AND ARRESTORS VER/AWD
10369 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2010-11-04 05:14 | 2010-11-04 09:15 | 3 | 241 | 51561-1 | 723 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CCC ISO TF 37820170000036 COD-3TRANSFORMER CUTOUT FAILED ON POLE 170-36. THIS WAS THE OUTAGE POLE. I REPLACED THE CUTOUT. VER/HFP L3/HFP IDC XXXX
10370 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-09-11 19:29 | 2016-09-12 01:30 | 2 | 361 | 4886201 | 722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKE SEC POLE, 306, 4/0 URD, NEED CREW, MAT. 3 IN CONDUIT, SHOULD BE ALL AND 306 POLE, CAN USE TRUCK TREE LIMB FALL HIT WIRE BROKE POLE RELEASED BY CREW 078S06// VER/DBM
10371 | Paintsville | 3420101 | MAYO TRAIL | NIPPA | 2020-09-09 10:20 | 2020-09-09 13:58 | 4 | 218 | 4444811 | 722 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25KVA transformer on 738-75. Crew enroute to replace.// had to open line fuse to safely change xfer, opened @1110 // repairs made and restored all customers @ 1358 // one customer miss mapped and the line fuse also feeds both ways, xfer 38830738A00072 was never off total COD is 4 // 3 on line fuse one on xfer
10372 | Pikeville | 3411801 | JOHNSCREEK | META | 2016-03-24 12:30 | 2016-03-24 14:54 | 5 | 144 | 4877281 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER HAS BURNED OUT OF THE HOT TAP ON PHASE B AT POLE 38821082000101. ALL THREE FUSES ARE IN AT POLE 38821082000098 BUT WILL HAVE TO BE OPENED WHEN REPAIRS ARE MADE. I OPENED THE LINE AT 14:45, AND CLOSED AT 14:54.// VER/ ADH
10373 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2021-09-09 15:16 | 2021-09-09 16:36 | 9 | 80 | 4227611 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE HARDWARE | related to 4226881 // lifted hottap on pole 38830278000189 in order to work on pole 38830278000093 // cod 9 // Released by crew 078H02
10374 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-12-11 08:24 | 2021-12-11 11:24 | 4 | 180 | 4172331 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout making repairs now..repairs made/ ISO 38830882D00053/ COD 4
10375 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2022-04-26 08:42 | 2022-04-26 12:42 | 3 | 240 | 4800741 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke//big bucket enroute//repair made//restored at 12:42//complete//em
10376 | Cannonsburg | 3000302 | BELLEFONT | FLATWOODS | 2010-09-20 12:30 | 2010-09-20 12:45 | 48 | 15 | H51191-1 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR#36940341//OPENED SWITCH 1148-504 ISOLATING FAULT POLE 1148-978 (POLE BURNT OFF DUE TO BAD CUTOUT) /THEN 1322 CLOSED SWITCH 20-1028 IN PICKING UP 47 CUST FROM THE BELLEFONTE/BELLEFONTE CIRCUIT RELEASED BY CREW 078S08 // ONLY CUSTOMERS OUT IS SOCCER FIELD //PUT FIRE OUT WILL WORK MONDAY 9/18 P R TOLLIVER//CREW ON SITE PR TOLLIVER 9/20/10// 1205 - CLOSED 1148-504 (RESTORE 1 CUST) //1230 - OPENED 20-1028 (48 CUST INTPT) 1245 - CLOSED 1148-2028 (RESTORE 48 CUST) //VER/GAH IDC DUP FOR SWITCHING XXXX
10377 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2012-01-26 17:25 | 2012-01-26 21:25 | 3 | 240 | 4295621 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED 8` ARM AND 3 CUTOUTS // JOE HEMLEPP & MIKE PHELLPS & NICK MCCANNARRIVED ON SCENE FOUND BAD CUTOUT, THAT HAS BURNTED THE END OF CROSSARM OFF, I OPEN UP TRANSFORMER BANK ON POLE 1073-504, FEEDS THE CITY BUILDING, I ISOLATED BAD CUTOUT, BY LIFTING HOT TAP, OTHER TWO PHASE ARE STILL HOT. CREW REQ, 3 MEN, BUCKET TRUCK, 8 FT CROSSARM, 3 NEW CUTOUTS COD-3 ISO LF 39831073A20502 VER/HFP L3/HFP IDC XXXX
10378 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-11-16 12:34 | 2009-11-16 14:34 | 6 | 120 | 60560-1 | 720 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ON SITE, CHECKING FOR TROUBLE COD-6 SERVICE FEED MTR BANK ON APT BLDG OTHER DROPS WERE OK VER/KEP L3/KEP IDC XXXX
10379 | Paintsville | 3401103 | FALCON | BURNINGFK | 2019-07-20 12:14 | 2019-07-20 18:14 | 2 | 360 | 4737461 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | patrolling line bad 25kva 120/240/7200 truck accessible crew on site restored L3/HFP
10380 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2022-05-18 18:24 | 2022-05-18 19:54 | 8 | 90 | 4907611 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Pole 37830042C00271 fell and is laying against house.//No outage at this time.//Need pole (old pole was 35-6)15KVA XFM 7200.// Cutout and bracket.Pole top pin and clevis. // OPENED LINE FUSE ON POLE 42-198 @1824. Repairs made. Pole replace with a 40 class 4. closed line fuse at 19:54.
10381 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2014-06-11 16:35 | 2014-06-11 19:35 | 4 | 180 | 4058271 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON PL158-80 BAD RIGHT OF WAY, WIRE IS RUNNING THROUGH TREES BAD CUTOUT ON PL158-114; POWER RESTORED AT 19:35
10382 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2020-11-22 16:20 | 2020-11-22 18:44 | 5 | 144 | 4715441 | 720 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | one span of open wire broke on ground power restored at 1844
10383 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2015-04-10 07:42 | 2015-04-10 09:12 | 8 | 90 | 4301531 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT 68A-723 PATROL 68-767 XFORM CUTOUT BROKE LAY ON XFORM, POLE GUYS NEED REPULLED,LINE CREW NO TR,LINE FUSE HOT 09:12, 2CUST OUT ON 68- 767 RELEASED BY CREW 078S04.--(REPLACED CUTOUT, REPAIRS MADE, SERVICE RESTORED.) RELEASED BY CREW 078F03//?????
10384 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-06-04 15:15 | 2011-06-04 17:15 | 6 | 120 | 4231531 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD LIGHTNING ARRESTOR AND ALSO FOUND #4 CU NEUTRAL DOWN, HAVE ARRESTOR CUT IN THE CLEAR AND HAVE NEUTRAL CUT IN THE CLEAR AS WELL GOING FROM POLE 902-102 TO 249, WELL NEED TREE CREW AND LINE TO BUT THIS NEUTAL BACK UP, WELL ROLL OF NEUTRAL, LEAVE AT THE BOTTOM OF TRANSFORMER POLE.//GARY MADE AN ABNORMAL//A PHASE ONLY IDC XXXX
10385 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-01-15 13:46 | 2021-01-15 16:10 | 5 | 144 | 4871471 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Arrester blown @ 38830809C30098.// did not end up having to take tap off transformer only off // closed transformer back at 1610 all restored
10386 | Pikeville | 3410602 | E.PRESTON | LANCER | 2008-01-07 13:22 | 2008-01-07 14:52 | 8 | 90 | 54380-1 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3410602// LIGHTNING ARRESTER BLOWN ON CSP XFMR. ISOLATED BAD ARRESTER AND WILL TRY FUSE ON POLE 38830955B00563. RE-FUSED 40T LINE FUSE. SH//COD 9//ISO 38830955B00563// VER/DBM IDC XXXX
10387 | Whitesburg | 3451202 | BEEFHIDE | DUNHAM | 2016-05-25 13:59 | 2016-05-25 19:59 | 2 | 360 | 4258581 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER ON 357-153. // VER/CRB
10388 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2018-10-26 09:15 | 2018-10-26 12:15 | 4 | 180 | 4324481 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED 911 W/ETA OF 0915//NO OUTAGE TILL TRANSFORMER 38830070B43591 OPENED //COD 4//CALLED 911 W/ETA OF 0915//.. opened xfmer @ 70-3591 @ 09:15. open wire secondary down from 70-3592,3613, 3614. 2 al trk to pole Released by crew 078S07 crew on site FETR 12:30 LRM all pwr restored @ 12:15 please close ticket LRM
10389 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-11-01 11:35 | 2014-11-01 12:15 | 18 | 40 | H4680281 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRIMARY CONDUCTOR BURNED DOWN UNDERNEATH A HOT TAP AT POLE 37820121000229. SOURCE SIDE IS IN THE CLEAR. I WILL CALL FOR HELP. I WILL LEAVE RECLOSER AT 97-134 ON UNTIL CREW GETS HERE, WE WILL HAVE TO OPEN IT TO PUT WIRE UP. OPENED RECLOSER ON POLE 97-134 AT 11:35. WE GOT WIRE PUT UP AND I CLOSED REC BACK IN AT 12:15// COD 73// RECLOSER IN ORGINALLY, DEENERGIZED FROM 229 DOWN, OPENED REC TO MAKE SAFE AND GROUNDED AT 229. CLOSED IN REC// AJB VER/DKG L3/DKGXXXC CNT THIS IS THE OUT FROM REC TO OPEN PT AT 229
10390 | Whitesburg | 3312902 | JENKINS | JENKINS | 2022-12-19 09:24 | 2022-12-19 10:44 | 9 | 80 | 4275341 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ETA 10:05.. customers service has burnt down. will be replacing service. replaced service,power restored
10391 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2018-02-27 13:00 | 2018-02-27 14:20 | 9 | 80 | 4887661 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | replaced 25kva with 50 due to problems customer where having. opened @ 13:00 closed @14:20
10392 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-05-16 08:39 | 2014-05-16 14:39 | 2 | 360 | 4713891 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPEN NEUTRAL, CALLING FOR A MAN, CANT FIND IT COD-2 ISO 37830227D00073 //NEED TO CALL OMS HOTLINE ON THIS ONE = PLEASE CLOSE ORDER IDC XXXX
10393 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-04-21 12:00 | 2008-04-21 13:00 | 12 | 60 | 52990-1 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER WILL CHECK ASAP CHECKED VOLTAGE AT METER AND IT WAS GOOD. FOUND BAD CUTOUT AND ARRESTOR AND REPLACED. HAD XFMR OPEN FROM 12:00 TO 13:00. TREE TRIMMERS WORKING IN AREA COULD HAVE CAUSED FLICKER. SH /// 12 CUSTOMERS -- COD/HFP VER/HFP IDCC TON1312 XXXX
10394 | Hazard | 3420001 | SOFT SHELL | VEST | 2012-01-11 16:54 | 2012-01-11 17:30 | 20 | 36 | H4247441 | 720 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE # 131-17 IS ON FIRE, BAD INSULATOR OR CUTOUT, //VER/GAH IDC XXXX
10395 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2020-07-19 14:41 | 2020-07-20 02:40 | 1 | 719 | 4183041 | 719 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout at 37820193A00343, no truck access, will be making repairs. Got cutout cjanged out, closed L/F back in @0240. 1 CC
10396 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-05-15 20:32 | 2010-05-16 08:31 | 1 | 719 | 62895-1 | 719 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER FUSE HANGING DOWN CUTOUT IS BROKE, GOING TO HELP JIM MULLINS WITH HOT SERVICE ON GROUNG AND COME BACK RELEASED BY CREW 077S05 VER/KEP L3/KEP IDC XXXX
10397 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2016-07-15 04:06 | 2016-07-15 07:15 | 4 | 189 | 4639561 | 719 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | BELIEVE TO BE RELATED TO RESTORATION ATTEMP FOR 4638971//COD 625//SUSPECT LOAD TOOK OUT RECLOSER//SEE DOL CASE 671791//
10398 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-06-09 22:13 | 2011-06-10 10:12 | 1 | 719 | 4281291 | 719 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | THE PRIMARY METERING ON POLE 167-444 IS BYPASSED. IT APPEARS THAT WE HAVE AN EPOXILATOR BREAKING DOWN. I OPENED THE BYPASS CUTOUTS ON THIS POLE AS PER D. MASSEY. RELEASED BY CREW 074S02//PER TIM HALL (PIKEVILLE OFFICE) WILL HAVE TO CLOSE DOWN 1 LANE OF THE 4 LANE TO DO THIS AND CUSTOMER HAS AGREED TO LET US FIX THIS ON MONDAY 6-13//PIKEVILLE OFFICE IS GENERATING AN OPS ORDER TO GO BACK ON THIS//CLOSING TRBL// VER/DBM IDC XXXX
10399 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-05-12 10:01 | 2020-05-12 16:00 | 2 | 359 | 4827791 | 718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | Broken crossarm on pole 488-26 and A phase fuse is open on stepdown transformer at 487-144 (1 COD) restored power at 16:00.. ¦¦¦ 1 SINGLE PHASE & 1 3 PHASE CUST
10400 | Pikeville | 3410602 | E.PRESTON | LANCER | 2009-02-04 13:28 | 2009-02-04 14:32 | 12 | 64 | 55575-1 | 718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR LEAKING CHANGED OUT FOR MAINT
10401 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2009-04-19 10:35 | 2009-04-19 16:34 | 2 | 359 | 58700-1 | 718 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000701//BAD 25 KVA TRANSFORMER TRUCK TO POLE MAY NEED FLAGGERS CREW IS BEING CALLED OUT TO CHANGE OUT BAD 25 KVA TRANSFORMER PHIL TOLLIVER AND CREW, CREW IS ENROUTE ORDER IS COMP, VER/KEP L3/KEP IDC XXXX
10402 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2021-08-16 23:58 | 2021-08-17 11:55 | 1 | 717 | 4083541 | 717 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DDC TAGS// DOL 1140326 // lf open on pole 925-95. pole 925-169 cut top off should be able to lower everything need c/o arrester bracket guy breaker d/e insulator. GROUND @ pole 925-169 DDC TAG @ 925-95. need service truck with jib//DDC TAGS ///Complete BR
10403 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-08-10 11:06 | 2022-08-10 15:05 | 3 | 239 | 4715021 | 717 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut out, replaced. Power restored at 15:05
10404 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2013-04-17 01:56 | 2013-04-17 04:55 | 4 | 179 | 4016561 | 716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I ISOLATED CUTOUT ON POLE 450-96 THAT SERVED NO ONE VER/KEP IDC XXXX
10405 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2011-04-05 22:53 | 2011-04-06 10:49 | 1 | 716 | 50220-1 | 716 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEM IF ANY/////SERVE-IN CONNECTION CAME APART AT XFR POLE,PROBABLY THE WIND BLOWING COND BACK AND FORTH.MADE NECESSARY REPAIRS,ALL OK AFTERWARDS//VER/CRB IDC XXXX
10406 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2015-09-09 18:01 | 2015-09-10 05:57 | 1 | 716 | 4219011 | 716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 238-56 NEED BIG BUCKETT AND LINE CREW. RELEASED BY CREW 078S01---CHANGED OUT BAD CUTOUT---COMPLTED 05:57---TBL TKT COMP VER/ARN
10407 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2016-01-19 04:50 | 2016-01-19 10:48 | 2 | 358 | 4630851 | 716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 7200. THREE 200 AMP SERVICES ARE ON THIS TRANSFORMER, 25 KVA SHOULD BE BIG ENOUGH. CAN USE BUCKET TRUCK. RELEASED BY CREW 079S02 COMPETED 01/19/16 10:48 TOM MCCWN/ VER/ AWD
10408 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2017-06-24 08:02 | 2017-06-24 14:00 | 2 | 358 | 4036441 | 716 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD @ 825-80 CHANGING NOW..
10409 | Hazard | 3308002 | JACKSON | PANBOWL | 2012-10-20 22:37 | 2012-10-21 01:00 | 5 | 143 | 4160141 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER DISPATCHED. XFMR IS BAD ON POLE 1084A-300 AND TOOK OUT LINE FUSE ON SAME POLE . XFMR HAS HOLE IN THE TOP OF IT , JUST FEEDS LIGHTS , CAN CHANGE MONDAY ( 10 KVA ) IDCC PN313, CNT3 XXXX
10410 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2018-01-06 09:25 | 2018-01-06 11:10 | 7 | 105 | 4712231 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Connection failed on xfmr sec riser to secondary conductor. Opened xfmr 978-224 @ 10:35, made repairs and closed @ 11:00. sh
10411 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2021-11-09 08:22 | 2021-11-09 09:27 | 11 | 65 | 4068941 | 715 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | part power/changed out connections on pole & at mast. pls close. tre
10412 | Pikeville | 3421001 | BREAKS | CITY | 2015-03-26 10:19 | 2015-03-26 11:24 | 11 | 65 | 4229511 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | RISER BURNED OUT OF HOT LINE CLAMP ON POLE 220-495, ELEVEN CUSTOMERS OUTAGED. VER/KEP
10413 | Pikeville | 3402002 | KEYSER | STONECOAL | 2011-08-03 12:15 | 2011-08-03 13:10 | 13 | 55 | H4658981 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | INS. BROKE @ 24-569// OPENED LINE FUSE ON 24-68 @ 12:15// CREW IN ROUTE TO REPAIR// REPAIRS MADE// POWER IS RESTORED// VINES NEEDS CUT ALL AROUND 24-569 OR THIS WILL HAPPEN AGAIN SOON// SEND TO C. FARMER VER/KEP IDCC DUP TO OPEN FUSE XXXX
10414 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2012-05-01 22:15 | 2012-05-01 23:20 | 11 | 65 | 4732751 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD SECONDARY CONNECTION. OPENED XFMR 785-43 @ 22:15, RE-WORKED ALL SEC CONNECTIONS AND CLOSED @ 23:20. SH RELEASED BY CREW 076S02//COD 11// VER/DBM IDC XXXX
10415 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2010-04-19 10:35 | 2010-04-19 11:40 | 11 | 65 | H64867-1 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 34725184 /// CENTER B PHASE (8 CUST) WIRE BROKE AT INSULATOR ON POLE 97-66. CUTOUT LEAD IS HOLDING WIRE UP. IT DID NOT BLOW LINE FUSE. POWER IS OFF FROM POLE 97-66 ON CENTER PHASE UP HOLLOW. TIM HALL IS SENDING HELP. WE WILL HAVE TO OPEN ALL 3 PHASES ON POLE 97-48 WHEN WE REPAIR WIRE. WE ONLY HAVE ABOUT 5 PEOPLE OUT AT THIS TIME. I OPENED ALL 3 LINE FUSES ON POLE 97-48 AT 10:35. (11 CUST) WE COMPLTED WORK AND CLOSED THEM BACK IN AT 11:40. SEE 64867-1 VER/HFP L3/HFP IDCC TOF0622 XXXX
10416 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2017-04-07 18:09 | 2017-04-07 19:14 | 11 | 65 | H4628841 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER//NO OUTAGE TILL FUSE OPENED @ 1809//CLOSED 1914// VER/CRB /// DUPLICATING FOR LINE FUSE OUTAGE - PER 1ST CALL CUST HAD PART POWER = L3/HFP HFPC DUP
10417 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2018-10-26 06:27 | 2018-10-26 08:50 | 5 | 143 | 4324161 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout Guidelines. Transformer fuse appears to have broke. Restored @ 8:50. sh L3/HFP
10418 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-05-11 13:47 | 2009-05-11 14:00 | 55 | 13 | 59363-1 | 715 | DISTRIBUTION LINE | EQUIPMENT FAILURE | REGULATOR | HIGH LINE VOLTAGE WILL CHECK REGULATOR//OPENED REC 1040-22 LONG ENOUGH TO ISO REGULATOR 1040-115 REGULATOR OPEN POWER RESTORED 05-11-09 G FUGATE REG CONTROLS TURNED OFF CONTROLS TAGGED EVERYTHING RAN TO ZERO MLR OK IDC CHANGED START TIME FROM 0952 XXXX
10419 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-01-28 11:03 | 2018-01-28 17:00 | 2 | 357 | 4778881 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UG conductor burnt in two. Released by crew 076S02// two phases burnt in two // starting repairs// repairs complete at 17:00// waiting on electrican repairs complete, restored at 17:00/ ISO 38830858B00066/ COD 2
10420 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-04-07 13:54 | 2019-04-07 18:54 | 24 | 300 | 4066641 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad 12 kv c/o. crew reqd. Released by crew 078S07.. opened line fuse for about 15 minutes to safely change a broken cutout.power should be restored by 7 p.m. all power restored at 18:54 Released by crew 078H07 L3/HFP
10421 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2017-05-27 18:47 | 2017-05-27 22:45 | 3 | 238 | 4871961 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMR CUTOUT , I CHANGED IT OUT/ ISO 37830426D00009/ COD 3/ VER/BOW
10422 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2008-12-06 07:18 | 2008-12-06 13:15 | 2 | 357 | 54840-1 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER IS BAD BUT THE FUSE WAS IN TWO CUSTOMERS OUT EVERYONE ELSE ON SAME PRIMARY IS ON...TURN ON CYNTHIA CHAPEL THEN LEFT ON ROSEBUSH HILL WHEN AT BIG CURVE ON TOP OF HILL GO STRIGHT THROUGHT CURVE BAD TRANSFORMER ON RIGHT AT TOP OF ROAD RELEASED BY CREW 078S02 CC 2 VER/PDP L3/KEP IDC XXXX
10423 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2022-08-07 12:18 | 2022-08-07 18:15 | 2 | 357 | 4698871 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 csp transformer 7200v 120-240/// crew required no trucks backyard machine Released by crew 078S09 Changed xfmr, voltage check good, closed at 18:15. Ticket complete.
10424 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2021-01-30 02:25 | 2021-01-30 14:19 | 1 | 714 | 4919501 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Opened underground pad mount everything looked good. Shot fuse and came back out . Suspect bad underground primary cable. Linecrew requred Released by crew 078S11--replaced 300 1/0 Prim UG cable--Riser fuse in on 477/68 @ 14:19---WO to be written---tbl tkt comp.rmv
10425 | South Williamson | 3404301 | SIDNEY | BIGCREEK | 2014-02-13 13:01 | 2014-02-13 13:43 | 17 | 42 | H4382721 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT ON POLE 989-B-291. HAD TO OPEN FUSE ON POLE 989-A-139 AT 13:01 TO CHANGE BAD CUTOUT. SHOULD BE BACK ON BY 14:00. OPENED FUSE AT 13:01 AND CLOSED BACK IN AT 13:43. ENTERED MD // VER/HFP L3/HFP IDC XXXX
10426 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2015-03-30 12:31 | 2015-03-30 14:13 | 7 | 102 | 4243321 | 714 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | PART POWER , BAD SPLICE IN SERVICE DROP , ONLY ONE CUSTOMER AFFECTED MADE REPAIRS RESTORED POWER AT 14:13.
10427 | Paintsville | 3401101 | FALCON | FALC-OILS | 2018-12-25 12:12 | 2018-12-25 16:10 | 3 | 238 | 4597821 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: customer reset breaker for trailer and house and niether have power/ customer said there is a line down from transformer to secondary pole Cutout broke - difficult location. Replacing. Restored @ 16:10. sh/ ISO 38830879000002/ COD 3 L3/HFP
10428 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2019-02-12 18:18 | 2019-02-12 20:00 | 7 | 102 | 4782741 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Hot Tap burnt off on pole 45-524 // crew req,,,
10429 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2011-03-21 03:43 | 2011-03-21 09:40 | 2 | 357 | 56152-1 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH AT REG WORK TIME TODAY. CUTOUT DOOR BURNT UP ON POLE 188B358. I WILL BE REPLACING CUTOUT. CHANGED BAD CUTOUT FUSED UP EVERYTHING OK. 37830188B00358 COD-2 VER/KEP IDC XXXX
10430 | Pikeville | 3120102 | STANVILLE | TRAM | 2022-07-03 13:48 | 2022-07-03 19:45 | 2 | 357 | 4370631 | 714 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans. fuse open @1053-A-117, checking.Trans. fuse open @1053-A1-300, checking. Fuse melted out, refused @1945.
10431 | Pikeville | 3408101 | SALISBURY | PRINTER | 2021-06-11 22:17 | 2021-06-12 10:10 | 1 | 713 | 4720411 | 713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kv 7200 csp xfm. bad on pole 1123-254..will need crew to make repairs this is non-truck access.will need 7200 cutout with bracket and 15kv 7200xfm. and sidexside to get xfm. to pole.please send copy to Steve Ray.will make repairs in the a.m.spoke with customer and he is aware.. Released by crew 074H09//repairs made // on @ 10:10 // replced bad c/o on pole 1123-119
10432 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-12-22 01:07 | 2018-12-22 13:00 | 1 | 713 | 4589741 | 713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 xfmr on 930-A-250//need line crew and big bucket//can use truck//driveway is a graveled drive//it is steep and has couple switchbacks// Released by crew 079S01/ CUST. HAS A SLIDE PL#930-250 IS IN A SLIDE PULLING URD FROM MTR BASE. REPAIRS HAVE BEEN MADE. CUST. IS HAVING CONT. WORK ON SLIDE. POLE WILL NEED RELOCATED R RAY//SENT TO TECH L3/HFP
10433 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2017-08-20 08:46 | 2017-08-20 16:45 | 7 | 479 | 4279831 | 713 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | PRIMARY POLE 91-C-243 HAS ROTTED AND FALLEN; AT 0846 MIKE PHELPS LIFTED TAP AT 91-C-209 TO ISOLATE; AT 0925 MIKE REPORTED INSTALLED HOT TAPS ON ALL 3 BREAKOFFS AT 91-C-242 AND LEFT TAP TOWARD 91-C-243 OPEN AND RESTORED TAP ON 91-C-209///HOT TAP INSTALLED ON 91-242 ISOLATING POLE 243. TRK TO POLE. TECH, LINE CREW RELEASED BY CREW 078S07 VER/AWD SJGC TOF08:05
10434 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2021-06-20 20:28 | 2021-06-21 08:20 | 1 | 712 | 4776031 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 7200 15 kva txmf, can get service material handler to pole. Crew required Released by crew 078S11/ work complete/ power on @ 0820/ please close ticket/ MLH
10435 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2011-05-26 08:49 | 2011-05-26 14:45 | 2 | 356 | 4171611 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | RELEASED BY CREW 074S05. REPLACE CUTOUT, PUT IN DATA BASE TWO ARRESTER NEED TO BE REPLACE...DKG/052611/ENTERED ARRESTERS INTO ABNORMAL DATABASE VER/DKG
10436 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-02-10 23:07 | 2009-02-11 10:59 | 1 | 712 | 57561-1 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7200 XFORMER. RELEASED BY CREW 078S01/CREW ON SITE/FETR1200/VEM/REPAIRS MADE AND CUST RESTORED 1059/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB
10437 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2010-01-31 17:37 | 2010-01-31 20:35 | 4 | 178 | 61778-1 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 33668631 // XFMR FUSE BLOWN ON POLE 37830048A20794-----CUTOUT BROKEN CALLED FOR ANOTHER MAN VER/HFP L3/HFP IDC XXXX
10438 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2008-08-28 17:14 | 2008-08-28 20:12 | 4 | 178 | H57097-1 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3401002// PRI. CONDUCTOR BROKE AT STIRRUP AND LET PRI. FALL BELOW NEUTRAL. HOT TAP IS ALL THAT IS HOLDING IT UP. I AM GOING TO OPEN LINE FUSE ON POLE 284-91 LONG ENOUGH TO REPAIR CONDUCTOR. I OPENED LINE FUSE AT 19:42, REPAIRED CONDUCTOR, AND CLOSED IT BACK IN AT 20:12.//VER/CRB IDCC OUTAGE FOR ORIGINAL CUSTOMERS OUT XXXX
10439 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2009-08-08 18:54 | 2009-08-08 22:18 | 6 | 204 | 64542-1 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR CUTOUT FAILED TAKING OUT LINE FUSE. XFMR BAD ON SAME POLE - WHEN XFMR FUSE DIDNT OPEN PROPERLY FAULTY XFMR BLEW LINE FUSE (CUTOUT DOOR TRACKED). ISOLATED AND CLOSED LINE FUSE AT 20:10 LEAVING TWO CUSTOMERS THAT ARE SERVED FROM THIS XFMR OFF. CREW ENROUTE TO CHANGE. RESTORED XFMR AT 22:18. SH IDCC ADDED STP XXXX
10440 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2019-07-06 07:44 | 2019-07-06 13:40 | 2 | 356 | 4664081 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | man. tree crew to meet at birdhouse/B MORGAN/ BAD XFERBad 15kva 7200 txmf. No trucks, Manual treecrew linecrew and 6 wheeler required.Bad 15kva 7200 txmf. No trucks, Manual treecrew linecrew and 6 wheeler required.arrived RM xfm change out power on @ 13:40 please cloce tic RM
10441 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2017-05-10 09:55 | 2017-05-10 15:51 | 2 | 356 | 4775871 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 2/3 SECONDARY DOWN FROM 69-4119 TO 4118 LINE CREW REQD. TRK TO POLE @ END OF THOMAS RELEASED BY CREW 078S07//COD 2 VER/CRB
10442 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-04-24 19:18 | 2020-04-24 22:16 | 4 | 178 | 4747511 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50 kva, single bushing 120/240, can use truck, first trailer on left from 23 coming out 503, soon as you cross the first bridge on the left Released by crew 078S06
10443 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2014-12-03 10:31 | 2014-12-03 12:00 | 8 | 89 | 4829651 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CHANGING OUT TRANSFORMER LEAKING OIL/ ISO 39831123B00487/ COD 8/ VER/BOW L3/HFP
10444 | Hazard | 3307301 | BULAN | ARY-HEINE | 2021-01-10 10:54 | 2021-01-10 12:23 | 8 | 89 | 4859621 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on pole 177-A-75, working to replace.
10445 | Pikeville | 3411801 | JOHNSCREEK | META | 2019-04-15 11:59 | 2019-04-15 17:55 | 2 | 356 | 4116251 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER & NO DISPLAY ON METER.trans cutout failed on 984-125 replaced cutout .restored power at 17:55
10446 | Hazard | 3310502 | HADDIX | CANOE | 2009-12-12 09:13 | 2009-12-12 15:09 | 2 | 356 | 61593-1 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 37830052000021- BAD 25KVA 7200 XFMR, CREW REQUIRED MANUEL ,\\\\\\ XFMR CHANGED OUT, POWER RESTORED VER/KEP L3/KEP
10447 | Hazard | 3311101 | STINNETT | REDBIRD | 2016-03-25 11:27 | 2016-03-25 14:25 | 4 | 178 | 4881681 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE GATE BURN UP CPHASE.REPLACE GATE/ ISO 37840576000090/ COD 4/ VER/BOW
10448 | Whitesburg | 3312901 | JENKINS | KONA | 2018-08-01 18:17 | 2018-08-01 20:45 | 8 | 148 | 4891401 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout is broke into 37830403B00044, I need one man this is manual location/ opened line fuse 37830403A00050 at 2015 closed at 2045
10449 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-05-07 09:49 | 2017-05-07 15:45 | 2 | 356 | 4764261 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANS//.REPLACED XFMR VER/CRB
10450 | South Williamson | 3200204 | BARRENSHE | POUNDING | 2014-01-29 15:01 | 2014-01-29 16:30 | 8 | 89 | 4324911 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT DOOR. VER/SEF
10451 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2022-01-07 08:19 | 2022-01-07 14:15 | 2 | 356 | 4318861 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 37830004B00374. MANUEL
10452 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-05-21 19:04 | 2009-05-22 01:00 | 2 | 356 | 58682-1 | 712 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ,,,BAD TRANSFORMER ON POLE 596-87 TRANSFORMER LEAKING A LITTLE POLE IS TRUCK ACCESSIBLE A 7200 25KVA IS RECOMMENDED RELEASED BY CREW 078S02 VER/PDP IDC XXXX
10453 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-11-16 18:33 | 2010-11-16 19:52 | 9 | 79 | H56441-1 | 711 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 37786173 ///....LIFTED HOT LINE CLAMP ON BAD CUTOUT (LINE FUSE) @17:45 0N POLE 1113-D-065.....CALLED 911....LOCAL FIRE DEPT ENROUTE...LINE CREW ENROUTE ALSO....//....FIRE DEPT ARRIVED....OPENED CUTOUT ON 1113-C-30 TO DE-ENERGIZE ALL CONDUCTRS ON POLE @ 18:33....FIRE EXTINGUISHED....MAKING POLE REPAIRS.....REPAIRS MADE....CLOSED CUTOUT ON 1113-C-30 @ 19:52....ALL POWER ON.....JRV....11/16/10//VER/CRB IDCC DUP TO OPEN TAP XXXX
10454 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2017-10-08 06:48 | 2017-10-08 10:45 | 3 | 237 | 4419471 | 711 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 19.9 CUTOUT ON 38830478D10292 NBT RELEASED BY CREW 078H01/ ISO 38830478D10292/ COD 3/ VER/BOW VER/HFP L3/HFP
10455 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-09-05 19:57 | 2012-09-05 21:16 | 9 | 79 | 4020171 | 711 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOK LIKE FUSE PULL INTO//COD 9// VER/DBM IDC XXXX
10456 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-11-26 15:06 | 2010-11-26 16:25 | 9 | 79 | 59928-1 | 711 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LATERAL FUSE OUT 989-A-61....NOT ON MAP.....CUTOUT DOOR BURNT UP.....MAY HAVE TO CHANGE CUTOUT...PATROLLING LATERAL 1ST.....//MADE A MD//VER/CRB IDC XXXX
10457 | Cannonsburg | 3001004 | HITCHINS | EK ROAD | 2011-08-22 10:20 | 2011-08-22 16:15 | 2 | 355 | 4742111 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BUCKET TREE CREW REQUIRED, TREES GROWING INTO OPENWIRE SECONDARY, TREE CREW IN ROUTE,, TREES CUT, BAD 25 KVA 7200 XFMR, TRUCK OK RELEASED BY CREW 078S05 //VER/CRB IDC XXXX
10458 | Pikeville | 3410602 | E.PRESTON | LANCER | 2015-03-26 19:43 | 2015-03-26 22:05 | 5 | 142 | 4232671 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLEW @ 955-160///FOUND BAD INSULATOR @ POLE 955-164///CHANGED INSULATOR OUT AND MADE REPAIRS ON POLE///CLOSED FUSE ON POLE 955-160 @ 22:05 RESTORING ALL CUST.///COMPLETE BR//COD 5// VER/DBM
10459 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-03-08 15:18 | 2016-03-08 17:40 | 5 | 142 | 4828161 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KV XFM 7200. NEED ONE MAN AND BIG BUCKET TO CHANGE OUT XFM ON POLE 48B-502.REPLACED XFM AND CLOSED BACK IN @ 17:40. COD-5 ISO TF 37830048B40502
10460 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2022-12-20 10:39 | 2022-12-20 11:50 | 10 | 71 | 4279651 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse door burnt into
10461 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-12 03:55 | 2018-02-12 09:50 | 2 | 355 | 4832821 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer, meter is blank//Dispatched in accordance with KYPCo Late Night Callout Guidelines//cutout broke on pole 767-207//going to open line fuse on pole 767-642 to climb pole and change cutout - no additional customer out ////repairs made//restored at 09:50//
10462 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-08-12 11:08 | 2011-08-12 17:03 | 2 | 355 | 4699661 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED TRUCKS OK BAD TRANSFORMER FROM 5 KVA TO 15 WAS CSP POLE ROTTEN NEW POLE ALREADY THERE NEEDS TRANSFERED OVER SEND TO MULLINS RELEASED BY CREW 078S03/CREW ON SITE/FETR1700/VEM/TECH TO WRITE JOB/REPAIRS MADE AND POWER RESTORED 1703/PLEASE CLOSE TICKET/THANKS/VEM//COD 2// VER/DBM IDC XXXX
10463 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2019-07-08 13:00 | 2019-07-08 18:55 | 2 | 355 | 4677491 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Broken 30cl6 Sec pole(AEP)--Tree crew/Line Crew/Tech needed--NO TRUCK--YD or HandSet--will need to access from 3014 29th St. ¦¦ NO CUST INITALLY OUT ¦¦Broken 30cl6 Sec pole(AEP)--Tree crew/Line Crew/Tech needed--NO TRUCK--YD or HandSet--will need to access from 3014 29th St.--Can access W/Truck & MoPads from 2949 Monroe st.Cut Sec loops on 69-1548--only 2 cust off @ 1300//ON @1855
10464 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-08-20 08:08 | 2015-08-20 10:30 | 5 | 142 | 4156491 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 374-104, REPLACED CUTOUT RESTORED POWER AT 10:30. COD-5 ISO TF 37830374D00104 VER/HFP L3/HFP
10465 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2012-04-18 10:30 | 2012-04-18 11:45 | 10 | 75 | 4681191 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WILL C HECK IN THE MORNING OF 04/18/12, POWER NOT OFF AT THIS TIME, POLE # 274-22 IS BROKE OFF AT GROUND LEVEL, CREW COMING TO REPLACE, PLEASE SEND TICKET TO TIM SMITH RELEASED BY CREW 077S02//OPENED LINE FUSE TO TRANSFER CONDUCTERS ///VER/CRB IDCC PN105 XXXX
10466 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-07-26 15:48 | 2020-07-26 18:10 | 5 | 142 | 4234681 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse on 1125-c-356 is blown, broken cutout on 1125-c-812, will be making repairs//POLE 38831125C20356 ONLY HAS 1 40T L/F//MD MADE//COD 5line fuse on 1125-c-356 is blown, broken cutout on 1125-c-812, will be making repairs. repairs made and linefuse restored at 18:10
10467 | South Williamson | 3202201 | LOVELY | LOVELY | 2016-02-13 03:06 | 2016-02-13 04:17 | 10 | 71 | 4692381 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | LEAD HAD COME LOOSE FROM BOTTOM SIDE OF CUTOUT ON 771-5 AND WAS ARCING///REPAIRS MADE//RESTORED AT 4:17//COMPLE VER/KEP
10468 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-11-17 14:52 | 2016-11-17 17:14 | 5 | 142 | 4108611 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 TRIPLEX BURNED INTO MIDSPAN,NEED 1/0,TIM HALL HAS HELP ENROUTE,SHAWN GOBLE ENROUTE/////////REPLACED COND&RESTORED,APPEARED SPLICE CONNECTIONS HEATED UP&BURNED COND DOWN 37820002000105 VER/AWD
10469 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-10-07 11:09 | 2012-10-07 13:31 | 5 | 142 | 4121271 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. RE-FUSED. SH//COD 5// IDC XXXX
10470 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-10-14 23:10 | 2021-10-15 11:00 | 1 | 710 | 4351451 | 710 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Held for daylight per KPCO late night callout guidelines. Bad 15KVA 7200 on pole 178-C1-671, truck access. Released by crew 077S04, all power restored @ 11:00 p.hicks
10471 | South Williamson | 3414302 | SIDNEY | COBURN MTN | 2021-11-18 23:31 | 2021-11-19 11:20 | 1 | 709 | 4107301 | 709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Dispatched in accordance with KYPCo Late Night Callout Guidelines..cust service wire pulled out of house knob.had to call an get someone with a taller ladder to reach it.opened transformer 1013D-261 up at 10:30 to make repairs and take slack out of secondary.got the transformer fuse on pole 1013D-261 back in @ 11:20 LR- The only call was an All Out call that came in at 23:31 on 11/18/21.
10472 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-08-26 21:39 | 2022-08-27 09:28 | 1 | 709 | 4800681 | 709 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | bad u/g, 1 cust out, hes ok with crew fixing tomorrow.will work in the am. Released by crew 076S01 // had to open xfmr on 858-b-157 to safley make repairs xfmr off@0905 both restored @0928 // send copy to bill johnson and josh smith
10473 | Hazard | 3301101 | CHAVIES | CHAVIES | 2014-08-21 22:42 | 2014-08-22 10:30 | 1 | 708 | 4399521 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED AND ADVISED CUSTOMER TO TURN MAIN BREAKER OFF UNTIL SOMEONE COMES TO CHECK THIS// REPLACED BAD 7200 CUTOUT VER/CRB
10474 | Hazard | 3308002 | JACKSON | PANBOWL | 2010-10-18 15:45 | 2010-10-18 16:44 | 12 | 59 | H60643-1 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND, WILL SET POLE AND RUN OVER HEAD OPEN TRANSFORMER AT 1545 AND CLOSED AT 1644 COD-12 NEED TO DUPLICATE IN HOIS VER/HFP L3/HFP IDC XXXX
10475 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2016-08-09 15:54 | 2016-08-09 19:50 | 3 | 236 | 4754451 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A & B PHASE CUTOUTS BROKEN. OPENING C PHASE UNTIL CREW CAN GET TO SITE.FOUND A AND B PHASE C/O BROKEN ON POLE 901-5660, CREW REQ, , ALSO C PHASE WAS STILL IN I OPENED UP C PHASE, MATERIAL LIST, 3 C/O. T GEORGE OBTAINED PERMISSION TO CUT CHAIN/TAKE DOWN FENCE.A & B PHASE CUTOUTS BROKEN. OPENING C PHASE UNTIL CREW CAN GET TO SITE.FOUND A AND B PHASE C/O BROKEN ON POLE 901-5660, CREW REQ, CAN NOT GET TRUCKS TO POLE, ISO 39830901C45660/ COD 3/ VER/BOW
10476 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-05-02 22:57 | 2011-05-03 00:55 | 6 | 118 | 53829-1 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | NO OUTAGE UNITL CREW OPENED FEEDER AT 2257, CUSTOMERS TRANSFERRED TO ALT SOURCES. RELEASED BY CREW 076S02 VER/PDP MAF IDC XXXX
10477 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2010-07-12 12:19 | 2010-07-12 16:15 | 3 | 236 | 65434-1 | 708 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD INSULINK CONNECTOR ON LASH CABLE ON XFRMER POLE...WILL REPLACE WITH DIFF CONNECTORS....//...REPLACED BAD INSULINK AND CABLE-LOCK CONNECTIONS ON BOTH HOT SECONDARY LEADS ON XFRMER...GOOD VOLTAGE NOW....JRV...07/12/10 COD-3 VER/HFP L3/HFP IDC XXXX
10478 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-12-24 12:54 | 2022-12-24 15:51 | 4 | 177 | 4346511 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | One of hot legs burned into at bushing,Will be making repairs..Have a bad 50 KVA Trans,Crew on the way to help make repairs.Have a bad 50 KVA Trans,Crew on the way to help make repairs.Restored at 15:51..
10479 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-09-20 18:04 | 2009-09-20 22:00 | 3 | 236 | 55765-1 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000301 WR # 31800351 //WR/31800351 BAD CUTOUTS ON POLE 20-7584 SEND TO BILL FRALEYWR/31800351 BAD CUTOUTS ON POLE 20-7584 SEND TO BILL FRALEY RELEASED BY CREW 078S08 IDC XXXX
10480 | Paintsville | 3409302 | KENWOOD | AUXIER | 2021-01-06 11:19 | 2021-01-06 15:15 | 3 | 236 | 4851881 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Underground service has faulted causing the TR fuse to blow--replacing servicexfmr fuse blown on 882-b-530//bad u/g service///crew enroute//xfmr fuse blown on 882-b-530//bad u/g service///crew enroute//repairs made//restored at 15:15//complete//em
10481 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2018-03-09 10:58 | 2018-03-09 13:55 | 4 | 177 | 4981531 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva, single bushing, 7200 120/240 v can use trucks, right behind wrights motel in alley, crew req. Released by crew 078S06 crew on site FETR 14:00/ ISO 39831072C45599/ COD 4
10482 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-06-20 19:11 | 2015-06-20 21:09 | 6 | 118 | 4622551 | 708 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE PULLED INTO, REFUSED AT 2109. COD-6 ISO TF 37830375A00312 VER/HFP L3/HFP
10483 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2012-03-04 09:22 | 2012-03-04 15:15 | 2 | 353 | 4543671 | 706 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | P TOLLIVER GAVE PERMISSION TO WORK ON HIS CIRCUIT//LMR. REPLACED SOME MELTED CONNECTIONS, XMF LEAKING BAD. TRIED FUSE, WOULD NOT HOLD. BAD 25KVA 19.9 XMF. WILL REQUIRE FLAGGING CREW AND HIGHLINE BUCKET ONLY WAY TO CHANGE XMF. ALL REPAIRES MADE ALL POWER RESTORED AT 1515 CLOSE TICKET //VER/CRB
10484 | Hazard | 3303903 | LESLIE | HALSFORK | 2010-04-02 13:24 | 2010-04-02 17:19 | 3 | 235 | 57398-1 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKEN, NEED CUTOUT /ARR, AND FIBERGLASS TEE BRACKET FOR 7.2 KV RELEASED BY CREW 077H01 // VER/KEP IDC XXXX
10485 | Hazard | 3307301 | BULAN | ARY-HEINE | 2012-01-06 07:20 | 2012-01-06 11:15 | 3 | 235 | 4236621 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA CSP TRANSFORMER, MIKE LEWIS CHECKED LOAD, NEED TO INSTALL 50 KVA HERE. NEED BIG BUCKET, LINE CREW, FLAGGERS, CUTOUT AND ARRESTOR, 7200 VOLTS. RELEASED BY CREW 077S04 INSTALLED NEW XFMR RESTORED POWERAT 1115 CREW 077H01//COD 3// VER/DBM IDC XXXX
10486 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2012-10-18 00:48 | 2012-10-18 04:43 | 3 | 235 | 4151271 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR. RICK RAY IS ON WAY WITH XFR. CC 3. REST AT 0443. VER/SDB IDC XXXX
10487 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2012-04-19 13:30 | 2012-04-19 17:25 | 3 | 235 | 4687671 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED FUSE TO REPLACE POLE ///VER/CRB IDC XXXX
10488 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-06-16 20:22 | 2009-06-17 00:17 | 3 | 235 | 63023-1 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | TREES GROWN UP INTO LINES HAD TWO FUSES BLOWN ON POLE 231-10 ONLY HAD 3 CUSTOMERS OUT OF POWER RESTORED POWER AT 0017 077H01//VER/CRB
10489 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2021-04-28 19:43 | 2021-04-28 20:30 | 15 | 47 | 4489901 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cut out, arrestor , or ptp is going bad needs changed out manual will take outage and line crew to make repairs. it has quite for now rain will start it back. Released by crew 077S12. // opened line fuse @1943 repaired and restored at 2030
10490 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2009-04-09 11:59 | 2009-04-09 14:20 | 5 | 141 | 50722-1 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3308602// REPLACED SERVICE DROP//COD 5 IDCC CNT6 XXXX
10491 | Hazard | 3308001 | JACKSON | S.JACKSON | 2016-01-24 20:09 | 2016-01-25 00:04 | 3 | 235 | 4648041 | 705 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 72 CUTOUT---RONNIE COMING TO HELP---
10492 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2013-03-26 03:23 | 2013-03-26 09:15 | 2 | 352 | 4958981 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL CHECK AT REGULAT WORK TIME FUSE LINK APPEARS TO HAVE BROKEN. REFUSED @ 9:15. SH COD-2 ISO TF 38830834A00662 VER/HFP L3/HFP IDC XXXX
10493 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2020-06-27 21:03 | 2020-06-27 22:07 | 11 | 64 | 4081521 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Think fuse pole 39831099D16039 is out but mapping issues rolled it to intellirupter. Line fuse restored @ 22:07///fuse broke (added 1 customer to count because there was one address that was mismapped and servicer verified should be fed from this line fuse)
10494 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2014-02-04 14:40 | 2014-02-04 15:12 | 22 | 32 | 4347901 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | GREG FUGATE TO OPEN LINE TO FIX BAD SPOT IN PRIMARY OPEN @______ CLOSE @_______GREG FUGATE TO OPEN LINE TO FIX BAD SPOT IN PRIMARY,,, OPENED FUSE ON POLE 37830273C10328 AT 14:40, CLOSED AT 15:12 VER/SEF IDC XXXX
10495 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2019-09-16 18:38 | 2019-09-17 00:30 | 2 | 352 | 4026101 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10t fuse out due to bad 50kva transformer. need 50kva 7200 can use truck also need flagging crew. changed bad 50kva transformer everything ok/ ISO 37830164000043/ COD 2
10496 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2010-08-18 20:11 | 2010-08-18 21:15 | 11 | 64 | 57899-1 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 91-630 BURNT OFF MADE TEP. REPAIRES SEND TO TEC. 30 CLASS 5 CO. POLE NEEDS REPLACED POLE 91-332 15T ON 21;15 BAD CUTOUT OR LA VER/KEP L3/KEP IDC XXXX
10497 | Pikeville | 3408103 | SALISBURY | MARTIN | 2015-12-27 09:17 | 2015-12-27 10:45 | 8 | 88 | 4563721 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | INSTALLED COVER ON XFMR BUSHING AND RISER, REPLACED CUTOUT AND FAILED ARRESTER, ALL WORK COMPLETE / GXJ// VER/ ADH
10498 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2011-08-05 10:44 | 2011-08-05 13:40 | 4 | 176 | 4667491 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER--NEED BIG BUCKET TO CHANGE OUT--HELP IS ON THE WAY RELEASED BY CREW 077S10//VER/CRB IDC XXXX
10499 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2020-05-31 08:26 | 2020-05-31 11:22 | 4 | 176 | 4935961 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole 37830270C00131. Released by crew 077H20.. all power restored @ 11:22 hrs..p.hicks
10500 | South Williamson | 2150103 | SPRIGG | SPRIGG | 2016-11-17 11:45 | 2016-11-17 12:17 | 22 | 32 | 4107131 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | KY CREW REPLACING POLE 38820992C00020/ ISO 38820992C00142/ COD 22/// CREW ON SITE./// OFF AT 11:45 BACK ON AT 12:17 TIM MCCOY/ VER/BOW L3/HFP HFPC CNT2 AJB
10501 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-04-11 10:42 | 2020-04-11 16:34 | 2 | 352 | 4620901 | 704 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on pole37830004C00014 replaced power ok
10502 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-06-20 18:13 | 2009-06-20 18:50 | 19 | 37 | 50344-1 | 703 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK IDC XXXX
10503 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-03-06 11:17 | 2015-03-06 23:00 | 1 | 703 | 4148781 | 703 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND CAN USE TEMP. HAVE WHO WORKS THIS CALL CALL ME WILL NEED TO TALK TO THEM DANNY NEED TO BRING ON PICKUP CLEAN DRIVE WAY RELEASED BY CREW 078S08 RESTORED 3-6-15 2300 VER/KEP
10504 | Hazard | 3303903 | LESLIE | HALSFORK | 2016-11-19 10:47 | 2016-11-19 11:24 | 19 | 37 | 4111801 | 703 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON LOAD SIDE OF STEPDOWN BAD === NEED LINE CREW OR 2 MEN AND BIG BUCKET AND 2 CUTOUTS AND T BRACKET --=== RELEASED BY CREW 077S03 OPENED AT 10;47 TO MAKE REPAIRS ::POWER RESTORED AT 11:24 VER/CRB VER/HFP XXXHFP
10505 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2022-12-28 16:10 | 2022-12-28 20:04 | 3 | 234 | 4372551 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200 120-240 25kva transformer truck ok crew required Released by crew 078S09.. repairs made xfm restored @ 20:04 on 44-D-7030 complete LG
10506 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2009-12-02 22:49 | 2009-12-02 23:15 | 27 | 26 | 60142-1 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ON SITE, BAD CUTOUT, CALLED R MARCUM FOR BIG BUCKET, POLE# 1088-43 NEED FUSE SIZE FOR MD. ON SITE, BAD CUTOUT, CALLED R MARCUM FOR BIG BUCKET, POLE# 1088-43, OPENED LINE FUSE AT POLE#1088-A-140 AT 2249,//10T FUSE//COD 27 IDC XXXX
10507 | South Williamson | 3411401 | DEWEY | INEZ | 2019-12-14 07:27 | 2019-12-14 11:21 | 3 | 234 | 4152761 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: no reading on meter,,bad cutout on 742-77 blew line fuse on 742-22, changing // Iso 38830742D00022 COD 3
10508 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2009-02-04 05:29 | 2009-02-04 11:20 | 2 | 351 | 55357-1 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 3410501//NEED TO REPLACE A 25 KVA U.G. TRANSFORMER 7200 KV MAY NEED TO REPLACE WITH A 50 KVA. ROAD IS SNOW COVER BE CAREFUL.SEND TO TIM HALL CREW RELEASED BY CREW 074S05. CREW 074H03 ON SITE, REPLACING TRANSFORMER. COD-2 VER/KEP L3/KEP
10509 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2012-07-06 12:09 | 2012-07-06 18:00 | 2 | 351 | 4541771 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN //WILL REFUSE//BAD 15 KVA //NEEDS CHANGED TO 25 KVA /// TRUCK APP.// CREW REQ. RELEASED BY CREW 074H14
10510 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2015-05-31 06:23 | 2015-05-31 08:20 | 6 | 117 | 4487091 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSTA LINK FAILED AND BURNT NEUTRAL INTO VER/KEP
10511 | South Williamson | 3200301 | BELFRY | BELFRY | 2014-09-29 10:13 | 2014-09-29 10:52 | 18 | 39 | 4535421 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE 1014-C2-50. VER/CRB L3/HFP
10512 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-06-09 22:07 | 2016-06-10 09:49 | 1 | 702 | 4330611 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA TRANSFORMER SINGLE BUSHING 7200 KV 120/240 CREW REQ, TRUCKS YES RELEASED BY CREW 078S09/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0949/PLEASE CLOSE TICKET/THANKS/VEM COD-1 ISO TF 39831047000040 VER/HFP L3/HFP
10513 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2017-08-10 13:51 | 2017-08-10 17:45 | 3 | 234 | 4247341 | 702 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED XFMR CUTOUT , ALL WORK COMPLETE / GXJ 38831121000117 VER/AWD
10514 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2014-06-04 23:19 | 2014-06-05 11:00 | 1 | 701 | 4980261 | 701 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL CHECK THIS FIRST THING 06/05/14 BAD WESTINGHOUSE CUTOUT, HAVE CHANGED AND POWER IS RESTORED AT THIS LOC AT 1100 VER/SEF
10515 | Hazard | 3308001 | JACKSON | S.JACKSON | 2015-02-18 19:58 | 2015-02-18 21:38 | 7 | 100 | 4040381 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP , CUTOUT WAS GOOD . CHANGED CUTOUT . CLOSED XFMR @ 21:38 7 CUST. ON XFMR . FAULT POLE 38831108A00402 VER/CRB L3/HFP XXX
10516 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2020-03-08 13:25 | 2020-03-08 16:20 | 4 | 175 | 4460961 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout failed. Replacing. Restored @ 16:20. sh Released by crew 076S02
10517 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2013-10-10 16:35 | 2013-10-10 18:15 | 7 | 100 | 4928531 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , REPLACED. COD-7 ISO TF 37830272A30707 VER/HFP L3/HFP
10518 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-08-02 05:11 | 2009-08-02 06:51 | 7 | 100 | 58708-1 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3001203-BROKEN FUSE LINK VER/LDA IDC XXXX
10519 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2009-02-10 23:55 | 2009-02-11 02:50 | 4 | 175 | 57574-1 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-4 SERVICER OPENED TRANSFORMER TO REPLACE BAD CONNECTIONS ON TRANSFORMER RISER WIRES. OUTAGE NECESSARY TO REPAIR PROBLEM ON TROUBLE ORDER 57537-1 L3/HFP
10520 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2018-01-14 05:45 | 2018-01-14 11:35 | 2 | 350 | 4745891 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200/// No truck/// Need line crew/// Replaced bad Xfm and changed cutout// Restored service @ 11:35
10521 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2017-11-14 10:20 | 2017-11-14 10:45 | 28 | 25 | 90003431 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | crew required pole 270-18 broke at deadend shoe no trucks primary only 1 customer at 270-263/ will have to have outage on 270-18 line fuse to repair/ opened line fuse and transformer on pole 38830270D00018/ ISO 38830270D00018/ COD 29/ 1020-1045/ 38830270D00263 shows no customers on map but per servicers comments there was 1 customer off who was shown to be on pole 38830270D00018
10522 | Pikeville | 3408103 | SALISBURY | MARTIN | 2017-03-17 11:25 | 2017-03-17 14:20 | 4 | 175 | 4564551 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT BROKE ON 1098-33. REPLACED AND RESTORED @ 14:20. SH/ ISO 38831098C00033/ COD 4/ VER/BOW
10523 | South Williamson | 3411401 | DEWEY | INEZ | 2014-09-19 11:20 | 2014-09-19 11:48 | 25 | 28 | 4511321 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SERVICER DE-ENERGIZING STEPDOWN TRANSFORMER 768-D2-62 TO CHANGE CUT-OUT GOING BAD.// COD 25// VER/ ADH AJB
10524 | Hazard | 3303902 | LESLIE | WOOTON | 2010-05-01 20:35 | 2010-05-01 23:30 | 4 | 175 | 53467-1 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE //VER/GAH IDC XXXX
10525 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2008-11-21 22:00 | 2008-11-21 23:10 | 10 | 70 | 50735-1 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 3400303// BAD 25KVA PAD MOUNT TRANSFORMER. I CALLED WILLIE HE IS CALLING A CREW TO HEAD THIS WAY // OPEN @ RISER POLE 1126-823 TO ISOLATE AND CHANGE PAD MOUNT// OPENED @ 2200 AND CLOSED @ 2310 // VER/TOM IDCC CDC92 XXXX
10526 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2011-01-05 08:55 | 2011-01-05 10:05 | 10 | 70 | 58838-1 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LEAD BURNED OFF , IOPENED XFMR AND REPLACED LEAD M.D.I. VER/KEP L3/KEP IDC XXXX
10527 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2011-09-02 15:50 | 2011-09-02 16:40 | 14 | 50 | H4785541 | 700 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WE HAVE PARTIAL POWER COMING TO A PEDESTAL IN TRL. PARK. SECONDARY IS OPEN SOEWHERE. DENNIS IS SENDING HELP. WE OPENED TRANS. AT 15:50 AND CLOSED IT IN AFTER REPAIRS AT 16:40.//COD 15// VER/DBM IDCC DUP CREATED TO OPEN TRANFORMER XXXX
10528 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-05-22 10:59 | 2014-05-22 16:49 | 2 | 350 | 4739451 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 078H22.. BAD 25 KVA CSP XFMR .. SPOKE WITH CUST AND SHE SAID IT WAS OK TO BACK TRUCK IN YARD.. CREW REQUIRED MATERIAL HANDLER BUCKET RELEASED BY CREW 078H22/CREW ON SITE/FETR1730/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST@1649/PLEASE CLOSE TICKET/THANKS/VEM VER/SEF
10529 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2018-04-12 13:57 | 2018-04-13 01:37 | 1 | 700 | 4214781 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | Secondary pole 45-c2-4751 broke, at the corner of 17th st and montgomery, need to bring roll of 4/2, trucks to pole, need line crew, and flaggers.---crew on site--38830045C24583--opened xfmr 38830045C24583 @ 0059--closed @ 01:37---all repairs made--number of customers out not correct--tbl tkt comp--rmv Released by crew 078H16//iso//cod 1
10530 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-06-29 08:15 | 2021-06-29 14:05 | 2 | 350 | 4820721 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7200 by truck that feeds a light green barn used to store equipment Released by crew 078H03 Ticket complete KMG
10531 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-04-20 11:00 | 2014-04-20 13:55 | 4 | 175 | 4618561-1 | 700 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CUST. HAS 92V ON EACH HOT LEG AND 187V ACROSS, FUSE BLOWN ON XFMR BANK. 4TH TIME ITS BLOWN, NEED TO CHANGE OUT 50KV 7200, MANUAL NEED POLE JIB. GATE AT SCHOOL HAS COMPANY LOCK ON IT, GO IN GATE ON STRONGS BR. NEED R/W CREW MANUAL, NEED 4 MAN LINE CREW. FORMAN, 2 AS, 1 COR D. BEHIND SCHOOL ON HILL! // ARCOS @ 0800 - P.HICKMAN, R.RICE, M.EMBERTON, B. CLEMONS// OUT - 1100 TO 1355 ON 4-20-14 //VER/GAH
10532 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2016-11-04 11:07 | 2016-11-04 13:27 | 5 | 140 | 4075321 | 700 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT TRANSFORMER. NEED BIG BUCKET.BAD CONNECTION @ XFMER COMPLETE VER/AWD
10533 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2011-06-11 19:19 | 2011-06-11 23:12 | 3 | 233 | 4297901 | 699 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LATERAL FUSE OT ON 1037D51.BAD XFMR CUTOUT ON 1037D156..WILL REPLACE CUTOUT & RE-FUSE LATERAL..//.REPLACED CUTOUT & RE-FUSED LATERAL..JRV...06/11/11 //VER/GAH
10534 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2013-06-13 22:21 | 2013-06-14 10:00 | 1 | 699 | 4321541 | 699 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANS 25KVA 19.9 IN BACK YARD HAND JOB CREW REQUIRED RELEASED BY CREW 074H15//COMPLETED 1000 6-14-13 PER ROBY BLAIR//COD 1// VER/DBM IDC XXXX
10535 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2010-08-26 07:02 | 2010-08-26 10:55 | 3 | 233 | 60650-1 | 699 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 36610833 //,, BAD 50KVA 7200 CSP, NEED NEW XFMR, CUTOUT, POLE BRACKET, TRUCK OK RELEASED BY CREW 078S05 TOOK LINE FUSE OUT AT 10;30 BACK ON AT 10;55 SEE H1141350-1 FOR FUSE OUTAGE VER/HFP L3/HFP IDCC TON1100 XXXX
10536 | South Williamson | 2150501 | BORDERLAND STA | NOLAN | 2020-03-29 16:47 | 2020-03-29 20:40 | 3 | 233 | 4535261 | 699 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | trans secondary riser fell out of lug.replaced lug.opened trans on 868D117 at 20:14,made repairs,restored power at 20:40
10537 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-02-06 18:00 | 2008-02-06 21:53 | 3 | 233 | 51876-1 | 699 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3407101// BAD CUTOUT ON POLE 210-95. WILL BE CHANGING OUT. VER/HFP IDC XXXX
10538 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2008-06-04 15:41 | 2008-06-04 21:30 | 2 | 349 | 56458-1 | 698 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401702//NEED TO REPLACE 199KV 120/240 TRANSFORMER. WILL NEED TO REWIRE SEC. SIDE OF TRANSFORMER HAS 4 SOLID IN IT NOW//NEED TO REPLACE 199KV 120/240 TRANSFORMER. WILL NEED TO REWIRE SEC. SIDE OF TRANSFORMER HAS 4 SOLID IN IT NOW. RELEASED BY CREW 074S08 COD-2 VER/KEP
10539 | Hazard | 3310501 | HADDIX | QUICKSAND | 2020-05-19 07:15 | 2020-05-19 13:04 | 2 | 349 | 4853241 | 698 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 38831062000045 \\ calling for crewgot broke cutout on pole 38831062000045, need two cutouts fo 19.9 big bucket and flagmen Released by crew 077S05
10540 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2012-08-14 11:07 | 2012-08-14 22:45 | 1 | 698 | 4935481 | 698 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 10 KVA TRUCKS OK RELEASED BY CREW 078S03//COD 1// VER/DBM IDC XXXX
10541 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-08-08 16:22 | 2009-08-08 22:10 | 2 | 348 | 63946-1 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR 31140087 // POLE 20-6053 NEED CUTOUT AND LA POLE 20-9002 NEED CUTOUT 100T LINE FUSE// COD 2 ALSO BAD 15 KVA TRANSFORMER ON POLE 20-6063 ALL POWER RESTORED AT 22:10 IDCC PN5063 XXXX
10542 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2016-06-22 14:34 | 2016-06-22 17:28 | 4 | 174 | 4408921 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 20T LINE FUSE HAD BROKE AT POLE 37820054000121. REPLACED THE FUSE AND POWER IS RESTORED AT 17:28. ENTERED MD VER/HFP L3/HFP
10543 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2022-02-24 09:34 | 2022-02-24 11:30 | 6 | 116 | 4539371 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout door, replacing cutout. Changed cotout, closed at 11:30. Voltage good Ticket complete
10544 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-03-20 08:43 | 2018-03-20 14:31 | 2 | 348 | 4029631 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 6T line fuse on pole 38820770D00081 was blowed. I replaced a bad cutout at pole 38820770D00160. Power restored at 14:31.
10545 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-12-03 07:08 | 2014-12-03 11:00 | 3 | 232 | 4828541 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE F ON SIDETAP HERE IS OUT,WILL RE-FUSE IF CLEAR////////NEED CREW,EPOXILATOR DE INSULATOR NEEDS REPLACED,CREW ENROUTE////////MADE REPAIRS AND RESTORED/ ISO 38821058C00052/ COD 3/ VER/BOW
10546 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-01-17 08:12 | 2009-01-17 14:00 | 2 | 348 | 57027-1 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD-2 WR # 28105410 /// TRANS. FUSE HAS MELTED OUT. I AM GOING TO REFUSE TRANS. TRANSFORMER IS BAD ON POLE 50-32. IT IS A 10 KVA VOLTAGE IS 19.9. TRUCK ACCESSIBLE. WILLIE IS GETTING ANOTHER CREW OUT TO CHANGE THIS. RELEASED CREBY CREW 074S01 CREW ON SITE TAKE ABOUT AN HOUR R RAY L3/HFP
10547 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2021-07-12 22:59 | 2021-07-13 10:35 | 1 | 696 | 4902961 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held per KPCO late night callout guidelines replaced broke cutout and repaird secondery
10548 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-12-22 21:41 | 2008-12-22 23:08 | 8 | 87 | 62839-1 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | 3402001//1 PHASE OF SECONDARY LEAD BURNT OFF//OPENED TRANSFORMER TO RE-SQUEEZE RISE//COD 8 COMPLTED REPAIRS AND REENERGIZED TRANS. AT 23:08 // VER/KEP L3/KEP IDC CHANGED TIME OFF FROM 2039 XXXX
10549 | Hazard | 3309301 | VICCO | REDFOX | 2009-08-11 23:04 | 2009-08-12 10:40 | 1 | 696 | 59223-1 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE OUT, CHECKING LINE///FOUND DEADEND INSULATOR BROKEN, WILL TRY TO REPLACE IT WITH MY BUCKET, AS SOON AS IT QUITS RAINING AND LIGHTENING QUITS. DECIDED TO WAIT TILL DAYLIGHT, CAUTION HORNETS NEST NEAR POLE. HORNETS-1 RANDY-0. POLE FAULTED IS 349-161. IN HEAD WERE RD FORKS TURN RT. BEFORE FUSE POLE FOLLOW RD TO POLE, POLE ON LEFT SIDE, TWO MEN AND BUCKET- CASE OF HORNET SPRAY// IDCC PN163, CDC83 XXXX
10550 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2020-12-31 18:16 | 2020-12-31 21:10 | 4 | 174 | 4839591 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, got greg shouse coming to grunt for me to change cutout
10551 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-12-11 19:27 | 2012-12-12 01:15 | 2 | 348 | 4462371 | 696 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSBAD 15 KVA// NEED CREW/// 25KVA// CUTOUT//FIBERGLASS BRACKET// 7200// MANUAL VER/PDP FER/PDP
10552 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2020-01-21 18:03 | 2020-01-21 19:30 | 8 | 87 | 4326701 | 696 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | sec conductor shorted out on 11137-A3-728 burning sec nuetral in two.opened trans on 1137-A-612at 18:03 made repairs restored power at 19:30 cod 8
10553 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2011-01-24 22:58 | 2011-01-25 10:33 | 1 | 695 | 64025-1 | 695 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE OUT....ON HILLSIDE....NEW INSTALLATION AFTER LAST WINTERS SNOW STORM....WILL RE-FUSE..//...BAD XFMR....RE-FUSED XFMR....FUSE DID NOT BLOW, BUT NO POWER COMING OUT OF LOW SIDE OX XFMR....NEED CREW...NO TRUCK ACCESS...XFMR POLE ON HILLSIDE....CALLED JOEY REED.....HE SAYS HE WILL WORK IT AT START TIME (7:30) IN MORNING....PLEASE HOLD TICKET FOR HIM....TALKED TO CUST....THATS OK WITH HIM TOO.....JRV...01/25/11 RELEASED BY CREW 080S01 //VER/CRB IDC XXXX
10554 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2009-06-18 11:15 | 2009-06-18 22:50 | 1 | 695 | 55760-1 | 695 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | PARTIAL POWER...U/G HAS 1 LEG OUT...CALLING MILLER..PUT ON AUTO TRANSFORMER CUST HAS FULL POWER UNTIL WE GET U/G REPLACED .BB//VER/CRB IDC XXXX
10555 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2016-07-07 13:01 | 2016-07-07 15:20 | 5 | 139 | 4556711 | 695 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | HOT LEG BURNED INTO AT SPLICE ON SERVICE DROP///MAKING REPAIRS//REPAIRS MADE//RESTORED TO NORMAL AT 15:20//COMPLETE//EM VER/AWD
10556 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-07-31 18:08 | 2009-07-31 23:55 | 2 | 347 | 53606-1 | 694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308402 BAD CUTOUT == NEED 1 MAN == REPLACED CUTOUT == POWER OK IDC XXXX
10557 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2008-01-25 11:23 | 2008-01-25 17:10 | 2 | 347 | 59830-1 | 694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309902//BAD 25 KVA TRANS//VER/CRB IDC XXXX
10558 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2014-07-01 05:57 | 2014-07-01 11:44 | 2 | 347 | 4177251 | 694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL DISPATCH AT START OF REGULAR SHIFT./// BROKE CUTOUT// WILL REPLACE// CHANGED CUTOUT & BAD ARRESTER// POWER RESTORED @ 11:44 VER/HFP L3/HFP
10559 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2015-10-03 17:26 | 2015-10-03 23:13 | 2 | 347 | 4312181 | 694 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100 KVA 7200 TRANS. AT POLE 375-351, WILL NEED 1 MAN TO HELP CHANGE. CHANGED OUT TRANS., CLOSED BACK IN AT 2313. VER/TOM L3/TOM
10560 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2016-01-19 02:51 | 2016-01-19 04:30 | 7 | 99 | 4630671 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OPEN AT POLE 375-342, WILL BE CHECKING. LINE FUSE MELTED OUT, CLOSED BACK IN AT 0430.//COD 7// VER/DBM
10561 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-08-03 08:01 | 2014-08-03 09:40 | 7 | 99 | 4326181 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 8T XFMR FUSE POLE 44-7081 MP VER/CRB
10562 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2022-12-29 05:09 | 2022-12-29 09:00 | 3 | 231 | 4373611 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Dispatched in accordance with KYPCo Late Night Callout GuidelinesTrans open at 145-320,Will be getting it back in..Trans open at 145-320,Will be getting it back in..Had a broke fuse repaired and restored 09:00..
10563 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2011-12-21 10:54 | 2011-12-21 14:45 | 3 | 231 | 4192881 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-1795 BAD CUTOUT LINE CREW TRUCK TO POLE OK RELEASED BY CREW 078S08//COD 3//BAD CROSSARM AND 3-CUTOUTS SENT FOR MATERIAL P R TOLLIVER//OPENED FUSES ON POLE 45-1593 (COD +1) TO REPLACE ARM///POWER RESTORED AT 14:45 PRTOLLIVER IDC XXXX
10564 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2014-01-24 07:55 | 2014-01-24 19:28 | 1 | 693 | 4306691 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | 2 FUSES BLEW ON PRI UNDERGR POLE 45-8167,OPEN 3TD FUSE PRI BUSHING BLEW OUT ON 3PH XFORM 500KVA 120/208 LINECREW REQ. SEND TOR.VIRGIN RELEASED BY CREW 078S04///CHANGING OUT BAD PAD MOUNT///PAD MOUNT CHANGED FINISHING UP SEC. SIDE///METERING FINISHING CTS///PWR BACK ON @ 19:28//COULD NOT GET AHOLD OF CUSTOMER TO TURN ON MAINS, LEFT MESSAGE NO RESPONCE///IF CUST CALLS BACK LET THEM KNOW ALL CHECKED OUT GOOD AND TO TURN ON THERE MAINS///COD 1?//ISO 38830045C14406 IDCC PN4406 XXXX
10565 | Hazard | 3308401 | BECKHAM | HINDMAN | 2014-01-11 07:51 | 2014-01-11 09:30 | 7 | 99 | 4271011 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE C/O BROKEN ON POLE 37830178A00019, HAVE TWO TAPS OFF// REPLACED C/O, POWER RESTORED - MAP DISC ENTERED// VER/TOM L3/TOM
10566 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-12-15 08:46 | 2013-12-15 09:49 | 11 | 63 | 4162801 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | DIP. FUSE BLOWN ON 37830047C10569//WILL REFUSE// FUSE APPEARED TO HAVE BROKE// POWER IS RESTORED VER/CRB L3/HFP IDC XXXX
10567 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2010-05-04 09:07 | 2010-05-04 12:58 | 3 | 231 | 55496-1 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 34958196 /// BAD 25KVA 19.9 TRANSFORMER; CREW REQUIRED; NOT TRUCK ACCESSABLE; COD-3 VER/HFP L3/HFP IDC XXXX
10568 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2015-03-23 14:57 | 2015-03-23 15:30 | 21 | 33 | 4219321 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | PRI. IS OFF INS. @ POLE 37820025B00383// CREW ENROUTE TO REPAIR/WILL BE OPENING LINE FUSE 25-B-3 WHEN CREW ARRCIVES TO SAFELY MAKE REPAIRS// OPENED L/F ON 25-3 @ 14:57 // CLOSE @ 15:30// TREE IN R/W FROM POLE 25-6 TO 25-383 NEEDS CUT // SEND TO R/W/EMAILED RW/ADH/COD 21// VER/ ADH AJB
10569 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-08-15 07:15 | 2008-08-15 08:54 | 7 | 99 | 52163-1 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3308602// FUSE LINK HAS DETERRIORATED AND BROKEN APART // VER/TOM IDC XXXX
10570 | Pikeville | 3421301 | RACCOON | ZEBULON | 2022-01-02 22:19 | 2022-01-03 09:52 | 1 | 693 | 4262821 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout on pole 1105C-248.cutout was arcing when i arrived.this is what caused our operations because this one span tap is not fused..i got the broke cutout iso on pole 248.will be crew req.non truck.pole is about 30yards off the gravel road..could use truck if ground was dry Released by crew 079S03//// Crew onsite.. Replaced C/O+arrester and restored @09:52
10571 | Pikeville | 3421001 | BREAKS | CITY | 2011-01-18 16:17 | 2011-01-18 16:50 | 21 | 33 | 62366-1 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED FAILED CUTOUT ON POLE 244-1//VER/CRB. IDCC CNT1 XXXX
10572 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2015-10-10 15:46 | 2015-10-10 17:25 | 7 | 99 | 4337131 | 693 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1099-140 BAD CUTOUT AND OLD LA CHGED BOTH/ ISO 39831099B10140/ COD 7/ VER/BOW L3/HFP XXXHFP
10573 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2009-08-09 12:44 | 2009-08-09 18:30 | 2 | 346 | 66440-1 | 692 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 1124-3042 BAD 25KVA TRANS. CALLED CREW WR31140829 RELEASED BY CREW 078S08 POWER RESTORED @ 18:30//COD 11// VER/DBM IDC CHANGED PN FROM 1618 AND COUNT FROM 11 XXXX
10574 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2015-10-08 09:50 | 2015-10-08 15:36 | 2 | 346 | 4327871 | 692 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFMR // @ 1443 CREW OPENED LINE FUSE TO SAFELY REPLACE BAD TRANSFORMER (25 CUST OUTAGED - 2 INITALLY OUT) ALL ON 1536 SEE DUP 4227871 FOR FUSE OUTAGE SEE H4327871 FOR FUSE OUTAGE VER/HFP L3/HFP
10575 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-08-13 23:07 | 2014-08-14 10:38 | 1 | 691 | 4367841 | 691 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | SECONDARY BUSHING BAD ON XFMR . NEED 15KVA 7200 XFMR & NEW CUTOUT & TBRACKET . CUST SAID WOULD BE OK TO CHANGE OUT IN THE MORNING . CUST HAS PART POWER NOW . CAN WORK POLE WITH BUCKET . SEPTIC TANK IS JUST PAST ROUND ROCK IN YARD . RELEASED BY CREW 075H04
10576 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-09-26 16:36 | 2014-09-26 17:45 | 10 | 69 | 4531371 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE 116-B-545 VER/CRB
10577 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2021-03-23 13:51 | 2021-03-23 17:41 | 3 | 230 | 4366281 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 254-153, T Smith crew coming to replace
10578 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2011-03-24 02:00 | 2011-03-24 13:30 | 1 | 690 | 57993-1 | 690 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | FOUND NEUTRAL BROKEN ON 4/3 SERVICE DROP, THIS IS A TREE AROUND POLE, AND I NEED TO CLIMB THIS POLE, CAN NOT GET TRUCK TO IT, TALKED TO CUST, SAID IT WOULD BE OK TO WAIT TILL TOMMOROW, TO TAKE CARE OF THIS ONE, I OPENED UP TRANSFORMER(@ APPROX 0200) TO KEEP FROM BURNING UP CUST STUFF, HOLD TILL TOMMORROW RELEASED BY CREW 078S06//COD 1// VER/DBM IDC XXXX
10579 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2015-12-03 19:42 | 2015-12-03 20:51 | 10 | 69 | 4508661 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE 833-227 BLEW///THE FUSE LINK HAD BROKE///REFUSED AT 20:51///COMPLETE BR/ ISO 38830833D00227/ COD 10/ VER/BOW
10580 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2014-07-30 13:15 | 2014-07-30 13:45 | 23 | 30 | 4310131 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | ISO 38830188B00373/// COD 23 AJB
10581 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2009-09-09 20:43 | 2009-09-10 00:33 | 3 | 230 | 61941-1 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WORK REQ # 31645988 //ONLY 1 CUSTOMER ON THIS TRANSFORMER-BAD 25 KVA TRANSFORMER-SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE /FETR0100/09-10-09/VEM/XFMR CHANGED/CUST RESTORED 0033/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
10582 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2020-01-02 12:32 | 2020-01-02 14:50 | 5 | 138 | 4204011 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | trans fuse failed on 1089-A-221.no hazards seen.restoredpower at 14:50.
10583 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2009-01-13 06:45 | 2009-01-13 12:30 | 2 | 345 | 54607-1 | 690 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28041075 // 25 KVA CSP TRANSFORMER BAD / GXJ RELEASED BY CREW 074S03 COD-2 L3/HFP IDC XXXX
10584 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2009-02-02 00:16 | 2009-02-02 11:45 | 1 | 689 | 54386-1 | 689 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL DISPATCH SERVR AT DAYLIGHT. SECONDARY LUG FAILED ON THE TRANSFORMER BANK. I REPLACED A SECTION OF THE RISER AND THE LUGS. VER/KEP L3/KEP
10585 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-03-13 18:37 | 2018-03-13 19:30 | 13 | 53 | 4012741 | 689 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 37830247D00941. Line fuse open 37830247D00852.Replaced cutout. Restored l/f at
10586 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-10-18 23:46 | 2013-10-19 11:15 | 1 | 689 | 4947661 | 689 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK DURING NORMAL WORK HOURS 10-19-13 RELEASED BY CREW 076S01WILL WORK DURING NORMAL WORK HOURS 10-19-13 ..FUSE LINK ON TRANSFORMER BROKEN.WILL WORK DURING NORMAL WORK HOURS 10-19-13 ..FUSE LINK ON TRANSFORMER BROKEN.REPLACED FUSE.//COD 1// VER/DBM L3/HFP IDC XXXX
10587 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2020-07-31 20:11 | 2020-08-01 00:01 | 3 | 230 | 4266371 | 689 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DOL 1041437// CKT OFF @ 2028 ON @ 2033/// bad 50 kva, opened bank @ 21-6636 , crew reqd. will need new copper riser. 120/208 bank Released by crew 078S07,repairs made all cust restored @ 0000 please close ticket thanks.bt
10588 | Hazard | 3303902 | LESLIE | WOOTON | 2009-08-10 15:05 | 2009-08-10 15:18 | 53 | 13 | 57301-1 | 689 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | VER/HFP WR # 31159040 // CREW OPENED LINE FUSE TO ALLOW THEM TO REPAIR CONDUCTOR THAT IS ALMOST BROKEN INTO L3/HFP IDC XXXX
10589 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-05-04 12:33 | 2022-05-04 15:25 | 4 | 172 | 4836651 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Replaced broke cut-out on 37830529B30208
10590 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2015-03-04 17:30 | 2015-03-04 20:22 | 4 | 172 | 4101341 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 371-55 BAD LINE C/O/// NEED BIG BUCKET 7200 C/O/// TALKED TO JEFF COMBS//// CUTOUT CHANGED, POWER RESTORED//COD 4// VER/DBM
10591 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2012-07-06 17:08 | 2012-07-06 20:00 | 4 | 172 | 4554201 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 68-77 IN BRENDA COLDIRONS BACK YARD @ 5404 HILL AVE. SMALL BUCKET TO POLE THRU BRENDAS YARD RELEASED BY CREW 078H07COMPLETE NO TRUCK PRT/// //VER/GAH
10592 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-11-05 11:29 | 2009-11-05 12:55 | 8 | 86 | 63020-1 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LOOKS LIKE FUSE BROKE IN TWO. REFUSED EVERYTHING OK. 10T FUSE VER/KEP L3/KEP IDCC FP "NONE" XXXX
10593 | Hazard | 3311103 | STINNETT | WENDOVER | 2009-06-02 16:40 | 2009-06-02 22:24 | 2 | 344 | 60505-1 | 688 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN SECONDARY 1BURNT DOWN OPENED AT 20:51 CLOSED AT 22:24 VER/KEP L3/KEP IDC XXXX
10594 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2013-12-23 21:47 | 2013-12-24 00:39 | 4 | 172 | 4198041 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 444-15, WILL HAVE TO OPEN RECLOSER ON POLE 419-72 TO ISOLATE//CALLED JEFF BAKER OUT TO ASSIST//BAD CUTOUT ON POLE 444-15, WILL HAVE TO OPEN RECLOSER ON POLE 419-72 TO ISOLATE, OPEN RECLOSER AT 23:55 MADE REPAIRS RESTORED POWER AT 00:39 ORDER 4198121 CREATED FOR RECL OUTAGE VER/PDP L3/HFP
10595 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2010-06-12 10:45 | 2010-06-12 13:37 | 4 | 172 | 60668-1 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000801//CREW REQUIRED THINK CAN GET WITH BIG BUCKET FROM ROAD//COD 4// VER/DBM
10596 | Pikeville | 3411801 | JOHNSCREEK | META | 2015-04-07 09:05 | 2015-04-07 11:57 | 4 | 172 | 4283111 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE F IS OUT AGAIN,WILL PTRL.///////////BAD CUTOUT POLE 38831007D00126,REPLACED IT////////RE-FUSED AND RESTORED/////////ALL OK AFTERWARDS VER/CRB
10597 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2018-01-30 11:13 | 2018-01-30 14:05 | 4 | 172 | 4783811 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA transformer. Crew enroute to replace. Xfmr replaced with 50KVA. Restored @ 14:05. sh
10598 | Cannonsburg | 3002104 | 10TH STREET | 3RD STREET | 2017-08-22 19:34 | 2017-08-22 21:00 | 8 | 86 | 4289681 | 688 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 45-6185 BAD CUTOUT POLE 45-6009 LINE FUSE OUT 30T/ ISO 38830045D16009/ COD 8/ VER/BOW
10599 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2014-10-19 16:11 | 2014-10-19 20:00 | 3 | 229 | 4644761 | 687 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 10 T TRANS FUSE ALL PWR RESTORED PLEASE CLOSE TICKET THANK YOU LRM/ ISO 38830405A10208/ COD 3// VER/BOW
10600 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2008-08-04 18:07 | 2008-08-05 05:34 | 1 | 687 | 65120-1 | 687 | DISTRIBUTION STATION | EQUIPMENT FAILURE | TRANSFORMER, POWER - LTC | 3308603// THIS IS OUT DUE TO THE STATION OUTAGE// MOBILE ENROUTE - VER/KEP IDC XXXX
10601 | South Williamson | 3411401 | DEWEY | INEZ | 2016-05-01 15:11 | 2016-05-01 19:00 | 3 | 229 | 4151191 | 687 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TREE ON SERVICE DROP///TREE REMOVED//CONNECTIONS REWORKED AT WEATHERHEAD//CUTOUT BROKE ON XFMR POLE// CHANGING CUTOUT//REPAIRS MADE//RESTORED AT 19:00//COMPLETE//EM// VER/ ADH
10602 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-02-21 16:11 | 2010-02-21 20:00 | 3 | 229 | 59558-1 | 687 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WR#33952345 /POLE44-478 BAD 25KVA CSP NEED 25KVA CUTOUT T-BRECKET 2-CUST ON TRANS (PER SERVICER)// TO THE LEFT OF 4224 KILLEN DR RELEASED BY CREW 078S08// VER/DBM IDC XXXX
10603 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2014-10-31 03:48 | 2014-10-31 09:31 | 2 | 343 | 4675991 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | WILL WORK @ START OF REGULAT SHIFT// . FUSE LINK BROKEN, REPLACED FUSE / ALL WORK COMPLETE / GXJ// COD 2//VER/ ADH
10604 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2008-12-19 18:33 | 2008-12-19 19:22 | 14 | 49 | 60989-1 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3402801// FUSE LINK BROKE. RE-FUSED XFMR. SH VER/KEP L3/KEP IDC XXXX
10605 | Whitesburg | 3409503 | BURDINE | JENKINS | 2014-09-11 15:19 | 2014-09-11 16:57 | 7 | 98 | 4490551 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT OUT AND ARRESTOR BAD , KENNY BROOM IS COMMING TO CHANGE OUT RELEASED BY CREW 077S12// CUT OUT AND ARRESTER CHANGED, POWER RESTORED AT 16:57// COD 7// VER/ ADH
10606 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2022-07-03 07:58 | 2022-07-03 13:41 | 2 | 343 | 4368911 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had to change transformer cutout got it back on at 13:41
10607 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2010-09-23 23:29 | 2010-09-24 10:55 | 1 | 686 | 52982-1 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA TRANSF == CUST SAID BE ALLRIGHT TO CHANGE OUT IN DAY LIGHT 9-24-10 == CUST HAS DAMAGES == CAN GET TRUCK TO POLE == RELEASED BY CREW 077S03 ,, CREW ON SITE CHANGEING TRANSF. TRANSF. CHANGED OUT VER/KEP L3/KEP IDC XXXX
10608 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2017-04-27 13:27 | 2017-04-27 15:05 | 7 | 98 | 4687901 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAS CUTOUT ON 38830020B43542.BAD CUTOUT POLE 20-3542 40T 20-3543 65T OUT 38830020B43543 VER/AWD L3/HFP XXXHFP
10609 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2013-03-21 11:34 | 2013-03-21 13:12 | 7 | 98 | 4945071 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/KEP IDC XXXX
10610 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-03-11 05:57 | 2017-03-11 11:40 | 2 | 343 | 4547891 | 686 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA 7200 TRAN--W/MATS BY TRK--DS0311 RELEASED BY CREW 078S01,REPLACED XFMR ALL CUST RESTORED @ 1140 PLEASE CLOSE TICKET THANKS.BT 38830209000022 VER/AWD
10611 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2011-05-11 06:23 | 2011-05-11 17:48 | 1 | 685 | 4050231 | 685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED @ 17:48. SH VER/HFP L3/HFP
10612 | Hazard | 3303902 | LESLIE | WOOTON | 2015-09-19 23:32 | 2015-09-20 10:57 | 1 | 685 | 4251781 | 685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE 7200 CUTOUT CUST SAID WE COULD CHANGE IT OUT IN THE MORNING RELEASED BY CREW 077S01 CUTOUT REPLACED AND POWER RESTORED AT 10:57 VER/KEP
10613 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2009-05-31 03:02 | 2009-05-31 14:27 | 1 | 685 | 52501-1 | 685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACING IT//COD 1// VER/DBM
10614 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2020-03-01 13:41 | 2020-03-01 15:58 | 5 | 137 | 4442391 | 685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout is broke on 190-C-197,Will make repairs and get back with a time.Got these customers restored at 15:58.
10615 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2011-02-10 13:34 | 2011-02-10 15:51 | 5 | 137 | 55934-1 | 685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | CALLED CREW--SEND TO TRAVIS RELEASED BY CREW 078S07 CREW ON SITE WILL HAVE TRANSFOMER OPEN AT POLE 212B43526 AFFECTING 2 MORE CUST WHILE MAKING REPAIRS,, NOTIFIED CUSTOMERS OPEN AT 1516//COD 1 + 6 IDC XXXX
10616 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2022-12-19 23:03 | 2022-12-20 01:20 | 5 | 137 | 4278111 | 685 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | power restored
10617 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2021-11-10 11:35 | 2021-11-10 15:23 | 3 | 228 | 4074041 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | L/F blown on 842-B-25 will check/// found bad arrester on 842-B-87. replced it and cutout and restored @15:23
10618 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2022-02-09 21:36 | 2022-02-10 01:24 | 3 | 228 | 4463511 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken 19.9 cutout. One span tap comes off pole 527-34 its not on atlas. Its behind house txmf pole not sure the number. HOME OWNER IS HOME AND SAID SHE WILL PUT DOGS UP ONCE CREW ARRIVES. DO NOT GO INSIDE FENCE WITH DOGS. Released by crew 078S11///Replaced C/O//Complete BR
10619 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-07-16 09:22 | 2011-07-16 13:10 | 3 | 228 | 4552941 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ,,,,ALLREPAIRS MADE POWER BACK ON//VER/CRB IDC XXXX
10620 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-02-24 16:11 | 2016-02-24 21:53 | 2 | 342 | 4761741 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ****SEE H4761741**** CUTOUT BROKE ON 169-91 (2 CUSTOMERS ORIGNALLY) // WILL NEED TO OPEN L/F ON 169-20 TO MAKE REPAIRS (1 MORE CUSTOMER) 21:20 //REPAIRS MADE // OPENED 21:20 // CLOSED 21:53/ALL POWER RESTORED 2153/ DUPLICATE IN HOIS/ VER/BOW
10621 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-04-16 16:58 | 2015-04-16 20:46 | 3 | 228 | 4327181 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 38830069C35016 BAD 15KVA BRING 25 KVA TRUCK TO POLE NEED FLAGGERS BAD PLACE RELEASED BY CREW 078S08//CREW ON SITE//UPGRADED TO 25KVA///VOLT CK 122/123/245V///TBL KTK COMP///RMV VER/TOM L3/TOM
10622 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2010-07-14 09:06 | 2010-07-14 11:00 | 6 | 114 | 50041-1 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT...CHANGING...CHANGED CUTOUT...BB//VER/CRB IDC XXXX
10623 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2012-05-04 13:14 | 2012-05-04 14:30 | 9 | 76 | 4744041 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | COMPLETE 14:30 ///VER/CRB L/3 IDC XXXX
10624 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-09-09 15:21 | 2009-09-09 15:57 | 19 | 36 | 60341-1 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT // VER/TOM L3/TOM IDC XXXX
10625 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2022-09-21 19:03 | 2022-09-22 00:45 | 2 | 342 | 4906631 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9 25kva manual on pole 501-167. Line fuse restored at 2035 restoring one customer. Linecrew required Released by crew 078S11 Closed at 00:45 ticket complete.
10626 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2016-05-02 07:24 | 2016-05-02 10:15 | 4 | 171 | 4157021 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | JOE MORELAND ASSISTING.OPEN LINE FUSES @ POLE 182D-338 TO REPLACE XFMR FUSE @ 182D-343 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/AWD L3/HFP HFPC FEC57
10627 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-06-18 20:51 | 2021-06-19 08:15 | 1 | 684 | 4768711 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Crews to work in AM on 6/19/21 /// A and C phase fuse open @bank pole 71-200, checking. Bad 25 kva 7200 240/480 trans. 3 bushing secondary and 2 bushing high side. Please send this to Paul Layne talked to UMG and this feeds one of their pumps and they are ok with waiting till the morning. Pole is ruck accessible. Released by crew 074S05 Released by crew 074H07
10628 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-10-13 09:26 | 2015-10-13 09:44 | 38 | 18 | 4343601 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED RECLOSER 20-116 TO SAFELEY MAKE REPAIRS ON TICKET 4343111 VER/CRB /// VER TIMES PER VOICE RECORDER = L3/HFP HFPC FP0 CCO FEC57 AJB
10629 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-03-01 23:13 | 2015-03-02 10:37 | 1 | 684 | 4089531 | 684 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE IS BROKE IN TWO PLACES AND PULLED LOOSE FROM XFMR, CUST AGREED TO WAIT UNTILL MORNING TO MAKE REPAIRS, WILL NEED HELP FROM CREW RELEASED BY CREW 077S02 VER/ARN L3/DKGXXXX
10630 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-10-06 18:47 | 2015-10-06 20:00 | 11 | 73 | 4323921 | 683 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | ALL CUST, RESTORED COMPLETE/ 38830182B30188/ 2+9/ MD MADE/ADH// VER/ ADH // VER WITH VOICE REC L3/HFP XXXHFP
10631 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-07-15 19:16 | 2018-07-15 21:03 | 41 | 107 | 4777551 | 682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opening recloser to safely make repairs on PO 4776941//// 2 customers transferred from outage 4776941, originally out at 19:16
10632 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-11-05 12:11 | 2015-11-05 12:42 | 22 | 31 | 4412101 | 682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | REPAIRING PRIMARY 38830114000009/ ISO 38830114000149/ COD 22,OPEN LINE FUSE @ 1211 REPAIRS MADE LINE FUSE IN @ 1242 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ VER/BOW L3/HFP XXXHFP AJB
10633 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2015-04-04 20:24 | 2015-04-05 02:05 | 2 | 341 | 4276271 | 682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 7200 2 BUSHING 120 208 NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05 L3/DKGXXXX
10634 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-09-28 09:55 | 2009-09-28 15:36 | 2 | 341 | 66525-1 | 682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SPAN OF 4/3 SEC FEEDING 2 HOUSES BURNT DOWN BETWEEN POLES 38830020C45509 AND 38830020C45510--NEED ROLL OF 1/0 AN LINE CREW-B REYNOLDS TO WORK RELEASED BY CREW 078S07..CORRECT CUST COUNT IS 2..BLR//VER/CRB IDC XXXX
10635 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-08-13 15:44 | 2009-08-13 19:30 | 7 | 226 | 56108-1 | 682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LINE CREW REQUIRED WITH FLAGGERS TRUCKS OK #2 ALUM. WIRE/204-34 12T LINE FUSE BACK ON AT1700 HRS 1 CUSTOMER STILL OFF AT 204-40/SEND TO LINKOUS//COD 7// WR# 31225214 // ALL POWER RESTORED AT 19:30 INSTALLED 12 T FUSE ON POLE 204-40 MD FILED VER/KEP L3/KEP IDC XXXX
10636 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-07-01 09:58 | 2008-07-01 11:00 | 11 | 62 | 60785-1 | 682 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 39831099D1603920T LINE FUSE BROKE VER/HFP IDC XXXX
10637 | Pikeville | 3408103 | SALISBURY | MARTIN | 2009-03-09 07:43 | 2009-03-09 11:30 | 3 | 227 | 56448-1 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP 3408103// FUSE BROKEN ... ALL WORK COMPLETE / GXJ COD-3 L3/HFP IDC XXXX
10638 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2022-08-19 16:43 | 2022-08-19 20:30 | 3 | 227 | 4766081 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | had a broke cut out on pole 188-A-2 changed cutout out and got xforner fuse at pole 188-A-2 restored at 20:30
10639 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2020-09-12 18:43 | 2020-09-12 22:30 | 3 | 227 | 4455231 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Tried the XFMR fuse on pole 418-72 and it immediately opened up. Bad 25KVA. Need a line crew with a small bucket. Released by crew 077H20. restored 22:30
10640 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-06-19 03:39 | 2022-06-19 15:00 | 1 | 681 | 4248941 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XCO failed on 1052-B1-491// will be making repairs
10641 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-10-22 09:55 | 2018-10-22 13:42 | 3 | 227 | 4308091 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout gate burned into
10642 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2013-04-17 08:34 | 2013-04-17 12:21 | 3 | 227 | 4017451 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED TO REPLACE 25KVA CSP WITH 25 KVA CONVENTIONAL, TRUCK ACCESS RELEASED BY CREW 074S03 VER/KEP IDC XXXX
10643 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2010-12-20 01:33 | 2010-12-20 05:20 | 3 | 227 | 54414-1 | 681 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER , TRUCKS TO POLE OK. NEED LINE CREW. RELEASED BY CREW 078S01//REPLACED 25KVA POWER RESTORED AT 05:20 P TOLLIVER //VER/GAH IDC XXXX
10644 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-10-07 10:10 | 2016-10-07 13:00 | 4 | 170 | 4966721 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | CREW MAKING REPAIRS ON UG SECONDARY OPENED PADMOUNT 39831147A30697 CREW ON SITE LRM ALL PWR RESTORED @ 13:00 PLEASE CLOSE TICKET VER/CRB // VER PER VOICE RECORDER = L3/HFP XXXHFP
10645 | Hazard | 3308401 | BECKHAM | HINDMAN | 2016-06-22 16:47 | 2016-06-22 19:03 | 5 | 136 | 4409981 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE FUSE CUTOUT ON POLE37830179D00050,WILL CHANGE IT OUT VER/AWD
10646 | Pikeville | 3413401 | GARRETT | GARRETT | 2009-03-14 18:37 | 2009-03-14 20:53 | 5 | 136 | 58591-1 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD, NO TRUCK ACCESS, T. FIELDS ENROUTE TO ASSIST ... REPLACED CUTOUT , POLE OK, ALL WORK COMPLETE / GXJ // VER/TOM L3/TOM IDCC CNT1 XXXX
10647 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-02-16 16:11 | 2016-02-16 18:27 | 5 | 136 | 4721211 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | MIDDLE PHASE DOWN BETWEEN 48B186 AND 48B185 DUE TO FAILED TENSION SLEEVE TRK APPROACH DUTY CREW SHOULD BE ENOUGH RESAGGED MIDDLE CONDUCTOR RESTORED POWER AT 18:27// VER/ ADH
10648 | Hazard | 3302703 | HAZARD | HAZARD | 2009-06-06 11:24 | 2009-06-06 12:49 | 8 | 85 | 50561-1 | 680 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | VER/HFP CUTOUT GATE BURNED UP REPLACED == POWER OK COD-8 ISO 37830296A30714 L3/HFP IDC XXXX
10649 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-05-02 10:39 | 2017-05-02 12:55 | 5 | 136 | 4729811 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED ON 834-302. REPLACED AND RESTORED @ 12:55. SH/ ISO 38830834B00302/ COD 5/ VER/BOW
10650 | Hazard | 3309302 | VICCO | JEFF | 2008-01-25 15:27 | 2008-01-25 17:43 | 5 | 136 | 59888-1 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309302//RELEASED BY CREW 077S03//25 KVA 120/240 7200 VOLT XFMR BAD CALLING FOR CREW TO ASSIST//VER/CRB IDC XXXX
10651 | Hazard | 3308401 | BECKHAM | HINDMAN | 2012-08-28 15:12 | 2012-08-28 16:20 | 10 | 68 | 4981051 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PATROLLING LINE, FOUND BAD ARRESTER AND CUT IN CLEAR, POWER RESTORED ///VER/CRB L/3 CRB IDC XXXX
10652 | Hazard | 3311103 | STINNETT | WENDOVER | 2018-08-31 13:50 | 2018-08-31 19:30 | 2 | 340 | 4023261 | 680 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | 350 CU LEADS BURNT UP GOING TO 336 3 PHASE LASH XFMR IS STILL ENERGIZED. WILL NEED TO REPALCE LEADS Released by crew 077S01, replaced leeds and cutouts restored @ 19:30
10653 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-03-10 18:49 | 2010-03-10 19:57 | 10 | 68 | 64807-1 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE IN--TRANSFORMER OUT ON POLE 38830094A31116--BROKEN FUSE LINK--NOT SURE OF CUSTOMER COUNT//COD 8//ISO// VER/DBM IDC XXXX
10654 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-11-15 14:30 | 2020-11-15 17:20 | 4 | 170 | 4687571 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Transformer fuse blown. #6 solid open wire secondary down over roadway. Line crew and flaggers enroute to assist. Made repairs and restored @ 17:20. sh
10655 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-08-21 23:30 | 2011-08-22 02:20 | 4 | 170 | 4739831 | 680 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT --- POWER RESTORED. VER/KEP IDC XXXX
10656 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2018-02-28 10:33 | 2018-02-28 12:10 | 7 | 97 | 4889931 | 679 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 134-271 Released by crew 077S02//L/F WAS OUT ON POLE 37830134A00023//COD 7//MADE MD TO SHOW TRANS ON THE LOAD SIDE OF L/F
10657 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2010-05-09 21:53 | 2010-05-09 23:30 | 7 | 97 | 58763-1 | 679 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | HAVE CENTER FASE OPEN ON POLE794-31 CHECKING LINE NOW.CUTOUT DOOR BURNT P REPACED BACK TO NORMAL VER/PDP IDC XXXX
10658 | Paintsville | 3401101 | FALCON | FALC-OILS | 2010-04-25 13:13 | 2010-04-25 13:20 | 97 | 7 | H50577-1 | 679 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401101// 805-217..TOP OF POLE BURNED OFF..DUE TO BAD CUTOUT ..CALLED TIM MILLER POLE CHG OUT .. TOOK SECOND OUTAGE DUE TO OUT OF PHASE SWITCHING //VER/GAH IDC XXXX
10659 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-02-09 23:18 | 2019-02-10 05:22 | 3 | 364 | 4774341 | 678 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | pri. elbow burnt off @ pad mount xfm.will need Class A lineman and C man to make repairs with 350 cable and elbow to make repairs..pri. elbow burnt off @ pad mount xfm.will need Class A lineman and C man to make repairs with 1/0 udr cable and elbow to make repairs..
10660 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2015-07-24 13:00 | 2015-07-24 18:39 | 2 | 339 | 4938651 | 678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 7200 - 25 KVA, TRUCK TO POLE. ASHLAND LITTLE LEAGUE PARKING LOT 39TH ST RELEASED BY CREW 078S07/CREW ON SITE/FETR1930/VEM/REPAIRS MADE AND ALL CUST RESTORED 1839/PLEASE CLOSE TICKET/THANKS/VEM COD-2 ISO TF 38830070A31022 VER/HFP L3/HFP
10661 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2011-02-04 16:05 | 2011-02-04 17:58 | 6 | 113 | 54082-1 | 678 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | STS WR # 38701261 // FUSE BLOWN ON XFMR BANK PART POWER.. LEAD BURNT INTOFUSE BLOWN ON XFMR BANK PART POWER.. LEAD BURNT INTO ... MADE REPAIRS RESTORED POWER AT 17:58 VER/HFP L3/HFP IDC DCMT XXXX
10662 | Pikeville | 3120103 | STANVILLE | HAROLD | 2022-06-14 15:12 | 2022-06-14 18:58 | 3 | 226 | 4112031 | 678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad CSP 25KVA 7200 XFM// send to Shawn Goble Released by crew 074S09/// Crew onsite to replace/// Replaced xfmr and restored @ 18:58
10663 | South Williamson | 3200302 | BELFRY | TOLER | 2011-05-04 07:14 | 2011-05-04 11:00 | 3 | 226 | 4006001 | 678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FAILED . POLE BURNING CALL BELFRY FIRE DEPT ENROUTE. FAULT POLE#990-D2-491. ISOLATED AT 990-D470 ALSO DE-ENERGIZED TRANSFORMER ON POLE 990-D-470 .PIKEVILLE WILL BE SENDING CREW TO MAKE REPAIRS RELEASED BY CREW 079H07//ISO//COD 3// VER/DBM IDC XXXX
10664 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2018-08-07 10:17 | 2018-08-07 15:27 | 3 | 310 | 4917461 | 678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 50t lf @ 1148-572 restored @ 11:15, xfmer @ 1148-866 bad 12 kv c/o a phase, b phase also open. crew reqd. trk to pole straddle ditch. Released by crew 078S07/crew on site/FETR 1445/vem/repairs made and power restored to all cust 1447/please close ticket/thanks/vem/new cutout spring is bent/new FETR 1545/vem/repairs made and all cust restored 1527/please close ticket/thanks/vem
10665 | Hazard | 3300602 | BLUEGRASS | HAZARD | 2010-01-05 21:21 | 2010-01-06 03:00 | 2 | 339 | 62372-1 | 678 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMER NEED 2 MEN AND 15 KVA. 7.2KV POWER ON AT 03:00 W.MELTON IDCC PN138 XXXX
10666 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2017-07-11 21:26 | 2017-07-12 01:12 | 3 | 226 | 4108121 | 678 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OPENWIRE SECONDARY BURNT INTO AT CONNECTION, MADE REPAIRS RESTORED POWER AT 01:12.. VER/ARN
10667 | Hazard | 3303902 | LESLIE | WOOTON | 2015-04-04 07:07 | 2015-04-04 18:24 | 1 | 677 | 4272411 | 677 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED COUPLE MEN BIG BUCKET BAD 19.9KV CUTOUT WILL NEED BIG BUCKET TO MAKE REPAIRS RELEASED BY CREW 077S01 COD-1 ISO TF 37830389A00216 VER/HFP L3/HFP
10668 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-07-30 09:12 | 2021-07-30 14:50 | 2 | 338 | 4981851 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LF is open on pole 22-3, didnt find any hazards, going to try fuse// cutout broke on pole 22-3, will be getting flaggers so i can get cutout changed
10669 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2016-05-01 22:44 | 2016-05-02 10:00 | 1 | 676 | 4155951 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE NEED LINE CREW TO REPAIR RELEASED BY CREW 078S05 REPLACED CUTOUT RESTORED POWER AT 10:00 PLEASE CLOSE TICKET THANKS DWW
10670 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2009-09-17 05:07 | 2009-09-17 10:45 | 2 | 338 | 63640-1 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FOUND A BAD 10 KVA ON POLE 902-267, WELL NEED CREW, CAN USE TRUCK, THIS IS IN BETWEEN 3RD STREET AND 4TH STREET ON THE LEFT SID OF THE ROAD //COD 2//CREW ON SITE WILL INSTALL NEW 15KVA PR TOLLIVER//COMPLETEP R TOLLIVER// VER/DBM IDC XXXX
10671 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2009-06-10 19:11 | 2009-06-11 00:49 | 2 | 338 | 54122-1 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFORMER NEED YARD DOG. RELEASED BY CREW 078S01/CREW ON SITE/FETR0300/VEM/ONLY ONE CUST OUT/XFMR AND CUTOUT REPLACED/POWER RESTORED AT 0049//PLEASE CLOSE TICKET/THANKS/VEM VER/PDP IDCC PN111 XXXX
10672 | Paintsville | 3401102 | FALCON | SALYERSVI | 2019-03-12 07:32 | 2019-03-12 10:12 | 7 | 160 | 4973121 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Secondary connection burnt in two on xfmr pole 875-133 affecting three customers. Opening xfmr to make repairs. Opened xfmr @ 9:23, made repairs and closed xfmr @ 10:12. sh
10673 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-12-11 01:42 | 2019-12-11 11:10 | 2 | 568 | 4143771 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | Had to open cust Transformer at 9:22 AM to make repairs,Going to pull in new service,The service is old and has several splices with a broke neutral,Will update ticket with time i restore service..Made my Repairs and restored service at 11:10 on customers XFM Checked voltage and it was good.
10674 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2021-08-15 14:02 | 2021-08-15 19:40 | 2 | 338 | 4071951 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9 XFM, need line crew and manual ROW crew
10675 | Hazard | 3308002 | JACKSON | PANBOWL | 2016-02-21 20:14 | 2016-02-22 01:52 | 2 | 338 | 4745181 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 277 / 480 7200 167 TRANSFORMER
10676 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2012-02-14 08:12 | 2012-02-14 13:50 | 2 | 338 | 4347131 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD. I AM CALLING FOR HELP. WE CHANGED TRANSFORMER. VER/KEP IDC XXXX
10677 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2022-01-22 12:12 | 2022-01-22 17:50 | 2 | 338 | 4396291 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 15 need 25 plus cleanup/truck ok material handler Released by crew 078S03 Ticket complete.
10678 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2013-07-23 20:25 | 2013-07-24 07:41 | 1 | 676 | 4584801 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD CSP 10 KVA 7200 XFORMER , NO TRUCKS UP ON HILL. NEED 4 MAN LINE CREW.// CUSTOMER WANTS CALLED (859)-325-3302 JIM GAUZE IF WE CAN OR CANT GET TO TONIGHT/SPOKE WITH CUST/HOPE TO BE THERE BY 6 AM/VEM/REPAIRS MADE AND POWER RESTORED 0741/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB L/3 CRB IDC XXXX
10679 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2016-05-01 22:44 | 2016-05-02 10:00 | 1 | 676 | 4155951 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE NEED LINE CREW TO REPAIR RELEASED BY CREW 078S05 REPLACED CUTOUT RESTORED POWER AT 10:00 PLEASE CLOSE TICKET THANKS DWW
10680 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2014-05-30 07:37 | 2014-05-30 13:15 | 2 | 338 | 4952851 | 676 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 075H03 BAD TRANSFORMER ON POLE 451-22 OPEN LINE FUSE ON POLE 451-14 VERY DIFFCULT LOCATION POWER RESTORED AT 13:15 VER/CRB
10681 | Whitesburg | 3312901 | JENKINS | KONA | 2013-08-13 12:45 | 2013-08-13 16:30 | 3 | 225 | 4660951 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR NEEDS TO BE CHANGED WILL TAKE CREW RELEASED BY CREW 077S12 CHANGED XFMR POWER RESTORED AT 1630//COD 3// VER/DBM
10682 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-11-04 23:30 | 2008-11-05 03:15 | 3 | 225 | 62220-1 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308002//BAD TRANSFORMER CALLING OUT HELP VER/ARN IDC ESTIMATED TIME OFF CHANGED FROM 2048 XXXX
10683 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2022-06-22 00:15 | 2022-06-22 11:30 | 1 | 675 | 4272791 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Failed TR and is manual job
10684 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-07-02 21:30 | 2008-07-03 01:15 | 3 | 225 | 61525-1 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308402// BAD XFMR VER/PDP IDC XXXX
10685 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2019-04-21 11:00 | 2019-04-21 13:15 | 5 | 135 | 4144491 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CALLED CUSTOMER//MTR BLANK// replaced 8t fuse looks to have just broke
10686 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-05-28 10:00 | 2016-05-28 13:45 | 3 | 225 | 4267291 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED LINE&TRANSFORMER CUTOUTS AT 10A /1101-328 S/P TAP HAS BAD CUTOUT. NEED 2 MEN BUCKET CROSSARM TO SPLICE POLE NEW CUTOUT/ARRESTOR ALL RESTORED AT 13:45P/ ISO 38831101D20327/ COD 3/ VER/BOW
10687 | Hazard | 3308001 | JACKSON | S.JACKSON | 2009-03-08 22:30 | 2009-03-08 23:45 | 9 | 75 | 56375-1 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD- 9 ISO POLE 38831108B00027 BAD CUTOUT L3/HFP IDC XXXX
10688 | Cannonsburg | 3001101 | HOODSCREE | SUMMIT | 2014-02-06 11:44 | 2014-02-06 15:29 | 3 | 225 | 4362661 | 675 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA///TRANSFER TO T BURTON//ROB COMPHER TO WORK JOB/// RELEASED BY CREW 078H16 COMPLETE//COD 3// VER/DBM IDC XXXX
10689 | Pikeville | 3403001 | PIKEVILLE | CITY | 2020-12-28 12:10 | 2020-12-28 13:25 | 9 | 75 | 4830641 | 675 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | Fuse door burned into on Bank of Transformers,replaced Door and Restored at 13:25..
10690 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2012-07-06 10:19 | 2012-07-06 15:56 | 2 | 337 | 4537061 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | BAD PRIMARY METERING ON 858-228..RECLOSER ON P-858-226 BACK ON AT 14.00. RELEASED BY CREW 076S01.OPEN RECLOSER@3:40 PUT LOOPS IN CLOSED BACK IN @3;56 // ENTERED AED ...HFP
10691 | Hazard | 3308401 | BECKHAM | HINDMAN | 2011-05-22 23:46 | 2011-05-23 11:00 | 1 | 674 | 4136581 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA PER KENNY NAPIER AND TIM SMITH. 05 23 11 ON SITE CHANGEING XFMR // COD-1 ISO TF 37830205A40538 VER/HFP L3/HFP IDC XXXX
10692 | South Williamson | 3411401 | DEWEY | INEZ | 2019-05-29 21:11 | 2019-05-30 08:25 | 1 | 674 | 4381571 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke 0n pole 744-b-487//i replaced cutout//restored at 8:25//complete//em
10693 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2008-06-20 16:18 | 2008-06-20 21:55 | 2 | 337 | 51227-1 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000303// BAD 25KV TRANSFORMER/NEED NEW CUTOUT/TRUCK OK// CUSTOMER COUNT WRONG-ONLY 2 CUSTOMERS ON TRANSFORMER-324 AN 400 BELLEFONTE RD RELEASED BY CREW 078S07//COD 4 IDCC CNT4 XXXX
10694 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2017-07-29 07:41 | 2017-07-29 13:18 | 2 | 337 | 4202081 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | LOOP OPEN ON POLE 37830208000059 -- LINE CREW AND ROW === MANUAL UP ON HILL === 2 CUST OUT RELEASED BY CREW 077S03 OPEN LOOP TO DO REPAIRS 37830208000052 1212 TILL1318 RELEASED BY CREW 077H04 *** SEE OUTAGE H4202081*** VER/CRB
10695 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2021-11-11 21:43 | 2021-11-12 08:57 | 1 | 674 | 4081631 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT//////////REPLACED&RESTORED@08:57
10696 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2020-11-01 18:48 | 2020-11-02 00:25 | 2 | 337 | 4622581 | 674 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 10kva 7200 120/240 on pole 38830069D16062, Trucks to pole, corner of south belmont and 168. Bring 25kva. crew required Released by crew 078S02/arrived RM power on @00:25 please close tic RM //
10697 | Hazard | 3309003 | JEFF | VIPER | 2016-12-18 09:14 | 2016-12-18 14:50 | 2 | 336 | 4213521 | 672 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONE LEG OF SERVICE WIRE PULLED OUT ON TRANSFORMER END TRUCK ACCESS,SERVICER JDM RELEASED BY CREW 077E01.. BAD CONNECTION AT XFMR , MADE REPAIRS RESTORED POWER AT 14:50..
10698 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-07-05 17:32 | 2017-07-05 23:08 | 2 | 336 | 4076881 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR F IS OUT,WILL RE-FUSE////////FUSE BLEW//////NEED 25KVA 19.9,CREW//////ALSO A FLAGGING CREW/////////////REPLACED XFR&RESTORED,ALL OK AFTERWARDS 38831056C00019 VER/AWD
10699 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2011-04-20 11:21 | 2011-04-20 15:05 | 3 | 224 | 61182-1 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED--BAD CUTOUT--NO TRUCK TOO WET RELEASED BY CREW 078S07//CREW ON SITE DIFFICULT LOCATION /// CREW OPENED TAP AT POLE 39831123C14076 AT 1415 TO REPLACE CUTOUTCREW REQUIRED--BAD CUTOUT--NO TRUCK TOO WET RELEASED BY CREW 078S07//CREW ON SITE DIFFICULT LOCATION/OPENED JUMPER PL# 1123-4076 @ 14:15 REPAIRS COMPLETE POWER RESTORED @ 15:05 J. HEMLEPP SEE H1151026-1 VER/HFP L3/HFP IDC XXXX
10700 | South Williamson | 3411401 | DEWEY | INEZ | 2019-11-30 19:04 | 2019-11-30 21:52 | 4 | 168 | 4107651 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on pole 768-24//cutout broke on pole 768-212//making repairs//repairs made//resored at 21:40//complete//e
10701 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2021-06-03 09:20 | 2021-06-03 11:38 | 7 | 138 | 4662221 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | L/F IS OPEN ON POLE 38830185000143 AS WELL AS TRANS//TRANS 38830185000142 IS NOT AFFECTED CUST IS MISMAPPED MD MADE//L/F ON POLE 38830185000143 FEEDS BOTH TAPS AND HAS NOT BEEN BUILT IN POR//SENT TO KEITH GATRELL TO MAP// line fuse restored @ 10:40 ,,crew required , bad xfr cutout 161-115 ,,no trucks Released by crew 078S05,repairs made all cust restored @ 1138 please close ticket thanks.bt Released by crew 078H02//THE MAP IS CORRECTED AS OF 1530 ON 06-03-2021
10702 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2021-08-19 12:41 | 2021-08-19 16:25 | 3 | 224 | 4119681 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | xfmr on 38830380000103 was open. when i closed the fuse in it held but inoticed there was oil on the side of the xfmr, when i checked the meter theres only 20 volts on each leg. this 7200/25kva xfmr needs changed. its not by truck. this only feeds one send email to vernon Released by crew 078S12// email sent
10703 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2014-08-08 14:31 | 2014-08-08 18:15 | 3 | 224 | 4342901 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE OUT WILL RE-FUSE//// BAD 50 KVA 7200 /// NO TRUCK /// DALE HAMILTON IS GETTING CREW TOGETHER WILL BE ENROUTE RELEASED BY CREW 074H17// COD 3// VER/ ADH
10704 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2009-10-19 10:17 | 2009-10-19 14:01 | 3 | 224 | 56966-1 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 32262568 // BUSHING LOOSE ON SECONDARY SIDE, NEEDS REPLACED. S WHITAKER CREW TO REPLACE RELEASED BY CREW 077S02 RELEASED BY CREW 077H02 COD-3 L3/HFP IDC XXXX
10705 | Hazard | 3303901 | LESLIE | HYDEN | 2015-04-27 17:05 | 2015-04-27 17:12 | 96 | 7 | 4370701 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD LIGHTENING ARRESTER 339-A-169, OPENING STEP DOWN AT POLE 339-A3-168 TO CLEAR/ARRESTER ON 12KV SIDE OF STEPDOWN XFMR BLEW UP , PICES OF ARRESTER HIT CUST. TRUCK SAID WOULD LIKE SOMEONE TO COME LOOK AT TRUCK . . OPENED STEPDOWN @ 17:05 CLOSED BACK @ 17:12 ./EMAILED HAZARD/PEGGY/MADE AED/ADH/COD 96 /// NOTE POWERON & FIELDVIEW SHOWS STEPDOWN & RECL ON POLE 339-168 (IS THIS CORRECT?) -- VER/HFP L3/HFP AJB
10706 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-09-02 19:56 | 2018-09-02 21:48 | 6 | 112 | 4036401 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse L3/HFP
10707 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2008-02-26 17:23 | 2008-02-26 19:15 | 6 | 112 | 50675-1 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3308402// REPLACED CUTOUT AND ARRESTOR ALSO 15-T LINE FUSE ON POLE 253-153//SENT REPORT TO MAPPING ON MISSING 15T (WAS NOT THE ISOLATING DEVICE)//COD 6// VER/DBM IDC XXXX
10708 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2017-11-13 23:33 | 2017-11-14 10:45 | 1 | 672 | 4554681 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | crew required pole 270-18 broke at deadend shoe no trucks primary only 1 customer at 270-263/ will have to have outage on 270-18 line fuse to repair/ opened line fuse and transformer on pole 38830270D00018/ ISO 38830270D00018/ COD 29/ 1020-1045/ 38830270D00263 shows no customers on map but per servicers comments there was 1 customer off who was shown to be on pole 38830270D00018
10709 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2020-04-26 19:58 | 2020-04-26 21:50 | 6 | 112 | 4754711 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 771-64//broke cutout on 771-222//repairs made//restored at 21:50//complete//em
10710 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2018-09-11 08:24 | 2018-09-11 10:00 | 7 | 96 | 4082151 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | New viper reclosures locked out beside pole 38830162C00366, Not on maps yet. Back in at 10:00 COD-7 ISO OCR 38830162C00366 CONTROL CABLE ON RECLOSER BAD SEE DOL Case #: 858750
10711 | Pikeville | 3407101 | TOPMOST | DEMA | 2011-10-02 00:16 | 2011-10-02 11:28 | 1 | 672 | H4939281 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3407101 -POLE BURNT OFF I OPENED RECLOSER 186-18 AT 01:45 OPENED SOLID BLADE 210-1 CLOSED RECLOSER POLE 186-18 AT 02:00 TO SOLID BLADE 210-1. POLE FIRE OUT. CREW REQUIRED NEED FIBERGLASS POLE EXSTENSION CUTOUT ARRESTER GAS DRILL. ROW CREW. NOT BY TRUCK. NEED TO ISO AND GROUND I JUST HAVE SOLID BLADE ON 210-1 OPEN AND TAGED RELEASED BY CREW 074S11CLOSED SOLID BLADE IN AT 11:27 COMPLETE // COD-59 ISO OCR 37830186000018 VER/HFP L3/HFP IDC DUP FOR ORIGINAL 1 CUSTOMER XXXX
10712 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2022-11-19 11:20 | 2022-11-19 12:16 | 12 | 56 | 4161861 | 672 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | transformer back in at 12:16. complete
10713 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2014-02-03 00:01 | 2014-02-03 01:02 | 11 | 61 | 4341211 | 671 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RELATED TO ORDER 4338711 / // CREW OPENED FUSE ON POLE 38821060B00119 TO ALLOW THEM TO MAKE REPAIRS /// OFF @ 0001 ON @ 0053 COD-11 ISO LF 38821060B00119 VER/HFP L3/HFP IDCC TOF0059 XXXX
10714 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-01-20 16:05 | 2010-01-20 17:06 | 11 | 61 | 56792-1 | 671 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTIONS ARE OVER HEATING AND WILL NEED REPLACED AFTER SCHOOL HOURS CALLING FOR CREW TO ASSIST RELEASED BY CREW 077S04 REPLACED CONNECTIONS RESTORED POWER AT 1706 CREW 077H01 VER/HFP L3/HFP IDC XXXX
10715 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2017-06-05 19:10 | 2017-06-06 06:21 | 1 | 671 | 4912801 | 671 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 38830184A00094 BROKE TRAN C/O --CREW REQ RELEASED BY CREW 078S01/CREW ON SITE/VEM/REPAIRS MADE AND ALL CUST RESTORED 0621/PLEASE CLOSE TICKET/THANKS/VEM/// VER/DKM
10716 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2019-11-27 16:25 | 2019-11-27 22:00 | 2 | 335 | 4091891 | 670 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | tree has grown into customer service drop will need to replace drop..will need one to two men to help..pole back up on hill.
10717 | Cannonsburg | 3001401 | LOUISA | CITY | 2013-03-09 09:29 | 2013-03-09 10:36 | 10 | 67 | 4893071 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE JUST BROKE /// COD-10 ISO TF 38830454B33131 VER/HFP L3/HFP IDC XXXX
10718 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2022-11-06 21:31 | 2022-11-06 23:45 | 5 | 134 | 4107911 | 670 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Neutral broke in 1/0 secondary between poles 144-110 and 144-533///repairs made and restored full power @ 23:45//Only 1 customer was affected
10719 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-05-12 10:55 | 2012-05-12 16:30 | 2 | 335 | 4784111 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE CREW SUP. ENROUTE FROM ASHLAND/XFMR.FUSE BLWN 245-137//BAD 10 KVA/ 2 MAN CREW REQ. /MAT. HAND BUCKET TO POLE/BRING A 25 KVA 7200/120-240 XFMER/LINE CREW ENROUTEREPAIRS COMP. POWER REST.@ 16:30 J. HEMLEPP//COD 2// VER/DBM IDC XXXX
10720 | Pikeville | 3413402 | GARRETT | LACKEY | 2017-05-25 10:20 | 2017-05-25 15:55 | 2 | 335 | 4857501 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | A PHASE XFMR CUTOUT FAILED, OPENED B & C PHASE XFMR CUTOUTS AT 12:45 . REPLACED A PHASE XFMR, 50 KVA 277/480 ( CRACKED PRIMARY BUSHING ) AND REPLACED ALL CUTOUTS AND ARRESTERS , RESTORED AT 15:55, ALL WORK COMPLETE / GXJ RELEASED BY CREW 074S03 37830041B00323 VER/AWD
10721 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2015-05-04 15:53 | 2015-05-04 17:00 | 10 | 67 | 4389601 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP BURNT OFF @ POLE 182-3581/ ISO 38830182B43581/ COD 10 VER/HFP L3/HFP
10722 | Hazard | 3311101 | STINNETT | REDBIRD | 2009-06-09 18:17 | 2009-06-09 23:52 | 2 | 335 | 62221-1 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT A BAD 25KVA 7200 XFMR, CAN CHANGE WITH MATERIAL HANDLER. NEED FLAGERS, ADDRESS 926 GREASY CRK. RD. POLE IS BY RD. GREG FUGATE AND JEFF BAKER WILL PROBABLY BE THE ONES COMMING OUT. MIKE SAID HE WILL TELL FLAGGERS TO MEET THEM AT LOTHAIR. RELEASED BY CREW 077S08//VER/CRB IDC XXXX
10723 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2008-09-30 20:30 | 2008-10-01 02:05 | 2 | 335 | 52424-1 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3110902// FOUND A BAD 5 KVA , LOOKS LIKE IT CAME OVER ON NOAHS ARK, NEED CREW TO CHANGE THIS OUT, ALSO NEED NEW CUTOUT , CAN USE TRUCKS ON THIS, COME UP STUART LN TO FORKS OF THE ROAD, STAY TO THE LEFT WILL SEE SIGN THAT SAYS PRIVATE DRIVE, GO ALL THE WAY TO THE END UP ON HILL, LAST HOUSE ON RIGHT, RELEASED BY CREW 078S06 IDCC CNT1 XXXX
10724 | Whitesburg | 3309302 | VICCO | JEFF | 2008-04-17 10:30 | 2008-04-17 16:05 | 2 | 335 | 51780-1 | 670 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309302// BAD TRANSFORMER ON POLE 373-120 WILL NEED A 10KVA AND A CUTOUT AND ARRESTOR RELEASED BY CREW 074S07// VER/HFP AJBC CNT1
10725 | Hazard | 3303901 | LESLIE | HYDEN | 2018-02-04 23:17 | 2018-02-05 10:26 | 1 | 669 | 4804821 | 669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | due to location and snow, servicer will check at start of shift 02/05/18/// REPLACED BAD CONNECTONS
10726 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-12-06 10:37 | 2013-12-06 12:56 | 11 | 139 | 4106601 | 669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | DRT ASSISTING--CREW REQUIRED--BAD 25 KVA TRANSFORMER--TRUCK TO POLE--LINE FUSE BACK IN AT 11:30 RELEASED BY CREW 078S07 RESTORED TRANS AT 1256 VER/SEF L3/HFP IDC XXXX
10727 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2017-06-11 18:06 | 2017-06-11 21:49 | 3 | 223 | 4931601 | 669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 CSP TRANSFORMER. NEED LMA AND BUCKET TRUCK, 15 KVA 7200, CUTOUT AND BRACKET AND OIL PADS. POWER IS RESTORED./// VER/DKM
10728 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2021-02-25 07:07 | 2021-02-25 10:50 | 3 | 223 | 4247671 | 669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Changed cutout, restored @ 10:50
10729 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2019-11-30 09:27 | 2019-11-30 13:10 | 3 | 223 | 4105161 | 669 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | changed cutout and restored @ 1310
10730 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2009-04-10 18:13 | 2009-04-10 21:00 | 4 | 167 | 51162-1 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SEND TO V MULLINS RELEASED BY CREW 078S07//WR#29314337SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/VEM/CUTTING LOOP AT 70-2222/THREE XFMRS OFF/CHANGING C/O ON 70-2225/FETR2200SEND TO V MULLINS RELEASED BY CREW 078S07/CREW ON SITE/VEM/CUTTING LOOP AT 70-2222/THREE XFMRS OFF/CHANGING C/O ON 70-2225/FETR2200/ALL CUST RESTORED 2037/PLEASE CLOSE TICKET/THANKS/VEM//VER/CRB
10731 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-03-04 13:40 | 2021-03-04 19:14 | 2 | 334 | 4302801 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 15kva 7200 transformer, 120/240. Trucks to pole. Crew required Released by crew 078S02,repairs made all cust restored please close ticket thanks.bt
10732 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2013-06-16 15:13 | 2013-06-16 18:00 | 4 | 167 | 4349241 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 3 MAN PRC CREW--BAD 50KVA TRANSFORMER--TRUCK TO POLE RELEASED BY CREW 078S07/ CREW EN-ROUTE/ PHELPS ON LOCATION REMOVING DEFECTIVE XFMER./ FETR 18:15 JEH/ REPAIRS COMP. POWER REST.@ 18:00 JEH//COD 4// VER/DBM IDC XXXX
10733 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2013-06-17 10:23 | 2013-06-17 13:10 | 4 | 167 | 4355061 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT XFMR RISER TO SECONDARY AFFECTING FOUR OF THE SIX CUSTOMERS FED FROM XFMR 954-91. REWORKED ALL CONNECTIONS ON XFMR POLE. RESTORED @ 13:10. SH VER/HFP L3/HFP
10734 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2017-08-04 14:53 | 2017-08-04 17:40 | 4 | 167 | 4225801 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE CUTOUT FOR SINGLE PHASE TAP AND TRANSFORMER CUTOUT BOTH FAILED ON POLE 38821112B00035/ REPLACED BOTH CUTOUTS AND REENERGIZED @1740/38821112B00035 COD 4 VER/AWD
10735 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2013-10-28 10:45 | 2013-10-28 13:32 | 4 | 167 | 4969461 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE BLOWN ON POLE 37830246B00004, CHECKING LINE/// ARRESTOR BAD ON POLE 37830246B20588 CUT IN CLEAR. VER/CRB L/3 CRB
10736 | Hazard | 3303903 | LESLIE | HALSFORK | 2014-01-29 06:56 | 2014-01-29 12:30 | 2 | 334 | 4321541 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA 7200 120/240 RELEASED BY CREW 077S01 ON SITE WORKING TRANSFORMER CHANGED AND POWER RESTORED AT 12:30 // COD-2 ISO TF 37830338000011 VER/HFP L3/HFP
10737 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-05-26 01:32 | 2016-05-26 12:40 | 1 | 668 | 4259891 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK AT START TIME 5-26-16 BAD XFMR, NOTE SENT TO CLIFF TO WRITE A JOB. HARVEY IS GOING TO SERVE FROM A 50 KVA FOR NOW.WILL WORK AT START TIME 5-26-16 BAD 15 KVA TRANSFORMER. THIS WILL BE HAD JOB ON TRANSFORMER. I HAVE TALKED TO TIM HALL. AND FOR NOW GOING TO RUN TEMP DROP FROM SEC POLE 42-435. WILL GET ORDER TO CHANGE POLE ARMS TRANSFORMER VER/AWD
10738 | Whitesburg | 3314401 | MAYKING | ERMINE | 2022-05-07 11:16 | 2022-05-07 16:50 | 2 | 334 | 4860121 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout broke on pole 449-C3-492. will need big bucket and couple men to change it out Released by crew 077S11
10739 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-07-12 08:58 | 2015-07-12 14:32 | 2 | 334 | 4780151 | 668 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE WAS BROKE . CLOSED XFMR BACK @ 14:32 .// VER/ ADH
10740 | Whitesburg | 3312902 | JENKINS | JENKINS | 2015-02-02 21:52 | 2015-02-02 22:21 | 23 | 29 | 4987181 | 667 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT LINE CLAMP ARCING AT POLE#79 OPENED "C" PHASE FUSE ON POLE#74 COD-23 @2152 TO MAKE REPAIRS/ NO OUTAGE TILL FUSE WAS OPENED/REPLACED CLAMP RESTORED POWER AT 22:21. VER/KEP L3/HFP AJB
10741 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2011-03-10 00:23 | 2011-03-10 04:05 | 3 | 222 | 52627-1 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 421-238 ALSO TOOK LINE FUSE OUT ON POLE421-148 REPLACED CUTOUT RESTORED POWER AT 04:05 VER/ARN IDCC PN238 XXXX
10742 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2008-04-13 07:03 | 2008-04-13 10:45 | 3 | 222 | 50773-1 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED LINKOUS RELEASED BY CREW 078S07 FAULT POLE 39831147D40679CALLED LINKOUS RELEASED BY CREW 078S07 REPLACED CUTOUT ; NO TRUCK;INSTALLED POLYMER CUTOUT VER/HFP AJB
10743 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2015-12-01 13:19 | 2015-12-01 14:33 | 9 | 74 | 4499341 | 666 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR ON XFORM BANK BAD REPLACE DOOR REFUSE 10T POWER RESTORED COD-9 ISO TF 38830021B43736 VER/HFP L3/HFP
10744 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2014-01-02 22:34 | 2014-01-03 09:40 | 1 | 666 | 4220721 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PER DUTY SUPERVISOR FOR THIS AREA, HOLDING NON-EMERGENCY CALLS UNTIL THE A.M. DUE TO TERRIBLE ROAD CONDITIONS// SPLICE BURNT INTO IN SERVICE GOING TO HOUSE RE-DONE ALL SPLICES RESTORED SERVICE GOOD VOLTAGE 118/118/236 ONLY 1 CUSTOMER AFFECTED VER/CRB IDC XXXX
10745 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2022-05-15 01:04 | 2022-05-15 12:10 | 1 | 666 | 4891761 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva 7200 120-240 transformer crew required truck ok Released by crew 078S09. crew on site to make repairs. repairs made transformer in on pole 139-365 @ 12:10. complete
10746 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2010-04-17 00:59 | 2010-04-17 02:50 | 6 | 111 | 64221-1 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | POLE 91-211 2-BAD LA TREES COVERED POLE TREES NEED CUT BAD ALSO POLE 91-48 LINE FUSE POLE TREES NEED CUT OPEN 2;00 AM ON 2;50 AM VER/LDA IDC XXXX
10747 | Hazard | 3303903 | LESLIE | HALSFORK | 2011-05-03 09:06 | 2011-05-03 14:39 | 2 | 333 | 4000341 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 39801572 // TOP OF CUTOUT BAD LEADS BROKEOUT RELEASED BY CREW 077S01 /// COD-2 ISO TF 37830411A10059 VER/HFP L3/HFP IDC XXXX
10748 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2009-08-10 12:14 | 2009-08-10 14:05 | 6 | 111 | 55008-1 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP DUPLICATING FOR C PHASE OUTAGE IN HOIS RECORD H1124413-1 // WR # 31155087 //POLE 141-92 19.9 INS. 40T FUSE OUT 141-72POLE 141-92 19.9 INS. 40T FUSE OUT 141-72 SEND TO BILL .POLE 141-92 19.9 INS. 40T FUSE OUT 141-72 SEND TO BILL . RELEASED BY CREW 078S08 ****** TOOK OTHER PHASE OFF @ 1315 L3/HFP IDC XXXX
10749 | Hazard | 3301101 | CHAVIES | CHAVIES | 2013-06-03 06:34 | 2013-06-03 12:07 | 2 | 333 | 4212221 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 30 D/D LIGHT POLE ROTTED AND FELL OVER, LANDED ON TRAMPOLINE...ALL POWER RESTORED @12:07 ///VER/CRB L/3 CRB
10750 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2009-06-26 17:23 | 2009-06-26 18:00 | 18 | 37 | 63641-1 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE ON POLE 38830205A10112 MELTED OUT UNDER LOAD, REPLACED WITH 30T FUSE, PLEASE SEND TO MAPPING//COD 18// ISO 38830205A10112// VER/DBM
10751 | South Williamson | 3202201 | LOVELY | LOVELY | 2010-08-11 22:39 | 2010-08-12 09:45 | 1 | 666 | 53211-1 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMER FUSE OUT. BAD 25KVA 19.9 XFMER FEEDS CELL TOWER ON COLLINS BRANCH RELEASED BY CREW 076H06//NEEDDS TO GO TO JOEY REED VER/KEP L3/KEP IDCC PN844 XXXX
10752 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2022-12-15 11:14 | 2022-12-15 13:05 | 6 | 111 | 4264431 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse cutout failed on 47-D-30, will have to open line fuse to make repairs. Top of Pole burnt - Pole needs replaced. E-mailed Bill Johnson for follow-up.
10753 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2016-04-10 00:51 | 2016-04-10 02:05 | 9 | 74 | 4076931 | 666 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED OUT BAD CUTOUT ON POLE 165-226 15T VER/KEP
10754 | Whitesburg | 3409503 | BURDINE | JENKINS | 2014-10-21 11:37 | 2014-10-21 13:50 | 5 | 133 | 4649131 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | REPLACING POLE DID NOT NOTIFY CUST//REPLACING POLE 37830382A30006//OPENED L/F 37830382A30004 COD 5 VER/CRB
10755 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2009-01-17 06:15 | 2009-01-17 07:50 | 7 | 95 | 56845-1 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401302// CUTOUT GATE IS BURNED UP. I AM GOING TO TRY TO FIND REPLACEMENT GATE VER/KEP L3/KEP
10756 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2021-07-16 15:20 | 2021-07-16 15:55 | 19 | 35 | 4921191 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | C phase fuse out(19 COD)// fuse was taken out by XFM on outage 4920821, restored at 1555
10757 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2018-07-24 17:24 | 2018-07-24 19:37 | 5 | 133 | 4849841 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrestor
10758 | South Williamson | 3200301 | BELFRY | BELFRY | 2014-05-07 17:52 | 2014-05-07 19:27 | 7 | 95 | 4672211 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFR CUTOUT IS BROKEN,WILL REPLACE IT/////////REPLACED XFR CUTOUT AND RESTORED POWER,ALL OK AFTERWARDS//COD 7// VER/DBM
10759 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2019-12-22 10:25 | 2019-12-22 17:00 | 7 | 395 | 4176021 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Linecrew required, bad cutout and this will require larger outage to replace when crew arrives at 38830428000065 CREW INSTALLED A 12T L/F / RECLOSER 38830428C10296 IS ON NR SOS 1060 REV 34 NORMAL @ 1715 //COD 1 FROM BEGINNING//MADE MD TO SHOW12TT L/F ON POLE 38830428000065 Linecrew required, bad cutout and this will require larger outage to replace when crew arrives at 38830404000198//arrived RM looking for better way to isolate line,cut in line fuse @428-65 open16:15-closed aT 1700
10760 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2020-06-06 08:17 | 2020-06-06 10:30 | 5 | 133 | 4968711 | 665 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3110903/replaced failed fuse in at 1030
10761 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2020-03-02 12:32 | 2020-03-02 16:46 | 4 | 254 | 4444091 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout help on the way opened tap at 15:28 closed at 16:46
10762 | Hazard | 3308404 | BECKHAM | PIPPA PASSES | 2018-12-31 18:59 | 2018-12-31 21:45 | 4 | 166 | 4616721 | 664 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | bad connection on transformer
10763 | Pikeville | 3401001 | ELWOOD | DORTON | 2008-02-06 17:24 | 2008-02-06 20:10 | 4 | 166 | 51835-1 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3401001//CUTOUT BROKE. I AN GOING TO CHANGE CUTOUT. I CHANGED CUTOUT.//COD 4// VER/DBM IDC XXXX
10764 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-03-26 09:15 | 2010-03-26 10:38 | 8 | 83 | 54587-1 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | I OPENED LINE FUSE ON POLE 332-128 AND I HAVE INSULATOR BAD ON POLE 332-129 A CREW IS IN ROUTE REPLACED CUTOUT AND INSULATOR ONLY 8 CUSTOMERS OUT DELETE THE 3 CUSTOMER OUT STEP IN HOIS...HFP VER/HFP L3/HFP IDCC PN115, TOF833 XXXX
10765 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2019-03-31 02:33 | 2019-03-31 08:05 | 2 | 332 | 4042951 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held per KPCO callout guidelines.Cut out broke on line fuse @ 241-258 will make repairs/// Changed bad cutout and restored service @ 08:05
10766 | Hazard | 3311101 | STINNETT | REDBIRD | 2015-03-31 18:54 | 2015-03-31 21:40 | 4 | 166 | 4252541 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD C/O///// REPLACED XFMR C/O, POWER RESTORED VER/KEP
10767 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-04-13 06:38 | 2011-04-13 12:10 | 2 | 332 | 56254-1 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 15 KVA TRANSFORMER IS BAD ON POLE 214-460. I AM CALLING FOR HELP COD-2 MD FILED ON MISMAPPED CUSTOMER VER/KEP
10768 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-12-02 13:56 | 2015-12-02 16:42 | 4 | 166 | 4504481 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON 37830463000090 VER/CRB
10769 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-12-17 09:13 | 2009-12-17 14:45 | 2 | 332 | 51973-1 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 33117290 // XFMR BAD .TIM HALL TO GET CREW TO REPLACE .WILL NEED MATERILA HANDLER,& 25 KVA.19.9/120/240 RELEASED BY CREW 074S04, XFMR CHNGED OUT POWER BACK ON COD-2 ISO TF 37830069000203 VER/HFP L3/HFP
10770 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2018-06-30 02:40 | 2018-06-30 08:12 | 2 | 332 | 4691351 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Current limiting fuse bad on trans. pole 49-90, changed out and closed back in @0812.//cod 2
10771 | Hazard | 3308401 | BECKHAM | HINDMAN | 2017-11-06 12:09 | 2017-11-06 12:17 | 83 | 8 | 4535191 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Crews opening recloser on 37830179C00073 to safely make emergency repairs to bypass cutout. opened at 12:09 closed back at `12:17
10772 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2020-11-15 18:34 | 2020-11-15 21:20 | 4 | 166 | 4691371 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | transformer cutout at pole 45c24696 broke truck ok linecrew required Released by crew 078H09. Cutout repaired/back on @ 21:20 // cod 4
10773 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2020-03-11 16:21 | 2020-03-12 03:25 | 1 | 664 | 4469791 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad neutral in UG service, Need power temp. Crew required. Narrow street, Without much room to turn around Released by crew 078S02///power temp installed///send copy to tech so they can write job to replace UG///complete BR // emailed to tech // cod 1
10774 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2011-02-16 15:13 | 2011-02-16 16:36 | 8 | 83 | 58261-1 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | STS WR # 38835143 // POLE 20-285 20T LINE FUSE POLE 20-365 BAD LA NO TRUCK POLE 20-449 6T TRANS FUSE BAD LA SEND NOTE TO RAYBURN // ENTERED MD...HFP COD-7 PLEASE CLOSE THIS ORDER...HFP//IT FORCE CLOSED IDCC PN284 XXXX
10775 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2013-08-24 18:07 | 2013-08-24 19:30 | 8 | 83 | 4704201 | 664 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | #4 CU OPEN WIRE SECONDARY BURNT DOWN--OPENED TRANSFORMER ON POLE 38830139C00032 AT 18:42--MADE REPAIRS VER/SEF IDC XXXX
10776 | South Williamson | 3202201 | LOVELY | LOVELY | 2021-11-02 00:17 | 2021-11-02 11:20 | 1 | 663 | 4047931 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER/CREW WILL RETURN IN MORNING TO REPLACE
10777 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2015-09-12 18:34 | 2015-09-12 22:15 | 3 | 221 | 4232751 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 100KVA 19.9 TRANS. ON POLE 375-259, JEFF CAUDILL IS ON HIS WAY TO HELP ME CHANGE. CHANGED TRANS., CLOSED BACK IN AT 2215. VER/SEF
10778 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-02-20 10:04 | 2011-02-20 13:45 | 3 | 221 | 59442-1 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//IT FORCE CLOSED IDC CHANGED THE START TIME FROM 1004 ESTIMATED TIME OFF XXXX
10779 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2014-02-08 00:19 | 2014-02-08 04:00 | 3 | 221 | 4367421 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT @ POLE 424-51 NEED LINE CREW TO REPLACE TRUCK OK RELEASED BY CREW 078S05/ CREW ON SITE JEH/ REPAIRS COMPLETE POWER REST. @ 04:00/ PLEASE CLOSE TICKET VER/KEP
10780 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2009-08-29 21:29 | 2009-08-29 22:08 | 17 | 39 | H56251-1 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3402001//REPLACE BAD CUTOUT VER/DKG L3/DKG IDCC DUP OPEN FUSE TO MAKE REPAIRS XXXX
10781 | Hazard | 3308401 | BECKHAM | HINDMAN | 2019-11-16 13:43 | 2019-11-16 17:24 | 3 | 221 | 4040391 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced c/o
10782 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2008-07-08 21:04 | 2008-07-09 00:45 | 3 | 221 | 65234-1 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | 3410601// BAD DEAD-END INSULATOR. CREW ENROUTE. REPAIRS UNDERWAY. REPLACED INSULATOR AND RE-FUSED LINE FUSE. SH 3 40T MD FILED VER/KEP IDC XXXX
10783 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2018-01-06 09:43 | 2018-01-06 13:24 | 3 | 221 | 4712361 | 663 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr, I need one man ,big bucket, and 25 kva 7200 xfmr/ ISO 37830420C00284/ COD 3
10784 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-02-09 23:28 | 2022-02-10 10:30 | 1 | 662 | 4463611 | 662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Held per KPCO late night callout guidelines.Line fuse open at 285-23,Will be trying to get it back in.Have a Broke Line fuse cutout at 285-23,Will need a big bucket to change it,Spoke with Paul Layne and He is on his way to help make repairs..Have a Broke Line fuse cutout at 285-23,Will need a big bucket to change it,Spoke with Paul Layne and He is on his way to help make repairs..Restored at 10:30.
10785 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2011-08-14 13:51 | 2011-08-14 19:22 | 2 | 331 | 4708151 | 662 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 ---- DUTY SUPERVISOR NOTIFIED. RELEASED BY CREW 077S04//COD 2// VER/DBM IDC XXXX
10786 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2019-10-07 10:48 | 2019-10-07 11:00 | 55 | 12 | 4109131 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | reclosure on 140-44 back in at 11:00 L3/HFP
10787 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-09-26 17:38 | 2017-09-26 21:18 | 3 | 220 | 4391651 | 660 | PARTIAL POWER | EQUIPMENT FAILURE | FUSE | TRANS POLE 38831127A00271 WAS CHANGED OUT TODAY AND ONE OF THE HOT LEGS WAS SWITCHED WITH THE NEUTRAL ON THE OPEN WIRE ON POLE 1127-A-164, CUSTOMERS AT 3 ADDRESSES WERE HAVING THE PROBLEM 40, 58, AND 72 RATLIFF RD. PLEASE SEND A COPY TO PEGGY WYSOG, CUSTOMERS DO HAVE DAMAGE, MADE REPAIRS @2118./// VER/DKM ACBC MCCDL, CNT9, CCERF, FEC57, TON 2142
10788 | South Williamson | 3411401 | DEWEY | INEZ | 2019-06-07 07:58 | 2019-06-07 10:10 | 5 | 132 | 4443601 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse blown on 769-D-110.failed cutout on 769-D-115.replaced cutout.restored power up tp 769D115.line fuse blown on 769D115.pole 769-D4--175 NTA burnt up due to forest fire.conductors are intact but laying on grd.isolated line at 769D115 and tagged to KY DDC.
10789 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2009-06-11 10:00 | 2009-06-11 13:40 | 3 | 220 | 58244-1 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN TRANFORMER CUTOUT ON POLE 38831125A00247/ CREW ENROUTE/REPLACED CUTOUT AND BRACKET/ LINE FUSE OUT ON POLE 38831125A00157//COD 3// VER/DBM IDC XXXX
10790 | Pikeville | 3421001 | BREAKS | CITY | 2014-10-06 15:45 | 2014-10-06 21:15 | 2 | 330 | 4559121 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT FELL BURNED CROSSARM// NEED 3 MAN LINE CREW WITH BIG BUCKET AJB// VER/BOW AJB SEE H4559121.
10791 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2009-02-22 00:18 | 2009-02-22 04:31 | 13 | 253 | 50109-1 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000301 - OPENED FUSES AT POLE 20-7002 INTERRUPTING 13 CUSTOMERS - OPENED LOOPS AT POLE 20-7007 RESTORING ALL BUT 2 CUSTOMERS - POLE 20-7010 TOP BURNT OFF WR/28621768 RELEASED BY CREW 078S08/CREW ON SITE MAKING REPAIRS VEM/LAST CUST RESTORED 0431/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H05 //VER/GAH IDCC PN7010, TOF2339 XXXX
10792 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2011-12-02 06:18 | 2011-12-02 08:30 | 5 | 132 | 4135191 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-589 BAD WESTINGHOUSE CUTOUT 8T FUSE COD-5 ISO PO 38830069A20589 VER/HFP L3/HFP IDC XXXX
10793 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2010-01-08 17:15 | 2010-01-08 18:21 | 10 | 66 | 50601-1 | 660 | PARTIAL POWER | EQUIPMENT FAILURE | CABLE TERMINATOR | REPLACED CONN ON TRANSFORMER POLE THE SECONDARY SIDE ON THIS NEEDS REPLACED I WILL TRY TO GET A CREW TO REPLACE THIS MONDAY // SENT TO GLEN COMBS VER/TOM IDC XXXX
10794 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2012-01-30 10:30 | 2012-01-30 16:00 | 2 | 330 | 4305091 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED XMF ON 642-15. ONE SPAN OF #4 SOLID COPPER DOWN LINE CREW REQUIRED RELEASED BY CREW 078S11OPENED XMF ON 642-15. ONE SPAN OF #4 SOLID COPPER DOWN LINE CREW REQUIRED APR AT 1600 CLOSE TICKET ///VER/CRB IDC XXXX
10795 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-11-06 00:50 | 2014-11-06 01:50 | 11 | 60 | 4703591 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW MAKING REPAIRS ON 4702651 VER/ARN AJB TOF? // PER VOICE RECORDER FOR 11/06/14 @ 01:53:43 ON RADIO CONSOLE 3 OPENED FUSE @ 0050 CLOSED @ 0150 L3/HFP HFPC TOF
10796 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-03-25 20:31 | 2021-03-25 23:16 | 4 | 165 | 4375641 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse is open on 98-B-683,We have a broke cutout on pole 98-A-472,Will have to climb pole and make repairs..Restored at 23:16.
10797 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2020-05-21 12:15 | 2020-05-21 15:00 | 4 | 165 | 4879561 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | the cutout gate burned up , I changed it out
10798 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-07-25 17:33 | 2010-07-25 19:45 | 5 | 132 | 56909-1 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | POLE 1123-6125 HOT TAP BURNT OFF TRANS. CSP INSTALLED LINE FUSE ON POLE 1123-6075 20T MD FILED VER/KEP L3/KEP IDC XXXX
10799 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2009-07-17 08:18 | 2009-07-17 11:58 | 3 | 220 | 52324-1 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT TAP LEAD BURNT OFF ON POLE 38830092A00434 GOING TO POLE 38830092A00437-NEED CREW RELEASED BY CREW 078S07/REPAIRS HAVE ALREADY BEEN MADE/PLEASE CLOSE TICKET/THANKS/VEM RELEASED BY CREW 078H14 VER/KEP L3/KEP IDCC CNT2, PN1016 XXXX
10800 | Hazard | 3303901 | LESLIE | HYDEN | 2013-06-08 12:15 | 2013-06-08 17:45 | 2 | 330 | 4239521 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 19.9 TRANSF ==== NEED 1 MAN AND TRANSF === RELEASED BY CREW 077S03BAD 19.9 TRANSF ==== NEED 1 MAN AND TRANSF === CHANGED TRANSF === POWER OK VER/KEP IDCC PN21 XXXX
10801 | Hazard | 3303902 | LESLIE | WOOTON | 2010-07-20 18:00 | 2010-07-21 05:00 | 1 | 660 | 54224-1 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9 TRUCK ACCESSABLE RELEASED BY CREW 077S10 RELEASED BY CREW 077H03BAD 25 KVA 19.9 TRUCK ACCESSABLE RELEASED BY CREW 077S10 REPLACED TRANSFORMER AND CHECKED VOLTAGE , RESTORING POWER AT 0500 //VER/GAH IDC XXXX
10802 | Paintsville | 3401103 | FALCON | BURNINGFK | 2009-02-05 08:40 | 2009-02-05 14:10 | 2 | 330 | 55839-1 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR ..CALLED TIM MILLER..HE WILL GET A CREW TOGETHER AND CALL... RELEASED BY CREW 076S01 COD-2 VER/KEP L3/KEP
10803 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2013-10-09 19:33 | 2013-10-09 20:33 | 11 | 60 | 4925591 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 44-7558 30/4 WINDSTREAM POLE ROTT FELL OVER UNDERGROND ON POLE AND OPEN WIRE SEC. SEND TO VERNON M. RELEASED BY CREW 078S08/NO CUST OUT AT THIS TIME/WINDSTREAM SETTING POLE/WILL OUTTAGE XFMR TO TRANSFER/VEM/APPROX 2 HOUR OUTAGE/VEM/OPENED XFMR @1933/REPAIRS MADE AND POWER RESTORED 2033/PLEASE CLOSE TICKET/THANKS/VEM COD-11 ISO TF 38830044D47508 VER/HFP L3/HFP IDC XXXX
10804 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-08-13 23:50 | 2011-08-14 02:35 | 4 | 165 | 4705221 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON LINE FUSE POLE == CHANGED CUTOUT == POWER OK VER/KEP IDC XXXX
10805 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2015-02-16 19:17 | 2015-02-17 00:47 | 2 | 330 | 4034571 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I HAVE A BAD 19.9 CUT OUT. WILL CALL FOR HELP. TIM MCCOY RELEASED BY CREW 074H10 VER/SEF L3/HFP XXX
10806 | Hazard | 3301401 | COMBS | COMBS | 2017-04-26 18:05 | 2017-04-26 19:55 | 6 | 110 | 4685711 | 660 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONN. AT XFMR . .REPLACED CONN . SEND TO DOUG C. TO MAKE JOB TO REPLACE CONN. AT XFMR . HAS SPLIT BOLT CLAMPS . 500 COPPER TO 4/0 ALUMINUM . CAN WORK WITH BUCKET . SERVICER CAN DO JOB . OPENED XFMR AT 19:45 , CLOSED BACK AT 19:55 .//SENT TO TECH VER/CRB L3/HFP XXXHFP
10807 | Pikeville | 3411801 | JOHNSCREEK | META | 2021-08-16 13:20 | 2021-08-16 17:00 | 3 | 220 | 4079741 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BEST I CAN TELL,UG XFR BAYONET FUSE IS BLOWN.RICK RAY ENROUTE WITH A FUSE OR TWO.///////25 KVA XFR IS BAD.19.9 120-240////OPS#80255797(STORMS WR,34065479(OPS ORDER#)//WILL WORK TOMORROW CUST APPROVAL
10808 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2015-03-10 17:30 | 2015-03-10 21:10 | 3 | 220 | 4179411 | 660 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE 38830091A30022 BAD CUTOUT OR 1350 UNKNOWN TRY FUSE CAME OUT VERY HARD NO TRUCKS TO OTHER POLES CALL CREWS RELEASED BY CREW 078S08 (BAD 1350 ON TAKE OFF POLE 91-22 ALL POWER RESTORED AT 21:10) VER/CRB
10809 | Pikeville | 3411901 | FORDSBRANCH | SHELBY | 2014-10-16 16:34 | 2014-10-16 18:15 | 9 | 101 | 4637891 | 659 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ETA 1630// OPENED B & C PHASE LINE FUSE ON POLE 72-D-470 @ 16:34 TO PUT FIRE OUT ON POLE #72-625//// NEED 1 MAN AND BIG BUCKET/// NEED CUTOUT AND ARRESTOR AND POLE EXT.//POLE 72-625 IS NOT ON MAP// RELEASED BY CREW 074H17 VER/CRB L3/HFP
10810 | Pikeville | 3409502 | BURDINE | LEVISA | 2019-04-05 17:25 | 2019-04-06 10:30 | 4 | 329 | 4061531 | 658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 kva trans. burndt up on pole 336-81,trans. putting 250 volts on 1 phase of each home, both customers have multiple appliances burndt up, this will take a line crew with our biggest bucket to change out, needs replaced with a 25 kva 7200. I opened trans. @1725, both customers breakers are off.
10811 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2013-03-05 20:20 | 2013-03-06 07:18 | 1 | 658 | 4873971 | 658 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | PARTIAL POWER.LOOSE CONNECTION ON XFMR POLE..REPLACED CONNS. VER/KEP IDC XXXX
10812 | Hazard | 3310501 | HADDIX | QUICKSAND | 2019-10-07 11:31 | 2019-10-07 17:00 | 2 | 329 | 4109661 | 658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 19.9 cutout on pole 38831040B30122. restored power at 17:00
10813 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2016-03-07 02:42 | 2016-03-07 08:11 | 2 | 329 | 4822341 | 658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | SECONDARY BURNT DOWN - MAKING REPAIRS @ 0737 //WILL WORK DURING NORMAL SHIFT.SECONDARY BURNT INTO ON POLE 444-18 SERVING POLE 444-124 DUE TO BAD SPLICE IN WIRE, OPENED XFMR AT 07:44 MADE REPAIRS , RESTORED POWER AT 08:11. VER/HFP L3/HFP AJB CNT10 CDC92 SEE H4822341
10814 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-03-09 21:36 | 2019-03-10 03:05 | 2 | 329 | 4965341 | 658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | crew required no trucks up on hillside/199-78 Released by crew 078S03 Restored @ 0305
10815 | Hazard | 3311101 | STINNETT | REDBIRD | 2022-07-18 15:44 | 2022-07-18 21:13 | 2 | 329 | 4515541 | 658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke cut-out on 37830482B00044. Need 7200 cut-out and t bracket. Pole is in field in soft ground. May reach with big buck. Crew required. Released by crew 077S06//MADE MD TO SHOW L/F
10816 | Whitesburg | 3312902 | JENKINS | JENKINS | 2012-10-26 09:01 | 2012-10-26 10:35 | 7 | 94 | 4173341 | 658 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | BAD SPLICE IN SECONDARY AT POLE 405-154.. MADE REPAIRS RESTORED POWER AT 10:35//COD 7// VER/DBM IDC XXXX
10817 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2018-10-21 18:22 | 2018-10-21 19:35 | 9 | 73 | 4305241 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut out failed on line fuse while trying to energize an xfer on a different outage ticket L3/HFP
10818 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2022-08-26 23:23 | 2022-08-27 08:35 | 8 | 552 | 4800941 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | Customer states okay to wait till tomorrow. Call cust before arrival and they will put their dogs up.melted sd connections. repaired.. open xfmer @ 1098-319. off @ 08:20, restored @ 08:35
10819 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2017-03-09 22:11 | 2017-03-10 01:50 | 3 | 219 | 4542951 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA XFR @ 280-27,,,SHOULD BE ABLE TO GET TRUCKS TO POLE ,,,BRING MOPADS RELEASED BY CREW 078S05--CREW ON SITE--FETR 02:19 CHG XFMR ALL PWR RESTORED @ 01:50 PLEASE CLOSE TICKET RMV VER/KEP
10820 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2021-06-30 11:41 | 2021-06-30 15:20 | 3 | 219 | 4826711 | 657 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 37.5 transformer. 120/240, 7200, two bushing. Trucks to pole. Leaked oil on concrete. Opened other two transformers @ 13:15. Please send to Luke Mccoy Released by crew 078S02 crew on site FETR 15:30 LRM//PART POWER FROM BEGINNING
10821 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2009-01-01 01:03 | 2009-01-01 02:16 | 9 | 73 | 50399-1 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3417602, ON SITE, CHECKING TROUBLE, CUTOUT DOOR BURNT UP, REPLACED DOOR // 27867341 VER/JHM L3/KEP IDC XXXX
10822 | Pikeville | 3402002 | KEYSER | STONECOAL | 2014-11-10 11:02 | 2014-11-10 12:15 | 9 | 73 | 4716551 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED L/F 37830024C00875 @ 1102 TO SAFELY CHANGE OUT TRANS ON TIX 4715751 VER/CRB L3/HFP
10823 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2012-01-07 16:33 | 2012-01-07 20:12 | 3 | 219 | 4240061 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL CHECK FOR PROBLEMS///////BAD XFR,1 LEG OPEN INSIDE,NEED 25KVA 7.2 ,MAT HANDLER,1 MAN//////REPLACED XFR AND RESTORED//COD 3// VER/DBM IDC XXXX
10824 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-05-16 16:43 | 2014-05-16 17:56 | 9 | 73 | 4716491 | 657 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKEN CUTOUT ON POLE 38831061D00097, NOT IN USE, REMOVED FROM LINE. COD-9 ISO LF 38831061D00071 VER/HFP L3/HFP
10825 | Pikeville | 3411701 | CEDAR CREEK | HOOPWOOD | 2020-03-29 19:15 | 2020-03-29 19:56 | 16 | 41 | 4534791 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | DOL 1004862/Emergency outage due to pole fire outside station/Fault pole 23-234/Opened sws at 37830023000239 to isolate after breaker opened @ 1915/Center pole top pin broke off @23-234 and let center phase fall against pole, pole is on fire will need to open Ivy Court circuit to make repairs. 30-45 minute outage.Center pole top pin broke off @23-234 and let center phase fall against pole, pole is on fire will need to open Ivy Court circuit to make repairs. 30-45 minute outage. off 1915-1956/
10826 | Pikeville | 3407101 | TOPMOST | DEMA | 2014-06-20 07:17 | 2014-06-20 12:45 | 2 | 328 | 4119971 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 30T FUSE OUT DUE TO BAD CUTOUT AT POLE 114-34 BURNT TOP OF POLE OFF. CREW REQUIRED . NEED 8FOOT CROSS ARM CUTOUT ARRESTER GUY ATT PRIMARY DEADEND. REPAIRS MADEFUSED UP EVERYTHING OK. VER/CRB
10827 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2012-08-04 21:24 | 2012-08-05 08:20 | 1 | 656 | 4897611 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANS, NO TRUCK BACK YARD THING RELEASED BY CREW 078S08 ( INSTALLED 37.5 KVA TRANS & NEW ARRESTOR POWERED RESTORED AT 08:20)//COD 1// VER/DBM IDC XXXX
10828 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2012-01-04 09:34 | 2012-01-04 15:02 | 2 | 328 | 4232121 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA CSP TRANSFORMER FAILED CREW ENROUTE RELEASED BY CREW 074S02// REPLACED BAD C.S.P. XFMR AND RESTORED POWER. TIM MCCOY ///VER/CRB IDC XXXX
10829 | Pikeville | 3403001 | PIKEVILLE | CITY | 2012-02-06 19:01 | 2012-02-06 19:42 | 16 | 41 | 4324351 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | FAULTED NEW PAD MOUNT TRANSFORMER IDCC CCO, CDC83 XXXX
10830 | Pikeville | 3402003 | KEYSER | MULLINS | 2016-09-05 15:32 | 2016-09-05 18:16 | 4 | 164 | 4869521 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 127-B-303 HAS ROTTED OFF AT THE GROUND, WILL NEED 2 MEN WITH A 30 FT. POLE AND A PIECE OF 1/0 SERVICE WIRE TO SPLICE WITH, HAD TO OPEN THE TRANS. ON POLE 38831127B00473 @ 1532 TO BEGIN MAKING REPAIRS. CHANGED OUT POLE AND CLOSED TRANS. @1816./ ISO 38831127B00473/ COD 4/ VER/BOW
10831 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2013-11-27 09:04 | 2013-11-27 14:32 | 2 | 328 | 4080101 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE FIRE NEED LINE CREW NO TRUCK RELEASED BY CREW 078S05R\W CUTTING TREES WILL BE LOWERING PHASE NEUTRAL KVA DW VER/CRB L3/HFP
10832 | Cannonsburg | 3001203 | HOWARDCOL | FLOYD | 2009-07-05 14:06 | 2009-07-05 14:47 | 16 | 41 | 66322-1 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 16// VER/DBM IDC XXXX
10833 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-02-01 02:12 | 2008-02-01 07:40 | 2 | 328 | 62981-1 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3311101** TRUCK DOWN WILL CK AT DAYLIGHT IF SINGLE CUST. 3311101 TRUCK DOWN WILL CK AT DAYLIGHT IF SINGLE CUST. BAD CUTOUT IDC XXXX
10834 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2014-12-01 21:39 | 2014-12-02 03:07 | 2 | 328 | 4823941 | 656 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MULLINS & MORGAN & HOWARD // 2 CUST OUT OPENED FUSE ON 20-B-3044 TO ISOLATE TROUBLE // GOING TO LOWER EQUIPMENT ON POLE/CREW ON SITE/FETR 0400/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 0307/PLEASE CLOSE TICKET/THANKS/VEM VER/ARN
10835 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2022-09-10 21:40 | 2022-09-11 08:35 | 1 | 655 | 4863691 | 655 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad transformer.cutout on arm at pole 33 will be crew required will need hardguard.manual pole.would be better to wait until morning time Released by crew 079S02
10836 | Cannonsburg | 3000901 | HIGHLAND | RUSSELL | 2008-07-25 05:33 | 2008-07-25 11:00 | 2 | 327 | 60033-1 | 654 | PARTIAL POWER | EQUIPMENT FAILURE | CUTOUT | 3000901/// BAD CUTOUT CREW ON WAY// CHANGE 3 CUTOUTS AND L/AS. TIME OFF 10:20 TIME ON 11:00 M.PHELPS 7/24/08 RELEASED BY CREW 078H12//COD 2// VER/DBM IDC XXXX
10837 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-05-23 12:08 | 2018-05-23 17:35 | 2 | 327 | 4401901 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cut-out busted on pole 1125-D-573, manual pole, will be making repairs. Got c/o replaced, closed back in @1735.
10838 | Hazard | 3310502 | HADDIX | CANOE | 2010-01-02 22:56 | 2010-01-03 09:50 | 1 | 654 | 57998-1 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | THIS IS 3 KVA TRANSFORMER , GOING TO SHOOT TRANSFORMER, BAD TRANSFORMER NEED 15 KVA AND BIG BUCKET RELEASED BY CREW 077S05/ DUTY SUPV SAID TO WORK IN MORNING DURING DAYLIGHT. / COD-1 ISO TF 37830052000023 VER/HFP L3/HFP IDC XXXX
10839 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2020-06-08 15:37 | 2020-06-08 19:15 | 3 | 218 | 4981041 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 15kva on pole 445-49. need at least one man and big bucket.. transformer changed. power restored @ 19:15
10840 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2020-10-20 20:32 | 2020-10-21 00:10 | 3 | 218 | 4571951 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad CSP xfmr 25kva. Have called for A Lineman & big bucket to replace/// Replaced xfmr and restored @00:10
10841 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2015-02-20 06:54 | 2015-02-20 17:48 | 1 | 654 | 4050241 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA 7200 TRANSFORMER. NTA POLE IN FIELD IS 1086-216. DIFFICULT LOCATION. NEED TO REPLACE CUTOUT AND STANDOFF ALSO. RELEASED BY CREW 079H07BAD 25KVA 7200 TRANSFORMER. NTA POLE IN FIELD IS 1086-216. DIFFICULT LOCATION. NEED TO REPLACE CUTOUT AND STANDOFF ALSO. REPLACED BAD 15KVA WITH A 25KVA. VER/HFP L3/HFP
10842 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2022-02-06 08:09 | 2022-02-06 13:36 | 2 | 327 | 4448621 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | got bad 25 19,9 transformer need bucket and new cutout and tee brkt and transformer Released by crew 077S05. all power restored @ 13:36
10843 | Paintsville | 3401103 | FALCON | BURNINGFK | 2016-07-31 08:47 | 2016-07-31 12:25 | 3 | 218 | 4714681 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT FAILED. REPLACED AND RESTORED @ 12:25. SH/ ISO 38830876D00043/ COD 3/ VER/BOW
10844 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2015-04-20 12:40 | 2015-04-20 14:29 | 6 | 109 | 4340201 | 654 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED XFMER @ 46-552, BAD 12KV CUTOUT, ARRESTOR RELEASED BY CREW 078S07/CREW ON SITE/FETR1457/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 1429/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830046A20552/ COD 6 VER/CRB L3/HFP XXX
10845 | Pikeville | 3408101 | SALISBURY | PRINTER | 2014-12-26 02:32 | 2014-12-26 05:15 | 4 | 163 | 4885111 | 652 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I OPENED TRANSFORMER ON POLE 1122-46 AT 04:00 DUE TO BAD CONNECTION AT WEATHER HEAD 1 SIDE HEATED UP WHERE CONNECTION WAS MADE AND GOT INTO THE NEUTRAL. REPAIRS MADE CLOSED TRANSFORMER FUSE BACK IN AT 05:15. SEND COPY OF THIS TO ENG PIKEVILLE NEED TO SET ANOTHER SEC POLE TO CUST IS SERVED FROM SEC POLE 1122-19 SERVICE DROP IS ABOUT 175 FOOT AND ALSO NEED TO INSTALL 2/3 SERVICE DROP
10846 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2013-12-12 21:18 | 2013-12-13 00:01 | 4 | 163 | 4157991 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 92-329 BAD 19.9 CUTOUT NO TRUCKS RELEASED BY CREW 078S08/ FETR// 00:30//JEH// REPAIRS COMP. POWER RESTORED @ 00:01// JEH VER/HFP L3/HFP
10847 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2014-07-15 08:09 | 2014-07-15 13:35 | 2 | 326 | 4247271 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 69-592 BAD WESTINGHOUSE CUTOUT AND LA REPAIRED//COD 2// VER/DBM
10848 | Hazard | 3303902 | LESLIE | WOOTON | 2022-05-30 16:39 | 2022-05-30 19:22 | 4 | 163 | 4983871 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Cut blown arrester in clear on 367-81. Power restored @ 19:22
10849 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2013-09-06 20:57 | 2013-09-06 23:40 | 4 | 163 | 4826571 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | CHANGED CUTOUT REPAIRED HOT TAP , ALL CUST OMERS WAS OUT 1140 WHEN BACK ON ON 1 OUTAGE FOR HOIS. VER/PDPC XXXX
10850 | Pikeville | 3409502 | BURDINE | LEVISA | 2009-01-16 08:24 | 2009-01-16 13:50 | 2 | 326 | 55682-1 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 28093905 //TRANSFORMER IS BAD WILL NEED A 25 KVA AND MATERIAL HANDLER RELEASED BY CREW 074S07 COD-2 L3/HFP
10851 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2022-03-20 14:20 | 2022-03-20 17:03 | 4 | 163 | 4650841 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required bad 25kva trucks ok Released by crew 078S03,repairs made all cust restored @ 1703 please close ticket thanks.bt
10852 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2020-09-16 09:32 | 2020-09-16 12:15 | 4 | 163 | 4468121 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on p 286-87 going to make repairs FETR 12:15 LRM all pwrrestored 12:15pleasecloseticket LRM
10853 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2012-09-07 11:47 | 2012-09-07 14:30 | 4 | 163 | 4026781 | 652 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | ARRESTOR BLOWN ON 785-392.LINE FUSE BLOWN ON 785-100.65 T FUSE.CHG ARRESTER.RE FUSED// MADE MDC ///VER/CRB L/3 CRB IDCC PN392 XXXX
10854 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2021-08-31 15:14 | 2021-09-01 02:05 | 1 | 651 | 4185911 | 651 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | crew required bad ug will need power temp. Released by crew 078H33 crew on site FETR2:20 all pwr restored 2:05 please close ticekt LRM
10855 | South Williamson | 3200302 | BELFRY | TOLER | 2018-08-09 10:14 | 2018-08-09 10:35 | 31 | 21 | 4932241 | 651 | DISTRIBUTION LINE | EQUIPMENT FAILURE | RECLOSER, LINE/OCR/BR | B phase (road) recl open///B phase recloser is open at pole 38821015D00081. Recloser opened when load was transferred to the Belfry / Toler from the Barrenshee / Pounding Mill. Power is restored. Released by crew 079S02 DUPLICATE ALSO OF THIS L3/HFP
10856 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-09-10 08:37 | 2018-09-10 19:28 | 1 | 651 | 4073621 | 651 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew required, Two bad 50kva 7200, 480 Power bank. Trucks to pole Released by crew 078H04/crew on site/will need to open fuses on 44-C3-5007 for repairs/aprox two hour outage/vem/opened fuses at 1645/vem/missing clips in cluster mount/NEW FETR 1945/vem/repairs made and power restored to all cust 1928/please close ticket/thanks/vem Released by crew 078H14
10857 | Pikeville | 3421001 | BREAKS | CITY | 2015-02-15 08:46 | 2015-02-15 19:37 | 1 | 651 | 4025861 | 651 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | WIRE DOWN AT POLE 37820220C0059/LINE CREW REQUIRED/COD1/ POLE DECAYED AT GROUNDLINE.POLE#220-591. TRANSFORMERS COMING FROM ASHLAND. VER/KEP L3/HFP XXX
10858 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2016-07-24 10:23 | 2016-07-24 12:33 | 5 | 130 | 4672801 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMER RISER BURNT OUT OF BOTTOM OF C/O. HENDRIX, TIGHT SPACING RELEASED BY CREW 078S07--CREW ON SITE---REPLACED CUTOUT AND MADE NEW CONNECTION---PWR RESTORED AT 12:33---TBL TKT COMP---RMV VER/AWD
10859 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2013-10-07 17:23 | 2013-10-07 18:28 | 10 | 65 | 4919901 | 650 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | STIRRUP BURNT IN TWO ALLOWING PHASE B LINE FUSE RISER TO FALL AGAINST PHASE A RISER. GOING TO PAINTSVILLE OFFICE TO GET A 556 MCM STIRRUP TO MAKE REPAIRS. REPLACED STIRRUP AND CUTOUT. OPENED THREE FUSES ON 785-967 @ 18:58 AND CLOSED @ 19:25. SH 10 = 3 PHASE CUST HAD PART POWER ---- SEE H4919901 FOR OUTAGE FOR 3 CUST WHEN FUSES OPENED. VER/HFP L3/HFP IDC XXXX
10860 | Pikeville | 3401001 | ELWOOD | DORTON | 2013-12-14 11:25 | 2013-12-14 16:50 | 2 | 325 | 4161111 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANS. IS BAD ON POLE 287-4. I AM CALLING FOR HELP. WE CHANGED TRANS. VER/CRB L3/HFP
10861 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2018-12-25 22:00 | 2018-12-25 23:05 | 10 | 65 | 4598221 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad cutout on 115-55, changed out and fuse back in at 23:05 L3/HFP
10862 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2011-11-22 08:01 | 2011-11-22 09:06 | 10 | 65 | 4099391 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FUSE IS OPEN ON 573-80 PATROLLING LINE. FOUND BLOWN ARRESTER ON 572-75 CLEARED ARRESSTER, PLEASE PLACE IN ABNORMAL NO TRUCKS TO POLE. APR AT 906 CLOSE TICKET//AED CREATED//COD 10// VER/DBM IDC XXXX
10863 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-05-16 10:30 | 2019-05-16 11:35 | 10 | 65 | 4276651 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPENED L/F 38820965B00043//COD 10//TO REPAIR CONDUCTOR ON POLE 38820965B00168 AND CHANGE CUTOUT ON THIS POLE//OFF @ 1030 ON @ 1135 L3/HFP
10864 | Hazard | 3308001 | JACKSON | S.JACKSON | 2019-07-11 15:47 | 2019-07-11 16:12 | 26 | 25 | 4695981 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on 1083-142, open to repair @ 15:47..closed back in @ 16:12 hra , all power restored p.hicks..as built complted. L3/HFP
10865 | Cannonsburg | 3000301 | BELLEFONT | WESTWOOD | 2018-05-22 19:30 | 2018-05-22 20:20 | 13 | 50 | 4396641 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Pole Fire @ 38830044C45646/ 30T Line Fuse open @ 38830044C35061/ Lifted Hot Tap on pole 38830044C35077/ Closed Line Fuse 38830044C35061 @ 2020/ closed hot tap 38830044C35077 @ 2329--crew on site--repaired burnt pole---
10866 | Cannonsburg | 3117602 | PRINCESS | ROUTE 180 | 2020-07-08 08:18 | 2020-07-08 13:43 | 2 | 325 | 4128541 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 2 Blown LA on xfmr bank--changing LAs--
10867 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2015-09-09 10:05 | 2015-09-09 12:15 | 5 | 130 | 4217361 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | REPLACED BAD INSULATORS ON POLES 68/17 & 68/131..TOOK OFF AT 10:05 AND RESTORED AT 12:15 DAVE LEWIS 9/9/15//LIFTED HOT LINE ON POLE 37830068000017 VER/CRB
10868 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2016-09-28 23:50 | 2016-09-29 10:40 | 1 | 650 | 4940311 | 650 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER ON 9-C-120 BAD TRK APPROACH POLE 25 KVA 19.9 TRANSFORMER RELEASED BY CREW 079H03 REPLACED BAD TRANSFORMER RESTORED CUSTOMER AT 10:40 ROBBIE WORRIX// VER/ADH
10869 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-03-06 21:41 | 2015-03-07 08:30 | 1 | 649 | 4153511 | 649 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONN. ON HOUSE REPAIRED VER/KEP
10870 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2018-06-02 14:36 | 2018-06-02 18:12 | 3 | 216 | 4547131 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | line fuse out, I cleared old lightning arrestor on pole 402-452 and refused line
10871 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2016-08-05 18:16 | 2016-08-05 23:40 | 2 | 324 | 4740091 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | POLE 304-30 ROTTED OFF AT GROUND LEVEL & FELL OVER. CAN OPEN LINE FUSE ON328-55 TO ISOLATE.POLE 304-30 ROTTED OFF AT GROUND LEVEL & FELL OVER.OPENED LINE FUSE ON POLE 328-55 AT 22:14 TO ISOLATE..POLE 304-30 ROTTED OFF AT GROUND LEVEL & FELL OVER.OPENED LINE FUSE ON POLE 328-55 AT 22:14 TO ISOLATE..MADE REPAIRS RESTORED POWER AT 23:34. VER/AWD
10872 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2015-09-30 07:38 | 2015-09-30 08:50 | 9 | 72 | 4293401 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | TRANSFORMER FUSE OUT... GUY BROKE AND FELL ACROSS PRIMARY BUSHING ON TRANSFORMER, REPAIRED GUY..POWER RESTORED @ 08:50 VER/CRB L3/HFP XXXHFP
10873 | Paintsville | 3402501 | MIDDLECREEK | DISTRIBUTION | 2016-04-28 11:53 | 2016-04-28 13:05 | 9 | 72 | 4137511 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIDDLE PHASE OUT ON REC 1047-141 PATROLLING LINE. FOUND BROKEN CUTOUT ON CAP BANK POLE 38831047000012 AND ISOLATED. CLOSED RECLOSER @ 13:05. I WILL SEND A JOB TO ENGINEERING TO HAVE CUTOUTS AND SENSOR INSULATOR REPLACED. SH RELEASED BY CREW 076S02/9COD/AED MADE/ADH// VER/ ADH
10874 | Cannonsburg | 3000105 | ASHLAND | 25-1 | 2008-05-02 11:52 | 2008-05-02 13:40 | 6 | 108 | 56316-1 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3000105//45-145 HOT TAP BROKE//ISO 38830045C30145//COD 6// VER/DBM
10875 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-11-09 04:00 | 2015-11-09 06:42 | 4 | 162 | 4420411 | 648 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | APPEARS TO BE A POOR HEATED-UP CONNECTION AT MAST,WILL REPAIR//////////////REPLACED CONNECTION,ALL OK AFTERWARDS ,WAS A POOR SQUEEZ-ON CONNECTION ON #2 TO 4/0 COPPER,APPEARED THAT CUSTS ENTRANCE WAS AN OLD COPPER MINING CABLE(VERY FINE STRANDED WIRE ALTHO IT WAS 4/0 WIRE) VER/ARN
10876 | Paintsville | 3401101 | FALCON | FALC-OILS | 2022-08-17 21:14 | 2022-08-18 00:50 | 3 | 216 | 4758041 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 Kva transformer failed. Crew enroute to replace.. Replaced and restored @ 00:50. sh
10877 | South Williamson | 3411401 | DEWEY | INEZ | 2015-12-22 10:48 | 2015-12-22 13:30 | 4 | 162 | 4550101 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 769-37//BIG BUCKET ENROUTE TO CHANGE OUT//REPAIRS MADE//RESTORED AT 13:30//COMPLETE//EM/ ISO 38820769C00037/ COD 4/ VER/BOW
10878 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-02-02 15:44 | 2014-02-02 19:20 | 3 | 216 | 4337541 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA 7200 XFMR, RELEASED BY CREW 077S11BAD 15 KVA 7200 XFMR, REPLACED XFMR REATORED POWER AT 19:20, ONLY 3 CUSTOMERS AFFECTED//COD 3?//ISO// VER/DBM
10879 | Pikeville | 3120103 | STANVILLE | HAROLD | 2019-04-26 19:15 | 2019-04-26 20:36 | 8 | 81 | 4175151 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 1/0 open wire burndt down on trans. pole 1101-D1-136, had to open trans. to make repairs. Opened @1915 Closed@2036. L3/HFP
10880 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2009-06-13 05:48 | 2009-06-13 08:30 | 4 | 162 | 59860-1 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SERVICER PATROLLING LINE. TIM MILLER COMING OUT TO HELP.CSP TRANSFORMER BAD 1 POLE PAST..785-1001..POLE IS NOT ON MAP NO POLE TAG..65 T FUSE BLOWN ON 785-693 MLR OK B PHASE
10881 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-11-22 17:31 | 2017-11-22 22:55 | 2 | 324 | 4596641 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 12kv xmfr. 25kva truck ok, crew required Released by crew 078S11/on site RM all power restored pleaase close ticket RM//cod 2
10882 | Paintsville | 3401101 | FALCON | FALC-OILS | 2014-01-07 10:06 | 2014-01-07 15:30 | 2 | 324 | 4249231 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA XFMR..NO TRUCK ACCESS.BOBBY TACKETT.TO CHANGE... RELEASED BY CREW 076S01//COD 2// VER/DBM
10883 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-01-21 13:14 | 2022-01-21 16:50 | 3 | 216 | 4393471 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | #4 cu primary pulled out of sleeve at 900-50. Made repairs and restored @ 16:50. sh
10884 | Pikeville | 3402002 | KEYSER | STONECOAL | 2022-12-24 11:54 | 2022-12-24 15:30 | 3 | 216 | 4345271 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 CSP trans. @1105-D-144, will be changing. Got trans. changed out and power restored @1530.
10885 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2009-05-27 17:20 | 2009-05-27 20:56 | 3 | 216 | 57123-1 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP WR # 30005734 // CUST HAS HIGH VOLTAGE PULLED MAY HAVE BAD TRANSFORMER COD-3 ISO 38830045C45728 CUST HAS HIGH VOLTAGE PULLED MAY HAVE BAD TRANSFORMER TRANSFORMER IS BAD GIVE TO LLOYD MCCARTY RELEASED BY CREW 078S09 L3/HFP IDC XXXX
10886 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-04-04 06:22 | 2017-04-04 09:58 | 3 | 216 | 4611091 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN @ 37820098A00035, BAD 19.9 CUT-OUT ON POLE 37820098A00362, STEVIE RAY COMING TO HELP CHANGE OUT. CHANGED C/O AND CLOSED BACK IN @0958./ ISO 37820098A00035/ COD 3/ VER/BOW L3/HFP XXXHFP
10887 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2012-06-23 23:54 | 2012-06-24 01:15 | 8 | 81 | 4956121 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY HOT-LINE CLAMP RISER BURNT OPEN. REPLACED ALUMINUM RISER WITH COPPER AND A NEW HOT-LINE CLAMP. RESTORED @ 1:15. SH. CC = 8. ENTIRE TAP OUT, 3 TR`S. VER/SDB
10888 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2012-04-24 09:37 | 2012-04-24 12:19 | 4 | 162 | 4701991 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW OPENED LINE FUSE TO ALLOW THE TO SAFELY REPLACE POLE BURNT OFF YESTERDAY WHEN A CUTOUT FAILED // COD-4 ISO LF @ 37820146000019 VER/HFP L3/HFP
10889 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2017-01-13 17:54 | 2017-01-13 21:30 | 3 | 216 | 4296151 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | COD 3//MD MADE//OPEN NEUTRAL INSIDE 25 KVA TRANSFORMER. THREE CUSTOMERS AFFECTED: 533594463 - 533594465 - 533594459.//SENT TO PEGGY WYSONG-CLAIMS//OPEN NEUTRAL INSIDE 25 KVA TRANSFORMER. THREE CUSTOMERS AFFECTED: 533594463 - 533594465 - 533594459. REPLACED XFMR, 100 WATT HPS LIGHT AND RESTORED @ 21:30. SH VER/CRB // RELATED TO 4296251 & 4296221 L3/HFP HFP
10890 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-11-12 13:21 | 2015-11-12 14:33 | 9 | 72 | 4435721 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LINE FUSE OUT ON POLE 900-23.. PATROLED DIDNT FIND ANYTHING..WHEN TAKEN DOOR DOWN THE FUSE HAD BROKE.. REFUSED AND CLOSED IN AT 14;33 TO RESTORE POWER.. COMPLETE RN // COD-9 ISO LF 38830900000023 VER/HFP L3/HFP
10891 | South Williamson | 3411401 | DEWEY | INEZ | 2018-08-07 22:07 | 2018-08-07 23:55 | 6 | 108 | 4922881 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | line fuse out on pole 744-9//cutout broke on pole 768-230//repairs made///restored at 23;55//complete//em //cod 6 L3/HFP
10892 | Pikeville | 3407103 | TOPMOST | KITE | 2016-01-29 09:09 | 2016-01-29 10:57 | 6 | 108 | 4657881 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY METERING TAGGED TO THE KYDDC// HOT TAP LEAD BURNT OFF ON POLE 209-100, CLEARED UP LEAD, CUST SAID ALRIGHT TO WAIT TILL MONDAY TO MAKE REPAIRS, GOT DISCONNECTS OPEN ON POLE 209-194 AT METERING,,NEED 4/0 AL SPLICE AND 2/0 COPPER LEAD AND HOT TAP,,OPENED REC ON POLE 209=200 AT 10:47,,, BACK IN AT 10:57 RELEASED BY CREW 074H07//SENT TO TIM HALL VER/CRB
10893 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2013-03-11 19:02 | 2013-03-11 21:30 | 6 | 148 | 4899081 | 648 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | "B" PHASE ONLY COD-6 MD FILED FUSE ON POLE#901-5008, LA BLOWN POLE#901-5022/RESTORED ALL BUT 901-5022 AT 2030/ ALSO HAD B PHASE TRANSFORMER FUSE OUT ON BANK POLE 901-5022 REFUSED AND EVERYTHING IS OK AT THIS LOC AT 2130 VER/KEP IDC XXXX
10894 | Pikeville | 3400701 | DRAFFIN | BELCHER | 2020-05-08 21:13 | 2020-05-09 08:00 | 1 | 647 | 4815131 | 647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA 7200 Xfm///Can use truck Needs cutout bracket & arrestorBad 25 KVA 7200 Xfm///Can use truck/// Will need cutout and bracket Released by crew 074S02 closed 0800
10895 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-04-17 17:43 | 2017-04-18 04:30 | 1 | 647 | 4652901 | 647 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | RELEASED BY CREW 075H04 XFMR FUSE OUT . BAD 15KVA 19.9 XFMR . NEED BIG BUCKET . SET IN ROAD TO WORK POLE . RELEASED BY CREW 075H04 REPLACED TRANSFORMER AND CUTOUT ,RESTORING POWER AT 0430//COD 1// L3/HFP XXXHFP
10896 | Hazard | 3303901 | LESLIE | HYDEN | 2009-04-01 15:07 | 2009-04-01 20:30 | 2 | 323 | 63817-1 | 646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WR # 29190298 // VER/TOM L3/TOM IDCC CNT1 XXXX
10897 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2019-10-07 12:02 | 2019-10-07 17:25 | 2 | 323 | 4110111 | 646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 7200- 37.5 xfmer. small bkt or yard dog. access from 106 country club ct off country club dr. Released by crew 078S07 restored @ 1725
10898 | South Williamson | 3404302 | SIDNEY | COBURN MTN | 2012-07-25 23:52 | 2012-07-26 10:38 | 1 | 646 | 4829681 | 646 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR.POLE 989B4-360..NEED CREW.LAST 500 FT OF ROAD TO ROUGH & NARROW FOR MATERIAL HANDLER.PICK UP &/OR SQUIRT BUCKET ACCESS ONLY.. RELEASED BY CREW 080S01//COD 1// VER/DBM
10899 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-04-25 11:06 | 2015-04-25 13:15 | 5 | 129 | 4364461 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | /CUTOUT FAILED AND CAUGHT POLE ON FIRE @ 37820073A00039/ ISO 37820073A00058/ COD 5. I REMOVED HOT TAP ON TRANS. AND PUT FIRE OUT. I AM GOING TO REFUSE LINE FUSE. I CLOSED LINE FUSE IN AND IT STAYED. VER/ARN
10900 | South Williamson | 3411401 | DEWEY | INEZ | 2021-06-11 08:50 | 2021-06-11 12:25 | 3 | 215 | 4713531 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 38830744D00111..also got the line fuse out on pole 38830744D00009.i got the cut out on pole replaced on 744-D-111 back in @ 12:10.i also got the linfuse on pole 744-D9 @ 12:25
10901 | Pikeville | 3413401 | GARRETT | GARRETT | 2017-05-13 17:05 | 2017-05-13 20:40 | 3 | 215 | 4796271 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CALLED CUSTOMER SEVERAL TIMES: NO ANSWER // LINE FUSE OPEN POLE 16-86, CSP XFMR BAD AT POLE 87, SERVES 150W HPS OL ONLY ON POLE 253 . SEND TO C. FREEMAN FOR JOB TO REROUTE SECONDARY OR REPLACE XFMR, COMPLETE / GXJ
10902 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2010-02-06 02:05 | 2010-02-06 12:50 | 1 | 645 | 65780-1 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE TOP BURNT OFF. NOTIFIED RANDALL MARCUM, WHO REPORTED WILL MAKE REPAIRS AFTER DAYLIGHT.WAITING FOR CREW FROM PIKEVILLE. IDC XXXX
10903 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2014-03-16 20:35 | 2014-03-17 00:10 | 3 | 215 | 4498861 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 7200 CUTOUT, NEED BUCKET AND CUTOUT AND ARR. AND TEE BRACKET. --- POWER RESTORED. VER/ARN
10904 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2014-11-17 15:58 | 2014-11-17 19:33 | 3 | 215 | 4737281 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE /// NEED 1 MAN NO TRUCK/ OPENING HOT TAP ON POLE 149-146 WILL HAVE 149-147 AND 149-155 CUTOUT BROKE /// NEED 1 MAN NO TRUCK/ OPENING HOT TAP ON POLE 149-146 WILL HAVE 149-147 AND 149-55// TOOK HOT TAP OFF @19:00 AND PUT HOT TAP BACK ON @ 19:31 THESE ARE TIMES FOR 37820149000155/// CHANGED BAD CUTOUT AND RESTRED SERVICE @ 19:33 37820149000147// ISO 37820149000147// COD 4 TOTAL/ H4737281/ VER/BOW
10905 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2015-07-09 23:45 | 2015-07-10 10:30 | 1 | 645 | 4760181 | 645 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT NEEDS REPLACED LINECREW REQUIRED NO TRUCK, TIME OFF WAS 2345 RELEASED BY CREW 078S11.. CREW ON SITE ETR 11:30.. CUTOUT AND LIGHTNING ARRESTER CHANGED AND POWER RESTORED AT 10:30.. COMPLETE// VR/ ADH
10906 | Hazard | 3309302 | VICCO | JEFF | 2009-12-08 19:46 | 2009-12-08 22:27 | 4 | 161 | 58170-1 | 644 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | PARTIAL POWER // CUST CANNOT RUN LARGE APPLIANCES OR HEAT //25 KVA CSP XFMR BAD 7200 120/240V REQUIRES TWO MEN WITH MATERIAL BUCKET ALSO CUTOUT AND T - BRACKET RELEASED BY CREW 077S04 CHANGED TRANSFORMER AND CHECKED VOLTAGE JKC//COD 4 IDC XXXX
10907 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2010-08-11 16:26 | 2010-08-11 19:07 | 4 | 161 | 52669-1 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK VER/KEP L3/KEP IDC XXXX
10908 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2011-05-17 14:45 | 2011-05-17 17:26 | 4 | 161 | 4105701 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE - POLE DAMAGED. DUTY SUPERVISOR NOTIFIED AND CREW IS ENROUTE. LIFTED HOTLINE CLAMP ON 38830978C10115 TO ISOLATE AND XFMR 978-16 IS OFFLINE UNTIL REPAIRS ARE COMPLETE. RELEASED BY CREW 076S02// CREW ON SITE STARTING REPAIRS TCM//ISO//COD 4// VER/DBM
10909 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2011-02-13 23:16 | 2011-02-14 10:00 | 1 | 644 | 56620-1 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED. 25 KVA TRANS. ON POLE 241-161 IS BAD. I CALLED STEVIE RAY AND HE SAID HE WOULD SEND CREW FIRST THING IN THE MORNING. TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. TRANSFORMER IS BAD. CUSTOMER SAID WE COULD WAIT UNTIL CREWS STARTED MONDAY MORNING AND CHANGE TRANSFORMER. RELEASED BY CREW 074S01 REPLACED TRANSFORMER AND CLOSED IN AT 10:00//VER/CRB IDC ONLY 1 SERVICE ON TRANSFORMER OTHER 2 SERVICES HAD BEEN REMOVED XXXX
10910 | South Williamson | 3411401 | DEWEY | INEZ | 2015-07-02 16:18 | 2015-07-02 21:40 | 2 | 322 | 4711161 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | BOTTOM SIDE RISER BURNT INTOON POLE 769C17 NTA HAVE RIGHT OF WAY CREW AND LINE CREW ON THEWAY GOT POWER RESTORED AT 21:40// VER/ ADH
10911 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2011-04-23 21:34 | 2011-04-24 00:15 | 4 | 161 | 63261-1 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | THIS ORDER IS COMPLTED--REPLACED BAD HOT TAP--RECLOSERS NOT OUT ONLY 1 TRANSFORMER ON POLE 38830045B22694 WAS OUT COD-4 VER/KEP IDC XXXX
10912 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2015-06-29 20:19 | 2015-06-29 23:00 | 4 | 161 | 4693971 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 141-53 20T LINE FUSE BAD 19.9 CTOT DOOR/38830141C00053 ISO DEVICE/COD 4// VER/ ADH
10913 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2012-10-14 12:24 | 2012-10-14 15:05 | 4 | 161 | 4138691 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, NEED A LINEMAN, BIG BUCKET, AND FLAGGERS // RICE, RONNIE C -- AWP BLEVINS, HOWARD & COLLETT, MARSHALL //// COD-4 ISO TF 37830246D00037 VER/HFP L3/HFP IDC XXXX
10914 | Pikeville | 3413402 | GARRETT | LACKEY | 2021-07-03 06:46 | 2021-07-03 17:30 | 1 | 644 | 4852641 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10kva xfmr/ 7200..need cutout and arrester.. truck access.. one ln paved road, little to no traffic.can set up in road to change. Released by crew 076S01; CREW ON-SITE, ON AT 17:30
10915 | Hazard | 3310502 | HADDIX | CANOE | 2010-01-24 15:58 | 2010-01-24 21:20 | 2 | 322 | 58843-1 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT NEED BIG BUCKET ONE MAN & CUTOUT//COD 2 IDC XXXX
10916 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-02-18 12:48 | 2009-02-18 14:20 | 7 | 92 | 64233-1 | 644 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | 3003701//TIE WIRE ON POLE 185-251 BROKE PRIMARY CAME OFF PIN . TRUCKS TO POLE OK.TIE WIRE ON POLE 185-251 BROKE PRIMARY CAME OFF PIN . TRUCKS TO POLE OK. RELEASED BY CREW 078S01//COD 7// VER/DBM IDC XXXX
10917 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2018-08-31 10:43 | 2018-08-31 13:24 | 4 | 161 | 4022651 | 644 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | made repairs, comp
10918 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2021-03-14 21:07 | 2021-03-15 12:18 | 6 | 211 | 4335451 | 643 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | sec neut broke, crew & tree crew reqd/bucket ok./ power temp installed going to bring tree crew back in morning LRM crew on site opened xfmr @ 10:30 in @ 12:18 please close ticket LRM////opened TR at 1030 and closed at 1218 to safely trim trees out
10919 | Hazard | 3310502 | HADDIX | CANOE | 2011-12-16 19:54 | 2011-12-17 01:15 | 2 | 321 | 4184141 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 15KVA 19.9 TR AND MATERIAL BUCKETBAD TRANS IDC XXXX
10920 | Paintsville | 3401102 | FALCON | SALYERSVI | 2018-02-10 07:09 | 2018-02-10 12:30 | 2 | 321 | 4822421 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | will need 25 kva 120/240 7.2 kv , 1 man and material handler . replaced 15 kva xfmr with 25 kva, ALL WORK COMPLETE / GXJ
10921 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-12-13 10:37 | 2015-12-13 12:24 | 6 | 107 | 4528701 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | NONE | FUSE OUT AT PL 39830902A00028 40-T FUSE LINK WAS BROKE NOT BLOWN POWER RESTORED KWB /// COD- 6 ISO LF 39830902A00028 VER/HFP L3/HFP
10922 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2018-02-26 19:21 | 2018-02-26 22:55 | 3 | 214 | 4885361 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | No reading on meter, bad line fuse cutout on pole 496-29, restored power at 22:55../ ISO 37830496000029/ COD 3
10923 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-11-18 08:46 | 2011-11-18 12:20 | 3 | 214 | 4089631 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | UNDERGROUND SEC. WIRE HAS A FAULT IN JUNCTION BOX. I AM GOING TO OPEN TRANS. ON POLE 262-193 AND FIX PROBLEM. I WILL HAVE TO BAIL WATER FIRST. JUNCTION BOX IS FULL TO GROUND LEVEL. I RESPLICED CONNECTION AND CLOSED TRANS. AT 12:20. SEND TO ENG. DEPT. WE NEED TO EITHER MAKE OWNER OF TRAILER COURT SET SERVICE POLES AND GO OVERHEAD OR SOMEHOW GET JUNCTIONS BOXES OUT OF WATER. /// VER/CRB IDC XXXX
10924 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2010-04-18 09:54 | 2010-04-18 15:15 | 2 | 321 | 64763-1 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR# 34717439 // BAD 15KVA TRUCK OK NEED 15 KVA CUTOUT AND BRECKER AND OIL CLEAN UP POLE NUMBER 46-2305 RELEASED BY CREW 078S08//ISO//COD 2// VER/DBM IDC XXXX
10925 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2009-01-17 00:26 | 2009-01-17 04:00 | 3 | 214 | 56535-1 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3401702//BAD 15KVA TRANSFORMER / GO BACK WITH 25KVA 19.9KV //3401702// WR#281050373401702// WR#28105037 REMOVED 15 KVA INSTALLED 25 KVA VER/LDA L3/HFP
10926 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2017-11-12 18:16 | 2017-11-12 21:50 | 3 | 214 | 4551751 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer: no answer Released by crew 077S12called customer: no answer. we changed bad xfmr
10927 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2008-01-18 07:15 | 2008-01-18 12:36 | 2 | 321 | 57516-1 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001003// CALLING FOR CREW WILL NEED A 45` POLE//POLE FIRE AT 38830183B00421, 1 CUST OUT, CAN NOT OPEN LINE TO THIS POLE, MIKE MAY IS ON SITE RELEASED BY CREW 078S05 COD ON TRANS 2 CREW SAID 1 VER/KEP IDC ESTIMATED TIME OFF CHANGED FROM 0707 XXXX
10928 | Paintsville | 3409302 | KENWOOD | AUXIER | 2018-09-10 09:59 | 2018-09-10 15:20 | 2 | 321 | 4074561 | 642 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Transformer cutout door burnt up. Pole is on hill and covered in vines. ROW crew enroute to cut a path. Cleared vines, replaced xfmr cutout and restored @ 15:20. sh
10929 | Hazard | 3310501 | HADDIX | QUICKSAND | 2014-10-29 10:31 | 2014-10-29 12:39 | 5 | 128 | 4670951 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ETA 1130// 2/3 TRIPLEX BURNED DOWN IN PROCESS OF REPLACING WITH 1/0 NOT A STRUCTURE FIRE SERVICE WIRE BURNED DOWN VER/CRB
10930 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2013-12-13 12:16 | 2013-12-13 13:36 | 8 | 80 | 4159531 | 640 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION IN 1/0 LASH SECONDARY, ONLY HAD PART POWER, MADE REPAIRS RESTORED AT 13:36 VER/CRB L3/HFP
10931 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2022-02-06 14:35 | 2022-02-06 17:15 | 4 | 160 | 4450041 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad xfmr cutout , changing.back on at 17:15
10932 | Pikeville | 3407101 | TOPMOST | DEMA | 2008-04-26 11:17 | 2008-04-26 13:25 | 5 | 128 | 54294-1 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3407101// FOUND BAD ARRESTOR AND CUTOUT// CHANGING - FIELD ETR 1345 VER/KEP IDC XXXX
10933 | Cannonsburg | 2206403 | SOUTH NEAL STATION | WHITES CREEK RD | 2019-05-09 22:46 | 2019-05-10 09:26 | 1 | 640 | 4247111 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | called customer, they don't need someone to come tonight, need fixed before end of day tomorrow//they have turned off main breaker//called customer, they dont need someone to come tonight, need fixed before end of day tomorrow//they have turned off main breaker//found bad conn on hot leg at xfmer pole 213-110///resqueezed service drop///complete BR
10934 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2016-08-25 11:06 | 2016-08-25 12:10 | 10 | 64 | H4834811 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | B PHASE BROKE ON CREW -- OPENED B PHASE RECL 122 CUST TO ISOLATE PHASE THAT IS DOWN OPENED @ 1106 CLOSED @ 1210 (112 CUST INTERRUPTED WHEN # 4 CU PHASE BROKE & 10 INTERUPTED WHEN RECL OPENED) DUP IN HOIS FOR 10 DUP OF 49834811 FOR RECL OUTAGE // VER/HFP L3/HFP
10935 | Whitesburg | 3312902 | JENKINS | JENKINS | 2016-09-09 07:55 | 2016-09-09 13:15 | 2 | 320 | 4879151 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR BAD PLEASE SEND TO GEORGE WHITAKER, RELEASED BY CREW 077S12 POWER RESTORED AT13:15/ ISO 37830381D40680/ COD 2/ VER/BOW
10936 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2018-10-05 17:24 | 2018-10-05 20:04 | 4 | 160 | 4202151 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | line fuse blown on pole 1126-298 patrolling. R/W issues.bad DE insulator on pole1126-313. making repairs. Restored @ 2004 L3/HFP
10937 | Hazard | 3310501 | HADDIX | QUICKSAND | 2015-02-19 22:17 | 2015-02-19 23:37 | 8 | 80 | 4045341 | 640 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HAD LASH BURNED IN TO AT THE TRANSFORMER OPEN TRANSFORMER AT 2319 AND CLOSED AT 2337 VER/CRB L3/HFP HFPC MCCDL CNT1 ALSO MADE H4045341 A DUP DUE TO SERVICER SAYING ON VOICE RECORDER HE HAD SECONDARY (LASHED) BURNT IN TO AT THE TRANSFORMER
10938 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2011-01-30 16:05 | 2011-01-30 17:25 | 8 | 80 | H52303-1 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | OPENED RISER FEEDING 809-1065 & 809-1066 @ 16:05 TO ISOLATE BAD UG XFMR COD 19.//FUSE PUT BACK AT 1725 WITH TRAN ISOLATED//OPENED RISER FEEDING 809-1065 & 809-1066 @ 16:05 TO ISOLATE BAD UG XFMR. RESTORED ALL EXCEPT BAD XFMR 809-1065 @ 17:25.OPENED RISER FEEDING 809-1065 & 809-1066 @ 16:05 TO ISOLATE BAD UG XFMR. RESTORED ALL EXCEPT BAD XFMR 809-1065 @ 17:25. CHANGED XFMR AND RESTORED REMAINING CUSTOMERS @ 19:25. SH//VER/CRB IDCC DUP TO OPEN FUSE XXXX
10939 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2014-09-05 16:00 | 2014-09-05 16:40 | 16 | 40 | 4468931 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED TO CHANGE 3 12KV CUTOUTS AND ARRESTERS @ WHITES MEAT MARKET RELEASED BY CREW 078H12/ OPENED 45-A1-0043 @ 16:00 TO SAFELY MAKE REPAIRS/ REPAIRS COMP. POWER RESTORED @ 16:40/ PLEASE CLOSE TICKET /JEH AJB
10940 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2009-10-19 05:01 | 2009-10-19 06:21 | 8 | 80 | 56300-1 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REPLACED BAD FUSE LINK IDC XXXX
10941 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2022-02-03 13:50 | 2022-02-03 19:10 | 2 | 320 | 4428671 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 19.9 25kva transfomer on pole 399-31. Rick maggard and his crew is in enroute. ETR 18:00. Hung new transformer and it was bad. New ETR of 20:30.
10942 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2009-05-16 11:18 | 2009-05-16 16:38 | 2 | 320 | 58441-1 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | ,,,MIDDLE TRANSFORMER BAD HAS BEEN OUT EARLIER TODAY BEEN OUT 3 TIMES TRIED IT AGAIN FUSE BURNT OUT 25KVA 19.9 TRANSFORMER ADDRESS WERE ITS TRUCK ACCESSIBLE IS 365 BRICK HOME RELEASED BY CREW 078S02// NO TRUCK/ TRACK BUCKET/ BACK ON @ 16:38 WILL NEED TO GET TRACK BUCKET OUT AND LOAD//VER/CRB IDC XXXX
10943 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2018-02-08 18:12 | 2018-02-08 20:20 | 5 | 128 | 4818841 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broke fuse on pole 37830343D00224. restored power at 20:20/ ISO 37830343D00224/ COD 5
10944 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2018-03-21 21:13 | 2018-03-21 22:33 | 8 | 80 | 4040401 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | no outage till opened fuse at 2113/squeeze on arcing at pole 376/ Repairs made, fuse closed back in at 22:33, all power restored/ ISO 38830068D00138/ COD 8
10945 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-12-15 18:15 | 2015-12-15 18:47 | 20 | 32 | H4535811 | 640 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | COD 2 ON ORIGINAL OUTAGE//HAD TO OPEN L/F ON POLE 39831098B33048 TO SAFELEY CHANGE CUTOUT ON FAUT POLE 39831098B33143// HAVE BAD CUTOUT CHG. ON POLE 1098-3143, OPENN L/F AT 1815, CLOSED BACK IN AT 1847, POWER RESTORED TO ALL CUST// VER/ ADH AJB
10946 | Hazard | 3302704 | HAZARD | KENMONT | 2008-11-25 11:34 | 2008-11-25 12:45 | 9 | 71 | 52177-1 | 639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3302704//XFMR FUSE ROTTED IN TWO VER/TOM IDC XXXX
10947 | Whitesburg | 3301701 | DAISY | LEATHERWOOD | 2009-02-23 08:32 | 2009-02-23 12:05 | 3 | 213 | 50496-1 | 639 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON SECONDARY SIDE GOING TO REPLACE TRANSFORMER MANUAL JOB // VER/TOM L3/TOM IDC XXXX
10948 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2020-07-06 14:27 | 2020-07-06 18:00 | 3 | 213 | 4117851 | 639 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmer. send to bob reynolds. thanks. tre Released by crew 078S04
10949 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2012-12-21 07:31 | 2012-12-21 18:09 | 1 | 638 | 4497691 | 638 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | XFMR RISER BURNT IN CLEAR/SERVICER TO MAKE REPAIRS/FETR 1830/VEM/ONE CUST/REPAIRS MADE AND FULL POWER RESTORED 1809/PLEASE CLOSE TICKET/THANKS/VEM ////VER/CRB L/3 CRB
10950 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2008-06-09 15:18 | 2008-06-09 20:37 | 2 | 319 | 60612-1 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 70-1577 BAD 25KVA NEEDS TRANS. BAG LID BLEW OFF 3- CUSTSPOLE 70-1577 BAD 25KVA NEEDS TRANS. LID BLOW OFF RELEASED BY CREW 078S08//3008002//XFMR CHANGED AND POWER RESTORED 2037/PLEASE CLOSE TICKET/THANKS/VEM // COD-2 // VER/LDA IDC XXXX
10951 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2013-07-04 16:32 | 2013-07-04 17:30 | 11 | 58 | 4463841 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT UP ON XFMR FUSE. CHANGED CUTOUT AND RESTORED @ 17:30. SH VER/CRB L/3 CRB
10952 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-05-25 14:32 | 2009-05-25 19:51 | 2 | 319 | 63981-1 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEED CREW RELEASED BY CREW 078S07/BROKEN CUTOUT ON HILLSIDE//COD 2// VER/DBM IDC XXXX
10953 | Hazard | 3420001 | SOFT SHELL | VEST | 2022-08-30 10:24 | 2022-08-30 15:43 | 2 | 319 | 4814641 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 15KVA 19/9 transfromer manual and needs ROW email sent crew will be working at later date
10954 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2013-02-01 11:11 | 2013-02-01 16:30 | 2 | 319 | 4781601 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON XFMR POLE WILL HAVE TO OPEN XFMR BANK TO REPAIR. REPAIRS MADE ON AT 16:30 ///VER/CRB L/3 CRB IDC XXXX
10955 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2017-03-14 14:20 | 2017-03-14 14:42 | 29 | 22 | 4555631 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION HEATING UP ON XFMR RISER. OPENING XFMR TO REPLACE. OPENED XFMR 809-518 @ 14:20, REWORKED CONNECTIONS AND CLOSED @ 14:42. SH/ ISO 38830809C30518/ COD 29/ VER/BOW AJB
10956 | Hazard | 3311101 | STINNETT | REDBIRD | 2018-01-05 15:51 | 2018-01-05 21:10 | 2 | 319 | 4710271 | 638 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | called customer no reading on meter bad xfmr 25 kva 19.9 need cutout t bracket
10957 | Cannonsburg | 3002103 | 10TH STREET | 12TH STREET | 2020-01-16 17:25 | 2020-01-16 18:14 | 13 | 49 | 4313941 | 637 | PARTIAL POWER | EQUIPMENT FAILURE | JUMPER/RISER | riser burnt up on top of cutout. replaced hot tap.. pls close. tre L3/HFP
10958 | South Williamson | 3411401 | DEWEY | INEZ | 2015-01-04 09:54 | 2015-01-04 11:25 | 7 | 91 | 4902771 | 637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE ON POLE 745-171//CHANGING NOW//REPAIRS MADE//RESTORED AT 11:25//COMPLETE//EM//COD7// VER/ ADH L3/HFP XXX
10959 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2012-08-24 16:36 | 2012-08-24 17:25 | 13 | 49 | 4969541 | 637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD XFMER CUTOUT @ POLE 38830785D20452///GOING TO CHANGE////MADE REPAIRS///COMPLETE BR//COD 13// VER/DBM IDC XXXX
10960 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2015-11-18 18:29 | 2015-11-18 20:00 | 7 | 91 | 4465441 | 637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1148-481 BAD CUT 6T TRANS FUSE POLE 1148-62 80T LINE FUSE A PHASE/ TO TECHNICIAN REPLACE CROSSARM BURNT NEED CHANGED ON 1148-481/ ISO 39831148A20062/ COD 7 CCC****/ EMAIL SENT/ VER/BOW
10961 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2017-11-14 23:13 | 2017-11-15 00:44 | 7 | 91 | 4557161 | 637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout//cod 7
10962 | South Williamson | 3200302 | BELFRY | TOLER | 2017-12-11 13:05 | 2017-12-11 14:36 | 7 | 91 | 4639501 | 637 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | conductor has come off pin insulator/ opening line fuse to repair/ ISO 38821063C00023/ COD 7.Opened at 14:00 made repairs. closed at 14:36
10963 | South Williamson | 3200201 | BARRENSHE | FREEBURN | 2011-04-12 09:46 | 2011-04-12 12:25 | 4 | 159 | 55698-1 | 636 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION ON 1 HOT LEG FROM XFMR SEC RISER TO 4/0 LASH CABLE ON POLE 1089A221....CAN REPLACE....WILL OPEN XFMR & LOG TIMES....//....OPENED XFMR @ 11:50....MADE REPAIRS....CLOSED @ 12:25....VOLTAGE GOOD NOW....JRV....04/12/11 VER/KEP
10964 | South Williamson | 3411401 | DEWEY | INEZ | 2008-03-13 14:32 | 2008-03-13 19:50 | 2 | 318 | 56921-1 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411401// 15KVA CSP TRANSF BAD//COD 2//VER/CRB IDC XXXX
10965 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-06-23 08:02 | 2008-06-23 13:20 | 2 | 318 | 52737-1 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008702// TRANSFORMER FAILED/CREW REPLACING/COD-2/ VER/KEP IDC XXXX
10966 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2022-03-26 04:50 | 2022-03-26 08:22 | 3 | 212 | 4675281 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | busted XCO on pole 1100-147// will be making repairs
10967 | Hazard | 3310501 | HADDIX | QUICKSAND | 2012-06-20 15:43 | 2012-06-20 19:15 | 3 | 212 | 4936431 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3 PHASE 2/0 SERVICE BURNT DOWN//// CUT TREE AND VINES OFF POLE, REPLACE CONNECTIONS ON 3 PHASE SERVICE AND ON SINGLE PHASE SERVICE. POWER RESTORED.//COD 3// VER/DBM IDC XXXX
10968 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-10-26 12:03 | 2008-10-26 17:21 | 2 | 318 | 59187-1 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | VER/HFP TRANS FUSE BLOWN ROTTON FUSE COD-2 IDCC CCO XXXX
10969 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-06-17 18:15 | 2011-06-17 23:33 | 2 | 318 | 4335591 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN//19.9 25 KVA BAD// TALKED TO STEVE // CREW ENROUTE RELEASED BY CREW 074H14//VER/CRB IDC XXXX
10970 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2010-05-28 09:09 | 2010-05-28 11:48 | 4 | 159 | 51973-1 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR, READING AROUND 150 VOLTS ON TXMR CALLED DUTY SUP. HE IS SENDING CREW.----REPLACED XFMR ALSO CHANGED OUT S/D VER/ARN IDCC PN28, CNT4, CCO XXXX
10971 | Pikeville | 3412901 | WEEKSBURY | DISTRIBUTION | 2015-07-17 15:19 | 2015-07-17 17:05 | 6 | 106 | 4902531 | 636 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED #2 CU RISERS WITH SAME, SENT IW70 TO TECH TO CHECK CAPACITY, ALL WORK COMPLETE / GXJ
10972 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-12-13 11:17 | 2009-12-13 12:10 | 12 | 53 | 50978-1 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | FOUND BAD LA POLE 44-7023 CHGED VER/KEP L3/KEP
10973 | Pikeville | 3401001 | ELWOOD | DORTON | 2011-09-07 20:13 | 2011-09-07 23:45 | 3 | 212 | 4846091 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN. I AM GOING TO REFUSE TRANS. --- 50 KVA TRANS. ON POLE 238-98 IS BAD. I HAVE CALLED FOR HELP. DALE IS SENDING EICK MCKINNEY WITH NEW TRANS. WE CHANGED TRANSFORMER. //VER/CRB IDC XXXX
10974 | Hazard | 3311101 | STINNETT | REDBIRD | 2010-08-12 16:33 | 2010-08-13 03:09 | 1 | 636 | 53832-1 | 636 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 19.9 120/240 RELEASED BY CREW 077S01 REPLACED TRANSFORMER AND RESTORED POWER AT 0309 JKC
10975 | South Williamson | 3202201 | LOVELY | LOVELY | 2012-07-30 23:16 | 2012-07-31 09:51 | 1 | 635 | 4868541 | 635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | NEUTRAL BROKE IN 1/0 SECONDARY COMING FROM 747-219 FEEDING TRINITY CHURCH//SERVICE DROP MELTED NEAR WEATHERHEAD// WILL NEED COUPLE MEN AND BUCKET TO REPAIR SECONDARY AND REPLACE SERVICE DROP//PLEASE HAVE CREW WORK TOMORROW//I DISCONNECTED CHURCH FOR THE NIGHT,WILL BE HAVING SERVICE HERE TOMORROW NIGHT/ RELEASED BY CREW 079S01// VER/DBM IDC XXXX
10976 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-01-01 13:43 | 2021-01-01 15:50 | 5 | 127 | 4841341 | 635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | bad dead end insulator on pole 179-200. restored power at 15:50
10977 | Whitesburg | 3312901 | JENKINS | KONA | 2011-08-15 07:50 | 2011-08-15 09:57 | 5 | 127 | 4711901 | 635 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | SECONDARY NEUTRAL BROKE INTO. I REPAIRED NEUTRAL COD-5 ISO SO 37830404D00061 VER/HFP L3/HFP IDC XXXX
10978 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2013-01-11 19:48 | 2013-01-11 21:55 | 5 | 127 | 4597231 | 635 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED DRT TO HELP/REPLACED CUTOUT//COD 5// VER/DBM IDC XXXX
10979 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2022-05-06 05:18 | 2022-05-06 10:35 | 2 | 317 | 4842261 | 634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke 7200 cutout. not by truck on pole 268 Released by crew 078S12. complete time on 10:35
10980 | Hazard | 3300601 | BLUEGRASS | WALKERTOWN | 2011-09-21 10:13 | 2011-09-21 15:30 | 2 | 317 | 4892181 | 634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | SPOKE WITH ENGINEER (MIKE LEWIS) AND HE SAYS WE NEED TO CHANGE TRANSFORMER, CAN CHANGE WITH BUCKET, NEED 15 KVA, 7.2 KV. CUTOUT, ARRESTOR AND TEE BRACKET. RELEASED BY CREW 077S04 VER/KEP IDC XXXX
10981 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-02-15 09:03 | 2018-02-15 14:20 | 2 | 317 | 4842691 | 634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | anchor has slip and guy wire is on transformer lead , going to try pulling guy up to get off transformer anchor is pulling out of ground, eed to burry new anchor and pull gy before making transformer hot , call glen and as soon as he get someone free up he will send Released by crew 077S05
10982 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-09-27 10:00 | 2015-09-27 20:34 | 1 | 634 | 4279751 | 634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WE HAVE 3PHASE POLE WITH 3 PHASE TAP BURNT INTO AT LOWER ARMS, CALLED BRUCE AND HE IS GOING TO HAVE TECH AND FORMAN LOOK AT THIS EARLY IN MORNING. DANGEROUS WORK PLACE VERY STEEP INCLINE, ONLY THING OUT IS LIBRARY/ OPENED TRANS BANK @ 10AM POWER RESTORED WITH SWITCH IN ORDER 4280801 @ 1940/ ISO 37830184B00182/ COD 2
10983 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-03-02 10:49 | 2019-03-02 16:06 | 2 | 317 | 4944981 | 634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFR MUST BE OPEN INSIDE,CANT GET IT TO CLOSE IN.JOEY REED ENROUTE W XFR////////REPLACED BAD XFR&RESTORED
10984 | Hazard | 3310501 | HADDIX | QUICKSAND | 2013-03-01 13:44 | 2013-03-01 16:34 | 9 | 170 | 4865201 | 634 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 54-65 IS ON FIRE , TOOK CLAMP OFF ON POLE 54-64 AND GOING TO MAKE REC HOT UP TO THIS POLE COD-9 ISO OCR 37830030000015 VER/HFP L3/HFP IDC XXXX
10985 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-09-19 08:26 | 2016-09-19 11:57 | 3 | 211 | 4907121 | 633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQ, A PHASE CUTOUT IS CRACKED, NEED CREW TO CHANGE IT CAN USE TRUCK, MATERAIL NEED 3 CUTOUTS, RELEASED BY CREW 078S06 A PHASE INITIALLY OUT (COD 2). OPENED B&C TO REPAIR (COD 2). CREW REQ, A PHASE CUTOUT IS CRACKED, NEED CREW TO CHANGE IT CAN USE TRUCK, MATERAIL NEED 3 CUTOUTS, RELEASED BY CREW 078S06,OPEN B & C @ 1127 REPAIRS MADE ALL CUST RESTORED @ 1157 PLEASE CLOSE TICKET THANKS.BT39831072C35052 VER/AWD
10986 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-05-31 08:00 | 2010-05-31 18:33 | 1 | 633 | 54059-1 | 633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 20-4577//COD 1//CREW ON SITE/FETR 1857/VEM/REPAIRS MADE/POWER RESTORED1833/PLEASE CLOSE TICKET/THANKS/VEM IDC XXXX
10987 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2011-05-12 07:57 | 2011-05-12 18:30 | 1 | 633 | 4070391 | 633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | LIMIT FUSE BAD 34.5
10988 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2010-05-01 19:01 | 2010-05-01 22:32 | 3 | 211 | 53445-1 | 633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POISON OAK ENGULFED TRANSFORMER; CLEARED IVY FROM TRANSFORMER; RE-FUSED CUTOUT; NO PWR,SUSPECT LINE INHIBITOR FUSE BAD OR TRANSFORMER; CALLED IN CREW; 50KVA 34.5 TRANSFORMER; RELEASE TO LINE CREW RELEASED BY CREW 078S12// POLE COVERED IN VINES CHANGING OUT 50 KVA //VER/GAH IDC XXXX
10989 | Whitesburg | 3312901 | JENKINS | KONA | 2014-04-13 13:25 | 2014-04-13 16:56 | 3 | 211 | 4599751 | 633 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED 1 MAN & BIG BUCKET & 25KVA 7.2 KV TR BAD 25 KVA XFMR 7200,BAD 25 KVA XFMR 7200,REPLACED XFMR & RESTORED POWER AT 16:56 COD-3 ISO TF 37830404D00106 VER/HFP L3/HFP
10990 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-06-01 11:37 | 2022-06-01 14:15 | 4 | 158 | 4992791 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva xfmr p-882-76 , dripping oil, need line crew material handler. truck accessible.
10991 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2022-04-26 09:13 | 2022-04-26 11:51 | 4 | 158 | 4801121 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Line fuse open at 165-16,Have a broke Trans cutout on pole 165-172,Will be making Repairs..Restored line fuse at 11:51..
10992 | Cannonsburg | 3010602 | RUSSELL | BEARRUN | 2015-04-10 08:58 | 2015-04-10 19:30 | 1 | 632 | 4302481 | 632 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | NEUTRAL BURNT INTO AT TWO BOLT CLAMP,OPENED CUT-OUTS ON POLE 39831148C00567 TO ISOLATE TROUBLE .WILL NEED SERVICER TO REPAIR TWO BOLT CLAMP. MAY NEED METER ELECTRIAN TO CHECK CTS ON POLE TO SEE IF THEY WERE DAMAGED . RELEASED BY CREW 078H18 POWER RESTORED AT THIS LOCATION AT 19:30// VER/ ADH
10993 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2009-11-20 23:14 | 2009-11-21 09:46 | 1 | 632 | 60502-1 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308402 WORK REQ # 32789008 //BAD TRANSFORMER ,, CUSTOMER SAID IT WAS OK TO CHANGE FIRST THING SAT. MORNING,, WILL NEED TWO MEN ,, BIG BUCKET AND 15 K.V.A. 19.9BG RELEASED BY CREW 077H12 @ 0123 , PAUL HICKMAN , D/S NOTIFIED & WILL ARRANGE FOR CREW TO REPLACE IN THE A.M. X-FMR AND CUT OUT REPLACED AND POWER RESTORED AT 9:46. V. HURT IDC XXXX
10994 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2015-10-09 23:01 | 2015-10-10 09:33 | 1 | 632 | 4335621 | 632 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND NEED TEMP SAT AS SOON AS A CREW BE FOUND TALKED TO CUST OK FOR TONIGHT RELEASED BY CREW 078S08---INSTALLED PWR TEMP---ISOL BAD LEG IN PED---VOLT CK GOOD---SEND NOTE TO B REYNOLDS/L RAYBURN TO HAVE UG CREW CHANGE OUT UG CABLE---TBL TKT COMP VER/ARN
10995 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2016-05-14 23:20 | 2016-05-15 09:52 | 1 | 632 | 4218871 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | KY DDC SPOKE WITH CUSTOMER - OK TO CHECK IN AM// PHASE CONDUCTOR IN SERVICE DROP HAD HEATED UP APROX 3 FT. FROM POLE & BURNED NETURAL CONDUCTOR INTO . REPLACED SERVICE DROP. VER/CRB
10996 | Hazard | 3309302 | VICCO | JEFF | 2014-03-14 11:17 | 2014-03-14 13:55 | 4 | 158 | 4491991 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 75 KVA TRANSF ==== NEED LINE CREW AND 75 KVA TRANSF 7200 === CAN GET TRUCK TO POLE === 50 KVA MAY WORK BACK === RELEASED BY CREW 077S03//COD 4// VER/DBM
10997 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-11-20 23:22 | 2017-11-21 02:00 | 4 | 158 | 4591021 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | service neutral burnt into..repaired at 2:00
10998 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2010-02-19 18:07 | 2010-02-19 20:45 | 4 | 158 | 59228-1 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | CURRENT LIMITING FUSE ON 19.9 TRANSFORMER.......DAH COD-4 VER/HFP L3/HFP IDC XXXX
10999 | Hazard | 3302704 | HAZARD | KENMONT | 2009-08-06 22:16 | 2009-08-06 23:35 | 8 | 79 | 56845-1 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-8 ENTERED MD...HFP L3/HFP IDC XXXX
11000 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-11-09 23:02 | 2010-11-10 01:40 | 4 | 158 | 54458-1 | 632 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ONLY ONE CUST AFFECTED.....BAD SPLICE (INSULINK) ON SERVICE DROP, NEAR XFMR POLE ....REPLACED BAD CONNECTIONS.....CUSTS SERVICE OK NOW....JRV....11/10/10 //VER/GAH IDC XXXX
11001 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2014-07-24 14:20 | 2014-07-24 19:36 | 2 | 316 | 4282941 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TREE FELL TORE SECONDARY DOWN ==== TRANSF OUT === CALLED FOR TREE CREW === PUT SECONDARY UP AND HAD BAD 50 KVA TRANSF === REPLACED TRANSF == POWER OK VER/CRB
11002 | South Williamson | 3202201 | LOVELY | LOVELY | 2022-01-24 09:56 | 2022-01-24 11:15 | 8 | 79 | 4399951 | 632 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout broke on pole 747-38//repairs made//restored at 11:05//complete//em
11003 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2011-04-05 09:50 | 2011-04-05 20:21 | 1 | 631 | 65609-1 | 631 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | OPEN SECONDARY NEUTRAL AT XRFM POLE NEED TO CLIMB POLE - NEEDS SPLICED INFORMED CUSTOMER TO KEEP MAIN BREAKER OFF- HE SAID IT WAS OFF RELEASED BY CREW 074M02///////MADE NECESSARY REPAIRS,NOBODY HOME,PRESUMED OK AFTERWARDS IDC XXXX
11004 | South Williamson | 3411401 | DEWEY | INEZ | 2018-12-02 00:04 | 2018-12-02 09:40 | 2 | 576 | 4498981 | 631 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | Dispatched in accordance with KYPCo Late Night Callout Guidelines//middle xfmr fuse blown on 744-400//stand off insulator broke on ride around riser///going to open tapon 744-398 to climb pole and repair//repairs made/opened tap at 8:45/closed at 9:40//complete//em L3/HFP
11005 | Hazard | 3308002 | JACKSON | PANBOWL | 2011-01-09 07:50 | 2011-01-09 09:56 | 5 | 126 | 60055-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | GOT LEAD BURNED OFF ON TRANSFORMER //VER/GAH IDC XXXX
11006 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2019-08-02 09:30 | 2019-08-02 10:05 | 18 | 35 | 4830731 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | GUY/ANCHOR | OPENED PRIMARY 37830092000049//COD 18//TO REPAIR GUY WIRE ON POLE 37830116000035// @i will be opening hotline clamp loop out from pole 92-49 due to guy wire hanging over primary at pole 92-54. opened at 09:30 closed hot line clamp loop back in at 10:05. send copy to eng pikeville guy wir and anchor needs to be replaced at pole 37830116000036. neutrals been stolen from pole 116-36 to pole 116-38 and 116-39//AED MADE L3/HFP
11007 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2013-09-06 10:15 | 2013-09-06 11:25 | 9 | 70 | 4824411 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | POLE 46-2561 CROSS ARM BROKE SEND TO BRENT T. RELEASED BY CREW 078S08, CREW ON SITE, OPENED FUSES TAGGED AND GROUNDED AT 10:15, REPAIRS MADE, GROUNDS AND TAGS REMOVED, CLOSED FUSES AT 11:25//COD 9// VER/DBM L3/HFP IDC XXXX
11008 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2015-05-12 09:50 | 2015-05-12 11:00 | 9 | 70 | 4419101 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN ON POLE 73-573 AND CAUGHT POLE ON FIRE. I OPENED LINE FUSE ON POLE 73-572 AT 09:50 TO ISOLATE FAULT. RICK RAY AND CREW ARE ON SITE TO HELP FIX PROBLEM./ MD DONE 20T LINE FUSE/ ISO 37820073B00572/ COD 9 L3/DKGXXX VERIFIED WITH VOICE RECORDER
11009 | Pikeville | 3408101 | SALISBURY | PRINTER | 2009-10-22 11:30 | 2009-10-22 13:15 | 6 | 105 | 64505-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FAILED CUTOUT//REPLACING//LIFTED TAP AT POLE 38831123A00009//ISO//COD 6// OPEN AT 11:30 ... ALL CUSTOMERS RESTORED AT 13:15 ... ALL WORK COMPLETE / GXJ// VER/DBM IDC XXXX
11010 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2013-10-24 09:35 | 2013-10-24 10:45 | 9 | 70 | 4959241 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | RELATED TO 4958701//CREWS OPENED FUSE IN ORDER TO MAKE REPAIRS TO DOWNED LINE//COD 9// VER/DBM L3/HFP IDC XXXX
11011 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-12-24 13:39 | 2016-12-24 15:24 | 6 | 105 | 4234841 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 15:24..//COD 6
11012 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2017-10-29 12:14 | 2017-10-29 12:59 | 14 | 45 | 4508331 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | POLE FIRE AT 38830206B02352. OPENED FUSE ON 38830206D02060 AT 1214. CLOSED AT POLE FIRE@ 206-2352,,MADE REPAIRS,,LINE FUSE 206-2060 OPENED @ 12:14 CLOSED @ 12:59 COMPLETE VER/AWD L3/HFP XXXHFP
11013 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2016-05-31 15:55 | 2016-05-31 17:25 | 7 | 90 | 4276581 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | REPLACED CONNECTIONS ON 1/0 SECONDARY VER/CRB
11014 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2016-08-13 00:49 | 2016-08-13 11:19 | 1 | 630 | 4769411 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN ON 38820795A00109 DUE TO BAD CUTOUT ON POLE 38820795A00110. ISO 38820795A00109 COD 2CUT OUT BAD ON POLE #38820795A00110 LINE FUSE OUT ON POLE#38820795A00109. HAVE HELP ON THE WAY. VER/AWD
11015 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2017-05-17 15:05 | 2017-05-17 16:50 | 6 | 105 | 4809161 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE CUTOUT ON 834-380 FAILED.//MADE MD TO SHOW TRANS ON LOAD SIDE OF L/F//CUSTS WERE RESTORED WITH L/FCOD 6 VER/CRB
11016 | Pikeville | 3403001 | PIKEVILLE | CITY | 2015-03-31 18:10 | 2015-03-31 19:20 | 9 | 70 | 4252301 | 630 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | OLD SQUEEZE HAD FAILED // REPAIRS MADE // OPENED @ 18:55 // CLOSED @ 19:20 VER/HFP L3/HFP
11017 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-03-30 14:10 | 2014-03-30 15:55 | 6 | 105 | 4543151 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED BAD CONNECTION VER/CRB
11018 | Cannonsburg | 3008002 | 47TH STREET | 39TH STREET | 2022-02-25 04:19 | 2022-02-25 05:22 | 10 | 63 | 4542761 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Cutout door burned up, restored @ 05:22
11019 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2008-06-29 04:12 | 2008-06-29 06:18 | 5 | 126 | 59010-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | PRI, LOOP OPEN G. SHOUSE VER/HFP IDCC CNT2, PN1108 XXXX
11020 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2009-10-10 19:00 | 2009-10-10 21:06 | 5 | 126 | H54525-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | WR/ 32146582 POLE 1123-1101 65T UNDERGROUND OUT RELEASED BY CREW 078S08/BAD U/G CABLE/CREW IS WORKING TOWARDS A PARTIAL RESTORATION. 1327 RESTORED 1147 & 1148// 1447 RESTORED 1105// 1900 INTERRUPTED 1105// 2106 RESTORED 1105 & 1103// 2121 RESTORED 1104//VEM RELEASED BY CREW 078H14 //VER/GAH IDC XXXX
11021 | Hazard | 3307301 | BULAN | ARY-HEINE | 2015-06-08 03:51 | 2015-06-08 13:45 | 4 | 594 | 4522191 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | TOP OF POLE #37830200D00146 BURNT AT TOP WERE NEUTRAL IS DEADENDED MIGHT BE ABLE TO LOWER THIS IS OPEN WIRE SEC. MAYBE REPLACE WITH 1/0 TRIPLEX , PROBABLY ABOUT 225 FEET THIS IS MANUEL POLE WITH 1 CUST STIL OUT. OPEN WIRE IS CUT IN CLEAR AT XFMR POLE #200-134 RELEASED BY CREW 077H14//@ 0403 ALL CUST RESTORED EXCEPT 1//TOP OF POLE #200-146 BURNT AT TOP WERE NEUTRAL IS DEADENDED MIGHT BE ABL IS MANUEL P VER/CRB
11022 | South Williamson | 3411401 | DEWEY | INEZ | 2021-08-19 17:04 | 2021-08-19 19:10 | 5 | 126 | 4122581 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | fuse door burnt out on pole 648-52//found nothing on tap//restored at 19:10//complete//em
11023 | Whitesburg | 3312901 | JENKINS | KONA | 2019-03-09 23:00 | 2019-03-10 09:30 | 1 | 630 | 4965671 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | one lead out of bushing, oil around closing switch and looks like a burned spot on the side of the can. we need two linemen and material handler to change xfmr in the morning. 25 kva and cutout and arrestor Released by crew 077S12. power restored @ 0930 ¦¦ HELD OVER NIGHT L3/HFP
11024 | Hazard | 3302703 | HAZARD | HAZARD | 2019-12-10 15:35 | 2019-12-10 16:10 | 18 | 35 | 4142361 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | transformer opened at 15:35 and closed at 16:10 opened to repait secondary connections
11025 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2009-10-08 17:50 | 2009-10-08 18:32 | 15 | 42 | 65629-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 70-3582 S/C CUTOUT FELL APART VER/KEP L3/KEP IDC XXXX
11026 | Hazard | 3307303 | BULAN | LOTTSCREEK | 2022-01-27 16:00 | 2022-01-27 17:30 | 7 | 90 | 4410551 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | cut arrester in clear on pole 37830249C00095
11027 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2021-03-13 15:15 | 2021-03-13 16:25 | 9 | 70 | 4333901 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Per Pat Thovson we have primary and neutral very low at pole 38830237000048/ needs looked at--38830237000049.streightened ? but more so lines need resaged toward 38830237000046--crew req-ds031321.. Released by crew 078S01 crew on site FETR 17:00 LRM opened solid blade on 237-63 @15:15 restored @1625
11028 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2009-09-18 10:15 | 2009-09-18 11:45 | 7 | 90 | 50890-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP WR # 31786607 // OPENED TR @ _10;15 CLOSED @ 10;45 COD-7 ISO TF 39831123B00580 L3/HFP IDC XXXX
11029 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2014-01-04 22:30 | 2014-01-05 09:00 | 1 | 630 | 4229531 | 630 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONTACTED CUSTOMER LAST NIGHT AND THEY ARE OK TO WAIT UNTIL TOMORROW AFTER DAYLIGHT TO CHECK PROBLEM ** CUSTOMER REPORTS THEY HAVE HEAT . VER/KEP IDC XXXX
11030 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-01-11 13:04 | 2011-01-11 13:18 | 45 | 14 | 60646-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | CREW GOING TO OPEN RECLOSER TO SAFELY CHANGE INSULATOR ON BPOLE 250-12...SHOULD BE OFF ONLY 30 MINUTES FROM TIME POWER IS INTERRUPTED.//COD 45// VER/DBM IDC XXXX
11031 | Hazard | 3302701 | HAZARD | BLACKGOLD | 2009-12-26 08:24 | 2009-12-26 11:54 | 3 | 210 | 63597-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND RESTORED POWER
11032 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2022-02-14 16:50 | 2022-02-14 18:00 | 9 | 70 | 4482191 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | connection bad only reading 60 volts got repaired power restored 18:00
11033 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2008-08-23 21:15 | 2008-08-24 02:30 | 2 | 315 | 54451-1 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3002001/// HAVE A BAD 25 KVA TRANSFORMER, THIS IS THE LAST HOUSE ON THE RIGHT ON WILLARD LANE, BESIDE OF THE FIRST CHURCH ON STATE ROUTE 784, CAN USE TRUCKS BACK IN BESIDE OF GARAGE, DO NOT GO IN FIELD SEPTIC TANK AND LEECH BED ARE IN FIELD RELEASED BY CREW 078S06//REPLACED BAD 25KVA BACKLOT OLD CONSTRUCTION P R TOLLIVER COMPLETE AT 02:30 IDCC CNT1 XXXX
11034 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2017-09-18 18:10 | 2017-09-18 21:40 | 3 | 210 | 4372111 | 630 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | FAILED TRANS ON 1078-138 15KVA 7200 TRK APPROACH CREW REQUIRED 1 MAN AND MATERIAL HANDLER REPLACED TRANS RESTORED POWER AT 21:40 VER/ARN L3/HFP XXXHFP
11035 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-01-04 11:21 | 2019-01-04 16:35 | 2 | 314 | 4627941 | 628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | putting temp overhead in contacted contractor to dig new urg will be next week tech writing job//COD 2
11036 | Whitesburg | 3308601 | COLLIER | UPPERROCK | 2016-12-28 23:32 | 2016-12-29 10:00 | 1 | 628 | 4247161 | 628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUSTOMER: NO ANSWER (2340). WILL HOLD FOR NORMAL WORK HOURS PER CALLOUT GUIDELINES. RELEASED BY CREW 077S11CALLED CUSTOMER: NO ANSWER (2340). WILL HOLD FOR NORMAL WORK HOURS PER CALLOUT GUIDELINES. BAD CUTOUT, REPLACED CUTOUT RESTORED POWER AT 10:00.// VER/ ADH
11037 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2021-04-22 06:13 | 2021-04-22 11:27 | 2 | 314 | 4469911 | 628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | We have a bad Trans on pole 145-44,One of the Bushings is burned out,Went ahead and opened it up,Spoke with Paul Layne and he is going to be coming to help with Repairs..Trans is 19-9 25 KVA.. Released by crew 074S01
11038 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2009-05-18 21:43 | 2009-05-19 00:20 | 4 | 157 | 64447-1 | 628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT--CALLED BUD TO HELP VER/ARN IDC XXXX
11039 | Hazard | 3303902 | LESLIE | WOOTON | 2012-08-14 03:08 | 2012-08-14 13:36 | 1 | 628 | 4934401 | 628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL DISPATCH AT REG WK TIME. NEED TO REPLACED XFMR CUTOUT AND ARRESTOR WILL NEED 10KVA 7200 120/240 PLUS R/W CREW RELEASED BY CREW 077S01 REPLACED XFMR AND RESTORED POWER AT 1336 (OPENED LINE AT 1145 AND RESTORED AT 1336 JKC IDC XXXX
11040 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2012-03-05 07:37 | 2012-03-05 18:05 | 1 | 628 | 4548221 | 628 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | BAD CONNECTION AT THE TRANSFORMER VER/HFP L3/HFP IDC XXXX
11041 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2016-12-23 02:20 | 2016-12-23 05:49 | 3 | 209 | 4230041 | 627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | KY DDC CONTACTED CUSTOMER AND THEY CONFIRMED NO POWER// 1148-334 BAD 7200,25 KVA. 120/240 TRK OK RELEASED BY CREW 078S07/CREW ON SITE/FETR0600/VEM/REPAIRS MAD AND ALL CUST RESTORED 0549/PLEASE CLOSE TICKET/THANKS/VEM VER/TOM L3/TOM
11042 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2022-03-24 07:20 | 2022-03-24 10:49 | 3 | 209 | 4667151 | 627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 2733 jason rd broken19.9 cutout 140b2023 crew required no truck Released by crew 078S09 crew on site FETR 11:30 LRM all pwr restored 10:49 please close ticket LRM
11043 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2011-06-05 15:19 | 2011-06-05 18:48 | 3 | 209 | 4237121 | 627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. IS BAD. WE NEED TO CHANGE 15 KVA TO A 25 KVA ON POLE 237-49. TIM IS SENDING HELP. WE CHANGED TRANS.//VER/CRB IDC XXXX
11044 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-07-07 19:45 | 2021-07-08 06:12 | 1 | 627 | 4869281 | 627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broken cutout on 117-165. Crew required, no trucks Released by crew 078S02
11045 | Pikeville | 3411801 | JOHNSCREEK | META | 2008-11-19 11:46 | 2008-11-19 15:15 | 3 | 209 | 66626-1 | 627 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR TO RE-FUSEXFR IS BAD,CREW ENROUTE W REPLACEMENT,NOTE FETR CHANGE COD-3 VER/KEP IDC XXXX
11046 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2017-05-17 17:32 | 2017-05-17 22:45 | 2 | 313 | 4809941 | 626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OUT ON 148--44OPENED CSP TRANS ON 148-81 TRIED FUSE CAME BACK OUT REPLACED ARRESTOR ON 148-197 CLOSED FUSE ON 148-44 AT 22:30CLOSED TRANS ON 148-81 AT 22:45
11047 | Hazard | 3303902 | LESLIE | WOOTON | 2014-03-29 10:47 | 2014-03-29 16:00 | 2 | 313 | 4533511 | 626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR CUTOUT BROKEN, NEED BIG BUCKET AND A-LINEMAN// GOT CUTOUT CHANGED OUT AND POWER ON. VER/CRB
11048 | Hazard | 3302704 | HAZARD | KENMONT | 2014-10-20 23:59 | 2014-10-21 10:25 | 1 | 626 | 4647891 | 626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANSFORMER FUSE IS NOT BLOWN, NO SEC. VOLTAGE, MANUAL TRANSFORMER, NEED 4 MAN CREW. RELEASED BY CREW 077S04 POWER RESTORED AT 1025 VER/CRB L3/HFP
11049 | Hazard | 3307301 | BULAN | ARY-HEINE | 2009-01-17 16:53 | 2009-01-17 22:06 | 2 | 313 | 57744-1 | 626 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | BAYONETT FUSE BLOW IN PADMOUNT//PADOUNT XFMR BAD 25 KVA OUTAGE TO REPLACE TR CONTAINED IN ORDER 57877-1 / COD-2 / VER/LDA L3/KEP
11050 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-06-05 14:04 | 2008-06-05 16:09 | 5 | 125 | 58347-1 | 625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3411802//LINEFUSE 1131-4 IS OUT AGAIN,WILL PATROL.WAS OUT EARLIER IN DAY ABT 2.5 HRS AGOREPLACED A POSSIBLE BAD CUTOUT//VER/CRB
11051 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2010-09-27 21:40 | 2010-09-27 22:05 | 25 | 25 | 54417-1 | 625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT IS BREAKING DOWN. IM CALLING FOR HELP. WE WILL HAVE TO OPEN LINE FUSE WHEN THEY GET HERE. 168-156. WE OPENED LINE CUTOUT ON POLE 168-6 AT 21:40 TO CHANGE CUTOUT AND CLOSED IT IN AT 22:05.//VER/CRB IDC XXXX
11052 | Hazard | 3308001 | JACKSON | S.JACKSON | 2008-10-08 08:00 | 2008-10-08 10:05 | 5 | 125 | 54078-1 | 625 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP STS WR # 26674858 // STS GOT BROKE CUTOUT ON POLE 38831107000029 , THIS TRANSFORMER DONT SERVICE ANYONE, GOING TO WALK UP THE HILL AND TAKE OFF LINESTS WR # 26674858 // STS GOT BROKE CUTOUT ON POLE 1107-29, THIS TRANSFORMER DONT SERVICE ANYONE, GOING TO WALK UP THE HILL AND TAKE OFF LINE IDC XXXX
11053 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-11-13 06:19 | 2021-11-13 08:55 | 4 | 156 | 4087321 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | servicer ETA approx 0700 // Xfmr cutout failed and burnt cross arm in two. One cust affected. Replaced cutout, cross arm and two arresters and restored @ 8:55. sh 4 customers
11054 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2018-04-14 20:53 | 2018-04-15 02:05 | 2 | 312 | 4225671 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Released by crew 074S11. 1.6t fuse out pole 140-b-272 due to bad cutout. replaced cutout fused up everything ok
11055 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2019-02-22 20:54 | 2019-02-22 23:30 | 4 | 156 | 4846221 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cut out,close to primary,need line crew Released by crew 077S04 power restored at 23:30
11056 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2009-03-25 09:33 | 2009-03-25 14:45 | 2 | 312 | 61327-1 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPEN LINE FUSE ON POLE 222-32 3 MAN CREW NEEDED 8FT CROSSARM /3 CUTOUTS WILL NEED MOPADS AT LEAST 6 CUT OUT AND ARM HAVE BURNT INTO RELEASED BY CREW 078S11//COD 2// J. HEMLEPP & CREW INROUTE / COMPLETED 03-25-09 J. HEMLEPP & CREW 8FT ARM, 3 CUTOUTS// VER/DBM IDCC TOF1100 XXXX
11057 | Cannonsburg | 3116101 | GRAYSON | LANSDOWNE | 2010-04-06 10:28 | 2010-04-06 11:20 | 12 | 52 | 59482-1 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | STINGER BROKE OFF OF CUTOUT, REPLACED STINGER AND CUTOUT/VER/CRB IDC XXXX
11058 | Hazard | 3308401 | BECKHAM | HINDMAN | 2022-08-18 16:10 | 2022-08-18 17:54 | 6 | 104 | 4761111 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | opened line fuse to make safe on pole 229-58 at 16:10 to make safe Released by crew 077H05 restored power at 17:54
11059 | Hazard | 3308502 | BONNYMAN | HAZARD | 2010-03-06 14:05 | 2010-03-06 17:33 | 3 | 208 | 63374-1 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUTS HAD TO WAIT ON HELP VER/KEP L3/KEP IDC XXXX
11060 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2011-01-02 14:38 | 2011-01-02 16:22 | 6 | 104 | 57974-1 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BURNT CUTOUT DOOR/NO CREW REQUIRED VER/TOM IDCC FEC49 XXXX
11061 | Cannonsburg | 3001402 | LOUISA | HIGHBOTTOM | 2014-04-25 13:55 | 2014-04-25 16:31 | 4 | 156 | 4634191 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLEW ON 454-6524 BAD XFORM CUTOUT ON 454-6537,REPLACED CUTOUT,REFUSE LINE CUTOUT MADE HOT POWER RESTORED.SEND TECH COPY TO CHECK 454-6537 ROTTEN POLE AT TOP VER/HFP L3/HFP
11062 | Paintsville | 3401103 | FALCON | BURNINGFK | 2013-11-01 03:02 | 2013-11-01 13:26 | 1 | 624 | 4988571 | 624 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | LOOSE SERVE END CONNECTION.RE SQUEEZED CONNECTION... VER/HFP L3/HFP
11063 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2013-03-11 16:24 | 2013-03-11 17:42 | 8 | 78 | 4898551 | 624 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BLOWN ON POLE 37830175000011, CHECKING LINE RELEASED BY CREW 077S08 ///VER/CRB L/3 CRB IDC XXXX
11064 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2013-01-30 08:34 | 2013-01-30 10:03 | 7 | 89 | 4754081 | 623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | STRONG WINDS & RAIN ARE NOW PASSING THROUGH THIS AREA. I WILL WAIT TILL THIS PASSES THROUGH TO CHECK XFMR PRIMARY RISER HAS COME OUT OF HOT TAP WILL NEED MATERIAL HANDLER TO REPAIR. ///VER/CRB L/3 CRB IDC XXXX
11065 | Pikeville | 3120101 | STANVILLE | MUDCREEK | 2020-06-25 00:22 | 2020-06-25 10:45 | 1 | 623 | 4071541 | 623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad TR crew to replaceHeld in accordance with KPCO late night callout guidelines.. bad transformer. 15KVA 7200 Released by crew 074S09Bad TR crew to replaceHeld in accordance with KPCO late night callout guidelines.. bad transformer. 15KVA 7200. made repairs. customer restored at 10:45
11066 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-02-28 17:42 | 2011-02-28 17:49 | 89 | 7 | H64538-1 | 623 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 38970839 // CUTOUT BROKEN ON POLE 37830201C00043 NEED 3 MEN AND BIG BUCKET AND FLAGGERS RELEASED BY CREW OFF 1742 ON 1749STS WR # 38970839 // CUTOUT BROKEN ON POLE 37830201C00043 NEED 3 MEN AND BIG BUCKET AND FLAGGERS RELEASED BY CREW 077S04 OPENED C PHASE REC AT 1742 CLOSED IN AT 1749 REPLACED CUTOUT CREW 077H01 DUPLICATE FOR RECL OUTAGE...SEE 64538-1 (C PHASE RECL 92 CUST - 4) VER/HFP L3/HFP IDC ADDED ONE THREE PHASE CUSTOMER XXXX
11067 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2011-08-15 15:19 | 2011-08-15 20:30 | 2 | 311 | 4713921 | 622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 10 KVA BRING 15 TRUCKS OK HAD LINE FUSE OPEN 12 T BACK ON AT 1640 HRS 1 CUSTOMER STILL OFF HAD FUSE WITH 4X FUSE TOOK LINE FUSE OUT RELEASED BY CREW 078S03//VER/CRB IDCC CNT1 LINE FUSE ALSO OUT PER CREW COMMENTS XXXX
11068 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2016-06-04 16:43 | 2016-06-04 21:54 | 2 | 311 | 4298301 | 622 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XFMR FUSE OUT . WILL REPLACE. BAD CUTOUT. I AM TRYING TO FIND A SOMEONE TO OPEN GATE SO I CAN CHANGE CUTOUT. VER/KEP
11069 | Hazard | 3302704 | HAZARD | KENMONT | 2021-03-23 18:35 | 2021-03-23 22:02 | 3 | 207 | 4367471 | 621 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 kva 7200 transformer on pole 37830297000083. Manual. Crew required Released by crew 077S06 replaced transformer and restored power at 22:02
11070 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2021-03-16 07:15 | 2021-03-16 10:42 | 3 | 207 | 4339411 | 621 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | got transformer fuse out on 60 foot pole ,cant reach with long stick, got flager comming to watch road to fuse with bucket
11071 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2008-08-16 17:39 | 2008-08-16 21:06 | 3 | 207 | 52606-1 | 621 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000903// MAP IS WRONG-CORRECT POLE# FOR TRANSFORMER IS 1123-283 BAD 10KVA TRANSFORMER-3 CUSTOMERS-CALLING CREW-SEND TO L MCCARTY COD-3 MD FILED VER/KEP IDC XXXX
11072 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2009-01-12 20:37 | 2009-01-12 22:41 | 5 | 124 | 54569-1 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 3001202//V MULLINS TO REPAIRV MULLINS TO REPAIR RELEASED BY CREW 078S07/CREW ON SITE/FETR2325/VEM/REPAIRS MADE AND POWER RESTORED TO ALL CUST 2241/PLEASE CLOSE TICKET/THANKS/VEM COD 5 VER/TOM L3/TOM IDC XXXX
11073 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2010-06-24 14:55 | 2010-06-25 01:15 | 1 | 620 | 56590-1 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL NEED A 19.9\120\240 VOLT TRANSFORMER AND CURRENT LIMITING FUSE, CAN GET 4X4 MATERIAL HANDLER IN TO POLE MAY NEED TO BE PULLED OUT RELEASED BY CREW 078H08STS#35721200/VER/CRB IDC XXXX
11074 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-04-07 14:05 | 2015-04-07 16:40 | 4 | 155 | 4284691 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFMR FUSE BLOWN // WILL REFUSE// BAD 50 KVA // CREW ENROUTE// REPAIRS MADE // POWER RESTORED @ 16:40 VER/CRB
11075 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2015-04-19 19:56 | 2015-04-19 22:00 | 5 | 124 | 4336091 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 279-197 IS BURNT OFF JUST ABOVE XFMR, ISOLATED PRIMARY ON POLE 279-130, POWER RESTORED AT 22:00 RELEASED BY CREW 077S02 VER/TOM L3/TOM
11076 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2015-11-17 23:16 | 2015-11-18 01:20 | 5 | 124 | 4456081 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED CUTOUT AND REFUSED LINE WITH 20T
11077 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2016-01-02 08:56 | 2016-01-02 11:00 | 5 | 124 | 4580931 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | XFMR LEADS BURNT UP, REPLACED LEADS/ OPENED TRANSFORMER @ 1015-11/ ISO 37830158000031/ COD 5/ VER/BOW
11078 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2015-06-19 13:05 | 2015-06-19 15:40 | 4 | 155 | 4610621 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TOP OF POLE 1098-3552 BURNTED OFF, 405 POLE, POLE AND CUTOUT AND ARRESTOR, EVERYTHING ELSE WILL WORK BACK, CREW REQ, CAN USE TRUCK, IN PARKING LOT OF CALVARY APOSTOLIC CHURCH LINE OPENED ON POLE 1098-3504 GROUNDED AND TAGGED TO DDC RELEASED BY CREW 078S06 VER/KEP
11079 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2012-06-17 12:46 | 2012-06-17 14:50 | 5 | 124 | 4922841 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR HAS BURNT UP ON POLE 38831127A00268 // B PH ONLY//COD 5// EVEERYTHING APPEARS OK GOING TO TRY FUSE /// FUSE STAYED IN AND POWER RESTORED @ 14:50 //VER/GAH IDC XXXX
11080 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-05-02 21:10 | 2010-05-03 07:30 | 1 | 620 | 54417-1 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NO CREW REQUIRED REPLACED CUTOUT//VER/CRB IDC XXXX
11081 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2011-05-20 13:50 | 2011-05-20 16:25 | 4 | 155 | 4117251 | 620 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | BAD SECONDARY UNDERGROUND, RELEASED BY CREW 077S04//WR# 40051011 // BAD SECONDARY UNDERGROUND, //WR# 40051011 // OPENED TRANSFORMER ON POLE 37830248A00657 AT 1550, CLOSED AT 1625 --- POWER RESTORED. VER/HFP L3/HFP IDC CHANGED TIME OFF FROM 1550 XXXX
11082 | Cannonsburg | 3004301 | SILOAM | DISTRIBUTION | 2018-07-25 15:46 | 2018-07-25 17:50 | 5 | 124 | 4856191 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 4/3 srv drp burnted down at the house, i rem 4/3 srv drp and install new 2/3 srv drp at this loc, check with cust before i lefted all seemed to be ok, comp by amg
11083 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2012-01-23 15:18 | 2012-01-23 16:20 | 10 | 62 | 4286831 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | FUSE OPEN ON 117-178 WIRE DOWN ON POLE117-481//TIE WIRE BROKE RETIED//CUST. AT 6020 COMPLAINING ABOUT # OF OUTAGES PLEASE SEND COPY TO GREG BELL TO RELOCATE FUSE? POWER RESTORED AT 16:20//EMAILED TO G BELL IDCC FEC57 , TON1623 XXXX
11084 | Pikeville | 3413401 | GARRETT | GARRETT | 2022-02-23 07:23 | 2022-02-23 13:20 | 2 | 357 | 4534231 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout failed at 37830016A00193 and burned top of pole off causing TR fuse to open//Opened LF 37830016C00163 at 0857 to make repairs//repaired and restored at 1320
11085 | Hazard | 3309302 | VICCO | JEFF | 2020-06-18 18:44 | 2020-06-18 23:54 | 2 | 310 | 4043901 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 7200 be tight getting mat hander bucket, probably need to bring line truck also incase can/t get material in there ,there r 2 fence post cust said we could pull up to get bucket in there Released by crew 077S05.. all power restored @ 23:54 hrs p.hicks //cod 2
11086 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2015-07-08 14:40 | 2015-07-08 19:50 | 2 | 310 | 4746411 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD 12 KV CUTOUT RELEASED BY CREW 078S07,REPLACE CUTOUT ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT/ ISO 39831124B22503/ COD 2/ VER/BOW
11087 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2019-01-02 17:27 | 2019-01-02 22:37 | 2 | 310 | 4623901 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 10 kva 7200v single bushing, can use truck, small bucket with jib, pole number 453-148, on rt 3396 bottom of hill on right crew req Released by crew 078S06/crew on site/FETR 2300/vem/repairs made and power restored to all cust 2237/please close ticket/thanks/vem
11088 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2018-09-27 16:37 | 2018-09-27 19:12 | 4 | 155 | 4169581 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I changed out bad cutout and refused line on pole 379-126
11089 | Paintsville | 3401102 | FALCON | SALYERSVI | 2008-12-24 12:03 | 2008-12-24 14:38 | 4 | 155 | 63396-1 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 25 KVA XFMR BAD...CALLED TIM MILLER, HE IS BRINGING NEW XFMR...BB RELEASED BY CREW 076S01// ON SITE CHANGING CC 4 POT TCM// VER/PDP L3/KEP IDC XXXX
11090 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-02-09 21:16 | 2021-02-09 23:20 | 5 | 124 | 4952901 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | 38830211000159 pole broke at the phone--35/4 has a lat and 25 kva tran per field view--crew req .per cust can use trk.but old garden spot and ground is a little soft .need track digger --ds020921 Released by crew 078S01 Crew on site. Opened tap and xfmr on pole 211-159 at 21:16 Closed at 23.20. Ticket complete. Released by crew 078H11/ ISO 38830211000159/
11091 | Cannonsburg | 3000102 | ASHLAND | 25-29STREET | 2021-07-22 13:21 | 2021-07-22 13:52 | 20 | 31 | 4946471 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | Emergency Outage affecting 20 customers for crews to safely make repairs to bundle conductor. Outage should last 45 mins from start. Approximate start time is 1300 Coins Call at 1156 /Coins Complete at 1207 Off at 1321 On at 1352 Switching to transfer portion of Ashland/29th to 47th/39th before this outage occurred
11092 | Hazard | 3302704 | HAZARD | KENMONT | 2013-11-27 22:25 | 2013-11-27 23:27 | 10 | 62 | 4085131 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURN UP === REPLACED POWER OK VER/KEP
11093 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2010-12-20 19:55 | 2010-12-20 22:30 | 4 | 155 | 54656-1 | 620 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE IN 1/0 SEC ABT 10 FT OUT APPEARS BAD,WILL CALL FOR CREW TO HELP REPAIR///////SERVE-IN WENT BAD,REPLACED ALL.ALL OK AFTERWARDS VER/HFP L3/HFP IDC FROM COMMENTS COULD BE LESS CUSTOMERS BUT LEFT AS IS XXXX
11094 | Hazard | 3303902 | LESLIE | WOOTON | 2017-07-28 16:10 | 2017-07-28 21:20 | 2 | 310 | 4196371 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10KVA CSP 37830510000122 VER/AWD
11095 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2016-08-11 13:20 | 2016-08-11 18:30 | 2 | 310 | 4763151 | 620 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND BETWEEN SECONDARY PEDESTAL 115-165 AND 115-358, WILL BE MAKING REPAIRS.CREW ONSITE.MADE REPAIRS AT 1830./ ISO38831150000165/ COD 2/ VER/BOW
11096 | Cannonsburg | 3010601 | RUSSELL | KENWOOD | 2014-12-23 18:49 | 2014-12-23 22:15 | 3 | 206 | 4877811 | 618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 1148-954 BAD CUTOUT, 12KV. LINE CREW REQD RELEASED BY CREW 078H12// COD3// VER/ ADH
11097 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2011-03-15 15:29 | 2011-03-15 17:12 | 6 | 103 | 54554-1 | 618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE DOWN//ONLY PHASE C OPEN //OPENED OTHER 2 PHASES @ 1700 OPEN OTHER DISC AT COD-9 --- 2 ON A - 1 B - & 6 3 PHASE ISO LF 37830024B10001 DUPLICATING FOR THE A & B PHASE OUTAGE IN H54554-1 VER/HFP L3/HFP IDC XXXX
11098 | Hazard | 3310501 | HADDIX | QUICKSAND | 2017-08-27 14:11 | 2017-08-27 19:20 | 2 | 309 | 4302531 | 618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA TRANSFORMER 19.9,NEED 2 MAN LINE CREW WITH BIG BUCKET.ALSO NEED NEW CUTOUT AND BRACKET,TRUCK ACCESSIBLE. VER/AWD L3/HFP XXXHFP
11099 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2013-03-19 17:34 | 2013-03-19 19:17 | 6 | 103 | 4923051 | 618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BAD ON UNDERGR. POLE , NEED TO OPEN OTHER CUTOUT ON SAME BRK IN ORDER TO REPLACE BAD CUTOUT ON 1147-436 REPLACE 2 CUTOUTS POWER RESTORED 19:17 (NO CUST ON OTHER CUTOUT - DIP FUSE) COD-6 ISO DF 39831147A00436 VER/HFP L3/HFP IDC XXXX
11100 | South Williamson | 3411401 | DEWEY | INEZ | 2021-02-03 12:06 | 2021-02-03 17:15 | 2 | 309 | 4933921 | 618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 KVA transformer failed. Personnel enroute to bring a new one. Replaced and restored @ 17:15. sh
11101 | Whitesburg | 3309101 | WHITESBURG | WHITESBURG | 2022-11-30 10:24 | 2022-11-30 13:50 | 3 | 206 | 4208041 | 618 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken cutout on pole 449-A2-111. manual pole.. already been in touch with crew to make repairs. open fuses on pole 449-29 @ 13:15 closed @ 13:50.. cutout replaced, power restored
11102 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2019-03-25 23:13 | 2019-03-26 09:30 | 1 | 617 | 4025061 | 617 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Checked with the beast and we have a bad connection on secondary pole/// tried to get to pole but this is difficult location @ night/// Talked to Railroad and they said they had generator running and it would be fine to wait till in the A.M Released by crew 074S02Checked with the beast and we have a bad connection on secondary pole/// tried to get to pole but this is difficult location @ night/// Talked to Railroad and they said they had generator running and it would be fine to wait till in th
11103 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2012-07-28 09:19 | 2012-07-28 11:53 | 4 | 154 | 4855931 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | NO CREW REQUIRED REPAIRED CONNECTION
11104 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2015-06-16 07:02 | 2015-06-16 08:30 | 7 | 88 | 4577391 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 70-526 BAD CUTOUT AND LA L3/DKG
11105 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2018-07-19 07:12 | 2018-07-19 08:40 | 7 | 88 | 4797581 | 616 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | Part power/457 Blackburn/606-571-0230/Fielder Copper over aluminum squeezed up on pole, repairs made good voltage L3/HFP
11106 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2015-04-03 17:10 | 2015-04-03 22:18 | 2 | 308 | 4266151 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE BLOWN// WILL REFUSE//FUSE APPEARS TO HAVE BROKE/ ISO 38831126C00495/ COD 2
11107 | Hazard | 3301101 | CHAVIES | CHAVIES | 2015-02-18 00:34 | 2015-02-18 10:50 | 1 | 616 | 4037761 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOLD UNTIL MORNING , WILL TAKE 4X4 PICKUP WITH CHAINS TO GET IN HOLLOW . RELEASED BY CREW 075H04 WIRE DOWN FROM POLE 63 TO 64 ISOLATED AT POLE 63 REFUSED ON POLE 194;26 WITH 40T FUSE NOT ON MAPS(FUSES SHOW IN POWER ON) NEED TO PUT WIRE UP AT A LATER DATE SEND TO GLEN COMBS O ONE OUT OF POWER//FOUND NOTHING THAT TOOK THIS DOWN... `ROTTEN` ACSR PER SERVICER//COD 1//EMAILED TO G COMBS// VER/DBM L3/HFP XXX
11108 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-02-06 18:49 | 2017-02-06 23:57 | 2 | 308 | 4362421 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 1METER BLANK I THINK THE ARRESTOR IS BAD ON 1127A371 WHICH IS NTA I WILL CLIMB POLE AND CHANGE ARRESTOR REPLACED BAD ARRESTOR ON 1127A371 RESTORED POWER AT 23:57/// VER/DKM L3/HFP XXXHFP
11109 | Pikeville | 3409401 | FEDSCREEK | FEDSCREEK | 2019-08-22 17:14 | 2019-08-23 03:30 | 1 | 616 | 4932101 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Trans. fuse open @174-52, checking.bad 5kva transformer,will need2 man line crew with big bucket,truck accessible,and new 15kva 7200 transformer Released by crew 074S05
11110 | South Williamson | 3411401 | DEWEY | INEZ | 2017-04-18 01:04 | 2017-04-18 11:20 | 1 | 616 | 4653431 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA 7200 XFMR ON POLE 672-195///TRUCK ACCESS WITH MATS///CREW ENROUTE//XFMR REPLACED//RESTORED AT 11:20//COMPLETE//EM 38830672A00195 VER/AWD L3/HFP XXXHFP
11111 | South Williamson | 3200302 | BELFRY | TOLER | 2008-04-07 20:46 | 2008-04-07 22:14 | 7 | 88 | 65047-1 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 3200302//FUSE BROKE//VER/CRB IDC XXXX
11112 | Pikeville | 3403002 | PIKEVILLE | MAINST | 2010-01-11 18:55 | 2010-01-11 20:23 | 7 | 88 | 52879-1 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | TRANSFORMER LEAD HAS BURNT OUT OF BUSHING I WILL SEE IF I CAN REPAIR IT MYSELF.//// REPAIRED SERVE END THAT HAD BURNED OUT ON THE SECONDARY LEAD RESQUEEZED ALL CONNECTIONS AND RESTORED POWER.TIM MCCOY//OPENED XFMR @ 2002 CLOSED 2023//COD 7 IDC XXXX
11113 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2016-04-08 06:42 | 2016-04-08 11:50 | 2 | 308 | 4070211 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WILL WORK AT START TIME 4-8-16 50 KVA TRANSFORMER IS BAD TIM HALL IS SENDING CREW TO REPLACE IT RELEASED BY CREW 079H03// CHANGED XFMR AND RESTORED POWER AT 11:50 TIM MCCOY RELEASED BY CREW 074H10 ISO 38821130000130 COD 2 VER/AWD
11114 | South Williamson | 3417602 | NEW CAMP | APP REG HOSP | 2019-06-29 14:34 | 2019-06-29 17:08 | 4 | 154 | 4618111 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Bad transformer cutout. Need big bucket truck to work the transformer pole.
11115 | Pikeville | 3408101 | SALISBURY | PRINTER | 2015-01-17 11:27 | 2015-01-17 16:35 | 2 | 308 | 4941121 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANSFORMER. CREW CALLED OUT. NEW 50 KVA TRANSFORMER INSTALLED EVERYTHING OK VER/CRB L3/HFP XXX
11116 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-08-08 12:37 | 2017-08-08 15:11 | 4 | 154 | 4240021 | 616 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | REPLACING BAD UNDERGROUND CREW ON SITE FETR 16:00----REPLACED 170 OF 4/0 UG SERV---PWR OFF AT 12:37 BACK ON AT 15:11---VOLT CK 123/123/246---TBL TKT COMP/ ISO 38830116B00574/ ISO 38830116B00574/ COD 4/ REMOVED FROM ABNORMAL/ VER/BOW
11117 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2010-03-13 12:15 | 2010-03-13 15:40 | 3 | 205 | 66310-1 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED. CUTOUT BROKE DOWN AND CAUGHT POLE 11D-514 { RECLOSER POLE } ON FIRE. I OPENED RECLOSER AND ALSO WENT TO POLE 11D-27 AND OPENED LINE CUTOUT ON THAT POLE TO ISOLATE RECLOSER POLE. WILLIE IS COMING WITH HELP. WE REPAIRED POLE AND CLOSED IN RECLOSER AT 15:40.//VER/CRB IDC XXXX
11118 | Hazard | 3303902 | LESLIE | WOOTON | 2021-03-06 09:20 | 2021-03-06 12:45 | 3 | 205 | 4309021 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout on pole 438-3 , opened xfmr fuse on pole 438-3 @ 12:15 . all power back on @ 12:45
11119 | Hazard | 3308502 | BONNYMAN | HAZARD | 2018-07-27 17:00 | 2018-07-27 20:25 | 3 | 205 | 4864441 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 1 span wire down primary need couple men big bucket, looks like sleeve pulled out
11120 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2008-11-20 15:19 | 2008-11-20 18:44 | 3 | 205 | 50279-1 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3408303/WR# 27382915/, ON SITE, XFORMER FUSE BLOWN, REFUSING IT, HAVE BAD 25 KVA XFORMER, CALLED R MARCUM, GETTING CREWSTARTED THIS WAY VER/TOM IDC XXXX
11121 | Hazard | 3302704 | HAZARD | KENMONT | 2010-11-20 09:35 | 2010-11-20 13:00 | 3 | 205 | 58333-1 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 37839710 // ON SITE CKING TROUBLE//BAD CUTOUT CALL DUTY FOR 1 MAN AND BIG BUCKET.ON SITE CKING TROUBLE//BAD CUTOUT CALL DUTY FOR 1 MAN AND BIG BUCKET.OPEN TAP AT 11;48AM AND CLOSE AT 1300//REPLACE TRANSFORMER AND CUTOUT ..BROKE BUSHING .. COD-3 TAP COD-1 SEE HH58333-1 FOR 1 CUSTOMER OUTAGE ON TAP VER/HFP L3/HFP IDC XXXX
11122 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-01-30 10:13 | 2015-01-30 12:16 | 5 | 123 | 4974581 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE IS BLOWN ON POLE 37820032C00006, PATROLLING THE LINE. BAD CUTOUT ON POLE 32-C-90, NO TRUCK ACCESS, ILL REPLACE THE CUTOUT. /// COD-5 ISO LF 37820032C00006/ VER/BOW
11123 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-01-10 10:05 | 2013-01-10 13:30 | 3 | 205 | 4583081 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUT OUT VER/KEP IDC XXXX
11124 | Hazard | 3303902 | LESLIE | WOOTON | 2011-10-15 08:45 | 2011-10-15 09:00 | 41 | 15 | 4984131 | 615 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, GROUNDING | FRAME GROUND ON STEPDOWN BURNT IN TWO CAUSING VOLTAGE TO CHANGE BURNING UP ALL LIGHTNING ARRESTERS AND CAUSING DAMAGE TO CUSTS POWER WASNT OFF TILL I TOOK IT OFF TO MAKE REPAIRS THEN WENT AND PUT SINGLE CUST BACK ON//OFF FROM 0845 UNTIL 0900 // COD 41// VER/DBM IDC XXXX
11125 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2016-10-07 18:48 | 2016-10-07 23:55 | 2 | 307 | 4968371 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | NEED LINE CREW BAD 50KVA MIT GET TRUCK TO POLE RELEASED BY CREW 078S08--ON JOB SITE--CHANGED 50KVA-LIGHTNING ARRESTOR AND CUTOUT---ALSO RESAGD PRIMARY AND 1/0 LASH SECONDARY---TBL TKT COMP---RMV/// VER/DKM L3/HFP XXXHFP
11126 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2014-02-27 15:20 | 2014-02-27 20:27 | 2 | 307 | 4438821 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OUT ON POLE 37830442000054, CHECKING LINE/// LINE CUTOUT BAD, NEED CREW MANUAL ON HILL RELEASED BY CREW 077S08 ON SITE EST. 21:00 REPLACED CUTOUT AND INSULATOR RESTORED POWER AT 2027 VER/CRB L3/GSL
11127 | Pikeville | 3120103 | STANVILLE | HAROLD | 2020-01-12 08:06 | 2020-01-12 18:20 | 1 | 614 | 4281791 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICER REQUIRED/XFR SEC LEAD COME OUT OF BUSHING. Released by crew 074E09Ha to open trans. to repair lead, opened up @1811,made repairs and closed back in @1820.
11128 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2021-06-22 08:08 | 2021-06-22 18:22 | 1 | 614 | 4789801 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | fuse on pole was not blown on pole 1113C-29..cust meter is not lighting up..only cust on that can..i checked voltage at the service.i think we have a bad transformer..25kva 7200.doubt you can reach it with a bucket Released by crew 079S03// ser. had grown into tree and failed// replaced s/d
11129 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-01-16 21:43 | 2009-01-17 02:50 | 2 | 307 | 56444-1 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3000201//,,,TRANSFORMER GAVE OUT FUSE STILL IN BUT NO VOLTAGE COMING OUT ,,,, TWO CUSTOMERS OUT RELEASED BY CREW 078S02//CREW TO REPLACE WITH 25KVA// VER/TOM L3/TOM
11130 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-02-28 16:21 | 2018-02-28 21:28 | 2 | 307 | 4890911 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer no answer/crew required no trucks bad location/ ISO 38830271000149/ COD 2
11131 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-03-12 08:16 | 2015-03-12 18:30 | 1 | 614 | 4185611 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM FUSE BLOWN WILL REFUSE/// XFM CAME BACK OUT DAVE SAMMONS IS ENROUTE RELEASED BY CREW 074H17 REPLACED BAD XFMR ON AT 18:30 D SAMMONS//COD 1// VER/DBM
11132 | Hazard | 3308002 | JACKSON | PANBOWL | 2013-09-06 15:10 | 2013-09-06 20:17 | 2 | 307 | 4825871 | 614 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE 1084 -311 GOT TRANSFORMER ON AT 2017 RELEASED BY CREW 077S05 VER/SEF
11133 | Hazard | 3310501 | HADDIX | QUICKSAND | 2022-12-22 06:27 | 2022-12-22 09:00 | 4 | 153 | 4285371 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | bad arrestor on the transformer on pole 87-5 . replaced arrestor and power restored @ 09:00
11134 | Paintsville | 3409303 | KENWOOD | HAGERHILL | 2008-03-12 11:37 | 2008-03-12 15:01 | 3 | 204 | 56511-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3409303// BAD XFMR. CREW EN-ROUTE TO CHANGE. RELEASED BY CREW 076S02 CHANGED XFMER TO A 25 KVA TOMMY GOBLE//VER/CRB IDC XXXX
11135 | Cannonsburg | 3001003 | HITCHINS | GRAYSON | 2017-12-13 08:45 | 2017-12-13 09:03 | 34 | 18 | 4645041 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 15 t line fuse melted out .increased fuse to 40t complete
11136 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2022-12-23 22:04 | 2022-12-24 03:10 | 2 | 306 | 4336031 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFM fuse open on 21-139// checking// bad 25 kva 19.9 XFM, crew required no truck
11137 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2008-07-02 22:11 | 2008-07-03 01:35 | 3 | 204 | 61530-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3400302//BAD 25KVA SINGLE BUSHING 120/240 7200. THE DRIVEWAY BETWEEN MEADE MEADOW LN AND ANTIQUE LN. TRANSFORMER IN BOTTOM WITH DOOR OPEN.......DAH // OUT @ //BAD 25KVA SINGLE BUSHING 120/240 7200. THE DRIVEWAY BETWEEN MEADE MEADOW LN AND ANTIQUE LN. TRANSFORMER IN BOTTOM WITH DOOR OPEN.......DAH RELEASED BY CREW 074S08 IDC XXXX
11138 | Hazard | 3307301 | BULAN | ARY-HEINE | 2013-05-25 03:51 | 2013-05-25 04:08 | 36 | 17 | 4182991 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SDB / OUTAGE TO SAFELY REPAIR PH C STIRRUP AT SW POLE 177-B-287. CC 36. ALSO SEE OUTAGE 4182631. OUTAGE FROM 0351-0408. IDC XXXX
11139 | Pikeville | 3403003 | PIKEVILLE | CEDAR CREEK | 2022-08-22 17:21 | 2022-08-22 20:45 | 3 | 204 | 4781601 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg in customers URD secondary, S. Goble is bringing an Add-A-Phase to get customer back on until we can make permanent repairs. Got add-a-phase hooke up @2045, only 1 customer was out.
11140 | Paintsville | 3402801 | PAINTSVILLE | CITY | 2009-08-13 14:44 | 2009-08-13 18:08 | 3 | 204 | 55702-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | FOUND BAD UG SPLICE. WILL HAVE TO DIG IT OUT TO REPAIR. CREW ONSITE AND ADDITIONAL CREW ENROUTE TO ASSIST. WILL HAVE XFMR 809-561 OPEN FOR APPROX 1 HOUR TO MAKE REPAIRS WHEN CREW ARRIVES. ONLY THREE CUST WITH PART OUT. OPENED XFMR 809-561 AT 16:45 INTERRUPTING REMAINING CUST UNTIL REPAIRS COMPLETE. 12 CUSTOMERS TOTAL. REPAIRS COMPLETE. RESTORED ALL CUSTOMERS AT 18:08. SH IDCC CNT7, CDC89 XXXX
11141 | Cannonsburg | 3001102 | HOODSCREE | RURAL | 2018-06-06 12:56 | 2018-06-06 16:20 | 3 | 204 | 4562141 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Tree crew at shop. Customer reported outage at Svc Ctr. broke cutout on pole 38830091C00212 NBT WILL NEED manuel tree crew to get to pole and line crew tree (tree crew will meet you at the shop) Released by crew 078H01repairs made all cust restored @ 1620 please close ticket thanks.bt
11142 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2008-06-23 20:17 | 2008-06-23 21:25 | 9 | 68 | 53253-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | JRV ON SITE @ 20:57.....BROKEN XFRMER CUTOUT ON POLE 1086-D-122.....WILL REPLACE & RE-FUSE......//...REPLACED BAD CUTOUT....FUSE NOT BLOWN......RESTORED POWER TO CUSTS.....JRV..06/23/08 VER/HFP IDC XXXX
11143 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2008-02-05 23:14 | 2008-02-06 04:20 | 2 | 306 | 50077-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308602// FOUND 15 KVA TRANSFORMER BURNED UP. NEED 3 MEN AND LINE TRUCK. THIS WILL BE A MANUAL JOB ON HILLSIDE COD-2 RELEASED BY CREW 077S07 VER/KEP IDC XXXX
11144 | Whitesburg | 3311401 | REEDY STATION | DEANE | 2014-01-07 01:09 | 2014-01-07 06:15 | 2 | 306 | 4243791 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD XFMR . I NEED TWO MEN A MATERIAL HANDLER AND A 25 KVA 19.9 XFMR VER/SEF
11145 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2012-12-29 12:17 | 2012-12-29 13:25 | 9 | 68 | 4550431 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | POLE 1123-6592 6T MELTED OUT INSTALLED 8T OVERLOADED// COD 9// VER/DBM
11146 | South Williamson | 3200301 | BELFRY | BELFRY | 2011-03-18 03:03 | 2011-03-18 04:45 | 6 | 102 | 55343-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | XFMR FUSE OUT ON POLE 38820990A00054 GOING TO REFUSE;;;; ( FUSE TAIL BROKE) REFUSED XFMR POWER BACK ON VER/PDP IDC XXXX
11147 | Hazard | 3303902 | LESLIE | WOOTON | 2018-05-29 13:14 | 2018-05-29 18:20 | 2 | 306 | 4516141 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT//MDC MADE TO SHOW CORRECT TRANS//L/F OPEN ON POLE 37830414000032//COD 2//PER SERVICER//
11148 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2010-10-03 13:59 | 2010-10-03 14:50 | 12 | 51 | 56439-1 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | WR# 37152914 //POLE 1123-7074 OPEN WIRE NEEDS CHGED TO COLSE TOGETHER PUT SPACES IN WIRE SEND TO TEC .//COD 12//EMAILED TO S MARTIN// VER/DBM IDC XXXX
11149 | Hazard | 3420002 | SOFT SHELL | LEBURN | 2017-01-19 17:26 | 2017-01-19 18:00 | 18 | 34 | 4313161 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED SECTIONALIZER ON 37830206C10261 TO SAFELY REPAIR CUTOUT ON 37830206000177 (ORDER 4313031). OPENED 1726-1800. VER/AWD L3/HFP HFP
11150 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2013-08-09 23:50 | 2013-08-10 00:58 | 9 | 68 | 4642321 | 612 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK//COD 9// VER/DBM
11151 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2019-06-24 13:42 | 2019-06-24 15:24 | 6 | 102 | 4574401 | 612 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Bill Johnson reported a broken neutral in service drop to house #193, replaced 4/3 service with 2/3 service, made repairs @1524.
11152 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2013-01-30 13:58 | 2013-01-30 14:45 | 13 | 47 | 4759431 | 611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON TAKE OFF POLE. ///VER/CRB L/3 CRB IDC XXXX
11153 | Cannonsburg | 3003702 | COALTON | CANNONSBURG | 2014-08-23 07:56 | 2014-08-23 11:48 | 5 | 232 | 4411611 | 611 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CENTER PHASE LINE FUSE OPEN AT POLE 139-144 ALSO BANK POLE 139-368 OPEN.. CLOSED IN LINE FUSE AT 0845// BAD TRANSFORMER CHANGEOUT ON 38830139A00144// 139-368CENTER PHASE LINE FUSE OPEN AT POLE 139-144 ALSO BANK POLE 139-368 OPEN.. CLOSED IN LINE FUSE AT 0845 BAD 100 KV TRANSFORMERCENTER PHASE LINE FUSE OPEN AT POLE 139-144 ALSO BANK POLE 139-368 OPEN.. CLOSED IN LINE FUSE AT 0845 BAD 100 KV TRANSFORMER CHANGED OUT POWER RESTORED AT 1148 RELEASED BY CREW 078Q08// VER/BOW
11154 | Hazard | 3309302 | VICCO | JEFF | 2012-12-19 11:10 | 2012-12-19 13:12 | 5 | 122 | 4482621 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SPLICE WENT BAD ON SECONDARY SIDE OF TRANSF === REPAIRED === POWER OK VER/KEP
11155 | Pikeville | 3408103 | SALISBURY | MARTIN | 2010-05-08 08:55 | 2010-05-08 14:00 | 2 | 305 | 57605-1 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | 65T FUSE OUT POLE 1098C101 WIRE OUT OF SAG IN TWO SPANS. RESAGED WIRE FUSED UP EVERYTHING OK . NO FUSES ON POLE1099-119. ON POLE 1099-20 B AND C PHASE LOOPS ARE CUT OPEN. I ONLY FUSED A PHASE UP ON POLE 1098C101//VER/CRB IDC XXXX
11156 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2018-09-15 12:16 | 2018-09-15 16:45 | 4 | 269 | 4101581 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva 7200 truck acess only 1 leg hot Released by crew 077H14//OPENED L/F @ 1609 TO SAFELY REPLACE TRANSFORMER//
11157 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2017-03-26 04:55 | 2017-03-26 10:00 | 2 | 305 | 4585271 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE TRAN C/O--REPLACED--TRAN IN AT 10:00--ALLGOOD-DSKG032617/ ISO 38830453000199/ COD 2/ VER/BOW
11158 | Hazard | 3303902 | LESLIE | WOOTON | 2008-12-17 06:45 | 2008-12-17 11:50 | 2 | 305 | 59399-1 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3303902// BAD CUTOUT//CREW REQUIRED//3303902//CUTOUT HAS BROKE//COD 2//ISO 37830415000004// VER/DBM L3/KEP IDCC CNT1 XXXX
11159 | Hazard | 3303901 | LESLIE | HYDEN | 2020-06-28 18:36 | 2020-06-28 20:38 | 5 | 122 | 4086111 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Bad K mate on 37830412C00370 took tranformer and line fuse out. Power restored @ 20:38
11160 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2014-03-22 11:40 | 2014-03-22 16:45 | 2 | 305 | 4517941 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSES BLEW ON 115-346 FUSE BLEW ON XFORM BANK Y-DELTA WITH GR. SWITCH NEED LINE CREW TR. OK 25 KVA 34.5 2- BUSHING AND 3 -19.9 ARRESTERS/ FETR/17:30/JEH/ REPAIRS COMP. POWER REST.@ 16:45/JEH VER/SEF
11161 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2011-10-10 11:58 | 2011-10-10 17:03 | 2 | 305 | 4961781 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | CROSSARM BRACES ARE BROKEN, ARM TILTED, CUTOUT LAYING AGAINST TRANSFORMER, CREW REQUIRED, MANUAL POLE UP ON HILL AT BOTTOM OF DWARF MTN. RELEASED BY CREW 077S04// VER/DBM IDC XXXX
11162 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2010-09-28 10:15 | 2010-09-28 15:20 | 2 | 305 | 54644-1 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CREW REQUIRED BURNT OFF 40/5 TECH. NEEDED ALSO TRUCKS OK ISOLATED ON 223-215/SEND TO FRALEY//COD 2//ISO 38830223000215// VER/DBM IDC XXXX
11163 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2008-03-27 12:08 | 2008-03-27 14:10 | 5 | 122 | 61199-1 | 610 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3116102//REPLACING CUTOUT/HAD TO OPEN 206-1122 AT 1359HRS OFF ABOUT 20 MIN./BACK ON AT 1410HRS RELEASED BY CREW 078S03 SHOWED RECLOSER OUTAGE ON SEPERATE ORDER VER/KEP IDC XXXX
11164 | South Williamson | 3411401 | DEWEY | INEZ | 2018-03-29 06:52 | 2018-03-29 10:15 | 3 | 203 | 4145251 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout and arrestor back on hill///crew enroute to help//repairs made//restored at 10:15//complete//em
11165 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-06-30 06:05 | 2008-06-30 09:28 | 3 | 203 | 59886-1 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904// RELEASED BY CREW 078S11 COD-3 VER/HFP IDC XXXX
11166 | Cannonsburg | 3117601 | PRINCESS | MEADE STATION | 2012-05-05 09:27 | 2012-05-05 12:50 | 3 | 203 | 4749161 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CHANGED 199 CUTOUT CLOSED LINEFUSE ONE POLE BACK///VER/CRB L/3 CRB IDCC CNT3, PN425, CDC83 XXXX
11167 | Hazard | 3308503 | BONNYMAN | BIGCREEK | 2011-12-27 15:33 | 2011-12-27 17:00 | 7 | 87 | 4206341 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD TRANSFORMER ON POLE 37830247A00068, CREW NOTIFIED. --- POWER RESTORED. ////VER/CRB IDC XXXX
11168 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-07-20 19:51 | 2008-07-21 06:00 | 1 | 609 | 54545-1 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD X-FMER. VER/KEP IDC XXXX
11169 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2016-01-25 10:57 | 2016-01-25 14:20 | 3 | 203 | 4648801 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BIG BUCKET ENROUTE, REPLACED CUTOUT., ALL WORK COMPLEE / GXJ/ VER/AWD
11170 | Hazard | 3301401 | COMBS | COMBS | 2009-05-21 16:02 | 2009-05-21 19:25 | 3 | 203 | 57825-1 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT = NEED 2 MEN ==CLIMB JOB == RELEASED BY CREW 077S03.... ON SIGHT TO CHANGE BAD C/O......ALL POWER RESTORED. 19:25 HRS. P.HICKS//COD 3// VER/DBM IDC XXXX
11171 | Cannonsburg | 3001401 | LOUISA | CITY | 2012-07-08 08:16 | 2012-07-08 11:39 | 3 | 203 | 4591841 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | XMF FUSE WAS BLOWN, EXAMINED CUTOUT FROM BUCKET, FOUND CRAKED CUTOUT AND REPLACED. APR CLOSE TICKET. DWEST//COD 3
11172 | Paintsville | 3409302 | KENWOOD | AUXIER | 2022-08-10 22:21 | 2022-08-11 08:30 | 1 | 609 | 4723101 | 609 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Called customer//no outage will work in thw AM// repairs made// Complete
11173 | Pikeville | 3403202 | BEAVERCREEK | PRICE | 2011-08-27 19:56 | 2011-08-28 01:00 | 2 | 304 | 4767361 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | METERING | A&B PHASE 65T FUSES OUT// SERVICER GOING TO PRIMARY MEETERING AT COAL COMPANY TO CHECK REPORT OF FIRE ON METER POLE//2 65T FUSE OUT DUE TO BAD PRIMARY METERING. CUST AT MINING SITE SAID HE SEEN FIRE COMING FROM TRANSFORMER ON THAT POLE. I HAVE METERING OFF LINE AND TAGED. I WAS ABLE TO GET BUCKET TO METERING POLE I WENT UP AND LOOKED AT TRANSFORMERS BUT WAS NOT ABLE TO TELL WERE THE FIRE WAS. SEND COPY TO TIM HALL AND ENG PIKEVILLE. AFTER BYPASSING METERING FUSED UP EVERYTHING OK IDC XXXX
11174 | Pikeville | 3413402 | GARRETT | LACKEY | 2018-09-26 23:06 | 2018-09-27 09:14 | 1 | 608 | 4163651 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | attempted to contact customer, no response // Dispatched in accordance with KYPCo Late Night Callout Guidelines. 6t fuse out due to broken cutout hanging down pole. replaced cutout fused up everytning ok
11175 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2010-01-05 08:37 | 2010-01-05 08:56 | 32 | 19 | 60809-1 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CREWS OPENED RECLOSER IN ORDER TO MAKE LOOPS BACK//RELATED TO ORDER 60729-1//COD 32// VER/DBM IDC XXXX
11176 | Pikeville | 3403001 | PIKEVILLE | CITY | 2008-04-13 22:58 | 2008-04-14 01:30 | 4 | 152 | 50897-1 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3403001/// NEED TO REPLACE CUTOUT AND ARRESTOR//CONTACTED D.MASSEY AND TURNED IT OVER TO HIM AND CLOSING TICKET IDC XXXX
11177 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-05-19 23:12 | 2011-05-19 23:20 | 76 | 8 | 4115601 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4115391 -- - CREW OPENED LINE FUSE TO ALLOW THEM TO MAKE UP LOOPS AFTER POLE REPAIRED/// COD-76 ISO LF 38831052B00389 VER/HFP L3/HFP IDC XXXX
11178 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2012-12-27 21:53 | 2012-12-28 00:25 | 4 | 152 | 4543051 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SERVICE DROP BURNT INTO AT SEC POLE 18-194 WILL BE MAKING REPAIRS. I HAVE REPAIRS MADE CHECKED VOLTAGE EVERYTHING OK. LOOKS LIKE SERV END HEATED UP MELTED BURNT NEUTRAL AND HOT CONDUCTOR INTO. SEND COPY TO ENG PIKEVILLE SEC FROM TRANSFORMER POLE 18-175 TO POLE 18-194 IS #2 4 CONDUCTOR 3 PHASE WIRE THIS SERVS 2 HOUSES 1 200AMP 3 PHASE AND 1 400AMP SINGLE PHASE CHECK LOAD MAKE SURE CONDUCTOR IS RIGHT SIZE. ALSO SEND COPY TO PEGGY IN DAMAGE CLAIMS. VER/ARN
11179 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2014-11-12 23:03 | 2014-11-13 01:35 | 4 | 152 | 4724191 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE BURNED UP. I CHANGED CUTOUT AND CHECKED AND REFUSED XFMR VER/KEP
11180 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2015-06-26 10:48 | 2015-06-26 15:52 | 2 | 304 | 4662181 | 608 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT === NEED 7200 CUTOUT AND ARESTER AND T BRACKET LINE CREW === THIS UP ON HILL NEED ROW CREW TO CUT TO POLE === RELEASED BY CREW 077S03 RELEASED BY CREW 077H10/ ISO 37830488000008/ COD 2/ VER/BOW
11181 | Whitesburg | 3314402 | MAYKING | MILLSTONE | 2021-08-24 18:05 | 2021-08-24 23:08 | 2 | 303 | 4145961 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | bad 26kva 7200 transformer// crew required
11182 | Cannonsburg | 3007903 | BUSSEYVILLE | LOUISA | 2008-11-24 06:26 | 2008-11-24 09:48 | 3 | 202 | 51463-1 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007903//,,,,,BROKE CUTOUT ON POLE 477-126,,,,,,BACK ON//VER/CRB IDC XXXX
11183 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2020-05-25 17:42 | 2020-05-25 22:45 | 2 | 303 | 4904981 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bud 7200 cutout not by truck. coming from rt 5 just past storage units on 1458 turn left on second gravel drive. theres anew pole set beside pole Released by crew 078H03 complted TL//cod 2
11184 | Cannonsburg | 3001204 | HOWARDCOL | SUMMIT | 2016-06-14 13:14 | 2016-06-14 23:20 | 1 | 606 | 4346591 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND SEND TO BRETT T. RELEASED BY CREW 078S08,,CREW ON SITE,,REPAIRED URD AND REPLACED ARMS AND CUTOUTS ON POLE..THIS IS DIRECT BURIED, MAY WANT TO SEND TO TECH TO WRITE A JOB TO REPLACE PRIMARY URD//SENT TO TECH VER/CRB
11185 | Pikeville | 3413402 | GARRETT | LACKEY | 2012-12-26 11:03 | 2012-12-26 14:25 | 3 | 202 | 4525801 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ISO POLE # IS 37830159000525, NEED 1 MAN , BIG BUCKET , CUTOUT, ARRESTER, AND BRACKET . ALL WORK COMPLETE / GXJ ///VER/CRB/ L/3 CRB
11186 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2013-04-19 09:38 | 2013-04-19 13:00 | 3 | 202 | 4025181 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | LINE FUSE BLOWN ON 38831149000050// WILL REFUSE// FUSE CAME BACK OUT// BAD DEADEND INS ON POLE 1149-115/// CREW ON WAY // 3 COD IDC XXXX
11187 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2017-03-19 22:39 | 2017-03-20 00:20 | 6 | 101 | 4571051 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | SECONDARY CONNECTOR BURNDT INTO @ 47-D-1, OPENED THE TRANS. @2335, MADE REPAIRS AND CLOSED BACK IN @0020. VER/KEP
11188 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2009-04-15 21:54 | 2009-04-15 23:35 | 6 | 101 | 55174-1 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3003701//PRIMARY OPEN AT POLE 38830184C00042//ISO//COD 6//LIFTED TAP ON POLE 38830184C00075 IN ORDER TO MAKE REPAIRS @ 2255//INTERRUPTED 5 MORE CUSTOMERS (SEE H55174-1)//BROKEN RISER ON HOT LINE CLAMP, REPAIRED WIRE. SEVERAL TREES BURNING IN LINE, NOT FUSED AT 3 PHASE, NEED CUTOUT AT POLE 184-75. ANY FAULTS ON THIS LINE WILL TAKE OUT 3 PHASE RECLOSURE.//EMAILED TO LLOYD RAYBURN// VER/DBM IDC XXXX
11189 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2008-09-04 10:22 | 2008-09-04 15:25 | 2 | 303 | 59234-1 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3307302//1 SPAN #2 PRIMARY DOWN& 19.9KV CUTOUT BROKEN ON POLE 177-8.WILL REQUIRE ROW CREW AND 3 MAN LINE CREW.MATERIAL NEEDED ,HAND COIL#2ACSR,19.9 CUTOUT & BRKT.//ISO 37830177D00008//.30T FUSE.// VER/DBM IDCC CNT1 XXXX
11190 | Hazard | 3310502 | HADDIX | CANOE | 2015-08-05 08:49 | 2015-08-05 13:52 | 2 | 303 | 4979851 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE BAD ON POLE 169A-369 , CLOSED LINE FUSE @ 13:52 . FUSE SIZE WAS 20T .// VER/ ADH
11191 | South Williamson | 3411401 | DEWEY | INEZ | 2012-02-24 07:52 | 2012-02-24 12:55 | 2 | 303 | 4491601 | 606 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | CONNECTION PULLED LOOSE ON SECONDARY POLE// I REWORKED ALL CONNECTIONS ON THIS POLE//RESTORED AT 12:55//COMPLETE//EM VER/HFP L3/HFP
11192 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2010-09-07 17:37 | 2010-09-07 20:59 | 3 | 202 | 64358-1 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | BAD UNDERGROUND, POWER TEMP INSTALLED M.P , JEH RELEASED BY CREW 078H12//VER/CRB IDC XXXX
11193 | Cannonsburg | 3000201 | BIG SANDY | FALLSBURG | 2009-06-11 07:48 | 2009-06-11 11:10 | 3 | 202 | 57021-1 | 606 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | REPLACED BAD CUTOUT ON POLE426-22 IDC XXXX
11194 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2010-06-22 10:05 | 2010-06-22 11:00 | 11 | 55 | 54337-1 | 605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUT OUT 10T FUSE//COMPLETE-PLEASE CLOSE-PRB VER/KEP L3/KEP IDC XXXX
11195 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2009-03-07 18:50 | 2009-03-07 19:45 | 11 | 55 | 56112-1 | 605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | BAD ARRESTER,,,BACK ON//3007904//VER/CRB IDC XXXX
11196 | Hazard | 3309302 | VICCO | JEFF | 2018-08-07 08:19 | 2018-08-07 10:20 | 5 | 121 | 4916961 | 605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout , replaced cutout restored power at 10:20..
11197 | Hazard | 3309302 | VICCO | JEFF | 2019-05-10 11:59 | 2019-05-10 14:00 | 5 | 121 | 4248841 | 605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | Pole 347A/311 bad lighting arrester changed it and cutout 347A/306 line fuse was out power ok
11198 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2009-01-13 08:45 | 2009-01-13 10:46 | 5 | 121 | 54628-1 | 605 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT GATE IS BURNED UP. I AM GOING TO TRY TO FIND A CUTOUT GATE. CREW IS ENROUTE TO HELP ME CHANGE CUTOUT//3309103//VER/CRB L3/KEP IDC XXXX
11199 | Hazard | 3308401 | BECKHAM | HINDMAN | 2008-02-03 02:29 | 2008-02-03 05:00 | 4 | 151 | 65779-1 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE # 178-101, CALLING FOR HELP VER/PDP IDCC PN102, CNT3 XXXX
11200 | Pikeville | 3402003 | KEYSER | MULLINS | 2017-01-19 07:19 | 2017-01-19 09:50 | 4 | 151 | 4310791 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50KVA TRANSFORMER CREW ENROUTEBAD 50 KVA-7200 TRANS. AT POLE 1103-213, WILL NEED MATERIAL HANDLER TO HELP CHANGE. CHANGED OUT TRANS. AND CLOSED BACK IN @0950./ ISO 38831103000213/ COD 4/ VER/BOW L3/HFP HFP
11201 | Pikeville | 3410503 | S.PIKEVILLE | HOSPITAL | 2016-12-24 07:40 | 2016-12-24 10:11 | 4 | 151 | 4233861 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ***SEE H4233861*** B PHASE L/F OPEN @48-D2-107 (4 CUSTOMERS ORIGINALLY), PATROLLING. CUT OUT BUSTED ON POLE 48-D2-682, WILL HAVE TO OPEN A AND C PHASE 37830048D20107 TO CHANGE OUT WILL KEEP TRACK OF TIMES. OPENED AAND C PHASE @0927, MADE REPAIRS AND CLOSED ALL 3 @1011./ DUPLICATE IN HOIS/ VER/BOW
11202 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-07-18 20:54 | 2013-07-19 01:56 | 2 | 302 | 4552171 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 50 KVA 19.9, CAN REPLACE WITH A 15KVA 19.9. NEED TO CUT OPEN WIRE SECONDARY LOOSE FROM TRANSFORMER. CAN USE BUCKET THIS IS THE FIRST DRIVE ON THE LEFT ABOVE WIDOES BR HOLLOW. CC 2 VER/SDB IDC XXXX
11203 | Pikeville | 3120102 | STANVILLE | TRAM | 2021-03-23 13:33 | 2021-03-23 16:04 | 4 | 151 | 4366211 | 604 | PARTIAL POWER | EQUIPMENT FAILURE | SPLICE, OH | neutral splice pulled apart causing damage in customers house, replaced splice and restored customer..
11204 | Hazard | 3311101 | STINNETT | REDBIRD | 2008-05-27 08:50 | 2008-05-27 18:54 | 1 | 604 | 51626-1 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CABLE TERMINATOR | TERMINATION IN PADMOUNT BURNT, CALLING BRUCE , FETR. SET AT 19:00//3311101, FETR. SET AT 19:00, CREW WILL HAVE TO REPLACE UNDERGROUND WIRE RELEASED BY CREW 077S08 REPLACED PRIMARY CONDUCTORS RESTORED POWETR AT 1854 VER/HFP IDCC CDC83, PN119 XXXX
11205 | Paintsville | 3401103 | FALCON | BURNINGFK | 2017-02-11 11:21 | 2017-02-11 21:25 | 1 | 604 | 4385941 | 604 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | RIGHT FUSE BLOWN ON POLE 875-359//TRIED FUSE AND CAME BACK OUT//CHECKED RISER FUSE ON POLE 875-508 AND IT WAS A BIGGER FUSE,LEFT IT OPEN AND GOING TO TRY 875-359 AGAIN//OVERHEAD STAYED IN//NEED 2 MEN//BAD UNDERGROUND ON 875-508///WE INSTALLED TEMPORARY SPAN OF WIRE TO RESTORE SERVI/// VER/DKM L3/HFP HFPC FP38830875C00359
11206 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2016-08-06 18:01 | 2016-08-06 23:03 | 2 | 302 | 4743541 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | LINE FUSE OPEN AT POLE 48-1117, HAD 2 BAD CUT-OUTS ON POLE 47-412, REPLACED THOSE AND CLOSED L/F BACK IN @2303.// MAP DISC DONE - 3-100T`S// COD = 23 // ISO POLE 37830048B11117
11207 | Paintsville | 3401802 | INDEX | HOSPITAL | 2012-03-11 19:10 | 2012-03-12 00:12 | 2 | 302 | 4570441 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA TRANSFORMER..NEED 1 MAN MATERIAL HANDLER AND XFMR..CUTOUT ARRESTOR..TRANSFORMER CHANGED OUT.. CC = 2. VER/SDB IDC XXXX
11208 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2009-01-25 21:13 | 2009-01-26 02:15 | 2 | 302 | 59809-1 | 604 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3312202// BAD TRANSFORMER ON HILL SIDE // COD-2 VER/LDA
11209 | Cannonsburg | 3001001 | HITCHINS | DENTON | 2015-03-14 08:45 | 2015-03-14 18:49 | 1 | 604 | 4192551 | 604 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | ROAD WASHED OUT NEED 6 WHEELER TO GET TO HOUSE RELEASED BY CREW 078S05/SERV END FAILED ON SERVICE DROP/WILL OPEN XFMR FOR REPAIRS/FETR1930/VEM/OPEN XFMR@1827/REPAIRS MADE AND FULL POWER RESTORED 1849/PLEASE CLOSE TICKET/THANKS/VEM/ ISO 38830256000031/ COD 1/ VER/BOW
11210 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2018-12-09 12:43 | 2018-12-09 13:50 | 9 | 67 | 4527461 | 603 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 38830070A20542 transformer fuse open. Broken fuse L3/HFP
11211 | Hazard | 3307302 | BULAN | AJAX-DWAR | 2010-10-21 07:27 | 2010-10-21 10:48 | 3 | 201 | 61517-1 | 603 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR IS OUT, BAD CSP XFMR, CALLING FOR HELP RELEASED BY CREW 077S02 REPLACED XFMR RESTORED POWER AT 1048 CREW 077H01 VER/KEP L3/KEP IDC XXXX
11212 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2011-12-01 21:54 | 2011-12-02 01:15 | 3 | 201 | 4134851 | 603 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XGMER BAD NEED CREW.LIFTED HOT TAP @ POLE 809-262@ 12:40 RESTORED @ 01:15 //VER/GAH IDC XXXX
11213 | Hazard | 3301101 | CHAVIES | CHAVIES | 2008-01-29 23:37 | 2008-01-30 09:40 | 1 | 603 | 60891-1 | 603 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, OH | CONNECTION BAD ON TRANSFORMER VER/ARN IDC XXXX
11214 | Cannonsburg | 3001201 | HOWARDCOL | 13 STREET | 2010-04-10 08:50 | 2010-04-10 09:57 | 9 | 67 | 61876-1 | 603 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | BROKEN FUSE LINK //VER/CRB IDC XXXX
11215 | Hazard | 3301101 | CHAVIES | CHAVIES | 2016-04-03 11:25 | 2016-04-03 16:26 | 2 | 301 | 4042191 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25KVA TRANSFORMER//REPAIRED BAD RED TO RED CHECKED VOLTAGE 141.5AND 281-NEXT TR OK 125/250 CALLED FOR 25 KVA 7200REPAIRED BAD RED TO RED CHECKED VOLTAGE 141.5AND 281-NEXT TR OK 125/250 CALLED FOR 25 KVA 7200 RELEASED BY CREW 077S06 RELEASED BY CREW 077H02..ALL POWER RESTORED @ 16:26 HRS P.HICKS VER/CRB
11216 | Pikeville | 3403201 | BEAVERCREEK | LIGON | 2011-11-13 00:54 | 2011-11-13 05:55 | 2 | 301 | 4070931 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | WAITING FOR MATERIAL HANDLER & FLAGGERS. NEED TO SEND ENG. DEPT A NOTE TO HAVE THIS POLE CHANGED OUT IT IS BURNED APROX 3/4 WAY IN TWO. VER/SDB IDC XXXX
11217 | Cannonsburg | 3001002 | HITCHINS | WILLARD | 2015-07-26 14:13 | 2015-07-26 19:14 | 2 | 301 | 4943901 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFR @ 424-56 NEED TO REPLACE WITH A 25 KVA ..CREW REQUIRED/// TRUCKS TO POLE///NEED FLAGGERS RELEASED BY CREW 078S05//7200 SINGLE BUSHING//CREW ON SITE/FETR2000/RM ALL POWER ON PLEASE CLOSE TIC RM VER/CRB
11218 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2017-05-20 08:09 | 2017-05-20 13:10 | 2 | 301 | 4826381 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA TRANSFORMER TALKED WITH B REYNOLDS AND SEND TICKET TO HIM RELEASED BY CREW 078S02/ ISO 38830018000107/ COD 2/ VER/BOW
11219 | Hazard | 3310503 | HADDIX | TROUBLESOME CRK | 2019-07-06 17:55 | 2019-07-06 18:38 | 14 | 43 | 4665971 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT 37830029000133 broken cutout on pole 290-133 LFOFF@ 1755 ON @ 1838 L3/HFP
11220 | Paintsville | 3403302 | PRESTONSBURG | UNIVERSITY | 2018-12-04 08:04 | 2018-12-04 09:30 | 7 | 86 | 4505881 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Transformer fuse appears to have broke. Restored @ 9:30. sh L3/HFP
11221 | Cannonsburg | 3008003 | 47TH STREET | CATLETTSBURG | 2008-03-09 03:19 | 2008-03-09 08:20 | 2 | 301 | 55590-1 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008003// BAD TRANSFORMER, NEED 50KVA // RELEASED BY CREW 078S08......REPLACED WITH 25KVA, CHECKED AMPERAGE, 50 AMPS ON ONE LEG, 71 AMPS ON THE OTHER @ 19 DEGREES ---BLR VER/JHM IDCC CDC91 XXXX
11222 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2022-03-30 19:30 | 2022-03-30 20:56 | 7 | 86 | 4692441 | 602 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | pole 70-68 rotted @ ground level and fell over, steve ray is coming to help with repairs// dig confirmation 2203301933// opened XFM @ 19:30 closed @20:56
11223 | Hazard | 3309003 | JEFF | VIPER | 2014-08-31 00:17 | 2014-08-31 10:18 | 1 | 601 | 4439731 | 601 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WILL WORK IN THE AM 8-31-14 BAD CUTOUT === NEED 1 A MAN === CUTOUT UP ON HILL ==== REPLACED CUTOUT === POWER OK VER/TOM L3/TOM
11224 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-03-30 14:42 | 2008-03-30 18:02 | 3 | 200 | 62153-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | 3310501//7200 VOLT ARRESTOR BAD ON XFMR POLE 37830128000185 - COD 3// ISO 37830128000031 // VER/TOM IDC XXXX
11225 | South Williamson | 3200202 | BARRENSHE | VULCAN | 2012-10-28 23:13 | 2012-10-28 23:53 | 15 | 40 | 4180041 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | SDB / 2313 / RECLOSERS 1115-D-8 OPENED DUE TO POLE FIRE AT POLE 1139-C-175. CC 15. SEE ORDER 4179901. ---- SDB / 2353 / RECLOSSERS AT POLE 8 CLOSED.. VER/SDB IDC XXXX
11226 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2008-02-06 16:00 | 2008-02-06 21:00 | 2 | 300 | 51663-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O DOOR BROKE WILL REPLACE CUTOUT ON XFMER POLE............CPS POLE 185-21 BAD 15KVA XFMER NO TRUCK NEED LINE CREW RELEASED BY CREW 078E04 VER/HFP IDC XXXX
11227 | Cannonsburg | 3000202 | BIG SANDY | BURNAUG-North | 2019-02-27 16:30 | 2019-02-27 16:45 | 40 | 15 | 4933921 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | repairing down neut across rd---open SB on PL# 38830285000020 to safely pull up neutral---minimal outage less than 30 min---OPENED @ 1630 CLOSED @ 1645//NO OUTAGE TILL SW OPENED
11228 | Pikeville | 3402002 | KEYSER | STONECOAL | 2008-06-04 13:13 | 2008-06-04 16:33 | 3 | 200 | 56175-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3402002//PART POWER ON SIDE OF TRANSFORMER, WILL NEED A TREE CREW TO RIDE-AWAY RELEASED BY CREW 074S05//COD 3// VER/DBM
11229 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2014-03-17 14:01 | 2014-03-17 14:11 | 60 | 10 | 4502661 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | LINE FUSE OPENED WHEN CREW REPLACING CUT OUT//,REPLACED ARRESTER LINE FUSE IN @ 1411 ALL CUST RESTORED PLEASE CLOSE TICKET THANKS.BT VER/SEF L3/HFP IDC XXXX
11230 | Paintsville | 3410601 | E.PRESTON | PRESTONSBURG | 2012-03-25 07:05 | 2012-03-25 09:05 | 5 | 120 | 4614971 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN IN XFMR FUSE. RE-FUSED @ 9:05. SH //VER/CRB IDC XXXX
11231 | Cannonsburg | 3000902 | HIGHLAND | FLATWOODS | 2008-06-03 17:43 | 2008-06-03 21:03 | 3 | 200 | 55252-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3000902//BAD CUTOUT ON POLE 1123-4056 REPLACED CUTOUT RELEASED BY CREW 078S11//VER/CRB IDC XXXX
11232 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2021-01-01 07:15 | 2021-01-01 10:35 | 3 | 200 | 4840111 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | Old 6 solid copper open-wire secondary and neutral down. Eliminated span of #6 sol open wire to 809-55, repaired primary neutral conductor and restored xfmr @ 10:35. sh
11233 | Hazard | 3309901 | SLEMP | DEFEATED CREEK | 2009-09-26 10:29 | 2009-09-26 12:29 | 5 | 120 | 63680-1 | 600 | TRANSMISSION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | LOST TRANSMISSION LINE CREWS WORKING TO RESTORE VER/KEP L3/KEP IDC XXXX
11234 | Hazard | 3309001 | JEFF | BOONE LEDGE | 2022-05-06 20:40 | 2022-05-06 23:10 | 4 | 150 | 4854121 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Broke xfmr cut out on pole 321C-253, blowed line fuse on 351C-251. Power restored.
11235 | Paintsville | 3401103 | FALCON | BURNINGFK | 2022-05-16 07:30 | 2022-05-16 10:00 | 4 | 150 | 4894991 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken line fuse cutout. changing
11236 | Cannonsburg | 3116102 | GRAYSON | DIXIEPARK | 2012-10-11 13:30 | 2012-10-11 15:30 | 5 | 120 | 4132181 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT DOOR BURNT IN HALF,, REPLACED DOOR, ALL POWER RESTORED VER/KEP IDC XXXX
11237 | Pikeville | 3402204 | MCKINNEY | MAYTOWN | 2013-04-24 19:10 | 2013-04-24 21:40 | 4 | 150 | 4045621 | 600 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | RELEASED BY CREW 074H08 PART POWER DUE TO BAD CONNECTION BURNT INTO REPLACEDED CONNECTIONS EVERYTHING OK// VER/DBM IDC XXXX
11238 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2010-03-29 09:35 | 2010-03-29 12:05 | 4 | 150 | 55421-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | POLE 37830248A00750 BURNED INTO AT TOP 7200 CUTOUT BAD OPENED LOOP AT POLE 37830248A00458 AT 09:35 SEND TO SHOUSE CREW RELEASED BY CREW 077S04 VER/KEP L3/KEP AJB CALL WAS TO REPORT TROUBLE ONLY
11239 | Hazard | 3310501 | HADDIX | QUICKSAND | 2008-11-04 11:31 | 2008-11-04 11:46 | 40 | 15 | 62083-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | VER/HFP CREW OPENED GOAB SWITCH ON POLE 1061-59 TO ALLOW CREW TO MAKE UP LOOPS AFTER REPAIRS MADE IN ORDER 61951-1 IDC XXXX
11240 | Cannonsburg | 3002002 | S.SHORE | DISTRIBUTION | 2012-12-05 18:52 | 2012-12-05 20:52 | 5 | 120 | 4445791 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND LINE FUSE OUT ON POLE 901-4541, PATROLLED FOUND LINE FUSE CUTOUT TO BE BAD, I HAVE IT CHANGED OUT AND POWER IS RESTORED AT THIS LOC AT 2052 COD-5 ISO LF 39830901C24541 VER/HFP L3/HFP IDC XXXX
11241 | South Williamson | 2150502 | BORDERLAND STA | CHATTAROY | 2017-05-27 18:53 | 2017-05-27 20:53 | 5 | 120 | 4872331 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | LINE FUSE IS BLOWN AT POLE 38820917C00103, PATROLLING THE LINE. BAD 15 KVA 7200. CAN USE BUCKET TRUCK TO CHANGE THE TRANSFORMER. I GOT THE REST OF THE CUSTOMERS 38820917C00103 BACK ON AT 20:53 (5 CUST). TRANSFORMER REPLACED AND BACK ON AT 00:25 ON THE 28TH. RELEASED BY CREW 079S02/ VER/BOW
11242 | South Williamson | 2150105 | SPRIGG | MATEWAN | 2014-03-13 12:10 | 2014-03-13 15:30 | 3 | 200 | H4488941 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELATED TO ORDER 4486601 // CREW REPLACING BURNT OFF 60` POLE // OPENED RECLOSER ON POLE 37820098B00572 @ 1210 4 CUST THEN OPENED NEWLY INSTALLED SWS ON POLE 37820098B00024 @ 1220 7 CUST // DALE HAS KENNY BROOM & DEWEY AKERS CREWS WITH HIM // CLOSED SW @ 1527 & RECL @ 1530 THIS IS RECL RECORD VER/HFP L3/HFP
11243 | Cannonsburg | 3008001 | 47TH STREET | 49 TH STREET | 2013-07-16 09:15 | 2013-07-16 11:15 | 5 | 120 | 4528361 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 70-640 BAD TRANS. NEED 25KVA FLAGGING NEEDED TRUCK TO POLE OPENED TRANS. 9:15 RELEASED BY CREW 078S08,, CREW ON SITE, REPLACED XFMR, ALL POWER RESTORED AT 11:15 VER/CRB L/3 CRB IDCC PN NULL, CNT3 XXXX
11244 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2008-04-11 18:59 | 2008-04-11 23:59 | 2 | 300 | 50033-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3008702 BAD 25 KVA TRANSFORMER...NEED 6 WHEELER FOR ACCESS DIFFICULT LOCATION//VER/CRB IDC XXXX
11245 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2019-06-17 18:50 | 2019-06-17 20:30 | 6 | 100 | 4529831 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | cutout failed will change.complted
11246 | South Williamson | 3411401 | DEWEY | INEZ | 2009-01-18 11:18 | 2009-01-18 16:18 | 2 | 300 | 58038-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | VER/HFP COD- 2 (PLUS 1 MISS MAPPED CUST - ENTERED MD) WR # 28107400 15KVA CSP TRANSF BAD ON POLE 696-A-86 L3/HFP
11247 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2014-10-29 08:19 | 2014-10-29 11:39 | 3 | 200 | 4670141 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE, 7.2 KV, TRUCK ACCESIBLE RELEASED BY CREW 077S02 CHANGED CUTOUT AND RESTORED POWER AT 1139 VER/CRB
11248 | Cannonsburg | 3001202 | HOWARDCOL | 29 STREET | 2018-02-25 15:55 | 2018-02-25 19:15 | 3 | 200 | 4882171 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | pole 38830069A31261 cutout on arm, top of cutout burned in clear. truck to pole. cutouts changed, power restored at 19:15
11249 | Pikeville | 3408402 | KIMPER | GRAPEVINE | 2020-03-27 22:08 | 2020-03-28 03:08 | 2 | 300 | 4517891 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR MUST BE OPEN INSIDE,FUSE WASNT BLOWN BUT HAVE NO SEC VOLTAGE,NEED A 50KVA7.2.MAY HAVE TO WINCH IT UP,MAYBE/lifted tap at 4-19 to iso/XFR MUST BE OPEN INSIDE,FUSE WASNT BLOWN BUT HAVE NO SEC VOLTAGE,NEED A 50KVA7.2.MAY HAVE TO WINCH IT UP,MAYBE//////////REPLACED XFR&RESTORED POWER/////////NOTE,XFR ACTUALLY ON POLE 4-22737820004000227 cod 2
11250 | South Williamson | 3200301 | BELFRY | BELFRY | 2015-04-20 13:37 | 2015-04-20 15:17 | 6 | 100 | 4339551 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | ******HOLD ORDER REQUIRED********B PHASE CUTOUT HAS A CRACK IN IT AND HAS BURNED THE END OF THE ARM OFF, THE HOT TAP ON THE TRANSFORMER CUTOUT IS ALL THAT IS HOLDING THE CONDUTOR UP. JOEY REED IS EN ROUTE TO REPLACE THE ARM. THIS WILL REQUIRE AN OUTAGE WHEN REPAIRS ARE MADE. LOAD TRANSFERED VER/KEP
11251 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2008-11-03 19:00 | 2008-11-03 19:50 | 12 | 50 | 61865-1 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 27103059 -- TR POLE 388300292B00035 COD-12 // 6000 US HW 60, HAVE TO GO TO NEXT HOUSE TO GET THERE THOUGH//OPENED XFRMR @ 1900 AND CLOSED BACK @ 1950//COD 12// VER/DBM IDC XXXX
11252 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2019-06-13 08:11 | 2019-06-13 13:11 | 2 | 300 | 4492361 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | crew requird bad 10kva need 25 with new risers/trucks ok Released by crew 078S03/arrived RM xfm in @13:11 please close tic RM
11253 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2016-01-18 20:43 | 2016-01-19 01:43 | 2 | 300 | 4629951 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA SINGLE BUSHING 7200V 120/240, CREW REQ, THINK YOU CAN GE TRUCK TO THIS, IN PASTURE FIELD, GATE IS NEXT HOUSE UP FROM THIS LOC, FOREMAN MAY WANT TO MAKE THE CALL, RELEASED BY CREW 078S06//1031 ADDRESS TO TURN @/CREW ON SITE/FETR0145/VEM/REPAIRS COMPLETE/POWER RESTORED TO ALL CUST 0143/PLEASE CLOSE TICKET/THANKS/VEM VER/CRB
11254 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2018-05-07 15:25 | 2018-05-07 17:55 | 4 | 150 | 4320961 | 600 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | no crew required replaced cutout
11255 | Pikeville | 3410501 | S.PIKEVILLE | PIKEVILLE | 2013-11-11 10:05 | 2013-11-11 15:09 | 2 | 304 | 4027721 | 599 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | CUST. HAS 1 PHASE OUT// CUST WANTS TO WAIT UNTIL 2:00 TO TAKE POWER OFF// REWORKED SER /// POWER IS RESTORED VER/ARN
11256 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2017-04-30 23:06 | 2017-05-01 09:05 | 1 | 599 | 4699711 | 599 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | WILL HAVE SERVICER CHECK AT START OF SHIFT 5/1/17. BAD SECONDARY CONNECTION ON POLE 187-016. REPAIRS MADE TICKET COMPLETE. VER/CRB L3/HFP XXXHFP
11257 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2010-07-01 10:02 | 2010-07-01 20:00 | 1 | 598 | 61209-1 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 15KVA CSP TRUCKS OK 1 CUSTOMER WILL NEED CUTOUT / WR# 35815776 RELEASED BY CREW 078H01//ON SITE REPLACING 2/3 SERV (60FT)AND SECONDARY (100FT) P R TOLLIVER//COMPLETE P R TOLLIVER//COD 1// VER/DBM IDC XXXX
11258 | South Williamson | 3411401 | DEWEY | INEZ | 2015-07-15 10:32 | 2015-07-15 20:30 | 1 | 598 | 4874861 | 598 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | HOT LEG RUBBED INTO ON CUSTOMERS SERVICE DROP GOING THROUGH TREE//REPAIRS MADE//RESTORED TO NORMAL AT 20:30//COMPLETE//EM
11259 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-06-20 09:17 | 2011-06-20 19:15 | 1 | 598 | 4350231 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | NEEDS REFUSED PER JAMES AMUBURGEY - GLEN COMBS --- REPLACED BAD CUTOUT GATE, --- POWER RESTORED. IDCC PN696 XXXX
11260 | Cannonsburg | 3000801 | HAYWARD | HALDEMAN | 2014-11-17 15:47 | 2014-11-18 01:45 | 1 | 598 | 4737241 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | POLE | BROKEN POLE 317-21 40/5 NEED CREW TRUCKS OK/INLINE POLE PICTURES TAKEN DAMAGE TO TRACTOR/UP THOMAS CEM RD /GROUNDED TAGEED TO REYNOLDS AND ISOLATED RELEASED BY CREW 078S03//COD 1// VER/DBM
11261 | Paintsville | 3400101 | ALLEN | DISTRIBUTION | 2018-05-05 09:54 | 2018-05-05 19:52 | 1 | 598 | 4309891 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 2 50 KVA XFRS FAULTED.IN A 3PHASE WYE/DELTA BANK.2 BUSHING XFRSMAY NEED CUTOUTS&ARRESTORS ALSO.HAD TO OPEN FUSES@1027-89 TO ISOLATE PROBLEM Released by crew 074S06 confr. 1805050076 for digs 45 4 brunt canged out closed in at 1952
11262 | Cannonsburg | 3007904 | BUSSEYVILLE STA. | TORCHLITE | 2008-04-24 13:01 | 2008-04-24 13:25 | 83 | 24 | 53844-1 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3007904//OPENED REC 619-3 SO CREW COULD LIFT HOT TAP AND SAFELY REPLACE CUTOUT//VER/CRB IDC XXXX
11263 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2020-06-18 08:51 | 2020-06-18 13:50 | 2 | 299 | 4040241 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Center xfmr fuse of bank was blown. Checked xfmr and it is bad opened remaing 2 xfmrs @10:50. Will need 50kva 120/208 and big bucket to replace.. Released by crew 076S03
11264 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2017-06-04 08:28 | 2017-06-04 13:27 | 2 | 299 | 4903371 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | POLE 164-36 TRANS. OUT AGAIN NEEDS SEC. INSTALLED TRANS ON POLE 164-211 CHGED TO 37.5 TRUCK TO POLE 164-211 NO TRUCK TO POLE 164-36 RELEASED BY CREW 078S08/CREW ON SITE/FETR 1400/VEM/ALL CUST RESTORED 1327/PLEASE CLOSE TICKET/THANKS/VEM 38830164B00036 VER/AWD
11265 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2020-02-16 18:39 | 2020-02-16 23:38 | 2 | 299 | 4410431 | 598 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25 kva xfmr, need two men material handlerand flaggers Released by crew 077S12.. transformer changed. power restored @ 23:38 L3/HFP
11266 | Pikeville | 3402002 | KEYSER | STONECOAL | 2012-04-21 20:21 | 2012-04-21 23:40 | 3 | 199 | 4693341 | 597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | JUMPER/RISER | APPEARS WE HAVE ONE PHASE OUT TO METERING.PATROLING.FOUND STIRRUP BURNT OFF RIGHT HAND PHASE ON POLE 38821129C00272.POLE IS ON SIDE OF THE HILL & PAUL LAYNE IS COMMING TO ASSIST.REPLACED STIRRUP AND POWER RESTORED // ONLY 1 THREE PHASE CUSTOMER AFFECTED IDCC CNT7, PN19 XXXX
11267 | Hazard | 3308002 | JACKSON | PANBOWL | 2020-12-30 18:11 | 2020-12-30 21:30 | 3 | 199 | 4836901 | 597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 50kva 7200, need mud boards to get to pole Released by crew 077S05 power restored at 21 :30
11268 | Pikeville | 3400101 | ALLEN | DISTRIBUTION | 2009-03-13 07:31 | 2009-03-13 10:50 | 3 | 199 | 57899-1 | 597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | RELEASED BY CREW 074S04REFUSED XFMR POWER BACK ON - FUSE BROKE - MAP DISC ISSUED FOR MISMAPPED CUSTOMER ON TRANSFORMER POLE # 93B-234 // VER/TOM L3/TOM IDC XXXX
11269 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2020-09-12 17:35 | 2020-09-12 20:54 | 3 | 199 | 4455151 | 597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | INSULATOR | SEC WIRE,#4COPPER BURNED DOWN MIDSPAN.NEED #4COPPER,1MAN,BUCKET.XFR 1136-1 FUSE IS BLOWN,2 CUSTS OUT IT APPEARS////////MADE REPAIRS&RESTORED@08:54/////////SECONDARY SPACER HAD BROKEN
11270 | Hazard | 3301402 | COMBS | AIRPORTGARDEN | 2017-02-09 06:30 | 2017-02-09 09:49 | 3 | 199 | 4374991 | 597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT/ ISO 37830248A00458/ COD 3 NEED 1 MAN AND BIG BUCKET === CALLED FOR 1 MAN & BUCKET ===CHANGED CUTOUT === POWER OK/ 37830248A00458/ COD 3/ VER/BOW L3/HFP XXXHFP
11271 | Paintsville | 3401103 | FALCON | BURNINGFK | 2015-01-26 07:56 | 2015-01-26 11:15 | 3 | 199 | 4963951 | 597 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KVA XFMR.CALLED TIM MILLER ,,HE WILL CHANGE. RELEASED BY CREW 076S01//CREW ON SITE TCM/ REPLACED PHASE C CAN CHECKED VOLTAGE BACK ON TCM// ISO 38830875C00012/ COD 3/ MAP SHOWS A PHASE/ VER/BOW
11272 | Pikeville | 3400602 | BURTON | WHEELWRIG | 2016-09-21 11:19 | 2016-09-21 13:48 | 4 | 149 | 4914641 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE OUT DUE TO FUSE BEING BROKEN REPLACED 6T FUSE EVERYTHING OK COD-1 ISO TF 37830211D00030 VER/HFP L3/HFP
11273 | Hazard | 3310502 | HADDIX | CANOE | 2016-12-16 17:03 | 2016-12-16 22:01 | 2 | 298 | 4201611 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15 KV TRANSFORMER 72 KV, ALSO NEED 72KV CUTOUT. NEED 2 MAN LINE CREW WITH SMALL BUCKET/ ISO 37830169C00034/ COD 2/ VER/BOW
11274 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2014-10-08 15:26 | 2014-10-08 20:24 | 2 | 298 | 4575171 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 40T MIDDLE FUSE BROKE/// 40T FUSE BROKE// REFUSED// ISO 38830761000157// COD 2// VER/BOW
11275 | Pikeville | 3402202 | MCKINNEY | GIBSON | 2016-07-21 11:58 | 2016-07-21 14:27 | 4 | 149 | 4663641 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | #4 COPPER DOWN CALLING TIM MILLER NOW.FUSE BLOWN ON POLE 42-71 CREW IS HERE MAKING REPAIRS VER/CRB
11276 | Whitesburg | 3308603 | COLLIER | SMOOTCRK | 2011-01-01 18:05 | 2011-01-01 20:34 | 4 | 149 | 57819-1 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CROSSARM | STS WR 38259248 //CROSSARM BRACE BROKE ALLOWING ARM TO MAKE CONTACT WITH CUTOUT WILL HAVE TO REPLACE BRACECROSSARM BRACE BROKE ALLOWING ARM TO MAKE CONTACT WITH CUTOUT WILL HAVE TO REPLACE BRACE... MADE REPAIRS RESTORED POWER AT 20:34 VER/ARN IDC DCMT XXXX
11277 | South Williamson | 3408304 | COLEMAN | CALLOWAY | 2020-05-24 12:50 | 2020-05-24 17:48 | 2 | 298 | 4896461 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 7.2 xfr,needs to be replaced.no access with truck.also some leakage on xfr&on the grnd under xfr///////////REPLACED XFR,RESTORED POWER
11278 | South Williamson | 3200302 | BELFRY | TOLER | 2021-02-08 10:47 | 2021-02-08 15:45 | 2 | 298 | 4948961 | 596 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25KVA 7200 XFM will be getting a crew to change it out// customers are restored
11279 | Cannonsburg | 3116702 | BELHAVEN STATION | INDIAN RUN | 2016-10-06 13:14 | 2016-10-06 18:12 | 2 | 298 | 4964461 | 596 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | CALLED CREW BAD UNDERGROUND SEND TO CREW RELEASED BY CREW 078S08,PLACED 2 POWER TEMPS SEND COPY TO BRENT TACKETT .BT SENT TO B TACKETT/AWD VER/AWD L3/HFP HFPC CDC91 FP
11280 | South Williamson | 3411401 | DEWEY | INEZ | 2018-02-02 12:55 | 2018-02-02 13:30 | 17 | 35 | 4794781 | 595 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | OPENED L/F 38820770A30275 TO REPLACE BAD TRANSFORMER CUTOUT ON POLE 38820770A00036//@ 1255//cutout broke on 770-36//opened line fuse 770-275 at 12:55 to make repairs//repairs made restored at 13:30//complete//em
11281 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2015-03-27 00:24 | 2015-03-27 10:18 | 1 | 594 | 4233281 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD TRANSFORMER CUTOUT AT POLE 38821137D00650, TAP FUSE 38821137D00384 BACK ON THE MOUNTAIN IS ALSO BLOWN. CAN GET TRUCK TO THE BAD CUTOUT. WILL WORK AT DAYLIGHT/COD 1// VER/ ADH
11282 | Cannonsburg | 3116703 | BELHAVEN STATION | ARGILLITE ROAD | 2017-11-23 18:47 | 2017-11-23 22:05 | 3 | 198 | 4598471 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | called customer: no answer-bad number..pole 19-41 bad 12 kv c/o, truck ok Released by crew 078S07/on site RM power on at 22:05 please close tic RM//cod 3
11283 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2015-07-09 01:05 | 2015-07-09 02:44 | 6 | 99 | 4748651 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BOBBY OPENING LINE FUSE TO SAFELY REPLACE XMER OPENED AT 0105 AND CLOSED AT 0244 VER/SEF
11284 | Cannonsburg | 3000303 | BELLEFONT | BELLEFONT | 2009-07-04 12:02 | 2009-07-04 13:41 | 6 | 99 | 64623-1 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | E MAIL TO RAYBURN--BAD ARRESTOR NEEDS REPLACED--NO BASKET ON PRIMARY AN HOTTAP IS FROZE UP//COD 6// VER/DBM IDC XXXX
11285 | Pikeville | 3411801 | JOHNSCREEK | META | 2014-12-12 09:21 | 2014-12-12 11:00 | 6 | 99 | 4856121 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WILL CHECK FOR PROBLEMS////////FOUND FROZEN-OUT SERVE-IN CONNECTION,MADE NECESSARY REPAIRS,ALL OK AFTERWARDS// ON 1100/COD6// VER/ ADH
11286 | Hazard | 3309902 | SLEMP | LEATHERWOOD | 2017-02-13 16:57 | 2017-02-13 20:15 | 3 | 198 | 4394701 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA 19.9/ ISO 37830511000023/ COD 3/ VER/BOW L3/HFP XXXHFP
11287 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2011-06-05 19:42 | 2011-06-05 23:00 | 3 | 198 | 4238071 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CSP XFMR MAY HAVE OPEN UP//XFMR BAD CALL T. MCCOY CREW ENROUTE THIS IS A 25 KVA// NO TRUCK//XFMR CHANGED AND BACK TO NORMAL VER/TOM L3/TOM IDC XXXX
11288 | Paintsville | 3409001 | W.PAINTSVILLE | PAINTSVIL | 2014-04-15 20:21 | 2014-04-15 21:15 | 11 | 54 | 4609551 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK APPEARS TO HAVE BROKEN. WILL TRY TO RE-FUSE 50 KVA ON 785-765. RESTORED @ 21:15. SH //VER/GAH IDC XXXX
11289 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2014-06-24 22:05 | 2014-06-25 03:02 | 2 | 297 | 4150961 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANDFORMER FUSE BLOWN WILL RE-FUSE/// BAD TRANSFORMER NEED 15 KVA 7200 TRUCK ACCESSIBLE//// SEND TO TIM MCCOY RELEASED BY CREW 074H17/// ON SITE WAITING ON CREW//CHANGED BAD TRANSFORMER AND RESTORED POWER AT 03:02// RESTORED LINE FUSE AT THE SAME TIME. TIM MCCOY RELEASED BY CREW 074H10 VER/KEP
11290 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2010-04-13 14:41 | 2010-04-13 16:20 | 6 | 99 | 62821-1 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | HOT-LINE-CLAMP BURNT OFF ON 760-114. MILLER EN-ROUTE TO ASSIST WITH REPAIRS.//ISO//COD 6// VER/DBM IDC XXXX
11291 | Pikeville | 3421001 | BREAKS | CITY | 2015-05-02 10:18 | 2015-05-02 15:15 | 2 | 297 | 4383701 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | INSTALLED NEW CONNECTORS AT TRANSFORMER POLE , ALL WORK COMPLETE / GXJ VER/CRB
11292 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2008-01-21 00:51 | 2008-01-21 05:48 | 2 | 297 | 58167-1 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3411802///CALLING FOR ONE MAN TO BRING TRANSFORMER, TRUCK ACCESIBLE/VER/CRB IDC XXXX
11293 | Cannonsburg | 3000802 | HAYWARD | LAWTON | 2015-09-04 12:05 | 2015-09-04 12:14 | 66 | 9 | 4197551 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON PL 296-28---OPENED OCR ON PL272-40 @ 12:05----REPAIRED CUTOUT AND CLOSED OCR @ 12:14---TBL TKT COMP VER/CRB L3/DKG AJB
11294 | South Williamson | 3200302 | BELFRY | TOLER | 2017-06-02 18:22 | 2017-06-02 21:40 | 3 | 198 | 4899671 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | TRANS FUSE FAILED DUE TO AGE I THINK RE-FUSED CUTOUT RESTORED POWER AT 21:40/ ISO 38820990C40228/ COD 3/ VER/BOW
11295 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2009-02-20 04:23 | 2009-02-20 09:20 | 2 | 297 | H65795-1 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | VER/HFP COD-7 OPEN WIRE SECONDARY DOWN--OPENED TRANSFORMER AT 08:01--CALLING CREW--#2 CU SECONDARY--NEED 4/0 RISERS FOR 50 KVA TRANSFORMER--B FRALEY TO WORK RELEASED BY CREW 078S07 L3/HFP IDCC DUP FOR FIRST 2 CUSTOMER OUT WITH PART POWER XXXX
11296 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2014-01-24 05:57 | 2014-01-24 09:15 | 3 | 198 | 4305901 | 594 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XFORMER 7200, NEED LINE CREW . TRUCKS OK. RELEASED BY CREW 078S01 COD-3 VER/HFP L3/HFP
11297 | Pikeville | 3402001 | KEYSER | THOMPSON RD | 2008-11-24 05:07 | 2008-11-24 15:00 | 1 | 593 | 51459-1 | 593 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | 3402001//WR#27414936 REPLACED 3PHASE U.G. PRIMARY AND TERMINATIONS ON POLE AND IN TRANSFORMER ON AT 15:00 //VER/CRB IDC XXXX
11298 | Pikeville | 3413401 | GARRETT | GARRETT | 2020-07-13 09:06 | 2020-07-13 10:20 | 8 | 74 | 4158221 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 20t fuse out pole 16-c-375. broken cutout. will be making repairs.replaced cutout closed 20t line fuse on pole16-c-375@ 10:20 everything ok
11299 | Cannonsburg | 3000203 | BIG SANDY | YATESVILLE | 2022-06-15 05:44 | 2022-06-15 10:40 | 2 | 296 | 4121171 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke cutout replaced
11300 | Whitesburg | 3308602 | COLLIER | LOWERROCK | 2010-04-17 03:33 | 2010-04-17 13:25 | 1 | 592 | 64251-1 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT MANUAL JOB//COD 1// VER/DBM IDC XXXX
11301 | Paintsville | 3401103 | FALCON | BURNINGFK | 2010-11-09 07:34 | 2010-11-09 12:30 | 2 | 296 | 54182-1 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE LINK BROKE. RE-FUSED @ 12:30. SH// COD 2// VER/DBM L3/ JKW IDC XXXX
11302 | Cannonsburg | 3001401 | LOUISA | CITY | 2008-12-11 09:19 | 2008-12-11 10:33 | 8 | 74 | 56588-1 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3001401//BROKE CUTOUT,,,,,,I REPLACED POWER RESTORED//VER/CRB L3/IDC IDC XXXX
11303 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2019-07-05 00:12 | 2019-07-05 10:04 | 1 | 592 | 4657571 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | bad cutout, replaced cutout restored power at 10:04..
11304 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2008-02-28 09:22 | 2008-02-28 11:50 | 4 | 148 | 51187-1 | 592 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | FAILED CONNECTION AT THE TRANSFORMER ON ONE HOT LEG. I REPLACED THE CONNECTION. TRANSFORME WAS OUT ON POLE 241-227 NOT LINE FUSE...TR ON POLE 241-C-101 IS ON THE LOAD SIDE OF FUSE ON THAT POLE ....TURNED IN MAP DES REPT...HFP VER/HFP IDCC PN101 XXXX
11305 | Pikeville | 3411902 | FORDSBRANCH | ROBINSONC | 2021-11-20 01:26 | 2021-11-20 02:40 | 8 | 74 | 4110071 | 592 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | Trans fuse open at 143-C-10,Going to refuse and Try it..Had a broke fuse got it changed and restored at 02:40../ ISO 37830143C00010/ COD 8
11306 | Cannonsburg | 3002107 | 10TH STREET | WEST CENTRAL | 2010-09-04 12:44 | 2010-09-04 17:40 | 2 | 296 | 63600-1 | 592 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | WR# 36751640 // BAD UNDERGROUND SEC. 2-CUST OUT RELEASED BY CREW 078S08/HAVING TO REPLACE 80 FT. OF UNDERGROUND SEC./ CORRECTION LOCATED FAULT, SPLICED UNDG. ALL CUST. RESTORED @ 17:40 J. HEMLEPP// VER/DBM IDC XXXX
11307 | South Williamson | 3201001 | TOMWATKIN | DISTRIBUTION | 2018-09-28 10:25 | 2018-09-28 15:04 | 5 | 279 | 4177181 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CALLED CUST REPORTED CUTOUT CAUGHT ON FIRE AND FELL IN YARD // FUSE & XFMR OUT ON POLE 38821086B00189
11308 | South Williamson | 3411401 | DEWEY | INEZ | 2012-07-17 08:36 | 2012-07-17 11:53 | 3 | 197 | 4746001 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | SPLICE, UG | <<ONLY ONE CUSTOMER AFFECTED>> SPLICE IN UG SERVICE HEATED UP AND BURNT UG NEUTRAL OPEN. FAULT IS JUST DOWN IN TOP OF CONDUIT - REPAIRING. REPAIRED AND RESTORED @ 11:48. SH
11309 | Cannonsburg | 3117603 | PRINCESS | MIDLAND TRAIL | 2020-06-11 17:52 | 2020-06-11 21:09 | 3 | 197 | 4007361 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | OTHER EQUIPMENT | door burnt up, crew reqd. no bucket, to close to do alone. may have to lift hot tap on pole 16B572 to safely make repairs. Released by crew 078S04, deenergized at 20:22 power restored 21:09 Released by crew 078Q12
11310 | Cannonsburg | 3002001 | S.SHORE | SILOAM | 2015-11-20 08:40 | 2015-11-20 11:57 | 3 | 197 | H4473221 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | PRIMARY PULLED OUT OF SLEEVE AT POLE 936-12 (30 CUST)//LAYING ON GROUND BURNING//OPENED SWITCH AT 936-8 TO ISOLATE///LINE CREW ENROUTE///REPAIRS MADE//RESTORED AT 11:57//COMPLETE//EM/ OPENED SWITCH AT 0840 38830936C00008 (3 CUST)/ ISO 38830936C00008/ COD 33/ DUPLICATE IN HOIS/ VER/BOW
11311 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2008-08-31 18:26 | 2008-08-31 21:43 | 3 | 197 | 58082-1 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 26041119 CREW REQUIRED BAD 10 KVA TRUCKS OK SEND TO JIM LINKOUS/TURN AT THE OLD RAYBOURN STORE OFF EMERSON GO UP THE OLD CREEK BED RELEASED BY CREW 078S03 VER/PDP IDC XXXX
11312 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2017-01-17 06:23 | 2017-01-17 09:40 | 3 | 197 | 4304331 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT BIG BUCKET ENROUTE VER/CRB L3/HFP HFP
11313 | Pikeville | 3411802 | JOHNSCREEK | RACCOON | 2009-10-28 11:55 | 2009-10-28 15:12 | 3 | 197 | 62489-1 | 591 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP TOP OF POLE BURNT INT0, POLE 1106-90, CUT LOOP ON POLE 1106-80 AND SQUEEZE HOT TAP ON WIRE. 1ST ROAD ON LEFT AFTER YOU PAST LEE ST . L3/HFP IDC I DONT THINK THIS IS CORRECT BUT I DO NOT KNOW HOW TO FIX IT XXXX
11314 | Cannonsburg | 3007906 | BUSSEYVILLE | WALBRIDGE | 2016-09-24 13:59 | 2016-09-24 18:54 | 2 | 295 | 4923081 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | C/O FAILED--REPLACED-18:54--ALLGOOD VER/KEP
11315 | Hazard | 3303902 | LESLIE | WOOTON | 2010-11-07 10:05 | 2010-11-07 15:00 | 2 | 295 | 53671-1 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BROKE//VER/CRB IDC CUTOUT ON HILL CALLED TWO MEN TO HELP WITH REPAIRS XXXX
11316 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2011-08-25 11:57 | 2011-08-25 13:55 | 5 | 118 | 4755501 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT PL#1073/2036---CREW REQ.---TRUCK TO POLE---CHANGE ALL 3 CUTOUTS WHILE HERE--CHANGED 3CUTOUTS---XFMR BANK PL#1073/2035 OFF @ 13:40 TO 13:55 VER/KEP IDC XXXX
11317 | Pikeville | 3400301 | BETSYLAYN | MUDCREEK | 2015-03-14 19:16 | 2015-03-14 20:15 | 10 | 59 | 4194461 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT ON POLE 1076-144 CAUSING POLE TO CATCH FIRE // POLE IS BURNED OVER HALF IN TWO // I OPENED L/F ON POLE 1076-20 // CREW ENROUTE// POWER RESTORED @ 20:15/ ISO 38831076000020/ COD 10/ VER/BOW AJBC TOF1701 INLT CUST CALLS TO REPORT TROUBLE ONLY.
11318 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2014-06-27 08:46 | 2014-06-27 09:45 | 10 | 59 | 4161541 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | PART OF 4161401//ARRESTOR HANGING DOWN AND CUTOUT BAD//SERVICER OPENED THIS LINE FUSE AT 0845 TO MAKE REPAIRS//COD 10// VER/DBM
11319 | Whitesburg | 3401302 | FLEMING | MCROBERTS | 2011-06-23 15:47 | 2011-06-23 17:45 | 5 | 118 | 4401011 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | RELEASED BY CREW 075H01CUTOUT GATE BURNED UP, I CHANGED GATE , POWER BACK ON COD-5 ISO TF 37830333A00069 VER/HFP L3/HFP IDC XXXX
11320 | Cannonsburg | 3116701 | BELHAVEN STATION | Diederich | 2010-06-22 12:14 | 2010-06-22 22:04 | 1 | 590 | 54513-1 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUT-OUT HAS FAIL BURNING POLE 1148-557 LINE FUSE OPENED AT POLE 1148-B-84,DEAD-END NEW STAND-OFF BRACKET AND CUT-OUT ,40-5 PO LE FOREIGN BELONGS TO WINDSTEAM COMM. CREW REQ 1 CUST OUT RELEASED BY CREW 078S09. //VER/GAH IDCCFEC60 XXXX
11321 | Pikeville | 3400302 | BETSYLAYN | TRAM12KV | 2011-09-04 19:22 | 2011-09-04 21:20 | 5 | 118 | 4810841 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER ARCING AND NO POWER OR PHONES HERE PER BOB SHURTLEFF //BAD CUTOUT ON 38831078000029// WILL CHANGE OUT//CHANGED CUTOUT// POWER IS RESTORED//COD 5// VER/DBM IDC XXXX
11322 | Hazard | 3308401 | BECKHAM | HINDMAN | 2009-06-22 20:46 | 2009-06-23 01:41 | 2 | 295 | 63467-1 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308401//@ 21:07 DDC CALLED DUTY SUPERVISOR TO FIND SERVICER FOR THIS TROUBLE// CSP OUT GOING TO TRY//BAD CSP//CREW REQUIRED//COD 2//STS WR # 30413156// COMP. 6/23/09 W.MELTON IDC XXXX
11323 | Hazard | 3308502 | BONNYMAN | HAZARD | 2015-03-19 17:51 | 2015-03-19 19:49 | 5 | 118 | 4210681 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | MIGHT HAVE BAD C/O ON POLE 200-B-154/// BAD C/O WILL CHANGE./// CHANGED OUT XFMR C/O. POWER RESTORED// VER/ ADH L3/DKGXXXX
11324 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2016-08-26 23:26 | 2016-08-27 00:25 | 10 | 59 | 4839931 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONE HOT LEG MELTED INTO ON CUST SERVICE DROP AT THE LASH TAKEOFF.. MADE BETTER CONNECTIONS CHECKED VOLTAGE TO BE GOOD.. CUST IS RESTORED PLEASE CLOSE TICKET CY VER/KEP
11325 | Hazard | 3312202 | ENGLE | GRAPEVINE | 2016-11-09 16:13 | 2016-11-09 17:12 | 10 | 59 | 4088191 | 590 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR UG | UNDERGROUND PEDESTAL BURNED UP SEVERAL SERVICES MELTED . WILL NEED TO REPLACE PEDESTAL & UNDERGROUND SERVICES .PULLED FUSE ON PADMOUNT XFMR37830126000170. MADE OPS ORDER #037750349 .WILL NEED TO WORK FIRST THING IN MORNING , PLANES IN HANGERS CANT OPEN DOORS . UNDERGROUND SERVICE SIZE 1/0 RELEASED BY CREW 075H04//ZEROED OUT CC @ 1745 //CUST SAID OK TO LEACE TO MORNING// AJB
11326 | Paintsville | 3402802 | PAINTSVILLE | NIPPA | 2009-02-02 23:01 | 2009-02-03 08:50 | 1 | 589 | 54943-1 | 589 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | 3402802 - INSULINK CONNECTION FROZE APART. REPLACED WITH SQUEEZ-ON. SH //VER/GAH
11327 | Hazard | 3303902 | LESLIE | WOOTON | 2019-04-15 00:01 | 2019-04-15 09:50 | 1 | 589 | 4110781 | 589 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | s. xfmr fuse out/// refused xfmr fuse power restored.
11328 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2016-01-02 20:39 | 2016-01-02 23:55 | 3 | 196 | 4581791 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | I NEED ONE MAN, BIG BUCKET AND FLAGGERS//COD 3// VER/DBM
11329 | Hazard | 3308502 | BONNYMAN | HAZARD | 2011-05-23 15:41 | 2011-05-23 17:05 | 7 | 84 | 4146691 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | WIRE BURNED OUT OF CUTOUT == REPLACED == PUT FUSE IN POWEROK VER/KEP
11330 | Hazard | 3303903 | LESLIE | HALSFORK | 2022-05-08 14:51 | 2022-05-08 19:45 | 2 | 294 | 4866351 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad xfmr 25 KVA 19.9, also need cutout, truck acess Released by crew 077S07. Power restored.
11331 | Paintsville | 3420103 | MAYO TRAIL | DAVIS BRANCH | 2016-11-29 13:36 | 2016-11-29 15:00 | 7 | 84 | H4142931 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, UG | *** SEE 4142931*** 25 KVA PADMOUNT TRANSFORMER BAD/ CREW ENROUTE TO REPLACE/ CREW ON SITE REPLACING PAD MOUNT/ PULLED ELBOW AT 811-183 (ADD 7 CUST) @ 1336 TO CHANGE BAD 50 KVA 38830811B10185 (ORIGINAL 5 CUT) ABOUT 12 CUSTOMERS OUTAGED TOTAL WHILE CHANGING PAD COUNTING THE 5 SERVIED OFF OF 811-185/ ALL POWER BACK ON AT 15:00/ NO CUSTOMERS SHOWN ON UNDERGROUND RISE FUSE 38830811B00062 AND NEED TO KNOW HOW MANY CUSTOMERS ON EACH UNDERGROUND XFMR/ ISO 38830811B10183/ COD 12/ VER/BOW
11332 | Cannonsburg | 3000903 | HIGHLAND | WURTLAND | 2017-05-30 10:21 | 2017-05-30 15:15 | 2 | 294 | 4881541 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 10 KVA, SINGLE BUSHING, CAN GET SMALL SERVICE BUCKET TO POLE, GO DOWN WALKER RD, TURN AT WALKER CEMENTRY AND FOLLOW MY TRACKS TO POLE. WILL BE CREW REQ RELEASED BY CREW 078S06--CREW ON SITE---TBL TKT COMP 39831098D00498 1515 VER/AWD
11333 | South Williamson | 3202202 | LOVELY | WOLFCREEK | 2011-07-26 07:48 | 2011-07-26 10:15 | 4 | 147 | 4623131 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | XFMR WAS CHANGED BUT OLD PORCELIN ARRESTER WAS NOT REMOVED AND HAS GONE BAD BLOWING LINE FUSE ON 818-5. THREE CUSTOMERS OUT. WILL HAVE TO CLIMB THIS POLE TO ELIMINATE BAD ARRESTER AS NEW XFMR HAS ONE ON IT AND THIS ONE ISNT NEEDED. RESTORED @ 10:15. SH RELEASED BY CREW 076S02 VER/KEP IDC XXXX
11334 | Pikeville | 3400303 | BETSYLAYN | HAROLD | 2013-04-12 08:02 | 2013-04-12 11:18 | 3 | 196 | 4002541 | 588 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | I OPENED TRANSFORMER ON POLE 1126-363 DUE TO BURNT CONNECTIONS. I HAVE REPAIRS MADE EVERYTHING OK. CLOSED TRANSFORMER BACK IN AT 11:18 OPENED TRANSFORMER AT 09:45.//COD 3// VER/DBM IDC XXXX
11335 | Paintsville | 3409302 | KENWOOD | AUXIER | 2016-04-06 23:46 | 2016-04-07 09:34 | 1 | 588 | 4061341 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | TRANSFORMER CUTOUT FAILED. WILL WORK IN THE AM AND RETURN WITH HELP TO WORK IT REPLACED CUTOUT AND RESTORED @ 9:34. SH VER/CRB
11336 | Hazard | 3310502 | HADDIX | CANOE | 2022-01-08 11:56 | 2022-01-08 16:50 | 2 | 294 | 4324731 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken 19.9 cutout. help on the way, p.hicks.. all power restored @ 16:50 p.hicks
11337 | Hazard | 3308401 | BECKHAM | HINDMAN | 2021-08-09 01:51 | 2021-08-09 11:39 | 1 | 588 | 4019941 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Dispatched in accordance with KYPCo Late Night Callout Guidelines bad cutout, calling for help power restored
11338 | Paintsville | 3401101 | FALCON | FALC-OILS | 2017-02-26 12:44 | 2017-02-26 16:00 | 3 | 196 | 4424041 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD LINE CUTOUT ON 830-51..CHANGING.
11339 | Hazard | 3309903 | SLEMP | BEECH FORK | 2015-05-15 06:51 | 2015-05-15 10:07 | 3 | 196 | 4431511 | 588 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | BAD REGULATOR IN STATION TOOK STATION XFMR OUT, BYPASSED REGULATORS RESTORED POWER AT 10:07. RELEASED BY CREW 077S11 VER/ARN
11340 | Whitesburg | 3309103 | WHITESBURG | COWAN | 2015-05-26 21:30 | 2015-05-26 23:08 | 6 | 98 | 4468911 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT , REPLACED CUTOUT RESTORED POWER AT 23:08./ ISO 37830472000145/ COD 6/ VER/BOW
11341 | Pikeville | 3411801 | JOHNSCREEK | META | 2017-07-04 11:48 | 2017-07-04 16:42 | 2 | 294 | 4071661 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT ON HILL BEHIND DW MAY BE BROKEN,SURGE ARRESTOR NEEDS REPLACED.WILL REPLACE PORCELIN CUTOUT WITH PLASTIC ONE WHILE ON POLE.NEED A B LINEMAN.ALSO A DD THERE TO REPAIR/REPLACE PER CUST(NOT WORKING)/////////REPAIRS COMPLETED,RESTORED VER/CRB
11342 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-08-31 11:44 | 2008-08-31 15:00 | 3 | 196 | 58002-1 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | ARRESTER | VER/HFP LINE FUSE OUT ON POLE 198-95.BAD ARRESTOR ON POLE198-216 .PHASE BEING OUT WAS CAUSING BACKFEED THROUGH XFMR BANK GIVING CUSTOMER LOW VOLTAGE.OPENED OTHER 2 PHASES AT 1440 ,CLOSED BACK IN AT 1500 ISO POLE 37830198D00095 COD - 7 //C PHASE 3 CUSTOMERS// A&B 4 IDCC PN183 XXXX
11343 | Hazard | 3310501 | HADDIX | QUICKSAND | 2010-01-25 07:29 | 2010-01-25 10:45 | 3 | 196 | 59219-1 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | STS WR # 33573747 // ON POLE 53-21 LOOP IS BROKE ON TAP FEEDING LANE BR. AND ONE WIRE ON MAIN LINE IS BROKE. GREG SHOUSE IS GOING TO COME AND FIX IT RELEASED BY CREW 077S05 VER/HFP L3/HFP IDCC PN43 XXXX
11344 | Pikeville | 3409502 | BURDINE | LEVISA | 2020-08-29 15:10 | 2020-08-29 16:48 | 6 | 98 | 4400761 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | We have a cracked cutout on pole 312-94,Got pole fire put out,going to change cutout and restore service,,Restored at 16:48.
11345 | South Williamson | 3408303 | COLEMAN | PETERCRK | 2013-01-05 08:06 | 2013-01-05 09:30 | 7 | 84 | 4570101 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | REMOVED BAD CURRENT LIMITING FUSE ON TRANSFORMER. POWER RESTORED. COD-7 ISO TF38821137A00177 VER/HFP L3/HFP IDC XXXX
11346 | South Williamson | 3200302 | BELFRY | TOLER | 2019-07-07 14:20 | 2019-07-07 15:58 | 6 | 98 | 4673461 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | opened l/f 1420 38821013C00060 pole fire L3/HFP
11347 | Paintsville | 3420102 | MAYO TRAIL | EUCLID | 2015-09-11 16:16 | 2015-09-11 17:40 | 7 | 84 | 4229511 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | FUSE BROKE IN XFMER CUTOUT///REFUSED AT 17:40///COMPLETE/ ISO 38830785D41361/ COD 7/ VER/BOW L3/DKG
11348 | Pikeville | 3400601 | BURTON | BEVINSONVILLE | 2015-04-26 07:26 | 2015-04-26 12:20 | 2 | 294 | 4366581 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | 6T FUSE LOOKS LIKE IT BROKE FUSED UP EVERYTHING OK/ ISO 37830163B00194/ COD 2/ VER/BOW
11349 | Cannonsburg | 3000701 | GRAYSBRAN | GRAYSBRAN | 2011-08-05 22:52 | 2011-08-06 00:30 | 6 | 98 | 4670031 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FOUND A BAD DEARBURD CUTOUT, HAVE IT CHANGED AND POWER IS RESTORED AT THIS LOC IDC XXXX
11350 | Cannonsburg | 3103101 | OLIVEHILL | GLOBE | 2014-06-21 06:20 | 2014-06-21 16:08 | 1 | 588 | 4133351 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | CREW REQUIRED BAD 25 KVA TRUCKS OK RELEASED BY CREW 078S03 VER/CRB
11351 | Paintsville | 3409003 | W.PAINTSVILLE | PLAZA | 2012-02-07 14:49 | 2012-02-07 18:05 | 3 | 196 | 4326671 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONN/CLAMP | WRONG METER GIVEN BY CUSTOMER. CONNECTION FAILED ON XFMR 784-91. WILL HAVE XFMR OPEN FOR 45 MINUTES TO RE-WORK CONNECTIONS. NO TRUCK ACCESS. DONT HAVE PROPER WIRE SIZE ON TRUCK - GOING IN TO PAINTSVILLE OFFICE. OPENED XFMR @ 17:15 AND CLOSED @ 18:05. SH//COD 1 + 2 IDC XXXX
11352 | Paintsville | 3409301 | KENWOOD | W VANLEAR | 2014-11-22 05:44 | 2014-11-22 09:00 | 3 | 196 | 4753161 | 588 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BAD CUTOUT.CHANGING VER/TOM L3/TOM
11353 | Pikeville | 3409402 | FEDSCREEK | LICKCREEK | 2010-01-06 21:53 | 2010-01-07 07:40 | 1 | 587 | 64435-1 | 587 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | ONLY ONE CUSTOMER OUT SERVICE DROP BURNED DOWN. I INSTALLED A NEW SERVICE. VER/HFP L3/HFP IDC XXXX
11354 | Hazard | 3310501 | HADDIX | QUICKSAND | 2018-11-05 08:59 | 2018-11-05 18:46 | 1 | 587 | 4363661 | 587 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | OPEN WIRE SECONDARY DOWN L3/HFP
11355 | Paintsville | 3403301 | PRESTONSBURG | CITY | 2020-12-13 00:01 | 2020-12-13 09:47 | 1 | 586 | 4764091 | 586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 10 kva is bad . will need 10 kva 7200 /120/240 ,material handler &1 a lineman Released by crew 074S04
11356 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2022-08-25 19:12 | 2022-08-26 00:05 | 2 | 293 | 4795401 | 586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | bad 25kva 19.9v transformer no trucks back yard machine or utv ok crew on site FETR 00:30 LRM all pwr restored 00:05
11357 | Cannonsburg | 3003703 | COALTON | TRACECREEK | 2021-05-09 15:29 | 2021-05-10 01:15 | 1 | 586 | 4554941 | 586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | replaced broke cutout. power restored at 0115
11358 | South Williamson | 3202203 | LOVELY | MT.STERLING | 2009-09-21 04:37 | 2009-09-21 09:30 | 2 | 293 | 55985-1 | 586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3202203// WILL DISPATCH IN THE MORNING CUTOUT BAD//COD 2// VER/DBM IDC XXXX
11359 | Hazard | 3301701 | DAISY | LEATHERWOOD | 2010-03-28 11:59 | 2010-03-28 16:52 | 2 | 293 | 55189-1 | 586 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 34423087 //RELEASED BY CREW 077S03.. BAD CUTOUTRELEASED BY CREW 077S03.. BAD CUTOUT .... REPLACED CUTOUT RESTORED POWER AT 16:52 VER/HFP L3/HFP IDC XXXX
11360 | Pikeville | 3410502 | S.PIKEVILLE | ISLANDCREEK | 2012-04-28 15:57 | 2012-04-28 19:12 | 3 | 195 | 4720281 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | XFR FUSE IS OUT,WILL RE-FUSE///////BAD 7.2 XFR 25 KVA,NEE 4WD MAT HANDLER,1 MAN,BELIEVE WE CAN GET TRUCK CLOSE ENOUGH,ALSO NEED CUTOUT AND ARRESTOR//////REPLACED XFR AND RESTORED POWER,ALL OK AFTERWARDS COD-3 ISO TF 37830071000028 VER/HFP L3/HFP IDC XXXX
11361 | Cannonsburg | 3003701 | COALTON | U.S.60 W | 2012-01-09 10:30 | 2012-01-09 13:45 | 3 | 195 | 4242061 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 15KVA XFORMER ON POLE 186-106, FIRST OPLE ON LEFT AS YOU TURN ON GEIGER LN. TRUCKS TO POLE OK. HIGH VOLTAGE 276 PHASE TO PHASE AND 136 PHASE TO GROUND. RELEASED BY CREW 078S01 VER/KEP IDCC PN197, CNT1 XXXX
11362 | South Williamson | 3411401 | DEWEY | INEZ | 2009-02-22 10:47 | 2009-02-22 20:32 | 1 | 585 | H50287-1 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED RECL @ 1145 CLOSED @ 1222TOP BLOWED OFF TRANSFTOP BLOWED OFF TRANSF RELEASED BY CREW 079S01// CREW ON SITE CHANGING POT OUT TCM//WAITING ON 2-HOLE PADS FROM PIKEVILLE// RESTORED AT 2032 //VER/GAH IDCC DUP FOR FIRST CUSTOMER OUT XXXX
11363 | Cannonsburg | 3008701 | CANNONSBURG | CANNONSBURG | 2011-05-17 21:00 | 2011-05-18 00:15 | 3 | 195 | 4107121 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | STS WR # 40007020 //BAD 19.9 CUTOUT ON POLE 188-510.THIS IS IN HORSE LOT. NO TRUCKS TO POLE.BAD 19.9 CUTOUT ON POLE 188-510.THIS IS IN HORSE LOT. NO TRUCKS TO POLE. RELEASED BY CREW 078S01/CREW ON SITE MAKING REPAIRSSTS WR # 40007020 //BAD 19.9 CUTOUT ON POLE 188-510.THIS IS IN HORSE LOT. NO TRUCKS TO POLE.BAD 19.9 CUTOUT ON POLE 188-510.THIS IS IN HORSE LOT. NO TRUCKS TO POLE. RELEASED BY CREW 078S01/CREW ON SITE MAKIN/REPAIRS COMP.POWER RESTORED @00:15 J. HEMLEPP & CREW
11364 | Hazard | 3308502 | BONNYMAN | HAZARD | 2013-12-15 16:00 | 2013-12-15 17:05 | 9 | 65 | 4163681 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | OPENED LINE FUSE TO SAFELY MAKE REPAIRS ON TIX 4163211//OPENED AT 16:00 CLOSED AT 17:05 VER/CRB L3/HFP HFPC CCSCO FEC57
11365 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2014-09-10 13:15 | 2014-09-10 14:20 | 9 | 65 | 4485551 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CONDUCTOR OVERHEAD | BAD 6A PRIMARY @ POLE 523-84// OPEN LINE FUSE 523-31 TO REPLACE CONDUCTOR OPENED LINE FUSE ON 523-31 AT 13:15 RESTORED POWER AT 14:20 PLEASE CLOSE TICKET THANKS DWW// VER/BOW
11366 | Hazard | 3311701 | SHAMROCK STATION | SHAMROCK | 2014-04-04 10:05 | 2014-04-04 13:20 | 3 | 195 | 4572581 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | FUSE BLOWN ON POLE 223A-198 AT SEC CRK CHURCH--TRIED REFUSING--FUSE STAYED A MIN THEN BLEW--NEED ROW CREW TO CLEAR UP PINE TREES AT CUST XFRM POLE.--4/4--11:55 BK RELEASED BY CREW 077M01 == BAD CUTOUT ON POLE 37830223B00201 == REPLACED REFUSED POWER OK//COD 3//ISO 37830223A00198// VER/DBM
11367 | Cannonsburg | 3002101 | 10TH STREET | 6TH STREET | 2010-10-29 15:00 | 2010-10-29 18:15 | 3 | 195 | 50007-1 | 585 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | STS WR # 37550991 // BAD 25KVA TWO BUSHING 120/240 TRANSBAD 25KVA TWO BUSHING 120/240 TRANS RELEASED BY CREW 078S08CREW ON SITE//REPLACED A PHASE TRANSFORMER CHECKED VOLTAGE 120/208 ALL POWER RESTORED AT 18:15 PR TOLLIVER// VER/HFP L3/HFP IDC DCMT XXXX
11368 | Pikeville | 3401702 | HENRYCLAY | REGINA | 2013-06-29 20:43 | 2013-06-30 01:35 | 2 | 292 | 4428781 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | TRANS. FUSE IS BLOWN IN BANK OF TANSFORMERS. I AM GOING TO REFUSE TRANS. I THINK 1 OF THE TRANSFORMERS IN THIS BANK IS BAD. I CALLED FOR HELP. WE CHANGED BAD TRANS. . VER/TOM L3/TOM
11369 | Cannonsburg | 3110903 | WURTLAND | RT.503 | 2018-08-09 10:04 | 2018-08-09 12:30 | 4 | 146 | 4932151 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broken c/o on pole 1146-154, will need crew to change, can use truck, right beside of road, c/o split in half is close to pri, i can not to to l/f to load bust open. will be crew req Released by crew 078S06
11370 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2018-06-24 19:11 | 2018-06-24 20:24 | 8 | 73 | 4658491 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | FUSE | broken fuse..replaced fuse,,all power restored/ ISO 38830142A00120/ COD 8
11371 | Whitesburg | 3309104 | WHITESBURG | CRAFTS COLLEY | 2011-09-13 09:23 | 2011-09-13 14:15 | 2 | 292 | 4863561 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3309104 / CSP TRANSFORMER WILL NOT GO IN , WILL NEED CREW TO CHANGE XFMR, 15 KVA XFMR AND CUTOUT THIS IS MANUAL RELEASED BY CREW 077S12 //VER/CRB IDC XXXX
11372 | Hazard | 3310501 | HADDIX | QUICKSAND | 2009-04-06 13:33 | 2009-04-06 18:25 | 2 | 292 | 66487-1 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | VER/HFP COD-2 BAD CUT OUT ;; MAY HAVE SOMETHING ON THE LINE ;;LBAD CUTOUT ON POLE 53 ANDS TREE ON LINE AT POLE 48 L3/HFP IDC XXXX
11373 | Cannonsburg | 3008702 | CANNONSBURG | ROUTE 3 | 2021-08-16 12:36 | 2021-08-16 15:02 | 4 | 146 | 4079421 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | broke c/o @ 118-B-157 lifted ht on pole 118-B-37 at 14:30 repairs made ht put on at 15:02 LR- 1st All out came in at 12:36
11374 | Paintsville | 3409002 | W.PAINTSVILLE | STAFFORDSVILLE | 2021-04-10 09:05 | 2021-04-10 18:15 | 2 | 550 | 4437221 | 584 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | Bad hot leg in 350 URD secondary, Rick Ray gonna bring add-a-phase trans. until we can get located and repaired. Had to open padmount @784-C2-585 to install add-a-phase, opened @1741, closed back in @1815.
11375 | Hazard | 3308002 | JACKSON | PANBOWL | 2008-08-14 19:17 | 2008-08-14 20:30 | 8 | 73 | 52114-1 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | 3308002//BAD CUTOUT... REPLACED CUTOUT RESTORED POWER AT 20:30//COD 8// VER/DBM IDC XXXX
11376 | Pikeville | 3401703 | HENRYCLAY | ASHCAMP | 2018-12-06 10:54 | 2018-12-06 13:20 | 4 | 146 | 4512331 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Xfm fuse blown will refuse// Replaced bad cutout and restored service @ 13:20 COD-4 ISO TF 37820241B00160
11377 | Pikeville | 3401002 | ELWOOD | VIRGIE-IN | 2018-06-19 21:53 | 2018-06-20 02:45 | 2 | 292 | 4625841 | 584 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | Cutout busted and pole covered in vines @ 166-126, will be making repairs. Changed cut-out and removed vines, closed back in @0245.
11378 | Paintsville | 3401101 | FALCON | FALC-OILS | 2020-09-11 16:29 | 2020-09-11 21:20 | 2 | 291 | 4452641 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | Bad 25 KVA transformer on 806-136. No truck access. Replaced and restored @ 21:20. sh
11379 | Hazard | 3308402 | BECKHAM | CARR CREEK | 2010-07-13 09:01 | 2010-07-13 12:15 | 3 | 194 | 65838-1 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | BROKE CUTOUT ON POLE 302-126, TOOK HOT TAP OFF POLE 302-71, REPLACED CUTOUT BUT SEEN TERRIBLE R-O-W, CALLED ASPLUNDH TO CUT WHILE POWER ON TAP IS OFF ON @ 1215 VER/HFP L3/HFP IDC XXXX
11380 | Paintsville | 3401801 | INDEX | DISTRIBUTION | 2015-03-21 20:56 | 2015-03-22 01:47 | 2 | 291 | 4216911 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | CUTOUT BURNED UP ON 825-10 ON TOP OF BUCKARM..NEED BIG BUCKET 1 MAN AND FLAGGERS..BACK ON AT 1.47 VER/TOM L3/TOM
11381 | Hazard | 3308502 | BONNYMAN | HAZARD | 2008-12-17 10:21 | 2008-12-17 15:12 | 2 | 291 | 59493-1 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | 3308502//== BAD TRANSF 10 KVA 19.9//.........REPLACED BAD TRANSFORMER.....GOOD VOLTAGE....W.M./R.R.//COD 2// VER/DBM L3/KEP IDC XXXX
11382 | Cannonsburg | 3002105 | 10TH STREET | MIDTOWN | 2008-01-30 12:03 | 2008-01-30 16:54 | 2 | 291 | 62243-1 | 582 | PARTIAL POWER | EQUIPMENT FAILURE | CONN/CLAMP | 3002105//HOT TAP BROKE ON MIDDLE PHASE WAITING ON HELPCOMP 1700 PM//COD 2// VER/DBM IDC XXXX
11383 | South Williamson | 3200302 | BELFRY | TOLER | 2018-03-29 08:52 | 2018-03-29 18:34 | 1 | 582 | 4145781 | 582 | PARTIAL POWER | EQUIPMENT FAILURE | CONDUCTOR UG | One leg of the secondary underground going to the car wash is bad. This is 350 aluminum. Made repairs checked voltage and restored power at 18:34 Tim McCoy
11384 | Cannonsburg | 3007905 | BUSSEYVILLE | MATTIE | 2011-09-07 08:29 | 2011-09-07 13:20 | 2 | 291 | 4841801 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | BAD 25 KVA XMF NO TRUCKS TO POLE RELEASED BY CREW 078S11 VER/KEP IDC XXXX
11385 | Hazard | 3308002 | JACKSON | PANBOWL | 2015-09-11 20:56 | 2015-09-12 00:10 | 3 | 194 | 4230091 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | TRANSFORMER, OH | GOT A BAD 25 KVA 7200 TRANSFORMER NEED TRANSFORMER CUTOUT TWO MEN BIG BUCKET RELEASED BY CREW 077S05 REPLACED TRANSFORMER AND RESTORED POWER AT 12:10 VER/SEF
11386 | Pikeville | 3402002 | KEYSER | STONECOAL | 2015-02-22 07:30 | 2015-02-22 12:21 | 2 | 291 | 4070121 | 582 | PARTIAL POWER | EQUIPMENT FAILURE | TRANSFORMER, OH | 1 XF OUT ON 3PHASE BANK HERE,NEED TO REPLACE XFR,APPEARS TO BE PUSHING OIL OUT OF BUSHING,DID NOT RE-FUSE IT.NEED 25KVA,MAT HANDLER,1MAN///////////REPLACED XFR,RESTORED,ALL OK AFTERWARDS/// TRANSFORMER 38821105C00152 IS THE ONE THAT WAS OFF// CUSTOMER MISMAPPED MD DONE // ISO 38821105C00152/ COD 3** I CHANGED IT TO 3 CUSTOMERS IN POWER ON BUT AFTER DISCREPANCY IT STILL SHOWS TWO CUSTOMERS/ VER/BOW
11387 | Hazard | 3309904 | SLEMP | ROYAL DIAMOND | 2015-05-15 06:51 | 2015-05-15 10:05 | 3 | 194 | 4431501 | 582 | DISTRIBUTION STATION | EQUIPMENT FAILURE | REGULATOR | BAD REGULATOR IN STATION TOOK STATION XFMR OUT, BYPASSED REGULATORS RESTORED POWER AT 10:05. RELEASED BY CREW 077S11 VER/ARN
11388 | Cannonsburg | 3110902 | WURTLAND | GREENUP | 2015-10-27 04:45 | 2015-10-27 09:36 | 2 | 291 | 4378851 | 582 | DISTRIBUTION LINE | EQUIPMENT FAILURE | CUTOUT | DDC HOLD TAG // FOUND BAD CUTOUT ON POLE 1073-92, OPEN UP LINE FUSE ON POLE 1073=85, JUST A SINGLE LINE TAP, NO GROUNDS, CREW REQ, NO TRUCKS, CLIMB JOB POLE IS TAGGED TO DDC // DDC HOLD TAG PLACED,CUTOUT REPLACED ALL CUST RESTORED @ 0936 PLEASE CLOSE TICKET THANKS.BT/ ISO 39831073B20085/ COD 2/ VER/BOW